## All Outage Details
HFTD WIRE-DOWN OUTAGE DETAILS (2013 - 2024) |  |  |  | Source: Extracted from Outage Database on 1/8/2025.
DISTRIBUTION CIRCUIT & TRANSFORMER-ONLY OUTAGES
(2.5b ME Days Only)
Division | Tier | Feeder Name | Feeder # | Device | Oper # | Date | FNL | OIS # | Duration | Outage Level | Basic Cause | Supplemental Cause | CESO | C Min | Weather | Failed/Involved Equipment | Equipment Condition | ILIS # | Const Type | Sus/Mom | PM # | Year | Month | Wire Down | Outage Fault Type | MEDay | Conductor Energized
DIABLO | Tier 2 | MORAGA-1104 | 13801104 | OTHER |  | 20141211 | 724 | 1131079 | 184 | Distribution Circuit | Equipment Failure/Involved | Other | 50 | 9200 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0075193 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
DIABLO | Tier 2 | ROSSMOOR-1101 | 14161101 | FUSE | 2649 | 20141211 | 1729 | 1135141 | 1308 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 3924 | Heavy rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0075788 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
DIABLO | Tier 3 | TASSAJARA-2112 | 14662112 | RECLOSER | 6392 | 20141211 | 638 | 1133429 | 2136 | Distribution Circuit | Equipment Failure/Involved | Other | 32 | 55978 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076234 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
DIABLO | Tier 3 | MORAGA-1101 | 13801101 | FUSE | 7123 | 20160305 | 1631 | 1417302 | 653 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 43206 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017600 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
DIABLO | Tier 3 | MORAGA-1101 | 13801101 | JUMPER | WIRE DOWN @ 236 EL TOYONAL | 20160305 | 1931 | 1418518 | 745 | Distribution Circuit | Vegetation | Tree - fell into line | 220 | 144349 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018145 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
DIABLO | Tier 2 | MORAGA-1104 | 13801104 | TRANSFORMER | 315232749960 | 20160305 | 1435 | 1416785 | 476 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1428 | Overcast-Drizzle-32-90 F | Transformer | Broken, wire on ground | 16-0017569 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | SOBRANTE-1102 | 14671102 | FUSE | 20534 | 20160305 | 2059 | 1419310 | 442 | Distribution Circuit | Vegetation | Tree - branch fell on line | 77 | 34034 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018036 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | ROSSMOOR-1101 | 14161101 | SECTIONALIZER | L551S | 20170103 | 2149 | 1617025 | 549 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1079 | 68015 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003314 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
DIABLO | Tier 3 | CLAYTON-2212 | 12022212 | FUSE | 12151 | 20170108 | 649 | 1625435 | 674 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 10110 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005186 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | MORAGA-1104 | 13801104 | OCB | 1104/2 | 20170108 | 1145 | 1625793 | 908 | Distribution Circuit | Vegetation | Tree - fell into line | 1708 | 706554 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0005237 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
DIABLO | Tier 3 | MORAGA-1105 | 13801105 | FUSE | 7194 | 20170108 | 654 | 1622872 | 1809 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 4905 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005423 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
DIABLO | Tier 3 | CLAYTON-2212 | 12022212 | FUSE | 12151 | 20170110 | 1831 | 1639207 | 1835 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 27525 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008230 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | LAS AROMAS-0401 | 13600401 | RECLOSER | 3342 | 20170110 | 1215 | 1633185 | 866 | Distribution Circuit | Vegetation | Tree - fell into line | 174 | 61530 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006571 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
DIABLO | Tier 2 | ALHAMBRA-1105 | 14101105 | FUSE | 1708 | 20170122 | 1037 | 1659787 | 550 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 3275 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0013028 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | Yes
DIABLO | Tier 2 | SOBRANTE-1102 | 14671102 | FUSE | 20534 | 20170207 | 111 | 1677318 | 427 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 32452 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018033 | OH | Sus | 31304292 | 2017 | FEB | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | TASSAJARA-2112 | 14662112 | RECLOSER | D514R | 20170207 | 2250 | 1681188 | 1273 | Distribution Circuit | Vegetation | Tree - fell into line | 1257 | 133984 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018811 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
DIABLO | Tier 2 | CLAYTON-2212 | 12022212 | FUSE | 14795 | 20170406 | 2043 | 1747043 | 2780 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 11120 | Overcast-Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0037948 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | TASSAJARA-2109 | 14662109 | OTHER | WIRE DOWN IRO 5433 OLD SCHOOL RD | 20171020 | 801 | 1905576 | 597 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 23826 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0089040 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | Yes
DIABLO | Tier 2 | CLAYTON-2212 | 12022212 | FUSE | 15535 | 20190117 | 240 | 274210 | 1190 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 10970 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011114 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
DIABLO | Tier 2 | ORINDA-0401 | 12350401 | OTHER | WIRE DOWN CORNER OF LA CINTILLA AND DIAS DOR | 20190214 | 2212 | 311050 | 240 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 5406 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0023752 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
DIABLO | Tier 2 | ROSSMOOR-1101 | 14161101 | FUSE | 6599 | 20190215 | 3 | 311057 | 661 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 27762 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023808 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
DIABLO | Tier 3 | CLAYTON-2212 | 12022212 | FUSE | 9264 | 20190217 | 753 | 315343 | 302 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 4530 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025051 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
DIABLO | Tier 2 | SOBRANTE-1102 | 14671102 | FUSE | 6597 | 20190227 | 40 | 325950 | 693 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 28413 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028748 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
DIABLO | Tier 2 | ALHAMBRA-1105 | 14101105 | FUSE | 7646 | 20200209 | 808 | 781136 | 411 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 7398 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0018960 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | Yes
DIABLO | Tier 2 | ALHAMBRA-1105 | 14101105 | OTHER | WIRE DOWN 1175 GARCIA RANCH RD | 20200927 | 1329 | 1095205 | 547 | Distribution Circuit | Vegetation | Tree - branch fell on line | 402 | 25980 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0102102 | OH | Sus | 31514676 | 2020 | SEP | Yes | Line to Ground | Yes | Yes
DIABLO | Tier 2 | CLAYTON-2215 | 12022215 | RECLOSER | 812394 | 20211024 | 758 | 1508525 | 600 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 17400 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135726 | OH | Sus | 0 | 2021 | OCT | Yes | Force Out | Yes | No
DIABLO | Tier 3 | ORINDA-0402 | 12350402 | FUSE | 275689 | 20211024 | 1036 | 1510041 | 273 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 16653 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136039 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | SOBRANTE-1102 | 14671102 | FUSE | 1151 | 20230110 | 230 | 1940798 | 1067 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 75757 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0012606 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | SOBRANTE-1103 | 14671103 | FUSE | 1160 | 20230110 | 225 | 1944248 | 1296 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 103680 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0012141 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | ROSSMOOR-1101 | 14161101 | FUSE | 6599 | 20230221 | 1618 | 1993081 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 18409 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0031574 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
EAST BAY | Tier 3 | BERKELEY F-1103 | 12061103 | FUSE | 8029 | 20131121 | 1949 | 908830 | 2608 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 28688 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0078749 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
EAST BAY | Tier 3 | OAKLAND K-1102 | 12101102 | FUSE | 172497 | 20131121 | 1849 | 908059 | 843 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 21918 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0078278 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE | 9428 | 20131121 | 2032 | 909208 | 804 | Distribution Circuit | Vegetation | Tree - bark fell into line | 44 | 35376 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078341 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | RECLOSER | CR214 | 20131121 | 1857 | 908099 | 1697 | Distribution Circuit | Vegetation | Tree - fell into line | 422 | 225292 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078070 | OH | Sus | 31038174 | 2013 | NOV | Yes | None | Yes
EAST BAY | Tier 2 | OAKLAND K-1103 | 12101103 | FUSE | 6533 | 20131122 | 311 | 910794 | 1809 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 136069 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078427 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | FUSE | 9024 | 20131122 | 641 | 911048 | 1611 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 105823 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078446 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | OTHER |  | 20131122 | 1857 | 912995 | 254 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1200 | 53781 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078764 | OH | Sus | 0 | 2013 | NOV | Yes | None | Yes
EAST BAY | Tier 2 | OAKLAND X-1106 | 12541106 | FUSE | 6639 | 20141203 | 1407 | 1123348 | 674 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 674 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0073553 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
EAST BAY | Tier 2 | OAK-0401 | 12600401 | OCB | OCB | 20141211 | 342 | 1128964 | 998 | Distribution Circuit | Equipment Failure/Involved | Other | 1011 | 150431 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0074841 | OH | Sus | 31120520 | 2014 | DEC | Yes | Line to Ground | Yes
EAST BAY | Tier 2 | EDES-1112 | 13681112 | RECLOSER | CR282 | 20141230 | 1355 | 1152491 | 409 | Distribution Circuit | Vegetation | Tree - fell into line | 1022 | 78068 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079107 | OH | Sus | 31123832 | 2014 | DEC | Yes | Line to Ground | Yes
EAST BAY | Tier 2 | SAN LEANDRO-1109 | 13111109 | FUSE | 9077 | 20141230 | 1739 | 1154510 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 24480 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079485 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE | 8940 | 20150206 | 1428 | 1175827 | 543 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 13032 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010355 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
EAST BAY | Tier 2 | SAN LEANDRO-1109 | 13111109 | FUSE | 9859 | 20150206 | 1021 | 1174507 | 376 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 14664 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010057 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
EAST BAY | Tier 2 | FLORENCE-0401 | 12690401 | OCB | OCB | 20151213 | 743 | 1360231 | 280 | Distribution Circuit | Vegetation | Tree - fell into line | 479 | 35020 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 15-0084558 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | OTHER | CR022 | 20151213 | 923 | 1360762 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 676 | 67870 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084701 | OH | Sus | 31205544 | 2015 | DEC | Yes | Open Circuit | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1102 | 12101102 | FUSE | 6589 | 20160217 | 2151 | 1407396 | 634 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 19107 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013482 | OH | Sus | 31219888 | 2016 | FEB | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | JUMPER | WIRE DOWN WESTOVER AND SHELTERWOOD | 20160217 | 1757 | 1406157 | 663 | Distribution Circuit | Vegetation | Tree - bark fell into line | 117 | 32864 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013324 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | Yes
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | JUMPER | WIRE DOWN 2/N/O 9024 | 20160305 | 2058 | 1419340 | 474 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 29762 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018006 | OH | Sus | 31222882 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | FUSE | 9089 | 20160305 | 2259 | 1420616 | 818 | Distribution Circuit | Vegetation | Tree - fell into line | 233 | 51016 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018093 | OH | Sus | 31222882 | 2016 | MAR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | SAN LEANDRO-1109 | 13111109 | RECLOSER | CR182 | 20160305 | 2100 | 1419339 | 840 | Distribution Circuit | Vegetation | Tree - fell into line | 419 | 83790 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017860 | OH | Sus | 31222882 | 2016 | MAR | Yes | Multi-Fault | Yes | No
EAST BAY | Tier 2 | EL CERRITO G-1105 | 12501105 | RECLOSER | BR160 | 20170108 | 1544 | 1627794 | 1481 | Distribution Circuit | Vegetation | Tree - fell into line | 2152 | 143997 | Overcast-Rain-32-90 F | Conductor, Overhead | On Ground | 17-0005469 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1102 | 12101102 | FUSE | 1369 | 20170108 | 1041 | 1625023 | 1579 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 93062 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005216 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | SAN LEANDRO-1109 | 13111109 | FUSE | 9166 | 20170108 | 957 | 1624525 | 353 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 6707 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005230 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 2 | OAKLAND J-1102 | 12091102 | FUSE | 6651 | 20170110 | 1317 | 1633358 | 919 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 42274 | Heavy Rain-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006655 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAKLAND K-1103 | 12101103 | FUSE | 7970 | 20170110 | 1334 | 1633406 | 366 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 8784 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006685 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE | 6465 | 20170110 | 1623 | 1634295 | 1138 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 39830 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006860 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | FUSE | 81195 | 20170110 | 1228 | 1633278 | 1006 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 14084 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006634 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAKLAND X-1106 | 12541106 | FUSE | 2457 | 20170111 | 19 | 1638166 | 1195 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 10755 | Overcast-Fog-Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007370 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAKLAND X-1106 | 12541106 | FUSE | 9749 | 20170123 | 433 | 1662783 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 10875 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013605 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
EAST BAY | Tier 2 | OAKLAND J-1102 | 12091102 | FUSE | 6673 | 20170207 | 304 | 1677526 | 610 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 17962 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018118 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | RECLOSER | CR206 | 20170207 | 604 | 1678074 | 506 | Distribution Circuit | Vegetation | Tree - branch fell on line | 221 | 27636 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018169 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAKLAND X-1106 | 12541106 | FUSE | 6935 | 20170218 | 619 | 1698965 | 1686 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 40464 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022917 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1102 | 12101102 | OTHER | WIRE DOWN 6995 ELVERTON DR | 20170221 | 33 | 1706964 | 1029 | Distribution Circuit | Vegetation | Tree - fell into line | 1323 | 345024 | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024836 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 2 | OAKLAND X-1106 | 12541106 | SWITCH | CR21 | 20170222 | 1705 | 1711077 | 609 | Distribution Circuit | Vegetation | Tree - fell into line | 1658 | 36593 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025740 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | BERKELEY F-1103 | 12061103 | FUSE | R8029 | 20170406 | 2052 | 1746827 | 1725 | Distribution Circuit | Vegetation | Tree - fell into line | 1931 | 22619 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037714 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 2 | FRANKLIN-1104 | 13921104 | OTHER | P136 | 20170406 | 2113 | 1749290 | 837 | Distribution Circuit | Equipment Failure/Involved | Overhead | 82 | 67233 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037545 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | Yes
EAST BAY | Tier 2 | OAKLAND K-1104 | 12101104 | RECLOSER | CR210 | 20170406 | 2131 | 1747837 | 1084 | Distribution Circuit | Equipment Failure/Involved | Overhead | 417 | 97411 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037451 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | OTHER | WIRE DOWN CORNER CHELTON LN & BAG S/S MTR 100 | 20170406 | 2025 | 1747442 | 505 | Distribution Circuit | Vegetation | Tree - branch fell on line | 154 | 67942 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037583 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | FUSE | 1353 | 20170406 | 2327 | 1748783 | 1873 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 91176 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0038059 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAKLAND X-1106 | 12541106 | SWITCH | 1454 | 20170407 | 623 | 1749549 | 796 | Distribution Circuit | Equipment Failure/Involved | Overhead | 204 | 29614 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037609 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | SAN LEANDRO-1109 | 13111109 | RECLOSER | CR182 | 20170407 | 114 | 1749128 | 1064 | Distribution Circuit | Equipment Failure/Involved | Overhead | 420 | 300305 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037629 | OH | Sus | 0 | 2017 | APR | Yes | Three Phase Fault | Yes | No
EAST BAY | Tier 2 | FLORENCE-0401 | 12690401 | OCB | 401/2 | 20171216 | 1622 | 1945670 | 414 | Distribution Circuit | Equipment Failure/Involved | Overhead | 492 | 63550 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102194 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | BERKELEY F-1103 | 12061103 | FUSE | R8029 | 20190106 | 1440 | 255424 | 714 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 9282 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005153 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAK SUB | 1260 | OCB | 401/2 | 20190116 | 1713 | 268446 | 654 | Distribution Circuit | Vegetation | Tree - fell into line | 1012 | 351822 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009986 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE | 9151 | 20190117 | 1237 | 273989 | 228 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 16188 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011128 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 2 | RIDGE-0401 | 12840401 | FUSE | R7941 | 20190202 | 602 | 286601 | 891 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 53460 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016981 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAKLAND K SUB | 1210 | OCB | 172 | 20190214 | 1113 | 308726 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 10992 | 808191 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023258 | OH | Sus | 31425494 | 2019 | FEB | Yes | Line to Line | Yes | No
EAST BAY | Tier 2 | SAN LEANDRO-1109 | 13111109 | FUSE | 9166 | 20190608 | 2045 | 401833 | 1094 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 20786 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0064773 | OH | Sus | 31452134 | 2019 | JUN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAKLAND J-1106 | 12091106 | FUSE | 67575 | 20200209 | 819 | 781217 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 72834 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0018981 | OH | Sus | 31490427 | 2020 | FEB | Yes | Three Phase Fault | Yes | No
EAST BAY | Tier 2 | BOSTON-0401 | 13320401 | OTHER | 1 PHASE DOWN C/O LEIMERT MONTEREY | 20210119 | 322 | 1214410 | 437 | Distribution Circuit | Equipment Failure/Involved | Overhead | 314 | 124442 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010158 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 2 | EL CERRITO G-1105 | 12501105 | FUSE | R8474 | 20210119 | 648 | 1215170 | 430 | Distribution Circuit | Company Initiated | Improper Construction | 136 | 58480 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010425 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | EL CERRITO G-1105 | 12501105 | FUSE | R8236 | 20210119 | 1215 | 1217017 | 442 | Distribution Circuit | Equipment Failure/Involved | Overhead | 117 | 51714 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010755 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAKLAND K-1102 | 12101102 | OCB | 1102/2 | 20210119 | 646 | 1215189 | 411 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1340 | 357711 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010280 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | OTHER | WIRE DOWN LOAD SIDE OF 9880 | 20210119 | 946 | 1216517 | 422 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1266 | Clear-32-90 F | Conductor, Overhead | On Ground | 21-0010704 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 2 | SPRUCE-0402 | 13340402 | FUSE | R3383 | 20210119 | 726 | 1215589 | 591 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 12411 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010529 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE | 9541 | 20211024 | 907 | 1509040 | 527 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 13608 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136022 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | EDES-1112 | 13681112 | FUSE | 6787 | 20211214 | 530 | 1569702 | 596 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2384 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0157820 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | PALO SECO-0401 | 13180401 | FUSE | 4137 | 20230314 | 850 | 2035370 | 309 | Distribution Circuit | Vegetation | Tree - fell into line | 307 | 87130 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0044645 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
MISSION | Tier 3 | CASTRO VALLEY-1108 | 14091108 | RECLOSER | MR243 | 20141230 | 1330 | 1152313 | 435 | Distribution Circuit | Vegetation | Tree - fell into line | 394 | 71393 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0079088 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
MISSION | Tier 2 | CAYETANO-2111 | 14422111 | FUSE | 71835 | 20141230 | 1820 | 1154724 | 365 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 8255 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079393 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
MISSION | Tier 2 | VINEYARD-2107 | 14502107 | FUSE | 72640 | 20141230 | 1419 | 1152687 | 1259 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 42125 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079180 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
MISSION | Tier 3 | SAN RAMON-2108 | 14232108 | FUSE | 8928 | 20170109 | 417 | 1630063 | 612 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3060 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005889 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
MISSION | Tier 3 | CASTRO VALLEY-1108 | 14091108 | FUSE | 12851 | 20170110 | 1412 | 1633645 | 721 | Distribution Circuit | Vegetation | Tree - fell into line | 121 | 87241 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006767 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
MISSION | Tier 3 | SAN RAMON-2108 | 14232108 | FUSE | 13115 | 20170110 | 31 | 1632426 | 1049 | Distribution Circuit | Vegetation | Tree - branch fell on line | 99 | 34726 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006380 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
MISSION | Tier 3 | CASTRO VALLEY-1108 | 14091108 | RECLOSER | MR243 | 20170120 | 1523 | 1654572 | 1198 | Distribution Circuit | Vegetation | Tree - fell into line | 385 | 84293 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011676 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
MISSION | Tier 3 | SUNOL-1101 | 14241101 | OTHER | WIRE DOWN @ 2373 KILKARE | 20170121 | 1715 | 1657026 | 941 | Distribution Circuit | Vegetation | Tree - fell into line | 205 | 99799 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012145 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
MISSION | Tier 2 | CAYETANO-2109 | 14422109 | FUSE | 12334 | 20170217 | 1946 | 1698321 | 449 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 21103 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022796 | OH | Sus | 0 | 2017 | FEB | Yes | None | Yes | No
MISSION | Tier 3 | SAN RAMON-2108 | 14232108 | RECLOSER | 53732 | 20181014 | 2305 | 195161 | 686 | Distribution Circuit | Vegetation | Tree - branch fell on line | 90 | 54411 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0090336 | OH | Sus | 43506702 | 2018 | OCT | Yes | Line to Line | Yes | No
MISSION | Tier 3 | CASTRO VALLEY-1108 | 14091108 | TRIP-SAVER | 10315 | 20181129 | 2218 | 229734 | 1062 | Distribution Circuit | 3rd Party | Vehicle | 67 | 57285 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 18-0105428 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
MISSION | Tier 3 | SUNOL-1101 | 14241101 | FUSE | 12787 | 20200816 | 2054 | 1014171 | 1235 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 132929 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0085343 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
MISSION | Tier 3 | TASSAJARA-2113 | 14662113 | FUSE | 62482 | 20211229 | 2239 | 1589247 | 692 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 692 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0161713 | OH | Sus | 31588487 | 2021 | DEC | Yes | Line to Ground | Yes | No
MISSION | Tier 3 | CASTRO VALLEY-1110 | 14091110 | FUSE | 779893 | 20230109 | 1301 | 1938202 | 484 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 484 | Heavy Rain-Strong Winds-Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0011302 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
MISSION | Tier 3 | SAN RAMON-2108 | 14232108 | FUSE | 6878 | 20230224 | 632 | 2003468 | 613 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 11034 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0034027 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 1097 | 20130408 | 530 | 768882 | 780 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 69630 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022762 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8319 | 20130408 | 651 | 769004 | 1209 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 37479 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022777 | OH | Sus | 0 | 2013 | APR | Yes | None | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 12917 | 20130408 | 416 | 768700 | 1336 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8016 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0022831 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER |  | 20131121 | 2105 | 909907 | 453 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 11325 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078168 | OH | Sus | 41991611 | 2013 | NOV | Yes | Open Circuit | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8981 | 20141203 | 1132 | 1123022 | 676 | Distribution Circuit | Vegetation | Tree - bark fell into line | 60 | 39445 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073444 | OH | Sus | 31118268 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 5417 | 20141203 | 1100 | 1122489 | 1029 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 44247 | Heavy rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0073538 | OH | Sus | 42283848 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 3 | HALF MOON BAY-1101 | 24101101 | FUSE | 8607 | 20141211 | 812 | 1131405 | 2198 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 17584 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075835 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4279 | 20141211 | 653 | 1131371 | 380 | Distribution Circuit | Vegetation | Tree - branch fell on line | 93 | 27093 | Rain-32 - 90 F | Anchor or Guy | Broken, wire on object | 14-0075453 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1067 | 20141211 | 823 | 1131545 | 887 | Distribution Circuit | Equipment Failure/Involved | Other | 13 | 11531 | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0075467 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER |  | 20141211 | 1320 | 1133906 | 532 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 12768 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075510 | OH | Sus | 31120659 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1127 | 20141211 | 752 | 1133548 | 758 | Distribution Circuit | Equipment Failure/Involved | Other | 34 | 25772 | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0075627 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER |  | 20141211 | 835 | 1134718 | 1210 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 20570 | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0075639 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 7687 | 20141211 | 529 | 1138004 | 2596 | Distribution Circuit | Equipment Failure/Involved | Other | 20 | 51920 | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0076299 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 13213 | 20141211 | 936 | 1132317 | 3529 | Distribution Circuit | Equipment Failure/Involved | Other | 5 | 14960 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076301 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | RECLOSER | 8512 | 20141211 | 1323 | 1133890 | 197 | Distribution Circuit | Equipment Failure/Involved | Other | 143 | 27170 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075502 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE | 13331 | 20141211 | 1922 | 1135637 | 1748 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 24472 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076457 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8972 | 20141211 | 848 | 1131818 | 95 | Distribution Circuit | Equipment Failure/Involved | Other | 68 | 6460 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075181 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8615 | 20141211 | 1138 | 1135029 | 1686 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 23604 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075739 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 7487 | 20141211 | 1818 | 1135345 | 1047 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 6282 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075765 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 7969 | 20141211 | 1537 | ODB-9919 | 3078 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 6156 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0076355 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4099 | 20141212 | 2215 | 1139311 | 807 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 10491 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076629 | OH | Sus | 31120659 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | BERESFORD-0403 | 24040403 | OTHER |  | 20141230 | 1950 | 1155308 | 1412 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1412 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079526 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | OTHER |  | 20141230 | 1557 | 1153668 | 1386 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 75738 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079363 | OH | Sus | 0 | 2014 | DEC | Yes | Open Circuit | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4429 | 20141230 | 1432 | 1153418 | 1488 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 40176 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079243 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER |  | 20150206 | 1407 | 1177361 | 3068 | Distribution Circuit | Equipment Failure/Involved | Other | 376 | 161503 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010578 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | PACIFICA-1103 | 22811103 | RECLOSER | 3907 | 20150206 | 1229 | 1174920 | 917 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 13755 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010125 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
PENINSULA | Tier 3 | WOODSIDE-1104 | 24251104 | FUSE | 3575 | 20150206 | 1858 | 1177970 | 972 | Distribution Circuit | Equipment Failure/Involved | Other | 27 | 26244 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010652 | OH | Sus | 31132845 | 2015 | FEB | Yes | Line to Line | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | SWITCH | 2031 | 20150207 | 939 | 1180953 | 431 | Distribution Circuit | Equipment Failure/Involved | Other | 66 | 28446 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011148 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4279 | 20150207 | 941 | 1180796 | 139 | Distribution Circuit | Equipment Failure/Involved | Other | 93 | 12927 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011160 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | BERESFORD-0403 | 24040403 | OTHER |  | 20150208 | 1814 | 1183727 | 716 | Distribution Circuit | Vegetation | Tree - fell into line | 625 | 46772 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011719 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | CAROLANDS-0404 | 24060404 | FUSE | 1723 | 20150208 | 2200 | 1185226 | 869 | Distribution Circuit | Equipment Failure/Involved | Other | 64 | 55616 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011987 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | EMERALD LAKE-0401 | 24080401 | TRANSFORMER |  | 20150208 | 1744 | 1185526 | 1387 | Distribution Circuit | Equipment Failure/Involved | Other | 37 | 33687 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011941 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8981 | 20150208 | 1544 | 1183225 | 1546 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 50146 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011695 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | BERESFORD-0403 | 24040403 | OTHER | WIRE DOWN | 20151213 | 1014 | 1361230 | 276 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 3334 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084772 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 2 | MENLO-1102 | 24131102 | FUSE | 4963 | 20151213 | 919 | 1360775 | 504 | Distribution Circuit | Vegetation | Tree - fell into line | 333 | 167832 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084641 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4133 | 20151213 | 1100 | 1361605 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2300 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084881 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | BELMONT-1103 | 24031103 | FUSE | 4913 | 20151224 | 1958 | 1371392 | 945 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 45285 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087178 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 12185 | 20160305 | 1610 | 1417315 | 717 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 25095 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017669 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 8739 | 20160305 | 1751 | 1417798 | 424 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 12904 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017983 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER | WIRE DOWN 9/N OF 8898 | 20160305 | 2101 | 1419333 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 9225 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018008 | OH | Sus | 0 | 2016 | MAR | Yes | Open Circuit | Yes | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | 98440 | 20160305 | 1614 | 1417174 | 1256 | Distribution Circuit | Vegetation | Tree - branch fell on line | 153 | 189248 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 16-0018045 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8311 | 20160305 | 1627 | 1417226 | 1240 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1240 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017753 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1104 | 24251104 | FUSE | 3585 | 20160305 | 1627 | 1417227 | 381 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 6096 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017826 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE | 3217 | 20170103 | 2009 | 1616723 | 913 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 14608 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003329 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8605 | 20170103 | 2041 | 1616773 | 1111 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 17776 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003321 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 3 | HALF MOON BAY-1101 | 24101101 | RECLOSER | 8972 | 20170108 | 1251 | 1626502 | 1650 | Distribution Circuit | Vegetation | Tree - branch fell on line | 68 | 92895 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0005286 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER | WIRE DOWN @ MTR# 10058597405 | 20170108 | 1009 | 1625271 | 1556 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 39020 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005168 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4265 | 20170108 | 1236 | 1626875 | 1409 | Distribution Circuit | Vegetation | Tree - branch fell on line | 53 | 57153 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005329 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | 98440 | 20170108 | 1126 | 1627946 | 1754 | Distribution Circuit | Equipment Failure/Involved | Overhead | 142 | 63454 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005515 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1127 | 20170108 | 1450 | 1627471 | 3146 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 102792 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005965 | OH | Sus | 31294580 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 5523 | 20170108 | 859 | 1623846 | 3381 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10143 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005971 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 8465 | 20170108 | 1530 | 1630921 | 1167 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 7002 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0006049 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-0401 | 24130401 | OTHER | WIRE DOWN | 20170108 | 113 | 1623835 | 1091 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 58679 | Strong Winds-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005033 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | PACIFICA-1103 | 22811103 | JUMPER | WIRE DOWN & CUT LD/S/ DDE | 20170108 | 1531 | 1628055 | 1389 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 16821 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005507 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8615 | 20170108 | 320 | 1622495 | 716 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 10024 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0004910 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER | WIRE DOWN @ MTR# 1003838035 | 20170108 | 833 | 1623805 | 899 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 82091 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005177 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 7487 | 20170108 | 1012 | 1624697 | 4798 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 201521 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005275 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 13255 | 20170108 | 944 | 1624335 | 1522 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 18264 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0005339 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER | WIRE DOWN MARINE RD | 20170108 | 1817 | 1628988 | 1351 | Distribution Circuit | Vegetation | Tree - fell into line | 193 | 26371 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005665 | OH | Sus | 31294580 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4433 | 20170108 | 2217 | 1629643 | 3020 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 33220 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005927 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4241 | 20170109 | 1145 | 1631090 | 20 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 60 | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0006088 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-0401 | 24130401 | SWITCH | 6743 | 20170109 | 952 | 1630373 | 748 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2244 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0006008 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4431 | 20170109 | 1930 | 1632155 | 1758 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 25516 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006295 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | EMERALD LAKE-0401 | 24080401 | FUSE | 267759 | 20170110 | 1745 | 1637906 | 1681 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1681 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007206 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 7985 | 20170110 | 1724 | 1634683 | 2670 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5340 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006851 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER | WIRE DOWN @ LA FONDA RD E/OF 4133 | 20170110 | 1937 | 1636276 | 2999 | Distribution Circuit | Vegetation | Tree - fell into line | 246 | 25597 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006973 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER | WIRE DOWN @ 17000 SKYLINE | 20170110 | 1742 | 1637400 | 1688 | Distribution Circuit | Vegetation | Tree - fell into line | 1692 | 805011 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007175 | OH | Sus | 31294580 | 2017 | JAN | Yes | Force Out | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1104 | 24251104 | FUSE | 9169 | 20170110 | 1414 | 1633654 | 868 | Distribution Circuit | Vegetation | Tree - branch fell on line | 74 | 64232 | Overcast-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on object | 17-0006723 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | HALF MOON BAY-1101 | 24101101 | FUSE | 8607 | 20170111 | 1649 | 1640373 | 1423 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 11384 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007870 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | SWITCH | 1015 | 20170111 | 1107 | 1639568 | 8 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 472 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0007567 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | SWITCH | 517 | 20170111 | 1130 | 1639630 | 674 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 54594 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0007567 | OH | Sus | 42913270 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 1097 | 20170111 | 1148 | 1639760 | 381 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 15621 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007876 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4429 | 20170111 | 2041 | 1641184 | 2104 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 10520 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008382 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1102 | 24131102 | FUSE | 4945 | 20170118 | 1533 | 1646768 | 1490 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 58110 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | On Ground | 17-0010229 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 47872 | 20170118 | 1923 | 1648539 | 618 | Distribution Circuit | Vegetation | Tree - branch fell on line | 226 | 148279 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010356 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 11229 | 20170120 | 736 | 1653033 | 508 | Distribution Circuit | Vegetation | Tree - branch fell on line | 67 | 34036 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011429 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE | 4311 | 20170120 | 1359 | 1654381 | 1056 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 15840 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011669 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 5703 | 20170122 | 315 | 1658576 | 772 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2316 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0012704 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER | WIRE DOWN | 20170122 | 426 | 1658740 | 507 | Distribution Circuit | Vegetation | Tree - branch fell on line | 579 | 9755 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012809 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | JUMPER | 1117 | 20170122 | 1200 | 1660898 | 705 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2820 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013115 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1067 | 20170122 | 914 | 1660216 | 811 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 10543 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013217 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4995 | 20170122 | 1603 | 1661628 | 4484 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 98648 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013347 | OH | Sus | 42928223 | 2017 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE | 1721 | 20170122 | 447 | 1658815 | 528 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 26400 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012863 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER | WIRE DOWN 4/SP/LINE SIDE 4737 | 20170122 | 949 | 1660198 | 790 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 19915 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013075 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1127 | 20170207 | 601 | 1678185 | 1010 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 34340 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018292 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 8125 | 20170207 | 906 | -1680268 | 1048 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 39824 |  | Conductor, Overhead | Broken, wire on ground | 17-0018614 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 1097 | 20170207 | 639 | 1678242 | 837 | Distribution Circuit | Equipment Failure/Involved | Overhead | 314 | 69594 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018195 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4737 | 20170207 | 942 | 1679537 | 708 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 14160 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0018462 | OH | Sus | 31304022 | 2017 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | SWITCH | 11417 | 20170207 | 941 | 1680647 | 1818 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 54540 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018677 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 8125 | 20170209 | 1900 | 1684093 | 1252 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 47576 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019634 | OH | Sus | 31304022 | 2017 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1127 | 20170209 | 2302 | 1684331 | 1058 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 15215 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019761 | OH | Sus | 42939220 | 2017 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8884 | 20170209 | 1345 | 1683562 | 524 | Distribution Circuit | Environmental/External | Flood/Erosion | 341 | 29789 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019480 | OH | Sus | 42939220 | 2017 | FEB | Yes | Force Out | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | RECLOSER | 8512 | 20170217 | 951 | 1693622 | 204 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 24271 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021980 | OH | Sus | 42950847 | 2017 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE | 4961 | 20170217 | 938 | 1693429 | 844 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3354 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022113 | OH | Sus | 31306686 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | JUMPER | 4279 | 20170218 | 614 | 1699086 | 468 | Distribution Circuit | Vegetation | Tree - fell into line | 160 | 36457 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022911 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | BERESFORD-0403 | 24040403 | JUMPER | WIRE DOWN IFO 773 EL CERRITO AVE | 20170220 | 2026 | 1705900 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4291 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024267 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | JUMPER | UNNUMBERED DISC | 20170220 | 1040 | 1702873 | 903 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 34314 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0023767 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4319 | 20170220 | 1804 | 1705161 | 2743 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 21944 | Overcast-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0024165 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | TRIP-SAVER | 8089 | 20170220 | 1635 | 1704608 | 1443 | Distribution Circuit | Equipment Failure/Involved | Overhead | 106 | 152958 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024680 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE | 1721 | 20170220 | 2044 | 1706007 | 2447 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 122350 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024802 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8974 | 20170220 | 639 | 1702537 | 527 | Distribution Circuit | Vegetation | Tree - fell into line | 314 | 44742 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023662 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER | WIRE DOWN 16995 SKYLINE BLVD | 20170220 | 1647 | 1704369 | 782 | Distribution Circuit | Vegetation | Tree - fell into line | 341 | 58195 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023943 | OH | Sus | 0 | 2017 | FEB | Yes | None | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4737 | 20170220 | 2029 | 1705908 | 1421 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 28420 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025078 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE | 10695 | 20170221 | 1341 | 1708768 | 349 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 5933 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025169 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | 6018 | 20170221 | 829 | 1707906 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 927 | 156962 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024948 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | RECLOSER | 8982 | 20170406 | 1939 | 1748111 | 1358 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 74690 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037356 | OH | Sus | 0 | 2017 | APR | Yes | Force Out | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8972 | 20170406 | 2028 | 1746810 | 1412 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 96016 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037279 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | TRIP-SAVER | 8601 | 20170406 | 2039 | 1746939 | 1366 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 57372 | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037971 | OH | Sus | 31316082 | 2017 | APR | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1102 | 24131102 | JUMPER | WIRE ON GROUND TWD 7550 ALPINE RD | 20170903 | 828 | 1867889 | 1231 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2750 | Clear-Heat Wave-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0075505 | OH | Sus | 0 | 2017 | SEP | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1102 | 24131102 | JUMPER | OJ 8 POLES 13329 | 20170903 | 1626 | 1869183 | 1341 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4023 | Clear-Heat Wave-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0075627 | OH | Sus | 0 | 2017 | SEP | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 2 | SNEATH LANE-1106 | 22721106 | OTHER | WIRE DOWN JUST LD SIDE OF 11089 | 20170911 | 1904 | 1876236 | 488 | Distribution Circuit | Environmental/External | Lightning | 4032 | 116781 | Partly Cloudy-Drizzle-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0077883 | OH | Sus | 0 | 2017 | SEP | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE | 10695 | 20171204 | 1650 | 1935846 | 604 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 13838 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099791 | OH | Sus | 43227146 | 2017 | DEC | Yes | Open Circuit | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | SWITCH | 7483 | 20171216 | 1527 | 1945909 | 525 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 8218 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102222 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | HALF MOON BAY-1101 | 24101101 | FUSE | 8607 | 20181108 | 1644 | 211874 | 148 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 1184 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0098441 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 13253 | 20181129 | 737 | 227952 | 633 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 32283 | Overcast-Heavy Rain-Lightning-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104871 | OH | Sus | 43587430 | 2018 | NOV | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | 98440 | 20190106 | 1732 | 255924 | 1088 | Distribution Circuit | Vegetation | Tree - branch fell on line | 154 | 19102 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005295 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | OTHER | SLATE CREEK & PORTOLA STATE PARK RD | 20190106 | 1310 | 255461 | 608 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 31685 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005121 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 13253 | 20190106 | 1727 | 255922 | 1574 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 80274 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005246 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 1099 | 20190106 | 1934 | 257428 | 1219 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 70600 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005477 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1102 | 24131102 | TRIP-SAVER | 12249 | 20190116 | 1728 | 268656 | 1402 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 37854 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010096 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1102 | 24131102 | OTHER | WIRE DOWN 2N/O 12249 | 20190116 | 1838 | 272060 | 1807 | Distribution Circuit | Vegetation | Tree - fell into line | 1157 | 603505 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010421 | OH | Sus | 0 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4737 | 20190116 | 1542 | 268252 | 1458 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 29160 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010086 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | TRIP-SAVER | 8601 | 20190116 | 2105 | 270948 | 1172 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 49224 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010441 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER | WIRE DOWN @ SOURCE SIDE 13253 | 20190116 | 2302 | 271784 | 938 | Distribution Circuit | Vegetation | Tree - fell into line | 310 | 96394 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010563 | OH | Sus | 31422194 | 2019 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8615 | 20190116 | 2343 | 272010 | 1503 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 21042 | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011180 | OH | Sus | 31422194 | 2019 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 7683 | 20190117 | 833 | 275982 | 1922 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 5766 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011907 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | JUMPER | OJ LINE SIDE 4277 | 20190117 | 812 | 276596 | 6241 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 18723 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0012088 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 3 | SAN CARLOS-1103 | 24181103 | FUSE | 6693 | 20190117 | 1744 | 274742 | 1373 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6865 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011332 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER | WIRE DOWN @ LD SIDE 7483 | 20190117 | 40 | 272190 | 890 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 22998 | Overcast-Fog-32-90 F | Conductor, Overhead | On Ground | 19-0010501 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | JUMPER | WIRE BROKEN @ 1 POLE N/O 11769 | 20190202 | 1832 | 288022 | 537 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 15573 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0017359 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER | WIRE DOWN 6 SPANS SOURCE SIDE 4737 | 20190202 | 405 | 286993 | 474 | Distribution Circuit | Vegetation | Tree - branch fell on line | 68 | 12927 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017036 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1123 | 20190205 | 559 | 291671 | 661 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 3966 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018303 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER | WIRE DOWN @ 2 SS REDWOOD & SHELDON | 20190205 | 1956 | 293676 | 464 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 11634 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0018773 | OH | Sus | 31424639 | 2019 | FEB | Yes | Open Circuit | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER | WIRE DOWN N/O 7867 | 20190210 | 2028 | 299395 | 2993 | Distribution Circuit | Vegetation | Tree - fell into line | 343 | 153185 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0020853 | OH | Sus | 31425315 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1123 | 20190212 | 2315 | 301628 | 917 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5502 | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0021721 | OH | Sus | 31425520 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE | 4149 | 20190213 | 746 | 303068 | 674 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1348 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022190 | OH | Sus | 43677704 | 2019 | FEB | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4263 | 20190213 | 1315 | 304592 | 605 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 5315 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022410 | OH | Sus | 31425418 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1621 | 20190213 | 1550 | 305146 | 4240 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 12720 | Overcast-Drizzle-32-90 F | Conductor, Overhead | On Ground | 19-0022524 | OH | Sus | 31425418 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 14653 | 20190213 | 1029 | 304425 | 3643 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 32787 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023318 | OH | Sus | 43677704 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE | 4309 | 20190213 | 616 | 302878 | 601 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 7212 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021938 | OH | Sus | 31425418 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE | 8549 | 20190213 | 2319 | 308290 | 2340 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 71108 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023372 | OH | Sus | 43677704 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1043 | 20190214 | 145 | 307798 | 3506 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 3506 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 19-0022945 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | HALF MOON BAY-1103 | 24101103 | FUSE | 6093 | 20190214 | 718 | 310489 | 2017 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 34333 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023599 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | 6018 | 20190214 | 1221 | 310866 | 4637 | Distribution Circuit | Vegetation | Tree - fell into line | 953 | 691981 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023737 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | RALSTON-1101 | 24141101 | FUSE | 8603 | 20190214 | 12 | 306027 | 3991 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 63856 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023500 | OH | Sus | 31425418 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8972 | 20190214 | 30 | 306070 | 1162 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 80178 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022723 | OH | Sus | 43677704 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER | PRI WIRE DOWN @ 1480 LA HONDA RD | 20190214 | 37 | 306275 | 844 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3230 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022743 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 6973 | 20190217 | 1014 | 315558 | 1790 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5540 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025121 | OH | Sus | 31425418 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 7985 | 20190217 | 1151 | 318142 | 3079 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6158 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0025737 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | WOODSIDE-1104 | 24251104 | TRIP-SAVER | 3583 | 20190227 | 41 | 325954 | 710 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 54746 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028725 | OH | Sus | 43684677 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8972 | 20200116 | 839 | 762280 | 535 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 36915 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009621 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 8125 | 20200816 | 903 | 1011595 | 507 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 16445 | Partly Cloudy-Drizzle-Lightning-Heat Wave-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0084802 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 12457 | 20200816 | 2134 | 1014238 | 1119 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1119 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0085352 | OH | Sus | 0 | 2020 | AUG | Yes | Force Out | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | OTHER | WIRE DOWN 6 SPAN LINE SIDE OF 8549 | 20210118 | 1007 | 1212401 | 532 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 29140 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0009656 | OH | Sus | 44628037 | 2021 | JAN | Yes | Open Circuit | Yes | No
PENINSULA | Tier 2 | SNEATH LANE-1106 | 22721106 | FUSE | 3185 | 20210119 | 454 | 1214799 | 567 | Distribution Circuit | Equipment Failure/Involved | Overhead | 120 | 68040 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010195 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 5417 | 20210119 | 32 | 1214103 | 569 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 22100 | Strong Winds-Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0010039 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8327 | 20210119 | 30 | 1213674 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1895 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010078 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 12917 | 20210127 | 712 | 1233425 | 339 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2373 | Strong Winds- | Conductor, Overhead | Broken, wire on ground | 21-0015827 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4279 | 20211213 | 952 | 1567887 | 671 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 53246 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0157413 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8615 | 20221210 | 1116 | 1881728 | 467 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 6538 | Heavy Rain-Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0138490 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1104 | 24251104 | FUSE | 3575 | 20230105 | 118 | 1920693 | 1444 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 38988 | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0007745 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE | 10695 | 20230110 | 406 | 1943256 | 869 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 11297 | Strong Winds- | Conductor, Overhead | Broken, wire on ground | 23-0012235 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4245 | 20230114 | 749 | 1954337 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1800 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016185 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | H80 | 20230114 | 2342 | 1955338 | 1033 | Distribution Circuit | Vegetation | Tree - fell into line | 647 | 178905 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0016493 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8884 | 20230114 | 824 | 1953267 | 468 | Distribution Circuit | Vegetation | Tree - fell into line | 343 | 85298 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016057 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8974 | 20230116 | 624 | 1956755 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 314 | 7438 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016957 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | Yes
PENINSULA | Tier 2 | WOODSIDE-1104 | 24251104 | TRIP-SAVER | 3583 | 20230116 | 734 | 1957216 | 709 | Distribution Circuit | Vegetation | Tree - fell into line | 103 | 47976 | Strong Winds-Heavy Rain-Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0017018 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
SAN FRANCISCO | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER | WIRE DOWN 8 SPANS LD S/O FUSE 4737 | 20170118 | 1759 | s1249610 | 694 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 9920 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010247 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 1222 | 20131121 | 1828 | 908019 | 1004 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1299 | 294380 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078046 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L2133 | 20131121 | 2006 | 909124 | 654 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 23544 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078137 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 1303 | 20131121 | 1831 | 908725 | 1024 | Distribution Circuit | Vegetation | Tree - bark fell into line | 216 | 221184 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078128 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | OCB | OCB | 20131121 | 2252 | 908797 | 386 | Distribution Circuit | Equipment Failure/Involved | Other | 2148 | 135968 | Strong winds-32 - 90 F | Crossarm, Wood | Broken, wire on object | 13-0078189 | OH | Sus | 0 | 2013 | NOV | Yes | None | Yes
STOCKTON | Tier 2 | ELECTRA-1102 | 162161102 | FUSE | 2135 | 20131122 | 1600 | 912641 | 260 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 4940 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078729 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | SWITCH | L3065 | 20131122 | 1222 | 912000 | 233 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 12815 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0078046 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
STOCKTON | Tier 2 | SALT SPRINGS-2101 | 163692101 | FUSE | 4693 | 20131122 | 943 | 911634 | 997 | Distribution Circuit | Equipment Failure/Involved | Other | 23 | 15001 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078682 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
STOCKTON | Tier 2 | SALT SPRINGS-2102 | 163692102 | RECLOSER | 8442 | 20131122 | 225 | 910516 | 1254 | Distribution Circuit | Vegetation | Tree - fell into line | 1998 | 1244943 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078275 | OH | Sus | 31038457 | 2013 | NOV | Yes | Line to Line | Yes
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 99353 | 20131122 | 742 | 911167 | 1113 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 6678 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0078547 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 1391 | 20131122 | 2007 | 913131 | 1168 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 47888 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0078812 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
STOCKTON | Tier 2 | CLAY-1101 | 163341101 | FUSE | 749 | 20141211 | 951 | 1132634 | 1173 | Distribution Circuit | Vegetation | Tree - bark fell into line | 119 | 26835 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075476 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
STOCKTON | Tier 2 | CORRAL-1101 | 162991101 | FUSE | 18719 | 20141211 | 1036 | 1132954 | 310 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 3594 | Strong winds-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0075411 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L1697 | 20141211 | 944 | 1132405 | 1052 | Distribution Circuit | Equipment Failure/Involved | Other | 241 | 104024 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075405 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L3829 | 20141211 | 1003 | 1132767 | 1598 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 51124 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075628 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | L485 | 20141211 | 1150 | 1134042 | 666 | Distribution Circuit | Vegetation | Tree - branch fell on line | 509 | 59610 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075526 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER | 36674 | 20141211 | 955 | 1132589 | 1141 | Distribution Circuit | Vegetation | Tree - fell into line | 304 | 346864 | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075436 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L1977 | 20141211 | 1024 | 1132842 | 1347 | Distribution Circuit | Equipment Failure/Involved | Other | 25 | 33675 | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076108 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L585 | 20141211 | 935 | 1132581 | 740 | Distribution Circuit | Equipment Failure/Involved | Other | 29 | 21460 | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075361 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 1311 | 20141211 | 929 | 1132248 | 1182 | Distribution Circuit | Equipment Failure/Involved | Other | 81 | 20205 | Rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075441 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | OTHER |  | 20141211 | 1202 | 1135324 | 1023 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 6138 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076084 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L1137 | 20141211 | 1154 | 1133389 | 1464 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 8784 | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076197 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
STOCKTON | Tier 3 | ELECTRA-1102 | 162161102 | FUSE | 1327 | 20141212 | 223 | 1136934 | 172 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 344 | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0076095 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L1697 | 20141230 | 1215 | 1152803 | 797 | Distribution Circuit | Vegetation | Tree - fell into line | 241 | 69294 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079128 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | OCB | OCB | 20141230 | 1309 | 1155815 | 641 | Distribution Circuit | Equipment Failure/Involved | Other | 1895 | 207213 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079072 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | OTHER |  | 20141230 | 1127 | 1152406 | 832 | Distribution Circuit | Equipment Failure/Involved | Other | 150 | 115320 | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079096 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L359 | 20141230 | 1039 | 1151246 | 894 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 19318 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079260 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | 5163 | 20141230 | 1340 | 1152368 | 1070 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 48560 | Combination wind/rain/lightning-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0079517 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L1977 | 20141230 | 836 | 1150510 | 601 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 15025 | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078917 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 77204 | 20141230 | 900 | 1150684 | 1793 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2021 | 1144821 | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078900 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
STOCKTON | Tier 2 | OLETA-1101 | 163541101 | FUSE | L6599 | 20150206 | 2214 | 1179141 | 1006 | Distribution Circuit | Equipment Failure/Involved | Other | 4 | 1540 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010828 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
STOCKTON | Tier 2 | CORRAL-1101 | 162991101 | RECLOSER | 12612 | 20150608 | 1418 | 1245781 | 337 | Distribution Circuit | 3rd Party | Vehicle | 314 | 65168 | Clear-Above 90 F | Pole-Wood | Broken, wire on ground | 15-0039368 | OH | Sus | 31159870 | 2015 | JUN | Yes | Line to Ground | Yes
STOCKTON | Tier 2 | OLETA-1101 | 163541101 | RECLOSER | 1208 | 20151213 | 1056 | 1361641 | 251 | Distribution Circuit | Vegetation | Tree - branch fell on line | 478 | 93486 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084811 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | ELECTRA-1102 | 162161102 | RECLOSER | 77204 | 20160217 | 1813 | 1406173 | 717 | Distribution Circuit | Vegetation | Tree - fell into line | 209 | 46864 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013358 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | ELECTRA-1102 | 162161102 | RECLOSER | 2646 | 20160217 | 1950 | 1406653 | 1189 | Distribution Circuit | Vegetation | Tree - fell into line | 204 | 120837 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013480 | OH | Sus | 0 | 2016 | FEB | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | JUMPER | O/J 2 SPANS S/E OF L6693 | 20160217 | 1906 | 1407515 | 504 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 10236 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013472 | OH | Sus | 0 | 2016 | FEB | Yes | Open Circuit | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | FUSE | 1315 | 20160217 | 1949 | 1406647 | 950 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 50350 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013512 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CLAY-1101 | 163341101 | FUSE | L3789 | 20160305 | 2034 | 1419051 | 1275 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 20100 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 16-0018160 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | RECLOSER | 7104 | 20160305 | 2209 | 1420144 | 832 | Distribution Circuit | Vegetation | Tree - fell into line | 620 | 222586 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017953 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | OLETA-1101 | 163541101 | FUSE | 1179 | 20160305 | 2052 | 1419210 | 483 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 13971 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017895 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | RECLOSER | 3170 | 20160305 | 2157 | 1419908 | 550 | Distribution Circuit | Vegetation | Tree - fell into line | 683 | 147306 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018028 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | FUSE | 1487 | 20160305 | 2222 | 1421239 | 1101 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 14313 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018279 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CLAY-1103 | 163341103 | RECLOSER | 59714 | 20170103 | 707 | 1615352 | 393 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 2002 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0002884 | OH | Sus | 31292586 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | JUMPER | WIRE DOWN AT MTR 1004902341 | 20170108 | 2026 | 1629108 | 501 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2263 | 401870 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005734 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
STOCKTON | Tier 2 | MARTELL-1101 | 163011101 | FUSE | 1025 | 20170108 | 920 | 1624332 | 335 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 15999 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005162 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | MARTELL-1103 | 163011103 | RECLOSER | 3152 | 20170108 | 950 | 1624448 | 873 | Distribution Circuit | Environmental/External | Flood/Erosion | 139 | 121347 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005193 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L6827 | 20170108 | 2342 | 1629790 | 983 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2949 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0005854 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER | 1305 | 20170108 | 16 | 1622373 | 907 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 63698 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004886 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | MARTELL-1101 | 163011101 | FUSE | L3161 | 20170109 | 703 | 1630345 | 791 | Distribution Circuit | Equipment Failure/Involved | Overhead | 77 | 47611 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006006 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | JUMPER | WIRE DOWN AT MTR 5000058384 | 20170109 | 950 | 1630756 | 1599 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4797 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006122 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 4790 | 20170109 | 526 | 1630069 | 2154 | Distribution Circuit | Environmental/External | Flood/Erosion | 1910 | 403369 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005879 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
STOCKTON | Tier 2 | CLAY-1101 | 163341101 | OCB | 1101/2 | 20170110 | 2110 | 1637469 | 885 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1711 | 118689 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007140 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | MARTELL-1101 | 163011101 | FUSE | L9705 | 20170110 | 1009 | 1632890 | 461 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1844 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006599 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | RECLOSER | 3170 | 20170110 | 1044 | 1632967 | 434 | Distribution Circuit | Vegetation | Tree - fell into line | 686 | 49270 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006529 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE | L4053 | 20170110 | 1939 | 1635597 | 1312 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 26240 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006977 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 789 | 20170110 | 52 | 1632443 | 998 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3992 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006384 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | JUMPER | @ MTR 1004974072 | 20170110 | 2140 | 1638375 | 1412 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4236 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007333 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | L2065 | 20170110 | 748 | 1632710 | 483 | Distribution Circuit | Vegetation | Tree - fell into line | 332 | 65496 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006485 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | SALT SPRINGS-2102 | 163692102 | RECLOSER | 8442 | 20170110 | 2337 | 1638099 | 3993 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2000 | 127889 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0007269 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L5685 | 20170110 | 730 | 1632588 | 711 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 6399 | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0006468 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 4790 | 20170110 | 2036 | 1636930 | 1332 | Distribution Circuit | Vegetation | Tree - fell into line | 1181 | 315066 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007222 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CLAY-1103 | 163341103 | FUSE | 721 | 20170111 | 614 | 1638735 | 1942 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 56982 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007682 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L3341 | 20170111 | 132 | 1638401 | 1869 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 21930 | Overcast-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0007774 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | ELECTRA-1102 | 162161102 | FUSE | 1321 | 20170111 | 145 | 1638461 | 2350 | Distribution Circuit | Vegetation | Tree - fell into line | 338 | 423252 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007667 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | OCB | 1102/2 | 20170111 | 123 | 1638362 | 685 | Distribution Circuit | Vegetation | Tree - fell into line | 4383 | 622884 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0007328 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | OTHER | WIRE DOWN MTR 1008715746 TAP | 20170111 | 559 | 1638729 | 2029 | Distribution Circuit | Vegetation | Tree - branch fell on line | 150 | 14098 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007823 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 5361 | 20170118 | 1542 | 1646817 | 658 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 5214 | Overcast-Fog-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0010154 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | SALT SPRINGS-2102 | 163692102 | RECLOSER | 97924 | 20170120 | 2059 | 1655172 | 8204 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 405005 | Overcast-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0011814 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 3142 | 20170120 | 1401 | 1654386 | 348 | Distribution Circuit | Vegetation | Tree - fell into line | 991 | 196316 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011646 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | 5387 | 20170120 | 1401 | 1655154 | 5510 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 380190 | Overcast-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 17-0011855 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L495 | 20170120 | 2018 | 1655127 | 5123 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 630129 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011856 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5381 | 20170120 | 2232 | 1661417 | 3899 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 280728 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013242 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | JUMPER | UNNUMBERED SBCO LD SIDE MTR 1008755737 | 20170120 | 2223 | 1666221 | 6637 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 19911 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0014509 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L1137 | 20170120 | 2332 | 1655312 | 3928 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 23568 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012134 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 1222 | 20170121 | 811 | 1655890 | 587 | Distribution Circuit | Equipment Failure/Involved | Overhead | 973 | 494544 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011926 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L3829 | 20170121 | 520 | 1656196 | 1893 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 84069 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011951 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L7193 | 20170121 | 434 | 1655869 | 1869 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 168210 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | On Ground | 17-0012011 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L2131 | 20170121 | 428 | 1655504 | 888 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 13320 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012051 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | L7287 | 20170121 | 812 | 1666897 | 6319 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 233803 | Clear-Below 32 F | Conductor, Overhead | On Ground | 17-0014731 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1701 | 162821701 | FUSE | 2641 | 20170121 | 247 | 1655445 | 1150 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 86250 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 17-0011887 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | STANISLAUS-1701 | 162821701 | RECLOSER | 1812 | 20170121 | 917 | 1656126 | 4541 | Distribution Circuit | Vegetation | Tree - fell into line | 816 | 741085 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011933 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 1888 | 20170121 | 552 | 1655236 | 724 | Distribution Circuit | Vegetation | Tree - fell into line | 1373 | 994052 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0011894 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | OTHER | WIRE DOWN COR/OF INDIAN ROCK & TOPANGA | 20170121 | 400 | 1655629 | 4661 | Distribution Circuit | Equipment Failure/Involved | Overhead | 114 | 520574 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011896 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 3142 | 20170121 | 623 | 1655779 | 3647 | Distribution Circuit | Vegetation | Tree - fell into line | 628 | 2260797 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011908 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L611 | 20170121 | 903 | 1656379 | 694 | Distribution Circuit | Vegetation | Tree - fell into line | 189 | 80646 | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0012019 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 37278 | 20170121 | 1014 | 1655642 | 1987 | Distribution Circuit | Vegetation | Tree - fell into line | 287 | 289340 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0012029 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L2695 | 20170121 | 532 | 1656960 | 2017 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 86212 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0012105 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L2371 | 20170121 | 448 | 1656981 | 5077 | Distribution Circuit | Vegetation | Tree - branch fell on line | 43 | 218311 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0012113 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | SWITCH | L3965 | 20170121 | 557 | 1657018 | 3607 | Distribution Circuit | Vegetation | Tree - fell into line | 153 | 551871 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0012126 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 1804 | 20170121 | 1715 | 1657023 | 20 | Distribution Circuit | Vegetation | Tree - fell into line | 399 | 7980 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012128 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L2203 | 20170121 | 1717 | 1657042 | 41 | Distribution Circuit | Vegetation | Tree - branch fell on line | 61 | 2501 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012133 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 1804 | 20170121 | 114 | s1251084 | 5189 | Distribution Circuit | Vegetation | Tree - fell into line | 1137 | 1708981 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011863 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5047 | 20170121 | 1819 | 1657097 | 1213 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 52159 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012542 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5141 | 20170121 | 1738 | 1657057 | 1555 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 29545 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0012950 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5379 | 20170121 | 2232 | 1660173 | 780 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 7020 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | On Ground | 17-0012987 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | 44955 | 20170121 | 534 | 1661350 | 6418 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 299962 | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0013222 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5383 | 20170121 | 1307 | 1661429 | 3377 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 50655 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013243 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L491 | 20170121 | 40 | 1661647 | 6797 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 747670 | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0013267 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5083 | 20170121 | 1822 | 1664016 | 4016 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 52208 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0013796 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5013 | 20170121 | 114 | 1664476 | 5202 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 150858 | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0013917 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L3309 | 20170121 | 429 | 1655532 | 2342 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 32788 | Strong Winds-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0011966 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L2217 | 20170121 | 4 | 1655328 | 2406 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 76992 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0011969 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER | 12256 | 20170121 | 1209 | 1655655 | 1433 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1153 | 390401 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0012006 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | Yes
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | JUMPER | OJ S/OF MTR #1008788068 | 20170121 | 1050 | 1656565 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 616 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012032 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | 1711 | 20170121 | 7 | 1657194 | 2706 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 224598 | Strong Winds-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 17-0012161 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L1981 | 20170121 | 446 | 1655550 | 1896 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 26544 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | On Ground | 17-0012015 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CORRAL-1101 | 162991101 | RECLOSER | 12608 | 20170122 | 322 | 1658391 | 508 | Distribution Circuit | Equipment Failure/Involved | Overhead | 413 | 98459 | Overcast-Drizzle-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0012688 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L2347 | 20170122 | 537 | 1659046 | 715 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 20060 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012972 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L3457 | 20170122 | 706 | 1659419 | 2042 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 10210 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0012977 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE | 1065 | 20170122 | 550 | 1659134 | 707 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 11312 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0013200 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER | WIRE DOWN 2N OF L1149 | 20170122 | 1311 | 1661303 | 457 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1070 | 203063 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013212 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | Yes
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | JUMPER | OJS 1W OF 63735 | 20170122 | 1318 | 1661997 | 2882 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 20482 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013338 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | 1151 | 20170122 | 1956 | 1662248 | 4250 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 30215 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013394 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5009 | 20170122 | 206 | 1658134 | 3591 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 75411 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0014330 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L3679 | 20170123 | 731 | 1663558 | 895 | Distribution Circuit | Equipment Failure/Involved | Overhead | 154 | 109984 | Overcast-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 17-0013697 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5053 | 20170123 | 1010 | 1663742 | 1741 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 13928 | Overcast-32-90 F | Conductor, Overhead | On Ground | 17-0013751 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L2065 | 20170123 | 2037 | 1664970 | 2699 | Distribution Circuit | Environmental/External | Ice or snow | 154 | 415646 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0014334 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L489 | 20170123 | 2037 | 1665800 | 2713 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 111233 | Overcast-Fog-Below 32 F | Conductor, Overhead | On Ground | 17-0014384 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | JUMPER | OJ @ MTR #1004654255 | 20170123 | 2037 | 1665877 | 2699 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 72873 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0014426 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L2219 | 20170123 | 419 | 1662774 | 738 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 50184 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013704 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L2217 | 20170123 | 842 | 1663256 | 725 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 23200 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013767 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | TRANSFORMER | 319920669198 | 20170123 | 1440 | 1663376 | 139 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 834 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013756 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER | L3733 | 20170123 | 906 | 1663699 | 1804 | Distribution Circuit | Vegetation | Tree - branch fell on line | 98 | 39137 | Overcast-Snow-32-90 F | Conductor, Overhead | On Ground | 17-0013878 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CORRAL-1103 | 162991103 | FUSE | 91311 | 20170207 | 1310 | 1680120 | 182 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 1670 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018600 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L2347 | 20170217 | 1447 | 1696592 | 833 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 19738 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022518 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | L6029 | 20170217 | 1916 | 1698213 | 595 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 33726 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022632 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CORRAL-1101 | 162991101 | OTHER | WIRE DOWN N/OF B452 | 20170218 | 500 | 1699005 | 1027 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 26665 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022892 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L2347 | 20170220 | 2019 | 1705859 | 431 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 8118 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024110 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | L3803 | 20170220 | 732 | 1702616 | 403 | Distribution Circuit | Equipment Failure/Involved | Overhead | 236 | 95108 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023681 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 93116 | 20170221 | 51 | 1707060 | 1197 | Distribution Circuit | Vegetation | Tree - fell into line | 339 | 118521 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024818 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L611 | 20170406 | 1604 | 1745743 | 397 | Distribution Circuit | Vegetation | Tree - fell into line | 189 | 56748 | Overcast-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037200 | OH | Sus | 42985900 | 2017 | APR | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER | 1303 | 20170406 | 2359 | 1748927 | 592 | Distribution Circuit | Vegetation | Tree - fell into line | 215 | 127280 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037539 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L5677 | 20170407 | 1039 | 1750513 | 351 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 10179 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037849 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | RECLOSER | 72036 | 20171009 | 446 | 1895664 | 843 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2466 | 312981 | Strong Winds-Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0085394 | OH | Sus | 31356040 | 2017 | OCT | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | ELECTRA-1102 | 162161102 | FUSE | L4015 | 20171204 | 1341 | 1935278 | 725 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3625 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0099721 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | OTHER | WIRE DWN MTR 1004978329 | 20171204 | 1421 | 1935747 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 1311 | 97276 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0099754 | OH | Sus | 0 | 2017 | DEC | Yes | Open Circuit | Yes | Yes
STOCKTON | Tier 2 | SALT SPRINGS-2101 | 163692101 | RECLOSER | 1216 | 20171204 | 1909 | 1936934 | 1510 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 75500 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0100140 | OH | Sus | 0 | 2017 | DEC | Yes | Multi-Fault | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | 1177 | 20171204 | 1731 | 1935962 | 1239 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 18585 | Clear-Strong Winds-Below 32 F | Conductor, Overhead | On Ground | 17-0099809 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | 44955 | 20171204 | 1756 | 1935884 | 1213 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 41242 | Clear-Strong Winds-Below 32 F | Conductor, Overhead | On Ground | 17-0099815 | OH | Sus | 0 | 2017 | DEC | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | L2065 | 20171204 | 1715 | 1935886 | 741 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 58016 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099836 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | 81017 | 20171204 | 1720 | 1935841 | 1158 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 56508 | Clear-Strong Winds-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0099850 | OH | Sus | 0 | 2017 | DEC | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | 91563 | 20171204 | 1820 | 1935925 | 1200 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 30056 | Clear-Strong Winds-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0099866 | OH | Sus | 31368344 | 2017 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 37276 | 20171204 | 1452 | 1935616 | 853 | Distribution Circuit | Vegetation | Tree - fell into line | 769 | 167781 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099725 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | OTHER | WIRE DOWN @ MTR 1004976890 | 20171204 | 1327 | 1935513 | 601 | Distribution Circuit | Vegetation | Tree - fell into line | 348 | 29088 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099706 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 2 | SALT SPRINGS-2101 | 163692101 | JUMPER | WIRE DOWN | 20171216 | 2107 | 1945975 | 982 | Distribution Circuit | Vegetation | Tree - fell into line | 908 | 42056 | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0102264 | OH | Sus | 0 | 2017 | DEC | Yes | Open Circuit | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 1357 | 20180316 | 559 | 45235 | 662 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 19198 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0023260 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | 1715 | 20180316 | 1606 | 46157 | 2919 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 117621 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023561 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | 1595 | 20180316 | 1636 | 46176 | 3054 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 76350 | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0023578 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L6007 | 20180316 | 1705 | 46261 | 4132 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 49584 | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0023751 | OH | Sus | 0 | 2018 | MAR | Yes | Multi-Fault | Yes | No
STOCKTON | Tier 2 | STANISLAUS-1701 | 162821701 | RECLOSER | 1812 | 20180316 | 1058 | 45419 | 2936 | Distribution Circuit | Vegetation | Tree - fell into line | 912 | 271973 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023352 | OH | Sus | 0 | 2018 | MAR | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1701 | 162821701 | FUSE | 1113 | 20180316 | 1751 | 46238 | 2463 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 38310 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023711 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L2709 | 20180316 | 741 | 45310 | 507 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 11154 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0023313 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | 2383 | 20180316 | 715 | 45282 | 418 | Distribution Circuit | Vegetation | Tree - branch fell on line | 281 | 117458 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023317 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 75348 | 20180316 | 1255 | 45876 | 1523 | Distribution Circuit | Vegetation | Tree - fell into line | 418 | 636614 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023419 | OH | Sus | 0 | 2018 | MAR | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | 6857 | 20180316 | 1341 | 45949 | 501 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 16032 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023526 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L433 | 20180316 | 1839 | 46308 | 2597 | Distribution Circuit | Vegetation | Tree - branch fell on line | 171 | 266265 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 18-0023618 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | 1183 | 20180316 | 1201 | 46634 | 2838 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 28380 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0023735 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5009 | 20180316 | 1913 | 46305 | 1212 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 25452 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | On Ground | 18-0023755 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | TIGER CREEK-0201 | 161380201 | FUSE | 1743 | 20180316 | 1447 | 46059 | 4380 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 13140 | Overcast-Drizzle-32-90 F | Insulator | Broken, wire on object | 18-0023507 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER | 12256 | 20180316 | 1042 | 45719 | 3347 | Distribution Circuit | Vegetation | Tree - fell into line | 1472 | 1227672 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0023417 | OH | Sus | 0 | 2018 | MAR | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L2217 | 20180316 | 1050 | 45729 | 3331 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 63250 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023736 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L3233 | 20180316 | 1054 | 47310 | 4496 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 26976 | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 18-0023880 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 1773 | 20180316 | 812 | 45340 | 3360 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 168000 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0023303 | OH | Sus | 31384483 | 2018 | MAR | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER | 1303 | 20180316 | 1154 | 45697 | 2002 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 155249 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023488 | OH | Sus | 0 | 2018 | MAR | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER | 1305 | 20180316 | 1321 | 45911 | 3168 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 278099 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023619 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 1222 | 20181014 | 1936 | 195004 | 2635 | Distribution Circuit | Vegetation | Tree - fell into line | 623 | 1641605 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0090288 | OH | Sus | 0 | 2018 | OCT | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 93116 | 20181014 | 1956 | 195020 | 2893 | Distribution Circuit | Vegetation | Tree - fell into line | 609 | 1694964 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0090290 | OH | Sus | 0 | 2018 | OCT | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1702 | 163451702 | OCB | 1702/2 | 20181129 | 1527 | 229315 | 1389 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4024 | 523222 | Overcast-Drizzle-Lightning-32-90 F | Conductor, Overhead | Broken, wire on object | 18-0105202 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | FUSE | 91241 | 20181129 | 752 | 228013 | 336 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 336 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104893 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 1679 | 20190106 | 1728 | 255894 | 430 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 28380 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005297 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CLAY-1101 | 163341101 | FUSE | 1833 | 20190106 | 1909 | 256855 | 1511 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3528 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005591 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CLAY-1103 | 163341103 | RECLOSER | 7142 | 20190106 | 1751 | 256076 | 1609 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 110371 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005229 | OH | Sus | 0 | 2019 | JAN | Yes | Multi-Fault | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | RECLOSER | 61816 | 20190106 | 1813 | 256272 | 615 | Distribution Circuit | Vegetation | Tree - fell into line | 372 | 141559 | Partly Cloudy-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005261 | OH | Sus | 0 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | L6029 | 20190106 | 1741 | 255991 | 1216 | Distribution Circuit | Vegetation | Tree - fell into line | 239 | 145852 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005220 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L559 | 20190106 | 1603 | 255579 | 535 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 5568 | Overcast-Fog-Snow-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0005159 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | FUSE | 1289 | 20190106 | 1659 | 257996 | 887 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 12418 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005424 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CORRAL-1101 | 162991101 | FUSE | 16065 | 20190116 | 1617 | 267328 | 651 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 10080 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0009917 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CORRAL-1103 | 162991103 | FUSE | L1991 | 20190116 | 1700 | 268230 | 200 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 4740 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010026 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L1279 | 20190116 | 2333 | 271922 | 2293 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 23704 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010826 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | MARTELL-1101 | 163011101 | FUSE | L5669 | 20190116 | 2323 | 271866 | 1190 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 16660 | Overcast-Fog-Heavy Rain-Lightning-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010669 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | MARTELL-1101 | 163011101 | FUSE | L2363 | 20190116 | 2327 | 271901 | 2048 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 16384 | Overcast-Fog-Heavy Rain-Lightning-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011256 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | TRIP-SAVER | 1765 | 20190116 | 2355 | 272062 | 835 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 67965 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010743 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | Yes
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | RECLOSER | 4788 | 20190116 | 2230 | 271610 | 1021 | Distribution Circuit | Vegetation | Tree - fell into line | 711 | 625611 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010339 | OH | Sus | 0 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L3231 | 20190117 | 1205 | 273879 | 1781 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 16029 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010994 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | TRIP-SAVER | 585 | 20190117 | 1710 | 274685 | 1042 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 80234 | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0011361 | OH | Sus | 0 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | CORRAL-1102 | 162991102 | FUSE | 19471 | 20190117 | 545 | 272568 | 415 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 830 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010586 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1702 | 163451702 | OTHER | WIRE DOWN @ MTR# 1004819778 | 20190117 | 58 | 272179 | 1070 | Distribution Circuit | Vegetation | Tree - fell into line | 239 | 38430 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010560 | OH | Sus | 0 | 2019 | JAN | Yes | Force Out | Yes | Yes
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L2751 | 20190117 | 0 | 272074 | 493 | Distribution Circuit | Vegetation | Tree - branch fell on line | 62 | 30566 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010499 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | TRIP-SAVER | L491 | 20190117 | 15 | 272322 | 1518 | Distribution Circuit | 3rd Party | Vehicle | 111 | 168498 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010514 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | 6681 | 20190117 | 200 | 272307 | 1418 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 54478 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010782 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | TRIP-SAVER | L485 | 20190117 | 729 | 272834 | 1930 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 42636 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010959 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 75348 | 20190117 | 13 | 272173 | 758 | Distribution Circuit | Vegetation | Tree - fell into line | 418 | 117666 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010460 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | L2657 | 20190202 | 751 | 286893 | 503 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 7079 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017029 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1701 | 162821701 | FUSE | 1103 | 20190202 | 1030 | 287195 | 550 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 36850 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017131 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 6028 | 20190202 | 802 | 286877 | 1854 | Distribution Circuit | Vegetation | Tree - fell into line | 947 | 411236 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0017012 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE | 869011 | 20190204 | 458 | 289473 | 900 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 18900 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0017827 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 1439 | 20190204 | 727 | 289520 | 442 | Distribution Circuit | Vegetation | Tree - fell into line | 237 | 16842 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0017737 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 13438 | 20190204 | 2207 | 291131 | 955 | Distribution Circuit | Vegetation | Tree - fell into line | 955 | 111619 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018191 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER | 3172 | 20190204 | 2348 | 291212 | 3968 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4362 | 5966430 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018203 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L1971 | 20190204 | 2348 | 294150 | 3933 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 66861 | Partly Cloudy-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0019078 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER | JWO MTR 1005018251 | 20190204 | 2348 | 294845 | 4940 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 415230 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0019376 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | 1485 | 20190204 | 2207 | 295231 | 5302 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 79530 | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0019560 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER | OJ 2 W/OF CGC# 224250028465 | 20190204 | 2348 | 295544 | 5519 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5519 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019749 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER | 34416 | 20190204 | 508 | 289485 | 408 | Distribution Circuit | Vegetation | Tree - fell into line | 450 | 75420 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 19-0017698 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L5679 | 20190204 | 1651 | s1413559 | 6591 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 32955 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0019771 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | CALAVERAS CEMENT-1101 | 162211101 | SWITCH | 1349 | 20190205 | 239 | 292459 | 3035 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 397585 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0018236 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L1635 | 20190205 | 754 | 291945 | 1920 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 29200 | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018437 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L477 | 20190205 | 1139 | 292553 | 2984 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 10720 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018566 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | CALAVERAS CEMENT-1101 | 162211101 | JUMPER | OJ AT 3620 SWISS RANCH RD | 20190205 | 105 | 294675 | 5149 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 30894 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019333 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | JUMPER | 91241 HIGH SIDE JPRS | 20190205 | 239 | 294962 | 3388 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3388 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019447 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | OTHER | WIRE DOWN ON MAINLINE FEEDING MTR# 10049782 | 20190205 | 1504 | 292931 | 845 | Distribution Circuit | Vegetation | Tree - fell into line | 624 | 107164 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018715 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 2 | FROGTOWN-1701 | 163451701 | FUSE | L2117 | 20190205 | 550 | 291667 | 625 | Distribution Circuit | Equipment Failure/Involved | Overhead | 101 | 37682 | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018332 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1701 | 163451701 | JUMPER | WIRE DOWN 2SP/LOAD SIDE OF L563 | 20190205 | 1541 | 293545 | 1502 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 78423 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018737 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
STOCKTON | Tier 3 | FROGTOWN-1701 | 163451701 | OTHER | WIRE DOWN LD SIDE OF L301 | 20190205 | 1149 | 294504 | 2828 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 8484 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0019268 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | TRIP-SAVER | 1021 | 20190205 | 1518 | 292941 | 1587 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 25958 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0018683 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 83098 | 20190205 | 718 | 291856 | 2375 | Distribution Circuit | Vegetation | Tree - fell into line | 198 | 467194 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018333 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L1117 | 20190205 | 544 | 292108 | 2463 | Distribution Circuit | Vegetation | Tree - fell into line | 150 | 369450 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018353 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | 76055 | 20190205 | 733 | 292405 | 2155 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 2155 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | On Ground | 19-0018413 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | OTHER | WIRE DOWN 4/S/SOUTH OF 12765 IRISHTOWN RD | 20190205 | 900 | 292454 | 490 | Distribution Circuit | Vegetation | Tree - fell into line | 535 | 27685 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018429 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L2217 | 20190205 | 900 | 292843 | 2163 | Distribution Circuit | Environmental/External | Ice or snow | 32 | 69216 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018608 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L3685 | 20190205 | 900 | 292943 | 1843 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 125324 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018360 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 1699 | 20190205 | 1918 | 293668 | 2707 | Distribution Circuit | Vegetation | Tree - fell into line | 975 | 227161 | Partly Cloudy-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019045 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L3109 | 20190205 | 900 | 294714 | 3337 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 83425 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019346 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L9769 | 20190205 | 900 | 295243 | 4773 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 38184 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019561 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | SALT SPRINGS-2101 | 163692101 | FUSE | 1589 | 20190205 | 1645 | 293028 | 10075 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 473525 | Partly Cloudy-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020162 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | STANISLAUS-1701 | 162821701 | RECLOSER | 59119 | 20190205 | 1226 | 292648 | 1502 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 50889 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0018519 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER | 4790 | 20190205 | 20 | 291260 | 5333 | Distribution Circuit | Vegetation | Tree - fell into line | 739 | 2006234 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018209 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | SWITCH | L3867 | 20190205 | 20 | 291610 | 5322 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 505590 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018209 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | TRIP-SAVER | 1303 | 20190205 | 8 | 291225 | 3977 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 441447 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018256 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L609 | 20190205 | 20 | 292308 | 2875 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 48875 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018397 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | TRIP-SAVER | L3733 | 20190205 | 44 | 291750 | 2275 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 220675 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018435 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | JUMPER | OJ CORNER OF WINTON RD & SKULL FLAT RD | 20190205 | 44 | 292901 | 3944 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 15776 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018624 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | JUMPER | OJ E OF MTR #1004935533 | 20190205 | 44 | 293004 | 2275 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2275 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018685 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | WEST POINT-1101 | 163201101 | FUSE | L1481 | 20190205 | 20 | 293110 | 3518 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 56288 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018725 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER | 36676 | 20190205 | 20 | 293663 | 4020 | Distribution Circuit | Vegetation | Tree - fell into line | 175 | 703500 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018749 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | 99353 | 20190205 | 20 | 293696 | 4020 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 24120 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on object | 19-0018760 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | 86823 | 20190205 | 44 | 294411 | 3944 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 59160 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0019217 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L871 | 20190205 | 900 | 294555 | 2088 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 29232 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | On Ground | 19-0019344 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L5679 | 20190209 | 927 | 296794 | 4848 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 24240 | Overcast-Fog-32-90 F | Conductor, Overhead | On Ground | 19-0020300 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
STOCKTON | Tier 2 | WEST POINT-1101 | 163201101 | FUSE | 1417 | 20190209 | 1022 | 296844 | 1819 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 10911 | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0020382 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 47968 | 20190210 | 502 | 298003 | 2398 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1157 | 229279 | Overcast-Fog-32-90 F | Insulator | Broken, wire on ground | 19-0020552 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 80930 | 20190210 | 622 | 298092 | 708 | Distribution Circuit | Vegetation | Tree - fell into line | 806 | 505850 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020604 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | RECLOSER | 61816 | 20190210 | 551 | 298046 | 625 | Distribution Circuit | Vegetation | Tree - fell into line | 360 | 191610 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020563 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | ELECTRA-1102 | 162161102 | RECLOSER | 2646 | 20190210 | 742 | 298370 | 629 | Distribution Circuit | Vegetation | Tree - fell into line | 309 | 147456 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020696 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | L1147 | 20190210 | 829 | 298386 | 578 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 3468 | Overcast-Snow-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0020719 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
STOCKTON | Tier 2 | MARTELL-1101 | 163011101 | OTHER | WIRE DOWN 1/N/OF L1669 | 20190210 | 629 | 298159 | 775 | Distribution Circuit | Equipment Failure/Involved | Overhead | 84 | 27748 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020636 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 2 | OLETA-1102 | 163541102 | FUSE | L2325 | 20190210 | 556 | 298050 | 870 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 46980 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020764 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | OTHER | WIRE DOWN N/OF 90281 | 20190210 | 434 | 298489 | 893 | Distribution Circuit | Vegetation | Tree - fell into line | 330 | 161234 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020740 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 36674 | 20190210 | 751 | 298123 | 167 | Distribution Circuit | 3rd Party | Vehicle | 100 | 16700 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on object | 19-0020591 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER | OJ AT CRN OF SHAKE RIDGE RD AND WANDERING HIL | 20190210 | 534 | 298529 | 768 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 5376 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020633 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | OTHER | WIRE DOWN 5 P/S OF 1715 | 20190210 | 535 | 298021 | 660 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 42108 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020689 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 80930 | 20190212 | 2158 | 301268 | 1006 | Distribution Circuit | Equipment Failure/Involved | Overhead | 320 | 296876 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021682 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L3469 | 20190212 | 2158 | 301646 | 899 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 899 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021688 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 1601 | 20190212 | 2158 | 303503 | 1213 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4852 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021994 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | JUMPER | OJ 3P SS MTR #1010028731 | 20190212 | 2158 | 305441 | 5313 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5313 | Overcast-32-90 F | Conductor, Overhead | On Ground | 19-0022521 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
STOCKTON | Tier 2 | ELECTRA-1102 | 162161102 | RECLOSER | 2646 | 20190212 | 2147 | 301202 | 2600 | Distribution Circuit | Equipment Failure/Involved | Overhead | 309 | 283608 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021705 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 13438 | 20190212 | 2201 | 301211 | 665 | Distribution Circuit | Vegetation | Tree - branch fell on line | 970 | 397339 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021636 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | OTHER | WIRE DOWN 1N OF LUEDERS CT ON BERTONE | 20190212 | 2206 | 301439 | 896 | Distribution Circuit | Vegetation | Tree - fell into line | 312 | 38519 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021737 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER | OJ 1SP N/OF MTR #1008768919 | 20190212 | 2309 | 304538 | 1129 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 10810 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0022237 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
STOCKTON | Tier 2 | STANISLAUS-1701 | 162821701 | FUSE | 2631 | 20190212 | 2344 | 301573 | 1061 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 11671 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021926 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | SWITCH | 1349 | 20190212 | 2158 | 305355 | 2399 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 338259 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021682 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 5889 | 20190212 | 2208 | 301311 | 3753 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 86319 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023879 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | STANISLAUS-1701 | 162821701 | FUSE | 43569 | 20190213 | 537 | 302980 | 240 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1395 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021927 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | TRIP-SAVER | L3733 | 20190213 | 419 | 302626 | 863 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 84574 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021834 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 4786 | 20190214 | 45 | 306057 | 1032 | Distribution Circuit | Vegetation | Tree - fell into line | 499 | 207326 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022721 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 47968 | 20190214 | 725 | 307292 | 1878 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 42123 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022883 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 36880 | 20190214 | 834 | 307824 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 279 | 89151 | Overcast-Fog-Heavy Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022953 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | JUMPER | OJS SS OF L5249 | 20190214 | 703 | 310391 | 1947 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9735 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0022883 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 2123 | 20190214 | 933 | 310174 | 1773 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 21276 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0023585 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | 8787 | 20190214 | 557 | 307096 | 276 | Distribution Circuit | Vegetation | Tree - fell into line | 138 | 20703 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022868 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | Yes
STOCKTON | Tier 2 | ELECTRA-1102 | 162161102 | FUSE | 185043 | 20190214 | 1430 | 309676 | 1630 | Distribution Circuit | Environmental/External | Water | 1 | 1630 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023377 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 1699 | 20190214 | 818 | 307704 | 1611 | Distribution Circuit | Vegetation | Tree - bark fell into line | 123 | 81827 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023309 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER | 4790 | 20190214 | 825 | 307719 | 554 | Distribution Circuit | Vegetation | Tree - fell into line | 1065 | 267879 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022935 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L5217 | 20190214 | 27 | 308001 | 1080 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2160 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022998 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | WEST POINT-1101 | 163201101 | TRIP-SAVER | 1341 | 20190214 | 1140 | 308760 | 1340 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 115240 | Overcast-Fog-Heavy Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023158 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 9149 | 20190215 | 1304 | 312173 | 1392 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 7455 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024085 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L3433 | 20190215 | 1805 | 312802 | 2583 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 51432 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024267 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5041 | 20190215 | 442 | 311324 | 873 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 31767 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023840 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | JUMPER | OJS 1P/E/OF MTR # 1004819624 | 20190215 | 1156 | 312361 | 421 | Distribution Circuit | Vegetation | Tree - fell into line | 670 | 22318 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0024011 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | 1853 | 20190217 | 1216 | 315830 | 1732 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 90064 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025153 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 13438 | 20190217 | 1455 | 316342 | 1724 | Distribution Circuit | Vegetation | Tree - fell into line | 946 | 337775 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025203 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | JUMPER | TREE THROUGH LINE LAST SPAN BEYOND L5981 | 20190217 | 2132 | 317122 | 875 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5894 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025518 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | OTHER | WIRE DOWN @ 27555 ASHLAND DR | 20190217 | 638 | 315356 | 2010 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 21210 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025037 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L2189 | 20190217 | 1612 | 316477 | 2825 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 42375 | Overcast-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025721 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 1888 | 20190226 | 1955 | 325192 | 608 | Distribution Circuit | Vegetation | Tree - fell into line | 1464 | 166100 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028537 | OH | Sus | 31426840 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CORRAL-1102 | 162991102 | JUMPER | WIRE DOWN AT TRANS POLE 10/198 | 20191010 | 419 | 652929 | 614 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3070 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0110003 | OH | Sus | 43986879 | 2019 | OCT | Yes | Open Circuit | Yes | Yes
STOCKTON | Tier 2 | CLAY-1103 | 163341103 | OCB | 1103/2 | 20191023 | 1221 | 677569 | 277 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1506 | 18960 | Clear-32-90 F | Pole-Wood | Broken, wire on object | 19-0115158 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | Yes
STOCKTON | Tier 2 | CORRAL-1102 | 162991102 | OTHER | WIRE DOWN 5479 PLEASANT OAK RD | 20191126 | 833 | 715107 | 343 | Distribution Circuit | Equipment Failure/Involved | Overhead | 123 | 41683 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0128739 | OH | Sus | 44107399 | 2019 | NOV | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L3679 | 20191127 | 657 | 720348 | 173 | Distribution Circuit | Vegetation | Tree - fell into line | 153 | 25845 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0129963 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER | OJ SE/OF L3539 | 20191127 | 712 | 720941 | 708 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 708 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0129963 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 1075 | 20191127 | 414 | 720133 | 931 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 51205 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0130339 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | STANISLAUS-1702 | 162821702 | FUSE | 1117 | 20191127 | 650 | 720327 | 570 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 12540 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0130126 | OH | Sus | 0 | 2019 | NOV | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 13438 | 20200117 | 1048 | 764762 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 539 | 89920 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010610 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L2245 | 20200117 | 24 | 763772 | 448 | Distribution Circuit | Vegetation | Tree - fell into line | 676 | 147619 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010393 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L2217 | 20200117 | 709 | 763865 | 302 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 9966 | Partly Cloudy-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0010476 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 2 | SALT SPRINGS-2102 | 163692102 | RECLOSER | 8442 | 20200315 | 252 | 851712 | 896 | Distribution Circuit | Vegetation | Tree - fell into line | 2007 | 70311 | Overcast-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 20-0032171 | OH | Sus | 0 | 2020 | MAR | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | SWITCH | L4045 | 20200316 | 1254 | 855570 | 342 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 19836 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032820 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | SALT SPRINGS-2102 | 163692102 | RECLOSER | 8442 | 20210118 | 618 | 1212119 | 703 | Distribution Circuit | Vegetation | Tree - fell into line | 2008 | 275749 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0009579 | OH | Sus | 0 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L485 | 20210119 | 317 | 1214377 | 774 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 21548 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010266 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5009 | 20210119 | 813 | 1215295 | 270 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 5670 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0010394 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L2049 | 20210119 | 717 | 1216152 | 629 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 74222 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010504 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | RECLOSER | 72036 | 20210119 | 917 | 1216087 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 2799 | 890430 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010491 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L2011 | 20210119 | 1717 | 1217783 | 138 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 2346 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0011070 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | CALAVERAS CEMENT-1101 | 162211101 | OTHER | WIRE DOWN 1 W/OF AND 1 S/OF 666931 | 20210125 | 526 | 1224366 | 898 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4490 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013680 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L3857 | 20210125 | 325 | 1223243 | 654 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 8525 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013820 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | OCB | 1101/2 | 20210125 | 349 | 1223291 | 883 | Distribution Circuit | Vegetation | Tree - fell into line | 1376 | 247531 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0013586 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L3101 | 20210125 | 437 | 1223338 | 616 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1848 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 21-0013821 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | JUMPER | WIRE DOWN 1 P S/W OF CGC 223836927246 | 20210126 | 58 | 1225470 | 526 | Distribution Circuit | Vegetation | Tree - fell into line | 280 | 52292 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0014249 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L2011 | 20210127 | 201 | 1232322 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 8738 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0015686 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | MARTELL-1103 | 163011103 | FUSE | L1247 | 20211011 | 1354 | 1493753 | 181 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 4887 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0129113 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | SALT SPRINGS-2102 | 163692102 | RECLOSER | 8442 | 20211011 | 2320 | 1495372 | 944 | Distribution Circuit | Vegetation | Tree - bark fell into line | 4470 | 2637835 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0129505 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CORRAL-1101 | 162991101 | RECLOSER | 12612 | 20211017 | 2302 | 1500403 | 897 | Distribution Circuit | 3rd Party | Vehicle | 322 | 69356 | Strong Winds-Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0132234 | OH | Sus | 35296048 | 2021 | OCT | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE | 1761 | 20211024 | 1548 | 1513915 | 142 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 2840 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136441 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L5247 | 20211025 | 1038 | 1518293 | 179 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 537 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0137138 | OH | Sus | 0 | 2021 | OCT | Yes | Open Circuit | Yes | Yes
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | RECLOSER | 61816 | 20211025 | 137 | 1516238 | 751 | Distribution Circuit | Vegetation | Tree - fell into line | 375 | 42917 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0136802 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | MARTELL-1101 | 163011101 | RECLOSER | 6074 | 20211025 | 540 | 1517030 | 570 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 5070 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136890 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 97924 | 20211025 | 1127 | 1518511 | 407 | Distribution Circuit | Vegetation | Tree - branch fell on line | 541 | 115868 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0137229 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | MARTELL-1101 | 163011101 | OCB | 1101/2 | 20211213 | 949 | 1566246 | 369 | Distribution Circuit | Vegetation | Tree - bark fell into line | 2275 | 82471 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0157044 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | RECLOSER | 3170 | 20211213 | 1846 | 1568471 | 227 | Distribution Circuit | Vegetation | Tree - fell into line | 679 | 54313 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0157540 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | OTHER | WIRE DOWN 16739 TONY LN | 20211213 | 1218 | 1570263 | 1654 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 4039 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0158043 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L5677 | 20211213 | 1221 | 1567081 | 504 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 6191 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0157351 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | FROGTOWN-1701 | 163451701 | FUSE | L483 | 20211214 | 800 | 1570100 | 244 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 488 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0157947 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L1161 | 20211214 | 426 | 1569581 | 784 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 7808 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0157930 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | 614959 | 20211226 | 133 | 1581988 | 587 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 30524 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0160678 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 4786 | 20221210 | 1711 | 1883787 | 289 | Distribution Circuit | Vegetation | Tree - fell into line | 166 | 29022 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138620 | OH | Sus | 0 | 2022 | DEC | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L5677 | 20221210 | 852 | 1881014 | 298 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 4517 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138260 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 269286 | 20221231 | 1217 | 1903871 | 175 | Distribution Circuit | Vegetation | Tree - fell into line | 2692 | 182904 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142569 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | OTHER | 1 PH WIRE DOWN S/OF L3293 | 20221231 | 1458 | 1904907 | 242 | Distribution Circuit | Vegetation | Tree - fell into line | 1779 | 155290 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142631 | OH | Sus | 0 | 2022 | DEC | Yes | Open Circuit | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 91241 | 20230104 | 53 | 1912612 | 676 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 676 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0005724 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | SWITCH | FIF | 20230105 | 755 | 1921332 | 436 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 58424 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0007053 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | 1065 | 20230110 | 949 | 1944308 | 294 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 4410 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0012186 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | OLETA-1102 | 163541102 | RECLOSER | 186326 | 20230110 | 414 | 1941794 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 876 | 203232 | Overcast-Fog-Drizzle-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0011885 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | OCB | 1102/2 | 20230110 | 434 | 1942529 | 265 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 15105 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0011905 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | RECLOSER | 4788 | 20230110 | 435 | 1943261 | 898 | Distribution Circuit | Vegetation | Tree - fell into line | 605 | 543290 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 23-0011905 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 34416 | 20230110 | 435 | 1943300 | 887 | Distribution Circuit | Vegetation | Tree - fell into line | 424 | 376088 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 23-0011905 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | RECLOSER | 72036 | 20230110 | 435 | 1943407 | 268 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 31624 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 23-0011905 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 93116 | 20230110 | 435 | 1943417 | 894 | Distribution Circuit | Vegetation | Tree - fell into line | 593 | 530142 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 23-0011905 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | SWITCH | L1047 | 20230110 | 435 | 1943958 | 881 | Distribution Circuit | Vegetation | Tree - fell into line | 410 | 361210 | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0011905 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 4790 | 20230110 | 435 | 1944174 | 890 | Distribution Circuit | Vegetation | Tree - fell into line | 506 | 450340 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0011905 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | SWITCH | L531 | 20230116 | 917 | 1957583 | 628 | Distribution Circuit | Vegetation | Tree - fell into line | 471 | 295788 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0017104 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | RECLOSER | 3142 | 20230116 | 1736 | 1958650 | 129 | Distribution Circuit | Vegetation | Tree - fell into line | 316 | 40764 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0017341 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | OCB | 1101/2 | 20230224 | 1520 | 2006053 | 189 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1408 | 49295 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0034248 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 53709 | 20230224 | 2202 | 2007457 | 646 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 646 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0035011 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER | 45292 | 20230227 | 1707 | 2013218 | 34 | Distribution Circuit | Vegetation | Tree - fell into line | 308 | 10472 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0036669 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L609 | 20230227 | 1435 | 2012700 | 389 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 6613 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0036613 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | JUMPER | OJ ON HARD TAP 1 W/OH 69623 | 20230228 | 2128 | 2017511 | 1026 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2052 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0037906 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | STANISLAUS-1701 | 162821701 | RECLOSER | 1812 | 20230228 | 1550 | 2016092 | 84 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 9072 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0037575 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
STOCKTON | Tier 2 | VALLEY SPRINGS-1101 | 168891101 | FUSE | 2119 | 20230309 | 1552 | 2027953 | 269 | Distribution Circuit | Equipment Failure/Involved | Overhead | 498 | 46830 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0042304 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | MARTELL-1101 | 163011101 | FUSE | L3801 | 20230314 | 918 | 2035466 | 298 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 25330 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0044675 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | ELECTRA-1102 | 162161102 | FUSE | L3841 | 20230321 | 1700 | 2058895 | 359 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 553 | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0049990 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE | 6677 | 20131121 | 1922 | 908563 | 386 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 25274 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078110 | OH | Sus | 41991609 | 2013 | NOV | Yes |  | Yes
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 23243 | 20141203 | 757 | 1121939 | 287 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 12054 | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073206 | OH | Sus | 31118857 | 2014 | DEC | Yes | Line to Ground | Yes
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9560 | 20141211 | 924 | 1132229 | 643 | Distribution Circuit | Vegetation | Tree - fell into line | 652 | 195121 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075233 | OH | Sus | 42295242 | 2014 | DEC | Yes | Line to Ground | Yes
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE | 5536 | 20141211 | 1941 | 1135767 | 325 | Distribution Circuit | Equipment Failure/Involved | Other | 109 | 10387 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075858 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | L2213 | 20141211 | 1204 | 1133731 | 532 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 21812 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075604 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
YOSEMITE | Tier 2 | COARSEGOLD-2102 | 254432102 | OCB | OCB | 20141230 | 1707 | 1155014 | 2766 | Distribution Circuit | Vegetation | Tree - fell into line | 1271 | 764428 | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079484 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE | 24198 | 20141230 | 1621 | 1155989 | 891 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 12849 | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079562 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
YOSEMITE | Tier 3 | OAKHURST-1102 | 254421102 | OCB | OCB | 20141230 | 1740 | 1154727 | 583 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1116 | 323217 | Combination wind/rain/lightning-32 - 90 F | Transformer | Broken, wire on ground | 14-0079361 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 77384 | 20141230 | 1646 | 1154124 | 859 | Distribution Circuit | Vegetation | Tree - fell into line | 460 | 267251 | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079321 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 10289 | 20141230 | 2024 | 1155444 | 1242 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 28566 | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079597 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 10060 | 20141230 | 1811 | 1154678 | 1254 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 62419 | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079412 | OH | Sus | 31123825 | 2014 | DEC | Yes | Line to Ground | Yes
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | OTHER |  | 20150208 | 1425 | 1183027 | 1414 | Distribution Circuit | Vegetation | Tree - branch fell on line | 663 | 102749 | Lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011639 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 6285 | 20151224 | 1603 | 1371220 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 220 | 24840 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087145 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | FUSE | 20082 | 20151224 | 334 | 1370699 | 573 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 5730 | Overcast-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 15-0087054 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 10337 | 20160217 | 1510 | 1405530 | 384 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 7716 | Strong Winds-Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0013219 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE | L1109 | 20160217 | 2032 | 1407085 | 501 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 15777 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013478 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | Yes
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20160217 | 2009 | 1406999 | 1529 | Distribution Circuit | Vegetation | Tree - fell into line | 157 | 143966 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0013527 | OH | Sus | 0 | 2016 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | CURTIS-1704 | 163351704 | FUSE | 1691 | 20160217 | 1710 | 1405975 | 794 | Distribution Circuit | Vegetation | Tree - fell into line | 145 | 104216 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0013320 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | FUSE | 20811 | 20160217 | 1941 | 1406828 | 880 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 8800 | Overcast-Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0013585 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE | L1773 | 20160217 | 1940 | 1406627 | 402 | Distribution Circuit | Vegetation | Tree - branch fell on line | 251 | 100902 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013458 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 10215 | 20160217 | 952 | 1404747 | 372 | Distribution Circuit | Vegetation | Tree - branch fell on line | 123 | 6386 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013041 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | L347 | 20160217 | 1905 | 1406346 | 425 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 9160 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013398 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 23246 | 20170108 | 1311 | 1626709 | 409 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3272 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0005473 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | OTHER | WIRE DOWN SS/OF 4569 | 20170108 | 1202 | 1625979 | 950 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 14250 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0005278 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | S1933 | 20170108 | 1428 | 1627326 | 302 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3322 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0005489 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 1715 | 20170109 | 523 | 1630215 | 301 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 13271 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005904 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 10569 | 20170110 | 2259 | 1638008 | 267 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 17955 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007281 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20170110 | 2200 | 1637832 | 3708 | Distribution Circuit | Vegetation | Tree - fell into line | 602 | 332739 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007385 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | CURTIS-1704 | 163351704 | FUSE | L537 | 20170110 | 1533 | 1634069 | 668 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 63460 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0006800 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 4642 | 20170110 | 2039 | 1636923 | 565 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 14690 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007153 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER | 8060 | 20170110 | 1904 | 1635913 | 550 | Distribution Circuit | Vegetation | Tree - branch fell on line | 918 | 245988 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0006975 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | FUSE | 20183 | 20170110 | 1902 | 1635853 | 992 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5952 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007396 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1704 | 163761704 | OCB | 1704/2 | 20170110 | 2337 | 1638092 | 219 | Distribution Circuit | Vegetation | Tree - fell into line | 677 | 112231 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007267 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1701 | 162831701 | FUSE | L1293 | 20170110 | 1737 | 1634756 | 1039 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 14546 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0006933 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1701 | 162831701 | FUSE | 21523 | 20170110 | 1927 | 1636153 | 1003 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 45135 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007288 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 5957 | 20170118 | 1723 | 1647381 | 338 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 5070 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010357 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 6165 | 20170119 | 449 | 1649895 | 541 | Distribution Circuit | Vegetation | Tree - fell into line | 204 | 21764 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0010667 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2103 | 254432103 | FUSE | 5868 | 20170120 | 1917 | 1655070 | 1182 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 35460 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0011778 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20170120 | 1006 | 1653644 | 805 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 57890 | Overcast-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0011538 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | OTHER | WIRE DOWN @ MTR 1004211477 | 20170120 | 2341 | 1655320 | 1243 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 23708 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011858 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S1219 | 20170120 | 2107 | 1656225 | 5553 | Distribution Circuit | Vegetation | Tree - bark fell into line | 404 | 1861104 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011965 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1701 | 162831701 | RECLOSER | 10720 | 20170120 | 2321 | 1655300 | 2459 | Distribution Circuit | Vegetation | Tree - fell into line | 153 | 376227 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011870 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | FUSE | 2543 | 20170121 | 645 | 1655701 | 1935 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 30960 | Overcast-Fog-Below 32 F | Insulator | Broken, wire on object | 17-0012069 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | FUSE | S1563 | 20170121 | 734 | 1655773 | 2111 | Distribution Circuit | Vegetation | Tree - grew into line | 32 | 23872 | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0012139 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | CURTIS-1705 | 163351705 | FUSE | S2041 | 20170121 | 132 | 1655410 | 3348 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 63152 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012155 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 20327 | 20170121 | 537 | 1655724 | 1938 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 25194 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | On Ground | 17-0011915 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 20325 | 20170121 | 535 | 1655723 | 657 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 17082 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011932 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 356738 | 20170121 | 803 | 1655833 | 3678 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 117696 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011991 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER | 10600 | 20170121 | 720 | 1656246 | 3730 | Distribution Circuit | Vegetation | Tree - fell into line | 304 | 791514 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011998 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 22625 | 20170121 | 701 | 1655730 | 4570 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 49023 | Overcast-Fog-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0012014 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 67455 | 20170121 | 1000 | 1656374 | 3277 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 51073 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0012061 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S2251 | 20170121 | 359 | 1655805 | 1062 | Distribution Circuit | Vegetation | Tree - fell into line | 354 | 343329 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012073 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 523056 | 20170121 | 1024 | 1656248 | 3537 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 53055 | Overcast-Fog-Snow-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0012081 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2067 | 20170121 | 504 | 1656221 | 4786 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 378094 | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 17-0012114 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 20329 | 20170121 | 652 | 1655708 | 4804 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 110492 | Overcast-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 17-0012136 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER | 8050 | 20170121 | 1843 | 1659135 | 1558 | Distribution Circuit | Vegetation | Tree - fell into line | 872 | 957431 | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0012821 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 1871 | 20170121 | 2056 | 1657288 | 3778 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 196456 | Overcast-Below 32 F | Conductor, Overhead | On Ground | 17-0013218 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2263 | 20170121 | 744 | 1655680 | 3410 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 264966 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013385 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2527 | 20170121 | 944 | 1656171 | 4626 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 60138 | Overcast-Fog-Below 32 F | Conductor, Overhead | On Ground | 17-0013433 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | PINECREST-0401 | 163160401 | FUSE | 1861 | 20170121 | 1935 | 1657181 | 2586 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 77580 | Clear-Below 32 F | Conductor, Overhead | On Ground | 17-0013264 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1103 | 252531103 | FUSE | 22593 | 20170121 | 1410 | 1656676 | 266 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 2926 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012085 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1701 | 162831701 | FUSE | 26307 | 20170121 | 1305 | 1664382 | 6026 | Distribution Circuit | Vegetation | Tree - branch fell on line | 106 | 638756 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013897 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1701 | 162831701 | JUMPER | OJS 1 S/OF CGC 321275160280 | 20170121 | 1553 | 1666433 | 5873 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 58730 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0014523 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | RECLOSER | 11290 | 20170122 | 4 | 1658371 | 3815 | Distribution Circuit | Equipment Failure/Involved | Overhead | 130 | 147843 | Overcast-Fog-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0013276 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2525 | 20170122 | 1341 | 1661133 | 2846 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 35642 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013168 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S2281 | 20170122 | 724 | 1664771 | 3269 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 134029 | Clear-Below 32 F | Crossarm, Wood | Broken, wire on ground | 17-0013996 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | Yes
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 10190 | 20170122 | 808 | 1659678 | 739 | Distribution Circuit | Vegetation | Tree - fell into line | 676 | 467067 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0013033 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 77384 | 20170122 | 1929 | 1662203 | 1360 | Distribution Circuit | Vegetation | Tree - fell into line | 455 | 183281 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013406 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1701 | 162831701 | FUSE | 20321 | 20170122 | 914 | 1664628 | 3581 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 204117 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013958 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE | 1617 | 20170123 | 217 | 1663088 | 537 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 51015 | Overcast-Snow-32-90 F | Conductor, Overhead | On Ground | 17-0013644 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | TRIP-SAVER | 10207 | 20170123 | 908 | 1663394 | 588 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 26460 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013784 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 10788 | 20170123 | 906 | 1663374 | 659 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 22439 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0013774 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2487 | 20170123 | 1257 | 1664078 | 504 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 49392 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013824 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 20311 | 20170123 | 1659 | 1664595 | 1355 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 7439 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0014015 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 20319 | 20170123 | 1726 | 1664713 | 1243 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 12979 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0014027 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | OTHER | WIRE DOWN 6 S/OF 6821 | 20170123 | 1000 | 1663553 | 1730 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 65870 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013981 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
YOSEMITE | Tier 3 | OAKHURST-1101 | 254421101 | FUSE | 5533 | 20170123 | 823 | 1664670 | 2042 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4084 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013968 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | FUSE | 2035 | 20170123 | 1120 | 1663805 | 550 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 6801 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013934 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 5725 | 20170123 | 1122 | 1663782 | 1474 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 47168 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0014033 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | FUSE | 86105 | 20170123 | 145 | 1662662 | 2076 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 45672 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013580 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1701 | 162831701 | FUSE | L1707 | 20170123 | 1304 | 1664106 | 3120 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 45808 | Partly Cloudy-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0014034 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1701 | 162831701 | FUSE | 26312 | 20170123 | 1257 | 1664076 | 3139 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 65919 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0014381 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | FUSE | 20771 | 20170207 | 103 | 1677320 | 706 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 14874 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018069 | OH | Sus | 31304303 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 12294 | 20170207 | 404 | 1677711 | 531 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 8282 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018129 | OH | Sus | 42939896 | 2017 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 7429 | 20170207 | 1111 | 1679892 | 1618 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 17334 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018653 | OH | Sus | 31304498 | 2017 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE | 2513 | 20170207 | 1211 | 1680090 | 681 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 18663 | Overcast-Drizzle-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018605 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2101 | 252192101 | RECLOSER | 10000 | 20170209 | 1728 | 1683971 | 594 | Distribution Circuit | Vegetation | Tree - fell into line | 196 | 53959 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0019623 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2101 | 252192101 | RECLOSER | 10000 | 20170217 | 927 | 1693299 | 322 | Distribution Circuit | Vegetation | Tree - fell into line | 196 | 41981 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022157 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER | 4170 | 20170217 | 1709 | 1697621 | 1461 | Distribution Circuit | Vegetation | Tree - fell into line | 900 | 590508 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022662 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | FUSE | 2545 | 20170217 | 1311 | 1695876 | 733 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 19791 | Overcast-Fog-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022408 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 56337 | 20170217 | 1540 | 1698618 | 1526 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 13734 | Overcast-Fog-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022767 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | KERCKHOFF-1101 | 252561101 | FUSE | 19022 | 20170217 | 1742 | 1697863 | 1675 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 14793 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022730 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE | 2272 | 20170217 | 1341 | 1696056 | 1530 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 44370 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022417 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2102 | 254452102 | JUMPER | WIRE DWN N/OF MTR 1007100638 | 20170217 | 1230 | 1696483 | 1753 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1753 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022326 | OH | Sus | 0 | 2017 | FEB | Yes | Open Circuit | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 20327 | 20170217 | 1218 | 1695543 | 800 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 1904 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022335 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2275 | 20170217 | 1935 | 1698261 | 1565 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 87640 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022774 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE | 92593 | 20170217 | 1747 | 1697933 | 1293 | Distribution Circuit | Vegetation | Tree - fell into line | 290 | 319070 | Overcast-Fog-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022963 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9560 | 20170220 | 1501 | 1703616 | 826 | Distribution Circuit | Vegetation | Tree - fell into line | 657 | 245117 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0023866 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2102 | 254432102 | JUMPER | OJ @ MTR#1005028543 | 20170220 | 1010 | 1702901 | 201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 201 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0023724 | OH | Sus | 0 | 2017 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 1723 | 20170220 | 1418 | 1703495 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 10487 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0023882 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | JUMPER | L1759 | 20170220 | 1828 | 1706344 | 557 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 5551 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024595 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER | 10600 | 20170220 | 1729 | 1704921 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 847 | 360667 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024006 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | OTHER | WIRE DOWN | 20170220 | 1812 | 1705891 | 793 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 10309 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024084 | OH | Sus | 0 | 2017 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | L347 | 20170220 | 1829 | 1705151 | 345 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 17250 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024077 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 90320 | 20170221 | 43 | 1706981 | 433 | Distribution Circuit | Vegetation | Tree - fell into line | 995 | 136819 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024773 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 21017 | 20170221 | 311 | 1707281 | 934 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 37360 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024994 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | MIWUK-1702 | 163661702 | JUMPER | WIRE DOWN AT INT OF RIDGE VIEW & CREEKSIDE | 20170221 | 934 | 1708246 | 393 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 60858 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025032 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | JUMPER | WIRE DWN .5 N/OF 22182 | 20170222 | 1429 | 1710873 | 246 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 492 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025713 | OH | Sus | 0 | 2017 | FEB | Yes | Open Circuit | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 19689 | 20170222 | 1645 | 1711109 | 1013 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5065 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025762 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9560 | 20170406 | 2250 | 1746649 | 1019 | Distribution Circuit | Vegetation | Tree - fell into line | 657 | 337855 | Overcast-Drizzle-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0037414 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE | L2297 | 20170406 | 2012 | 1746573 | 883 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 43910 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037524 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 2071 | 20170406 | 2018 | 1746627 | 1152 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 46554 | Overcast-Drizzle-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037621 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 44913 | 20170406 | 2019 | 1746872 | 734 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2202 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037385 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2057 | 20170406 | 2254 | 1748568 | 873 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 65460 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037600 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1705 | 163781705 | RECLOSER | 70198 | 20170406 | 2131 | 1747854 | 1400 | Distribution Circuit | Vegetation | Tree - fell into line | 1453 | 585827 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037401 | OH | Sus | 0 | 2017 | APR | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | JUMPER | WIRE DOWN 4 SPANS W/OF 4172 HWY 132 | 20170407 | 528 | 1749492 | 471 | Distribution Circuit | Vegetation | Tree - fell into line | 207 | 11226 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037649 | OH | Sus | 0 | 2017 | APR | Yes | Open Circuit | Yes | Yes
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 254432104 | JUMPER | 1 S/OF METER 1005028923 | 20170407 | 1225 | 1750653 | 180 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 180 | Overcast-Rain-32-90 F | Insulator | Broken, wire on ground | 17-0037885 | OH | Sus | 0 | 2017 | APR | Yes | Open Circuit | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE | 4585 | 20170407 | 338 | 1749338 | 827 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 51895 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037588 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 83411 | 20170407 | 805 | 1749567 | 782 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4485 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0037651 | OH | Sus | 0 | 2017 | APR | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | JUMPER | WIRE DOWN 2 SPANS N/OF 1005639096 | 20170407 | 557 | 1750837 | 1011 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 13630 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037882 | OH | Sus | 0 | 2017 | APR | Yes | Open Circuit | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | RECLOSER | 8120 | 20170407 | 2158 | 1752019 | 173 | Distribution Circuit | Vegetation | Tree - fell into line | 421 | 72833 | Overcast-Rain-32-90 F | Conductor, Overhead | On Ground | 17-0038164 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 10140 | 20171204 | 2239 | 1936143 | 501 | Distribution Circuit | Vegetation | Tree - fell into line | 1025 | 303452 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099860 | OH | Sus | 31368360 | 2017 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | FUSE | 22797 | 20180316 | 1231 | 45965 | 654 | Distribution Circuit | Vegetation | Tree - branch fell on line | 100 | 17304 | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 18-0023455 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 20319 | 20180316 | 939 | 46303 | 2141 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 36397 | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 18-0023597 | OH | Sus | 0 | 2018 | MAR | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE | S1555 | 20180316 | 1111 | 45874 | 1835 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 135790 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0023543 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE | 22785 | 20180316 | 1153 | 45960 | 404 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3636 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0023545 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | Yes
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER | 6018 | 20180316 | 1421 | 46035 | 1776 | Distribution Circuit | Vegetation | Tree - fell into line | 614 | 856508 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0023546 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE | S1551 | 20180316 | 1421 | 46156 | 1645 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 27965 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0023559 | OH | Sus | 0 | 2018 | MAR | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE | S1557 | 20180316 | 1423 | 46334 | 1643 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 221805 | Overcast-Fog-Below 32 F | Crossarm, Wood | Broken, wire on ground | 18-0023616 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S1219 | 20181129 | 8 | 227311 | 483 | Distribution Circuit | Vegetation | Tree - fell into line | 403 | 194649 | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0104659 | OH | Sus | 0 | 2018 | NOV | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S2281 | 20181129 | 413 | 227701 | 987 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 29079 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0104767 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 24459 | 20190106 | 1838 | 256566 | 1322 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 7682 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005556 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | MERCED FALLS-1102 | 252811102 | FUSE | 8522 | 20190106 | 1855 | 256767 | 891 | Distribution Circuit | Equipment Failure/Involved | Overhead | 544 | 43545 | Overcast-Fog-Heavy Rain-32-90 F | Insulator | Broken, wire on ground | 19-0005406 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2477 | 20190106 | 1737 | 255964 | 1337 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 29414 | Overcast-Fog-Snow-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005274 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2489 | 20190106 | 1739 | 255977 | 1446 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 40226 | Overcast-Fog-Snow-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0005331 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE | 10507 | 20190116 | 2345 | 272021 | 1137 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 23877 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010502 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S1787 | 20190116 | 2137 | 271839 | 1320 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 141240 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on object | 19-0010410 | OH | Sus | 0 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 523056 | 20190116 | 2335 | 273854 | 1292 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 19380 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on object | 19-0010983 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER | 1808 | 20190116 | 1936 | 269994 | 1396 | Distribution Circuit | Vegetation | Tree - fell into line | 280 | 122341 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010113 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | CURTIS-1703 | 163351703 | RECLOSER | 9240 | 20190117 | 26 | 272170 | 885 | Distribution Circuit | Vegetation | Tree - fell into line | 2643 | 1033194 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010458 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | OTHER | WIRE DOWN ON GRD SOURCE SIDE OF L1207 | 20190117 | 1309 | 274086 | 1201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1269 | 82537 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011065 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 2317 | 20190117 | 1409 | 275202 | 1809 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 8898 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011525 | OH | Sus | 0 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | FUSE | L1473 | 20190117 | 2 | 272081 | 2163 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 21945 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010831 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 24458 | 20190117 | 635 | 272681 | 1727 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 13816 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010833 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | OCB | 1701/2 | 20190117 | 13 | 272123 | 1254 | Distribution Circuit | Vegetation | Tree - fell into line | 2841 | 1041827 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0010443 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2477 | 20190117 | 212 | 272325 | 932 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 20504 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010572 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2261 | 20190117 | 1209 | 273894 | 386 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 71796 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011074 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | JUMPER | WIERE DOWN | 20190117 | 715 | 272786 | 2065 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 2515 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011654 | OH | Sus | 0 | 2019 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | FUSE | 1921 | 20190117 | 619 | 275675 | 2072 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12432 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011723 | OH | Sus | 0 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 4636 | 20190202 | 534 | 286531 | 828 | Distribution Circuit | Animal | Other | 33 | 20102 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0016964 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE | S1999 | 20190202 | 1207 | 287373 | 401 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1840 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017193 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | FUSE | 1997 | 20190202 | 532 | 286525 | 485 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5820 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 19-0017053 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 5679 | 20190204 | 1559 | 290667 | 308 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 37576 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0018110 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20190204 | 1057 | 290037 | 4853 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 227913 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0017879 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | JUMPER | WIRE DOWN @ MTR#1005968059 | 20190204 | 356 | 289483 | 791 | Distribution Circuit | Vegetation | Tree - fell into line | 3921 | 44912 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017701 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 5120 | 20190204 | 1458 | 290572 | 4393 | Distribution Circuit | Vegetation | Tree - fell into line | 405 | 1778127 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0018046 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 77384 | 20190204 | 2124 | 291114 | 1256 | Distribution Circuit | Vegetation | Tree - fell into line | 466 | 201670 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018163 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 10813 | 20190204 | 1641 | 290715 | 4003 | Distribution Circuit | Vegetation | Tree - fell into line | 140 | 439643 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018207 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 5585 | 20190204 | 1935 | 290897 | 2694 | Distribution Circuit | Environmental/External | Ice or snow | 33 | 88902 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018502 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 23987 | 20190204 | 1911 | 292665 | 4110 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 83195 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018959 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 10060 | 20190204 | 1913 | 290889 | 1020 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 80823 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018141 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER | 4170 | 20190205 | 917 | 292153 | 376 | Distribution Circuit | Vegetation | Tree - fell into line | 416 | 155480 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018372 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 10714 | 20190205 | 29 | 292453 | 2511 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 22599 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018428 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 23942 | 20190205 | 29 | 293666 | 2511 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 198369 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018744 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE | 2254 | 20190205 | 325 | 292939 | 2275 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 86187 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018651 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 10443 | 20190205 | 835 | 292039 | 3543 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 47139 | Overcast-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018767 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | RECLOSER | 68380 | 20190205 | 116 | 291286 | 3940 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 520747 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018218 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | RECLOSER | 8000 | 20190205 | 335 | 291292 | 3774 | Distribution Circuit | Vegetation | Tree - fell into line | 246 | 876060 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018245 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 37158 | 20190205 | 329 | 292224 | 2075 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 10375 | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018388 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 2505 | 20190205 | 49 | 292339 | 4338 | Distribution Circuit | Vegetation | Tree - fell into line | 204 | 884952 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on object | 19-0018398 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | SWITCH | 111443 | 20190205 | 49 | 292372 | 4367 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 235818 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on object | 19-0018407 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | FUSE | 2439 | 20190205 | 116 | 292733 | 3940 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 149720 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018550 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE | S2263 | 20190205 | 429 | 291709 | 3653 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 51142 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018632 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 22184 | 20190205 | 602 | 293063 | 3460 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 20760 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | On Ground | 19-0018713 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE | L2155 | 20190205 | 602 | 293674 | 3188 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 47820 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018754 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 22955 | 20190205 | 602 | 293723 | 3288 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 23016 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018770 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 89917 | 20190205 | 602 | 293975 | 4853 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 57423 | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018263 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | TRIP-SAVER | 9111 | 20190205 | 602 | 294031 | 2300 | Distribution Circuit | Vegetation | Tree - fell into line | 266 | 525355 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019034 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | FUSE | 85609 | 20190205 | 116 | 295287 | 3940 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 31520 | Clear-Below 32 F | Conductor, Overhead | On Ground | 19-0019594 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 2535 | 20190205 | 116 | 295365 | 4001 | Distribution Circuit | Vegetation | Tree - fell into line | 160 | 640160 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019632 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | JUMPER | OJ 4 SW/OF MTR# 1004235694 | 20190205 | 335 | 295829 | 6178 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6178 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019811 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | CURTIS-1703 | 163351703 | RECLOSER | 9330 | 20190205 | 129 | 291313 | 2431 | Distribution Circuit | Vegetation | Tree - fell into line | 276 | 101536 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018224 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | CURTIS-1703 | 163351703 | FUSE | L1927 | 20190205 | 12 | 295701 | 4173 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 95979 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019778 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | RECLOSER | 11290 | 20190205 | 710 | 291831 | 4570 | Distribution Circuit | Vegetation | Tree - branch fell on line | 132 | 113685 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018284 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | FUSE | L1413 | 20190205 | 1905 | 293635 | 697 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 19516 | Partly Cloudy-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018961 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | JUMPER | JPRS OPEN 1 E/OF MTR# 1004937489 | 20190205 | 1905 | 293856 | 2915 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5830 | Partly Cloudy-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018962 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | CURTIS-1704 | 163351704 | JUMPER | WIRE DOWN 4SP/LOAD SIDE 20807 | 20190205 | 1930 | 293662 | 1038 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 20016 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018977 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | OTHER | WIRE DOWN 1 S/LOAD SIDE OF 22357 | 20190205 | 812 | 291982 | 1918 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7672 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019232 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 19472 | 20190205 | 143 | 291320 | 2285 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 25135 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018463 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 19464 | 20190205 | 759 | 292598 | 4456 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 13368 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018489 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 21473 | 20190205 | 455 | 292759 | 4595 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 18380 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018565 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 21469 | 20190205 | 759 | 292784 | 528 | Distribution Circuit | Environmental/External | Ice or snow | 162 | 58285 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018581 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | JUMPER | JPRS @ BUCKHORN MOUNTAIN RD & ROB RIC RD | 20190205 | 755 | 293014 | 3030 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 27270 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018690 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | JUMPER | JPRS @ ANDRA DR & BLACK OAK RD | 20190205 | 629 | 293099 | 2061 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 39159 | Overcast-Fog-Snow-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0018723 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | SWITCH | L1021 | 20190205 | 759 | 293920 | 1978 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 219631 | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0018309 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | CURTIS-1705 | 163351705 | FUSE | S2041 | 20190205 | 226 | 294198 | 2385 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 109710 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019111 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | CURTIS-1705 | 163351705 | FUSE | 2473 | 20190205 | 226 | 294231 | 3485 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 209100 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019131 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 19514 | 20190205 | 226 | 294234 | 3485 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 45305 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0019132 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2525 | 20190205 | 446 | 291615 | 2333 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 30329 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018659 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MIWUK-1702 | 163661702 | RECLOSER | 47143 | 20190205 | 120 | 291213 | 2457 | Distribution Circuit | Vegetation | Tree - fell into line | 183 | 414415 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018222 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | OCB | 1702/2 | 20190205 | 330 | 291297 | 2522 | Distribution Circuit | Vegetation | Tree - fell into line | 3248 | 2051686 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018244 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 5541 | 20190205 | 807 | 291898 | 571 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 48535 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018410 | OH | Sus | 31424289 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 10293 | 20190205 | 1141 | 292923 | 4360 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 34580 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018772 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 19617 | 20190205 | 1820 | 293145 | 2664 | Distribution Circuit | Vegetation | Tree - branch fell on line | 226 | 102889 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019368 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER | 69124 | 20190205 | 712 | 291840 | 1986 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 333648 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018287 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER | 3186 | 20190205 | 635 | 291777 | 3281 | Distribution Circuit | Vegetation | Tree - fell into line | 645 | 452257 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018294 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | RECLOSER | 9190 | 20190205 | 1007 | 292342-2 | 1755 | Distribution Circuit | Vegetation | Tree - fell into line | 791 | 838169 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018399 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | JUMPER | JPRS 1 N/OF 320294755490 | 20190205 | 1007 | 294032 | 2962 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5924 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0019036 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
YOSEMITE | Tier 3 | RACETRACK-1703 | 163761703 | SWITCH | UNNUM | 20190205 | 1007 | 294131 | 2945 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 58900 | Overcast-Snow-Below 32 F | Conductor, Overhead | On Ground | 19-0019064 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | JUMPER | OJ @ 749 SHAWS FLAT | 20190205 | 846 | 294448 | 3209 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6418 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019240 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 26384 | 20190205 | 1341 | 292776 | 4424 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4424 | Overcast-Drizzle-32-90 F | Conductor, Overhead | On Ground | 19-0019273 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 673480 | 20190205 | 842 | 292065 | 1620 | Distribution Circuit | Vegetation | Tree - fell into line | 889 | 546452 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018600 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | FUSE | 10212 | 20190205 | 1815 | 294471 | 2460 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 19680 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019298 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | OTHER | WIRE DOWN @ MTR# 1008929795 | 20190205 | 715 | 291830 | 699 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 959 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018528 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
YOSEMITE | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | SWITCH | 5424 | 20190205 | 630 | 291604 | 3270 | Distribution Circuit | Equipment Failure/Involved | Overhead | 179 | 6474 | Overcast-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0018272 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
YOSEMITE | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 10236 | 20190205 | 516 | 291635 | 888 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 88800 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018443 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 70225 | 20190205 | 727 | 291864 | 1644 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 16440 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018802 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | TRANSFORMER | 320303056730 | 20190209 | 2220 | 297487 | 2189 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2189 | Rain-Overcast-32-90 F | Transformer | Broken, wire on ground | 19-0020474 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 19617 | 20190209 | 1451 | 297222 | 1464 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 43920 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020388 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 10277 | 20190209 | 2124 | 298732 | 2382 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2382 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020653 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 7277 | 20190210 | 532 | 298014 | 1898 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 49382 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020666 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | FUSE | 19526 | 20190210 | 542 | 298029 | 663 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 19160 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020620 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20190210 | 645 | 298026 | 1126 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 150544 | Overcast-Fog-Snow-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0020568 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | CURTIS-1704 | 163351704 | JUMPER | OJ TWD MTR# 1004720077 | 20190210 | 802 | 298856 | 714 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 714 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0020594 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | FUSE | 20811 | 20190210 | 900 | 298461 | 710 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 8520 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020720 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | RECLOSER | 39256 | 20190210 | 943 | 298591 | 337 | Distribution Circuit | Vegetation | Tree - fell into line | 521 | 69186 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020660 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 10493 | 20190210 | 720 | 298268 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 156 | 88452 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020587 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 79097 | 20190210 | 629 | 298472 | 657 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 7884 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0020626 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | OTHER | WIRE DOWN @ FUCO 26389 | 20190210 | 544 | 298288 | 650 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3508 | 366649 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0020606 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
YOSEMITE | Tier 2 | RACETRACK-1704 | 163761704 | FUSE | L2627 | 20190210 | 702 | 298156 | 192 | Distribution Circuit | Equipment Failure/Involved | Overhead | 555 | 34605 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020582 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | FUSE | 10256 | 20190210 | 1011 | 298642 | 479 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 14849 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020702 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 10060 | 20190210 | 1315 | 298972 | 295 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 13580 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020721 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | TAR FLAT-0401 | 163240401 | FUSE | 1879 | 20190210 | 723 | 298200 | 339 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 8166 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020641 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | JUMPER | BUCK LINE DOWN 1E &1S OF MTR 1006926367 | 20190212 | 2351 | 302499 | 890 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 26700 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021752 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9560 | 20190213 | 246 | 302244 | 979 | Distribution Circuit | Vegetation | Tree - fell into line | 662 | 308990 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021738 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | JUMPER | WIRE DOWN 2 NW/OF MTR# 1004898423 | 20190213 | 806 | 303130 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 469 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022034 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 10219 | 20190213 | 720 | 302991 | 2065 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8478 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022218 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | RECLOSER | 10250 | 20190213 | 205 | 301872 | 48 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 48 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021739 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER | 953336 | 20190213 | 433 | 302650 | 558 | Distribution Circuit | Vegetation | Tree - fell into line | 360 | 147520 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021776 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER | 79118 | 20190213 | 632 | 302899 | 736 | Distribution Circuit | Vegetation | Tree - fell into line | 139 | 66400 | Overcast-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0021822 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | JUMPER | WIRE DOWN | 20190213 | 740 | 304757 | 465 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 930 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022332 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 23937 | 20190214 | 655 | 307259 | 6355 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7441 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022980 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 4629 | 20190214 | 1109 | 308494 | 1785 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 230265 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023251 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 10714 | 20190214 | 1109 | 309451 | 3288 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 29592 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023307 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9560 | 20190214 | 1231 | 309804 | 1663 | Distribution Circuit | Vegetation | Tree - fell into line | 520 | 172967 | Overcast-Heavy Rain-Lightning-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023274 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 23943 | 20190214 | 1541 | 310011 | 1694 | Distribution Circuit | Vegetation | Tree - bark fell into line | 8 | 13552 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023624 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | BEAR VALLEY-2105 | 252192105 | FUSE | 10268 | 20190214 | 1723 | 312097 | 4252 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 29764 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024031 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 23939 | 20190214 | 1109 | 312712 | 1918 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5754 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023307 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | RECLOSER | 5380 | 20190214 | 1308 | 309344 | 4357 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 71879 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023285 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2104 | 254432104 | FUSE | 10275 | 20190214 | 1035 | 308712 | 203 | Distribution Circuit | Vegetation | Tree - bark fell into line | 123 | 24969 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023104 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | CURTIS-1703 | 163351703 | RECLOSER | 9240 | 20190214 | 628 | 307191 | 645 | Distribution Circuit | Vegetation | Tree - fell into line | 2474 | 654340 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022848 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20190214 | 1205 | 308894 | 532 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 36708 | Overcast-Heavy Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023182 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE | L2287 | 20190214 | 1302 | 309596 | 1763 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 172774 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023349 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | SWITCH | S1215 | 20190214 | 1205 | 310867 | 3294 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 209390 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023182 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1705 | 163781705 | FUSE | 20829 | 20190214 | 641 | 307244 | 912 | Distribution Circuit | Vegetation | Tree - branch fell on line | 101 | 68652 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023359 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1705 | 163781705 | FUSE | 53401 | 20190214 | 1110 | 308497 | 588 | Distribution Circuit | Vegetation | Tree - bark fell into line | 22 | 12936 | Overcast-Heavy Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023399 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | CURTIS-1703 | 163351703 | RECLOSER | 9330 | 20190215 | 1735 | 312723 | 1098 | Distribution Circuit | Vegetation | Tree - fell into line | 371 | 287294 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024219 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | SWITCH | 6323 | 20190215 | 1735 | 313231 | 1085 | Distribution Circuit | Vegetation | Tree - bark fell into line | 156 | 169260 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024219 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 5651 | 20190215 | 1737 | 314639 | 2611 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 20888 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024630 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | JUMPER | DDE 1P/S OF 20991 | 20190215 | 1737 | 315882 | 2903 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 14515 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025144 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | JUMPER | OJ 1 P/N & 3 P/W OF 5651 | 20190215 | 1737 | 315885 | 5663 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 11469 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025145 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 4553 | 20190215 | 1610 | 312565 | 206 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 19570 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024204 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 5120 | 20190215 | 2042 | 312996 | 2338 | Distribution Circuit | Vegetation | Tree - fell into line | 669 | 1235032 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024287 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2525 | 20190216 | 1424 | 314599 | 1685 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 21905 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024690 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2481 | 20190216 | 1749 | 314878 | 140 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 7280 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024703 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2523 | 20190216 | 1749 | 315045 | 2916 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2916 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0024755 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S2251 | 20190216 | 1807 | 314908 | 2847 | Distribution Circuit | Vegetation | Tree - fell into line | 355 | 805589 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025095 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | L2213 | 20190216 | 1657 | 315774 | 4117 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 32138 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025234 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER | 8090 | 20190216 | 1353 | 314559 | 1664 | Distribution Circuit | Environmental/External | Ice or snow | 611 | 220748 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024598 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER | 1808 | 20190216 | 1742 | 314873 | 3067 | Distribution Circuit | Vegetation | Tree - fell into line | 208 | 124801 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024698 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | TRIP-SAVER | S2247 | 20190216 | 2119 | 315193 | 2609 | Distribution Circuit | Vegetation | Tree - fell into line | 194 | 152040 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025060 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 10060 | 20190216 | 1003 | 313840 | 481 | Distribution Circuit | Equipment Failure/Involved | Overhead | 109 | 11398 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024467 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER | 9690 | 20190216 | 1055 | 313959 | 4412 | Distribution Circuit | Vegetation | Tree - fell into line | 687 | 201858 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024502 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2481 | 20190217 | 453 | 315233 | 949 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 49348 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025065 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | OCB | 1701/2 | 20190217 | 1142 | 315741 | 391 | Distribution Circuit | Vegetation | Tree - fell into line | 3739 | 345369 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025122 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 851 | 20190217 | 1329 | 315995 | 2788 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 55760 | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0025202 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2261 | 20190217 | 1809 | 316637 | 1521 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 89104 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025313 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2525 | 20190217 | 1916 | 316743 | 1546 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 20098 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025367 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER | 1808 | 20190217 | 1505 | 317521 | 2493 | Distribution Circuit | Vegetation | Tree - fell into line | 185 | 442429 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025206 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1101 | 254421101 | FUSE | 5533 | 20190217 | 940 | 315503 | 1594 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 3188 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025209 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
YOSEMITE | Tier 2 | PEORIA FLAT-1705 | 163781705 | FUSE | 53401 | 20190226 | 1336 | 324566 | 667 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 4831 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028420 | OH | Sus | 31426754 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 1993 | 20190923 | 2304 | 608006 | 1208 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 24160 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0102785 | OH | Sus | 31473062 | 2019 | SEP | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | RECLOSER | 439030 | 20191127 | 947 | 720969 | 399 | Distribution Circuit | Equipment Failure/Involved | Overhead | 398 | 158802 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0130133 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 19165 | 20191127 | 859 | 720816 | 684 | Distribution Circuit | Vegetation | Tree - bark fell into line | 3 | 2052 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0130160 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | TRANSFORMER | 321690936488 | 20191127 | 829 | 721762 | 605 | Distribution Circuit | Vegetation | Tree - bark fell into line | 1 | 605 | Snow-Overcast-Fog-32-90 F | Transformer | Broken, wire on ground | 19-0130432 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | OTHER | WIRE DOWN 1 S/E OF 42875 | 20191127 | 207 | 720359 | 927 | Distribution Circuit | Vegetation | Tree - fell into line | 515 | 94402 | Overcast-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 19-0129973 | OH | Sus | 0 | 2019 | NOV | Yes | Open Circuit | Yes | Yes
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | FUSE | 6095 | 20200209 | 716 | 781175 | 608 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 58368 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0018918 | OH | Sus | 44182951 | 2020 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER | 9690 | 20200315 | 1046 | 852234 | 501 | Distribution Circuit | Vegetation | Tree - fell into line | 687 | 344187 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032283 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | FUSE | 19526 | 20200316 | 1401 | 855544 | 221 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 8840 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032980 | OH | Sus | 0 | 2020 | MAR | Yes | None | Yes | No
YOSEMITE | Tier 3 | CURTIS-1704 | 163351704 | FUSE | 20809 | 20200316 | 1058 | 854413 | 384 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 19200 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032792 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE | 10302 | 20200316 | 2316 | 856114 | 1226 | Distribution Circuit | Vegetation | Tree - fell into line | 148 | 141152 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 20-0033119 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 10204 | 20200316 | 2326 | 856117 | 1174 | Distribution Circuit | Environmental/External | Ice or snow | 19 | 8698 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 20-0033114 | OH | Sus | 31497454 | 2020 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 2443 | 20200316 | 1222 | 855076 | 411 | Distribution Circuit | Vegetation | Tree - branch fell on line | 117 | 48087 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032871 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | INDIAN FLAT-1104 | 252691104 | OTHER | WIRE DOWN 1211 YOSEMITE WAY | 20210119 | 612 | 1215499 | 780 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 61 | 38155 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0010698 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 22618 | 20210119 | 406 | 1217697 | 942 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 27318 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010175 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1101 | 254421101 | JUMPER | OJ 2 POLES S/OF 5422 | 20210119 | 912 | 1217448 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3094 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010941 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE | S1795 | 20210125 | 814 | 1224186 | 508 | Distribution Circuit | Equipment Failure/Involved | Overhead | 185 | 93980 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0013806 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 21665 | 20210125 | 243 | 1223111 | 867 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 53754 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0013596 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | FUSE | 6825 | 20210125 | 354 | 1223872 | 624 | Distribution Circuit | Equipment Failure/Involved | Overhead | 149 | 92976 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0013719 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE | L1773 | 20210125 | 351 | 1223284 | 435 | Distribution Circuit | Equipment Failure/Involved | Overhead | 261 | 90068 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0013688 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | RECLOSER | 6014 | 20210125 | 341 | 1223279 | 102 | Distribution Circuit | Vegetation | Tree - branch fell on line | 446 | 45492 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013585 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | JUMPER | WIRE DOWN 1/W/OF 19102 | 20210125 | 18 | 1224516 | 1082 | Distribution Circuit | Vegetation | Tree - branch fell on line | 247 | 35745 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0013937 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE | 10022 | 20210128 | 116 | 1238248 | 824 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 61800 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0017155 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 19463 | 20211025 | 119 | 1516277 | 1214 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4856 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0137086 | OH | Sus | 0 | 2021 | OCT | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | OTHER | WIRE DOWN 3 SS/OF CGC# 100000037108 | 20211025 | 116 | 1516833 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 56511 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136851 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 10190 | 20211025 | 419 | 1516886 | 687 | Distribution Circuit | Vegetation | Tree - fell into line | 726 | 259365 | Clear-32-90 F | Crossarm, Wood | Broken, wire on object | 21-0136865 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 2093 | 20211214 | 523 | 1569737 | 635 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 46990 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0157884 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 56337 | 20211214 | 540 | 1569722 | 717 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 4199 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158125 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | OTHER | 322485738261 | 20211226 | 453 | 1582365 | 493 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 20809 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0160737 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 10519 | 20211227 | 2141 | 1586360 | 981 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 29187 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0161276 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | FUSE | 10247 | 20211227 | 1048 | 1585627 | 259 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 14245 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161101 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 26389 | 20211227 | 720 | 1584778 | 633 | Distribution Circuit | Vegetation | Tree - fell into line | 464 | 189292 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0161015 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | OTHER | 10385 | 20211227 | 1454 | 1585940 | 113 | Distribution Circuit | Vegetation | Tree - branch fell on line | 212 | 23956 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161145 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 43781 | 20230105 | 151 | 1920312 | 653 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1959 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0006974 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2102 | 254452102 | FUSE | 10317 | 20230105 | 653 | 1920796 | 787 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 21458 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0007187 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2103 | 254432103 | FUSE | 10217 | 20230107 | 1013 | 1926319 | 296 | Distribution Circuit | Equipment Failure/Involved | Overhead | 96 | 12936 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0008760 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER | 13430 | 20230109 | 540 | 1935901 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 77400 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0010835 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 10788 | 20230109 | 1030 | 1937640 | 266 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 20482 | Clear-32-90F | Conductor, Overhead | On Ground | 23-0011139 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | RECLOSER | 10040 | 20230110 | 437 | 1942284 | 844 | Distribution Circuit | Equipment Failure/Involved | Overhead | 425 | 209316 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0011883 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 254432104 | RECLOSER | 10110 | 20230110 | 616 | 1942993 | 3448 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1068 | 108166 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 23-0011949 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | RECLOSER | 65908 | 20230110 | 444 | 1942407 | 887 | Distribution Circuit | Vegetation | Tree - fell into line | 673 | 219896 | Overcast-Fog-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0011897 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER | 8130 | 20230110 | 447 | 1942567 | 2198 | Distribution Circuit | Vegetation | Tree - fell into line | 431 | 297449 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0011902 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE | 6821 | 20230110 | 446 | 1944475 | 835 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 35905 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0011898 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 77384 | 20230110 | 558 | 1944321 | 651 | Distribution Circuit | Vegetation | Tree - fell into line | 468 | 168550 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0011937 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S2251 | 20230116 | 1159 | 1957937 | 321 | Distribution Circuit | Vegetation | Tree - fell into line | 362 | 81552 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0017281 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER | 693441 | 20230116 | 906 | 1957423 | 630 | Distribution Circuit | Vegetation | Tree - fell into line | 491 | 200052 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0017056 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | RECLOSER | 10050 | 20230219 | 300 | 1988470 | 566 | Distribution Circuit | 3rd Party | Gun Shot | 2323 | 807587 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0030517 | OH | Sus | 45679421 | 2023 | FEB | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | OCB | 1701/2 | 20230221 | 1557 | 1992869 | 346 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1921 | 539322 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0031430 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 10373 | 20230224 | 1520 | 2005969 | 304 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 6080 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0034447 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2481 | 20230227 | 802 | 2011317 | 717 | Distribution Circuit | Equipment Failure/Involved | Overhead | 54 | 38718 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0036222 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 19515 | 20230228 | 712 | 2014844 | 410 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 15580 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0037206 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | Yes
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 10753 | 20230309 | 54 | 2027145 | 585 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 19890 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0041906 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | Yes
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 10498 | 20230321 | 1045 | 2054004 | 459 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 19278 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0049375 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER | 9280 | 20230909 | 1749 | 2213994 | 35 | Distribution Circuit | Company Initiated | Coordination failure | 847 | 29645 | Partly Cloudy-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0114492 | OH | Sus | 0 | 2023 | SEP | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3283 | 20130408 | 648 | 768993 | 602 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 3817 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022464 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 3975 | 20130408 | 112 | 768222 | 918 | Distribution Circuit | Vegetation | Tree - branch fell on line | 68 | 41827 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022150 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 2525 | 20130408 | 948 | 769568 | 528 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 651 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022485 | OH | Sus | 0 | 2013 | APR | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1260 | 20130408 | 1138 | 769912 | 527 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 14670 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022531 | OH | Sus | 0 | 2013 | APR | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 1273 | 20130408 | 1158 | 770205 | 752 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 752 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022575 | OH | Sus | 0 | 2013 | APR | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8547 | 20130408 | 607 | 769799 | 578 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1156 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022453 | OH | Sus | 0 | 2013 | APR | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3163 | 20130408 | 1645 | 770959 | 1181 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 44878 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022757 | OH | Sus | 0 | 2013 | APR | Yes | Three Phase Fault | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 1677 | 20130408 | 550 | 768874 | 425 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 6375 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022231 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 8769 | 20130408 | 859 | 769414 | 646 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3876 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022646 | OH | Sus | 0 | 2013 | APR | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | FUSE | 1997 | 20130408 | 834 | 769769 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4347 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022562 | OH | Sus | 0 | 2013 | APR | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 2500 | 20130408 | 318 | 768751 | 574 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 66584 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022207 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1709 | 20131121 | 1626 | 908219 | 1574 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6296 | Strong winds-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 13-0078055 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | LUCERNE-1103 | 43351103 | OCB | OCB | 20131121 | 1904 | 908530 | 2720 | Distribution Circuit | Vegetation | Tree - fell into line | 2885 | 1301516 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on object | 13-0078065 | OH | Sus | 0 | 2013 | NOV | Yes | Three Phase Fault | Yes
HUMBOLDT | Tier 2 | LUCERNE-1103 | 43351103 | FUSE | 4873 | 20131121 | 2114 | 910446 | 2379 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 92781 | Strong winds-32 - 90 F | Conductor, Underground | Broken, wire on ground | 13-0078266 | OH | Sus | 0 | 2013 | NOV | Yes | None | Yes
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER | 1904 | 20131121 | 1921 | 908604 | 1703 | Distribution Circuit | Vegetation | Tree - branch fell on line | 347 | 590941 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0078100 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER | 64118 | 20131121 | 2006 | 908967 | 2659 | Distribution Circuit | Vegetation | Tree - branch fell on line | 135 | 358965 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0078220 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE | 2335 | 20131121 | 2129 | 911058 | 2881 | Distribution Circuit | Equipment Failure/Involved | Other | 27 | 77787 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0078985 | OH | Sus | 0 | 2013 | NOV | Yes | None | Yes
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 8301 | 20131121 | 1907 | 908325 | 686 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 18585 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0078139 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
HUMBOLDT | Tier 2 | HOPLAND-1101 | 42251101 | FUSE | 9395 | 20131122 | 133 | 910379 | 1013 | Distribution Circuit | Equipment Failure/Involved | Other | 9 | 9117 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078282 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 4086 | 20131122 | 919 | 911595 | 388 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 19853 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078480 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | FUSE | 4139 | 20131122 | 1545 | 912607 | 1525 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 28975 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0078968 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | LUCERNE-1103 | 43351103 | FUSE | 7205 | 20131122 | 9 | 913272 | 3821 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 106492 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078827 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | LUCERNE-1106 | 43351106 | FUSE | 8955 | 20131122 | 1820 | 912867 | 1773 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5319 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0079011 | OH | Sus | 0 | 2013 | NOV | Yes | None | Yes
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1102 | 42281102 | RECLOSER | 95878 | 20131122 | 446 | 910836 | 794 | Distribution Circuit | Equipment Failure/Involved | Other | 140 | 111160 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078486 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | REDBUD-1101 | 43191101 | RECLOSER | 400 | 20131122 | 1204 | 912235 | 1659 | Distribution Circuit | Vegetation | Tree - fell into line | 673 | 560037 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078777 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE | 6663 | 20131122 | 2354 | 913310 | 2461 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 22058 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0078913 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 91810 | 20131122 | 1357 | 912370 | 811 | Distribution Circuit | Vegetation | Tree - branch fell on line | 860 | 576690 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078846 | OH | Sus | 0 | 2013 | NOV | Yes | Open Circuit | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3173 | 20141203 | 2138 | 1123974 | 962 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1924 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073664 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4577 | 20141211 | 1841 | 1135402 | 919 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 18052 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075914 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 9497 | 20141211 | 1841 | 1136409 | 1229 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 43015 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075943 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER | 69032 | 20141211 | 58 | 1128814 | 892 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 101712 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074826 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5065 | 20141211 | 312 | 1128977 | 1700 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 91800 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074868 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3283 | 20141211 | 520 | 1131093 | 1045 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 7315 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075069 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5009 | 20141211 | 850 | 1131843 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 7840 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0075198 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 7339 | 20141211 | 756 | 1131143 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 5550 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075265 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3287 | 20141211 | 1439 | 1132161 | 731 | Distribution Circuit | Vegetation | Tree - branch fell on line | 62 | 16937 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075648 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3151 | 20141211 | 1651 | 1135010 | 130 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 1950 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075694 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5651 | 20141211 | 1448 | 1135353 | 1797 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 14376 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075750 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5187 | 20141211 | 1452 | 1134484 | 626 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5634 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075762 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5173 | 20141211 | 1452 | 1134455 | 935 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 12155 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075768 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 2223 | 20141211 | 747 | 1131092 | 953 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3812 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075843 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | EEL RIVER 1101 | 192381101 | RECLOSER | 4814 | 20141211 | 322 | 1128944 | 3546 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 276588 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0074833 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1260 | 20141211 | 58 | 1128908 | 852 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 80652 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074837 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | OTHER |  | 20141211 | 420 | 1129440 | 1016 | Distribution Circuit | Vegetation | Tree - branch fell on line | 62 | 60768 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075128 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 3975 | 20141211 | 720 | 1131282 | 378 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 25471 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075457 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 5533 | 20141211 | 548 | 1129593 | 837 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 17718 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075495 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 1905 | 20141211 | 258 | 1128914 | 1687 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 38801 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075929 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 3273 | 20141211 | 1023 | 1132834 | 1981 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 13867 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075986 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 5233 | 20141211 | 231 | 1131630 | 2374 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 78174 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076256 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | RECLOSER | 4622 | 20141211 | 428 | 1129538 | 842 | Distribution Circuit | Vegetation | Tree - fell into line | 371 | 312382 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075001 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 5985 | 20141211 | 2143 | 1136223 | 786 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11004 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075970 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 1497 | 20141211 | 440 | 1129126 | 2055 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 28770 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075975 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 979 | 20141211 | 1917 | 1135604 | 1324 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 9326 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076152 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3341 | 20141211 | 309 | 1129115 | 931 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 31288 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074900 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER | 31304 | 20141211 | 426 | 1129098 | 497 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 59908 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075156 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3941 | 20141211 | 653 | 1130303 | 1072 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 37692 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075253 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3099 | 20141211 | 425 | 1129072 | 670 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 38639 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075271 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 8573 | 20141211 | 514 | 1129329 | 841 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 9251 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075281 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 94575 | 20141211 | 653 | 1133065 | 868 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 10416 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075351 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | OTHER |  | 20141211 | 653 | 1133090 | 643 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 643 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075356 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | OTHER |  | 20141211 | 653 | 1133407 | 475 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 5225 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075418 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3979 | 20141211 | 656 | 1130203 | 1111 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 14443 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075899 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 8505 | 20141211 | 2041 | 1135977 | 797 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 10361 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076054 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3969 | 20141211 | 1811 | 1135291 | 1162 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 66234 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076237 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 411 | 20141211 | 433 | 1129100 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 7168 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075020 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 3295 | 20141211 | 637 | 1129998 | 752 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 9024 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075311 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER | 1690 | 20141211 | 510 | 1129409 | 2410 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 52229 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074908 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 6054 | 20141211 | 441 | 1129160 | 1389 | Distribution Circuit | Vegetation | Tree - fell into line | 593 | 704376 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074878 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 1587 | 20141211 | 535 | 1132583 | 1360 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1360 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075272 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 56048 | 20141211 | 305 | 1128850 | 2538 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 298569 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074827 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 8652 | 20141211 | 152 | 1129431 | 2184 | Distribution Circuit | Vegetation | Tree - fell into line | 244 | 432315 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074918 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER |  | 20141211 | 152 | 1135483 | 2184 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4368 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075778 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2581 | 20141211 | 1247 | 1133677 | 1511 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 4533 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075925 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 561 | 20141211 | 357 | 1128996 | 614 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 65084 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074955 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 6693 | 20141211 | 346 | 1128973 | 556 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1112 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075092 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 561 | 20141211 | 1420 | 1134356 | 22 | Distribution Circuit | Vegetation | Tree - branch fell on line | 106 | 2332 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075570 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 8167 | 20141211 | 743 | 1131034 | 475 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 5225 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075244 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 7325 | 20141211 | 1028 | 1132876 | 1792 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3584 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075644 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 4205 | 20141211 | 402 | 1129049 | 458 | Distribution Circuit | Vegetation | Tree - fell into line | 286 | 130988 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074888 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 4213 | 20141211 | 702 | 1130255 | 458 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 10076 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075320 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 2749 | 20141211 | 708 | 1130322 | 398 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 8756 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075191 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER | 4230 | 20141211 | 217 | 1128884 | 3701 | Distribution Circuit | Equipment Failure/Involved | Other | 25 | 86504 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0074812 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | UKIAH-1114 | 42771114 | FUSE | 3371 | 20141211 | 1430 | 1134793 | 1250 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 7500 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075651 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | SWITCH | 3053 | 20141212 | 1000 | 1137967 | 1595 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 17545 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076378 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3911 | 20141212 | 1045 | 1138029 | 366 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 1830 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076302 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1815 | 20141212 | 612 | 1137161 | 986 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 28594 | Fog-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0076297 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1799 | 20141212 | 816 | 1138674 | 981 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4905 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076558 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 37054 | 20141212 | 2150 | 1139284 | 29 | Distribution Circuit | Equipment Failure/Involved | Other | 102 | 2958 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074827 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER |  | 20141212 | 2123 | 1139299 | 118 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 118 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074827 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 68415 | 20141230 | 846 | 1150568 | 339 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 339 | Fog-32 - 90 F | Cutout, fuse holder | Broken, wire on ground | 14-0078927 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4583 | 20150206 | 335 | 1173712 | 850 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11900 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009900 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 1265 | 20150206 | 830 | 1173680 | 3243 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3243 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009896 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3281 | 20150206 | 1353 | 1176004 | 1412 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 30158 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010339 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 2431 | 20150206 | 937 | 1176443 | 1941 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 67935 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010416 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5065 | 20150206 | 937 | 1176460 | 1698 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 91692 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010417 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3033 | 20150206 | 952 | 1173969 | 1640 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 23272 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010434 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3151 | 20150206 | 937 | 1180028 | 2260 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 33900 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010956 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 6543 | 20150206 | 2050 | 1180637 | 1000 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3000 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011064 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3967 | 20150206 | 1719 | 1178233 | 2506 | Distribution Circuit | Equipment Failure/Involved | Other | 65 | 162890 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011350 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 87163 | 20150206 | 1141 | 1174550 | 1666 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 36652 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010380 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 5533 | 20150206 | 924 | 1173906 | 1896 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 54984 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010536 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1298 | 20150206 | 1921 | 1179285 | 1539 | Distribution Circuit | Vegetation | Tree - fell into line | 501 | 642067 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010596 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 3921 | 20150206 | 1921 | 1179792 | 1614 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 111366 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010883 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 5233 | 20150206 | 1921 | 1180961 | 2464 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 101024 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011147 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 94127 | 20150206 | 1921 | 1181087 | 2430 | Distribution Circuit | Equipment Failure/Involved | Other | 5 | 12150 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011181 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 1319 | 20150206 | 1921 | 1181210 | 5571 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 16713 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011215 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 3919 | 20150206 | 1921 | 1181383 | 2859 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 71475 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011272 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER | 31304 | 20150206 | 604 | 1173268 | 2403 | Distribution Circuit | Vegetation | Tree - branch fell on line | 131 | 171322 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009853 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER | 816 | 20150206 | 935 | 1173905 | 279 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 15419 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010016 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 1603 | 20150206 | 1656 | 1176920 | 1289 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 79918 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010526 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 6081 | 20150206 | 1241 | 1177383 | 1633 | Distribution Circuit | Vegetation | Tree - fell into line | 469 | 758707 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010612 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3969 | 20150206 | 1241 | 1181873 | 2025 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 115425 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011375 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1987 | 20150206 | 1838 | 1177568 | 2449 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 17143 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010605 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | OCB | OCB | 20150206 | 1006 | 1174140 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 370 | 158397 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010206 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1770 | 20150206 | 2240 | 1179355 | 760 | Distribution Circuit | Vegetation | Tree - fell into line | 389 | 295877 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010792 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1750 | 20150206 | 2252 | 1179359 | 952 | Distribution Circuit | Vegetation | Tree - fell into line | 117 | 111384 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0010794 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1717 | 20150206 | 2240 | 1181233 | 2809 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 53371 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011224 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 8652 | 20150206 | 1211 | 1174721 | 4996 | Distribution Circuit | Equipment Failure/Involved | Other | 181 | 0 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010098 | OH | Sus | 0 | 2015 | FEB | Yes |  | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 3759 | 20150206 | 2302 | 1180532 | 3858 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 46730 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011045 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2505 | 20150206 | 127 | 1181957 | 5359 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 182206 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011404 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 3433 | 20150206 | 522 | 1173199 | 3233 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 85190 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009837 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER | 445166 | 20150206 | 806 | 1173546 | 1644 | Distribution Circuit | Vegetation | Tree - fell into line | 261 | 425914 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0010247 | OH | Sus | 0 | 2015 | FEB | Yes | Three Phase Fault | Yes
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 561 | 20150206 | 654 | 1173411 | 1593 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 128380 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010399 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 4451 | 20150206 | 837 | 1181135 | 4703 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 27681 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011195 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 4437 | 20150206 | 3 | 1173196 | 2367 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 54441 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009808 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 4429 | 20150206 | 613 | 1173310 | 2204 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 37468 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010933 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 6487 | 20150206 | 702 | 1173418 | 3391 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 9437 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011027 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | HARTLEY-1101 | 43211101 | FUSE | 58095 | 20150206 | 2206 | 1179022 | 4129 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12792 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010829 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 2577 | 20150206 | 2327 | 1179466 | 1277 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 58742 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010876 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 5259 | 20150206 | 2303 | 1179382 | 1437 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 27303 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011282 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | LUCERNE-1106 | 43351106 | RECLOSER | 38632 | 20150206 | 808 | 1173540 | 312 | Distribution Circuit | Vegetation | Tree - fell into line | 257 | 24814 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009903 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | OTHER |  | 20150206 | 803 | 1173629 | 547 | Distribution Circuit | Vegetation | Tree - fell into line | 216 | 112716 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009878 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 2653 | 20150206 | 648 | 1173398 | 1861 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 14888 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010193 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 8989 | 20150206 | 1900 | 1178783 | 2580 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 15480 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010860 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 1363 | 20150206 | 1819 | 1178748 | 1536 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 87552 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011364 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER | 4230 | 20150206 | 938 | 1173932 | 4799 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 119975 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009940 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 37506 | 20150206 | 623 | 1173389 | 436 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 34148 | Strong winds-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 15-0009869 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 3811 | 20150206 | 910 | 1173752 | 560 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 10640 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010215 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 2813 | 20150206 | 2332 | 1180166 | 868 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 51212 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010995 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | FUSE | 8467 | 20150206 | 511 | 1173191 | 596 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 17284 | Strong winds-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 15-0009819 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 3769 | 20150206 | 2217 | 1179196 | 1033 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 114663 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010821 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 2981 | 20150206 | 1540 | 1176256 | 4235 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8470 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010597 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 6073 | 20150207 | 1629 | 1181535 | 2026 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12156 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011311 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 4987 | 20150207 | 731 | 1180319 | 721 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 7210 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011231 | OH | Sus | 0 | 2015 | FEB | Yes | Multi-Fault | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3173 | 20150207 | 1451 | 1181372 | 1629 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 3258 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011263 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 5985 | 20150207 | 1030 | 1180918 | 1530 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 21420 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011491 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 1767 | 20150207 | 1126 | 1181031 | 1724 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 13792 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011512 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | OTHER |  | 20150207 | 123 | 1180149 | 874 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 149914 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011041 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 8279 | 20150207 | 721 | 1180710 | 3224 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 58032 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011153 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | SWITCH | 1869 | 20150207 | 1512 | 1181387 | 3375 | Distribution Circuit | Equipment Failure/Involved | Other | 16 | 54000 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010794 | OH | Sus | 0 | 2015 | FEB | Yes | Open Circuit | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1771 | 20150207 | 1539 | 1181508 | 1873 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 14984 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011336 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 8207 | 20150207 | 1501 | 1181648 | 3089 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 27801 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011333 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 431 | 20150207 | 907 | 1180682 | 4798 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 43182 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011167 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | OCB | OCB | 20150207 | 200 | 1180393 | 1122 | Distribution Circuit | Vegetation | Tree - fell into line | 739 | 679197 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011102 | OH | Sus | 0 | 2015 | FEB | Yes | Three Phase Fault | Yes
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | OTHER |  | 20150207 | 1838 | 1181885 | 2809 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 7691 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011390 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | RECLOSER | 37222 | 20150207 | 901 | 1187254 | 4900 | Distribution Circuit | Vegetation | Tree - fell into line | 146 | 715400 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012327 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | RECLOSER | 1308 | 20150207 | 158 | 1179796 | 3591 | Distribution Circuit | Vegetation | Tree - fell into line | 292 | 444437 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011100 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | FUSE | 3909 | 20150207 | 221 | 1180697 | 3764 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 11292 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011075 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | UKIAH-1114 | 42771114 | FUSE | 1711 | 20150207 | 2056 | 1180643 | 2399 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 9596 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011699 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | WILLOW CREEK-1101 | 192171101 | FUSE | 3021 | 20150207 | 343 | 1179969 | 662 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 25818 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010931 | OH | Sus | 0 | 2015 | FEB | Yes | Three Phase Fault | Yes
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 3079 | 20150207 | 1356 | 1181284 | 2764 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 96740 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011377 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 8483 | 20150208 | 2042 | 1185254 | 2568 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 43059 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012201 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | FUSE | 6785 | 20150208 | 1452 | 1182767 | 91 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 637 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011615 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 7339 | 20150208 | 1552 | 1183171 | 155 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 6975 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011715 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER | 79628 | 20150208 | 1927 | 1183900 | 2094 | Distribution Circuit | Vegetation | Tree - fell into line | 365 | 764310 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011805 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 5061 | 20150208 | 811 | 1182137 | 484 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 9196 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011533 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3069 | 20150208 | 809 | 1182153 | 294 | Distribution Circuit | Vegetation | Tree - fell into line | 172 | 50568 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011466 | OH | Sus | 0 | 2015 | FEB | Yes | Three Phase Fault | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3969 | 20150208 | 807 | 1182144 | 498 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 19966 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011508 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1607 | 20150208 | 739 | 1182795 | 646 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2584 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011649 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER | 1602 | 20150208 | 839 | 1182183 | 3295 | Distribution Circuit | Equipment Failure/Involved | Other | 87 | 259017 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011463 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT SEWARD-1122 | 192321122 | FUSE | 1651 | 20150208 | 1433 | 1185122 | 2867 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 17202 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012266 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2571 | 20150208 | 912 | 1182208 | 1938 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 19380 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011579 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | SWITCH | 6084 | 20150208 | 2356 | 1185303 | 1254 | Distribution Circuit | Vegetation | Tree - branch fell on line | 63 | 0 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011878 | OH | Sus | 0 | 2015 | FEB | Yes |  | Yes
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER | 445166 | 20150208 | 1954 | 1183953 | 1256 | Distribution Circuit | Vegetation | Tree - fell into line | 261 | 322458 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011784 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | HIGHLANDS-1103 | 43361103 | FUSE | 61699 | 20150208 | 2151 | 1185637 | 3929 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 43219 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0012272 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3247 | 20150208 | 910 | 1181995 | 3248 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 3248 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011469 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | OTHER |  | 20150208 | 2124 | 1184578 | 1867 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1867 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011973 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | RECLOSER | 402 | 20150208 | 2223 | 1185631 | 3117 | Distribution Circuit | Equipment Failure/Involved | Other | 684 | 688758 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011985 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 2577 | 20150208 | 706 | 1185678 | 2089 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 87734 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011997 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 3789 | 20150208 | 2153 | 1184870 | 2644 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 15864 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012582 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | FUSE | 3705 | 20150208 | 2129 | 1185839 | 1744 | Distribution Circuit | Vegetation | Tree - branch fell on line | 52 | 90688 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012139 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 2637 | 20150208 | 1831 | 1184062 | 1269 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 39339 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011819 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 2813 | 20150208 | 2153 | 1185281 | 1330 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 120152 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011870 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 8301 | 20150208 | 8 | 1184756 | 4159 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 324438 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011879 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2117 | 20150208 | 2132 | 1184681 | 536 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 22512 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011957 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 8049 | 20150208 | 2216 | 1187271 | 1709 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 8545 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012336 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | FUSE | 1429 | 20150208 | 2144 | 1185613 | 716 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 57082 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011981 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 2540 | 20150406 | 2232 | 1214427 | 790 | Distribution Circuit | Vegetation | Tree - fell into line | 311 | 180026 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0024650 | OH | Sus | 0 | 2015 | APR | Yes | Multi-Fault | Yes
HUMBOLDT | Tier 2 | UKIAH-1115 | 42771115 | FUSE | 3405 | 20150608 | 1123 | 1245614 | 196 | Distribution Circuit | 3rd Party | Vehicle | 128 | 17408 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0039293 | OH | Sus | 42401929 | 2015 | JUN | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | COVELO-1101 | 43061101 | FUSE | 2719 | 20150718 | 1859 | 1270312 | 411 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2466 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0048410 | OH | Sus | 0 | 2015 | JUL | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | JUMPER | 2 SPANS SS 4487 | 20150718 | 1700 | 1270334 | 894 | Distribution Circuit | Vegetation | Tree - fell into line | 250 | 51806 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0048394 | OH | Sus | 0 | 2015 | JUL | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | KONOCTI-1102 | 43311102 | FUSE | 4103 | 20150718 | 139 | 1269867 | 531 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 23364 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0048315 | OH | Sus | 31170009 | 2015 | JUL | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE | 3737 | 20150718 | 634 | 1269890 | 630 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3150 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0048331 | OH | Sus | 31170011 | 2015 | JUL | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4597 | 20151213 | 542 | 1359974 | 1085 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 9765 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084681 | OH | Sus | 0 | 2015 | DEC | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER | 1052 | 20151213 | 716 | 1360154 | 492 | Distribution Circuit | Vegetation | Tree - branch fell on line | 582 | 131494 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084657 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER | 79628 | 20151213 | 1312 | 1362196 | 254 | Distribution Circuit | Vegetation | Tree - fell into line | 366 | 76479 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084969 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3967 | 20151213 | 716 | 1362680 | 1036 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 67340 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084977 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | BRIDGEVILLE-1102 | 192461102 | FUSE | 3455 | 20151213 | 753 | 1360262 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 32376 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084833 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER 1101 | 192381101 | FUSE | 1909 | 20151213 | 514 | 1359857 | 536 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 12864 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084576 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1300 | 20151213 | 1017 | 1361284 | 638 | Distribution Circuit | Vegetation | Tree - fell into line | 424 | 74987 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084853 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 3945 | 20151213 | 1353 | 1362477 | 1467 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 8652 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0085022 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | JUMPER | OJ 5 SPANS LOAD SIDE FUCO 5187 | 20151213 | 1332 | 1362297 | 793 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 6533 | Clear-32-90 F | Conductor, Overhead | On Ground | 15-0085026 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 3137 | 20151213 | 1331 | 1362244 | 776 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 119504 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0085196 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 3975 | 20151213 | 1322 | 1362218 | 763 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 52647 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0085197 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 1905 | 20151213 | 1021 | 1361267 | 1146 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 29796 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0085210 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3115 | 20151213 | 435 | 1359783 | 306 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2448 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084488 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | SWITCH | 91017 | 20151213 | 600 | 1359981 | 413 | Distribution Circuit | Vegetation | Tree - branch fell on line | 176 | 72688 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084591 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 7365 | 20151213 | 713 | 1359994 | 467 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4203 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084543 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER | 816 | 20151213 | 1304 | 1362179 | 416 | Distribution Circuit | Vegetation | Tree - branch fell on line | 439 | 172554 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084934 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 3109 | 20151213 | 603 | 1361545 | 858 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 64835 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084740 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | FUSE | 3931 | 20151213 | 917 | 1362083 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 7189 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084910 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | OCB | OCB | 20151213 | 523 | 1359885 | 2202 | Distribution Circuit | Equipment Failure/Involved | Overhead | 682 | 361679 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084489 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3769 | 20151213 | 1001 | 1361112 | 746 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 6246 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084912 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | SWITCH | 1687 | 20151213 | 523 | 1363666 | 2279 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 22790 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0085352 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1514 | 20151213 | 640 | 1360038 | 579 | Distribution Circuit | Vegetation | Tree - fell into line | 220 | 123430 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084515 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1770 | 20151213 | 532 | 1362412 | 1348 | Distribution Circuit | Vegetation | Tree - fell into line | 332 | 229513 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084908 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 56048 | 20151213 | 450 | 1359909 | 676 | Distribution Circuit | Vegetation | Tree - fell into line | 332 | 160358 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084503 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2505 | 20151213 | 450 | 1362029 | 970 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 33950 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084816 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 8223 | 20151213 | 1904 | 1362915 | 473 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1892 | Partly Cloudy-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 15-0085050 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HARRIS-1109 | 192431109 | FUSE | 5577 | 20151213 | 734 | 1360205 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4728 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084616 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 6795 | 20151213 | 1617 | 1362253 | 453 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2265 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0085003 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 4613 | 20151213 | 1035 | 1361376 | 265 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 4505 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084774 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 7527 | 20151213 | 1039 | 1361403 | 387 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 774 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084857 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | JUMPER | WIRE DOWN | 20151213 | 714 | 1361225 | 293 | Distribution Circuit | Equipment Failure/Involved | Overhead | 670 | 168198 | Overcast-Heavy Rain-32-90 F | PGs, Kearneys | Broken, wire on ground | 15-0084696 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | FUSE | 7017 | 20151213 | 1759 | 1362856 | 361 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 5415 | Clear-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0085044 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2415 | 20151213 | 719 | 1360144 | 541 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1082 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084887 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER | 3090 | 20151213 | 514 | 1359863 | 847 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 38962 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084479 | OH | Sus | 0 | 2015 | DEC | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | RECLOSER | 37484 | 20151224 | 1135 | 1370806 | 3104 | Distribution Circuit | Environmental/External | Ice or snow | 38 | 42349 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087101 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | JUMPER | WIRE DOWN 2 SP S/SIDE OF FUSE 4087 | 20151224 | 445 | 1371067 | 3628 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 112690 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 15-0087118 | OH | Sus | 0 | 2015 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 5233 | 20151224 | 839 | 1370809 | 313 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 11369 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087079 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 1381 | 20151224 | 1850 | 1371354 | 229 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 458 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087176 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3909 | 20151224 | 1306 | 1371037 | 109 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 3270 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087120 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 1673 | 20151224 | 1619 | 1371732 | 4025 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 44275 | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 15-0087414 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 7287 | 20151224 | 950 | 1370858 | 684 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 684 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087119 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 4160 | 20151224 | 656 | 1370702 | 3497 | Distribution Circuit | Vegetation | Tree - fell into line | 379 | 1236891 | Overcast-Fog-32-90 F | Crossarm, Wood | Broken, wire on ground | 15-0087061 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 2094 | 20151224 | 1253 | 1370999 | 4432 | Distribution Circuit | Environmental/External | Ice or snow | 326 | 1281395 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 15-0087111 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | REDBUD-1101 | 43191101 | JUMPER | HOT WIRE DOWN 1/S/OF 8263 TWD 83975 | 20151224 | 1233 | 1370995 | 274 | Distribution Circuit | Vegetation | Tree - fell into line | 1593 | 146925 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087108 | OH | Sus | 0 | 2015 | DEC | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | REDBUD-1101 | 43191101 | RECLOSER | 91960 | 20151224 | 1211 | 1371041 | 541 | Distribution Circuit | Vegetation | Tree - fell into line | 533 | 125745 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087115 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 3053 | 20151224 | 1943 | 1371413 | 4001 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 106920 | Snow-Sleet or Ice-Rain-Hail-Combination-Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 15-0087223 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | RECLOSER | 4904 | 20151224 | 2202 | 1371438 | 1713 | Distribution Circuit | Vegetation | Tree - branch fell on line | 151 | 230322 | Snow-Sleet or Ice-Rain-Hail-Combination-Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 15-0087227 | OH | Sus | 0 | 2015 | DEC | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1102 | 192171102 | OCB | OCB | 20151224 | 2309 | s1177329 | 3101 | Distribution Circuit | Vegetation | Tree - fell into line | 146 | 92054 | Snow-Sleet or Ice-Rain-Combination-Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 15-0087248 | OH | Sus | 0 | 2015 | DEC | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER | 3090 | 20151224 | 2223 | 1371460 | 3301 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 151846 | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 15-0087230 | OH | Sus | 0 | 2015 | DEC | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 7881 | 20151224 | 2130 | 1371813 | 2630 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 31560 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 15-0087306 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | MENDOCINO-1101 | 42951101 | FUSE | 3443 | 20160217 | 841 | 1404619 | 155 | Distribution Circuit | Animal | Bird found | 134 | 20770 | Strong Winds-Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0012987 | OH | Sus | 42632252 | 2016 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3045 | 20160305 | 1748 | 1417769 | 852 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 20956 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017769 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | JUMPER | 3 PHASES WIRE DOWN AT SW 4101 | 20160305 | 1811 | 1418018 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 23408 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017789 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | CALPELLA-1101 | 43411101 | FUSE | 7493 | 20160305 | 1708 | 1417544 | 640 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6400 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0017610 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER 1101 | 192381101 | FUSE | 1907 | 20160305 | 1559 | 1417041 | 317 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 4353 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017648 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 3975 | 20160305 | 1636 | 1417367 | 418 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 28842 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017657 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | SWITCH | 427 | 20160305 | 1831 | 1418141 | 864 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 40608 | Partly Cloudy-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017977 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 2857 | 20160305 | 1550 | 1417010 | 250 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 7500 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017626 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3969 | 20160305 | 1752 | 1417862 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 19175 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017717 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | OTHER | WIRE DOWN | 20160305 | 1811 | 1417980 | 581 | Distribution Circuit | Vegetation | Tree - branch fell on line | 131 | 56128 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017818 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER | 3902 | 20160305 | 1942 | 1418672 | 1200 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1934 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017757 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 47739 | 20160305 | 1612 | 1417127 | 467 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 934 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017678 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | Yes
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | OTHER | 7449 | 20160305 | 1625 | 1417218 | 487 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2642 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017702 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER | WIRE DOWN | 20160305 | 638 | 1416467 | 1140 | Distribution Circuit | Vegetation | Tree - fell into line | 439 | 187153 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017426 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | JUMPER | WIRE DOWN 4 SP LD SIDE OF 1510 | 20160305 | 1528 | 1416920 | 690 | Distribution Circuit | Vegetation | Tree - fell into line | 372 | 177661 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017558 | OH | Sus | 0 | 2016 | MAR | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER | 4230 | 20160305 | 1410 | 1416493 | 922 | Distribution Circuit | Vegetation | Tree - fell into line | 327 | 286241 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0017549 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | FUSE | 1997 | 20160305 | 1410 | 1421227 | 1577 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 11039 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018474 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1903 | 20161014 | 1113 | 1559350 | 400 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2800 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072159 | OH | Sus | 0 | 2016 | OCT | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 1637 | 20161014 | 2312 | 1560488 | 868 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 15932 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072393 | OH | Sus | 42815227 | 2016 | OCT | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 97300 | 20161014 | 335 | 1558105 | 751 | Distribution Circuit | Vegetation | Tree - fell into line | 442 | 35593 | Clear-32-90 F | Conductor, Overhead | On Ground | 16-0071846 | OH | Sus | 0 | 2016 | OCT | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2571 | 20161014 | 828 | 1558710 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6220 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072089 | OH | Sus | 0 | 2016 | OCT | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3969 | 20170103 | 1959 | 1616676 | 460 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 27140 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 17-0003288 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 1659 | 20170103 | 1106 | 1615658 | 3194 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12776 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003620 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3775 | 20170103 | 719 | 1615363 | 1181 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 11810 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0002980 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 6635 | 20170103 | 629 | 1615340 | 9461 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 37844 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0002947 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3259 | 20170103 | 1423 | 1615837 | 8580 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 154440 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003117 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 3304 | 20170103 | 1722 | 1615913 | 8978 | Distribution Circuit | Vegetation | Tree - fell into line | 531 | 3365902 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0003166 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | SWITCH | 3231 | 20170103 | 1711 | 1618211 | 5822 | Distribution Circuit | Vegetation | Tree - fell into line | 172 | 948974 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0003545 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | HOOPA-1101 | 192401101 | JUMPER | WIRE DOWN @ 2ND HARD TAP BEYOND 3243 | 20170103 | 1854 | 1618495 | 4213 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 45209 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003662 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 4679 | 20170103 | 1627 | 1618621 | 4370 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 30590 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003722 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | OTHER | WIRE DOWN LD SIDE @ 3073 | 20170103 | 1627 | 1618624 | 4370 | Distribution Circuit | Vegetation | Tree - fell into line | 164 | 716680 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003723 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3239 | 20170103 | 1854 | 1619843 | 5634 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 233712 | Overcast-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 17-0004114 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 5209 | 20170103 | 1809 | 1619858 | 5265 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 101438 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004117 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3277 | 20170103 | 1254 | 1619903 | 8871 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 62097 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004142 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3369 | 20170103 | 1722 | 1632442 | 10021 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 190399 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0006364 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER | 532 | 20170103 | 2232 | 1617141 | 916 | Distribution Circuit | Vegetation | Tree - fell into line | 302 | 52372 | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0003334 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 2853 | 20170103 | 23 | 1615253 | 979 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 98096 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0002897 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | RECLOSER | 5002 | 20170103 | 1918 | 1616446 | 2353 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 108238 | Overcast-Fog-Strong Winds-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0003212 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1101 | 192171101 | JUMPER | OJ'S 1 S/OF 2905 | 20170103 | 1918 | 1618098 | 2353 | Distribution Circuit | Vegetation | Tree - fell into line | 424 | 997672 | Clear-Strong Winds-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0003212 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1101 | 192171101 | FUSE | 3059 | 20170103 | 1914 | 1618290 | 2790 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 181350 | Clear-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0003576 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 3009 | 20170103 | 1417 | 1618586 | 4463 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 17852 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0003705 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1101 | 192171101 | FUSE | 2985 | 20170103 | 1918 | 1618737 | 2786 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 153230 | Clear-Strong Winds-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0003760 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1102 | 192171102 | OCB | 1102/2 | 20170103 | 1957 | 1616369 | 1705 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 223355 | Overcast-Fog-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0003227 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER | 3090 | 20170103 | 1956 | 1616675 | 2126 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 99922 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003223 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 3119 | 20170103 | 2001 | 1618353 | 2686 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 75208 | Clear-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0003607 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | JUMPER | OJ 1 E/OF MTR 1008027868 | 20170103 | 1853 | 1618674 | 2924 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 55556 | Clear-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0003735 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 6775 | 20170103 | 1650 | 1618816 | 4136 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 62040 | Clear-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0003770 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 5113 | 20170108 | 921 | 1624138 | 4839 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5289 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005127 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | JUMPER | UN-NUMBERED FUSES | 20170108 | 1427 | 1627324 | 4293 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4293 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005452 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER | 79628 | 20170108 | 633 | 1622773 | 2228 | Distribution Circuit | Vegetation | Tree - fell into line | 328 | 751702 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004982 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3283 | 20170108 | 630 | 1623848 | 4666 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 32662 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005035 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3291 | 20170108 | 633 | 1624724 | 4502 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 81036 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005099 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5731 | 20170108 | 910 | 1626791 | 2093 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 102557 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005320 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5173 | 20170108 | 758 | 1629882 | 3616 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 47008 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005813 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | JUMPER | OPEN JUMPERS SOURCE SIDE OF METER 1009653056 | 20170108 | 633 | 1632081 | 4850 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 14550 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006277 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | RECLOSER | 37484 | 20170108 | 1006 | 1625400 | 3324 | Distribution Circuit | Vegetation | Tree - fell into line | 399 | 164480 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0005481 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1899 | 20170108 | 852 | 1623812 | 3054 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 33594 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006463 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 5931 | 20170108 | 1426 | 1627318 | 2877 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5754 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005393 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1260 | 20170108 | 1043 | 1625132 | 3060 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 278301 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005459 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 5781 | 20170108 | 804 | 1628114 | 4741 | Distribution Circuit | Equipment Failure/Involved | Overhead | 194 | 373423 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005521 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | JUMPER | OJ 1 SPAN LD SIDE OF 1701 - 2 | 20170108 | 1211 | 1631719 | 4683 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4683 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006223 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 6069 | 20170108 | 931 | 1624355 | 1895 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 75800 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005173 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 5681 | 20170108 | 835 | 1628402 | 2294 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 22940 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005554 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 5561 | 20170108 | 543 | 1622949 | 3482 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 141424 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004949 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 8575 | 20170108 | 752 | 1625350 | 740 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 17760 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005181 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 5661 | 20170108 | 904 | 1627222 | 2082 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 52050 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005378 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | SWITCH | 5989 | 20170108 | 752 | 1628133 | 2174 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 104352 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005525 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 503683 | 20170108 | 754 | 1623345 | 2376 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 21384 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005676 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3969 | 20170108 | 752 | 1629170 | 2963 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 174817 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005679 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 1513 | 20170108 | 752 | 1629027 | 3293 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 125134 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005731 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | JUMPER | OJ'S SS OF MTR # 1009672629 | 20170108 | 2029 | 1630364 | 2671 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2671 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005906 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 7253 | 20170108 | 2029 | 1630596 | 1505 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 18060 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005953 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3321 | 20170108 | 733 | 1630767 | 4977 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 19908 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006009 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 2275 | 20170108 | 959 | 1624699 | 1691 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 40584 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006089 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 5601 | 20170108 | 810 | 1633163 | 3311 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 16555 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004949 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 5579 | 20170108 | 850 | 1633166 | 3315 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 13260 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004949 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 5593 | 20170108 | 850 | 1633168 | 3400 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 23800 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004949 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 5589 | 20170108 | 850 | 1633172 | 3430 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10290 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004949 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 5583 | 20170108 | 850 | 1633178 | 4511 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 9022 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004949 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 1687 | 20170108 | 959 | 1624538 | 4660 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 27960 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007706 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 6545 | 20170108 | 833 | 1623560 | 4487 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 21980 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005184 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1607 | 20170108 | 1110 | 1627166 | 3565 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 14260 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005366 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1477 | 20170108 | 1038 | 1627181 | 3509 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10527 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005370 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | FUSE | 3965 | 20170108 | 924 | 1627686 | 4592 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4592 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005446 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 6054 | 20170108 | 905 | 1624053 | 4792 | Distribution Circuit | Vegetation | Tree - branch fell on line | 579 | 758109 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005153 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 6064 | 20170108 | 851 | 1623842 | 1497 | Distribution Circuit | Equipment Failure/Involved | Overhead | 66 | 98802 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005236 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 7359 | 20170108 | 905 | 1626914 | 4760 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 9520 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005334 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 1679 | 20170108 | 942 | 1630783 | 4427 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 203642 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006014 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 7215 | 20170108 | 905 | 1634644 | 4647 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 88293 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006845 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 1523 | 20170108 | 1247 | 1626410 | 4393 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 52716 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007672 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1514 | 20170108 | 716 | 1623071 | 3397 | Distribution Circuit | Vegetation | Tree - fell into line | 248 | 532194 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0004963 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1569 | 20170108 | 716 | 1627314 | 2116 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 12696 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005392 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2529 | 20170108 | 717 | 1626362 | 2238 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 11190 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005277 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2523 | 20170108 | 716 | 1627478 | 6253 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 68783 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005420 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 3791 | 20170108 | 746 | 1628465 | 4899 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4899 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005565 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1965 | 20170108 | 746 | 1628478 | 1900 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 74100 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005572 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | JUMPER | OJ'S ON HARD TAP FEEDING TRANSF#114418827490 | 20170108 | 717 | s1246410 | 4743 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 18309 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006824 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | OTHER | 481 | 20170108 | 1022 | 1625185 | 1708 | Distribution Circuit | Vegetation | Tree - fell into line | 408 | 657236 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005226 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 9407 | 20170108 | 1037 | 1624980 | 3171 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 19026 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005299 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3319 | 20170108 | 1008 | 1624651 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4125 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005089 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3153 | 20170108 | 1106 | 1625243 | 317 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2536 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0005164 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER | 532 | 20170108 | 754 | 1623559 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 302 | 32722 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005055 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | OTHER | WIRE DOWN 2 SPANS FROM 2311 | 20170108 | 1034 | 1625492 | 1934 | Distribution Circuit | Vegetation | Tree - fell into line | 762 | 169590 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005356 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | Yes
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | OTHER | WIRE DOWN | 20170108 | 1708 | 1628373 | 1104 | Distribution Circuit | Vegetation | Tree - fell into line | 304 | 328917 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005602 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 6467 | 20170108 | 922 | 1634625 | 4883 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 24415 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006842 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 2463 | 20170108 | 930 | 1624230 | 672 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 47712 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005260 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 7093 | 20170108 | 1223 | 1626168 | 1627 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 42302 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005310 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE | 7071 | 20170108 | 923 | 1624170 | 2081 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 45782 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005156 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | SWITCH | 625 | 20170108 | 1645 | 1627779 | 2655 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 76995 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005547 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | FUSE | 2919 | 20170108 | 1011 | 1625129 | 1863 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 44712 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006107 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | RECLOSER | 83354 | 20170108 | 452 | 1622539 | 844 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 21100 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005038 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 7871 | 20170108 | 524 | 1622556 | 2018 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 10090 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005092 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | JUMPER | WIRE DOWN 2 SP LD SIDE OF 97045 | 20170108 | 920 | 1624135 | 2981 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 8943 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005416 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 6415 | 20170108 | 949 | 1624384 | 5826 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 5826 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008416 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER | 4230 | 20170108 | 919 | 1626741 | 4835 | Distribution Circuit | Environmental/External | Water | 324 | 1130611 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005307 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | RECLOSER | 5002 | 20170108 | 2139 | 1629613 | 1158 | Distribution Circuit | Vegetation | Tree - fell into line | 590 | 683220 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005759 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1121 | 192021121 | FUSE | 1217 | 20170109 | 125 | 1630127 | 510 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 33150 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005890 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 551 | 20170109 | 1656 | 1632051 | 3060 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 52020 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006269 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 7719 | 20170109 | 1638 | 1632115 | 1649 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3298 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006281 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER | 69032 | 20170109 | 1633 | 1631858 | 1111 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 135542 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006290 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3287 | 20170109 | 2031 | 1632509 | 1146 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 69906 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006466 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 7273 | 20170109 | 2029 | 1635771 | 2559 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 115155 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006922 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 5233 | 20170109 | 1412 | 1631461 | 1487 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 60967 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006162 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | OTHER | WIRE DOWN @ MTR#1009140678 | 20170109 | 3 | 1631738 | 3902 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10813 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006228 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3183 | 20170109 | 1330 | 1639668 | 3101 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6202 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007604 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3099 | 20170109 | 913 | 1630647 | 2155 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 53710 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005974 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 5153 | 20170109 | 1014 | 1630823 | 2294 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4588 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006183 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | OTHER | WIRE DOWN 4 SP LD SIDE OF 1595 | 20170109 | 1002 | 1630946 | 3704 | Distribution Circuit | Vegetation | Tree - fell into line | 221 | 222140 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006207 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3283 | 20170109 | 706 | 1630298 | 1952 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 9760 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005896 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 654897 | 20170109 | 759 | 1630434 | 731 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5117 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005923 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3127 | 20170109 | 1135 | 1631069 | 287 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 861 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006079 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 4160 | 20170109 | 2215 | 1632328 | 2570 | Distribution Circuit | Vegetation | Tree - fell into line | 416 | 626894 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006339 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LUCERNE-1106 | 43351106 | FUSE | 571 | 20170109 | 813 | 1630342 | 1593 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4779 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005930 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | SWITCH | 5779 | 20170109 | 959 | 1630771 | 1831 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9155 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006116 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE | 1413 | 20170109 | 1556 | 1631690 | 2837 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 28370 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006219 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | FUSE | 893 | 20170109 | 1209 | 1631170 | 1481 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5924 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006166 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | FUSE | 6115 | 20170109 | 1926 | 1632134 | 2422 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2422 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006506 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | RECLOSER | 76842 | 20170110 | 1730 | 1634723 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 171 | 191436 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007513 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 8481 | 20170110 | 805 | 1632657 | 2185 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 34960 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006521 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 1579 | 20170110 | 449 | 1632488 | 845 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 14365 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006581 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | FUSE | 4115 | 20170110 | 2310 | 1635202 | 879 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3516 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007252 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1260 | 20170110 | 1839 | 1635588 | 1511 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 111625 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006956 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8561 | 20170110 | 1515 | 1633970 | 1251 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 18765 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006810 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3173 | 20170110 | 1512 | 1633956 | 1784 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3568 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006994 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 7085 | 20170110 | 1725 | 1634687 | 1733 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2714 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007231 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | JUMPER | OPEN JUMPERS NORTH OF 2071 @ LINE & BUCK | 20170110 | 948 | 1632845 | 1874 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 7496 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006493 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 1801 | 20170110 | 1702 | 1634566 | 85 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 850 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006836 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | JUMPER | OJ'S FEEDING MTR# 1006277257 | 20170110 | 2114 | 1637989 | 1266 | Distribution Circuit | Vegetation | Tree - fell into line | 128 | 5173 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0007238 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1757 | 20170110 | 1051 | 1633702 | 1786 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 28576 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006726 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 4599 | 20170110 | 1136 | 1633088 | 1868 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 13076 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006555 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 8437 | 20170110 | 1611 | 1635231 | 229 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 7328 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006904 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LUCERNE-1106 | 43351106 | RECLOSER | 38632 | 20170110 | 1224 | 1633199 | 666 | Distribution Circuit | Vegetation | Tree - fell into line | 259 | 17964 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006612 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE | 1311 | 20170110 | 800 | 1632630 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7566 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006516 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 37506 | 20170110 | 1348 | 1633520 | 1900 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 122926 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0006682 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4599 | 20170111 | 1520 | 1640218 | 28 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 112 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007780 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 5233 | 20170111 | 29 | 1638185 | 1111 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 45551 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007483 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 1457 | 20170111 | 805 | 1638984 | 624 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5616 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007543 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8259 | 20170111 | 1701 | 1640399 | 89 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 178 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007840 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | SWITCH | 5989 | 20170111 | 2319 | 1640874 | 789 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 39450 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0008241 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 4365 | 20170111 | 1120 | 1639677 | 340 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1360 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007609 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1707 | 20170111 | 1005 | 1639395 | 1551 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 9306 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007652 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1879 | 20170111 | 1319 | 1639605 | 1608 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 10800 | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0007725 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 5395 | 20170111 | 849 | 1639110 | 1658 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1658 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007778 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 1729 | 20170111 | 1233 | 1639774 | 1668 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 11676 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0008438 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LUCERNE-1106 | 43351106 | FUSE | 4123 | 20170111 | 105 | 1638293 | 1090 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 57882 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007389 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | RECLOSER | 3700 | 20170111 | 1520 | 1640169 | 1515 | Distribution Circuit | Vegetation | Tree - branch fell on line | 243 | 18939 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0007819 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | SWITCH | 4571 | 20170118 | 415 | 1645681 | 986 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 69074 | Overcast-Drizzle-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0009722 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | BRIDGEVILLE-1102 | 192461102 | FUSE | 3717 | 20170118 | 1140 | 1646052 | 265 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 530 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010058 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1909 | 20170118 | 1908 | 1648406 | 901 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 21624 | Partly Cloudy-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010541 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 5823 | 20170118 | 1501 | 1646586 | 1256 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6280 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010227 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | JUMPER | WIRE DOWN 3 POLES SOUTH/OF 87707 | 20170118 | 1425 | s1249472 | 388 | Distribution Circuit | Vegetation | Tree - fell into line | 177 | 68466 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010088 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 6054 | 20170118 | 1458 | 1646619 | 1532 | Distribution Circuit | Vegetation | Tree - branch fell on line | 565 | 62542 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010049 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 6084 | 20170118 | 1428 | 1646451 | 1851 | Distribution Circuit | Vegetation | Tree - fell into line | 117 | 132061 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010015 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 4651 | 20170118 | 1419 | 1648814 | 1646 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 8230 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010411 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | JUMPER | OJ FLYING BELL 1/P/N/OF 8519 | 20170118 | 1643 | 1647122 | 1570 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7805 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010184 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 7291 | 20170118 | 1154 | 1646083 | 326 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 652 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0009905 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE | 1311 | 20170118 | 1541 | 1646802 | 1170 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 15210 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010236 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 7527 | 20170118 | 1047 | 1646050 | 1473 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2946 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0009930 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | RECLOSER | 83354 | 20170118 | 1254 | 1646194 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 24864 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010007 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 3651 | 20170118 | 1217 | 1646119 | 1755 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 27209 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0009995 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 551 | 20170119 | 253 | 1649783 | 682 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 11594 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010660 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | JUMPER | WIRE DOWN N/O 4471 | 20170119 | 956 | 1650538 | 404 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 13453 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010867 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 1803 | 20170120 | 808 | 1653293 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 24477 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011511 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3789 | 20170120 | 749 | 1652023 | 362 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 724 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011329 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2823 | 20170120 | 724 | 1653014 | 312 | Distribution Circuit | Vegetation | Tree - fell into line | 251 | 78312 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011322 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER | 31304 | 20170121 | 2320 | 1657760 | 2170 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 121680 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012563 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 7333 | 20170121 | 1200 | 1656548 | 1776 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1776 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012042 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3769 | 20170121 | 54 | 1655381 | 603 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 9045 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011880 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER | 445166 | 20170121 | 2151 | 1657406 | 1192 | Distribution Circuit | Vegetation | Tree - branch fell on line | 317 | 286999 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0012530 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 9289 | 20170121 | 2316 | 1657750 | 947 | Distribution Circuit | Vegetation | Tree - branch fell on line | 54 | 36615 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012978 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 4086 | 20170121 | 333 | 1655460 | 827 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 41570 | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 17-0011878 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | FUSE | 4137 | 20170121 | 928 | 1656470 | 246 | Distribution Circuit | Environmental/External | Ice or snow | 72 | 17712 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012000 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | FUSE | 4185 | 20170121 | 730 | 1655765 | 645 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 14 | 9030 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012120 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 90655 | 20170122 | 712 | 1659444 | 421 | Distribution Circuit | Vegetation | Tree - fell into line | 145 | 21229 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012951 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | JUMPER | HOT WIRE DOWN | 20170122 | 914 | 1660366 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2272 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013022 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1815 | 20170122 | 133 | 1658053 | 1967 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 57043 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012937 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 8223 | 20170122 | 736 | 1659534 | 654 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2616 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013117 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 7287 | 20170122 | 744 | 1659576 | 374 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 6358 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013134 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | Yes
HUMBOLDT | Tier 2 | HARRIS-1109 | 192431109 | FUSE | 6259 | 20170122 | 1343 | 1661587 | 168 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 2856 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013256 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 4086 | 20170122 | 646 | 1659328 | 2133 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 123714 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012851 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | NEWBURG-1133 | 192151133 | FUSE | 4401 | 20170122 | 2223 | 1662544 | 692 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3460 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013525 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | RECLOSER | 474 | 20170122 | 205 | 1658149 | 546 | Distribution Circuit | Equipment Failure/Involved | Overhead | 217 | 118482 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0012794 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 2653 | 20170122 | 1041 | 1660436 | 1540 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 12320 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013057 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 8989 | 20170122 | 1154 | 1660722 | 1492 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8952 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013189 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1101 | 192251101 | FUSE | 1907 | 20170122 | 1144 | 1660670 | 340 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 5440 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013081 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE | 4773 | 20170122 | 1204 | 1660776 | 196 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 1960 | Overcast-Below 32 F | Conductor, Overhead | Broken, wire on object | 17-0013094 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 5365 | 20170122 | 151 | 1658097 | 705 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 3525 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012601 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | BRIDGEVILLE-1102 | 192461102 | FUSE | 3711 | 20170123 | 1204 | 1663955 | 649 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 649 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0013845 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 56048 | 20170123 | 750 | 1663109 | 507 | Distribution Circuit | Vegetation | Tree - branch fell on line | 117 | 64904 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013631 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 2853 | 20170123 | 845 | 1663288 | 423 | Distribution Circuit | Vegetation | Tree - branch fell on line | 93 | 32239 | Clear-32-90 F | Insulator | Broken, wire on ground | 17-0013701 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | JUMPER | OJ'S 2 SPAN SS MTR 1008761141 | 20170123 | 845 | 1664091 | 555 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 555 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013827 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1260 | 20170207 | 401 | 1677894 | 488 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 37336 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018160 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 801579 | 20170207 | 410 | 1677713 | 874 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 3496 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018345 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 6069 | 20170207 | 316 | 1679710 | 2024 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 41580 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018464 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3173 | 20170207 | 1025 | 1679718 | 1565 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3130 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018588 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 551 | 20170207 | 35 | 1677632 | 925 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 15725 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018313 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3071 | 20170207 | 1152 | 1680018 | 163 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 163 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018615 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3321 | 20170207 | 717 | 1679122 | 707 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2828 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018704 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER | 1690 | 20170207 | 231 | 1677429 | 606 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 53694 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018052 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 2026 | 20170207 | 2130 | 1679549 | 806 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 7254 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018744 | OH | Sus | 0 | 2017 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1879 | 20170207 | 943 | 1681736 | 1900 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 30400 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018949 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 2747 | 20170207 | 326 | 1677594 | 879 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 18459 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018352 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 7093 | 20170207 | 843 | 1678957 | 346 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 8996 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018452 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 78083 | 20170207 | 825 | 1678936 | 330 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1490 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018425 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | RECLOSER | 1308 | 20170207 | 226 | 1677401 | 872 | Distribution Circuit | Vegetation | Tree - fell into line | 292 | 206364 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0018119 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | RECLOSER | 34008 | 20170207 | 359 | 1677687 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 298 | 68528 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018179 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 5415 | 20170207 | 546 | 1677989 | 888 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 19536 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018490 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER | 2936 | 20170207 | 431 | 1678835 | 1698 | Distribution Circuit | Vegetation | Tree - fell into line | 290 | 475244 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018311 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 5689 | 20170209 | 818 | 1682859 | 407 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2035 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019388 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 6073 | 20170209 | 1159 | 1683246 | 1745 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 12215 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019580 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1103 | 192381103 | FUSE | 6527 | 20170209 | 744 | 1682821 | 279 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1674 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019302 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 94127 | 20170209 | 915 | 1682966 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2025 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019380 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3163 | 20170209 | 909 | 1683016 | 321 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 12519 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019338 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 1931 | 20170209 | 1428 | 1683640 | 465 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4185 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019577 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3961 | 20170209 | 1608 | 1683856 | 2817 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 43631 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019589 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 6054 | 20170209 | 1009 | 1683053 | 234 | Distribution Circuit | Vegetation | Tree - branch fell on line | 551 | 40158 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019336 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1103 | 192221103 | FUSE | 2505 | 20170209 | 439 | 1682851 | 2216 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 77560 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019322 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1103 | 192221103 | RECLOSER | 1103/2 | 20170209 | 1303 | 1683446 | 1859 | Distribution Circuit | Vegetation | Tree - fell into line | 2653 | 1247182 | Overcast-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0019450 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER | 445166 | 20170209 | 1223 | 1683371 | 507 | Distribution Circuit | Vegetation | Tree - fell into line | 315 | 65541 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019494 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 37202 | 20170209 | 35 | 1682655 | 883 | Distribution Circuit | Environmental/External | Flood/Erosion | 64 | 56512 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019229 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | RECLOSER | 2026 | 20170209 | 2346 | 1684385 | 2504 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 62600 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019960 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE | 821 | 20170209 | 31 | 1682652 | 747 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 24051 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019209 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 1659 | 20170209 | 728 | 1682804 | 431 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 20257 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019288 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 8831 | 20170209 | 1018 | 1683066 | 438 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 13578 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019395 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5651 | 20170217 | 1202 | 1695273 | 474 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2448 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022268 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 4427 | 20170217 | 1101 | 1694634 | 319 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 26158 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022153 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | RECLOSER | 1294 | 20170217 | 1157 | 1695296 | 773 | Distribution Circuit | Vegetation | Tree - fell into line | 544 | 118435 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022229 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | MAPLE CREEK-1101 | 192101101 | FUSE | 6529 | 20170217 | 1127 | 1694961 | 178 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 534 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022109 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | CARLOTTA-1121 | 192291121 | OTHER | WIRE DOWN 4/S/LD/OF 5841 | 20170218 | 351 | 1698869 | 414 | Distribution Circuit | Vegetation | Tree - fell into line | 230 | 27697 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022876 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 7415 | 20170218 | 424 | 1699084 | 570 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2850 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022905 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 1687 | 20170218 | 649 | 1699000 | 641 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3846 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022935 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 6793 | 20170218 | 408 | 1698868 | 442 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3536 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022959 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 2345 | 20170218 | 805 | 1699127 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1755 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022953 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 37506 | 20170218 | 1019 | 1699420 | 822 | Distribution Circuit | Vegetation | Tree - branch fell on line | 89 | 35363 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023003 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 5113 | 20170220 | 2050 | 1708048 | 1079 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4814 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024976 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5651 | 20170220 | 1641 | 1704236 | 1254 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 40192 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0023957 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | SWITCH | 1599 | 20170220 | 1953 | 1705782 | 1028 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 35879 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024078 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER | 445166 | 20170220 | 322 | 1702367 | 841 | Distribution Circuit | Equipment Failure/Involved | Overhead | 314 | 264074 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023655 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | OTHER | 6591 | 20170220 | 940 | 1702931 | 320 | Distribution Circuit | Environmental/External | Flood/Erosion | 1 | 320 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023732 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 3174 | 20170220 | 1741 | 1705017 | 1467 | Distribution Circuit | Vegetation | Tree - branch fell on line | 133 | 156970 | Partly Cloudy-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023979 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | SWITCH | 3155 | 20170220 | 1741 | 1708350 | 1745 | Distribution Circuit | Vegetation | Tree - fell into line | 465 | 811425 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025064 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER | 532 | 20170220 | 1856 | 1705418 | 90 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 25380 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024064 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | TRIP-SAVER | 1079 | 20170220 | 2034 | 1705947 | 1508 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 48324 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024320 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 1073 | 20170220 | 2348 | 1706765 | 2384 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 50064 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024838 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 78083 | 20170220 | 2119 | 1706142 | 1459 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 8754 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024905 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | RECLOSER | 37222 | 20170220 | 2125 | 1706809 | 863 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 44345 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024560 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | UKIAH-1115 | 42771115 | FUSE | 3405 | 20170220 | 829 | 1702742 | 716 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 27302 | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023733 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | RECLOSER | 504 | 20170220 | 1440 | 1703577 | 1390 | Distribution Circuit | Vegetation | Tree - fell into line | 938 | 271604 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023880 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 9215 | 20170220 | 1439 | 1706083 | 1645 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 13160 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024132 | OH | Sus | 0 | 2017 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | HUMBOLDT BAY-1102 | 192341102 | FUSE | 5301 | 20170221 | 1231 | 1708531 | 266 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1064 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025205 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 4539 | 20170221 | 534 | 1707450 | 481 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1924 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024934 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | KONOCTI-1108 | 43311108 | FUSE | 513427 | 20170222 | 1501 | 1710847 | 238 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 5957 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025699 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER | 1904 | 20170222 | 1450 | 1710908 | 590 | Distribution Circuit | Vegetation | Tree - fell into line | 357 | 62400 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025703 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | RECLOSER | 4218 | 20170406 | 147 | 1745114 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 8806 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0036900 | OH | Sus | 0 | 2017 | APR | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | OTHER | 2/3 WIRES DOWN @ MTR# 1008391365 | 20170406 | 1934 | 1747547 | 1197 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 129435 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037311 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 8127 | 20170406 | 1847 | 1746093 | 1437 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 30177 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037320 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5087 | 20170406 | 1931 | 1751113 | 1364 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 13640 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037983 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1929 | 20170406 | 540 | 1745261 | 1760 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 12320 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037112 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 1719 | 20170406 | 1833 | 1745940 | 2472 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 12360 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037472 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 6645 | 20170406 | 1910 | 1746107 | 1310 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 15720 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037475 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 3041 | 20170406 | 2029 | 1746809 | 1055 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 31650 | Partly Cloudy-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037495 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 8639 | 20170406 | 1924 | 1746221 | 2544 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 15264 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037728 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8595 | 20170406 | 25 | 1745025 | 278 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 556 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0036882 | OH | Sus | 42984508 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 6069 | 20170406 | 1902 | 1746177 | 2734 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 78664 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037309 | OH | Sus | 0 | 2017 | APR | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3015 | 20170406 | 2306 | 1748639 | 2524 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 25240 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037511 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | JUMPER | OJ'S AT 42765 CASPAR LITTLE LAKE RD | 20170406 | 1914 | 1749127 | 1476 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1476 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037500 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER | 95324 | 20170406 | 137 | 1745074 | 516 | Distribution Circuit | Vegetation | Tree - fell into line | 223 | 114508 | Partly Cloudy-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0036890 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | OTHER | 1 OF 3 HOT WIRES DOWN | 20170406 | 2013 | 1748482 | 1090 | Distribution Circuit | Vegetation | Tree - fell into line | 1039 | 975240 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037421 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | RECLOSER | 1294 | 20170406 | 1725 | 1745838 | 2964 | Distribution Circuit | Vegetation | Tree - fell into line | 624 | 166036 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037246 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 5621 | 20170406 | 2043 | 1747039 | 2393 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 38288 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037463 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HARRIS-1109 | 192431109 | FUSE | 6671 | 20170406 | 231 | 1745200 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 7710 | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0036920 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3073 | 20170406 | 1334 | 1745565 | 356 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 60520 | Strong Winds-Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037151 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 2307 | 20170406 | 2204 | 1748190 | 1006 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 39234 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037481 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 2094 | 20170406 | 256 | 1745167 | 2511 | Distribution Circuit | Vegetation | Tree - fell into line | 304 | 104424 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0036905 | OH | Sus | 0 | 2017 | APR | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | MAPLE CREEK-1101 | 192101101 | FUSE | 5917 | 20170406 | 924 | 1745327 | 656 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 656 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037077 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 4165 | 20170406 | 1244 | 1745500 | 257 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 771 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037181 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | TRIP-SAVER | 1325 | 20170406 | 2101 | 1747398 | 851 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 82547 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037415 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 3807 | 20170406 | 1543 | 1745780 | 555 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 32745 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0037203 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 91948 | 20170406 | 2056 | 1747345 | 1333 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 57121 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037342 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 3651 | 20170406 | 2109 | 1747443 | 1131 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 19227 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037441 | OH | Sus | 0 | 2017 | APR | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 8049 | 20170406 | 2132 | 1747803 | 1279 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2543 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037531 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 8831 | 20170406 | 1829 | 1745935 | 1444 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 8287 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037272 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 7343 | 20170407 | 1407 | 1750166 | 208 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 2704 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0037941 | OH | Sus | 0 | 2017 | APR | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1909 | 20170407 | 17 | 1748995 | 938 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 22512 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037706 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 1659 | 20170407 | 743 | 1749889 | 1832 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7328 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038023 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | OTHER | WIRE DOWN @ CAP BK 884 | 20170407 | 1423 | 1751068 | 2802 | Distribution Circuit | Vegetation | Tree - fell into line | 2452 | 132368 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037967 | OH | Sus | 0 | 2017 | APR | Yes | Open Circuit | Yes | Yes
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 654897 | 20170407 | 717 | 1749779 | 1847 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4145 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037815 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 42871101 | RECLOSER | 1276 | 20170407 | 1903 | 1751575 | 888 | Distribution Circuit | Vegetation | Tree - fell into line | 291 | 127434 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038106 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 1949 | 20170421 | 1424 | 1764233 | 759 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3795 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0042022 | OH | Sus | 42999178 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 1837 | 20170618 | 1056 | 1807649 | 198 | Distribution Circuit | 3rd Party | Vehicle | 6 | 1188 | Clear-Heat Wave-32-90 F | Pole-Wood | Broken, wire on ground | 17-0056092 | OH | Sus | 0 | 2017 | JUN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | HIGHLANDS-1103 | 43361103 | FUSE | 7117 | 20171008 | 2018 | 1893966 | 1293 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 67236 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085214 | OH | Sus | 31355575 | 2017 | OCT | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 3587 | 20171008 | 2254 | 1894140 | 2451 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 186751 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085739 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | CALPELLA-1101 | 43411101 | FUSE | 3513 | 20171009 | 620 | 1895763 | 10105 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 111 | 1048890 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0085418 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | OTHER | WIRE DOWN 1P S/SIDE OF 9789 | 20171009 | 142 | 1894986 | 2690 | Distribution Circuit | Vegetation | Tree - branch fell on line | 336 | 218099 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085344 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | Yes
HUMBOLDT | Tier 2 | LUCERNE-1106 | 43351106 | OCB | 1106/2 | 20171009 | 51 | 1894798 | 2036 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2972 | 1633084 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085361 | OH | Sus | 0 | 2017 | OCT | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | MENDOCINO-1101 | 42951101 | FUSE | 80695 | 20171009 | 52 | 1898710 | 8143 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 7 | 57001 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085395 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | REDBUD-1101 | 43191101 | JUMPER | 4/P/LD 90439 | 20171009 | 29 | 1894896 | 630 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 13314 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085335 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | JUMPER | WIRE DOWN | 20171216 | 1151 | 1945058 | 353 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 26120 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102101 | OH | Sus | 0 | 2017 | DEC | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | CALPELLA-1101 | 43411101 | FUSE | 6369 | 20180316 | 453 | 45212 | 447 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 447 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023246 | OH | Sus | 43302651 | 2018 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 7927 | 20181108 | 945 | 211460 | 423 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2538 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0098214 | OH | Sus | 43533911 | 2018 | NOV | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1929 | 20181121 | 216 | 219464 | 579 | Distribution Circuit | 3rd Party | Gun Shot | 78 | 4834 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0101683 | OH | Sus | 43584639 | 2018 | NOV | Yes | Open Circuit | Yes | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1770 | 20181129 | 36 | 227355 | 748 | Distribution Circuit | Vegetation | Tree - fell into line | 350 | 79638 | Clear-32-90 F | Conductor, Overhead | On Ground | 18-0104657 | OH | Sus | 31417162 | 2018 | NOV | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1915 | 20190106 | 1140 | 255289 | 235 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 235 | Overcast-Fog-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0005081 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 4451 | 20190106 | 2326 | 258392 | 826 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5782 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005695 | OH | Sus | 31421138 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4557 | 20190116 | 1206 | 266852 | 1541 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 46230 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009691 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 5113 | 20190116 | 1400 | 267082 | 1613 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 9678 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009773 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3611 | 20190116 | 1706 | 268214 | 2548 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 10192 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010041 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5173 | 20190116 | 1719 | 268442 | 2448 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 31824 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010128 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 79817 | 20190116 | 1745 | 268768 | 2655 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 124785 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010291 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 4197 | 20190116 | 1951 | 269761 | 2434 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 36510 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010308 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 8189 | 20190116 | 1703 | 268196 | 2429 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 12145 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010336 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1909 | 20190116 | 1727 | 268538 | 1463 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 7371 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010091 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1298 | 20190116 | 1353 | 267068 | 1727 | Distribution Circuit | Vegetation | Tree - fell into line | 908 | 154568 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009782 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1260 | 20190116 | 1431 | 267175 | 3958 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 141214 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009901 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | OTHER | WIRE DOWN 1 SOURCE SIDE OF 3921 | 20190116 | 1825 | 269163 | 2425 | Distribution Circuit | Vegetation | Tree - fell into line | 151 | 363151 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010079 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 8639 | 20190116 | 1431 | 276225 | 4207 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 25242 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011962 | OH | Sus | 0 | 2019 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | TRIP-SAVER | 3113 | 20190116 | 1811 | 268999 | 1600 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 82069 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010545 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3311 | 20190116 | 1727 | 268518 | 1688 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 35448 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010022 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 3109 | 20190116 | 1724 | 268821 | 1291 | Distribution Circuit | Vegetation | Tree - branch fell on line | 83 | 107153 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010170 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1487 | 20190116 | 1724 | 270366 | 1700 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6582 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010172 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER | 8860 | 20190116 | 1841 | 269539 | 2552 | Distribution Circuit | Vegetation | Tree - fell into line | 159 | 405768 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010078 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | FUSE | 8301 | 20190116 | 1802 | 273261 | 2539 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2539 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011499 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 56048 | 20190116 | 1711 | 268396 | 2868 | Distribution Circuit | Vegetation | Tree - fell into line | 850 | 1157121 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009952 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1971 | 20190116 | 1855 | 269534 | 2645 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 21160 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011360 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 2011 | 20190116 | 1211 | 267002 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 32630 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009660 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 4437 | 20190116 | 1234 | 266894 | 1601 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 40025 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009931 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HIGHLANDS-1103 | 43361103 | FUSE | 49361 | 20190116 | 1859 | 269559 | 2461 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 36915 | Strong Winds-Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010287 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HUMBOLDT BAY-1102 | 192341102 | FUSE | 7617 | 20190116 | 1858 | 269555 | 1073 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 3315 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010238 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER | 532 | 20190116 | 1836 | 269390 | 1181 | Distribution Circuit | Vegetation | Tree - fell into line | 336 | 394688 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010056 | OH | Sus | 0 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 2343 | 20190116 | 1906 | 269618 | 2632 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 42112 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011295 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | RECLOSER | 68436 | 20190116 | 1805 | 268942 | 2922 | Distribution Circuit | Vegetation | Tree - fell into line | 127 | 278574 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010012 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LUCERNE-1106 | 43351106 | RECLOSER | 38632 | 20190116 | 1849 | 269490 | 1703 | Distribution Circuit | Vegetation | Tree - fell into line | 260 | 100636 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010069 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MENDOCINO-1101 | 42951101 | FUSE | 2771 | 20190116 | 2044 | 270797 | 2691 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 39115 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011132 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 7871 | 20190116 | 1139 | 266819 | 1472 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5888 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009593 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 37506 | 20190116 | 1802 | 268983 | 4161 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 145920 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010021 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 7653 | 20190116 | 2302 | 272101 | 3734 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 29872 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010431 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 538 | 20190116 | 1816 | 269159 | 4077 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 82839 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010932 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 6423 | 20190116 | 1808 | 268951 | 2963 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 57914 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011203 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 3769 | 20190116 | 1803 | 268915 | 2807 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 129612 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010175 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 8771 | 20190117 | 1726 | 274715 | 1378 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2756 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011320 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 6069 | 20190117 | 508 | 273608 | 1927 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 98277 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010918 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | FUSE | 3931 | 20190117 | 159 | 272304 | 984 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 15678 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010961 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 54634 | 20190117 | 1226 | 273945 | 1672 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3344 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011223 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | TRIP-SAVER | 1079 | 20190117 | 125 | 272256 | 2369 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 50222 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011149 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 547 | 20190117 | 647 | 273871 | 1922 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 34596 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011198 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | RECLOSER | 1308 | 20190117 | 1952 | 274924 | 2899 | Distribution Circuit | Vegetation | Tree - branch fell on line | 455 | 233033 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011465 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 262813 | 20190202 | 240 | 286092 | 662 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 7282 | Partly Cloudy-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016978 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 8205 | 20190202 | 724 | 286748 | 312 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 312 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017015 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1121 | 192021121 | OTHER | 1269 | 20190204 | 1210 | 290365 | 385 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5390 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018024 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 8519 | 20190204 | 1834 | 291084 | 1166 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5830 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018155 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 5233 | 20190204 | 1431 | 290570 | 1448 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 26064 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018075 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 3621 | 20190209 | 1304 | 297028 | 386 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 758 | Overcast-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0020356 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1121 | 192021121 | FUSE | 1269 | 20190209 | 925 | 296874 | 382 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5348 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020326 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | RECLOSER | 37484 | 20190209 | 1724 | 297227 | 5824 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 124272 | Overcast-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020385 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 3304 | 20190209 | 2350 | 297595 | 8364 | Distribution Circuit | Vegetation | Tree - fell into line | 510 | 2240269 | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0020485 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 8435 | 20190209 | 2350 | 299370 | 8364 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 184008 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020836 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3261 | 20190209 | 2350 | 300809 | 8282 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 82820 | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0021513 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | OTHER | WIRE DOWN 3 NW/OF 3161 | 20190209 | 1323 | 297041 | 8994 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 570842 | Overcast-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0020330 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 55437 | 20190209 | 1326 | 299771 | 8969 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 8969 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020999 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | FUSE | 6267 | 20190210 | 17 | 299274 | 3938 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 15752 | Clear-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020808 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | JUMPER | OJ TO CGC 114440453436 | 20190210 | 17 | 300885 | 4018 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8036 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0021548 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | FUSE | 4591 | 20190210 | 16 | 300888 | 3969 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 15876 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021549 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | FUSE | 5457 | 20190210 | 17 | 300892 | 3960 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 23760 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021550 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | RECLOSER | 1101/2 | 20190210 | 316 | 297827 | 5268 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 320960 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020528 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | FUSE | 4119 | 20190210 | 316 | 300203 | 6632 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 53056 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021196 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1102 | 192461102 | FUSE | 3473 | 20190210 | 1009 | 298639 | 1656 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 39744 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020741 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1102 | 192461102 | FUSE | 3463 | 20190210 | 629 | 298087 | 1791 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 19701 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020837 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | CARLOTTA-1121 | 192291121 | RECLOSER | 44150 | 20190210 | 554 | 298064 | 3629 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 49966 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020567 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 1637 | 20190210 | 1121 | 298832 | 2873 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 54587 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021156 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER | 95324 | 20190210 | 654 | 298132 | 2118 | Distribution Circuit | Vegetation | Tree - branch fell on line | 224 | 393741 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020569 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | OCB | 1141/2 | 20190210 | 928 | 298309 | 1963 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 330690 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020635 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 6865 | 20190210 | 827 | 298480 | 1943 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 184585 | Clear-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020811 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 35706 | 20190210 | 447 | 298139 | 2050 | Distribution Circuit | Vegetation | Tree - fell into line | 323 | 517807 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020571 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | OCB | 1101/2 | 20190210 | 710 | 298102 | 6230 | Distribution Circuit | Vegetation | Tree - fell into line | 985 | 1158702 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020576 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 4521 | 20190210 | 638 | 299983 | 2136 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12816 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021112 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 2500 | 20190210 | 502 | 297966 | 2134 | Distribution Circuit | Vegetation | Tree - fell into line | 446 | 747992 | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0020546 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 1102/2 | 20190210 | 510 | 297988 | 5074 | Distribution Circuit | Vegetation | Tree - fell into line | 1360 | 1786477 | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0020550 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | JUMPER | OJ'S 1 SS/OF MTR#1008282876 | 20190210 | 121 | 299421 | 3829 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 38290 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020857 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3247 | 20190210 | 121 | 300150 | 5049 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5049 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0021186 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 2577 | 20190210 | 1056 | 298795 | 309 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 14523 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020682 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 91239 | 20190210 | 1142 | 298823 | 368 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1104 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020691 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 2094 | 20190210 | 904 | 298476 | 5951 | Distribution Circuit | Vegetation | Tree - fell into line | 302 | 563459 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020621 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | MAPLE CREEK-1101 | 192101101 | OCB | 1101/2 | 20190210 | 59 | 297704 | 5176 | Distribution Circuit | Vegetation | Tree - fell into line | 130 | 371859 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020494 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | MAPLE CREEK-1101 | 192101101 | FUSE | 6235 | 20190210 | 59 | 299287 | 5311 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 74354 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020815 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | NEWBURG-1131 | 192151131 | FUSE | 7049 | 20190210 | 231 | 297796 | 2288 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 19346 | Overcast-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 19-0020596 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER | 4230 | 20190210 | 1337 | 298987 | 1890 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 49140 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020718 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 37506 | 20190210 | 938 | 298539 | 521 | Distribution Circuit | Equipment Failure/Involved | Overhead | 88 | 12521 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0020639 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 826 | 20190210 | 1621 | 299174 | 232 | Distribution Circuit | Vegetation | Tree - branch fell on line | 868 | 96096 | Clear-32-90 F | Conductor, Overhead | On Ground | 19-0020798 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | RECLOSER | 34008 | 20190210 | 1306 | 298957 | 1358 | Distribution Circuit | Vegetation | Tree - fell into line | 571 | 70142 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020714 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | OTHER | 2 WIRES DOWN FEEDING LR 4904 | 20190210 | 109 | 298903 | 6299 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 317669 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020693 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1101 | 192171101 | SWITCH | 394285 | 20190210 | 109 | 298999 | 3925 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 15700 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020724 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 5233 | 20190210 | 109 | 299589 | 5121 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 92178 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020920 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1102 | 192171102 | JUMPER | OJ'S ON HARD TAP FEEDING MTR# 1006304361 | 20190210 | 109 | 299101 | 2283 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 15981 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020772 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1102 | 192171102 | FUSE | 68539 | 20190210 | 109 | 299601 | 4136 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 49632 | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0020924 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1102 | 192171102 | FUSE | 5521 | 20190210 | 109 | 300749 | 6706 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 114002 | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0021476 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER | 3090 | 20190210 | 109 | 300865 | 8423 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 404304 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0021540 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 7507 | 20190210 | 109 | 305581 | 10949 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 10949 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022555 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 48809 | 20190210 | 109 | 305605 | 12027 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 216486 | Clear-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0022557 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | JUMPER | OJ 1 SS MTR 1008024281 | 20190210 | 109 | 307307 | 10944 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 32832 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0022872 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 2971 | 20190210 | 109 | 308264 | 11297 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 214643 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0023086 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3151 | 20190212 | 1906 | 301003 | 4154 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 58156 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021585 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3725 | 20190212 | 2131 | 301312 | 2712 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 8136 | Clear-32-90 F | Conductor, Overhead | On Ground | 19-0021652 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | OTHER | WIRE DOWN BETWEEN FUCO 7713 AND FUCO 667805 | 20190212 | 2218 | 301347 | 2582 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 168090 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021694 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5187 | 20190212 | 2156 | 301237 | 2744 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 24696 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022095 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 1917 | 20190212 | 2152 | 301209 | 953 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 19060 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022224 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3163 | 20190212 | 1852 | 312377 | 5228 | Distribution Circuit | Vegetation | Tree - grew into line | 39 | 185620 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024119 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER | 816 | 20190212 | 2213 | 301152 | 1221 | Distribution Circuit | Vegetation | Tree - branch fell on line | 389 | 441731 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021642 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3969 | 20190212 | 2111 | 302651 | 2582 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 152338 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 19-0021777 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 7253 | 20190212 | 2209 | 301307 | 2666 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 45322 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021882 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1607 | 20190212 | 1935 | 305318 | 2819 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 11276 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022482 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 4483 | 20190212 | 1311 | 300706 | 234 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 468 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021502 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER | 1294 | 20190212 | 2128 | 301150 | 1031 | Distribution Circuit | Vegetation | Tree - fell into line | 611 | 68487 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021644 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 7287 | 20190212 | 2128 | 304443 | 2200 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 37400 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022211 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 4160 | 20190212 | 2234 | 301375 | 3935 | Distribution Circuit | Equipment Failure/Involved | Overhead | 417 | 1303157 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021645 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MENDOCINO-1101 | 42951101 | FUSE | 2771 | 20190212 | 1714 | 300901 | 4355 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 23593 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021565 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | RECLOSER | 2600 | 20190212 | 2010 | 301078 | 4348 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 120301 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021577 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2831 | 20190212 | 1651 | 301404 | 3926 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 340423 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021648 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2823 | 20190212 | 1914 | 301069 | 3724 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 160132 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021651 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 4961 | 20190212 | 1651 | 301765 | 4311 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 99153 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021712 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 1661 | 20190212 | 1651 | 301790 | 4311 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 303710 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0021717 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 1843 | 20190212 | 2156 | 302591 | 3667 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 88008 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021761 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | JUMPER | OJ'S 2 S/OF 3651 | 20190212 | 1914 | 310247 | 4225 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8450 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023527 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | FUSE | 8019 | 20190212 | 1829 | 300962 | 1633 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 74161 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021579 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | FUSE | 2785 | 20190212 | 1843 | 300977 | 1527 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 38175 | Strong Winds-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021580 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 722265 | 20190213 | 1054 | 303948 | 4614 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 240124 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022122 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3015 | 20190213 | 407 | 304736 | 2058 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 20580 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022322 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8541 | 20190213 | 228 | 304741 | 2223 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 17784 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022325 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3173 | 20190213 | 228 | 305557 | 3742 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 7484 | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0022550 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8567 | 20190213 | 2222 | 305807 | 1113 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 10017 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023535 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 6081 | 20190213 | 457 | 302680 | 1030 | Distribution Circuit | Vegetation | Tree - fell into line | 140 | 123432 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021790 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 7361 | 20190213 | 1023 | 303686 | 1877 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5631 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022128 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | JUMPER | OJ SS/O MTR 1008944984 | 20190213 | 620 | 302883 | 3260 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3260 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022379 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3069 | 20190213 | 2315 | 305877 | 1160 | Distribution Circuit | Vegetation | Tree - fell into line | 160 | 101050 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022736 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 2857 | 20190213 | 1834 | 305522 | 1238 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 37140 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023044 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 8247 | 20190213 | 407 | 302618 | 3437 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6874 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021812 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 262813 | 20190213 | 1259 | 304548 | 2793 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 30723 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022525 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | KONOCTI-1102 | 43311102 | FUSE | 2297 | 20190213 | 1903 | 305550 | 1032 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 51239 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022577 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 5097 | 20190213 | 1008 | 303457 | 1889 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 26446 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022315 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | UKIAH-1114 | 42771114 | FUSE | 781 | 20190213 | 138 | 301798 | 5337 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 112077 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021840 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1101 | 192171101 | SWITCH | 394285 | 20190213 | 326 | 302813 | 484 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1936 | Clear-Strong Winds-Below 32 F | Conductor, Overhead | On Ground | 19-0021803 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 7745 | 20190214 | 1414 | 309608 | 1479 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7395 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023579 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1899 | 20190214 | 513 | 307177 | 392 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 4312 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022956 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | SWITCH | 3901 | 20190214 | 645 | 309266 | 1725 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 36225 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023262 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 8639 | 20190214 | 805 | 307595 | 3286 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 19716 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023437 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1260 | 20190214 | 1843 | 310646 | 1290 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 64164 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023621 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 2023 | 20190214 | 730 | 307400 | 1605 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 57780 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022944 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2595 | 20190214 | 846 | 307912 | 494 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 494 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0022972 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 8223 | 20190214 | 726 | 307384 | 3144 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12576 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023207 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3151 | 20190215 | 1911 | 312909 | 1150 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 16100 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024370 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | FUSE | 6697 | 20190215 | 2225 | 313201 | 848 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 848 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024369 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | FUSE | 67185 | 20190215 | 1024 | 311845 | 1651 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4953 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024050 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 37498 | 20190215 | 1917 | 312684 | 1234 | Distribution Circuit | Vegetation | Tree - fell into line | 144 | 177696 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024262 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | JUMPER | OJ'S 9 SPANS LS OF LR-3090 | 20190215 | 2133 | 314703 | 1214 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4856 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024651 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 5247 | 20190215 | 2133 | 314800 | 2221 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 33315 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024674 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | RECLOSER | 1101/2 | 20190216 | 1124 | 314020 | 1761 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 66199 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024517 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER | 445166 | 20190216 | 1154 | 314111 | 347 | Distribution Circuit | Vegetation | Tree - fell into line | 316 | 100494 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024570 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1102 | 192461102 | FUSE | 3463 | 20190217 | 1152 | 315780 | 238 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 2618 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025194 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER | 1602 | 20190217 | 1116 | 315683 | 1594 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 47908 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025107 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | FUSE | 4157 | 20190217 | 801 | 315353 | 2024 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12144 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025268 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1102 | 192171102 | FUSE | 3113 | 20190217 | 1531 | 316405 | 1415 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 39620 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025278 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 3079 | 20190217 | 1745 | 316582 | 1281 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 10248 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025294 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | JUMPER | 5503 | 20190226 | 709 | 324052 | 435 | Distribution Circuit | Vegetation | Tree - fell into line | 225 | 97875 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028121 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 8127 | 20190226 | 2333 | 326174 | 1167 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 24507 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028957 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5651 | 20190226 | 2213 | 325435 | 1159 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8906 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029110 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | JUMPER | WIRE DOWN AT SB 134281 | 20190226 | 2255 | 325726 | 937 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 50542 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028688 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 87163 | 20190226 | 2316 | 325565 | 969 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 21107 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028724 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 1905 | 20190226 | 2332 | 325724 | 1157 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 26611 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029001 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 6069 | 20190226 | 2229 | 325488 | 2181 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 111231 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028935 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8947 | 20190226 | 2227 | 325313 | 7982 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 17474 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029288 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER | 35592 | 20190226 | 1739 | 324987 | 329 | Distribution Circuit | Vegetation | Tree - fell into line | 537 | 82593 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028507 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 8573 | 20190226 | 1723 | 324950 | 955 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 11460 | Clear-32-90 F | Conductor, Overhead | On Ground | 19-0028509 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 3109 | 20190226 | 1423 | 324816 | 217 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 18879 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028461 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1757 | 20190226 | 2114 | 325303 | 2428 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 38848 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028598 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2529 | 20190226 | 1447 | 324701 | 1528 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7640 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028503 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 7461 | 20190226 | 745 | 324064 | 5825 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 34950 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028126 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | KONOCTI-1102 | 43311102 | FUSE | 92677 | 20190226 | 817 | 324061 | 605 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2420 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028161 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE | 4687 | 20190226 | 731 | 323924 | 295 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 7375 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028170 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE | 773 | 20190226 | 627 | 323875 | 414 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 1342 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028100 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 8247 | 20190226 | 1121 | 324322 | 149 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 298 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028252 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1102 | 192171102 | RECLOSER | 3090 | 20190226 | 1931 | 325167 | 1424 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 68352 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028550 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 6073 | 20190227 | 1037 | 326844 | 1590 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 25471 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029138 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 7341 | 20190227 | 224 | 326677 | 1074 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4296 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029014 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 5233 | 20190227 | 4 | 325930 | 2135 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 32399 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028962 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 4451 | 20190227 | 321 | 326234 | 2327 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 16289 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029004 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 7155 | 20190227 | 226 | 326167 | 701 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 22238 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028726 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | FUSE | 9059 | 20190227 | 906 | 326674 | 452 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4068 | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0028929 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 79817 | 20190610 | 1120 | 403592 | 200 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 9400 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0065314 | OH | Sus | 43837205 | 2019 | JUN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 1473 | 20190923 | 513 | 604148 | 389 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3890 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0102283 | OH | Sus | 0 | 2019 | SEP | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1907 | 20191120 | 130 | 710642 | 536 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 8576 | Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0126622 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 2431 | 20191126 | 1601 | 716168 | 1565 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 27358 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0129754 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | OTHER | WIRE DOWN 1 SP LD SIDE OF 3223 | 20191126 | 1536 | 716066 | 290 | Distribution Circuit | Vegetation | Tree - branch fell on line | 495 | 82500 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0129264 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1121 | 192021121 | FUSE | 1359 | 20200116 | 202 | 761903 | 2101 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 81939 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009594 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | FUSE | 5709 | 20200116 | 146 | 761891 | 689 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 11024 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0009498 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | RECLOSER | 1101/2 | 20200116 | 432 | 761980 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 55514 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009497 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 1659 | 20200116 | 614 | 765253 | 4630 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 18520 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 20-0010994 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 4367 | 20200116 | 614 | 766118 | 4897 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 73455 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0011174 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER | 8860 | 20200116 | 610 | 762125 | 601 | Distribution Circuit | Vegetation | Tree - fell into line | 161 | 96761 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009525 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 1679 | 20200116 | 726 | 766142 | 4968 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 228528 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0011186 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 1510 | 20200116 | 413 | 761956 | 2265 | Distribution Circuit | Vegetation | Tree - fell into line | 356 | 792687 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009495 | OH | Sus | 0 | 2020 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1793 | 20200116 | 413 | 763648 | 2265 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 18120 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010326 | OH | Sus | 0 | 2020 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1787 | 20200116 | 413 | 765118 | 3457 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 48398 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0010920 | OH | Sus | 0 | 2020 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER | 1294 | 20200116 | 318 | 761942 | 347 | Distribution Circuit | Vegetation | Tree - fell into line | 630 | 62299 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009489 | OH | Sus | 0 | 2020 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 8435 | 20200116 | 259 | 763568 | 6605 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 145310 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010303 | OH | Sus | 0 | 2020 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 7535 | 20200116 | 259 | 765494 | 5001 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 25005 | Overcast-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 20-0011049 | OH | Sus | 0 | 2020 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 6633 | 20200116 | 259 | 766566 | 10666 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 42664 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0011341 | OH | Sus | 0 | 2020 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | RECLOSER | 518 | 20200116 | 627 | 762105 | 4832 | Distribution Circuit | Vegetation | Tree - fell into line | 525 | 1796587 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010377 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 2503 | 20200116 | 545 | 762026 | 4945 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 39560 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009710 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 4639 | 20200116 | 606 | 762073 | 3579 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 60843 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009939 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 2457 | 20200116 | 613 | 762038 | 3195 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 146765 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009955 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 2577 | 20200116 | 649 | 765124 | 2290 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 107630 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010932 | OH | Sus | 0 | 2020 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 5259 | 20200116 | 620 | 762221 | 822 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 15618 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009576 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | OCB | 1102/2 | 20200116 | 748 | 762227 | 1973 | Distribution Circuit | Vegetation | Tree - fell into line | 601 | 270017 | Overcast-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on object | 20-0009587 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | JUMPER | OJ 20 SPANS LD SIDE OF 3893 | 20200116 | 519 | 763565 | 1744 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 22672 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010301 | OH | Sus | 0 | 2020 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 80039 | 20200116 | 658 | 763582 | 2023 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 135541 | Overcast-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0010309 | OH | Sus | 0 | 2020 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 2359 | 20200116 | 1153 | 763354 | 3187 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 54179 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010315 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 2094 | 20200116 | 317 | 761945 | 2412 | Distribution Circuit | Vegetation | Tree - fell into line | 303 | 275436 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009490 | OH | Sus | 0 | 2020 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | MAPLE CREEK-1101 | 192101101 | OCB | 1101/2 | 20200116 | 125 | 761886 | 976 | Distribution Circuit | Vegetation | Tree - fell into line | 146 | 34096 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009480 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER | 4230 | 20200116 | 217 | 761896 | 11 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 286 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0009483 | OH | Sus | 0 | 2020 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | RECLOSER | 29362 | 20200116 | 134 | 761887 | 9185 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 871469 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009481 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | SWITCH | 3139 | 20200116 | 259 | 762158 | 6436 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 51488 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0009554 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 3053 | 20200116 | 300 | 764770 | 3522 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 91572 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010592 | OH | Sus | 0 | 2020 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 7283 | 20200116 | 259 | 765175 | 6649 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6649 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0010959 | OH | Sus | 0 | 2020 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 5521 | 20200116 | 300 | 763576 | 3425 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 58225 | Clear-Below 32 F | Connector or Splice (OH) | Broken, wire on ground | 20-0010307 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 2899 | 20200116 | 1942 | 764754 | 2576 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 54096 | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 20-0010579 | OH | Sus | 0 | 2020 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | JUMPER | WIRE DOWN 3 SPANS LD SIDE OF 2989 | 20200116 | 1921 | 764829 | 2601 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 6841 | Partly Cloudy-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010636 | OH | Sus | 0 | 2020 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | FUSE | 4199 | 20200209 | 1230 | 784209 | 592 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1776 | Clear | Pole-Wood | Broken, wire on ground | 20-0019275 | OH | Sus | 0 | 2020 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | OCB | 1101/2 | 20200315 | 406 | 851771 | 800 | Distribution Circuit | Environmental/External | Ice or snow | 1270 | 158601 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032183 | OH | Sus | 0 | 2020 | MAR | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | OTHER | WIRE DOWN 46800 N. HIGHWAY 101 | 20200315 | 623 | 851911 | 323 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 2263 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0032241 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 2499 | 20200315 | 634 | 851917 | 794 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 12704 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032250 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 4943 | 20200315 | 836 | 852070 | 249 | Distribution Circuit | Vegetation | Tree - fell into line | 113 | 10545 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032249 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOPLAND-1101 | 42251101 | FUSE | 5865 | 20200816 | 1503 | 1013103 | 434 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 19530 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 20-0085153 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LUCERNE-1106 | 43351106 | RECLOSER | 38632 | 20200816 | 552 | 1010933 | 560 | Distribution Circuit | Vegetation | Tree - fell into line | 259 | 145040 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0084718 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER | 64118 | 20201025 | 2041 | 1127408 | 956 | Distribution Circuit | Vegetation | Tree - branch fell on line | 634 | 604799 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0113188 | OH | Sus | 0 | 2020 | OCT | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 1817 | 20210118 | 248 | 1212078 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3600 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0009573 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | KONOCTI-1102 | 43311102 | RECLOSER | 64664 | 20210119 | 142 | 1214075 | 818 | Distribution Circuit | Vegetation | Tree - fell into line | 305 | 100272 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0010034 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 37484 | 20210119 | 546 | 1214919 | 1057 | Distribution Circuit | Vegetation | Tree - fell into line | 319 | 80153 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0010215 | OH | Sus | 0 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 6865 | 20210126 | 1541 | 1226346 | 289 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 27455 | Clear-32-90 F | Conductor, Overhead | On Ground | 21-0014749 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 2540 | 20210126 | 1708 | 1226433 | 8712 | Distribution Circuit | Vegetation | Tree - fell into line | 347 | 215664 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0014752 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER | 75970 | 20210126 | 1255 | 1226028 | 235 | Distribution Circuit | Equipment Failure/Involved | Overhead | 210 | 7772 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0014550 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 63170 | 20210128 | 1745 | 1240385 | 222 | Distribution Circuit | Vegetation | Tree - fell into line | 146 | 32412 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0017859 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | MAPLE CREEK-1101 | 192101101 | OCB | 1101/2 | 20210804 | 55 | 1433291 | 102 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 150 | 6191 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0099421 | OH | Sus | 0 | 2021 | AUG | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 5681 | 20211017 | 1502 | 1499622 | 533 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 5330 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0132067 | OH | Sus | 31554914 | 2021 | OCT | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | OTHER | 4571 | 20211024 | 213 | 1507503 | 634 | Distribution Circuit | Vegetation | Tree - fell into line | 130 | 82420 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135570 | OH | Sus | 0 | 2021 | OCT | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3909 | 20211024 | 750 | 1508616 | 209 | Distribution Circuit | Vegetation | Tree - branch fell on line | 141 | 5920 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135839 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 7253 | 20211024 | 710 | 1508214 | 301 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 5117 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135917 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1757 | 20211024 | 736 | 1508483 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 8704 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136152 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1879 | 20211024 | 1149 | 1509238 | 391 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 3796 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136049 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | FUSE | 2603 | 20211024 | 605 | 1507762 | 658 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 27636 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135812 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 502837 | 20211025 | 1310 | 1519411 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 325 | Clear-32-90 F | Conductor, Overhead | On Ground | 21-0137448 | OH | Sus | 0 | 2021 | OCT | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER | WIRE DOWN 2 SS/OF 8035 | 20211213 | 319 | 1565670 | 478 | Distribution Circuit | Vegetation | Tree - fell into line | 375 | 163972 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0156920 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1607 | 20211215 | 1517 | 1572900 | 363 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1815 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158512 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HARRIS-1109 | 192431109 | FUSE | 893 | 20211215 | 1127 | 1572477 | 344 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 9632 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158440 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HUMBOLDT BAY-1102 | 192341102 | FUSE | 4301 | 20211215 | 1135 | 1572633 | 425 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 16575 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158436 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 2853 | 20211215 | 1046 | 1572419 | 347 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 15946 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158432 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 461681 | 20211225 | 158 | 1581130 | 714 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 19278 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160523 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | RECLOSER | 2600 | 20211225 | 2353 | 1581956 | 540 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 22232 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160664 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 8049 | 20211226 | 1213 | 1582444 | 467 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1868 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160770 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 6423 | 20211226 | 1324 | 1582635 | 293 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 8204 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160782 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | FUSE | 43757 | 20211227 | 246 | 1585593 | 2427 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4854 | Clear-32-90F | Conductor, Overhead | On Ground | 21-0160942 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1102 | 42661102 | FUSE | 1765 | 20211227 | 149 | 1583825 | 501 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 60120 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160947 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | OTHER | 6779 | 20211227 | 1228 | 1585745 | 329 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1316 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0161157 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 2007 | 20211227 | 709 | 1584730 | 306 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 12240 | Clear-32-90F | Conductor, Overhead | On Ground | 21-0161012 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 2500 | 20220907 | 1502 | 1804705 | 413 | Distribution Circuit | Vegetation | Tree - fell into line | 452 | 165918 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0107533 | OH | Sus | 31615353 | 2022 | SEP | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER | 79628 | 20221210 | 409 | 1880294 | 517 | Distribution Circuit | Vegetation | Tree - fell into line | 371 | 152117 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138047 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 8721 | 20221210 | 542 | 1880333 | 278 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 6672 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138072 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 6645 | 20221210 | 426 | 1880375 | 650 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 7800 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138069 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | OTHER | WIRE DOWN 1 LD SIDE 215049057372 | 20221210 | 611 | 1880349 | 526 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 10729 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138077 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2519 | 20221210 | 248 | 1880253 | 841 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 10682 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 22-0138343 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER | 7514 | 20221210 | 118 | 1880153 | 815 | Distribution Circuit | Vegetation | Tree - fell into line | 1274 | 699327 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138032 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 37506 | 20221231 | 1519 | 1904736 | 411 | Distribution Circuit | Equipment Failure/Involved | Overhead | 84 | 20742 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142634 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | CALPELLA-1101 | 43411101 | RECLOSER | 542 | 20230104 | 631 | 1912349 | 5182 | Distribution Circuit | Vegetation | Tree - fell into line | 390 | 173125 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0005533 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3139 | 20230104 | 635 | 1912357 | 398 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 21492 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0005593 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 8229 | 20230104 | 754 | 1913135 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 586 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0005723 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 364133 | 20230104 | 823 | 1913458 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 7504 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0005797 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | MENDOCINO-1101 | 42951101 | RECLOSER | 48750 | 20230104 | 1140 | 1913604 | 4713 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 27967 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0005861 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | JUMPER | OJ'S 2 SS OF MTR 1008917383 | 20230107 | 1037 | 1926384 | 441 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 882 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0008775 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3063 | 20230109 | 359 | 1935576 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 23230 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0010804 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | JUMPER | OJS 1 SPAN S/S OF FUCO 7593 | 20230109 | 815 | 1937153 | 540 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1080 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0010931 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 3 | LAYTONVILLE-1102 | 42681102 | FUSE | 2583 | 20230109 | 1238 | 1937492 | 261 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1566 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0011200 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3291 | 20230110 | 748 | 1943475 | 606 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 10908 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0012134 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LUCERNE-1106 | 43351106 | FUSE | 4131 | 20230110 | 1110 | 1944767 | 282 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 1128 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0012389 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE | 821 | 20230110 | 533 | 1943137 | 790 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 31366 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0012160 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 1855 | 20230110 | 56 | 1939843 | 1000 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 32000 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0012104 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3287 | 20230114 | 650 | 1952957 | 357 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 22134 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015919 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER | 69032 | 20230114 | 949 | 1953753 | 584 | Distribution Circuit | Vegetation | Tree - fell into line | 126 | 73584 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0016021 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1102 | 192461102 | RECLOSER | 55612 | 20230114 | 701 | 1952925 | 330 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 9240 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015866 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1260 | 20230114 | 637 | 1952832 | 447 | Distribution Circuit | Vegetation | Tree - branch fell on line | 96 | 20272 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015849 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 600433 | 20230114 | 810 | 1953177 | 662 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6620 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016075 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1122 | 192321122 | OTHER | WIRE DOWN, 3 SPANS LD SIDE | 20230114 | 727 | 1954161 | 767 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1311 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016123 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | OTHER | WIRE DOWN 16 LD SIDE 202293 | 20230114 | 633 | 1952847 | 557 | Distribution Circuit | Vegetation | Tree - fell into line | 1146 | 336874 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015853 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | JUMPER | WIRE DOWN 10 SPANS S/E/OF 8331 | 20230114 | 655 | 1952901 | 197 | Distribution Circuit | Vegetation | Tree - fell into line | 1109 | 89069 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015863 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | MENDOCINO-1101 | 42951101 | RECLOSER | 48750 | 20230114 | 659 | 1952917 | 352 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 14204 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015859 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | RECLOSER | 2600 | 20230114 | 842 | 1953415 | 11 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 836 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015950 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | FUSE | 2625 | 20230114 | 903 | 1953566 | 288 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2299 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015973 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER | 64118 | 20230114 | 709 | 1952931 | 529 | Distribution Circuit | Equipment Failure/Involved | Overhead | 652 | 191492 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015868 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | JUMPER | WIRE DOWN LD SIDE METER # 1009745169 | 20230114 | 654 | 1953656 | 680 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1770 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015998 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | RECLOSER | 528344 | 20230116 | 805 | 1957295 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 61712 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0017014 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 7287 | 20230116 | 1526 | 1958442 | 217 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 3689 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0017317 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3279 | 20230221 | 1055 | 1990124 | 513 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 7290 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0031017 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 1319 | 20230221 | 1057 | 1990128 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1320 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0031177 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 4399 | 20230221 | 1328 | 1991346 | 373 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2611 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0031467 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1102 | 192461102 | RECLOSER | 1102/2 | 20230223 | 851 | 1999038 | 624 | Distribution Circuit | Vegetation | Tree - fell into line | 248 | 70532 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0032941 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1899 | 20230223 | 520 | 1998840 | 678 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 7458 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0033088 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 6625 | 20230224 | 1036 | 2005092 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 750 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0034009 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 1767 | 20230224 | 1008 | 2004907 | 524 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4192 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0034056 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | RECLOSER | 34008 | 20230224 | 31 | 2001317 | 1168 | Distribution Circuit | Vegetation | Tree - fell into line | 571 | 430706 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0033529 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | KONOCTI-1102 | 43311102 | OTHER | WIRE DOWN SS OF CGC#217743946937 | 20230227 | 1543 | 2012905 | 2843 | Distribution Circuit | Environmental/External | Ice or snow | 1183 | 109614 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0036652 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER | 640888 | 20230227 | 812 | 2011373 | 465 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 45105 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0036118 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 1999 | 20230227 | 1009 | 2011737 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 28755 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0036509 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | OTHER | WIRE DOWN 13 SP LD SIDE OF 4557 | 20230228 | 551 | 2014155 | 396 | Distribution Circuit | Vegetation | Tree - fell into line | 229 | 13944 | Overcast-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0037087 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | Yes
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3769 | 20230228 | 702 | 2019853 | 3467 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 52005 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0038783 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER | 76498 | 20230228 | 1115 | 2014256 | 220 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 5060 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0037272 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 91810 | 20230228 | 442 | 2014119 | 808 | Distribution Circuit | Equipment Failure/Involved | Overhead | 811 | 393278 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0037049 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 7801 | 20230309 | 1609 | 2027935 | 115 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 805 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0042317 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 1855 | 20230309 | 1434 | 2027784 | 203 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 6496 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0042311 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1298 | 20230314 | 1224 | 2038408 | 455 | Distribution Circuit | Vegetation | Tree - fell into line | 914 | 387465 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0044999 | OH | Sus | 0 | 2023 | MAR | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 1931 | 20230314 | 900 | 2035483 | 520 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4680 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0044611 | OH | Sus | 0 | 2023 | MAR | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 8652 | 20230314 | 1203 | 2038135 | 180 | Distribution Circuit | Vegetation | Tree - fell into line | 254 | 45016 |  | Conductor, Overhead | Broken, wire on ground | 23-0044947 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 7461 | 20230314 | 1010 | 2043726 | 475 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2850 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0045651 | OH | Sus | 0 | 2023 | MAR | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 4475 | 20230314 | 713 | 2035294 | 362 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 4706 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0044559 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 4053 | 20230314 | 910 | 2035433 | 372 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 22320 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0044660 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 5085 | 20230314 | 1311 | 2040093 | 425 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 2585 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0045438 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 1363 | 20230314 | 1058 | 2036339 | 330 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 18810 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0044894 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | FUSE | 7167 | 20230321 | 1128 | 2054126 | 302 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 906 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0049334 | OH | Sus | 31640137 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | FUSE | 623 | 20130408 | 750 | 769920 | 690 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 31274 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0022604 | OH | Sus | 30988242 | 2013 | APR | Yes | Line to Ground | Yes
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 8321 | 20131122 | 721 | 911109 | 984 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3936 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078697 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 2663 | 20131122 | 210 | 910505 | 795 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 795 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0078272 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
NORTH BAY | Tier 2 | SILVERADO-2104 | 43432104 | SECTIONALIZER | 7917 | 20131122 | 29 | 910249 | 946 | Distribution Circuit | Vegetation | Tree - fell into line | 225 | 198570 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0078276 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 3345 | 20131122 | 218 | 910590 | 1043 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 46101 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078295 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
NORTH BAY | Tier 2 | PUEBLO-2103 | 43292103 | FUSE | 5479 | 20140824 | 329 | 1071789 | 1156 | Distribution Circuit | Environmental/External | Earthquake | 9 | 10404 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0052765 | OH | Sus | 0 | 2014 | AUG | Yes | Line to Ground | Yes
NORTH BAY | Tier 2 | PUEBLO-1104 | 43291104 | FUSE | 1091 | 20141203 | 1448 | 1123622 | 677 | Distribution Circuit | Vegetation | Tree - bark fell into line | 16 | 10832 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073572 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 5561 | 20141203 | 243 | 1121645 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3252 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073189 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 463 | 20141203 | 842 | 1122049 | 423 | Distribution Circuit | Vegetation | Tree - branch fell on line | 124 | 14652 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073264 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
NORTH BAY | Tier 2 | ALTO-1125 | 42031125 | FUSE | 5173 | 20141211 | 727 | 1130628 | 1498 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 55426 | Heavy rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0075690 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH BAY | Tier 2 | ALTO-1125 | 42031125 | FUSE | 1207 | 20141211 | 601 | 1129696 | 1986 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 25053 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075862 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
NORTH BAY | Tier 2 | BOLINAS-1101 | 42261101 | RECLOSER | 504 | 20141211 | 51 | 1128816 | 2253 | Distribution Circuit | Vegetation | Tree - fell into line | 820 | 179748 | Heavy rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0074792 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
NORTH BAY | Tier 2 | BOLINAS-1101 | 42261101 | RECLOSER | 1232 | 20141211 | 1734 | 1135428 | 773 | Distribution Circuit | Equipment Failure/Involved | Other | 415 | 320761 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075789 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 8321 | 20141211 | 946 | 1132435 | 344 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1376 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075425 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH BAY | Tier 3 | GREENBRAE-1102 | 43091102 | FUSE | 2379 | 20141211 | 1005 | 1132651 | 1773 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 69147 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076269 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3585 | 20141211 | 433 | 1129103 | 772 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 14668 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075216 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 7467 | 20141211 | 433 | 1132169 | 772 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5404 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075224 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1973 | 20141211 | 800 | 1131786 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 21800 | Strong winds-Below 32 F | Conductor, Overhead | On Ground | 14-0075312 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 4965 | 20141211 | 727 | 1130627 | 423 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 10152 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075400 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | RECLOSER | 1250 | 20141211 | 527 | 1129451 | 1133 | Distribution Circuit | Equipment Failure/Involved | Other | 19 | 19709 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074913 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 4505 | 20141211 | 847 | 1131567 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 3712 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075242 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 4585 | 20141211 | 1736 | 1135264 | 1475 | Distribution Circuit | Vegetation | Tree - branch fell on line | 70 | 103250 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075853 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 6841 | 20141212 | 1053 | 1138059 | 382 | Distribution Circuit | Equipment Failure/Involved | Other | 32 | 12224 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076370 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | FUSE | 2147 | 20141230 | 1432 | 1152819 | 501 | Distribution Circuit | Equipment Failure/Involved | Other | 63 | 31563 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0079431 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH BAY | Tier 2 | CALISTOGA-1101 | 42711101 | FUSE | 9541 | 20141230 | 1534 | 1153473 | 807 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 8877 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0079308 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | OTHER |  | 20141230 | 1651 | 1154541 | 1274 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 1274 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0079480 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH BAY | Tier 3 | SILVERADO-2105 | 43432105 | FUSE | 3363 | 20141230 | 1654 | 1154549 | 1271 | Distribution Circuit | Equipment Failure/Involved | Other | 36 | 26696 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0079407 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | FUSE | 5869 | 20150206 | 2201 | 1178926 | 1716 | Distribution Circuit | Equipment Failure/Involved | Other | 90 | 154440 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011343 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE | 3523 | 20150206 | 1315 | 1175327 | 1440 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 113760 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010514 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE | 54471 | 20150206 | 2210 | 1179101 | 2104 | Distribution Circuit | Equipment Failure/Involved | Other | 9 | 18936 | Strong winds-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0010738 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER | 602 | 20150206 | 417 | 1173145 | 801 | Distribution Circuit | Vegetation | Tree - fell into line | 155 | 124155 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009790 | OH | Sus | 31133058 | 2015 | FEB | Yes | Line to Line | Yes
NORTH BAY | Tier 2 | PUEBLO-2103 | 43292103 | FUSE | 1391 | 20150206 | 1514 | 1176092 | 644 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3098 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010393 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 3323 | 20150206 | 1924 | 1177915 | 1839 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 33102 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011247 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 6745 | 20150206 | 1332 | 1175419 | 298 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 5662 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010265 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 2743 | 20150206 | 1919 | 1177855 | 1306 | Distribution Circuit | Vegetation | Tree - branch fell on line | 85 | 65650 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010897 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | OTHER |  | 20150206 | 527 | 1173403 | 613 | Distribution Circuit | Vegetation | Tree - branch fell on line | 233 | 125603 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on object | 15-0009841 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 953 | 20150206 | 1358 | 1175657 | 779 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 39128 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010282 | OH | Sus | 0 | 2015 | FEB | Yes | Three Phase Fault | Yes
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 2629 | 20150206 | 1737 | 1176969 | 1318 | Distribution Circuit | Vegetation | Tree - branch fell on line | 64 | 84352 | Strong winds-32 - 90 F | Cutout, Fused, Distribution | Broken, wire on ground | 15-0011262 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH BAY | Tier 2 | ALTO-1125 | 42031125 | FUSE | 2243 | 20150207 | 1839 | 1181788 | 201 | Distribution Circuit | Equipment Failure/Involved | Other | 357 | 67711 | Strong winds-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0011368 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1703 | 20150207 | 5 | 1179608 | 2376 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 3429 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on object | 15-0010826 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1677 | 20150207 | 1519 | 1180503 | 2862 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 44011 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011361 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH BAY | Tier 2 | SAN RAFAEL-1109 | 42011109 | FUSE | 2213 | 20150207 | 54 | 1179707 | 1396 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 36296 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011001 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH BAY | Tier 2 | SAN RAFAEL-1109 | 42011109 | OTHER |  | 20150207 | 855 | 1180841 | 400 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 1925 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011143 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
NORTH BAY | Tier 2 | SILVERADO-2104 | 43432104 | FUSE | 489 | 20150207 | 338 | 1179963 | 942 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 8478 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010991 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 863 | 20150208 | 2359 | 1185454 | 2623 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 10492 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011936 | OH | Sus | 0 | 2015 | FEB | Yes | Three Phase Fault | Yes
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 2387 | 20150208 | 1803 | 1183583 | 364 | Distribution Circuit | Vegetation | Tree - fell into line | 205 | 74620 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011721 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1891 | 20150608 | 2050 | 1246905 | 990 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 5347 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0039553 | OH | Sus | 0 | 2015 | JUN | Yes | Line to Ground | Yes
NORTH BAY | Tier 2 | PUEBLO-1105 | 43291105 | FUSE | 7553 | 20150608 | 1000 | 1245524 | 229 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 794 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0039246 | OH | Sus | 42401796 | 2015 | JUN | Yes | Line to Ground | Yes
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE | 2227 | 20151213 | 849 | 1360540 | 471 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5652 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 15-0084782 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE | 3979 | 20151213 | 1505 | 1362526 | 66 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 132 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084945 | OH | Sus | 0 | 2015 | DEC | Yes | None | Yes | No
NORTH BAY | Tier 2 | BOLINAS-1101 | 42261101 | RECLOSER | 504 | 20151213 | 843 | 1360524 | 853 | Distribution Circuit | Vegetation | Tree - fell into line | 820 | 208420 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0084593 | OH | Sus | 42589004 | 2015 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1102 | 42711102 | OTHER | WIRE DOWN AT 1011 TWD 9139 | 20151213 | 928 | s1174426 | 367 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 20027 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084758 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | MONTICELLO-1101 | 43051101 | RECLOSER | 4360 | 20151213 | 829 | 1360465 | 866 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 22516 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 15-0084650 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | JUMPER | WIRE DOWN @ PANORAMIC AND ST JUDE | 20160305 | 1736 | 1417941 | 635 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1297 | 195739 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0017642 | OH | Sus | 0 | 2016 | MAR | Yes | Open Circuit | Yes | Yes
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE | 2249 | 20160305 | 2008 | 1418779 | 1387 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 66576 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on object | 16-0018041 | OH | Sus | 0 | 2016 | MAR | Yes | Three Phase Fault | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3585 | 20160305 | 1045 | 1416501 | 648 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 16601 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017457 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | OTHER | WIRE DOWN @ 8 PINEHILL RD | 20160305 | 2304 | 1420950 | 1793 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 16418 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018142 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | PUEBLO-1105 | 43291105 | FUSE | 1767 | 20160305 | 1453 | 1417281 | 322 | Distribution Circuit | Vegetation | Tree - fell into line | 161 | 46642 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017566 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 311 | 20160305 | 1449 | 1416818 | 821 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 9031 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0017530 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1145 | 20160305 | 1729 | 1417663 | 481 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2886 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017956 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 3583 | 20160305 | 2205 | 1420745 | 1136 | Distribution Circuit | Vegetation | Tree - fell into line | 191 | 112494 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018138 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 2499 | 20160305 | 2012 | 1418810 | 935 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 15895 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017902 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 797 | 20160305 | 1831 | 1418159 | 1441 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 138380 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 16-0018152 | OH | Sus | 0 | 2016 | MAR | Yes | Three Phase Fault | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | OTHER | WIRE DOWN @1700 HOWELL MTN RD | 20160305 | 2125 | 1421101 | 1039 | Distribution Circuit | Equipment Failure/Involved | Overhead | 528 | 471460 | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018237 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | OCB | 1101/2 | 20160305 | 2051 | 1419222 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 1211 | 71100 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017833 | OH | Sus | 0 | 2016 | MAR | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 2 | WOODACRE-1102 | 43021102 | JUMPER | OJ LINE SIDE OF 40 DE BURGH DR | 20160305 | 2038 | 1419315 | 1217 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 17038 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 16-0018236 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | CALISTOGA-1102 | 42711102 | OCB | 1102/2 | 20161014 | 2357 | 1560534 | 297 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2112 | 151605 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072389 | OH | Sus | 0 | 2016 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 4497 | 20161014 | 1102 | 1559009 | 299 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 7375 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072063 | OH | Sus | 0 | 2016 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | SILVERADO-2102 | 43432102 | SWITCH | 5101 | 20161014 | 1024 | 1559279 | 775 | Distribution Circuit | Equipment Failure/Involved | Overhead | 354 | 258709 | Overcast-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0072113 | OH | Sus | 0 | 2016 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | ALTO-1122 | 42031122 | FUSE | 1075 | 20170103 | 2301 | 1617421 | 625 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 18323 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003388 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | RECLOSER | 902 | 20170103 | 1852 | 1616469 | 2148 | Distribution Circuit | Equipment Failure/Involved | Overhead | 202 | 396358 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0003201 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE | 54471 | 20170103 | 1917 | 1616573 | 827 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 8270 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003346 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 5377 | 20170103 | 1746 | 1616324 | 638 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 12760 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003331 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | OTHER | WIRE DOWN 31 FERNHILL | 20170103 | 2215 | 1617093 | 559 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 10360 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0003348 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 797 | 20170103 | 1901 | 1616550 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 48680 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003221 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | ALTO-1122 | 42031122 | FUSE | 6385 | 20170108 | 725 | 1623105 | 1631 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 45668 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005176 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | ALTO-1122 | 42031122 | FUSE | 1073 | 20170108 | 915 | 1623260 | 757 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 102195 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005514 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE | 6333 | 20170108 | 1251 | 1626580 | 1965 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 180780 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005562 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | Yes
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 731 | 20170108 | 1200 | 1625954 | 770 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 34650 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0005267 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 9415 | 20170108 | 1845 | 1628653 | 1860 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1860 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005607 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 473 | 20170108 | 1139 | 1630079 | 2276 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 31864 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005870 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 757 | 20170108 | 840 | 1623734 | 957 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 33495 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 17-0005059 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 4479 | 20170108 | 909 | 1624182 | 1866 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 40413 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005063 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3261 | 20170108 | 834 | 1623684 | 846 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2428 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005182 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 311 | 20170108 | 1056 | 1629785 | 5800 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 61300 | Strong Winds-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005782 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1945 | 20170108 | 1632 | 1628054 | 2930 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 43950 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005873 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1143 | 20170108 | 726 | 1623182 | 2694 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 33654 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005183 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 3343 | 20170108 | 1526 | 1627922 | 1307 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 32028 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005512 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | PUEBLO-2103 | 43292103 | FUSE | 9275 | 20170108 | 1116 | 1628573 | 899 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2697 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005589 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 3583 | 20170108 | 1222 | 1626146 | 3133 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 164801 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005592 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | OTHER | WIRE DOWN | 20170108 | 107 | 1622436 | 412 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1648 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004893 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 3913 | 20170108 | 713 | 1622984 | 1127 | Distribution Circuit | Vegetation | Tree - fell into line | 408 | 60186 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005004 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | RECLOSER | 322 | 20170108 | 1015 | 1624812 | 1337 | Distribution Circuit | Vegetation | Tree - fell into line | 3074 | 752850 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0005119 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2105 | 43432105 | FUSE | 835 | 20170108 | 1107 | 1625288 | 1679 | Distribution Circuit | Vegetation | Tree - branch fell on line | 143 | 293696 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005447 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | STAFFORD-1101 | 43201101 | RECLOSER | 1298 | 20170108 | 1331 | 1626941 | 1004 | Distribution Circuit | Vegetation | Tree - fell into line | 2023 | 332436 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005360 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 2387 | 20170108 | 703 | 1623118 | 2241 | Distribution Circuit | Vegetation | Tree - fell into line | 203 | 454923 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004985 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | Yes
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | OCB | 1102/2 | 20170108 | 1219 | 1623506 | 798 | Distribution Circuit | Vegetation | Tree - fell into line | 2689 | 563462 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005332 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | OTHER | WIRE DOWN MADERA AND LONE TREE | 20170109 | 435 | 1630371 | 975 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 37810 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005937 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 5411 | 20170109 | 1702 | 1631874 | 486 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 6804 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006273 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2102 | 43432102 | FUSE | 2093 | 20170109 | 723 | 1631788 | 3382 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 37202 | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006287 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE | 3115 | 20170110 | 1913 | 1636046 | 699 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 8388 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007204 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 683 | 20170110 | 1451 | 1635050 | 2190 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 37136 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0007563 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE | 9195 | 20170110 | 2255 | 1638828 | 2640 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 179520 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007648 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE | 6143 | 20170110 | 1455 | 1634935 | 2762 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 16572 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008265 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | LAS GALLINAS A-1105 | 42991105 | FUSE | 3221 | 20170110 | 1824 | 1635375 | 1566 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 7830 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007214 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER | 602 | 20170110 | 8 | 1632412 | 1034 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 138556 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006360 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5469 | 20170110 | 1537 | 1634107 | 585 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 39780 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006843 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | OTHER | WIRE DOWN 43 ALLYNN RD | 20170110 | 1835 | 1635382 | 393 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 13473 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006947 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | RECLOSER | 1250 | 20170110 | 1921 | 1638850 | 2312 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 43928 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007429 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 7341 | 20170110 | 622 | 1632520 | 686 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 10290 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006405 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | SWITCH | 4397 | 20170110 | 1439 | 1633752 | 1756 | Distribution Circuit | Vegetation | Tree - fell into line | 182 | 93355 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006748 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | OTHER | OJ SS OF 1449 | 20170110 | 1822 | 1636689 | 1041 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1457 | 283939 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007284 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 4419 | 20170110 | 1812 | 1638666 | 1372 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 18964 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007412 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 5369 | 20170110 | 1805 | 1635219 | 2117 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 86797 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008244 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | STAFFORD-1102 | 43201102 | OTHER | WIRE DOWN W/O MTR 100837551 | 20170110 | 1034 | 1632937 | 476 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 1936 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006551 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 5827 | 20170110 | 1535 | 1634078 | 1825 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 33458 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006778 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | ALTO-1125 | 42031125 | FUSE | 5189 | 20170111 | 2245 | 1640827 | 380 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 6460 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008222 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 2641 | 20170111 | 633 | 1638794 | 803 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4015 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007601 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 5803 | 20170111 | 722 | 1639211 | 1110 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 22200 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007902 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 5461 | 20170111 | 800 | 1639386 | 2090 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12540 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007915 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 3805 | 20170111 | 1728 | 1640464 | 27019 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 79402 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008208 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 9229 | 20170111 | 1748 | 1640498 | 2727 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 18887 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0008211 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 3391 | 20170111 | 1802 | 1640528 | 3148 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 18888 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008261 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE | 585 | 20170111 | 1351 | 1640898 | 1724 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 6896 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008240 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE | 1589 | 20170111 | 532 | 1638656 | 1211 | Distribution Circuit | Vegetation | Tree - fell into line | 175 | 70469 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007473 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 4475 | 20170111 | 622 | 1638730 | 438 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 22776 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007427 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER | 75686 | 20170118 | 1820 | 1648052 | 1216 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 229787 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010296 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 2627 | 20170118 | 1834 | 1648173 | 550 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 44000 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010389 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | BOLINAS-1101 | 42261101 | RECLOSER | 806 | 20170120 | 217 | 1652054 | 171 | Distribution Circuit | Environmental/External | Flood/Erosion | 345 | 58995 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011176 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5469 | 20170120 | 431 | 1652308 | 566 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 38488 | Overcast-Heavy Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011252 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 1455 | 20170120 | 1828 | 1655055 | 2800 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5600 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011762 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3585 | 20170122 | 310 | 1658395 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 14170 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012750 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 1763 | 20170122 | 313 | 1658356 | 1068 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8544 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0012834 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | ALTO-1120 | 42031120 | FUSE | 941 | 20170207 | 1305 | 1680203 | 448 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1792 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018590 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE | 2395 | 20170207 | 423 | 1677751 | 849 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 40814 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018116 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE | 3121 | 20170207 | 513 | 1677921 | 3687 | Distribution Circuit | Environmental/External | Flood/Erosion | 1840 | 294046 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0018157 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 3805 | 20170207 | 503 | 1677878 | 1232 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 23408 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018453 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE | 9195 | 20170207 | 501 | 1678224 | 4186 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 189914 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018290 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
NORTH BAY | Tier 2 | SAN RAFAEL-1105 | 42011105 | FUSE | 5753 | 20170207 | 555 | 1678003 | 357 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 4641 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018180 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | RECLOSER | 404 | 20170207 | 616 | 1678087 | 1189 | Distribution Circuit | Vegetation | Tree - fell into line | 831 | 300856 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018209 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 1089 | 20170207 | 126 | 1677340 | 853 | Distribution Circuit | Vegetation | Tree - fell into line | 228 | 100460 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018072 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | Yes
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 7103 | 20170207 | 322 | 1677630 | 803 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2409 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018092 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1579 | 20170209 | 858 | 1682925 | 1169 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 14028 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019421 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3585 | 20170209 | 1337 | 1683477 | 1207 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 31382 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019470 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 5827 | 20170209 | 1333 | 1683536 | 792 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 18216 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019512 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | ALTO-1120 | 42031120 | FUSE | 941 | 20170217 | 733 | 1691532 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1576 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021922 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 473 | 20170217 | 908 | 1692915 | 2859 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 40026 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022009 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | PUEBLO-1104 | 43291104 | RECLOSER | 1304 | 20170217 | 1114 | 1694844 | 3406 | Distribution Circuit | Equipment Failure/Involved | Overhead | 156 | 266906 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022594 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3585 | 20170218 | 1351 | 1699976 | 673 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 17498 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023166 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 7103 | 20170218 | 709 | 1699027 | 1354 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4062 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022923 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE | 6333 | 20170220 | 2200 | 1706294 | 1332 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 121656 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024649 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1102 | 42711102 | JUMPER | UN-NUMBERED FUCO | 20170220 | 2309 | 1707410 | 1086 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2172 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025059 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER | 602 | 20170220 | 154 | 1702308 | 763 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 113687 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023603 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5445 | 20170220 | 1610 | 1703959 | 1191 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 9528 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024023 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 3583 | 20170220 | 1709 | 1704507 | 974 | Distribution Circuit | Vegetation | Tree - fell into line | 153 | 62117 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023993 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 2 | SILVERADO-2102 | 43432102 | FUSE | 1601 | 20170220 | 1615 | 1704065 | 735 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 8550 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023987 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 4019 | 20170220 | 2230 | 1706528 | 974 | Distribution Circuit | Equipment Failure/Involved | Overhead | 87 | 32258 | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024727 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 4535 | 20170220 | 2115 | 1706127 | 850 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 6800 | Overcast-Fog-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024745 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 1089 | 20170220 | 2052 | 1706016 | 1052 | Distribution Circuit | Equipment Failure/Involved | Overhead | 228 | 77342 | Overcast-Fog-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024264 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 4475 | 20170221 | 732 | 1707705 | 448 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 21952 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025139 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 1455 | 20170221 | 1044 | 1708265 | 651 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1302 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025168 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 3583 | 20170222 | 2317 | 1711480 | 2468 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 128336 | Clear-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025873 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 3345 | 20170222 | 1406 | 1710827 | 572 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 18943 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025669 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | BOLINAS-1101 | 42261101 | OTHER | WIRE DOWN 12 SPANS LOAD SIDE OF 1232 | 20170406 | 1923 | 1746312 | 1682 | Distribution Circuit | Equipment Failure/Involved | Overhead | 477 | 799044 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037454 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | PUEBLO-1105 | 43291105 | OTHER | WIRE ON GRD 1 POLE LD SIDE OF 1767 | 20170406 | 1940 | 1750156 | 1345 | Distribution Circuit | Equipment Failure/Involved | Overhead | 211 | 219306 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037692 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | RECLOSER | 1210 | 20170406 | 1058 | 1745410 | 844 | Distribution Circuit | Vegetation | Tree - fell into line | 544 | 166949 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037052 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 479 | 20170406 | 2229 | 1748349 | 1361 | Distribution Circuit | Equipment Failure/Involved | Overhead | 266 | 50506 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037447 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | MONTICELLO-1101 | 43051101 | OTHER | WIRE DOWN SS OF 9769 | 20170407 | 723 | 1751153 | 3107 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 8804 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037995 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE | 3453 | 20170407 | 1754 | 1751460 | 2762 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 24858 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038061 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | SAN RAFAEL-1107 | 42011107 | FUSE | 5993 | 20170407 | 1036 | 1750502 | 665 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 26600 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037800 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 1385 | 20170407 | 207 | 1749185 | 1963 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 111644 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037727 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 479 | 20170407 | 2334 | 1752201 | 1053 | Distribution Circuit | Equipment Failure/Involved | Overhead | 266 | 57355 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038178 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | GREENBRAE-1103 | 43091103 | FUSE | 4997 | 20170911 | 420 | 1874799 | 548 | Distribution Circuit | Vegetation | Tree - branch fell on line | 80 | 13896 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0077470 | OH | Sus | 31350105 | 2017 | SEP | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | CALISTOGA-1101 | 42711101 | FUSE | 8339 | 20171008 | 1841 | 1893704 | 20024 | Distribution Circuit | Equipment Failure/Involved | Overhead | 62 | 1241488 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085175 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | CALISTOGA-1101 | 42711101 | RECLOSER | 890 | 20171008 | 2202 | 1893951 | 19823 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 149 | 1855187 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085239 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | CALISTOGA-1101 | 42711101 | JUMPER | 1/E/OF 773 | 20171008 | 2120 | 1898920 | 24194 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 3 | 66878 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086476 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | SWITCH | 4879 | 20171008 | 2202 | 1903474 | 21238 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 42476 | Clear-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0088360 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | CALISTOGA-1101 | 42711101 | FUSE | 1843 | 20171008 | 2202 | 1903598 | 19950 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 39900 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0088407 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 1463 | 20171008 | 2324 | 1908131 | 21147 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 63441 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0089778 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | PUEBLO-1104 | 43291104 | SWITCH | 9595 | 20171008 | 2259 | 1901273 | 19761 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 513786 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087501 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | PUEBLO-1105 | 43291105 | FUSE | 7565 | 20171008 | 2220 | 1899635 | 17025 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 34050 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086893 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1143 | 20171008 | 2225 | 1894077 | 21285 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 617265 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086273 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER | 722 | 20171008 | 2149 | 1893975 | 2774 | Distribution Circuit | Vegetation | Tree - branch fell on line | 526 | 1416648 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085216 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE | 589 | 20171009 | 11 | 1895660 | 5298 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 84768 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085393 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | MONTICELLO-1101 | 43051101 | RECLOSER | 93384 | 20171009 | 138 | 1900638 | 10906 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 535 | 5266351 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087310 | OH | Sus | 0 | 2017 | OCT | Yes | Three Phase Fault | Yes | No
NORTH BAY | Tier 2 | PUEBLO-1105 | 43291105 | FUSE | 567 | 20171009 | 154 | 1902561 | 16497 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 41 | 676377 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087984 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2105 | 43432105 | JUMPER | O/J 3 SPANS W/OF 9319 | 20171014 | 2018 | 1901035 | 972 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2916 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087429 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 5073 | 20171204 | 921 | 1934647 | 620 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2480 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099600 | OH | Sus | 0 | 2017 | DEC | Yes | Three Phase Fault | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 731 | 20171204 | 911 | 1934633 | 454 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 20884 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099617 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 767 | 20171204 | 1121 | 1934978 | 834 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3336 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099624 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 415 | 20171204 | 813 | 1934532 | 954 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 11448 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099647 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 7103 | 20171204 | 1736 | 1935873 | 319 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 957 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099800 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | FUSE | 915 | 20171216 | 908 | 1944195 | 394 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 21670 | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0101966 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | FUSE | 6953 | 20171216 | 939 | 1944273 | 477 | Distribution Circuit | Vegetation | Tree - fell into line | 1792 | 21402 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0101995 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 6075 | 20171216 | 845 | 1944152 | 285 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1425 | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0101947 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1143 | 20171216 | 924 | 1944474 | 1112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 23408 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0102074 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | SAUSALITO-1102 | 42491102 | FUSE | 3033 | 20171216 | 1033 | 1944459 | 481 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 3896 | Clear-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0102014 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | Yes
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | FUSE | 2201 | 20180316 | 108 | 45156 | 620 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 19220 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023225 | OH | Sus | 43301932 | 2018 | MAR | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | JUMPER | OJS 4 SPANS N/O 3654 | 20181108 | 1220 | 211569 | 265 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 265 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0098264 | OH | Sus | 0 | 2018 | NOV | Yes | None | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2103 | 43432103 | FUSE | 3721 | 20181129 | 945 | 228416 | 5925 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 22241 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104940 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 7449 | 20181129 | 727 | 227916 | 554 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 23822 | Overcast-Heavy Rain-Lightning-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104908 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | ALTO-1125 | 42031125 | FUSE | 5191 | 20190106 | 922 | 255021 | 280 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 33600 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005045 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | GREENBRAE-1103 | 43091103 | OTHER | WIRE DOWN @ 1 EDEN LANE STAIRS | 20190106 | 1227 | 255244 | 983 | Distribution Circuit | Vegetation | Tree - fell into line | 406 | 303746 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0005083 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | FUSE | 3141 | 20190116 | 1445 | 267248 | 221 | Distribution Circuit | Vegetation | Tree - branch fell on line | 45 | 9945 | Strong Winds-Heavy Rain-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009817 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE | 2167 | 20190116 | 1714 | 268460 | 1718 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 86010 | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009996 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE | 2227 | 20190116 | 1617 | 267772 | 4060 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 48720 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010130 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1102 | 42711102 | RECLOSER | 634 | 20190116 | 1542 | 267581 | 644 | Distribution Circuit | Vegetation | Tree - fell into line | 597 | 88673 | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009830 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | GREENBRAE-1102 | 43091102 | FUSE | 5301 | 20190116 | 2031 | 270515 | 1272 | Distribution Circuit | Vegetation | Tree - branch fell on line | 104 | 132288 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010784 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | MONTICELLO-1101 | 43051101 | RECLOSER | 630 | 20190116 | 1906 | 272351 | 2859 | Distribution Circuit | Equipment Failure/Involved | Overhead | 141 | 403119 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010528 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1881 | 20190116 | 2144 | 271248 | 2315 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 25465 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010417 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1117 | 20190116 | 1954 | 270323 | 1351 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 26179 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010778 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 2565 | 20190116 | 1633 | 267952 | 1918 | Distribution Circuit | Equipment Failure/Involved | Overhead | 158 | 228868 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010037 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 2753 | 20190116 | 2020 | 272420 | 1442 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 37492 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010556 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 6647 | 20190116 | 1735 | 268629 | 249 | Distribution Circuit | Vegetation | Tree - branch fell on line | 124 | 30876 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009999 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | SAN RAFAEL-1109 | 42011109 | FUSE | 5397 | 20190116 | 2027 | 270621 | 959 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 26852 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010346 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 141 | 20190116 | 2017 | 270487 | 2533 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 15198 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010312 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | STAFFORD-1102 | 43201102 | FUSE | 949 | 20190116 | 1754 | 269292 | 1636 | Distribution Circuit | Vegetation | Tree - branch fell on line | 72 | 117792 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010046 | OH | Sus | 0 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 5605 | 20190116 | 1418 | 267131 | 1824 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 9120 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009786 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 2657 | 20190116 | 1540 | 267467 | 440 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 3488 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009821 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 3603 | 20190116 | 1525 | 267552 | 503 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 24144 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009840 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | WOODACRE-1102 | 43021102 | JUMPER | OJ FEEDING FUCO 1421 | 20190116 | 1523 | 267446 | 550 | Distribution Circuit | Equipment Failure/Involved | Overhead | 511 | 54460 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009925 | OH | Sus | 0 | 2019 | JAN | Yes | Force Out | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | RECLOSER | 137662 | 20190116 | 1930 | 269720 | 1098 | Distribution Circuit | Vegetation | Tree - fell into line | 1046 | 571468 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010122 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 2635 | 20190116 | 2046 | 270625 | 1329 | Distribution Circuit | Vegetation | Tree - bark fell into line | 36 | 47844 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010751 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 3391 | 20190117 | 524 | 272547 | 3171 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 19026 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011067 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | OTHER | WIRE DOWN @ 17 OAK KNOLL AVE | 20190117 | 135 | 272275 | 1645 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1222 | 60277 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010496 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | JUMPER | WIRE DOWN 3 N/OF FUCO 2197 | 20190117 | 422 | 273917 | 1868 | Distribution Circuit | Vegetation | Tree - branch fell on line | 546 | 40233 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011021 | OH | Sus | 0 | 2019 | JAN | Yes | Force Out | Yes | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | JUMPER | O/J MEDWAY AND SAN ANSELMO | 20190117 | 2333 | 275084 | 329 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 8883 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011488 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2102 | 43432102 | SWITCH | 42999 | 20190117 | 149 | 274009 | 973 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 39893 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011023 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2103 | 43432103 | FUSE | 3721 | 20190117 | 651 | 272718 | 1329 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 18606 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011167 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2105 | 43432105 | JUMPER | OJ 3/S/W/OF 5937 | 20190117 | 1035 | 273624 | 2950 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 5900 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010906 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE | 2167 | 20190213 | 2116 | 305746 | 1244 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 18165 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022711 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | BOLINAS-1101 | 42261101 | OTHER | WIRE DOWN 5 S/OF 1803 | 20190213 | 1052 | 303957 | 3231 | Distribution Circuit | Vegetation | Tree - fell into line | 831 | 2532753 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022172 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 757 | 20190213 | 1924 | 305582 | 1032 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 36120 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022565 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | ALTO-1120 | 42031120 | FUSE | 941 | 20190214 | 1719 | 310362 | 1544 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6176 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023559 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE | 701 | 20190214 | 322 | 307396 | 831 | Distribution Circuit | Vegetation | Tree - fell into line | 171 | 119045 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023243 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | Yes
NORTH BAY | Tier 2 | BOLINAS-1101 | 42261101 | OCB | 1101/2 | 20190214 | 822 | 307670 | 3227 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1160 | 122660 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022934 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | BOLINAS-1101 | 42261101 | OTHER | WIRE DOWN @ 78 BOSQUE AVE | 20190214 | 948 | s1422019 | 4632 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 23160 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023654 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | GREENBRAE-1102 | 43091102 | FUSE | 6371 | 20190214 | 1859 | 310675 | 2801 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 33612 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023821 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | LAS GALLINAS A-1105 | 42991105 | RECLOSER | 99904 | 20190214 | 401 | 306699 | 3782 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 224052 | Overcast-Fog-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022798 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | MONTICELLO-1101 | 43051101 | RECLOSER | 654 | 20190214 | 500 | 306973 | 3643 | Distribution Circuit | Vegetation | Tree - fell into line | 220 | 717520 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022832 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3513 | 20190214 | 250 | 308096 | 2386 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 57264 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023067 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1579 | 20190214 | 804 | 307586 | 3266 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 39192 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023235 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1117 | 20190214 | 358 | 306689 | 1012 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 21565 | Overcast-Fog-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022842 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 5543 | 20190214 | 456 | 306898 | 2240 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 20160 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023130 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 4497 | 20190214 | 1205 | 308867 | 728 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 18928 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023178 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER | 632 | 20190214 | 1042 | 308405 | 1359 | Distribution Circuit | Vegetation | Tree - fell into line | 752 | 618261 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023276 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | WOODACRE-1102 | 43021102 | RECLOSER | 1280 | 20190214 | 156 | 306278 | 3606 | Distribution Circuit | Equipment Failure/Involved | Overhead | 729 | 525588 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023143 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 1089 | 20190214 | 233 | 306422 | 2444 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3064 | 402449 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023501 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | TRIP-SAVER | 3121 | 20190216 | 1743 | 314867 | 1285 | Distribution Circuit | Vegetation | Tree - fell into line | 195 | 54393 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024717 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3393 | 20190226 | 2041 | 325274 | 3310 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 49650 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028584 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 53821 | 20190226 | 2107 | 325299 | 253 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1771 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028590 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 757 | 20190226 | 2338 | 325753 | 876 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 30660 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028660 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5683 | 20190226 | 2210 | 325428 | 1211 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6055 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028662 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 5343 | 20190226 | 1607 | 324846 | 1542 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 21171 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028528 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER | 806 | 20190226 | 900 | 324120 | 370 | Distribution Circuit | Equipment Failure/Involved | Overhead | 415 | 65005 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028156 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER | 726 | 20190226 | 1914 | 325146 | 1225 | Distribution Circuit | Vegetation | Tree - fell into line | 351 | 417965 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028529 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 2631 | 20190226 | 1746 | 324998 | 1424 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7120 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028517 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 2617 | 20190226 | 1931 | 325159 | 1344 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 6720 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028561 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | WOODACRE-1101 | 43021101 | RECLOSER | 96844 | 20190226 | 2203 | 325405 | 694 | Distribution Circuit | Equipment Failure/Involved | Overhead | 274 | 82726 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028591 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | IGNACIO-1105 | 42481105 | FUSE | 6221 | 20190227 | 206 | 326120 | 956 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 42888 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028691 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5467 | 20190610 | 1912 | 404560 | 1503 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3006 | Partly Cloudy-Heat Wave-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0065525 | OH | Sus | 0 | 2019 | JUN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 1189 | 20190923 | 1259 | 606674 | 257 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 771 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0102537 | OH | Sus | 43964150 | 2019 | SEP | Yes | None | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | OTHER | WIRE DOWN 2 SPANS LD SIDE OF 947917 | 20191126 | 1802 | 716982 | 301 | Distribution Circuit | Equipment Failure/Involved | Overhead | 391 | 33779 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0129529 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 2117 | 20200117 | 1622 | 765121 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 405 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010955 | OH | Sus | 44159086 | 2020 | JAN | Yes | Force Out | Yes | No
NORTH BAY | Tier 3 | ALTO-1122 | 42031122 | FUSE | 3897 | 20200209 | 947 | 781825 | 382 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 34442 | Clear-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0019092 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | SILVERADO-2105 | 43432105 | OTHER | WIRE DOWN 4 SPANS LD SIDE OF 3403 | 20200209 | 1440 | 786619 | 1413 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 6539 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0019668 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | STAFFORD-1102 | 43201102 | RECLOSER | 1202 | 20200817 | 300 | 1014482 | 965 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 20290 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0085412 | OH | Sus | 44437092 | 2020 | AUG | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | CALISTOGA-1101 | 42711101 | RECLOSER | 890 | 20210118 | 530 | 1212104 | 466 | Distribution Circuit | Vegetation | Tree - fell into line | 161 | 75026 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0009559 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 6549 | 20210118 | 854 | 1212242 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4230 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0009698 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | CALISTOGA-1102 | 42711102 | RECLOSER | 131531 | 20210118 | 435 | 1212094 | 495 | Distribution Circuit | Vegetation | Tree - branch fell on line | 70 | 7113 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0009557 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | PUEBLO-1105 | 43291105 | OTHER | WIRE DOWN TAP W/OF 9259 | 20210118 | 537 | 1212105 | 428 | Distribution Circuit | Vegetation | Tree - fell into line | 148 | 34744 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0009586 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5469 | 20210119 | 421 | 1214621 | 845 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 56615 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0010406 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER | 632 | 20210119 | 331 | 1214440 | 537 | Distribution Circuit | Vegetation | Tree - fell into line | 739 | 356565 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0010126 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2105 | 43432105 | FUSE | 5439 | 20210119 | 441 | 1214705 | 800 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4000 | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010761 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | JUMPER | WIRE DOWN 4 SPAN SS OF 4307 | 20210119 | 216 | 1214175 | 949 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2813 | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010771 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | OLEMA-1101 | 42291101 | FUSE | 311 | 20211215 | 1408 | 1572800 | 578 | Distribution Circuit | Vegetation | Tree - fell into line | 113 | 43607 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158500 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | RECLOSER | 902 | 20221210 | 642 | 1880379 | 318 | Distribution Circuit | Vegetation | Tree - branch fell on line | 204 | 61243 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138070 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 2565 | 20221210 | 726 | 1880453 | 796 | Distribution Circuit | Vegetation | Tree - fell into line | 156 | 75252 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138159 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 2565 | 20221220 | 1539 | 1894528 | 328 | Distribution Circuit | Vegetation | Tree - fell into line | 156 | 24548 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0140801 | OH | Sus | 31633601 | 2022 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 2623 | 20230107 | 1656 | 1927206 | 147 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 1617 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0008930 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | JUMPER | OJS 1 SPAN LD SIDE OF CGC 3141091171 | 20230108 | 5 | 1932237 | 1117 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 20809 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0009825 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 2681 | 20230109 | 739 | 1936505 | 511 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 3577 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0010921 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | RECLOSER | 510 | 20230110 | 201 | 1939991 | 985 | Distribution Circuit | Equipment Failure/Involved | Overhead | 391 | 214567 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0011743 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | SAN RAFAEL-1109 | 42011109 | RECLOSER | 418 | 20230110 | 527 | 1942704 | 505 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1779 | 422965 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0011919 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | RECLOSER | 430 | 20230114 | 704 | 1952924 | 626 | Distribution Circuit | Vegetation | Tree - fell into line | 980 | 118325 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015862 | OH | Sus | 35419665 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 2387 | 20230309 | 1814 | 2028496 | 419 | Distribution Circuit | Vegetation | Tree - bark fell into line | 202 | 83225 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0042458 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | WOODACRE-1102 | 43021102 | RECLOSER | 1280 | 20230314 | 1019 | 2035862 | 573 | Distribution Circuit | Equipment Failure/Involved | Overhead | 792 | 343178 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0044682 | OH | Sus | 35431693 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 1640 | 20130408 | 1034 | 769861 | 1693 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 283234 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022592 | OH | Sus | 30988243 | 2013 | APR | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER | 13026 | 20131121 | 1813 | 907875 | 1481 | Distribution Circuit | Vegetation | Tree - fell into line | 166 | 182166 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078087 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 9595 | 20131121 | 845 | 906786 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 6902 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0077677 | OH | Sus | 31037684 | 2013 | NOV | Yes |  | Yes
NORTH VALLEY | Tier 2 | ORO FINO-1102 | 103031102 | FUSE | 1937 | 20131121 | 2121 | 909633 | 3996 | Distribution Circuit | Vegetation | Tree - fell into line | 307 | 639553 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078134 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 1139 | 20131121 | 1301 | 907169 | 421 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2105 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0077871 | OH | Sus | 41991455 | 2013 | NOV | Yes |  | Yes
NORTH VALLEY | Tier 2 | RED BLUFF-1104 | 103541104 | RECLOSER | 51238 | 20131121 | 634 | 906606 | 451 | Distribution Circuit | Vegetation | Tree - fell into line | 350 | 22255 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0077612 | OH | Sus | 31037645 | 2013 | NOV | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 1097 | 20131121 | 1546 | 907438 | 1224 | Distribution Circuit | Vegetation | Tree - bark fell into line | 4 | 4896 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0077991 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | FUSE | 10505 | 20131121 | 356 | 906536 | 374 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 56848 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0077607 | OH | Sus | 31037575 | 2013 | NOV | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | FUSE | 4331 | 20131121 | 1056 | 907038 | 733 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 6142 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0077798 | OH | Sus | 31038092 | 2013 | NOV | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | RECLOSER | 1502 | 20131121 | 1933 | 908743 | 507 | Distribution Circuit | Vegetation | Tree - fell into line | 1440 | 301083 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078093 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | BANGOR-1101 | 103191101 | RECLOSER | 85780 | 20131122 | 1333 | 912326 | 641 | Distribution Circuit | Equipment Failure/Involved | Other | 457 | 263412 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078626 | OH | Sus | 0 | 2013 | NOV | Yes | Multi-Fault | Yes
NORTH VALLEY | Tier 3 | BUCKS CREEK-1103 | 102211103 | FUSE | 9203 | 20131122 | 1307 | 912310 | 188 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 2444 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0078619 | OH | Sus | 0 | 2013 | NOV | Yes | None | Yes
NORTH VALLEY | Tier 3 | BUCKS CREEK-1103 | 102211103 | RECLOSER | 1103 | 20131122 | 2146 | 913255 | 1497 | Distribution Circuit | Equipment Failure/Involved | Other | 321 | 477233 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0078839 | OH | Sus | 31037615 | 2013 | NOV | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 17427 | 20131122 | 45 | 910277 | 2455 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 120295 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0078298 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 27019 | 20131122 | 402 | 910689 | 437 | Distribution Circuit | Vegetation | Tree - fell into line | 167 | 87508 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078347 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2096 | 20131122 | 543 | 910892 | 2127 | Distribution Circuit | Vegetation | Tree - branch fell on line | 267 | 175075 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078367 | OH | Sus | 0 | 2013 | NOV | Yes | Three Phase Fault | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 1139 | 20131122 | 135 | 912292 | 2555 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 12775 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0078612 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 4925 | 20131122 | 1004 | 911871 | 221 | Distribution Circuit | Equipment Failure/Involved | Other | 46 | 6308 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0078543 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 5135 | 20131122 | 1010 | 911733 | 285 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 855 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0078597 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | FUSE | 7569 | 20131122 | 733 | 911134 | 222 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1332 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078514 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | WHITMORE-1101 | 103601101 | RECLOSER | 1594 | 20131122 | 20 | 910238 | 991 | Distribution Circuit | Vegetation | Tree - fell into line | 542 | 253021 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078271 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
NORTH VALLEY | Tier 3 | WYANDOTTE-1105 | 102911105 | FUSE | 23667 | 20131122 | 557 | 910878 | 1920 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 5547 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0078378 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 23675 | 20141203 | 1301 | 1123165 | 323 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 969 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0073477 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | BUCKS CREEK-1103 | 102211103 | FUSE | 1129 | 20141211 | 957 | 1132571 | 4646 | Distribution Circuit | Vegetation | Tree - fell into line | 313 | 1013602 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075380 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | ELK CREEK-1101 | 102781101 | RECLOSER | 2004 | 20141211 | 819 | 1131506 | 299 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 45670 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075288 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
NORTH VALLEY | Tier 3 | GIRVAN-1101 | 103401101 | RECLOSER | 1330 | 20141211 | 654 | 1130432 | 436 | Distribution Circuit | Vegetation | Tree - fell into line | 416 | 59392 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075121 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | RECLOSER | 41356 | 20141211 | 933 | 1132382 | 474 | Distribution Circuit | Equipment Failure/Involved | Other | 352 | 82248 | Strong winds-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0075354 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 301 | 20141211 | 1123 | 1133225 | 1685 | Distribution Circuit | Equipment Failure/Involved | Other | 8 | 13480 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075550 | OH | Sus | 0 | 2014 | DEC | Yes | Open Circuit | Yes
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | RECLOSER | 1448 | 20141211 | 954 | 1132765 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 233 | 54873 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075451 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 16653 | 20141211 | 605 | 1129739 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3080 | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075081 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2236 | 20141211 | 822 | 1131600 | 229 | Distribution Circuit | Equipment Failure/Involved | Other | 1070 | 125303 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075147 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
NORTH VALLEY | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 4587 | 20141211 | 826 | 1131592 | 738 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 50922 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075364 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | PIT NO 3-2101 | 103732101 | RECLOSER | 1482 | 20141211 | 1203 | 1133458 | 166 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 2625 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075430 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | RISING RIVER-1101 | 103551101 | RECLOSER | 1530 | 20141211 | 535 | 1129851 | 1421 | Distribution Circuit | Vegetation | Tree - fell into line | 534 | 718580 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075028 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | RECLOSER | 75906 | 20141211 | 925 | 1132232 | 94 | Distribution Circuit | Vegetation | Tree - fell into line | 250 | 23500 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075234 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | OTHER |  | 20141211 | 925 | 1133115 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1725 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075234 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | FUSE | 949 | 20141211 | 755 | 1131175 | 500 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 10500 | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075186 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | FUSE | 26487 | 20141211 | 816 | 1132500 | 634 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 17118 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075484 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 850245 | 20141211 | 436 | 1129110 | 1311 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 11358 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075300 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | FUSE | 7245 | 20141211 | 508 | 1129265 | 1213 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 8563 | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075499 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
NORTH VALLEY | Tier 2 | VOLTA-1102 | 102541102 | FUSE | 7611 | 20141211 | 1342 | 1134016 | 648 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 6462 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075672 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | WHITMORE-1101 | 103601101 | FUSE | 2211 | 20141211 | 538 | 1129600 | 1535 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 53023 | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075066 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | WYANDOTTE-1105 | 102911105 | FUSE | 2757 | 20141211 | 818 | 1131476 | 1166 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 37022 | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075554 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | FUSE | 1795 | 20141212 | 701 | 1138660 | 934 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4670 | Fog-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0076473 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | GRAYS FLAT-0401 | 102530401 | FUSE | 3079 | 20141212 | 939 | 1137798 | 1923 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 72085 | Fog-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0076376 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | GRAYS FLAT-0401 | 102530401 | FUSE | 1787 | 20141212 | 1636 | 1138902 | 1054 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 12648 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076492 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
NORTH VALLEY | Tier 2 | WYANDOTTE-1102 | 102911102 | OTHER |  | 20141212 | 1137 | 1138174 | 302 | Distribution Circuit | Equipment Failure/Involved | Other | 37 | 8306 | Overcast-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0076425 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
NORTH VALLEY | Tier 2 | WYANDOTTE-1107 | 102911107 | FUSE | 13517 | 20141212 | 714 | 1137603 | 473 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 946 | Fog-32 - 90 F | Conductor, Overhead | On Ground | 14-0076251 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 1811 | 20141230 | 1050 | 1151296 | 406 | Distribution Circuit | Equipment Failure/Involved | Other | 50 | 20300 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0078998 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | OCB | OCB | 20141230 | 1021 | 1151159 | 909 | Distribution Circuit | Vegetation | Tree - fell into line | 726 | 157627 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0078943 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | FUSE | 2705 | 20141230 | 948 | 1150861 | 1200 | Distribution Circuit | Vegetation | Tree - fell into line | 204 | 244800 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079100 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | FUSE | 27231 | 20141230 | 928 | 1150821 | 1377 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 22032 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079487 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 17343 | 20141230 | 1205 | 1151741 | 790 | Distribution Circuit | Vegetation | Tree - branch fell on line | 89 | 70310 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079339 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 17613 | 20141230 | 929 | 1150781 | 2031 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 34527 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0078941 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 5181 | 20141230 | 1431 | 1152920 | 1012 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 27995 | Strong winds-32 - 90 F | Anchor or Guy | Broken, wire on object | 14-0079237 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | PARADISE-1104 | 102831104 | RECLOSER | 45674 | 20141230 | 849 | 1150608 | 587 | Distribution Circuit | Vegetation | Tree - fell into line | 1768 | 507031 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078902 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
NORTH VALLEY | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 1583 | 20141230 | 916 | 1150736 | 1772 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 31832 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078916 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 4523 | 20141230 | 1029 | 1151947 | 1186 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 87709 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0079284 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | PARADISE-1106 | 102831106 | FUSE | 2785 | 20141230 | 828 | 1150497 | 1380 | Distribution Circuit | Vegetation | Tree - fell into line | 291 | 156005 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0079211 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | FUSE | 4697 | 20141230 | 824 | 1150498 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 45333 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0078914 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 1555 | 20141230 | 803 | 1150437 | 267 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 20559 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078922 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | WHITMORE-1101 | 103601101 | RECLOSER | 1598 | 20141230 | 750 | 1150422 | 832 | Distribution Circuit | Vegetation | Tree - fell into line | 174 | 94299 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078898 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE | 1477 | 20141230 | 705 | 1150386 | 288 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 5760 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078885 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE | 1433 | 20141230 | 855 | 1150606 | 242 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 4840 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078907 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | WYANDOTTE-1105 | 102911105 | FUSE | 17135 | 20141230 | 800 | 1156019 | 1458 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 36702 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079584 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER | 2510 | 20150206 | 531 | 1173218 | 6233 | Distribution Circuit | Equipment Failure/Involved | Other | 3 | 18699 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009807 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | BURNEY-1101 | 103311101 | FUSE | 7831 | 20150206 | 209 | 1173106 | 3696 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 88704 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009789 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | BURNEY-1101 | 103311101 | FUSE | 10083 | 20150206 | 157 | 1173072 | 2383 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 285960 | Overcast-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0009796 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | BURNEY-1101 | 103311101 | RECLOSER | 9042 | 20150206 | 235 | 1173101 | 5557 | Distribution Circuit | Vegetation | Tree - fell into line | 398 | 191233 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009806 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | BURNEY-1101 | 103311101 | FUSE | 76411 | 20150206 | 209 | 1173714 | 2260 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 58760 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0009901 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | BURNEY-1101 | 103311101 | FUSE | 10093 | 20150206 | 1029 | 1174173 | 2916 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 137052 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010034 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | BURNEY-1101 | 103311101 | RECLOSER | 9042 | 20150206 | 1006 | ODB-9918 | 532 | Distribution Circuit | Equipment Failure/Involved | Other | 257 | 77704 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009806 | OH | Sus | 0 | 2015 | FEB | Yes |  | Yes
NORTH VALLEY | Tier 2 | BURNEY-1101 | 103311101 | OTHER |  | 20150206 | 500 | 1173184 | 5220 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 32472 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010479 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | FUSE | 1967 | 20150206 | 1209 | 1174689 | 824 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 6592 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010385 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 1064 | 20150206 | 1206 | 1174714 | 645 | Distribution Circuit | Vegetation | Tree - fell into line | 198 | 89506 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010127 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 23413 | 20150206 | 1225 | 1174804 | 1491 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5964 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010512 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | FUSE | 18545 | 20150206 | 920 | 1175443 | 1821 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 16389 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010205 | OH | Sus | 0 | 2015 | FEB | Yes | Open Circuit | Yes
NORTH VALLEY | Tier 2 | GRAYS FLAT-0401 | 102530401 | FUSE | 3079 | 20150206 | 555 | 1173556 | 2246 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 87594 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009866 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 799 | 20150206 | 1210 | 1175980 | 1762 | Distribution Circuit | Equipment Failure/Involved | Other | 25 | 44050 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0010742 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | RECLOSER | 1382 | 20150206 | 2157 | 1178915 | 2434 | Distribution Circuit | Vegetation | Tree - fell into line | 242 | 239578 | Strong winds-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0010732 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 5673 | 20150206 | 2116 | 1178599 | 2534 | Distribution Circuit | Equipment Failure/Involved | Other | 64 | 122386 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011122 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2236 | 20150206 | 425 | 1173164 | 593 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1077 | 365976 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009795 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | PIT NO 3-2101 | 103732101 | OCB | OCB | 20150206 | 744 | 1173484 | 6438 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 465599 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0009924 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | PIT NO 3-2101 | 103732101 | FUSE | 8543 | 20150206 | 744 | 1180610 | 6186 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 43302 | Strong winds-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 15-0011058 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | PIT NO 3-2101 | 103732101 | FUSE | 7903 | 20150206 | 744 | 1180625 | 3343 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 90261 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011060 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | PIT NO 3-2101 | 103732101 | OTHER |  | 20150206 | 744 | 1181299 | 4756 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4756 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011241 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | RISING RIVER-1101 | 103551101 | RECLOSER | 1530 | 20150206 | 114 | 1173064 | 6814 | Distribution Circuit | Vegetation | Tree - fell into line | 192 | 1173616 | Overcast-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0009784 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | RISING RIVER-1101 | 103551101 | OCB | OCB | 20150206 | 229 | ODB-9918 | 1052 | Distribution Circuit | Vegetation | Tree - fell into line | 201 | 91514 | Overcast-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0009784 | OH | Sus | 0 | 2015 | FEB | Yes |  | Yes
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 80454 | 20150206 | 355 | 1173144 | 541 | Distribution Circuit | Vegetation | Tree - fell into line | 240 | 63900 | Overcast-32 - 90 F | Conductor, Overhead | On Ground | 15-0009791 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 1640 | 20150206 | 455 | 1173195 | 3722 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 482901 | Overcast-32 - 90 F | Conductor, Overhead | On Ground | 15-0009799 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | OTHER |  | 20150206 | 355 | 1175407 | 4780 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4780 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009791 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | VOLTA-1102 | 102541102 | RECLOSER | 93418 | 20150206 | 201 | 1173093 | 2279 | Distribution Circuit | Vegetation | Tree - fell into line | 1441 | 1622357 | Overcast-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 15-0009778 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | BUCKS CREEK-1102 | 102211102 | RECLOSER | 1102 | 20150207 | 257 | 1180224 | 5083 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 265640 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011094 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | BUCKS CREEK-1103 | 102211103 | RECLOSER | 2414 | 20150207 | 132 | 1181709 | 2165 | Distribution Circuit | Vegetation | Tree - fell into line | 314 | 618504 | Strong winds-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 15-0011349 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | BUCKS CREEK-1103 | 102211103 | FUSE | 18103 | 20150207 | 2115 | 1181923 | 3021 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3021 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011398 | OH | Sus | 0 | 2015 | FEB | Yes | Three Phase Fault | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER | 13026 | 20150207 | 1330 | 1181235 | 1875 | Distribution Circuit | Equipment Failure/Involved | Other | 167 | 300525 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011564 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | OCB | OCB | 20150207 | 131 | 1179787 | 687 | Distribution Circuit | Equipment Failure/Involved | Other | 889 | 256542 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010880 | OH | Sus | 0 | 2015 | FEB | Yes | Multi-Fault | Yes
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | RECLOSER | 9072 | 20150207 | 821 | 1180550 | 524 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 143733 | Strong winds-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0011193 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | DESCHUTES-1101 | 103351101 | FUSE | 9847 | 20150207 | 739 | 1179627 | 652 | Distribution Circuit | Equipment Failure/Involved | Other | 3 | 1956 | Fog-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011020 | OH | Sus | 0 | 2015 | FEB | Yes | Three Phase Fault | Yes
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | SWITCH | 3491 | 20150207 | 1820 | 1181726 | 1719 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 39537 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011355 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | FUSE | 79151 | 20150207 | 1548 | ODB-9918 | 2607 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 49533 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009920 | OH | Sus | 0 | 2015 | FEB | Yes |  | Yes
NORTH VALLEY | Tier 2 | MC ARTHUR-1101 | 103491101 | FUSE | 4233 | 20150207 | 735 | 1180334 | 2112 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 35792 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011207 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 17629 | 20150207 | 445 | 1180042 | 644 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1932 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0010964 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 85234 | 20150207 | 39 | 1179687 | 949 | Distribution Circuit | Equipment Failure/Involved | Other | 391 | 296599 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0010854 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 1175 | 20150207 | 39 | 1181929 | 2186 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 48092 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010854 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
NORTH VALLEY | Tier 2 | VOLTA-1102 | 102541102 | FUSE | 7607 | 20150207 | 342 | 1179968 | 2628 | Distribution Circuit | Equipment Failure/Involved | Other | 29 | 14052 | Strong winds-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0011126 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | WHITMORE-1101 | 103601101 | FUSE | 7653 | 20150207 | 935 | 1180768 | 1660 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6704 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011091 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | WHITMORE-1101 | 103601101 | OTHER |  | 20150207 | 200 | 1182385 | 2370 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2370 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011496 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | WYANDOTTE-1105 | 102911105 | FUSE | 1735 | 20150207 | 26 | 1180221 | 2119 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 55094 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011326 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | PANORAMA-1102 | 103461102 | FUSE | 2017 | 20150208 | 1150 | 1182637 | 705 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 1410 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011538 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | PARADISE-1101 | 102831101 | TRANSFORMER |  | 20150208 | 2333 | 1185248 | 867 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 6290 | Strong winds-32 - 90 F | Transformer | Broken, wire on ground | 15-0011917 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 655 | 20150718 | 1643 | 1270179 | 485 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 6305 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 15-0048403 | OH | Sus | 31170289 | 2015 | JUL | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | OCB | OCB | 20151213 | 856 | 1360571 | 175 | Distribution Circuit | Vegetation | Tree - fell into line | 2493 | 190854 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084609 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 4513 | 20151213 | 858 | 1360574 | 249 | Distribution Circuit | Vegetation | Tree - fell into line | 165 | 41085 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084753 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | CORNING-1102 | 103331102 | FUSE | 2027 | 20151224 | 2028 | 1371398 | 694 | Distribution Circuit | 3rd Party | Gun Shot | 61 | 39836 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087229 | OH | Sus | 31208880 | 2015 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER | 98174 | 20160217 | 2054 | 1407205 | 557 | Distribution Circuit | Vegetation | Tree - fell into line | 355 | 197735 | Snow-Overcast-Below 32 F | Conductor, Overhead | Broken, wire on ground | 16-0013446 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | FUSE | 3317 | 20160305 | 1746 | 1417752 | 1319 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 14509 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017920 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | BANGOR-1101 | 103191101 | RECLOSER | 1804 | 20160305 | 2219 | 1420171 | 2464 | Distribution Circuit | Vegetation | Tree - fell into line | 426 | 131385 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018147 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | BUCKS CREEK-1101 | 102211101 | RECLOSER | 1101 | 20160305 | 2343 | 1420831 | 2625 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 60741 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018442 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 1064 | 20160305 | 1923 | 1418475 | 354 | Distribution Circuit | Vegetation | Tree - fell into line | 198 | 54878 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017808 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1101 | 103381101 | FUSE | 2907 | 20160305 | 1755 | 1417821 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 13625 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017773 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | JUMPER | WIRE DOWN | 20160305 | 2211 | 1422568 | 1389 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 9723 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018537 | OH | Sus | 0 | 2016 | MAR | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 1917 | 20160305 | 1727 | 1417653 | 1052 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 28846 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 16-0017656 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2040 | 20160305 | 2132 | 1419627 | 138 | Distribution Circuit | Vegetation | Tree - fell into line | 316 | 43608 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017617 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2236 | 20160305 | 1741 | 1417726 | 166 | Distribution Circuit | Vegetation | Tree - fell into line | 997 | 147826 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017617 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 1593 | 20160305 | 1812 | 1417976 | 498 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 10458 | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017771 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 17285 | 20160305 | 2156 | 1419848 | 579 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 6948 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018169 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1105 | 102831105 | JUMPER | LINE BURNED OPEN | 20160305 | 2146 | 1420623 | 324 | Distribution Circuit | Vegetation | Tree - fell into line | 1291 | 93786 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 16-0018010 | OH | Sus | 0 | 2016 | MAR | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 2 | RED BLUFF-1101 | 103541101 | FUSE | 4189 | 20160305 | 1820 | 1418086 | 196 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 12788 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017720 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | RED BLUFF-1103 | 103541103 | RECLOSER | 1702 | 20160305 | 2101 | 1419432 | 191 | Distribution Circuit | Equipment Failure/Involved | Overhead | 221 | 42211 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017941 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | JUMPER | TSB 2 E/OF MTR# 1008302681 | 20160305 | 1807 | 1417935 | 1926 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 15408 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017805 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 80454 | 20160305 | 2021 | 1418987 | 1401 | Distribution Circuit | Vegetation | Tree - fell into line | 240 | 84830 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0017879 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1107 | 102911107 | FUSE | 13057 | 20160305 | 2037 | 1419076 | 285 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 9405 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017865 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1109 | 102911109 | SWITCH | 68821 | 20160305 | 2119 | 1420604 | 376 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 32712 | Partly Cloudy-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018025 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | RECLOSER | 1646 | 20161014 | 132 | 1558011 | 826 | Distribution Circuit | Vegetation | Tree - fell into line | 540 | 213622 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0071832 | OH | Sus | 0 | 2016 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1102 | 102541102 | FUSE | 1531 | 20161014 | 432 | 1558437 | 779 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 38950 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0071897 | OH | Sus | 0 | 2016 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE | 1611 | 20170103 | 2111 | 1616945 | 753 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 24942 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003454 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 1147 | 20170103 | 2302 | 1617383 | 564 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 64860 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003359 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | PIT NO 3-2101 | 103732101 | OCB | 2101/2 | 20170103 | 2025 | 1616744 | 1497 | Distribution Circuit | Vegetation | Tree - branch fell on line | 154 | 157796 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003238 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | BUCKS CREEK-1102 | 102211102 | OCB | 1102/2 | 20170108 | 1941 | 1630293 | 6944 | Distribution Circuit | Environmental/External | Flood/Erosion | 131 | 909664 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006104 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 23423 | 20170108 | 1318 | 1626785 | 1917 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 29216 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005584 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | CLARK ROAD-1102 | 103091102 | FUSE | 815317 | 20170108 | 1516 | 1627654 | 1588 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 28584 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005653 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 1413 | 20170108 | 1808 | 1628523 | 2522 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 20176 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006505 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | NOTRE DAME-1104 | 102041104 | TRIP-SAVER | 2537 | 20170108 | 1426 | 1626728 | 1946 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 85624 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005492 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1101 | 102831101 | TRANSFORMER | 221085576774 | 20170108 | 1123 | 1631133 | 3177 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 9531 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006093 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1103 | 102831103 | RECLOSER | 43008 | 20170108 | 1139 | 1625697 | 1370 | Distribution Circuit | Vegetation | Tree - fell into line | 564 | 584314 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005345 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 17327 | 20170108 | 814 | 1623578 | 515 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3090 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005084 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1105 | 102831105 | FUSE | 1377 | 20170108 | 1336 | 1629184 | 2502 | Distribution Circuit | Vegetation | Tree - bark fell into line | 31 | 77562 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0005685 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 85234 | 20170108 | 1316 | 1626779 | 2917 | Distribution Circuit | Vegetation | Tree - fell into line | 548 | 1435667 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005624 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1103 | 102911103 | FUSE | 791 | 20170108 | 1224 | 1626167 | 1786 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 25004 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005410 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE | 5427 | 20170108 | 1430 | 1627346 | 1768 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 18803 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006051 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER | 2476 | 20170109 | 2236 | 1632352 | 4787 | Distribution Circuit | Vegetation | Tree - fell into line | 2747 | 1407309 | Overcast-Fog-Snow-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0006341 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | JUMPER | OJ COR NEW YORK AND SESAME | 20170109 | 1547 | 1631669 | 128 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 512 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006215 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1107 | 102911107 | RECLOSER | 1510 | 20170109 | 2323 | 1632387 | 1042 | Distribution Circuit | Vegetation | Tree - fell into line | 661 | 381461 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006353 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 1875 | 20170110 | 534 | 1632530 | 689 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 28938 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006490 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | BIG BEND-1101 | 103751101 | FUSE | 2851 | 20170110 | 1507 | 1633938 | 187 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 12155 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006772 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | JUMPER | WIRE DOWN S/SIDE OF 18145 ON MAINLINE | 20170110 | 1413 | 1634235 | 601 | Distribution Circuit | Equipment Failure/Involved | Overhead | 199 | 89910 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0006828 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER | 13026 | 20170110 | 1628 | 1634391 | 4379 | Distribution Circuit | Vegetation | Tree - fell into line | 167 | 558905 | Overcast-Fog-Snow-Strong Winds-Below 32 F | Crossarm, Wood | Broken, wire on ground | 17-0007278 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1102 | 102931102 | FUSE | 2085 | 20170110 | 1247 | 1633298 | 67 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 67 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006595 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | JUMPER | LINE & BUCK RIPPED CLEAR | 20170110 | 1922 | 1638026 | 1507 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 10549 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007245 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 79226 | 20170110 | 1848 | 1636626 | 225 | Distribution Circuit | Vegetation | Tree - fell into line | 896 | 70817 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0007034 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | BANGOR-1101 | 103191101 | RECLOSER | 1804 | 20170118 | 1350 | 1646317 | 1332 | Distribution Circuit | Vegetation | Tree - fell into line | 433 | 138251 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0009979 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | BUCKS CREEK-1103 | 102211103 | RECLOSER | 2414 | 20170118 | 1859 | 1648330 | 6012 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 704056 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0010942 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 5462 | 20170118 | 1300 | 1646223 | 463 | Distribution Circuit | Vegetation | Tree - branch fell on line | 457 | 209843 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0009937 | OH | Sus | 42928979 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KESWICK-1101 | 103451101 | OCB | 1101/2 | 20170118 | 1558 | 1646895 | 971 | Distribution Circuit | Vegetation | Tree - fell into line | 789 | 207405 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0010121 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | WILDWOOD-1101 | 103611101 | RECLOSER | 1576 | 20170118 | 1859 | 1649034 | 1152 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 117426 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0010452 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | WILDWOOD-1101 | 103611101 | OTHER | WIRE DOWN 2 SP S/S OF MTR#1008299576 | 20170118 | 2157 | 1649972 | 1248 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 19544 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010844 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE | 8159 | 20170119 | 1145 | 1651052 | 1705 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 157640 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010851 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CEDAR CREEK-1101 | 103321101 | FUSE | 4881 | 20170119 | 1923 | 1653273 | 2709 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 21672 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011583 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER | 98174 | 20170119 | 1001 | 1650579 | 8944 | Distribution Circuit | Vegetation | Tree - fell into line | 458 | 2592877 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010776 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | CHESTER-1102 | 103181102 | FUSE | 9337 | 20170119 | 943 | 1650512 | 237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1970 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0010850 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | WILDWOOD-1101 | 103611101 | TRANSFORMER | 117065039030 | 20170119 | 1845 | 1651932 | 1155 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4575 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011106 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | BURNEY-1101 | 103311101 | FUSE | 9251 | 20170120 | 1003 | 1653620 | 196 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 392 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on object | 17-0011415 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE | 1635 | 20170120 | 1711 | 1655174 | 5360 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 187737 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011812 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | RECLOSER | 9072 | 20170120 | 812 | 1653526 | 464 | Distribution Circuit | Vegetation | Tree - fell into line | 287 | 128458 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011380 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | KANAKA-1101 | 103221101 | OTHER | WIRE DOWN | 20170120 | 1445 | 1654952 | 1033 | Distribution Circuit | Equipment Failure/Involved | Overhead | 179 | 21676 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011750 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | OTHER | WIRE DOWN 4 SPANS N/OF 5221 | 20170120 | 1854 | 1655074 | 160 | Distribution Circuit | Vegetation | Tree - fell into line | 983 | 24544 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011771 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2560 | 20170120 | 412 | 1652273 | 702 | Distribution Circuit | Vegetation | Tree - fell into line | 561 | 327080 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011171 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ORO FINO-1102 | 103031102 | OTHER | WIRE DOWN | 20170120 | 1618 | 1655046 | 1188 | Distribution Circuit | Vegetation | Tree - branch fell on line | 316 | 368832 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011760 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | PIT NO 3-2101 | 103732101 | RECLOSER | 1482 | 20170120 | 810 | 1653191 | 9058 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 85733 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0011326 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | PIT NO 5-1101 | 101321101 | RECLOSER | 1606 | 20170120 | 1311 | 1654321 | 8844 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 344374 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011653 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | PIT NO 5-1101 | 101321101 | RECLOSER | 1618 | 20170120 | 1848 | 1655023 | 7210 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7210 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011755 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | PIT NO 5-1101 | 101321101 | RECLOSER | 1658 | 20170120 | 1958 | 1655969 | 2953 | Distribution Circuit | Vegetation | Tree - bark fell into line | 12 | 35206 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011986 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | PIT NO 5-1101 | 101321101 | JUMPER | WIRE DWN 11 SP LD S/O FUSE 8379 | 20170120 | 1958 | 1657663 | 5593 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 33558 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012538 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | RECLOSER | 48950 | 20170120 | 310 | 1652103 | 518 | Distribution Circuit | Vegetation | Tree - fell into line | 626 | 146318 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0011156 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | JUMPER | OJ'S @ L&B FEEDING 7133 | 20170120 | 405 | 1653087 | 592 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4144 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011293 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 1640 | 20170120 | 1543 | 1654632 | 3102 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 800762 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011675 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1101 | 103401101 | FUSE | 96125 | 20170121 | 2025 | 1657241 | 337 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 16176 | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012368 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 1875 | 20170122 | 2355 | 1662593 | 847 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 35574 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013567 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | FUSE | 18719 | 20170122 | 1912 | 1662164 | 1098 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 18666 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 17-0013702 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | OTHER | WIRE DOWN | 20170122 | 2224 | 1662615 | 971 | Distribution Circuit | Vegetation | Tree - fell into line | 458 | 64158 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013557 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | WYANDOTTE-1107 | 102911107 | RECLOSER | 1510 | 20170122 | 300 | 1658314 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 444 | 179089 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012653 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO LOMA-1102 | 255371102 | RECLOSER | 2560 | 20170123 | 517 | 1662842 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 561 | 154169 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013588 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | PIT NO 3-2101 | 103732101 | RECLOSER | 1386 | 20170123 | 903 | 1663345 | 721 | Distribution Circuit | Environmental/External | Ice or snow | 64 | 45652 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013829 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | FUSE | 7145 | 20170123 | 632 | 1662910 | 333 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 8991 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0013629 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER | 2248 | 20170207 | 1400 | 1680318 | 136 | Distribution Circuit | Equipment Failure/Involved | Overhead | 975 | 132600 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018641 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 9635 | 20170207 | 419 | 1677732 | 960 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 5172 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018423 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 11579 | 20170207 | 425 | 1677761 | 769 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 9228 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0018327 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1103 | 102911103 | RECLOSER | 77578 | 20170207 | 418 | 1677739 | 744 | Distribution Circuit | 3rd Party | Vehicle | 3403 | 883011 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018125 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE | 5437 | 20170207 | 1816 | 1680856 | 996 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1278 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018747 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1107 | 102911107 | FUSE | 535 | 20170207 | 231 | 1677406 | 451 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 21054 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018097 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | OTHER | WIRE DOWN SS MTR 1009720193 | 20170209 | 1014 | 1683059 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 957 | 26340 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019391 | OH | Sus | 0 | 2017 | FEB | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | FUSE | 18127 | 20170220 | 2139 | 1706186 | 1201 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 25221 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024762 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER | 2510 | 20170220 | 1857 | 1708664 | 2655 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 222027 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025138 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1101 | 102931101 | FUSE | 6005 | 20170220 | 1614 | 1703746 | 1216 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2789 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023920 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | EAST QUINCY-1101 | 102551101 | FUSE | 3141 | 20170220 | 2149 | 1706525 | 1058 | Distribution Circuit | Vegetation | Tree - fell into line | 180 | 47934 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024697 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 1640 | 20170220 | 2042 | 1705973 | 3975 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 615828 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024102 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | FUSE | 18607 | 20170221 | 521 | 1707440 | 3181 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 206504 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024889 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 3 | BUCKS CREEK-1103 | 102211103 | RECLOSER | 2414 | 20170221 | 28 | 1710770 | 3709 | Distribution Circuit | Equipment Failure/Involved | Overhead | 314 | 1164626 | Overcast-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0025633 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | OTHER | WIRE DOWN | 20170221 | 1117 | 1708329 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 358 | 221997 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0025092 | OH | Sus | 0 | 2017 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | FUSE | 3067 | 20170221 | 1250 | 1708599 | 1633 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 11431 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025118 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | GRAYS FLAT-0401 | 102530401 | FUSE | 1787 | 20170221 | 938 | 1708126 | 2027 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 24324 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025080 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | GRAYS FLAT-0401 | 102530401 | FUSE | 3079 | 20170221 | 702 | 1708248 | 666 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 26640 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0025128 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 1811 | 20170221 | 210 | 1707259 | 2330 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 22708 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024936 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 1997 | 20170221 | 119 | 1707121 | 2131 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 17048 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024980 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | SPANISH CREEK-4401 | 103104401 | OTHER | WIRE DOWN 3 SPANS LD SIDE OF 18129 | 20170221 | 547 | 1707859 | 753 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 19179 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025199 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | SPANISH CREEK-4401 | 103104401 | FUSE | 3051 | 20170221 | 1752 | 1709219 | 2630 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2630 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025267 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | FUSE | 10437 | 20170221 | 230 | 1707228 | 612 | Distribution Circuit | Vegetation | Tree - fell into line | 1167 | 163416 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024840 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | Yes
NORTH VALLEY | Tier 3 | CENTERVILLE-1101 | 102021101 | TRIP-SAVER | 1243 | 20170406 | 2224 | 1748364 | 679 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 25918 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037564 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1102 | 103441102 | RECLOSER | 1550 | 20170406 | 2303 | 1748675 | 345 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1408 | 150746 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037446 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 65606 | 20170406 | 2304 | 1748789 | 1365 | Distribution Circuit | Vegetation | Tree - fell into line | 425 | 330489 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037632 | OH | Sus | 0 | 2017 | APR | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | PARADISE-1103 | 102831103 | FUSE | 17469 | 20170406 | 2224 | 1748319 | 699 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 19799 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037563 | OH | Sus | 0 | 2017 | APR | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | FUSE | 1953 | 20170407 | 1900 | 1751570 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3360 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038086 | OH | Sus | 0 | 2017 | APR | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1101 | 102931101 | FUSE | 7185 | 20170407 | 201 | 1749183 | 494 | Distribution Circuit | Vegetation | Tree - branch fell on line | 85 | 9928 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037544 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 799 | 20170407 | 857 | 1750170 | 523 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 12029 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037693 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1103 | 102831103 | FUSE | 7025 | 20170407 | 11 | 1748900 | 514 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1542 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037522 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1103 | 102831103 | FUSE | 4665 | 20170407 | 148 | 1749167 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 19312 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037584 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1103 | 102831103 | RECLOSER | 2488 | 20170407 | 1220 | 1750770 | 506 | Distribution Circuit | Vegetation | Tree - fell into line | 769 | 79028 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037908 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE | 13751 | 20170407 | 19 | 1749374 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4112 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037572 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BIG BEND-1101 | 103751101 | FUSE | 2851 | 20171008 | 2012 | 1893777 | 943 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 60352 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085339 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CENTERVILLE-1101 | 102021101 | RECLOSER | 2592 | 20171008 | 2015 | 1893833 | 372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 409 | 134500 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085303 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 1064 | 20171008 | 2039 | 1893816 | 2591 | Distribution Circuit | Vegetation | Tree - branch fell on line | 200 | 100195 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085263 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 1835 | 20171008 | 2129 | 1893943 | 2675 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 22535 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085359 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | CLARK ROAD-1102 | 103091102 | FUSE | 17483 | 20171008 | 2255 | 1894161 | 2535 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 160479 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085276 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | DESCHUTES-1101 | 103351101 | FUSE | 2593 | 20171008 | 639 | 1892952 | 581 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 22340 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0085039 | OH | Sus | 31355701 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1103 | 102831103 | FUSE | 1289 | 20171008 | 1917 | 1893731 | 1738 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 50577 | Clear-32-90 F | Pole-Wood | Broken, wire on object | 17-0085314 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | Yes
NORTH VALLEY | Tier 3 | PARADISE-1103 | 102831103 | JUMPER | HOT WIRE DOWN 1 SS OF MTR 1007551383 | 20171008 | 2219 | 1896055 | 2125 | Distribution Circuit | Vegetation | Tree - fell into line | 772 | 42839 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085504 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 27187 | 20171008 | 1839 | 1894153 | 761 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 6849 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085265 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | RECLOSER | 1974 | 20171008 | 2039 | 1893810 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 616 | 181992 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085196 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | JUMPER | WIRE DOWN 2 SPANS LD SIDE OF 3491 | 20171009 | 834 | 1896296 | 305 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 7625 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085524 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 83288 | 20171020 | 54 | 1904944 | 594 | Distribution Circuit | Vegetation | Tree - fell into line | 214 | 78976 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0088893 | OH | Sus | 43198926 | 2017 | OCT | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 693 | 20171020 | 335 | 1905198 | 777 | Distribution Circuit | Vegetation | Tree - bark fell into line | 59 | 45843 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0088896 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 17291 | 20171020 | 658 | 1905445 | 597 | Distribution Circuit | Vegetation | Tree - grew into line | 16 | 9552 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0088953 | OH | Sus | 43198933 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ORO FINO-1102 | 103031102 | FUSE | 1945 | 20171204 | 1130 | 1935634 | 628 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 46472 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099731 | OH | Sus | 31368299 | 2017 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | BUCKS CREEK-1103 | 102211103 | RECLOSER | 2414 | 20171216 | 924 | 1944580 | 3250 | Distribution Circuit | Vegetation | Tree - fell into line | 314 | 875514 | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0102019 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | OTHER | WIRE DOWN 1 SP LD SIDE OF 1553 | 20171216 | 1206 | 1944712 | 221 | Distribution Circuit | Vegetation | Tree - fell into line | 1076 | 155662 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102098 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | BURNEY-1101 | 103311101 | RECLOSER | 1322 | 20180316 | 644 | 45248 | 188 | Distribution Circuit | Environmental/External | Ice or snow | 66 | 8092 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 18-0023263 | OH | Sus | 31384484 | 2018 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | PIT NO 3-2101 | 103732101 | OCB | 2101/2 | 20180316 | 954 | 45480 | 466 | Distribution Circuit | Vegetation | Tree - branch fell on line | 155 | 57958 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023329 | OH | Sus | 43302933 | 2018 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | RISING RIVER-1101 | 103551101 | RECLOSER | 1530 | 20180316 | 1013 | 45549 | 429 | Distribution Circuit | Vegetation | Tree - branch fell on line | 536 | 123960 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023409 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1101 | 103401101 | FUSE | 3489 | 20180728 | 449 | 146126 | 14779 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 10 | 80 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0065462 | OH | Sus | 0 | 2018 | JUL | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1101 | 103401101 | FUSE | 4191 | 20180728 | 449 | 146134 | 14874 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 30 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0065468 | OH | Sus | 0 | 2018 | JUL | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1101 | 103401101 | FUSE | 4855 | 20180728 | 449 | 146141 | 14885 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 31 | 775 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0065470 | OH | Sus | 0 | 2018 | JUL | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1101 | 103401101 | FUSE | 1861 | 20180728 | 449 | 148785 | 13955 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 18 | 72 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0066705 | OH | Sus | 0 | 2018 | JUL | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1107 | 102911107 | FUSE | 513 | 20180728 | 1808 | 142676 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 6264 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0064616 | OH | Sus | 0 | 2018 | JUL | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1101 | 102931101 | FUSE | 5985 | 20181014 | 1123 | 194784 | 397 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 945 | Clear-Strong Winds-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0090193 | OH | Sus | 0 | 2018 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | BIG BEND-1101 | 103751101 | SWITCH | 1721 | 20181108 | 746 | 212778 | 42326 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 206 | 8647832 | Clear-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 18-0098064 | OH | Sus | 0 | 2018 | NOV | Yes | None | Yes | No
NORTH VALLEY | Tier 2 | CLARK ROAD-1102 | 103091102 | RECLOSER | 47006 | 20181108 | 1044 | 211509 | 20092 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 148 | 2672214 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0098208 | OH | Sus | 0 | 2018 | NOV | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | CLARK ROAD-1102 | 103091102 | FUSE | 815317 | 20181108 | 1050 | 214503 | 10465 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 18 | 188370 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0099384 | OH | Sus | 0 | 2018 | NOV | Yes | None | Yes | No
NORTH VALLEY | Tier 2 | CLARK ROAD-1102 | 103091102 | JUMPER | OJ'S ON HARD TAP 1 POLE S/OF 815317 | 20181108 | 1050 | 214521 | 8866 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 17732 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0099388 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | NOTRE DAME-1104 | 102041104 | TRIP-SAVER | 2537 | 20181108 | 1907 | 211953 | 22615 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 44 | 995060 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0098438 | OH | Sus | 0 | 2018 | NOV | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | RECLOSER | 2022 | 20181129 | 114 | 227403 | 171 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1053 | 180063 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 18-0104677 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER | 2476 | 20190106 | 1147 | 255177 | 760 | Distribution Circuit | Vegetation | Tree - fell into line | 1372 | 622480 | Overcast-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0005061 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 5460 | 20190106 | 1821 | 256415 | 1136 | Distribution Circuit | Vegetation | Tree - fell into line | 457 | 440995 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005266 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | OTHER | WIRE DOWN | 20190106 | 1012 | 255066 | 158 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1086 | 148398 | Overcast-Fog-Heavy Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0005051 | OH | Sus | 43626761 | 2019 | JAN | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 1147 | 20190106 | 2011 | 257518 | 929 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 107764 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005497 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | PIT NO 5-1101 | 101321101 | RECLOSER | 1606 | 20190106 | 1936 | 257186 | 961 | Distribution Circuit | Environmental/External | Ice or snow | 126 | 93721 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005346 | OH | Sus | 0 | 2019 | JAN | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | OTHER | 5405 | 20190106 | 2255 | 259151 | 895 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 76075 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005794 | OH | Sus | 0 | 2019 | JAN | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | CLARK ROAD-1102 | 103091102 | RECLOSER | 2070 | 20190116 | 1818 | 269193 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 403 | 92881 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 19-0010040 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | CLARK ROAD-1102 | 103091102 | FUSE | 17791 | 20190116 | 2134 | 271174 | 1122 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 28602 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010867 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | GRAYS FLAT-0401 | 102530401 | OTHER | WIRE DOWN 8 SPANS SS OF 865983 | 20190116 | 1159 | 266846 | 415 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 12134 | Overcast-Fog-Drizzle-Strong Winds-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0009948 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 83288 | 20190116 | 1902 | 270864 | 1427 | Distribution Circuit | Vegetation | Tree - fell into line | 214 | 93211 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010243 | OH | Sus | 0 | 2019 | JAN | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 79226 | 20190116 | 2150 | 271283 | 875 | Distribution Circuit | Vegetation | Tree - fell into line | 1146 | 704347 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010311 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | PARADISE-1104 | 102831104 | FUSE | 17707 | 20190116 | 2313 | 271838 | 1137 | Distribution Circuit | Equipment Failure/Involved | Overhead | 161 | 126335 | Overcast-Heavy Rain-Strong Winds-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0010386 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | BUCKS CREEK-1103 | 102211103 | RECLOSER | 338520 | 20190117 | 834 | 273115 | 1796 | Distribution Circuit | Vegetation | Tree - fell into line | 315 | 517838 | Overcast-Fog-Snow-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011368 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1103 | 102911103 | RECLOSER | 1508 | 20190117 | 1659 | 274653 | 641 | Distribution Circuit | 3rd Party | Vehicle | 1365 | 711942 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011300 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE | 6857 | 20190202 | 3 | 285901 | 631 | Distribution Circuit | Vegetation | Tree - fell into line | 243 | 7815 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016836 | OH | Sus | 31424435 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER | 2476 | 20190204 | 2107 | 291101 | 1025 | Distribution Circuit | Vegetation | Tree - fell into line | 1372 | 645067 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018159 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2556 | 20190204 | 457 | 289465 | 343 | Distribution Circuit | Vegetation | Tree - fell into line | 181 | 61453 | Overcast-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0017711 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | RISING RIVER-1101 | 103551101 | RECLOSER | 1530 | 20190204 | 1014 | 289947 | 1795 | Distribution Circuit | Vegetation | Tree - fell into line | 536 | 712220 | Overcast-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0017942 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 53118 | 20190204 | 225 | 289396 | 621 | Distribution Circuit | Equipment Failure/Involved | Overhead | 784 | 486659 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017688 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE | 1467 | 20190204 | 1157 | 290383 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 28600 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017998 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1101 | 103401101 | RECLOSER | 323094 | 20190205 | 624 | 291738 | 325 | Distribution Circuit | 3rd Party | Gun Shot | 163 | 47900 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018269 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 1064 | 20190209 | 1911 | 297357 | 1125 | Distribution Circuit | Vegetation | Tree - fell into line | 202 | 78956 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020401 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | RECLOSER | 1376 | 20190212 | 2335 | 301544 | 12306 | Distribution Circuit | Vegetation | Tree - branch fell on line | 67 | 771489 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021674 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | RECLOSER | 1520 | 20190212 | 2317 | 314747 | 6793 | Distribution Circuit | Vegetation | Tree - branch fell on line | 83 | 563819 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0021707 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | JUMPER | OJ'S AT SNOWBIRD LN & BIG OAK LD | 20190212 | 2317 | 315656 | 9853 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 137942 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025104 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | FUSE | 2301 | 20190212 | 2317 | 316031 | 11235 | Distribution Circuit | Environmental/External | Ice or snow | 32 | 359520 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025181 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | FUSE | 3319 | 20190212 | 2337 | 317926 | 12212 | Distribution Circuit | Environmental/External | Ice or snow | 99 | 1208988 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025677 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1101 | 102931101 | SWITCH | 85689 | 20190212 | 2309 | 314821 | 9426 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 480726 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024682 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1102 | 102931102 | FUSE | 2081 | 20190212 | 2242 | 314930 | 6600 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 59400 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024710 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1102 | 102931102 | FUSE | 5997 | 20190212 | 2242 | 314937 | 8167 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 253177 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024712 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1102 | 102931102 | FUSE | 5405 | 20190212 | 2242 | 315506 | 6569 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 72259 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025073 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | RECLOSER | 1616 | 20190212 | 2329 | 301522 | 5402 | Distribution Circuit | Vegetation | Tree - fell into line | 468 | 2035242 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021669 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | RECLOSER | 9072 | 20190212 | 2342 | 301568 | 9452 | Distribution Circuit | Vegetation | Tree - fell into line | 290 | 2662630 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021680 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | JUMPER | OJ @ GOLDEN MEADOW & GOLDEN DOE | 20190212 | 2329 | 305838 | 5440 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 54400 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022697 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE | 1369 | 20190212 | 2349 | 311492 | 5526 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 77364 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023842 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE | 6843 | 20190212 | 2329 | 312121 | 5232 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 181660 | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024037 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE | 6367 | 20190212 | 2329 | 312536 | 5438 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 304528 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024173 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | JUMPER | OJ | 20190212 | 2329 | 314843 | 6841 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6841 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024689 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | DESCHUTES-1101 | 103351101 | RECLOSER | 1380 | 20190212 | 2321 | 301501 | 5446 | Distribution Circuit | Vegetation | Tree - fell into line | 1082 | 2124073 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021843 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | DESCHUTES-1101 | 103351101 | SWITCH | 9471 | 20190212 | 2321 | 305197 | 9680 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 234492 | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022438 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | DESCHUTES-1101 | 103351101 | JUMPER | OJ 2 SPANS LD SIDE OF MTR# 1010342071 | 20190212 | 2321 | 319098 | 12320 | Distribution Circuit | Vegetation | Tree - fell into line | 319 | 85814 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026190 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1101 | 103381101 | JUMPER | OJ @ 15173 TRINITY MTN RD | 20190212 | 2122 | 319138 | 11251 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 281535 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0026201 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1101 | 103381101 | JUMPER | OJ @ 15864 TRINITY MTN RD | 20190212 | 2315 | 320010 | 13965 | Distribution Circuit | Environmental/External | Ice or snow | 50 | 666330 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0026603 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1101 | 103401101 | RECLOSER | 1330 | 20190212 | 2305 | 301456 | 9607 | Distribution Circuit | Vegetation | Tree - fell into line | 200 | 1654387 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021661 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1101 | 103401101 | JUMPER | OJ'S /SS/OFF MAINLINE TWDS MTR#1008046102 | 20190212 | 2357 | 312203 | 11203 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 22406 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024070 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1101 | 103401101 | FUSE | 1835 | 20190212 | 2305 | 317713 | 9754 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 224342 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025639 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1101 | 103401101 | FUSE | 3489 | 20190212 | 2305 | 317714 | 11180 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 111800 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025640 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1101 | 103401101 | FUSE | 5017 | 20190212 | 2305 | 317717 | 9611 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 326774 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025641 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1101 | 103401101 | FUSE | 1837 | 20190212 | 2305 | 318964 | 12277 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 184155 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026127 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1101 | 103401101 | FUSE | 2073 | 20190212 | 2305 | 319266 | 12004 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 12004 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026238 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1102 | 103401102 | FUSE | 4407 | 20190212 | 2316 | 302895 | 9687 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 116244 | Snow-Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021821 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1102 | 103401102 | FUSE | 9603 | 20190212 | 2356 | 310768 | 5526 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 176832 | Snow-Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023659 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1102 | 103401102 | FUSE | 6897 | 20190212 | 132 | 312460 | 5255 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 47295 | Overcast-Fog-Snow-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0024143 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | RECLOSER | 41356 | 20190212 | 2312 | 301476 | 10995 | Distribution Circuit | Vegetation | Tree - fell into line | 325 | 2925182 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021665 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | JUMPER | OJ 4547 HIGH SIDE | 20190212 | 2251 | 303350 | 8382 | Distribution Circuit | Environmental/External | Ice or snow | 103 | 863346 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021931 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | JUMPER | OJ'S/TWDS MTR#1008942651 | 20190212 | 2343 | 312125 | 8253 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 8253 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024039 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | TRIP-SAVER | 2839 | 20190212 | 2343 | 313880 | 9767 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 848127 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024483 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | FUSE | 53313 | 20190212 | 2343 | 314876 | 6886 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 68860 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024700 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | JUMPER | OJ'S N/OF FUCO 53313 | 20190212 | 2343 | 314909 | 9591 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 143865 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024706 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | FUSE | 6767 | 20190212 | 2342 | 316780 | 9693 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 67851 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025315 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | JUMPER | OJ SS TO 5937 | 20190212 | 2312 | 317688 | 11230 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 33690 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025638 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | JUMPER | OJ 6 SPANS SS OF CGC# 118661241120 | 20190212 | 2312 | 317766 | 10868 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 76076 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025656 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | FUSE | 4089 | 20190212 | 2312 | 318005 | 10983 | Distribution Circuit | Environmental/External | Ice or snow | 9 | 98847 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025699 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | JUMPER | OJ 1 /E/OF 88301 | 20190212 | 2356 | 319213 | 10789 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 10789 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026231 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1102 | 103441102 | FUSE | 2377 | 20190212 | 2303 | 314542 | 8372 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 125580 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024592 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1102 | 103441102 | SWITCH | 1995 | 20190212 | 2303 | 316487 | 8427 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 935397 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025250 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1103 | 103441103 | JUMPER | OJ 1 SPAN SE/O MTR 5000009730 | 20190212 | 2358 | 311617 | 3604 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 72080 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023874 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | SWITCH | 11123 | 20190212 | 2340 | 305193 | 6717 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 664983 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022436 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 11131 | 20190212 | 2340 | 314444 | 9644 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 125372 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024564 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 6151 | 20190212 | 2340 | 314631 | 8243 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 140131 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024624 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 6149 | 20190212 | 2340 | 314634 | 9415 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 122395 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024625 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 6153 | 20190212 | 2340 | 314636 | 9271 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 9271 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024628 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 6161 | 20190212 | 2340 | 318179 | 9419 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 103609 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0025745 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 6155 | 20190212 | 2340 | 318190 | 9575 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 306400 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0025748 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANDERSON-1101 | 103261101 | JUMPER | OJ'S 1 LD SIDE OF 9573 | 20190213 | 238 | 304559 | 9091 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 63637 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022248 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANDERSON-1103 | 103261103 | JUMPER | OJ'S 5 SS/OF 3243 | 20190213 | 114 | 307279 | 6754 | Distribution Circuit | Environmental/External | Ice or snow | 41 | 231212 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022862 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANDERSON-1103 | 103261103 | JUMPER | OJ'S AT L&B FEEDING SINGLE PHASE TO THE NORTH | 20190213 | 115 | 316716 | 7952 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 24261 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025306 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | ANTLER-1101 | 103271101 | FUSE | 2283 | 20190213 | 57 | 317955 | 11122 | Distribution Circuit | Environmental/External | Ice or snow | 10 | 111220 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025686 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | ANTLER-1101 | 103271101 | JUMPER | 5137 SS JUMPERS | 20190213 | 57 | 317956 | 13363 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 80178 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025688 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | FUSE | 8285 | 20190213 | 57 | 318032 | 11067 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 154938 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025706 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | BIG BEND-1102 | 103751102 | OTHER | WIRE DOWN 1 LD SIDE OF MTR #1007906658 | 20190213 | 344 | 303383 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 41238 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021983 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | CEDAR CREEK-1101 | 103321101 | OTHER | WIRE DOWN W/O 27107 HWY 299 | 20190213 | 1 | 301740 | 5425 | Distribution Circuit | Equipment Failure/Involved | Overhead | 789 | 2031981 | Overcast-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021704 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 2 | COTTONWOOD-1101 | 102931101 | FUSE | 1375 | 20190213 | 202 | 311533 | 3498 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 111936 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023849 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1101 | 102931101 | JUMPER | OJ | 20190213 | 202 | 312882 | 5187 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 41484 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0024258 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1101 | 102931101 | FUSE | 7185 | 20190213 | 202 | 304403 | 3733 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 317305 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022201 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1102 | 102931102 | FUSE | 2057 | 20190213 | 216 | 308961 | 8104 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 853888 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023195 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | DESCHUTES-1101 | 103351101 | JUMPER | OJ'S 1 SS/OF 2707 | 20190213 | 221 | 308505 | 4857 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 63141 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023129 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | DESCHUTES-1101 | 103351101 | FUSE | 9463 | 20190213 | 221 | 308515 | 9354 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 9354 | Overcast-Fog-Heavy Rain-32-90 F | Anchor or Guy | Broken, wire on object | 19-0023136 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | DESCHUTES-1104 | 103351104 | JUMPER | OJ'S 1 S/OF 7487 | 20190213 | 121 | 304780 | 10631 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 10631 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022339 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | DESCHUTES-1104 | 103351104 | FUSE | 6607 | 20190213 | 121 | 305190 | 2419 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 26609 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022435 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | DESCHUTES-1104 | 103351104 | JUMPER | WIRE DOWN @ MTR# 5000076164 | 20190213 | 2142 | 307194 | 4071 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 38642 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023002 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1101 | 103381101 | OCB | 1101/2 | 20190213 | 415 | 302628 | 12008 | Distribution Circuit | Environmental/External | Ice or snow | 187 | 1180095 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021769 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1101 | 103401101 | FUSE | 7959 | 20190213 | 145 | 305742 | 9600 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 153600 | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022606 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1101 | 103401101 | JUMPER | OJ | 20190213 | 204 | 307993 | 9031 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 18062 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022996 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1102 | 103401102 | RECLOSER | 1028 | 20190213 | 154 | 301532 | 3793 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 508262 | Snow-Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 19-0021724 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1102 | 103401102 | FUSE | 9791 | 20190213 | 108 | 311741 | 9490 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 104390 | Snow-Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023902 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1102 | 103401102 | JUMPER | OJ'S/SS/TO 2843 | 20190213 | 153 | 311867 | 12387 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 734691 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023952 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1102 | 103401102 | FUSE | 6917 | 20190213 | 119 | 312588 | 11000 | Distribution Circuit | Vegetation | Tree - bark fell into line | 25 | 275000 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024179 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1102 | 103401102 | FUSE | 6921 | 20190213 | 153 | 312605 | 12177 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 395417 | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024182 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1102 | 103401102 | FUSE | 1859 | 20190213 | 153 | 312638 | 11168 | Distribution Circuit | Vegetation | Tree - branch fell on line | 36 | 402048 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024194 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | FUSE | 6959 | 20190213 | 49 | 319132 | 11039 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 430521 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0026200 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1102 | 103441102 | RECLOSER | 1550 | 20190213 | 103 | 301726 | 9407 | Distribution Circuit | Vegetation | Tree - fell into line | 860 | 5167335 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021709 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1102 | 103441102 | JUMPER | OJ'S/1/P/SS/TO 10231 | 20190213 | 29 | 311493 | 8626 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 17252 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023841 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1102 | 103441102 | FUSE | 10245 | 20190213 | 103 | 313719 | 10027 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 157922 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0024433 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1102 | 103441102 | JUMPER | OJ 1 P/E/OF 10257 | 20190213 | 103 | 317655 | 12471 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 67032 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0025629 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1103 | 103441103 | FUSE | 9903 | 20190213 | 5 | 307864 | 11005 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 22010 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022960 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1103 | 103441103 | FUSE | 9905 | 20190213 | 5 | 308059 | 11158 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 44632 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023010 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KESWICK-1101 | 103451101 | RECLOSER | 9712 | 20190213 | 47 | 301717 | 6881 | Distribution Circuit | Vegetation | Tree - fell into line | 274 | 1755928 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 19-0021700 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KESWICK-1101 | 103451101 | JUMPER | OJ'S AT MTR 1008048270 | 20190213 | 47 | 315717 | 10978 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 21956 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025112 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KESWICK-1101 | 103451101 | JUMPER | OJ'S ON MAINLINE FEEDING MTR 1008044666 | 20190213 | 47 | 315866 | 9583 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 153328 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025139 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | KESWICK-1101 | 103451101 | FUSE | 2653 | 20190213 | 47 | 315869 | 8083 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 193992 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025141 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | KESWICK-1101 | 103451101 | FUSE | 2435 | 20190213 | 23 | 315878 | 8207 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 49242 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025142 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | KESWICK-1101 | 103451101 | JUMPER | OJ'S AT REDBLUFF RD & MIDDLE CREEK RD | 20190213 | 44 | 316485 | 11964 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 622128 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025248 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | RECLOSER | 1382 | 20190213 | 314 | 302537 | 9308 | Distribution Circuit | Vegetation | Tree - fell into line | 243 | 1131261 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021795 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | RECLOSER | 49144 | 20190213 | 227 | 303048 | 11057 | Distribution Circuit | Vegetation | Tree - fell into line | 414 | 2406517 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023890 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | JUMPER | OJ'S AT MTR # 1008045869 | 20190213 | 227 | 312522 | 9484 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 294004 | Overcast-Fog-Snow-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0024169 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE | 3175 | 20190213 | 227 | 315979 | 11058 | Distribution Circuit | Environmental/External | Ice or snow | 51 | 563958 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025167 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE | 4623 | 20190213 | 236 | 302490 | 10813 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 227073 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025208 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE | 2891 | 20190213 | 13 | 317477 | 12232 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 61160 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025587 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE | 2413 | 20190213 | 227 | 317513 | 11058 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 77406 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025595 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | JUMPER | OJ 1 N/OF 3177 | 20190213 | 227 | 320065 | 12098 | Distribution Circuit | Environmental/External | Ice or snow | 22 | 266156 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026616 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 5377 | 20190213 | 345 | 309799 | 7999 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 459117 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023411 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | JUMPER | OJ'S FEEDING MTR# 1006191323 | 20190213 | 345 | 310024 | 6345 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6345 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023459 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 7009 | 20190213 | 345 | 310314 | 6568 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 85384 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023545 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | JUMPER | OJ'S 1 W/OF 5567 | 20190213 | 202 | 310324 | 9216 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 46080 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023548 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | SWITCH | 1949 | 20190213 | 40 | 314657 | 8279 | Distribution Circuit | Vegetation | Tree - fell into line | 234 | 1937286 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024635 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 3491 | 20190213 | 41 | 314872 | 9709 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 29127 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024697 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | OCB | 1104/2 | 20190213 | 209 | 301902 | 7681 | Distribution Circuit | Vegetation | Tree - fell into line | 687 | 3078183 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021850 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | Yes
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 8641 | 20190213 | 116 | 305203 | 8284 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 124260 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0022445 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 5673 | 20190213 | 209 | 308677 | 4011 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 260715 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023141 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 11485 | 20190213 | 209 | 310127 | 10659 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 42636 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023489 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | JUMPER | VJ'S FEEDING 8515 | 20190213 | 209 | 310855 | 10933 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 54665 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023686 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 11585 | 20190213 | 209 | 312611 | 9135 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 63945 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024184 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 11587 | 20190213 | 209 | 312776 | 7841 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 39205 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024234 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 11595 | 20190213 | 204 | 312778 | 8196 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 73764 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024235 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 11599 | 20190213 | 51 | 312782 | 8290 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 24870 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024239 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | OCB | 1101/2 | 20190213 | 441 | 302659 | 926 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4318 | 1174921 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021783 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 17167 | 20190213 | 634 | 302898 | 971 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 13323 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022452 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2556 | 20190213 | 837 | 303256 | 895 | Distribution Circuit | Vegetation | Tree - fell into line | 181 | 160987 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0022507 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | RED BLUFF-1104 | 103541104 | FUSE | 1991 | 20190213 | 652 | 302933 | 655 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 66155 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021969 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | RECLOSER | 1320 | 20190213 | 33 | 301697 | 8289 | Distribution Circuit | Vegetation | Tree - fell into line | 436 | 1564961 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021695 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | FUSE | 55301 | 20190213 | 33 | 308218 | 13671 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 451143 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023063 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | FUSE | 4675 | 20190213 | 33 | 312380 | 11227 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 233622 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024118 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | JUMPER | OJ AT TAP FEEDING 88969 & 4697 | 20190213 | 33 | 314532 | 6925 | Distribution Circuit | Equipment Failure/Involved | Overhead | 70 | 484702 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024584 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | FUSE | 3307 | 20190213 | 33 | 316532 | 6859 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 569297 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025284 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | FUSE | 7133 | 20190213 | 33 | 316534 | 7981 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 183563 | Overcast-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0025286 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | JUMPER | SPAN SS OF 4695 REMOVED | 20190213 | 33 | 316803 | 9517 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 9517 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025323 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | FUSE | 3309 | 20190213 | 33 | 317560 | 10835 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 32505 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025614 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | FUSE | 3327 | 20190213 | 33 | 317567 | 9361 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 102971 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025615 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | FUSE | 3311 | 20190213 | 33 | 317570 | 8189 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 253859 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025616 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | JUMPER | OJ 2/SS/OF MTR# 1007054564 | 20190213 | 33 | 318113 | 9508 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 19016 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025725 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | JUMPER | OJ 1/SS/OF 7145 FEEDING TWD MTR# 1008045723 | 20190213 | 33 | 318115 | 9729 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 107019 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025726 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | JUMPER | TAP TO 4713 CUT IN CLEAR | 20190213 | 249 | 312440 | 10751 | Distribution Circuit | Environmental/External | Ice or snow | 53 | 569803 | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024145 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | FUSE | 1959 | 20190213 | 249 | 312516 | 6666 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 253318 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024166 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | FUSE | 5957 | 20190213 | 249 | 312708 | 10860 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 32580 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024215 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | SWITCH | 10389 | 20190213 | 220 | 315012 | 8108 | Distribution Circuit | Vegetation | Tree - branch fell on line | 52 | 374638 | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024741 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | FUSE | 3337 | 20190213 | 220 | 315391 | 8104 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 56728 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025041 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | FUSE | 3341 | 20190213 | 220 | 317994 | 9379 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 703425 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025695 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 80454 | 20190213 | 221 | 301942 | 6704 | Distribution Circuit | Environmental/External | Ice or snow | 218 | 749622 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021731 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 85533 | 20190213 | 229 | 305354 | 3391 | Distribution Circuit | Environmental/External | Ice or snow | 13 | 44083 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022489 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 850247 | 20190213 | 229 | 305552 | 3677 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 22062 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022549 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 65764 | 20190213 | 229 | 311926 | 3679 | Distribution Circuit | Environmental/External | Ice or snow | 149 | 547544 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023867 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | RECLOSER | 1504 | 20190213 | 725 | 303015 | 6468 | Distribution Circuit | Vegetation | Tree - fell into line | 1169 | 6266140 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021846 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | WHITMORE-1101 | 103601101 | RECLOSER | 1598 | 20190213 | 823 | 303217 | 7467 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 1253635 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025089 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | WHITMORE-1101 | 103601101 | JUMPER | OJ @ MAIN LINE SS OF 7661 | 20190213 | 823 | 316518 | 7756 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 31024 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0025273 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | WHITMORE-1101 | 103601101 | FUSE | 2215 | 20190213 | 822 | 318677 | 10748 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 150472 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025997 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | WHITMORE-1101 | 103601101 | FUSE | 6699 | 20190213 | 822 | 318982 | 11888 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 47552 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026140 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | CORNING-1102 | 103331102 | FUSE | 1905 | 20190214 | 1658 | 310308 | 1494 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 7470 | Overcast-Fog-Snow-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0023542 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1102 | 102931102 | FUSE | 10031 | 20190214 | 1511 | 309869 | 3049 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12196 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024567 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | DESCHUTES-1104 | 103351104 | FUSE | 4303 | 20190214 | 1713 | 308200 | 4362 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 200652 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023665 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 83288 | 20190214 | 429 | 306999 | 896 | Distribution Circuit | Vegetation | Tree - fell into line | 214 | 98132 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022876 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 1044 | 20190214 | 758 | 307625 | 372 | Distribution Circuit | Vegetation | Tree - fell into line | 249 | 42714 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022912 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 1435 | 20190214 | 2031 | 310841 | 5429 | Distribution Circuit | Vegetation | Tree - branch fell on line | 64 | 47913 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023762 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 6377 | 20190214 | 1737 | 310457 | 8687 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 78183 | Overcast-Drizzle-32-90 F | Pole - Tower, steel | Broken, wire on ground | 19-0024190 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | JUMPER | OJ'S 1 LD SIDE OF MTR# 5000078976 | 20190214 | 1800 | 312797 | 2860 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 11440 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024240 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 7835 | 20190214 | 1800 | 314931 | 8568 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 34272 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024711 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | VOLTA-1101 | 102541101 | JUMPER | 85534 | 20190214 | 1600 | 310172 | 6881 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 68810 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023508 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1103 | 102911103 | RECLOSER | 1508 | 20190214 | 442 | 306861 | 523 | Distribution Circuit | Vegetation | Tree - fell into line | 1191 | 732699 | Partly Cloudy-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022815 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | JUMPER | WIRE DOWN | 20190214 | 1840 | 310717 | 865 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 73441 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023641 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
NORTH VALLEY | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE | 8085 | 20190215 | 1443 | 312463 | 1419 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 18447 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024211 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CEDAR CREEK-1101 | 103321101 | JUMPER | WIRE DOWN | 20190215 | 1739 | 312728 | 1131 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 29403 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024236 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | FUSE | 1953 | 20190215 | 1145 | 312250 | 1560 | Distribution Circuit | Environmental/External | Ice or snow | 3 | 4680 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024102 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1101 | 102931101 | FUSE | 43801 | 20190215 | 1922 | 312900 | 1252 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 15024 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024612 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1102 | 102931102 | FUSE | 1801 | 20190215 | 531 | 311356 | 659 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1318 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023868 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | ELK CREEK-1101 | 102781101 | FUSE | 2349 | 20190215 | 1917 | 312894 | 2799 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 41985 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024410 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1101 | 103401101 | FUSE | 3331 | 20190215 | 1423 | 312323 | 7069 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 98966 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024610 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | SWITCH | 7823 | 20190215 | 1020 | 310511 | 483 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 16905 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024207 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | FUSE | 6685 | 20190215 | 2205 | 313086 | 3975 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 166950 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024356 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE | 653 | 20190216 | 1206 | 314128 | 4346 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 22300 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025320 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | RECLOSER | 1520 | 20190217 | 1653 | 316517 | 1142 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 93644 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025285 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | JUMPER | OJ'S AT L&B FEEDING MTR# 1009724158 | 20190217 | 1653 | 317554 | 4352 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4352 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025611 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1101 | 102931101 | FUSE | 6861 | 20190217 | 928 | 315481 | 4823 | Distribution Circuit | Environmental/External | Ice or snow | 6 | 28938 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0026365 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE | 6587 | 20190217 | 821 | 316557 | 2073 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 122307 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025593 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE | 7283 | 20190217 | 828 | 316555 | 3172 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 15966 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025684 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1101 | 103381101 | RECLOSER | 1464 | 20190217 | 1306 | 315894 | 3164 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12656 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025150 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1102 | 103381102 | OTHER | WIRE DOWN 11 LD SD LR 1462 | 20190217 | 932 | 315566 | 4674 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 135500 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025086 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1101 | 103401101 | JUMPER | OJ 2/SP/SS/OF MTR# 1009717918 | 20190217 | 1213 | 315816 | 317 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 317 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025130 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1101 | 103401101 | JUMPER | 3 WIRES DOWN 5 POLES SS OF 2675 | 20190217 | 1623 | 316486 | 4397 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 26382 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025909 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1102 | 103441102 | FUSE | 10273 | 20190217 | 1917 | 316792 | 1398 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 27960 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025603 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1102 | 103441102 | FUSE | 2379 | 20190217 | 1917 | 317812 | 2511 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 10044 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025667 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KESWICK-1101 | 103451101 | FUSE | 2411 | 20190217 | 835 | 315359 | 5860 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 69790 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025043 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 3 | KESWICK-1101 | 103451101 | FUSE | 107703 | 20190217 | 1519 | 318449 | 3041 | Distribution Circuit | Environmental/External | Ice or snow | 2 | 6082 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025889 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | KESWICK-1101 | 103451101 | FUSE | 2443 | 20190217 | 804 | 320347 | 6326 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 69586 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026780 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | OTHER | WIRE DOWN @ MTR# 1009767053 | 20190217 | 1619 | 316488 | 1286 | Distribution Circuit | Equipment Failure/Involved | Overhead | 393 | 120656 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025253 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 11591 | 20190217 | 1800 | 316966 | 4122 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8244 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025327 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | PANORAMA-1102 | 103461102 | RECLOSER | 1632 | 20190217 | 729 | 315319 | 3536 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 35360 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025697 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER | 2510 | 20190226 | 137 | 323788 | 2531 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 7575 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028060 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | FUSE | 2935 | 20190226 | 103 | 323772 | 957 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4785 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028347 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | JUMPER | OJ'S @ L&B FEEDING MTR# 1008829224 | 20190226 | 58 | 324565 | 3762 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3762 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028356 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BUCKS CREEK-1102 | 102211102 | FUSE | 1381 | 20190226 | 1217 | 324110 | 4239 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 4239 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028296 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | BUCKS CREEK-1102 | 102211102 | OTHER | WIRE DOWN MAINLINE SS 1809 | 20190226 | 946 | 324441 | 1577 | Distribution Circuit | Equipment Failure/Involved | Overhead | 130 | 52991 | Overcast-Fog-Snow-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on object | 19-0028322 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 1064 | 20190226 | 1849 | 325116 | 1271 | Distribution Circuit | Vegetation | Tree - fell into line | 202 | 197116 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028520 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | EAST QUINCY-1101 | 102551101 | FUSE | 3071 | 20190226 | 1005 | 324219 | 360 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 360 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028273 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | FUSE | 1797 | 20190226 | 149 | 324636 | 3783 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 98358 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 19-0028383 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | RECLOSER | 2046 | 20190226 | 259 | 323824 | 1024 | Distribution Circuit | Vegetation | Tree - fell into line | 203 | 207872 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028069 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | PANORAMA-1102 | 103461102 | OTHER | WIRE DOWN MAINLINE AT MTR# 1006233956 | 20190226 | 1451 | 324969 | 1139 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 92651 | Partly Cloudy-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028501 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 80454 | 20190226 | 739 | 323939 | 1902 | Distribution Circuit | Vegetation | Tree - fell into line | 242 | 61868 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028109 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 1640 | 20190226 | 2344 | 325782 | 2472 | Distribution Circuit | Environmental/External | Ice or snow | 784 | 1384234 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028635 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1110 | 102911110 | TRANSFORMER | 221356467877 | 20190226 | 1016 | 324240 | 390 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 724 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028263 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | OTHER | WIRE DOWN @ LINE AND BUCK FEEDING 3157 | 20190227 | 551 | 326416 | 390 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1359 | 94474 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0028746 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | CORNING-1101 | 103331101 | FUSE | 85223 | 20190227 | 340 | 326503 | 659 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 6905 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on object | 19-0028762 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 83288 | 20190227 | 129 | 326308 | 1145 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 68258 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028766 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | RECLOSER | 49144 | 20190227 | 209 | 326128 | 1885 | Distribution Circuit | Vegetation | Tree - fell into line | 536 | 293776 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028696 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | RECLOSER | 1382 | 20190227 | 1057 | 326877 | 404 | Distribution Circuit | Vegetation | Tree - branch fell on line | 244 | 48120 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028938 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 2595 | 20190227 | 1442 | 327241 | 1099 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 13086 | Partly Cloudy-Rain-32-90 F | Woodpin | Broken, wire on object | 19-0029136 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | FUSE | 2499 | 20190227 | 1257 | 326778 | 413 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 9912 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029026 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE | 1487 | 20190608 | 308 | 401169 | 736 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 62560 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0064515 | OH | Sus | 31451974 | 2019 | JUN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 7033 | 20190925 | 627 | 612845 | 518 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 7066 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0103372 | OH | Sus | 0 | 2019 | SEP | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | BIG BEND-1102 | 103751102 | OTHER | WIRE DOWN 1 P E/O 13759 | 20191126 | 2219 | 720482 | 1143 | Distribution Circuit | Vegetation | Tree - fell into line | 301 | 207583 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0130373 | OH | Sus | 0 | 2019 | NOV | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 3 | BANGOR-1101 | 103191101 | JUMPER | OJ'S 1 E/O 709 | 20191127 | 1604 | 721990 | 76 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 76 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0130575 | OH | Sus | 0 | 2019 | NOV | Yes | Force Out | Yes | Yes
NORTH VALLEY | Tier 3 | BIG BEND-1101 | 103751101 | FUSE | 1735 | 20191127 | 47 | 719578 | 1012 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 25300 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0130351 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 23415 | 20191127 | 1415 | 721945 | 182 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 546 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0129558 | OH | Sus | 0 | 2019 | NOV | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | BIG BEND-1102 | 103751102 | FUSE | 1467 | 20200116 | 1502 | 763226 | 1353 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 121770 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010251 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 83288 | 20200116 | 1545 | 763291 | 285 | Distribution Circuit | Vegetation | Tree - branch fell on line | 136 | 28120 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010211 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 1405 | 20200116 | 1600 | 763499 | 1570 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4710 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0010625 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | WHITMORE-1101 | 103601101 | JUMPER | WIRE DOWN 1/S/N/OF 7649 | 20200116 | 1101 | 762714 | 337 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 31375 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0009909 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 1971 | 20200209 | 1218 | 783724 | 262 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 786 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0019320 | OH | Sus | 31490408 | 2020 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | OTHER | WIRE DOWN MAINLINE 2 S/O MTR 1007888458 | 20200315 | 615 | 851915 | 732 | Distribution Circuit | Vegetation | Tree - fell into line | 201 | 135037 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032219 | OH | Sus | 44259032 | 2020 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | SYCAMORE CREEK-1111 | 102971111 | RECLOSER | 2014 | 20200817 | 818 | 1015209 | 391 | Distribution Circuit | Environmental/External | Lightning | 537 | 209967 | Partly Cloudy-Lightning-Heat Wave-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0085570 | OH | Sus | 0 | 2020 | AUG | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | RECLOSER | 48950 | 20200908 | 1025 | 1060925 | 673 | Distribution Circuit | Vegetation | Tree - fell into line | 256 | 172261 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0094909 | OH | Sus | 0 | 2020 | SEP | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 2755 | 20210118 | 421 | 1212092 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 9792 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0009558 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | ORO FINO-1102 | 103031102 | RECLOSER | 38698 | 20210119 | 944 | 1216245 | 516 | Distribution Circuit | Vegetation | Tree - fell into line | 312 | 82044 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0010539 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | OTHER | WIRE DOWN 5 SPANS S/S 1596 | 20210125 | 502 | 1223363 | 566 | Distribution Circuit | Vegetation | Tree - fell into line | 779 | 429455 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013592 | OH | Sus | 44634092 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE | 5123 | 20210127 | 400 | 1232641 | 603 | Distribution Circuit | Vegetation | Tree - fell into line | 104 | 68050 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0015779 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE | 7283 | 20210127 | 136 | 1231931 | 685 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3425 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0015916 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1102 | 103401102 | FUSE | 2843 | 20210127 | 329 | 1232739 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 33604 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0015647 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | OCB | 1101/2 | 20210127 | 159 | 1232087 | 891 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2336 | 1346507 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0015526 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | CORNING-1102 | 103331102 | FUSE | 6081 | 20210128 | 1003 | 1239240 | 445 | Distribution Circuit | Environmental/External | Ice or snow | 8 | 1798 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0017650 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | PIT NO 1-1101 | 103721101 | RECLOSER | 1101/2 | 20210910 | 521 | 1467342 | 785 | Distribution Circuit | Animal | Other | 883 | 299396 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0115712 | OH | Sus | 0 | 2021 | SEP | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | OCB | 1102/2 | 20211017 | 2058 | 1500244 | 407 | Distribution Circuit | Equipment Failure/Involved | Overhead | 898 | 145162 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0132188 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | BIG BEND-1102 | 103751102 | FUSE | 1435 | 20211024 | 739 | 1508400 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 42504 | Strong Winds-Heavy Rain-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136508 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1103 | 102831103 | FUSE | 4665 | 20211024 | 906 | 1509005 | 556 | Distribution Circuit | Vegetation | Tree - fell into line | 229 | 90288 | Strong Winds-Heavy Rain-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136052 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 272749 | 20211025 | 1532 | 1519479 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 811 | Strong Winds-Heavy Rain-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0137602 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1102 | 103401102 | FUSE | 3875 | 20211213 | 826 | 1565969 | 893 | Distribution Circuit | Environmental/External | Water | 16 | 2483 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0157006 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 3357 | 20211213 | 1438 | 1567626 | 312 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 5928 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0157433 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | FUSE | 943 | 20211213 | 424 | 1565729 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 34086 | Clear-32-90F | Conductor, Overhead | On Ground | 21-0156941 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | OTHER | 1 SPAN DOWN | 20211214 | 101 | 1569214 | 1253 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 10120 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0157724 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | RECLOSER | 90334 | 20211214 | 222 | 1569053 | 1062 | Distribution Circuit | Vegetation | Tree - fell into line | 302 | 297104 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0157716 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 80454 | 20211214 | 201 | 1569263 | 734 | Distribution Circuit | Vegetation | Tree - fell into line | 239 | 175426 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0157708 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | GRAYS FLAT-0401 | 102530401 | JUMPER | WIRE DOWN @ 209 RIVER VIEW DR | 20211225 | 1642 | 1581491 | 198 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 594 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160600 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | OTHER | WIRE DOWN 1.5 LD SIDE OF 55453 | 20211226 | 923 | 1582593 | 377 | Distribution Circuit | Environmental/External | Ice or snow | 6 | 2262 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160774 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | OTHER | 1 WIRE DOWN HOT | 20211227 | 242 | 1584041 | 375 | Distribution Circuit | Equipment Failure/Involved | Overhead | 631 | 236625 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160981 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | OTHER | WIRE DOWN 2 LD SIDE OF 697 | 20211229 | 1221 | 1588470 | 263 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 5508 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161578 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 23199 | 20211229 | 1048 | 1588340 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1137 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161623 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | OTHER | WIRE DOWN SS OF FUCO 17833 | 20211229 | 639 | 1587908 | 413 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4776 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161488 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | FUSE | 1415 | 20211229 | 1358 | 1588874 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 960 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161638 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 27019 | 20211229 | 218 | 1587678 | 892 | Distribution Circuit | Vegetation | Tree - fell into line | 167 | 114987 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161537 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | BIG BEND-1101 | 103751101 | RECLOSER | 1101/2 | 20221210 | 1021 | 1881519 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 312 | 93362 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138281 | OH | Sus | 0 | 2022 | DEC | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1105 | 102831105 | FUSE | 1267 | 20221210 | 909 | 1880603 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 7632 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138180 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | PIT NO 3-2101 | 103732101 | RECLOSER | 1482 | 20221210 | 838 | 1880898 | 735 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 7251 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138142 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | WILDWOOD-1101 | 103611101 | FUSE | 1671 | 20221210 | 845 | 1881352 | 532 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 20216 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138228 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | CLARK ROAD-1102 | 103091102 | RECLOSER | 47006 | 20230108 | 258 | 1932083 | 957 | Distribution Circuit | Vegetation | Tree - fell into line | 147 | 57924 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0009775 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | RISING RIVER-1101 | 103551101 | RECLOSER | 1532 | 20230108 | 655 | 1932564 | 665 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 19950 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0009879 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | RECLOSER | 1520 | 20230109 | 548 | 1935918 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 21225 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0010800 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 83288 | 20230109 | 414 | 1935571 | 275 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 36059 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0010755 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2560 | 20230109 | 236 | 1935039 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 574 | 239699 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0010725 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BUTTE-1105 | 103081105 | RECLOSER | 2511 | 20230110 | 430 | 1942126 | 811 | Distribution Circuit | Vegetation | Tree - fell into line | 200 | 70691 | Partly Cloudy-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 23-0011867 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | FUSE | 2243 | 20230114 | 348 | 1952763 | 891 | Distribution Circuit | Vegetation | Tree - fell into line | 164 | 50380 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0015833 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | BUTTE-1105 | 103081105 | RECLOSER | 612016 | 20230114 | 910 | 1953563 | 442 | Distribution Circuit | Vegetation | Tree - fell into line | 204 | 49075 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015972 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1101 | 103381101 | TRIP-SAVER | 2905 | 20230114 | 755 | 1953067 | 905 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 13370 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0016072 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | BIG BEND-1102 | 103751102 | FUSE | 1449 | 20230224 | 814 | 2004402 | 350 | Distribution Circuit | Equipment Failure/Involved | Overhead | 85 | 29750 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 23-0034188 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CLARK ROAD-1102 | 103091102 | JUMPER | WIRE DOWN 1 SP LD SIDE OF 1711 | 20230224 | 741 | 2003573 | 494 | Distribution Circuit | Environmental/External | Ice or snow | 160 | 74763 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0033847 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | DESCHUTES-1101 | 103351101 | OTHER | 3001 | 20230224 | 1746 | 2006654 | 216 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 432 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0034485 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1102 | 103401102 | FUSE | 2469 | 20230224 | 724 | 2003277 | 435 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 10440 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0034256 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 9635 | 20230224 | 835 | 2004251 | 588 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 3552 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0034107 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | RECLOSER | 49144 | 20230224 | 506 | 2002710 | 539 | Distribution Circuit | Equipment Failure/Involved | Overhead | 536 | 248719 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0033662 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 5721 | 20230224 | 437 | 2002466 | 837 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 11084 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0034298 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | RED BLUFF-1101 | 103541101 | FUSE | 85811 | 20230224 | 520 | 2005593 | 831 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 7479 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0034169 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1107 | 102911107 | RECLOSER | 38438 | 20230224 | 959 | 2004228 | 1184 | Distribution Circuit | Vegetation | Tree - fell into line | 268 | 47397 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0033935 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | TYLER-1105 | 103571105 | FUSE | 2069 | 20230225 | 1802 | 2009088 | 302 | Distribution Circuit | 3rd Party | Gun Shot | 5 | 1422 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0035489 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | FUSE | 685 | 20230227 | 1126 | 2011973 | 274 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 2740 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0036472 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1105 | 102831105 | RECLOSER | 829194 | 20230228 | 855 | 2014509 | 674 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3565 | 174884 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 23-0037149 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | FUSE | 10629 | 20230228 | 1136 | 2015110 | 563 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 563 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0037480 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | RECLOSER | 640652 | 20230314 | 1604 | 2043133 | 294 | Distribution Circuit | Vegetation | Tree - fell into line | 442 | 129948 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0045523 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1107 | 102911107 | RECLOSER | 38438 | 20230314 | 1659 | 2043638 | 118 | Distribution Circuit | Equipment Failure/Involved | Overhead | 243 | 28674 | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 23-0045625 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | BIG BEND-1101 | 103751101 | OTHER | 7031 | 20230321 | 643 | 2053576 | 272 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1632 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on object | 23-0049162 | OH | Sus | 0 | 2023 | MAR | Yes | Open Circuit | Yes | Yes
SACRAMENTO | Tier 2 | VACA DIXON-1105 | 63591105 | FUSE | 40983 | 20131122 | 1225 | 912077 | 545 | Distribution Circuit | Equipment Failure/Involved | Other | 95 | 18781 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0078622 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | RECLOSER | 7446 | 20141230 | 840 | 1150530 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 520 | 79320 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078910 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SACRAMENTO | Tier 2 | BROWNS VALLEY-1101 | 152921101 | FUSE | 6811 | 20141230 | 1630 | 1153984 | 300 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2400 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0079333 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 1895 | 20170108 | 1227 | 1626017 | 257 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 7710 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005344 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | NARROWS-2101 | 153132101 | FUSE | 36129 | 20170108 | 1239 | 1626357 | 453 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 12606 | Partly Cloudy-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005482 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | VACAVILLE-1108 | 63601108 | FUSE | 1475 | 20170110 | 1917 | 1636080 | 930 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5580 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | On Ground | 17-0007253 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | JUMPER | WIRE DOWN BEYOND 459277 | 20170118 | 1527 | 1646735 | 229 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 458 | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0010068 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
SACRAMENTO | Tier 2 | PUTAH CREEK-1102 | 63681102 | RECLOSER | 67858 | 20170222 | 2134 | 1711452 | 956 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 30897 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025868 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BROWNS VALLEY-1101 | 152921101 | JUMPER | WIRE DOWN | 20170903 | 1855 | 1869070 | 115 | Distribution Circuit | Equipment Failure/Involved | Overhead | 582 | 55325 | Partly Cloudy-Heat Wave-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0075611 | OH | Sus | 0 | 2017 | SEP | Yes | Line to Ground | Yes | Yes
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 5807 | 20171008 | 2322 | 1896866 | 6701 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 69 | 462369 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0085755 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 18539 | 20171008 | 2322 | 1899357 | 8197 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 4 | 32788 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086750 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 173629 | 20171008 | 2322 | 1899487 | 6858 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 20574 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086819 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 459277 | 20171008 | 2322 | 1899490 | 6991 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 13982 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086820 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 188009 | 20171008 | 2322 | 1899491 | 7601 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 7601 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086821 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 307759 | 20171008 | 2322 | 1899493 | 8123 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 8123 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086822 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 693385 | 20171008 | 2322 | 1899495 | 7863 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 29 | 228027 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086823 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 527809 | 20171008 | 2322 | 1899496 | 6703 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 13406 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086825 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 1803 | 20171008 | 2322 | 1899498 | 6839 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 151 | 897785 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086826 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | JUMPER | OJ'S 1 NE/OF 17889 | 20171008 | 2308 | 1899500 | 6882 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 6882 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086827 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15803 | 20171008 | 2308 | 1899501 | 6502 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 4 | 26008 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086828 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15805 | 20171008 | 2316 | 1899504 | 6894 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 6894 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086829 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15807 | 20171008 | 2316 | 1899506 | 6874 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 6874 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086830 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15809 | 20171008 | 2316 | 1899516 | 6884 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 6884 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086833 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | JUMPER | OJ'S 1 N/E OF 15809 | 20171008 | 2308 | 1899517 | 6939 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 6939 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086835 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15811 | 20171008 | 2322 | 1899520 | 6886 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 6886 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086837 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15813 | 20171008 | 2322 | 1899523 | 6890 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 11 | 75790 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086838 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 1895 | 20171008 | 2322 | 1894286 | 8085 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 30 | 242550 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086839 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15815 | 20171008 | 2322 | 1899525 | 6669 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 20007 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086840 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15819 | 20171008 | 2322 | 1899526 | 6662 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 19986 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086841 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15821 | 20171008 | 2322 | 1899529 | 6893 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 13786 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086842 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15823 | 20171008 | 2316 | 1899530 | 6779 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 13558 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086845 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15825 | 20171008 | 2322 | 1899532 | 6768 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 6768 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086846 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15827 | 20171008 | 2322 | 1899533 | 6758 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 20274 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086847 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15829 | 20171008 | 2308 | 1899536 | 6767 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 13534 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086849 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | DOBBINS-1101 | 153741101 | RECLOSER | 1808 | 20171008 | 2205 | 1894014 | 3750 | Distribution Circuit | Vegetation | Tree - fell into line | 169 | 426606 | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085274 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | DOBBINS-1101 | 153741101 | FUSE | 17309 | 20171008 | 2145 | 1893968 | 4099 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4099 | Strong Winds-Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086135 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 3 | DOBBINS-1101 | 153741101 | FUSE | 18445 | 20171020 | 59 | 1905604 | 771 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1542 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0089070 | OH | Sus | 43199090 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | NARROWS-2101 | 153132101 | FUSE | 18555 | 20190117 | 146 | 272280 | 714 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 8568 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011107 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SACRAMENTO | Tier 2 | DOBBINS-1101 | 153741101 | OTHER | WIRE DOWN 2 SS OF MTR# 1008859464 | 20211024 | 1444 | 1512993 | 277 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 554 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136382 | OH | Sus | 0 | 2021 | OCT | Yes | Force Out | Yes | Yes
SACRAMENTO | Tier 2 | NARROWS-2101 | 153132101 | FUSE | 2527 | 20230105 | 10 | 1920285 | 1368 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 28728 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0007542 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 3 | DOBBINS-1101 | 153741101 | FUSE | 15911 | 20230314 | 1437 | 2042432 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2560 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0045549 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | RECLOSER | 2180 | 20130408 | 1324 | 770213 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 481 | 92952 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022600 | OH | Sus | 30988246 | 2013 | APR | Yes | Line to Ground | Yes
SIERRA | Tier 3 | ALLEGHANY-1102 | 152101102 | FUSE | 6747 | 20131121 | 2129 | 911665 | 2681 | Distribution Circuit | Equipment Failure/Involved | Other | 4 | 10724 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078484 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | OCB | OCB | 20131121 | 2047 | 909364 | 21 | Distribution Circuit | Equipment Failure/Involved | Other | 5436 | 114156 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0078113 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | OTHER |  | 20131121 | 2154 | 909799 | 2511 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 5022 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078998 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 3 | DRUM-1101 | 152321101 | RECLOSER | 1602 | 20131121 | 2127 | 909663 | 1323 | Distribution Circuit | Vegetation | Tree - fell into line | 320 | 225275 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0078249 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 18511 | 20131121 | 1915 | 908474 | 1555 | Distribution Circuit | Equipment Failure/Involved | Other | 84 | 105254 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0078237 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 2224 | 20131121 | 1609 | 907493 | 1269 | Distribution Circuit | Vegetation | Tree - fell into line | 967 | 565491 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0077956 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
SIERRA | Tier 2 | ALLEGHANY-1101 | 152101101 | FUSE | 7905 | 20131122 | 1508 | 912541 | 2872 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 31592 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078701 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE | 3919 | 20131122 | 1259 | 912551 | 1847 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 59320 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078675 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER | 51486 | 20131122 | 1237 | 912181 | 1632 | Distribution Circuit | Vegetation | Tree - fell into line | 1038 | 630848 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078615 | OH | Sus | 0 | 2013 | NOV | Yes | Three Phase Fault | Yes
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 9795 | 20131122 | 1531 | 912620 | 1515 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 81810 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078726 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 3 | DRUM-1101 | 152321101 | FUSE | 9215 | 20131122 | 734 | 911141 | 2241 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 40338 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0078583 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 2 | EL DORADO PH-2101 | 152762101 | RECLOSER | 52456 | 20131122 | 43 | 910278 | 1049 | Distribution Circuit | Equipment Failure/Involved | Other | 189 | 109436 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078241 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 2 | EL DORADO PH-2101 | 152762101 | FUSE | 1571 | 20131122 | 43 | 911857 | 3837 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 249405 | Strong winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0078541 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9351 | 20131122 | 1900 | 913036 | 1385 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6925 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0078771 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 4489 | 20131122 | 2046 | 913186 | 1092 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 58968 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078837 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 9712 | 20131122 | 1141 | 911991 | 2290 | Distribution Circuit | Vegetation | Tree - fell into line | 1107 | 425449 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078568 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20131122 | 1114 | 911910 | 735 | Distribution Circuit | Vegetation | Tree - fell into line | 1012 | 126224 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078552 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6619 | 20131122 | 933 | 911606 | 2562 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 77256 | Strong winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0078544 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6617 | 20131122 | 1540 | 912375 | 1697 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 17253 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078691 | OH | Sus | 0 | 2013 | NOV | Yes | Open Circuit | Yes
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6631 | 20131122 | 2131 | 913244 | 1317 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 36519 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0078862 | OH | Sus | 0 | 2013 | NOV | Yes | None | Yes
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6635 | 20131122 | 1253 | 912242 | 2167 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 31816 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0078891 | OH | Sus | 0 | 2013 | NOV | Yes | Three Phase Fault | Yes
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 10019 | 20140824 | 1928 | 1072340 | 283 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 19736 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0052913 | OH | Sus | 31096822 | 2014 | AUG | Yes | Line to Line | Yes
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21355 | 20141203 | 958 | 1122204 | 817 | Distribution Circuit | Equipment Failure/Involved | Other | 14 | 11438 | Rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0073345 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE | 31321 | 20141203 | 1428 | 1123470 | 691 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 33713 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073530 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8035 | 20141203 | 1418 | 1123401 | 1337 | Distribution Circuit | Equipment Failure/Involved | Other | 41 | 20689 | Fog-32 - 90 F | Conductor, Underground | Broken, wire on ground | 14-0073563 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
SIERRA | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 1113 | 20141203 | 609 | 1121757 | 421 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 31996 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073194 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 5781 | 20141203 | 1149 | 1122888 | 259 | Distribution Circuit | Vegetation | Tree - fell into line | 173 | 43781 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073415 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | RECLOSER | 39104 | 20141203 | 306 | 1121664 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 875 | 150128 | Rain-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0073135 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 18861 | 20141203 | 511 | 1121716 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 7636 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073166 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 3 | ALLEGHANY-1102 | 152101102 | OCB | OCB | 20141211 | 556 | 1129858 | 2284 | Distribution Circuit | Vegetation | Tree - fell into line | 153 | 49907 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075037 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 7959 | 20141211 | 949 | 1132513 | 511 | Distribution Circuit | Vegetation | Tree - fell into line | 192 | 70642 | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0075426 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21345 | 20141211 | 833 | 1131657 | 1597 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 11179 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0075600 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 9593 | 20141211 | 1030 | 1132899 | 765 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 25180 | Strong winds-32 - 90 F | Cutout, Fused, Distribution | Broken, wire on ground | 14-0075553 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 6279 | 20141211 | 729 | 1130716 | 339 | Distribution Circuit | Equipment Failure/Involved | Other | 53 | 17967 | Drizzle-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0075130 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | CLARKSVILLE-2103 | 153612103 | FUSE | 11049 | 20141211 | 620 | 1129852 | 275 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 19377 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075022 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 2212 | 20141211 | 638 | 1130009 | 628 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 45216 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075279 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8129 | 20141211 | 955 | 1132485 | 290 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 4060 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075342 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | FUSE | 8469 | 20141211 | 717 | 1130439 | 538 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 10576 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075221 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | NARROWS-2102 | 153132102 | OTHER |  | 20141211 | 125 | 1128899 | 305 | Distribution Circuit | Equipment Failure/Involved | Other | 85 | 25925 | Partly cloudy-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0074819 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 8213 | 20141211 | 1048 | 1132493 | 700 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 15400 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075552 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | SHINGLE SPRINGS-2108 | 153652108 | RECLOSER | 19622 | 20141211 | 554 | 1129635 | 1951 | Distribution Circuit | Vegetation | Tree - fell into line | 1667 | 212744 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0074971 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11997 | 20141211 | 921 | 1132264 | 307 | Distribution Circuit | Equipment Failure/Involved | Other | 2039 | 49545 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075377 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 22331 | 20141211 | 1026 | 1132860 | 1089 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 50094 | Rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075446 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER | 806 | 20141212 | 719 | 1137348 | 109 | Distribution Circuit | Equipment Failure/Involved | Other | 81 | 8829 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076193 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
SIERRA | Tier 2 | ALLEGHANY-1101 | 152101101 | RECLOSER | 978 | 20141212 | 1519 | 1138694 | 2844 | Distribution Circuit | Equipment Failure/Involved | Other | 198 | 142613 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076542 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | DRUM-1101 | 152321101 | RECLOSER | 75874 | 20141212 | 454 | 1137073 | 2361 | Distribution Circuit | Equipment Failure/Involved | Other | 103 | 86102 | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076149 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 18215 | 20141212 | 1125 | 1138145 | 335 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 1910 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076356 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
SIERRA | Tier 2 | SUMMIT-1101 | 152591101 | OCB | OCB | 20141212 | 250 | 1136968 | 1130 | Distribution Circuit | Vegetation | Tree - fell into line | 1046 | 411830 | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 14-0076114 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6653 | 20141212 | 907 | 1137709 | 1733 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 10398 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076718 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 11943 | 20141230 | 1022 | 1151136 | 846 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4230 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079527 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE | 9779 | 20141230 | 922 | 1150847 | 550 | Distribution Circuit | Equipment Failure/Involved | Other | 110 | 60500 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079102 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER | 51486 | 20141230 | 842 | 1150810 | 1278 | Distribution Circuit | Vegetation | Tree - fell into line | 993 | 560377 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079003 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 6759 | 20141230 | 842 | 1153922 | 1751 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 105060 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079252 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 3935 | 20141230 | 1601 | 1153724 | 1438 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 18694 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079477 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | FUSE | 3907 | 20141230 | 952 | 1150873 | 797 | Distribution Circuit | Vegetation | Tree - fell into line | 113 | 69303 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0078959 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 4373 | 20141230 | 1003 | 1150967 | 2926 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 27680 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079256 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 4493 | 20141230 | 1602 | 1153754 | 1508 | Distribution Circuit | Equipment Failure/Involved | Other | 52 | 78416 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079528 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | OTHER |  | 20141230 | 1049 | 1154477 | 1251 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 136278 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079318 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 2177 | 20141230 | 1040 | 1151257 | 1150 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 9200 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079441 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 2 | DIAMOND SPRINGS-1107 | 152261107 | FUSE | 10287 | 20141230 | 1040 | 1151251 | 1212 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 13980 | Strong winds-32 - 90 F | Transformer | Broken, wire on object | 14-0079203 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 2417 | 20141230 | 1630 | 1154043 | 1140 | Distribution Circuit | Equipment Failure/Involved | Other | 22 | 25080 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0079272 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 20835 | 20141230 | 1830 | 1155026 | 580 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1160 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079386 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE | 3225 | 20141230 | 2121 | 1155662 | 1077 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 2154 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 14-0079488 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | RECLOSER | 995672 | 20141230 | 1035 | 1151235 | 1751 | Distribution Circuit | Vegetation | Tree - fell into line | 216 | 210631 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079200 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | HIGGINS-1109 | 152691109 | FUSE | 9935 | 20141230 | 1147 | 1151659 | 1639 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 4298 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079241 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1184 | 20141230 | 902 | 1150699 | 928 | Distribution Circuit | Vegetation | Tree - fell into line | 306 | 270317 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078904 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
SIERRA | Tier 2 | NARROWS-2102 | 153132102 | FUSE | 32995 | 20141230 | 1013 | 1151157 | 1074 | Distribution Circuit | Vegetation | Tree - fell into line | 240 | 257760 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079082 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 4599 | 20141230 | 1116 | 1151512 | 1723 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 37906 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079281 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | OTHER |  | 20141230 | 1657 | 1154574 | 1231 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4924 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079518 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 4197 | 20141230 | 1007 | 1151658 | 3237 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 61503 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0079558 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 9712 | 20141230 | 1048 | 1151193 | 1137 | Distribution Circuit | Vegetation | Tree - fell into line | 1375 | 353622 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078955 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 32365 | 20141230 | 1029 | 1152210 | 1217 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2434 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079071 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | SWITCH | 5851 | 20141230 | 1029 | 1152978 | 1217 | Distribution Circuit | Vegetation | Tree - fell into line | 127 | 154559 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079146 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 6053 | 20141230 | 1019 | 1154418 | 915 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 59485 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079469 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 20749 | 20141230 | 1246 | 1153941 | 964 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 16388 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079438 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 1445 | 20141230 | 1455 | 1153156 | 1405 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 8054 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079464 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 2197 | 20141230 | 1037 | 1151241 | 1948 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 21324 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079550 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 11359 | 20141230 | 1123 | 1151556 | 1460 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 17520 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079563 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 9103 | 20141230 | 1209 | 1151755 | 916 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 14607 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079011 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 20451 | 20141230 | 1215 | 1151794 | 615 | Distribution Circuit | Equipment Failure/Involved | Other | 20 | 4300 | Strong winds-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0079078 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 10077 | 20141230 | 957 | 1153521 | 978 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 38694 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079209 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 10321 | 20141230 | 957 | 1154411 | 1388 | Distribution Circuit | Equipment Failure/Involved | Other | 87 | 115198 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079311 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | FUSE | 6175 | 20141230 | 1000 | 1150948 | 307 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 18113 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078949 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | RECLOSER | 97086 | 20150206 | 1357 | 1175598 | 1641 | Distribution Circuit | Vegetation | Tree - fell into line | 443 | 598787 | Strong winds-32 - 90 F | Conductor, Underground | Broken, wire on ground | 15-0010532 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 2005 | 20150206 | 605 | 1173272 | 1825 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 31025 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010100 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 20861 | 20150206 | 1412 | 1176109 | 1528 | Distribution Circuit | Equipment Failure/Involved | Other | 58 | 88376 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on object | 15-0010458 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | RECLOSER | 940 | 20150206 | 1250 | 1175132 | 1761 | Distribution Circuit | Vegetation | Tree - fell into line | 1219 | 635170 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010285 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 6597 | 20150206 | 422 | 1173180 | 503 | Distribution Circuit | Vegetation | Tree - branch fell on line | 43 | 8509 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009836 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 7117 | 20150206 | 1227 | 1175745 | 2749 | Distribution Circuit | Vegetation | Tree - fell into line | 157 | 431593 | Strong winds-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 15-0010527 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE | 33111 | 20150206 | 1321 | 1175365 | 1529 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 131494 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010684 | OH | Sus | 0 | 2015 | FEB | Yes | Three Phase Fault | Yes
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 7119 | 20150206 | 1238 | 1179246 | 4381 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 198813 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011142 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE | 9861 | 20150206 | 1243 | 1175015 | 1861 | Distribution Circuit | Equipment Failure/Involved | Other | 14 | 26054 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011312 | OH | Sus | 0 | 2015 | FEB | Yes | Open Circuit | Yes
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER | 1030 | 20150206 | 1230 | 1174902 | 1597 | Distribution Circuit | Vegetation | Tree - fell into line | 1202 | 532333 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0010341 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 34175 | 20150206 | 1237 | 1175199 | 1463 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 24871 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010731 | OH | Sus | 42328531 | 2015 | FEB | Yes | Line to Line | Yes
SIERRA | Tier 2 | CLARKSVILLE-2103 | 153612103 | OTHER |  | 20150206 | 602 | 1173302 | 796 | Distribution Circuit | Vegetation | Tree - fell into line | 2001 | 244527 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009826 | OH | Sus | 31132929 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | OTHER |  | 20150206 | 952 | 1173968 | 3068 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 9420 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010035 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 2 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8115 | 20150206 | 1914 | 1177774 | 1327 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 49099 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011115 | OH | Sus | 31132899 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | DRUM-1101 | 152321101 | OCB | OCB | 20150206 | 1353 | 1175581 | 1615 | Distribution Circuit | Vegetation | Tree - branch fell on line | 193 | 22175 | Clear-32 - 90 F | Crossarm, Wood | Broken, wire on object | 15-0010248 | OH | Sus | 0 | 2015 | FEB | Yes |  | Yes
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 22771 | 20150206 | 1222 | 1175368 | 1678 | Distribution Circuit | Vegetation | Tree - fell into line | 450 | 129316 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010365 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | SWITCH | 22399 | 20150206 | 1542 | 1176263 | 3175 | Distribution Circuit | Vegetation | Tree - fell into line | 275 | 29718 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010649 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 18407 | 20150206 | 637 | 1173384 | 324 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2916 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009919 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 21023 | 20150206 | 1631 | 1176562 | 1669 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5333 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010510 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9383 | 20150206 | 639 | 1173390 | 364 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 12375 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0009882 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | RECLOSER | 2748 | 20150206 | 1202 | 1174623 | 1121 | Distribution Circuit | Vegetation | Tree - fell into line | 880 | 375194 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0010334 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | OTHER |  | 20150206 | 1231 | 1175866 | 2870 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 14350 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0010297 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 8211 | 20150206 | 1231 | 1176836 | 3219 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3219 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0010485 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 31163 | 20150206 | 747 | 1173489 | 486 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 486 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009898 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 3773 | 20150206 | 653 | 1173408 | 1033 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2066 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010083 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 13322 | 20150206 | 605 | 1173314 | 272 | Distribution Circuit | Equipment Failure/Involved | Other | 624 | 118178 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009821 | OH | Sus | 0 | 2015 | FEB | Yes |  | Yes
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 4651 | 20150206 | 1958 | 1178209 | 1352 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 202456 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011119 | OH | Sus | 0 | 2015 | FEB | Yes | Three Phase Fault | Yes
SIERRA | Tier 2 | ALLEGHANY-1101 | 152101101 | FUSE | 30317 | 20150207 | 709 | 1183003 | 2286 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 2286 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011604 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21135 | 20150207 | 2050 | 1181895 | 910 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3640 | Rain-32 - 90 F | Conductor, Overhead | On Ground | 15-0011412 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | SWITCH | 9821 | 20150207 | 1614 | 1181653 | 1426 | Distribution Circuit | Equipment Failure/Involved | Other | 167 | 238142 | Overcast-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 15-0011338 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | FUSE | 7259 | 20150207 | 1732 | 1181675 | 1243 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 1477 | Drizzle-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011345 | OH | Sus | 0 | 2015 | FEB | Yes | Open Circuit | Yes
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 4493 | 20150207 | 1232 | 1181149 | 1553 | Distribution Circuit | Equipment Failure/Involved | Other | 52 | 12620 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011227 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 8223 | 20150207 | 1351 | 1181589 | 1704 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5752 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011318 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 18319 | 20150207 | 213 | 1180346 | 846 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 32890 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011019 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
SIERRA | Tier 2 | SUMMIT-1101 | 152591101 | OCB | OCB | 20150207 | 319 | 1180207 | 529 | Distribution Circuit | Vegetation | Tree - fell into line | 1036 | 502076 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011037 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8197 | 20150208 | 2007 | 1183975 | 938 | Distribution Circuit | Equipment Failure/Involved | Other | 3 | 2814 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011797 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 12615 | 20151213 | 1123 | 1361721 | 642 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 43014 | Overcast-Fog-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 15-0084850 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1110 | 153081110 | FUSE | 12989 | 20151213 | 1111 | 1361650 | 296 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 9472 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084894 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PENRYN-1107 | 152561107 | FUSE | 5259 | 20151224 | 1150 | 1370952 | 167 | Distribution Circuit | 3rd Party | Vehicle | 97 | 11766 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087106 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE | 1433 | 20160217 | 1952 | 1408518 | 2741 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 16446 | Partly Cloudy-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013867 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE | 1313 | 20160217 | 2041 | 1407581 | 1385 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 34625 | Overcast-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0013786 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 13253 | 20160217 | 1955 | 1407634 | 1508 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 24128 | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013521 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21161 | 20160217 | 2015 | 1407847 | 1378 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2756 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013615 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | AUBURN-1102 | 152161102 | FUSE | 8611 | 20160217 | 2059 | 1407233 | 255 | Distribution Circuit | Vegetation | Tree - fell into line | 185 | 47175 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013475 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | JUMPER | 3 POLE FROM EOL OPEN JUMPERS | 20160217 | 1301 | 1405446 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 2540 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013188 | OH | Sus | 31219754 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER | 3 PHASE WIRE DOWN 2/LD SIDE OF 2130 | 20160217 | 749 | 1404658 | 443 | Distribution Circuit | Vegetation | Tree - fell into line | 203 | 36514 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0012990 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 9075 | 20160217 | 944 | 1404585 | 269 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 13450 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013009 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 1333 | 20160217 | 2015 | 1407534 | 1284 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 32100 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013396 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1107 | 152261107 | FUSE | 41463 | 20160217 | 2027 | 1407069 | 1753 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 20485 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 16-0013566 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 6647 | 20160217 | 731 | 1404530 | 663 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 29835 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013111 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | RECLOSER | 6852 | 20160217 | 1959 | 1406901 | 1322 | Distribution Circuit | Vegetation | Tree - fell into line | 3294 | 1569268 | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 16-0013390 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 3147 | 20160217 | 725 | 1404729 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5382 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0012962 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 7535 | 20160217 | 725 | 1404730 | 414 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3726 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0012962 | OH | Sus | 0 | 2016 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 4491 | 20160217 | 2006 | 1407048 | 1058 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 165496 | Partly Cloudy-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0013479 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1111 | 153081111 | JUMPER | OPEN JUMPERS @ 4/N/OF 2503 | 20160217 | 1910 | 1406951 | 921 | Distribution Circuit | Equipment Failure/Involved | Overhead | 80 | 17295 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013392 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 9375 | 20160217 | 1956 | 1406733 | 876 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 55382 | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013499 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20160217 | 731 | 1404541 | 618 | Distribution Circuit | Vegetation | Tree - fell into line | 1015 | 161119 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0012964 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 22943 | 20160217 | 738 | 1404550 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 5140 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013097 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11479 | 20160217 | 1944 | 1406632 | 525 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 67725 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013561 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 21799 | 20160217 | 2111 | 1407292 | 1507 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 19378 | Partly Cloudy-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013605 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11437 | 20160217 | 1949 | 1406645 | 1336 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 131360 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013669 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 1555 | 20160217 | 1957 | 1406788 | 1201 | Distribution Circuit | Vegetation | Tree - fell into line | 258 | 119826 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013524 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 4665 | 20160305 | 2245 | 1421177 | 1198 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 23960 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018340 | OH | Sus | 31223007 | 2016 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1105 | 152481105 | FUSE | 30029 | 20160305 | 2014 | 1418826 | 1157 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 34710 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017839 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 4493 | 20160305 | 2237 | 1421366 | 2538 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 51774 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018400 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | JUMPER | OJ'S 1 SS OF MTR 1009800191 | 20160305 | 2237 | 1422204 | 2543 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2543 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018459 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE | 6005 | 20160305 | 2102 | 1419429 | 809 | Distribution Circuit | Vegetation | Tree - branch fell on line | 298 | 224099 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017988 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE | 7825 | 20160305 | 2119 | 1421530 | 2296 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 34188 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018433 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | FUSE | 8469 | 20160305 | 1719 | 1417619 | 316 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 6952 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017621 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 6875 | 20160305 | 2150 | 1419747 | 1005 | Distribution Circuit | Vegetation | Tree - fell into line | 262 | 263310 | Strong Winds-Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018360 | OH | Sus | 0 | 2016 | MAR | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2422 | 20160305 | 2042 | 1419150 | 207 | Distribution Circuit | Vegetation | Tree - fell into line | 602 | 45367 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017820 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | RECLOSER | 1730 | 20160305 | 2157 | 1421605 | 2481 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 154286 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0018350 | OH | Sus | 31223007 | 2016 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 4821 | 20161014 | 705 | 1558419 | 580 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6960 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0071922 | OH | Sus | 0 | 2016 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | OCB | 1101/2 | 20170103 | 548 | 1615292 | 404 | Distribution Circuit | Vegetation | Tree - fell into line | 513 | 90044 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0002880 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER | 2210 | 20170103 | 1056 | 1615646 | 1999 | Distribution Circuit | Vegetation | Tree - branch fell on line | 652 | 471639 | Overcast-Fog-Snow-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0002967 | OH | Sus | 42908603 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 35424 | 20170103 | 2309 | 1617255 | 1248 | Distribution Circuit | Vegetation | Tree - fell into line | 237 | 187104 | Overcast-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0003403 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 38373 | 20170103 | 536 | 1615461 | 831 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 9141 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0002908 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | RECLOSER | 1720 | 20170103 | 1927 | 1616634 | 4448 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 133251 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003215 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | RECLOSER | 12832 | 20170108 | 2019 | 1629044 | 1118 | Distribution Circuit | Vegetation | Tree - fell into line | 760 | 315709 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005783 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 18843 | 20170108 | 1016 | 1626858 | 604 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 8456 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005435 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 186912 | 20170108 | 2115 | 1629283 | 1352 | Distribution Circuit | Vegetation | Tree - fell into line | 1226 | 309908 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005727 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER | 2200 | 20170108 | 657 | 1622900 | 252 | Distribution Circuit | Vegetation | Tree - branch fell on line | 114 | 19722 | Strong Winds-Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004980 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE | 4637 | 20170108 | 1024 | 1624846 | 344 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 15136 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005157 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER | 2104 | 20170108 | 1216 | 1627010 | 1464 | Distribution Circuit | Vegetation | Tree - fell into line | 2032 | 789644 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005426 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 33773 | 20170108 | 1453 | 1627510 | 1197 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 56259 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005737 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8115 | 20170108 | 1219 | 1626111 | 1510 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 55870 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005422 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | SWITCH | 1257 | 20170108 | 2129 | 1628985 | 1153 | Distribution Circuit | Vegetation | Tree - fell into line | 197 | 24281 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005730 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 20383 | 20170108 | 722 | 1623078 | 283 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 2830 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005057 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 21913 | 20170108 | 1205 | 1625997 | 543 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 14706 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005377 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 18417 | 20170108 | 1017 | 1624755 | 557 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 11140 | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005243 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | JUMPER | O/J 2 E/OF 7085 | 20170108 | 815 | 1624970 | 268 | Distribution Circuit | Environmental/External | Lightning | 572 | 98692 | Overcast-Fog-Rain-Lightning-Strong Winds-32-90 F | Jumper | Broken, wire on object | 17-0005126 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1101 | 152031101 | FUSE | 32729 | 20170108 | 1351 | 1627090 | 1486 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 29720 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005704 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 6585 | 20170108 | 2209 | 1629610 | 2398 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 38368 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006004 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 4115 | 20170108 | 1904 | 1628748 | 2730 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 20778 | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005732 | OH | Sus | 31294707 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20170108 | 2202 | 1629607 | 1390 | Distribution Circuit | Vegetation | Tree - fell into line | 1019 | 1011862 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005757 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2108 | 153652108 | FUSE | 2659 | 20170108 | 1729 | 1628414 | 2684 | Distribution Circuit | Vegetation | Tree - fell into line | 150 | 214164 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005683 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 12965 | 20170108 | 1757 | 1627977 | 1054 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 12814 | Overcast-Fog-Rain-32-90 F | Anchor or Guy | Broken, wire on ground | 17-0005586 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SUMMIT-1102 | 152591102 | FUSE | 6829 | 20170108 | 1020 | 1625922 | 7734 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 30936 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005234 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | FUSE | 5401 | 20170108 | 1218 | 1626097 | 222 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 4392 | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0005295 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | RECLOSER | 307494 | 20170108 | 1502 | 1627596 | 683 | Distribution Circuit | Vegetation | Tree - grew into line | 267 | 63858 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005433 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 6931 | 20170109 | 135 | 1629925 | 2133 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 12137 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005861 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE | 8949 | 20170109 | 1524 | 1631582 | 1279 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 5025 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006205 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | ECHO SUMMIT-1101 | 158031101 | FUSE | 2429 | 20170109 | 657 | 1633309 | 6208 | Distribution Circuit | Environmental/External | Flood/Erosion | 6 | 37248 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006597 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1107 | 152691107 | FUSE | 80845 | 20170109 | 357 | 1630021 | 827 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 10751 | Strong Winds-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005942 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | HIGGINS-1109 | 152691109 | FUSE | 7863 | 20170109 | 558 | 1630218 | 1670 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 27672 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0005979 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 38111 | 20170109 | 607 | 1630221 | 2344 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 9376 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006249 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2102 | 153132102 | FUSE | 7251 | 20170109 | 626 | 1630242 | 711 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 25477 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006005 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | JUMPER | WIRE DOWN 2 P/W/O 1008964630 | 20170109 | 2021 | 1632219 | 1224 | Distribution Circuit | Vegetation | Tree - fell into line | 166 | 9051 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005598 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE | 59355 | 20170109 | 38 | 1629879 | 2349 | Distribution Circuit | Equipment Failure/Involved | Overhead | 752 | 37353 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005829 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 18223 | 20170109 | 925 | 1630275 | 1770 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4857 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005978 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 6185 | 20170109 | 311 | 1629982 | 1248 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 19968 | Strong Winds-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005932 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 3369 | 20170110 | 2124 | 1637618 | 2476 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 14856 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008227 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | FUSE | 3907 | 20170110 | 1727 | 1634697 | 1533 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 14641 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006879 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | OCB | 1101/2 | 20170110 | 1936 | 1636324 | 2670 | Distribution Circuit | Vegetation | Tree - fell into line | 1130 | 1246286 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007467 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | COLUMBIA HILL-1101 | 152471101 | FUSE | 919149 | 20170110 | 1500 | 1633879 | 2914 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 17484 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0008336 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 7431 | 20170110 | 1747 | 1634447 | 1588 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 15117 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006912 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 18615 | 20170110 | 2102 | 1637108 | 2773 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5546 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008527 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 6661 | 20170110 | 1646 | 1634503 | 2979 | Distribution Circuit | Vegetation | Tree - fell into line | 169 | 257366 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006894 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 21593 | 20170110 | 2043 | 1636978 | 2823 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 26585 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0007848 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 21931 | 20170110 | 1533 | 1634068 | 2950 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 29950 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006795 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 2167 | 20170110 | 2119 | 1637575 | 2394 | Distribution Circuit | Equipment Failure/Involved | Overhead | 118 | 282492 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007580 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | DRUM-1101 | 152321101 | RECLOSER | 75874 | 20170110 | 631 | 1632529 | 3645 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 270882 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006395 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | DRUM-1101 | 152321101 | JUMPER | 1602 | 20170110 | 1514 | 1634159 | 1589 | Distribution Circuit | Vegetation | Tree - fell into line | 151 | 86286 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006803 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | DRUM-1101 | 152321101 | FUSE | 9215 | 20170110 | 942 | 1632834 | 5248 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 94464 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0007913 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | DRUM-1101 | 152321101 | FUSE | 9213 | 20170110 | 548 | 1632510 | 6290 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 106930 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008310 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE | 4151 | 20170110 | 2005 | 1636661 | 2783 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 33396 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0007794 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 36679 | 20170110 | 1738 | 1634764 | 1602 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6408 | Overcast-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0007027 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 4763 | 20170110 | 1913 | 1636038 | 1224 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 35496 | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007107 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | RECLOSER | 2414 | 20170110 | 2119 | 1637588 | 248 | Distribution Circuit | Vegetation | Tree - fell into line | 382 | 45873 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007233 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 9957 | 20170110 | 2046 | 1636999 | 1249 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 14454 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007264 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1109 | 152691109 | FUSE | 7863 | 20170110 | 1907 | 1637690 | 1273 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 61104 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007172 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9345 | 20170110 | 1207 | 1633157 | 3127 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 10600 | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006646 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | TRIP-SAVER | 7203 | 20170110 | 1840 | 1635621 | 982 | Distribution Circuit | Vegetation | Tree - fell into line | 226 | 221932 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007000 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | OLETA-1102 | 163541102 | FUSE | 20527 | 20170110 | 946 | 1632898 | 190 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 570 | Heavy Rain-Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006508 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PENRYN-1103 | 152561103 | FUSE | 5253 | 20170110 | 1822 | 1635361 | 1336 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 73480 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007276 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | PENRYN-1105 | 152561105 | FUSE | 9143 | 20170110 | 1620 | 1634282 | 1122 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 33666 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006867 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | PLACERVILLE-1111 | 153081111 | OTHER | WIRE DOWN | 20170110 | 1855 | 1635762 | 493 | Distribution Circuit | Vegetation | Tree - fell into line | 616 | 150379 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007113 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 9372 | 20170110 | 1937 | 1636509 | 2965 | Distribution Circuit | Vegetation | Tree - fell into line | 1272 | 265975 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006989 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11705 | 20170110 | 2038 | 1636915 | 879 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 35160 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007314 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11703 | 20170110 | 1844 | 1635609 | 2793 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 34080 | Overcast-Fog-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007783 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 22355 | 20170110 | 659 | 1632548 | 1900 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 34079 | Heavy Rain-Strong Winds-Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006476 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | JUMPER | OJ'S 1 SPAN S/OF CGC# 223091035721 | 20170110 | 1155 | 1633126 | 1653 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1653 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006729 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 2 | SUMMIT-1101 | 152591101 | FUSE | 6627 | 20170110 | 2251 | 1637987 | 3879 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 170972 | Overcast-Snow-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008250 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6617 | 20170110 | 2141 | 1643785 | 5573 | Distribution Circuit | Vegetation | Tree - grew into line | 54 | 300942 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0008785 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 22021 | 20170111 | 732 | 1638868 | 2229 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 11145 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007889 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 2585 | 20170111 | 111 | 1638319 | 1372 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 79576 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007372 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE | 6005 | 20170111 | 126 | 1638376 | 1304 | Distribution Circuit | Vegetation | Tree - fell into line | 288 | 256170 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007365 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 4935 | 20170111 | 817 | 1639018 | 543 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 11138 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007524 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2422 | 20170111 | 104 | 1638322 | 1321 | Distribution Circuit | Vegetation | Tree - fell into line | 604 | 171496 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007320 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 5247 | 20170111 | 1343 | 1639923 | 395 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 5730 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007809 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE | 33317 | 20170111 | 929 | 1639249 | 1658 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 16580 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007765 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 20469 | 20170111 | 1040 | 1639501 | 485 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 4063 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007639 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6633 | 20170111 | 1736 | 1640476 | 1921 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 95086 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0008220 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6619 | 20170111 | 743 | 1638902 | 2593 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 72604 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0008417 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 6227 | 20170111 | 929 | 1639330 | 589 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 9424 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007746 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | FUSE | 7795 | 20170111 | 24 | 1638181 | 957 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 22968 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007650 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 4373 | 20170118 | 2116 | 1649065 | 1339 | Distribution Circuit | Vegetation | Tree - branch fell on line | 36 | 48204 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010566 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1109 | 152691109 | FUSE | 172971 | 20170118 | 1539 | 1646985 | 635 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 34335 | Partly Cloudy-Rain-32-90 F | Pole-Wood | Broken, wire on object | 17-0010132 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | NARROWS-2102 | 153132102 | FUSE | 32993 | 20170118 | 2058 | 1648991 | 934 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 79390 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010489 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PENRYN-1103 | 152561103 | FUSE | 8909 | 20170118 | 1507 | 1646633 | 279 | Distribution Circuit | Vegetation | Tree - fell into line | 633 | 27919 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010100 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 21045 | 20170118 | 1541 | 1646804 | 1474 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5896 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010225 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 1555 | 20170118 | 2342 | 1649578 | 816 | Distribution Circuit | Vegetation | Tree - fell into line | 258 | 151576 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010698 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 30745 | 20170118 | 1554 | 1646615 | 1066 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 58630 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010188 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | FUSE | 6175 | 20170118 | 1731 | 1646477 | 380 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 22420 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010264 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | FUSE | 5365 | 20170118 | 1558 | 1646766 | 625 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 33750 | Partly Cloudy-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0010218 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | FUSE | 3255 | 20170118 | 1546 | 1646832 | 3130 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 62600 | Rain-Strong Winds-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 17-0010326 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | RECLOSER | 307494 | 20170118 | 2042 | 1648942 | 2527 | Distribution Circuit | Equipment Failure/Involved | Overhead | 266 | 196977 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010437 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE | 6375 | 20170119 | 133 | 1649725 | 2176 | Distribution Circuit | Vegetation | Tree - fell into line | 121 | 245124 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010744 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE | 69925 | 20170119 | 12 | 1649609 | 1110 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 31080 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010628 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | LINCOLN-1104 | 153701104 | FUSE | 37461 | 20170119 | 1023 | 1650642 | 1500 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4500 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010786 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6631 | 20170119 | 1227 | 1651144 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 69734 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on object | 17-0010918 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6617 | 20170119 | 1555 | 1651558 | 1271 | Distribution Circuit | Equipment Failure/Involved | Overhead | 54 | 68634 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011142 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BELL-1107 | 152701107 | FUSE | 9429 | 20170120 | 1030 | 1653713 | 1594 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 7300 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0011549 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER | #1 PHASE WIRE DOWN 4/S/OF 31909 | 20170120 | 827 | 1653712 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2020 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011445 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 4753 | 20170120 | 718 | 1652948 | 787 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 5509 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011592 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 2500 | 20170120 | 203 | 1652044 | 2589 | Distribution Circuit | Equipment Failure/Involved | Overhead | 246 | 327105 | Overcast-Snow-Below 32 F | Connector or Splice (OH) | Broken, wire on ground | 17-0011145 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1101 | 152101101 | JUMPER | JUMPERS 3/W/OF 7939 | 20170121 | 428 | 1661218 | 5041 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 15123 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013190 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER | WIRE DOWN E/OF 31909 | 20170121 | 648 | 1655705 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 68015 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011949 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 6521 | 20170121 | 1831 | 1659879 | 1350 | Distribution Circuit | Equipment Failure/Involved | Overhead | 123 | 166050 | Overcast-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0012930 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | SWITCH | 6523 | 20170121 | 1713 | 1659965 | 1469 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 45077 | Strong Winds-Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012948 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | RECLOSER | 2416 | 20170121 | 115 | 1655395 | 614 | Distribution Circuit | Vegetation | Tree - fell into line | 1309 | 160761 | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on object | 17-0011873 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | DRUM-1101 | 152321101 | FUSE | 30479 | 20170121 | 420 | 1655484 | 755 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3775 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0011882 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 22771 | 20170121 | 13 | 1655343 | 1045 | Distribution Circuit | Vegetation | Tree - fell into line | 450 | 300438 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0011867 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | EL DORADO PH-2101 | 152762101 | SWITCH | 13141 | 20170121 | 1154 | 1655261 | 7312 | Distribution Circuit | Vegetation | Tree - branch fell on line | 443 | 598639 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010893 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 93529 | 20170121 | 557 | 1655615 | 518 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 8409 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011929 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 35987 | 20170121 | 1117 | 1656404 | 623 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 48594 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0012150 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | RECLOSER | 12832 | 20170122 | 651 | 1659939 | 969 | Distribution Circuit | Vegetation | Tree - fell into line | 760 | 303638 | Partly Cloudy-Fog-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012943 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 8661 | 20170122 | 1951 | 1662238 | 882 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 35280 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013485 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | JUMPER | WIRE DOWN 1 LD SIDE OF 7047 | 20170122 | 1920 | 1662532 | 1244 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 15011 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013519 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 20371 | 20170122 | 1403 | 1661177 | 1737 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3474 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013239 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | JUMPER | WIRE ON GRD 1 1/2 SPAN W/O 18585 | 20170122 | 1854 | 1662147 | 383 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1174 | 304136 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013373 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 3 | DRUM-1101 | 152321101 | FUSE | 9217 | 20170122 | 330 | 1659270 | 2107 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 185416 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013185 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | OTHER | WIRE DOWN S SPANS LD SD 5829 | 20170122 | 2101 | 1662269 | 1407 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 116781 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013537 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | WISE-1102 | 152271102 | RECLOSER | 307494 | 20170122 | 450 | 1658832 | 435 | Distribution Circuit | Vegetation | Tree - fell into line | 267 | 53545 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012764 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE | 6685 | 20170123 | 721 | 1663029 | 2162 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 13164 | Snow-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013710 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 8372 | 20170123 | 710 | 1662972 | 1786 | Distribution Circuit | Vegetation | Tree - fell into line | 696 | 396322 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013612 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 1051 | 20170123 | 403 | 1663102 | 765 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 52020 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013628 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 22399 | 20170123 | 319 | 1662930 | 5194 | Distribution Circuit | Vegetation | Tree - fell into line | 254 | 986037 | Partly Cloudy-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0013630 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 20553 | 20170123 | 354 | 1663455 | 836 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 836 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013686 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21153 | 20170123 | 723 | 1663566 | 1808 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 19888 | Drizzle-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013698 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 21393 | 20170123 | 319 | 1664337 | 3713 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 33417 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0013876 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 20911 | 20170123 | 406 | 1664354 | 2129 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 6387 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013887 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 5121 | 20170123 | 1157 | 1663933 | 465 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 8835 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0014000 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 6761 | 20170123 | 1759 | 1664762 | 931 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2793 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013995 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER | 51486 | 20170123 | 800 | 1663148 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 1007 | 209089 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013655 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 2177 | 20170123 | 1429 | 1664345 | 1444 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 11552 | Partly Cloudy-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013975 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | DRUM-1101 | 152321101 | RECLOSER | 75874 | 20170123 | 110 | 1662624 | 2563 | Distribution Circuit | Equipment Failure/Involved | Overhead | 87 | 222981 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013556 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 3 | DRUM-1101 | 152321101 | RECLOSER | 1602 | 20170123 | 121 | 1662642 | 2429 | Distribution Circuit | Equipment Failure/Involved | Overhead | 105 | 203778 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013558 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 2 | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 2500 | 20170123 | 1829 | 1664813 | 1351 | Distribution Circuit | Equipment Failure/Involved | Overhead | 640 | 830590 | Overcast-Below 32 F | Crossarm, Wood | Broken, wire on ground | 17-0014026 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 19752 | 20170123 | 416 | 1662767 | 983 | Distribution Circuit | Vegetation | Tree - fell into line | 1142 | 383946 | Partly Cloudy-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013576 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 11791 | 20170123 | 349 | 1662723 | 3253 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 24010 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0014356 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | SECTIONALIZER | 1762 | 20170123 | 830 | 1663209 | 330 | Distribution Circuit | Vegetation | Tree - fell into line | 591 | 121954 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013678 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 2224 | 20170123 | 153 | 1662476 | 2115 | Distribution Circuit | Vegetation | Tree - fell into line | 896 | 491372 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | On Ground | 17-0013563 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER | 2200 | 20170207 | 633 | 1678716 | 938 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 66747 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018350 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1104 | 152481104 | FUSE | 7121 | 20170207 | 801 | 1678913 | 1837 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 99198 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018437 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7053 | 20170207 | 1548 | 1680568 | 1403 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 75762 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018698 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 9487 | 20170207 | 431 | 1677779 | 2016 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 26208 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018900 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | FUSE | 3673 | 20170207 | 708 | 1678445 | 1770 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4770 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018596 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 18497 | 20170207 | 1229 | 1680149 | 335 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 3685 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018623 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE | 5929 | 20170207 | 559 | 1678016 | 1997 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 15827 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018308 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 4487 | 20170207 | 48 | 1677300 | 997 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 24411 | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018042 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 4715 | 20170207 | 613 | 1678069 | 637 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 66885 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018258 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-1104 | 153651104 | FUSE | 20629 | 20170207 | 735 | 1678787 | 340 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 9520 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0018358 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 1149 | 20170209 | 2320 | 1684439 | 1101 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 105696 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019741 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER | OJ @ 34451 | 20170209 | 1244 | 1683408 | 229 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 229 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019423 | OH | Sus | 0 | 2017 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 8922 | 20170209 | 2159 | 1684259 | 1239 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 59472 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019708 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 6293 | 20170209 | 911 | 1682879 | 398 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 2944 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019309 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | RECLOSER | 12832 | 20170220 | 2327 | 1706706 | 1081 | Distribution Circuit | Equipment Failure/Involved | Overhead | 759 | 111751 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024784 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 3277 | 20170220 | 2301 | 1706611 | 1061 | Distribution Circuit | Vegetation | Tree - fell into line | 224 | 237664 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024798 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 6417 | 20170220 | 2036 | 1708834 | 2590 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 118828 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025187 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER | 2200 | 20170220 | 2310 | 1707254 | 2622 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 149454 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025005 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE | 33683 | 20170220 | 2258 | 1707124 | 1091 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 50186 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024796 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | CLARKSVILLE-2104 | 153612104 | FUSE | 2039 | 20170220 | 1947 | 1705719 | 1257 | Distribution Circuit | Vegetation | Tree - fell into line | 205 | 184993 | Overcast-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0024364 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 2500 | 20170220 | 2312 | 1706647 | 3899 | Distribution Circuit | Equipment Failure/Involved | Overhead | 293 | 450134 | Overcast-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0024714 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 18411 | 20170220 | 1943 | 1705704 | 996 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 72708 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024080 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | RECLOSER | 76178 | 20170220 | 2019 | 1705858 | 1505 | Distribution Circuit | Vegetation | Tree - fell into line | 613 | 649253 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024082 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | FUSE | 6225 | 20170220 | 2113 | 1706118 | 1336 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 13360 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024721 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1109 | 152691109 | FUSE | 7863 | 20170220 | 2205 | 1706301 | 883 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 42384 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024793 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1111 | 153081111 | FUSE | 2507 | 20170220 | 2341 | 1706752 | 844 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 10256 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024815 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 1104 | 20170220 | 1924 | 1705555 | 1481 | Distribution Circuit | Equipment Failure/Involved | Overhead | 645 | 573918 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024047 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 4655 | 20170220 | 2153 | 1706251 | 1777 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 56864 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024857 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SIERRA CITY DIESEL-1101 | 158011101 | RECLOSER | 978 | 20170220 | 2006 | 1707364 | 14116 | Distribution Circuit | Vegetation | Tree - fell into line | 554 | 1789554 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025679 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SUMMIT-1101 | 152591101 | SECTIONALIZER | 48632 | 20170220 | 2040 | 1706415 | 3965 | Distribution Circuit | Vegetation | Tree - fell into line | 238 | 505460 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024705 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SUMMIT-1102 | 152591102 | FUSE | 6813 | 20170220 | 909 | 1702805 | 4973 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 14919 | Overcast-Snow-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0023949 | OH | Sus | 0 | 2017 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 2 | SUMMIT-1102 | 152591102 | RECLOSER | 49484 | 20170220 | 2303 | 1706446 | 2397 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 89981 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024702 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 4383 | 20170221 | 204 | 1707324 | 723 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 58563 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024960 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 6279 | 20170221 | 150 | 1707161 | 1042 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 55226 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0025071 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7025 | 20170221 | 223 | 1707223 | 687 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 20307 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024881 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE | 33279 | 20170221 | 1145 | 1708413 | 1648 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 19776 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025160 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | FUSE | 33687 | 20170221 | 737 | 1707723 | 1798 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 26970 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024972 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | ECHO SUMMIT-1101 | 158031101 | FUSE | 12861 | 20170221 | 1452 | 1711171 | 4195 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 20975 | Partly Cloudy-Below 32 F | Crossarm, Wood | Broken, wire on ground | 17-0025739 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 18415 | 20170221 | 1217 | 1708496 | 1493 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 19409 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025147 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 7583 | 20170221 | 224 | 1708238 | 1981 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8798 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025185 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | LINCOLN-1101 | 153701101 | FUSE | 9415 | 20170221 | 153 | 1707165 | 2347 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4694 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024864 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 6943 | 20170221 | 620 | 1707480 | 1858 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 42734 | Overcast-Fog-Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025166 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 1261 | 20170221 | 351 | 1707321 | 2042 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 55134 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024990 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 20679 | 20170221 | 1011 | 1708200 | 912 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 7296 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025175 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SUMMIT-1102 | 152591102 | FUSE | 6829 | 20170221 | 2308 | 1709592 | 2580 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 10320 | Overcast-Snow-Below 32 F | Conductor, Overhead | On Ground | 17-0026002 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 6193 | 20170221 | 26 | 1706854 | 2503 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 120144 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025208 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | FUSE | 6399 | 20170221 | 142 | 1707147 | 993 | Distribution Circuit | Vegetation | Tree - fell into line | 221 | 165903 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024841 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21461 | 20170222 | 1236 | 1710649 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1542 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025604 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | ECHO SUMMIT-1101 | 158031101 | OTHER | 8922 | 20170222 | 1129 | 1710507 | 238 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 11186 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025542 | OH | Sus | 0 | 2017 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | RECLOSER | 97982 | 20170406 | 2233 | 1748398 | 842 | Distribution Circuit | Vegetation | Tree - fell into line | 753 | 422384 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037397 | OH | Sus | 31318176 | 2017 | APR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 7117 | 20170406 | 2222 | 1748343 | 1299 | Distribution Circuit | Vegetation | Tree - fell into line | 155 | 201345 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037746 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1104 | 152481104 | RECLOSER | 2112 | 20170406 | 2102 | 1747359 | 1033 | Distribution Circuit | Vegetation | Tree - fell into line | 505 | 277904 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037304 | OH | Sus | 42985912 | 2017 | APR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 7079 | 20170406 | 2009 | 1746543 | 840 | Distribution Circuit | Vegetation | Tree - branch fell on line | 308 | 258720 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037315 | OH | Sus | 42985909 | 2017 | APR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1101 | 152031101 | FUSE | 8185 | 20170406 | 2115 | 1747621 | 1054 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5620 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037317 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | NARROWS-2102 | 153132102 | FUSE | 7437 | 20170406 | 2347 | 1750120 | 1643 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 23002 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037945 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1110 | 152691110 | JUMPER | HOT WIRE DOWN AT MTR 1009741819 | 20170407 | 809 | 1750085 | 227 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 2985 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037675 | OH | Sus | 0 | 2017 | APR | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE | 6303 | 20170407 | 51 | 1749080 | 974 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 22138 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037549 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 22595 | 20170407 | 2052 | 1751947 | 934 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 15878 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038159 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACER-1103 | 152461103 | JUMPER | OJ @ MTR#1009206068 | 20170903 | 717 | 1867829 | 218 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 218 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0075507 | OH | Sus | 31349005 | 2017 | SEP | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE | 7123 | 20171008 | 2303 | 1894177 | 2350 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 30550 | Clear-32-90 F | Pole-Wood | Broken, wire on object | 17-0085778 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 31865 | 20171008 | 2209 | 1894021 | 2127 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2229 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085266 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | RECLOSER | 2664 | 20171008 | 2325 | 1894346 | 1044 | Distribution Circuit | Vegetation | Tree - fell into line | 1759 | 252040 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085282 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 5357 | 20171008 | 1931 | 1893744 | 2723 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 46291 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085204 | OH | Sus | 43169673 | 2017 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | SWITCH | 879 | 20171008 | 2258 | 1894156 | 978 | Distribution Circuit | Vegetation | Tree - fell into line | 223 | 198802 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0085355 | OH | Sus | 31355729 | 2017 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE | 7835 | 20171008 | 2347 | 1894921 | 4128 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 41 | 169248 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086029 | OH | Sus | 0 | 2017 | OCT | Yes | None | Yes | No
SIERRA | Tier 2 | NARROWS-2102 | 153132102 | JUMPER | JUMPERS 1/S/E OF 3987 | 20171008 | 2327 | 1897902 | 5463 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 29043 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086150 | OH | Sus | 31360786 | 2017 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | JUMPER | JUMPERS 1/N/E OF MTR# 1007521741 | 20171008 | 2343 | 1897875 | 3677 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 5 | 18385 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086143 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 4529 | 20171008 | 2352 | 1897935 | 5230 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 125520 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0086158 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | JUMPER | WIRE DOWN AT SPRING AND MILL | 20171008 | 2110 | 1894011 | 1098 | Distribution Circuit | Vegetation | Tree - fell into line | 258 | 255784 | Clear-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0085261 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 3579 | 20171008 | 2153 | 1896299 | 1357 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 17773 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085527 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 5801 | 20171008 | 2108 | 1893857 | 1312 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 10496 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085600 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 21931 | 20171009 | 920 | 1896202 | 408 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 2438 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085492 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE | 6003 | 20171009 | 1945 | 1897030 | 174 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 174 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085795 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | OCB | 1103/2 | 20171009 | 124 | 1894576 | 4031 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1424 | 2445169 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085336 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | JUMPER | JUMPERS LD SIDE OF MTR#1008936587 | 20171009 | 104 | 1897872 | 5033 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 56 | 281848 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086141 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | SWITCH | 34463 | 20171009 | 104 | 1899353 | 5488 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 5488 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086747 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SUMMIT-1101 | 152591101 | TRIP-SAVER | 6627 | 20171009 | 427 | 1895640 | 507 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 23322 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085436 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | OTHER | WIRE DOWN, 1 CONDUCTOR 2 P W/O 33617 | 20171020 | 119 | 1905467 | 706 | Distribution Circuit | Equipment Failure/Involved | Overhead | 155 | 102410 | Overcast-Fog-Heavy Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0088957 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7053 | 20171020 | 108 | 1904968 | 2488 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 47369 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0089061 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7645 | 20171204 | 1032 | 1934860 | 1328 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 30299 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0099679 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1102 | 152101102 | RECLOSER | 1102/2 | 20171216 | 1122 | 1944589 | 3283 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 58853 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102021 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BELL-1108 | 152701108 | FUSE | 9927 | 20171216 | 1611 | 1945541 | 163 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 2659 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102185 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SUMMIT-1101 | 152591101 | FUSE | 6625 | 20171216 | 940 | 1944327 | 393 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 6288 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102011 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6631 | 20171216 | 2221 | 1946009 | 1138 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 30601 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0102266 | OH | Sus | 35024126 | 2017 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER | 804 | 20180316 | 516 | 45306 | 848 | Distribution Circuit | Vegetation | Tree - fell into line | 603 | 157730 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023258 | OH | Sus | 0 | 2018 | MAR | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 2825 | 20180316 | 859 | 45398 | 1192 | Distribution Circuit | Vegetation | Tree - fell into line | 126 | 198450 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023498 | OH | Sus | 0 | 2018 | MAR | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 2491 | 20180316 | 1523 | 46098 | 1541 | Distribution Circuit | Vegetation | Tree - fell into line | 247 | 65694 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0023752 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 6521 | 20180316 | 804 | 45335 | 2068 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 102268 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023318 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 20685 | 20180316 | 1333 | 45927 | 1532 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 12256 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023501 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | ECHO SUMMIT-1101 | 158031101 | FUSE | 1571 | 20180316 | 738 | 45625 | 4673 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 322437 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0023361 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | OCB | 2101/2 | 20180316 | 1225 | 45766 | 1706 | Distribution Circuit | Vegetation | Tree - fell into line | 2184 | 777200 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023399 | OH | Sus | 0 | 2018 | MAR | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 6797 | 20180316 | 950 | 46111 | 3337 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 90099 | Overcast-Fog-Snow-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0023538 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 6799 | 20180316 | 1140 | 46114 | 1979 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 120719 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0023539 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 2391 | 20180316 | 842 | 46170 | 3015 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 93465 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023563 | OH | Sus | 0 | 2018 | MAR | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 1385 | 20180316 | 834 | 47271 | 3461 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 10383 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023873 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | RECLOSER | 19612 | 20180316 | 820 | 45315 | 3571 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1257 | 2290224 | Overcast-Fog-Snow-32-90 F | Crossarm, Wood | Broken, wire on object | 18-0023279 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 18511 | 20180316 | 1003 | 45615 | 3470 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 262819 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023411 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 10987 | 20180316 | 1141 | 45734 | 1913 | Distribution Circuit | Environmental/External | Ice or snow | 95 | 181735 | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 18-0023586 | OH | Sus | 0 | 2018 | MAR | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | OCB | 2102/2 | 20180316 | 2036 | 46283 | 1476 | Distribution Circuit | Vegetation | Tree - fell into line | 3242 | 622369 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 18-0023620 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 13059 | 20180316 | 1533 | 46268 | 2749 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 131952 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023723 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 20829 | 20180316 | 1145 | 45676 | 3268 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 13072 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023750 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | JUMPER | OJ'S AT MTR# 1007479834 | 20180316 | 1141 | 46981 | 2936 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 23488 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0023800 | OH | Sus | 0 | 2018 | MAR | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 787997 | 20180316 | 918 | 45439 | 975 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 10725 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 18-0023446 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 92903 | 20180728 | 633 | 142227 | 417 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 15429 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0064545 | OH | Sus | 0 | 2018 | JUL | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 4819 | 20181014 | 1815 | 194986 | 1048 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 8688 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0090287 | OH | Sus | 43506621 | 2018 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7673 | 20181129 | 1000 | 228573 | 483 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 6762 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0104944 | OH | Sus | 31416672 | 2018 | NOV | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 7755 | 20181129 | 1032 | 228677 | 656 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 11152 | Partly Cloudy-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0105035 | OH | Sus | 0 | 2018 | NOV | Yes | Force Out | Yes | Yes
SIERRA | Tier 2 | SUMMIT-1102 | 152591102 | OCB | 1102/2 | 20181129 | 1133 | 228831 | 1448 | Distribution Circuit | Equipment Failure/Involved | Overhead | 292 | 64558 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105014 | OH | Sus | 0 | 2018 | NOV | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 11427 | 20190106 | 1854 | 256757 | 1013 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 8448 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005388 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BELL-1108 | 152701108 | FUSE | 5773 | 20190106 | 1408 | 255378 | 467 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 18213 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005098 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 6415 | 20190106 | 2105 | 258055 | 1051 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 21233 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005481 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 4693 | 20190106 | 2014 | 257526 | 963 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5778 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005419 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER | 2130 | 20190106 | 1811 | 256324 | 987 | Distribution Circuit | Equipment Failure/Involved | Overhead | 207 | 19399 | Snow-Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005255 | OH | Sus | 43626490 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PIKE CITY-1102 | 152201102 | FUSE | 8801 | 20190106 | 1801 | 256154 | 2934 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 79218 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005852 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1110 | 153081110 | JUMPER | OJ 1/E/O 21681 | 20190106 | 2019 | 257563 | 1028 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6168 | Overcast-Fog-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005457 | OH | Sus | 0 | 2019 | JAN | Yes | None | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | RECLOSER | 2058 | 20190106 | 2033 | 257875 | 1091 | Distribution Circuit | Vegetation | Tree - fell into line | 408 | 107385 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005518 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | OTHER | WIRE DOWN @ 3777 DOGWOOD | 20190116 | 2333 | 272041 | 2762 | Distribution Circuit | Vegetation | Tree - fell into line | 450 | 291918 | Overcast-Fog-Heavy Rain-Lightning-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010662 | OH | Sus | 0 | 2019 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 186912 | 20190116 | 2325 | 271904 | 2462 | Distribution Circuit | Vegetation | Tree - fell into line | 1172 | 754567 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0010402 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 11937 | 20190116 | 2336 | 271987 | 2391 | Distribution Circuit | Vegetation | Tree - fell into line | 173 | 165864 | Overcast-Fog-Heavy Rain-Lightning-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010542 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 2019 | 20190116 | 2329 | 273570 | 2456 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 50671 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010884 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | JUMPER | OJ'S 1 E/O 18833 | 20190116 | 2325 | 273614 | 1300 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 11700 | Overcast-Fog-Heavy Rain-Lightning-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010901 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 20033 | 20190116 | 2338 | 272817 | 1357 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 16284 | Partly Cloudy-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010989 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 10303 | 20190116 | 2329 | 273883 | 2504 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 12520 | Overcast-Fog-Heavy Rain-Lightning-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0010995 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 95655 | 20190116 | 2329 | 273898 | 2381 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4762 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010999 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 11657 | 20190116 | 2325 | 274204 | 2463 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 78816 | Overcast-Fog-Snow-Strong Winds-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0011110 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 1055 | 20190116 | 2345 | 272796 | 2477 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 86695 | Partly Cloudy-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011168 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 37441 | 20190116 | 2134 | 271170 | 821 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 80458 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010352 | OH | Sus | 31422233 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 31887 | 20190116 | 2259 | 271766 | 1371 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2742 | Lightning-Fog-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0010448 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 764 | 20190116 | 2132 | 271190 | 1388 | Distribution Circuit | Vegetation | Tree - fell into line | 256 | 337277 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010290 | OH | Sus | 43635519 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 13217 | 20190116 | 2332 | 271920 | 2386 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 11930 | Overcast-Fog-Heavy Rain-Lightning-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011802 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 63464 | 20190116 | 2346 | 272052 | 3719 | Distribution Circuit | Vegetation | Tree - fell into line | 1155 | 196676 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010424 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 9991 | 20190116 | 2315 | 271824 | 2238 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 40284 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010711 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 18401 | 20190116 | 2334 | 272263 | 979 | Distribution Circuit | Vegetation | Tree - fell into line | 117 | 37439 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010493 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | FORESTHILL-1102 | 152181102 | RECLOSER | 1102/2 | 20190116 | 1956 | 270326 | 938 | Distribution Circuit | Equipment Failure/Involved | Overhead | 423 | 100008 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010162 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 32761 | 20190116 | 2003 | 270324 | 1286 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 10288 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0010268 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 9737 | 20190116 | 2229 | 271618 | 1118 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 80496 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010488 | OH | Sus | 31422233 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1109 | 152691109 | FUSE | 3173 | 20190116 | 2350 | 272043 | 1327 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 14764 | Partly Cloudy-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010946 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1109 | 152691109 | TRIP-SAVER | 7831 | 20190116 | 2159 | 271401 | 2489 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 151810 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011009 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1110 | 152691110 | OTHER | WIRE DOWN 1 S/O 35307 | 20190116 | 1922 | 269727 | 935 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 18813 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010314 | OH | Sus | 43635519 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | NARROWS-2102 | 153132102 | RECLOSER | 2718 | 20190116 | 823 | 266550 | 689 | Distribution Circuit | Vegetation | Tree - fell into line | 1173 | 78141 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0009441 | OH | Sus | 31422068 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | RECLOSER | 2748 | 20190116 | 849 | 266596 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 886 | 65200 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0009451 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20190116 | 1747 | 268772 | 1579 | Distribution Circuit | Vegetation | Tree - fell into line | 1026 | 265796 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009985 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 6161 | 20190116 | 2324 | 271875 | 2301 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 62127 | Partly Cloudy-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011166 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 12573 | 20190117 | 1335 | 275935 | 2880 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 11520 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011849 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | TRIP-SAVER | 12025 | 20190117 | 1100 | 273887 | 1679 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 71964 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010996 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21319 | 20190117 | 8 | 272652 | 2431 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 13340 | Overcast-Fog-Heavy Rain-Lightning-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011242 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BELL-1107 | 152701107 | FUSE | 4857 | 20190117 | 1124 | 273831 | 494 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 2214 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010979 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE | 6379 | 20190117 | 2 | 272663 | 2247 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 31458 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011243 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 31895 | 20190117 | 747 | 272918 | 1718 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3436 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011808 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 8483 | 20190117 | 205 | 272316 | 764 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 40478 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010875 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 41595 | 20190117 | 350 | 273552 | 1875 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3750 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011388 | OH | Sus | 43635519 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 5503 | 20190117 | 804 | 276146 | 2005 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 6015 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011945 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 4105 | 20190117 | 950 | 273445 | 1504 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 16544 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010912 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 20865 | 20190117 | 622 | 272650 | 1908 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9540 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011302 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 21033 | 20190117 | 432 | 272492 | 793 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 25376 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010870 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | FUSE | 6263 | 20190117 | 651 | 272716 | 459 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2295 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010857 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | FUSE | 30657 | 20190117 | 50 | 272208 | 863 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 14671 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010881 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE | 6413 | 20190204 | 2314 | 291191 | 6336 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 272706 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018389 | OH | Sus | 31424310 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 22085 | 20190204 | 2120 | 291112 | 2701 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 216439 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018728 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | OCB | 2102/2 | 20190204 | 2005 | 290949 | 5496 | Distribution Circuit | Vegetation | Tree - fell into line | 3456 | 14931003 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018147 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 13247 | 20190204 | 2005 | 291125 | 4244 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 72148 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018188 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 1333 | 20190204 | 2005 | 293649 | 4002 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 100050 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018747 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 2133 | 20190204 | 2005 | 293740 | 4016 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 124496 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018781 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 13243 | 20190204 | 2005 | 294010 | 3966 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 106890 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019027 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 24137 | 20190204 | 2005 | 294332 | 6834 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 20502 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0019176 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | JUMPER | OJ 1 SPAN N/W/O CGC 5185 | 20190204 | 2005 | 294337 | 6798 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 115566 | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0019177 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 11491 | 20190204 | 2005 | 294365 | 5363 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 316417 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0019193 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 12187 | 20190204 | 2005 | 294581 | 8451 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 267929 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019309 | OH | Sus | 31424310 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 12691 | 20190204 | 2005 | 294665 | 5579 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 89264 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0019331 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | JUMPER | OJ 1 SPAN E/O CGC 5160 | 20190204 | 2005 | 294691 | 5365 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 10730 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0019340 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 11793 | 20190204 | 2005 | 294948 | 4911 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 39288 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0019438 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 10597 | 20190204 | 2005 | 294961 | 5382 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 113022 | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0019444 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 21415 | 20190204 | 1805 | 291035 | 10056 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 181008 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019448 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 21407 | 20190204 | 2005 | 295068 | 9972 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 129636 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019500 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 10225 | 20190204 | 2005 | 295030 | 7080 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 182939 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0019538 | OH | Sus | 31424310 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 21403 | 20190204 | 2005 | 295530 | 9917 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 29751 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019731 | OH | Sus | 31424310 | 2019 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 21393 | 20190204 | 2005 | 300051 | 10365 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 93285 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0021148 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | OTHER | WIRE DOWN 1 E/O 38643 | 20190204 | 801 | 289699 | 464 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4440 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0017821 | OH | Sus | 31424257 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 1299 | 20190204 | 457 | 289476 | 533 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 36777 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017722 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 18797 | 20190204 | 835 | 289722 | 650 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 21450 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017832 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 13097 | 20190204 | 1225 | 290256 | 1340 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 21081 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018008 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 21933 | 20190204 | 2313 | 294151 | 2557 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 25570 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019079 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | EL DORADO PH-2101 | 152762101 | RECLOSER | 507864 | 20190204 | 1607 | 290684 | 7371 | Distribution Circuit | Environmental/External | Ice or snow | 1487 | 6904706 | Overcast-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018081 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | OTHER | WIRE DOWN 1 S/O MTR 1005208316 | 20190204 | 2205 | 291576 | 4030 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 247513 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018240 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 12645 | 20190204 | 1608 | 291138 | 2943 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 258984 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018681 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 13251 | 20190204 | 2337 | 291206 | 3352 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 97208 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0019229 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | FUSE | 311367 | 20190204 | 755 | 289665 | 312 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 2216 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017836 | OH | Sus | 31424320 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1103 | 153661103 | OTHER | WIRE DOWN 1 SPAN LD SIDE OF CGC #22367243816 | 20190205 | 15 | 291233 | 806 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2418 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018225 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | JUMPER | OJS 1 P/W/O 11445 ON TAP | 20190205 | 600 | 292502 | 2040 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4080 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018446 | OH | Sus | 31424310 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1103 | 153661103 | FUSE | 18469 | 20190205 | 1347 | 292792 | 2938 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5876 | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0018585 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE | 12097 | 20190205 | 1237 | 292672 | 399 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 26 | 10374 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018656 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE | 41067 | 20190205 | 1400 | 292936 | 1485 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5430 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018706 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE | 6387 | 20190205 | 1348 | 293048 | 4467 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 56457 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0018707 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE | 1427 | 20190205 | 1351 | 293066 | 2769 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 11076 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018750 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1103 | 153661103 | FUSE | 18475 | 20190205 | 1415 | 294177 | 3233 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 64660 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0019096 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1103 | 153661103 | FUSE | 18473 | 20190205 | 328 | 291689 | 3699 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 77679 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0019102 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1103 | 153661103 | OTHER | HOT WIRE DOWN 7 S/O 6633 | 20190205 | 1412 | 294330 | 2965 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 125536 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0019175 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE | 1467 | 20190205 | 1348 | 292795 | 1602 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 86508 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on object | 19-0019209 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1103 | 153661103 | FUSE | 18477 | 20190205 | 1359 | 295750 | 4321 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 25926 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0019791 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | RECLOSER | 12832 | 20190205 | 808 | 291613 | 5953 | Distribution Circuit | Vegetation | Tree - fell into line | 423 | 1188276 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018316 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE | 1313 | 20190205 | 142 | 292643 | 2622 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 65550 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018506 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 94593 | 20190205 | 523 | 291644 | 2182 | Distribution Circuit | Vegetation | Tree - bark fell into line | 11 | 24002 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018699 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | RECLOSER | 2100 | 20190205 | 632 | 291764 | 1868 | Distribution Circuit | Environmental/External | Ice or snow | 633 | 801734 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018273 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 2167 | 20190205 | 632 | 293117 | 3605 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 439810 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018726 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 20351 | 20190205 | 2259 | 293786 | 1006 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8048 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018799 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 11321 | 20190205 | 1358 | 292986 | 2976 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 32736 | Overcast-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0018886 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 1161 | 20190205 | 119 | 294139 | 5082 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 696234 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019070 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 18797 | 20190205 | 119 | 294496 | 5082 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 167706 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019265 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 26000 | 20190205 | 507 | 291626 | 6324 | Distribution Circuit | Environmental/External | Ice or snow | 655 | 3029661 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018257 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 6852 | 20190205 | 916 | 291952 | 2773 | Distribution Circuit | Vegetation | Tree - fell into line | 1442 | 1454949 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018370 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | OCB | 2102/2 | 20190205 | 731 | 291874 | 681 | Distribution Circuit | Vegetation | Tree - fell into line | 1649 | 512931 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018302 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1111 | 153081111 | SWITCH | 52599 | 20190205 | 611 | 292222 | 899 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 45849 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018387 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | OTHER | WIRE DOWN SOURCE SIDE OF 5833 | 20190205 | 855 | 292101 | 340 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2360 | 89237 | Overcast-Fog-Snow-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0018473 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 12613 | 20190205 | 620 | 291730 | 1932 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 197064 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018646 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1102 | 152101102 | RECLOSER | 1102/2 | 20190209 | 1928 | 297365 | 5097 | Distribution Circuit | Vegetation | Tree - fell into line | 164 | 283891 | Overcast-Fog-Snow-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020403 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | OCB | 1103/2 | 20190209 | 1826 | 297302 | 2624 | Distribution Circuit | Vegetation | Tree - fell into line | 1824 | 194084 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020394 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 18559 | 20190209 | 2144 | 297460 | 2327 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 41886 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020476 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE | 6377 | 20190209 | 2057 | 297424 | 1285 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 147775 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020473 | OH | Sus | 31424320 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 30711 | 20190209 | 2057 | 297419 | 2787 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 256404 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0020420 | OH | Sus | 31424320 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 5749 | 20190209 | 1830 | 299268 | 2657 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5314 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on object | 19-0020807 | OH | Sus | 31424320 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER | 51486 | 20190209 | 2110 | 297435 | 959 | Distribution Circuit | Vegetation | Tree - fell into line | 1059 | 394653 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020434 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 18619 | 20190209 | 2224 | 297491 | 1258 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 11322 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0020544 | OH | Sus | 43666953 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1107 | 152261107 | FUSE | 41463 | 20190209 | 2308 | 297566 | 966 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 42504 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020560 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 11791 | 20190209 | 2339 | 297587 | 2326 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 27912 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020669 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 20869 | 20190209 | 1522 | 305017 | 7228 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 36140 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0022378 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 1385 | 20190209 | 1522 | 305286 | 7344 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 22032 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0022473 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | OCB | 2102/2 | 20190209 | 2249 | 297461 | 4141 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1097 | 3128800 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020499 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 18501 | 20190209 | 2148 | 299064 | 2740 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 87680 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020748 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 18407 | 20190209 | 2115 | 299702 | 4235 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 38115 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020958 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 18401 | 20190209 | 2115 | 299860 | 4235 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 160930 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021032 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | TRIP-SAVER | 5731 | 20190209 | 2040 | 297407 | 1050 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 97650 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020450 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | APPLE HILL-1103 | 153661103 | OTHER | WIRE DOWN 1 W/O 223655138715 | 20190210 | 16 | 297828 | 2274 | Distribution Circuit | Vegetation | Tree - fell into line | 233 | 395822 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020529 | OH | Sus | 43666953 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 20190210 | 804 | 297872 | 2154 | Distribution Circuit | Vegetation | Tree - fell into line | 640 | 326964 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020600 | OH | Sus | 31424310 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 18553 | 20190210 | 117 | 297773 | 3478 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 76516 | Overcast-Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0020799 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 3369 | 20190210 | 352 | 298337 | 3548 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 24836 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020831 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 7963 | 20190210 | 352 | 299366 | 3525 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 52875 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020834 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 7965 | 20190210 | 352 | 299195 | 3563 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 99764 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0021142 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 186912 | 20190210 | 657 | 298148 | 615 | Distribution Circuit | Vegetation | Tree - fell into line | 1215 | 81335 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020572 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 21505 | 20190210 | 1446 | 299068 | 1461 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 100809 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020887 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 10987 | 20190210 | 1626 | 299177 | 2548 | Distribution Circuit | Vegetation | Tree - branch fell on line | 103 | 128114 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0021011 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 6123 | 20190210 | 1152 | 298880 | 3245 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 113575 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0021026 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | RECLOSER | 1101/2 | 20190210 | 224 | 297571 | 946 | Distribution Circuit | Equipment Failure/Involved | Overhead | 399 | 273390 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0020521 | OH | Sus | 31424320 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | OTHER | WIRE DOWN 1 SP N/O 44675 | 20190210 | 343 | 297900 | 526 | Distribution Circuit | Vegetation | Tree - fell into line | 139 | 72376 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020643 | OH | Sus | 31424320 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | SWITCH | 6433 | 20190210 | 1238 | 298919 | 194 | Distribution Circuit | Environmental/External | Ice or snow | 127 | 24638 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020703 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 130441 | 20190210 | 1855 | 299288 | 1275 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4979 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020821 | OH | Sus | 31424320 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 26000 | 20190210 | 114 | 297664 | 3680 | Distribution Circuit | Vegetation | Tree - fell into line | 655 | 99252 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020501 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 6795 | 20190210 | 333 | 298342 | 2233 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 44660 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020598 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 4741 | 20190210 | 125 | 298784 | 6625 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 72875 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020667 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 22391 | 20190210 | 333 | 298897 | 922 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 7376 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020690 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 1273 | 20190210 | 213 | 299062 | 2059 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12354 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020745 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 1104 | 20190210 | 107 | 297594 | 2487 | Distribution Circuit | Vegetation | Tree - fell into line | 658 | 491996 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020496 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 1104 | 20190210 | 428 | 297836 | 2276 | Distribution Circuit | Vegetation | Tree - fell into line | 479 | 389929 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020496 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE | 20849 | 20190212 | 2325 | 301511 | 4050 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 48600 | Overcast-Drizzle-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0021897 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | OTHER | WIRE DOWN N/O 80645 | 20190212 | 2154 | 301255 | 952 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1711 | 148676 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021637 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 2661 | 20190212 | 2239 | 301383 | 1071 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 100674 | Overcast-Drizzle-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0021874 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 6411 | 20190212 | 758 | 300407 | 518 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 23752 | Partly Cloudy-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0021345 | OH | Sus | 31424320 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 6407 | 20190212 | 2147 | 301343 | 922 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 117015 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021859 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 20190212 | 2248 | 301407 | 735 | Distribution Circuit | Vegetation | Tree - fell into line | 1517 | 170849 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021653 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | PENRYN-1105 | 152561105 | FUSE | 5893 | 20190212 | 2258 | 301454 | 1023 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 11882 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022266 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PIKE CITY-1102 | 152201102 | OTHER | WIRE DOWN 8 SPANS SS OF 8801 | 20190212 | 1213 | 300654 | 1712 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 46224 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021425 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER | 808 | 20190213 | 854 | 303404 | 2913 | Distribution Circuit | Vegetation | Tree - fell into line | 387 | 414101 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021943 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 10023 | 20190213 | 304 | 302351 | 989 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 3956 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022505 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | OTHER | WIRE DOWN 2 LD SIDE 10463 | 20190213 | 1526 | 305256 | 140 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 3982 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021637 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | CLARKSVILLE-2103 | 153612103 | FUSE | 10979 | 20190213 | 848 | 303310 | 1727 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6908 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022175 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9313 | 20190213 | 1713 | 305363 | 1050 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5250 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022544 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 32419 | 20190213 | 337 | 302511 | 648 | Distribution Circuit | Vegetation | Tree - fell into line | 928 | 68664 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021817 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 8372 | 20190214 | 810 | 307642 | 494 | Distribution Circuit | Vegetation | Tree - fell into line | 712 | 136054 | Overcast-Drizzle-32-90 F | Capacitor | Broken, wire on ground | 19-0022910 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 7959 | 20190214 | 819 | 307726 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 194 | 38182 | Overcast-Fog-Heavy Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023109 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 21485 | 20190214 | 2000 | 310790 | 1162 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4648 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023669 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE | 9063 | 20190214 | 820 | 307717 | 2161 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 30254 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023299 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER | 2200 | 20190214 | 811 | 307702 | 2065 | Distribution Circuit | Vegetation | Tree - fell into line | 988 | 493014 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022925 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 8893 | 20190214 | 1630 | 310190 | 1630 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 22260 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | On Ground | 19-0023817 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 3605 | 20190214 | 216 | 306358 | 2331 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 27972 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022843 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE | 8677 | 20190214 | 322 | 306770 | 2353 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 91767 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022976 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | DIAMOND SPRINGS-1104 | 152261104 | FUSE | 18807 | 20190214 | 749 | 307494 | 1811 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 14488 | Overcast-Drizzle-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0023294 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 4595 | 20190214 | 846 | 307913 | 734 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 17765 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023077 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | RECLOSER | 32120 | 20190214 | 122 | 306138 | 1045 | Distribution Circuit | Vegetation | Tree - fell into line | 1660 | 501037 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022733 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 31299 | 20190214 | 329 | 306570 | 3541 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 21246 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023576 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 30377 | 20190214 | 1918 | 310859 | 1253 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 12530 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023744 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5869 | 20190214 | 633 | 307197 | 817 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 7353 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023580 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 5833 | 20190214 | 721 | 307366 | 681 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 13626 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023516 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 1319 | 20190214 | 313 | 306513 | 967 | Distribution Circuit | Vegetation | Tree - fell into line | 211 | 137201 | Overcast-Drizzle-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0023200 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 58241 | 20190214 | 246 | 306426 | 1086 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 17376 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023618 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | FUSE | 5401 | 20190214 | 304 | 306487 | 450 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 13500 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022782 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | OTHER | HOT WIRE DOWN | 20190215 | 1859 | 313126 | 1011 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 35000 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024353 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | RECLOSER | 19562 | 20190215 | 2231 | 313131 | 917 | Distribution Circuit | Vegetation | Tree - fell into line | 504 | 80245 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024355 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | RECLOSER | 76178 | 20190215 | 138 | 311107 | 838 | Distribution Circuit | Vegetation | Tree - fell into line | 621 | 241224 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023772 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 3083 | 20190215 | 125 | 311100 | 743 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 31949 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023780 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 7965 | 20190216 | 652 | 313518 | 4835 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 135380 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024509 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | RECLOSER | 97982 | 20190216 | 509 | 313269 | 5084 | Distribution Circuit | Vegetation | Tree - fell into line | 686 | 424731 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0024386 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE | 6389 | 20190216 | 1822 | 314938 | 2679 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 16074 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024752 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 62847 | 20190216 | 2312 | 315155 | 1239 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6195 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025018 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 1309 | 20190216 | 1033 | 313872 | 226 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 4520 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024545 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | SWITCH | 21275 | 20190216 | 1527 | 315874 | 3148 | Distribution Circuit | Vegetation | Tree - fell into line | 307 | 608094 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025143 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 7091 | 20190216 | 839 | 313702 | 341 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 5797 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024444 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 18401 | 20190216 | 405 | 314041 | 3586 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 54053 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024518 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | OTHER | WIRE DOWN @ MTR# 1008772529 | 20190216 | 359 | 313468 | 684 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 24884 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024393 | OH | Sus | 31424320 | 2019 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | OTHER | WIRE DOWN 6 POLES SS/O 32001 | 20190216 | 130 | 313722 | 1473 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 115880 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024463 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 30801 | 20190216 | 731 | 313538 | 2048 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4096 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024475 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PIKE CITY-1102 | 152201102 | FUSE | 8801 | 20190216 | 325 | 315723 | 2300 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 62097 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025115 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 1104 | 20190216 | 1154 | 314164 | 3428 | Distribution Circuit | Vegetation | Tree - fell into line | 475 | 656583 | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0024541 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 6903 | 20190216 | 937 | 315158 | 3565 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 28520 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0024963 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | JUMPER | OJ'S 3 E/O 3440 WOODPECKER CT | 20190216 | 422 | 318138 | 5096 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 20384 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025734 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | OTHER | WIRE DOWN SS OF 12221 | 20190217 | 1630 | 316643 | 1227 | Distribution Circuit | Vegetation | Tree - fell into line | 2378 | 76952 | Partly Cloudy-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025299 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 21145 | 20190217 | 328 | 315218 | 504 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 6552 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0025044 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 2825 | 20190217 | 1027 | 315576 | 103 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 10094 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025117 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 21495 | 20190217 | 1024 | 315786 | 198 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 5544 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025120 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 7959 | 20190217 | 1038 | 315614 | 1597 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 88903 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0025178 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE | 7353 | 20190217 | 810 | 316019 | 1750 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 21000 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025179 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE | 6391 | 20190217 | 810 | 316026 | 3305 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 128895 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025180 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 6421 | 20190217 | 1031 | 316476 | 2060 | Distribution Circuit | Vegetation | Tree - grew into line | 7 | 14420 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025239 | OH | Sus | 31424320 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | OTHER | WIRE DOWN @ 3619 | 20190217 | 1115 | 315675 | 3169 | Distribution Circuit | Vegetation | Tree - fell into line | 201 | 123681 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0025165 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 68757 | 20190217 | 935 | 315499 | 658 | Distribution Circuit | Vegetation | Tree - fell into line | 562 | 351561 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025087 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 18411 | 20190217 | 1259 | 315892 | 467 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 34091 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025157 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 6852 | 20190217 | 1334 | 315960 | 1651 | Distribution Circuit | Vegetation | Tree - fell into line | 1166 | 602490 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025163 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 20867 | 20190217 | 939 | 315988 | 1504 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 91744 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025171 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 19612 | 20190217 | 1303 | 315909 | 3319 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 564230 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025200 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 18949 | 20190217 | 939 | 316434 | 768 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 15360 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025227 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 1081 | 20190217 | 1216 | 315826 | 2872 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 48824 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025261 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 4741 | 20190217 | 1303 | 317233 | 3319 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 36509 | Overcast-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0025534 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1180 | 20190217 | 900 | 315453 | 560 | Distribution Circuit | Vegetation | Tree - fell into line | 235 | 73936 | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0025057 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 95773 | 20190217 | 941 | 315504 | 303 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 9999 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025085 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1110 | 153081110 | FUSE | 21759 | 20190217 | 956 | 315526 | 377 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 6786 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025168 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | JUMPER | WIRE DOWN 1 S/OF 5845 | 20190217 | 1440 | 317409 | 1653 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 21286 | Partly Cloudy-Fog-Below 32 F | Connector or Splice (OH) | Broken, wire on ground | 19-0025572 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER | 1101/2 | 20190226 | 13 | 323739 | 10688 | Distribution Circuit | Vegetation | Tree - fell into line | 1075 | 3063636 | Overcast-Fog-Snow-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028071 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 34911 | 20190226 | 2231 | 325497 | 696 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6960 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028630 | OH | Sus | 31426710 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2101/2 | 20190226 | 2312 | 325667 | 201 | Distribution Circuit | Vegetation | Tree - fell into line | 3664 | 483938 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028627 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2102 | 153132102 | FUSE | 32973 | 20190226 | 702 | 323901 | 703 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6596 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028294 | OH | Sus | 31426712 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11479 | 20190226 | 2334 | 326648 | 726 | Distribution Circuit | Vegetation | Tree - fell into line | 130 | 94380 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028825 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SPAULDING-1101 | 152251101 | FUSE | 91077 | 20190226 | 1145 | 324380 | 1319 | Distribution Circuit | Vegetation | Tree - fell into line | 325 | 20759 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028268 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SPAULDING-1101 | 152251101 | SWITCH | 34807 | 20190226 | 1610 | 325163 | 8792 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 26376 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028532 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | SPAULDING-1101 | 152251101 | RECLOSER | 75874 | 20190226 | 2029 | 325256 | 8434 | Distribution Circuit | Vegetation | Tree - fell into line | 319 | 753746 | Overcast-Fog-Snow-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028556 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | JUMPER | OJ 1 E/O CGC# 222835549678 | 20190226 | 2237 | 325506 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2240 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028978 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 8739 | 20190227 | 21 | 326443 | 2355 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 15741 | Partly Cloudy-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0029117 | OH | Sus | 31426712 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 7349 | 20190227 | 220 | 326150 | 2081 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 13536 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028802 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8115 | 20190227 | 307 | 326222 | 996 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 36852 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028884 | OH | Sus | 31426712 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE | 86845 | 20190227 | 343 | 326257 | 1866 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3732 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028926 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | RECLOSER | 39104 | 20190227 | 324 | 326235 | 850 | Distribution Circuit | Vegetation | Tree - fell into line | 892 | 503360 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028697 | OH | Sus | 31426710 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1109 | 152691109 | OTHER | WIRE DOWN @ 22365 CHERYL | 20190227 | 701 | 326563 | 584 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 2684 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028781 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | HIGGINS-1110 | 152691110 | FUSE | 3651 | 20190227 | 141 | 326086 | 765 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 14535 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028877 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 32425 | 20190227 | 955 | 326830 | 611 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 611 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028907 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 30779 | 20190227 | 1923 | 327564 | 92 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 3470 | Strong Winds-Rain-Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028627 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6613 | 20190227 | 716 | 327317 | 1829 | Distribution Circuit | Vegetation | Tree - branch fell on line | 64 | 104929 | Strong Winds-Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029148 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 12633 | 20190610 | 1854 | 404516 | 1013 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 16 | 16208 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0065574 | OH | Sus | 43837871 | 2019 | JUN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 5987 | 20190610 | 1627 | 404148 | 768 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 14169 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0065481 | OH | Sus | 31452985 | 2019 | JUN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | COLUMBIA HILL-1101 | 152471101 | FUSE | 7355 | 20191026 | 1824 | 692399 | 5741 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 86115 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0118081 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | JUMPER | OJ'S 1 E/O 3585 | 20191026 | 1855 | 691431 | 2737 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 13685 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0115927 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1101 | 152031101 | FUSE | 32729 | 20191026 | 1841 | 691709 | 5430 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 108600 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0117871 | OH | Sus | 0 | 2019 | OCT | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | JUMPER | OJ'S E/OF 222683551520 | 20191026 | 1705 | 691899 | 5312 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5312 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0115965 | OH | Sus | 0 | 2019 | OCT | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | JUMPER | OJ'S 4 N/OF 222702153142 | 20191026 | 1705 | 691977 | 5418 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5418 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0115965 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 18229 | 20191026 | 1811 | 690417 | 2924 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 81872 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0117572 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 33905 | 20191026 | 1858 | 688974 | 2688 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 34944 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0117452 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | LINCOLN-1101 | 153701101 | FUSE | 9195 | 20191029 | 1513 | 694256 | 1213 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 14556 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0118709 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | TRIP-SAVER | 12625 | 20191127 | 405 | 719839 | 687 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 84135 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0130005 | OH | Sus | 0 | 2019 | NOV | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER | 2200 | 20191127 | 654 | 720344 | 642 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 51186 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0129944 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 68757 | 20191127 | 2355 | 722494 | 1276 | Distribution Circuit | Vegetation | Tree - fell into line | 521 | 602844 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0130790 | OH | Sus | 0 | 2019 | NOV | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 13253 | 20200116 | 946 | 762549 | 234 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 1404 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009767 | OH | Sus | 31486518 | 2020 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | JUMPER | WIRE DOWN 5151 CLEAR CREEK | 20200116 | 1641 | 763348 | 269 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2402 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010264 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7043 | 20200116 | 1426 | 763096 | 1258 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 42772 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010227 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7067 | 20200116 | 1625 | 763329 | 1122 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 63954 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010296 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 6757 | 20200116 | 1819 | 763551 | 1106 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 18802 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010333 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | OTHER | WIRE DOWN AT 13630 FOREST PARK LN | 20200116 | 1815 | 763673 | 1430 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 18479 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010339 | OH | Sus | 0 | 2020 | JAN | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | NARROWS-2102 | 153132102 | JUMPER | 6/P/LD SIDE OF 32993 | 20200116 | 929 | 762623 | 258 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 21930 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009717 | OH | Sus | 31486515 | 2020 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 8213 | 20200116 | 1555 | 765314 | 4105 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 111642 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010254 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 7853 | 20200117 | 49 | 763778 | 2022 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 55692 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010891 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 4543 | 20200117 | 654 | 764495 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1956 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010528 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE | 5907 | 20200117 | 1007 | 764712 | 167 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 9352 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010564 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 5831 | 20200117 | 1825 | 765201 | 135 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 53 | 7155 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010985 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | SWITCH | 87861 | 20200209 | 1725 | 785891 | 260 | Distribution Circuit | Vegetation | Tree - branch fell on line | 660 | 24811 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0019493 | OH | Sus | 0 | 2020 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 2 | NARROWS-2102 | 153132102 | FUSE | 31481 | 20200209 | 904 | 781421 | 503 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 12584 | Clear- | Pole-Wood | Broken, wire on ground | 20-0019060 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1112 | 153081112 | RECLOSER | 19742 | 20200209 | 1100 | 782689 | 670 | Distribution Circuit | Vegetation | Tree - branch fell on line | 758 | 71411 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0019161 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 82493 | 20200209 | 714 | 781231 | 426 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 2556 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0018955 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 65865 | 20200209 | 1129 | 783029 | 305 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 26535 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0019238 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 22341 | 20200209 | 742 | 781243 | 476 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 32844 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0019082 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6655 | 20200209 | 933 | 781707 | 374 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 20944 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0019137 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER | 2130 | 20200315 | 303 | 851720 | 719 | Distribution Circuit | Vegetation | Tree - branch fell on line | 201 | 116997 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032190 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | OCB | 2102/2 | 20200315 | 418 | 851598 | 865 | Distribution Circuit | Vegetation | Tree - fell into line | 773 | 409373 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032186 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER | 2200 | 20200316 | 259 | 853310 | 933 | Distribution Circuit | Vegetation | Tree - branch fell on line | 114 | 86474 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032482 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7039 | 20200316 | 637 | 853567 | 533 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 27183 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0032861 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | RECLOSER | 2230 | 20200815 | 316 | 1003656 | 468 | Distribution Circuit | 3rd Party | Vehicle | 849 | 297015 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0084057 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 10267 | 20200816 | 1235 | 1012726 | 515 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2060 | Partly Cloudy-Heat Wave-Above 90 | Pole-Wood | Broken, wire on ground | 20-0085010 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE | 30717 | 20200816 | 1517 | 1013150 | 381 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 1799 | Clear-Heat Wave-Above 90 | Conductor, Overhead | Broken, wire on ground | 20-0085084 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 1361 | 20210119 | 115 | 1213909 | 601 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 13823 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010382 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | RECLOSER | 97982 | 20210119 | 1035 | 1216483 | 163 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 17115 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010618 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE | 6391 | 20210119 | 548 | 1214912 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 6803 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0010524 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 33617 | 20210119 | 140 | 1213869 | 924 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 27720 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010110 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 34225 | 20210119 | 48 | 1214339 | 971 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 27188 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010111 | OH | Sus | 44629093 | 2021 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE | 4183 | 20210119 | 4 | 1213435 | 815 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 13285 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010477 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 9819 | 20210119 | 911 | 1216050 | 377 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3393 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010727 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | DRUM-1101 | 152321101 | JUMPER | 1602 | 20210119 | 829 | 1216130 | 258 | Distribution Circuit | Vegetation | Tree - fell into line | 194 | 16128 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010494 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 481660 | 20210119 | 1403 | 1217323 | 266 | Distribution Circuit | Equipment Failure/Involved | Overhead | 78 | 8214 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010869 | OH | Sus | 0 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | PENRYN-1105 | 152561105 | FUSE | 9143 | 20210119 | 1319 | 1217221 | 339 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 4407 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010975 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | OTHER | HOT WIRE DOWN 5837 | 20210119 | 1011 | 1216521 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 669 | 74519 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010790 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 2197 | 20210119 | 407 | 1214541 | 728 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 12376 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0010573 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6617 | 20210119 | 840 | 1214938 | 445 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 24920 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0010453 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE | 18545 | 20210125 | 554 | 1223453 | 684 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 15048 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013871 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 13247 | 20210125 | 508 | 1223369 | 722 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 12274 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0013624 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | OTHER | WIRE DOWN 6 POLES LD SIDE OF 2025 | 20210125 | 126 | 1223043 | 881 | Distribution Circuit | Vegetation | Tree - fell into line | 369 | 20015 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013682 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 2029 | 20210125 | 1141 | 1224340 | 184 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 10304 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013927 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | JUMPER | WIRE DOWN @ 6760 DIABLO VIEW CT | 20210125 | 1420 | 1224725 | 94 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 2250 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013999 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE | 6007 | 20210125 | 547 | 1223441 | 811 | Distribution Circuit | Vegetation | Tree - branch fell on line | 117 | 94887 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013869 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | OTHER | WIRE DOWN 2 SPANS LD SIDE OF 6149 | 20210125 | 900 | 1224119 | 260 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 520 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013786 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 6955 | 20210125 | 540 | 1223404 | 767 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 25194 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0013636 | OH | Sus | 35227541 | 2021 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 8439 | 20210125 | 349 | 1224083 | 847 | Distribution Circuit | Vegetation | Tree - branch fell on line | 96 | 54612 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0013770 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | HIGGINS-1110 | 152691110 | FUSE | 31279 | 20210125 | 650 | 1223557 | 781 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 15620 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0013797 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 2 | HIGGINS-1110 | 152691110 | FUSE | 7489 | 20210125 | 634 | 1223521 | 798 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 24738 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013970 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 8569 | 20210125 | 2155 | 1225369 | 1143 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 23973 | Clear-32-90F | Cutout, fuse holder | Broken, wire on ground | 21-0014492 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE | 64017 | 20210125 | 337 | 1224107 | 990 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11076 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0014073 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | RECLOSER | 2740 | 20210125 | 28 | 1222999 | 989 | Distribution Circuit | Vegetation | Tree - fell into line | 547 | 517834 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013546 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21143 | 20210126 | 1106 | 1226025 | 448 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 448 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0014549 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 4373 | 20210126 | 2340 | 1230775 | 759 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 27324 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0016028 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 8203 | 20210126 | 2340 | 1230882 | 1030 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 89610 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0016180 | OH | Sus | 0 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21315 | 20210127 | 928 | 1234435 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 9494 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0015917 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21457 | 20210127 | 915 | 1234584 | 487 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 36259 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0015947 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 12319 | 20210127 | 1044 | 1235118 | 426 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 6816 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0016139 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | Yes
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | RECLOSER | 19542 | 20210127 | 331 | 1232541 | 633 | Distribution Circuit | Vegetation | Tree - fell into line | 618 | 225024 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0015601 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 477265 | 20210127 | 331 | 1232550 | 917 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 14672 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0015807 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | Yes
SIERRA | Tier 2 | HIGGINS-1107 | 152691107 | FUSE | 3533 | 20210127 | 819 | 1233887 | 341 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 1991 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0016007 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 4717 | 20210127 | 157 | 1232043 | 629 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 33337 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0015704 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 6679 | 20210127 | 649 | 1233327 | 546 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 15352 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0016189 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | RECLOSER | 1102/2 | 20210128 | 2244 | 1240766 | 1052 | Distribution Circuit | Vegetation | Tree - fell into line | 362 | 363083 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0018068 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 31233 | 20210128 | 1000 | 1239227 | 685 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3425 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0017673 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SPAULDING-1101 | 152251101 | OTHER | WIRE DOWN @ 35859 | 20210128 | 1730 | 1241215 | 2766 | Distribution Circuit | Equipment Failure/Involved | Overhead | 85 | 116422 | Snow-Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0018317 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 51800 | 20210910 | 813 | 1467728 | 633 | Distribution Circuit | 3rd Party | Vehicle | 1005 | 313378 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0115798 | OH | Sus | 0 | 2021 | SEP | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 51800 | 20211011 | 1247 | 1493339 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 1005 | 214783 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0128898 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | RECLOSER | 1704 | 20211024 | 934 | 1508700 | 477 | Distribution Circuit | Vegetation | Tree - fell into line | 452 | 125384 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135853 | OH | Sus | 0 | 2021 | OCT | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | RECLOSER | 2058 | 20211024 | 840 | 1508811 | 85 | Distribution Circuit | Vegetation | Tree - fell into line | 317 | 26945 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135774 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 7742 | 20211025 | 853 | 1517847 | 1544 | Distribution Circuit | Vegetation | Tree - fell into line | 1004 | 287188 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0137022 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 8372 | 20211213 | 1120 | 1566809 | 457 | Distribution Circuit | Equipment Failure/Involved | Overhead | 718 | 183289 | Strong Winds-Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0157144 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 35281 | 20211213 | 1415 | 1567530 | 240 | Distribution Circuit | Vegetation | Tree - branch fell on line | 120 | 28800 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0157378 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | OTHER | WIRE DOWN 17197 NORLENE WAY | 20211213 | 454 | 1565722 | 310 | Distribution Circuit | Vegetation | Tree - branch fell on line | 967 | 137701 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0156929 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | RECLOSER | 23190 | 20211213 | 2348 | 1569127 | 1296 | Distribution Circuit | Vegetation | Tree - fell into line | 1994 | 1735810 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 21-0157672 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | OTHER | WIRE DOWN CAUSING 18473 TO BLOW | 20211214 | 417 | 1570166 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 8061 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0157855 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7097 | 20211214 | 136 | 1569234 | 862 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 12068 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0157812 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | OCB | 1101/2 | 20211214 | 450 | 1569628 | 721 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 66859 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0157773 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9387 | 20211214 | 353 | 1569500 | 1024 | Distribution Circuit | Vegetation | Tree - branch fell on line | 87 | 78316 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158005 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 6109 | 20211214 | 333 | 1569465 | 551 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 67773 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0157844 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 6193 | 20211214 | 441 | 1569610 | 688 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 54751 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0157901 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 6125 | 20211214 | 550 | 1569764 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 32344 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158094 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | FUSE | 6103 | 20211214 | 429 | 1569587 | 791 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 25312 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158146 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | RECLOSER | 76178 | 20211225 | 920 | 1581205 | 445 | Distribution Circuit | Vegetation | Tree - fell into line | 629 | 48530 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160544 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | OTHER | WIRE DOWN 1/N/OF CGC# 222615464625 | 20211225 | 1055 | 1581301 | 297 | Distribution Circuit | Vegetation | Tree - branch fell on line | 139 | 38338 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160561 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1112 | 153081112 | JUMPER | OJ 2 SPANS SOURCE SIDE OF 12913 | 20211227 | 1905 | 1587223 | 1501 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 15010 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161237 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 6693 | 20211229 | 1125 | 1588393 | 480 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 11040 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161622 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 12392 | 20220907 | 151 | 1803884 | 726 | Distribution Circuit | Equipment Failure/Involved | Overhead | 870 | 450048 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0107108 | OH | Sus | 0 | 2022 | SEP | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | JUMPER | WIRE DOWN AT MTR 1009711651 | 20221210 | 721 | 1880431 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 1224 | 41105 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0138129 | OH | Sus | 0 | 2022 | DEC | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 8463 | 20221210 | 1246 | 1882399 | 355 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 18105 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0138498 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 22399 | 20221231 | 1 | 1902894 | 656 | Distribution Circuit | Vegetation | Tree - fell into line | 293 | 100678 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142451 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 4693 | 20221231 | 2253 | 1907455 | 1003 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6018 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0004228 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | JUMPER | WIRE DOWN @ CGC#222859652943 | 20230105 | 1000 | 1921585 | 280 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1073 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0007275 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | HIGGINS-1107 | 152691107 | FUSE | 9901 | 20230108 | 115 | 1931567 | 1133 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 101833 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0010209 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HORSESHOE-1101 | 152571101 | FUSE | 3861 | 20230108 | 27 | 1930945 | 938 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 46900 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0009910 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 7227 | 20230108 | 724 | 1932516 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 8624 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0010014 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PENRYN-1105 | 152561105 | FUSE | 69443 | 20230108 | 102 | 1931466 | 1186 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 41510 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0010224 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER | 173934 | 20230109 | 338 | 1935489 | 857 | Distribution Circuit | Vegetation | Tree - fell into line | 471 | 142317 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0010749 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7055 | 20230109 | 646 | 1936288 | 664 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 14608 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0011137 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5891 | 20230109 | 1427 | 1938448 | 211 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 3413 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0011369 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-1110 | 153081110 | OTHER | WIRE DOWN LS/OF CGC 223397939251 | 20230109 | 332 | 1937719 | 934 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 28190 | Overcast-Fog-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0011078 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 7371 | 20230110 | 430 | 1942234 | 854 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 15242 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0012259 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 2167 | 20230110 | 421 | 1941946 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 70971 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0012039 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | OTHER | WIRE DOWN LD SIDE 583890 TWD 223579337115 | 20230110 | 513 | 1942622 | 2063 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 3024 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0012871 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1107 | 152261107 | OTHER | WIRE DOWN CGC#223188638303 | 20230110 | 413 | 1941636 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 4729 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0012209 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE | 7847 | 20230110 | 422 | 1943827 | 634 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 15216 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0012056 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | TRIP-SAVER | 4281 | 20230110 | 423 | 1942026 | 806 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 29294 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0012101 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1130 | 20230110 | 421 | 1941932 | 609 | Distribution Circuit | Vegetation | Tree - fell into line | 291 | 177219 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0011872 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | PENRYN-1103 | 152561103 | RECLOSER | 604 | 20230110 | 407 | 1941623 | 786 | Distribution Circuit | Vegetation | Tree - fell into line | 782 | 119325 | Partly Cloudy-Drizzle-32-90 F | Transformer (OH) | Broken, wire on ground | 23-0011894 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11707 | 20230110 | 659 | 1941600 | 364 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 7644 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0011997 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 22355 | 20230110 | 518 | 1942642 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 10530 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0012045 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | RECLOSER | 2054 | 20230114 | 955 | 1953769 | 663 | Distribution Circuit | Vegetation | Tree - fell into line | 315 | 24801 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016026 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | DIAMOND SPRINGS-1107 | 152261107 | FUSE | 20791 | 20230221 | 1453 | 1991982 | 643 | Distribution Circuit | 3rd Party | Vehicle | 44 | 28292 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0031476 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 7371 | 20230224 | 519 | 2003069 | 499 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 15469 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0033780 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE | 7669 | 20230224 | 943 | 2004823 | 306 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 6263 | Clear-32-90F | Transformer (OH) | Broken, wire on ground | 23-0034000 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 9483 | 20230224 | 1217 | 2005329 | 350 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2100 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0034159 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | RECLOSER | 995672 | 20230224 | 727 | 2003780 | 290 | Distribution Circuit | Equipment Failure/Involved | Overhead | 337 | 63124 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0033760 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 35323 | 20230224 | 1054 | 2004949 | 383 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 766 | Clear-32-90F | Transformer (OH) | Broken, wire on ground | 23-0034037 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 8571 | 20230224 | 1336 | 2005689 | 211 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 1477 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0034322 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PENRYN-1107 | 152561107 | FUSE | 38443 | 20230224 | 407 | 2002443 | 548 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1644 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0033884 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 1445 | 20230224 | 1534 | 2006036 | 331 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 4634 | Clear-32-90 F | Conductor, Overhead | On Ground | 23-0034492 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER | 2200 | 20230226 | 2342 | 2011101 | 752 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 56772 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0036049 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 8175 | 20230226 | 1711 | 2010410 | 307 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 3684 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0035924 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 33795 | 20230227 | 10 | 2011109 | 836 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2508 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0036136 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 9741 | 20230227 | 1306 | 2012384 | 251 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 32379 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0036534 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1112 | 153081112 | SWITCH | 774186 | 20230227 | 1348 | 2012573 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 1238 | 175580 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0036485 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 5837 | 20230314 | 1208 | 2038155 | 276 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2208 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0045246 | OH | Sus | 0 | 2023 | MAR | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 61892 | 20230314 | 1132 | 2037179 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 410 | 108875 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0044842 | OH | Sus | 0 | 2023 | MAR | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 8145 | 20230314 | 1129 | 2037159 | 209 | Distribution Circuit | Vegetation | Tree - fell into line | 190 | 39710 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0045110 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 779 | 20130408 | 453 | 768788 | 2509 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 110396 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022201 | OH | Sus | 0 | 2013 | APR | Yes | Line to Line | Yes
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | OTHER |  | 20130408 | 1611 | 770677 | 399 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 399 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0022686 | OH | Sus | 0 | 2013 | APR | Yes | None | Yes
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | SWITCH | 90299 | 20130408 | 2218 | 771228 | 282 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 17484 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0022819 | OH | Sus | 0 | 2013 | APR | Yes | None | Yes
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 7401 | 20130408 | 136 | 768287 | 619 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 40854 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022175 | OH | Sus | 0 | 2013 | APR | Yes |  | Yes
SONOMA | Tier 2 | GEYSERVILLE-1102 | 42891102 | SWITCH | 12751 | 20131121 | 2045 | 909300 | 420 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 2520 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0078169 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
SONOMA | Tier 3 | GEYSERVILLE-1102 | 42891102 | FUSE | 735 | 20131121 | 1940 | 907687 | 3995 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 35955 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078591 | OH | Sus | 0 | 2013 | NOV | Yes | None | Yes
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 2379 | 20131121 | 1816 | 909415 | 2519 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 103279 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078339 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2225 | 20131121 | 1624 | 907529 | 424 | Distribution Circuit | Equipment Failure/Involved | Other | 90 | 38160 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078018 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
SONOMA | Tier 2 | CLOVERDALE-1101 | 42821101 | FUSE | 7373 | 20131122 | 943 | 911852 | 1518 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 36432 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078555 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | OTHER |  | 20131122 | 812 | 911278 | 543 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 543 | Clear-32 - 90 F | Other | Broken, wire on object | 13-0078403 | OH | Sus | 0 | 2013 | NOV | Yes | None | Yes
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 841 | 20131122 | 1659 | 912782 | 1278 | Distribution Circuit | Vegetation | Tree - branch fell on line | 134 | 169952 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078767 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
SONOMA | Tier 2 | PENNGROVE-1101 | 43471101 | FUSE | 9875 | 20131122 | 1947 | 913093 | 583 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 5247 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078815 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE | 2883 | 20141203 | 1208 | 1122972 | 252 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 9828 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073417 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
SONOMA | Tier 3 | DUNBAR-1103 | 43071103 | FUSE | 3075 | 20141203 | 1050 | 1122427 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 6496 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073428 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1045 | 20141203 | 1503 | 1123301 | 587 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 39329 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073573 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | OTHER |  | 20141203 | 1009 | 1122245 | 324 | Distribution Circuit | Vegetation | Tree - branch fell on line | 687 | 109791 | Heavy rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0073321 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 2 | COTATI-1105 | 42271105 | SECTIONALIZER | 244 | 20141211 | 46 | 1128815 | 276 | Distribution Circuit | Equipment Failure/Involved | Other | 360 | 89341 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074824 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 2 | COTATI-1105 | 42271105 | OTHER |  | 20141211 | 534 | 1132514 | 926 | Distribution Circuit | Equipment Failure/Involved | Other | 489 | 384387 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075304 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 124 | 20141211 | 28 | 1128777 | 2252 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 18310 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074797 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | OCB | OCB | 20141211 | 303 | 1128916 | 1115 | Distribution Circuit | Vegetation | Tree - fell into line | 462 | 461704 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074867 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 2699 | 20141211 | 1008 | 1134366 | 1827 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 60291 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075623 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 2989 | 20141211 | 2051 | 1136039 | 1299 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5196 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075869 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 2 | GEYSERVILLE-1101 | 42891101 | OTHER |  | 20141211 | 840 | 1131721 | 1595 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 1595 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0075482 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
SONOMA | Tier 2 | MIRABEL-1101 | 42091101 | FUSE | 1003 | 20141211 | 47 | 1128802 | 2373 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 152658 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074821 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 4859 | 20141211 | 632 | 1131265 | 1423 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 65458 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075419 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1499 | 20141211 | 108 | 1128864 | 430 | Distribution Circuit | Vegetation | Tree - branch fell on line | 132 | 56760 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074817 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 2 | MIRABEL-1102 | 42091102 | FUSE | 13669 | 20141211 | 503 | 1132545 | 1657 | Distribution Circuit | Equipment Failure/Involved | Other | 9 | 14913 | Heavy rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0075269 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 12003 | 20141211 | 52 | 1129030 | 930 | Distribution Circuit | Equipment Failure/Involved | Other | 1317 | 445904 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074858 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 3053 | 20141211 | 546 | 1133068 | 1483 | Distribution Circuit | Equipment Failure/Involved | Other | 105 | 155715 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075353 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 18387 | 20141211 | 1602 | 1134777 | 2540 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5080 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075664 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 525 | 20141211 | 308 | 1131740 | 1338 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 49506 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075729 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 396 | 20141211 | 604 | 1129964 | 1465 | Distribution Circuit | Equipment Failure/Involved | Other | 227 | 332555 | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075998 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | SWITCH | 4477 | 20141211 | 1115 | 1133331 | 502 | Distribution Circuit | Vegetation | Tree - branch fell on line | 210 | 105420 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075540 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 53477 | 20141211 | 951 | 1132494 | 842 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 47994 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075605 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 74315 | 20141211 | 6 | 1128755 | 2699 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 53980 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076101 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | OCB | OCB | 20141211 | 405 | 1129219 | 655 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1151 | 583570 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074894 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 346 | 20141211 | 341 | 1129058 | 852 | Distribution Circuit | Vegetation | Tree - branch fell on line | 468 | 218171 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074859 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 8227 | 20141211 | 334 | 1128950 | 580 | Distribution Circuit | Equipment Failure/Involved | Other | 17 | 9860 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074877 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 5026 | 20141211 | 608 | 1130871 | 593 | Distribution Circuit | Vegetation | Tree - fell into line | 288 | 170784 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075114 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 296 | 20141211 | 445 | 1129291 | 319 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 34066 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075014 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 632 | 20141211 | 1219 | 1133696 | 1846 | Distribution Circuit | Equipment Failure/Involved | Other | 80 | 36527 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075806 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2225 | 20141211 | 519 | 1130725 | 779 | Distribution Circuit | Vegetation | Tree - branch fell on line | 90 | 70110 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075375 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE | 2331 | 20141211 | 707 | 1139324 | 3084 | Distribution Circuit | Vegetation | Tree - bark fell into line | 13 | 40092 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076607 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 2 | DUNBAR-1101 | 43071101 | FUSE | 65797 | 20141212 | 430 | 1137036 | 608 | Distribution Circuit | Vegetation | Tree - fell into line | 151 | 91808 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076165 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 4523 | 20141212 | 1742 | 1139001 | 448 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 7168 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076514 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 1789 | 20141212 | 753 | 1137435 | 962 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 38480 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0076248 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 1793 | 20141212 | 838 | 1137618 | 2032 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 25648 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076336 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 9797 | 20141212 | 827 | 1137572 | 1684 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 35364 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076360 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 883 | 20141212 | 1150 | 1138263 | 555 | Distribution Circuit | Vegetation | Tree - branch fell on line | 92 | 19006 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076369 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 12683 | 20141212 | 1022 | 1137969 | 1398 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1398 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076400 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER | 87402 | 20141212 | 1235 | 1138438 | 1549 | Distribution Circuit | Equipment Failure/Involved | Other | 36 | 10649 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076454 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 2 | DUNBAR-1101 | 43071101 | FUSE | 9373 | 20141230 | 1601 | 1153721 | 854 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11956 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079356 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 17875 | 20141230 | 1530 | 1153449 | 780 | Distribution Circuit | Equipment Failure/Involved | Other | 4 | 3120 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0079501 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 11985 | 20141230 | 1434 | 1152843 | 690 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4830 | Strong winds-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0079275 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 202 | 20141230 | 1149 | 1151733 | 499 | Distribution Circuit | Vegetation | Tree - branch fell on line | 113 | 51971 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0079069 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | SWITCH | 17557 | 20141230 | 1201 | 1152477 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 48667 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079106 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2269 | 20141230 | 1305 | 1152111 | 258 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 6450 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079131 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE | 4125 | 20150206 | 1227 | 1174830 | 368 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 2944 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010115 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 2 | COTATI-1105 | 42271105 | FUSE | 6563 | 20150206 | 1601 | 1176374 | 485 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5820 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010559 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 13153 | 20150206 | 1725 | 1176885 | 99 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 297 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010497 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 13983 | 20150206 | 1601 | 1176715 | 1684 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 69900 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010736 | OH | Sus | 0 | 2015 | FEB | Yes | Multi-Fault | Yes
SONOMA | Tier 3 | FULTON-1107 | 42561107 | FUSE | 3655 | 20150206 | 1618 | 1176570 | 2903 | Distribution Circuit | Equipment Failure/Involved | Other | 33 | 16869 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010611 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 5183 | 20150206 | 1742 | 1177023 | 2609 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 82103 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010861 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 1027 | 20150206 | 2107 | 1178547 | 1742 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 20904 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0010966 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1499 | 20150206 | 1607 | 1176448 | 675 | Distribution Circuit | Vegetation | Tree - branch fell on line | 132 | 89100 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0010550 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 841 | 20150206 | 1700 | 1176792 | 514 | Distribution Circuit | Equipment Failure/Involved | Other | 133 | 41682 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010595 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 3041 | 20150206 | 1539 | 1176244 | 2886 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 37518 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010694 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 1525 | 20150206 | 2350 | 1178988 | 1007 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 55385 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on object | 15-0010802 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 3437 | 20150206 | 2131 | 1178755 | 1457 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 28193 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0010818 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 5687 | 20150206 | 2244 | 1181667 | 2358 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 14148 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011359 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | OTHER |  | 20150206 | 1250 | 1175208 | 377 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 1885 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010163 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 3891 | 20150206 | 1440 | 1175912 | 2920 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 90520 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010448 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 74315 | 20150206 | 1659 | 1176717 | 761 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 15220 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010655 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 2579 | 20150206 | 1704 | 1176749 | 2685 | Distribution Circuit | Equipment Failure/Involved | Other | 11 | 29535 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010757 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 652 | 20150206 | 1214 | 1176051 | 1615 | Distribution Circuit | Vegetation | Tree - branch fell on line | 314 | 411978 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010357 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 2055 | 20150206 | 1717 | 1176832 | 630 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 21420 | Strong winds-32 - 90 F | Conductor, Underground | Broken, wire on ground | 15-0010626 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 879 | 20150206 | 1600 | 1176515 | 2280 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 54720 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010647 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 8163 | 20150206 | 2214 | 1179148 | 587 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 42851 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010852 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 3331 | 20150206 | 1245 | 1175033 | 1030 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 18221 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010414 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | OTHER |  | 20150206 | 1632 | 1176571 | 48 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 48 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on object | 15-0010439 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 2771 | 20150206 | 1544 | 1176277 | 1452 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 15972 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010464 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE | 5797 | 20150206 | 1844 | 1177691 | 766 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 91920 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010779 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2225 | 20150206 | 2154 | 1179103 | 933 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 83970 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0010970 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | SALMON CREEK-1101 | 43161101 | FUSE | 615 | 20150206 | 1321 | 1175364 | 399 | Distribution Circuit | Equipment Failure/Involved | Other | 16 | 3121 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on object | 15-0010264 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE | 2331 | 20150206 | 1259 | 1175978 | 1988 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 25844 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010472 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | DUNBAR-1102 | 43071102 | FUSE | 4897 | 20150207 | 124 | 1179757 | 2093 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 23023 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011266 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 46763 | 20150207 | 1403 | 1181312 | 1663 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3326 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011246 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 3031 | 20150207 | 1056 | 1181025 | 1804 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 30668 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011265 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 769 | 20150207 | 1859 | 1181810 | 1081 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 33511 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011393 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 4523 | 20150207 | 1038 | 1180965 | 1782 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 28512 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011245 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 15445 | 20150207 | 415 | 1180005 | 748 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 10472 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0010948 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 15479 | 20150207 | 2202 | 1181943 | 143 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 1859 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on object | 15-0011400 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 4573 | 20150207 | 1600 | 1181494 | 1452 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 15972 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011300 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
SONOMA | Tier 2 | CLOVERDALE-1102 | 42821102 | FUSE | 809 | 20150208 | 2124 | 1186201 | 802 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 17981 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012112 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 485 | 20150208 | 1656 | 1183291 | 279 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 279 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011744 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 1709 | 20150208 | 2115 | 1184510 | 1224 | Distribution Circuit | Vegetation | Tree - fell into line | 166 | 176994 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0011921 | OH | Sus | 0 | 2015 | FEB | Yes | Three Phase Fault | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 74315 | 20150208 | 2054 | 1184128 | 1056 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 21120 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011867 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 3891 | 20150208 | 2348 | 1185265 | 737 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 22847 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011976 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 15417 | 20150208 | 2059 | 1184157 | 893 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 14288 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011835 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 4573 | 20150208 | 2206 | 1184985 | 1106 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 12166 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012083 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1031 | 20150208 | 2128 | 1185394 | 802 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 17395 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011971 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | SWITCH | 62841 | 20150208 | 2127 | 1184674 | 875 | Distribution Circuit | Vegetation | Tree - branch fell on line | 78 | 36996 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011887 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2269 | 20150208 | 2354 | 1185274 | 1221 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 30525 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011952 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 779 | 20150608 | 2017 | 1246807 | 895 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 40275 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0039527 | OH | Sus | 0 | 2015 | JUN | Yes | Line to Ground | Yes
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 3069 | 20151213 | 757 | 1362231 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2985 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084863 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 13053 | 20151213 | 932 | 1360868 | 763 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1910 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084968 | OH | Sus | 0 | 2015 | DEC | Yes | Force Out | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 134 | 20151213 | 715 | 1360165 | 1045 | Distribution Circuit | Vegetation | Tree - fell into line | 229 | 147116 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084603 | OH | Sus | 42588659 | 2015 | DEC | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 7401 | 20151213 | 822 | 1360429 | 329 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 21714 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084637 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | OTHER | WIRE DOWN 501 SANDRETTO | 20151213 | 750 | 1360617 | 520 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 14215 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084615 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 4913 | 20151213 | 824 | 1360443 | 546 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2730 | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084773 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 429 | 20151213 | 813 | 1360357 | 749 | Distribution Circuit | Equipment Failure/Involved | Overhead | 116 | 72844 | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084775 | OH | Sus | 0 | 2015 | DEC | Yes | Force Out | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | OCB | 1112/2 | 20151213 | 803 | 1360333 | 984 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1122 | 251687 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084555 | OH | Sus | 42588659 | 2015 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | RECLOSER | 334 | 20151224 | 1543 | 1371213 | 515 | Distribution Circuit | Equipment Failure/Involved | Overhead | 92 | 16100 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087141 | OH | Sus | 31208799 | 2015 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | CLOVERDALE-1102 | 42821102 | RECLOSER | 156 | 20160305 | 2214 | 1420157 | 447 | Distribution Circuit | Vegetation | Tree - fell into line | 590 | 83569 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017975 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 2987 | 20160305 | 1557 | 1417038 | 1419 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 82053 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017578 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 134 | 20160305 | 1618 | 1417447 | 621 | Distribution Circuit | Equipment Failure/Involved | Overhead | 229 | 135141 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017625 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 3437 | 20160305 | 1841 | 1418200 | 291 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 4901 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017842 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 8139 | 20160305 | 1704 | 1417545 | 525 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 18900 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017743 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 1581 | 20160305 | 1909 | 1418337 | 1393 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 11144 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017810 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 346 | 20160305 | 1823 | 1418145 | 314 | Distribution Circuit | Vegetation | Tree - branch fell on line | 515 | 100456 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017683 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1997 | 20160305 | 1759 | 1417948 | 632 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 69520 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017746 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 781 | 20170103 | 2055 | 1616778 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 7530 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003336 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | RECLOSER | 322 | 20170103 | 1657 | 1616109 | 659 | Distribution Circuit | Vegetation | Tree - fell into line | 376 | 31670 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003174 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | JUMPER | LINE/ 830 MONTGOMERY | 20170103 | 1638 | 1616642 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 9090 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003218 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6899 | 20170103 | 1626 | 1616007 | 358 | Distribution Circuit | Vegetation | Tree - branch fell on line | 81 | 21198 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003158 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE | 59789 | 20170108 | 522 | 1630212 | 5333 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 10666 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005878 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 36536 | 20170108 | 1321 | 1626893 | 454 | Distribution Circuit | Vegetation | Tree - branch fell on line | 662 | 219114 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005343 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | DUNBAR-1101 | 43071101 | FUSE | 4829 | 20170108 | 1854 | 1628711 | 3901 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 15604 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007499 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | DUNBAR-1103 | 43071103 | OTHER | WIRE DOWN @ MTR#1007382525 | 20170108 | 1745 | 1628450 | 1013 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 89606 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005754 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | Yes
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | JUMPER | OJ AT L/B 2 SPANS LD SIDE OF 4367 | 20170108 | 1448 | 1627674 | 1497 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 20958 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005443 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | FULTON-1107 | 42561107 | OTHER | WIRE DOWN BTWN 4265 & LR 604 | 20170108 | 1216 | 1626173 | 1646 | Distribution Circuit | Vegetation | Tree - fell into line | 222 | 77180 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005412 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | Yes
SONOMA | Tier 2 | GEYSERVILLE-1101 | 42891101 | JUMPER | WIRE DOWN 3 LD SIDE OF 12427 | 20170108 | 1528 | 1627707 | 2646 | Distribution Circuit | Vegetation | Tree - branch fell on line | 72 | 21360 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005449 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 2913 | 20170108 | 1504 | 1627577 | 2951 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 17706 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005608 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 5183 | 20170108 | 1753 | 1628472 | 1132 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 64240 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005677 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1139 | 20170108 | 636 | 1625477 | 2083 | Distribution Circuit | Vegetation | Tree - fell into line | 143 | 209900 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005472 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 8457 | 20170108 | 1132 | 1625565 | 1364 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 17732 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006024 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1101 | 42571101 | OTHER | WIRE DOWN 4/S/LS/ 4417 | 20170108 | 1115 | 1625342 | 4515 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 61454 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005594 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 1761 | 20170108 | 1338 | 1626975 | 1775 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 60350 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006196 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 1525 | 20170108 | 547 | 1622733 | 2049 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 114744 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004973 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 104 | 20170108 | 738 | 1623186 | 845 | Distribution Circuit | Vegetation | Tree - fell into line | 1242 | 1038565 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004977 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6917 | 20170108 | 738 | 1625138 | 1614 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 124278 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005148 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 1181 | 20170108 | 1117 | 1625928 | 3360 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 54271 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005527 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 525 | 20170108 | 1243 | 1626420 | 1518 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 54648 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005528 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 3053 | 20170108 | 738 | 1628823 | 1756 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 159870 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005627 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 12019 | 20170108 | 1704 | 1629175 | 4325 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 56225 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005725 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 8139 | 20170108 | 734 | 1623134 | 4948 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 178128 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005105 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 2659 | 20170108 | 1050 | 1625102 | 2998 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 110926 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005648 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 2301 | 20170108 | 1951 | 1631579 | 1524 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 27432 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006214 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 17177 | 20170108 | 945 | 1624342 | 3122 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6244 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006173 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1053 | 20170108 | 626 | 1622748 | 371 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 42294 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004983 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 4597 | 20170108 | 651 | 1622833 | 304 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 3952 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004990 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1313 | 20170108 | 816 | 1623555 | 1785 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 168231 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005113 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | OTHER | HOT WIRE DOWN | 20170108 | 849 | 1625486 | 2025 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 161839 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005190 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 2787 | 20170108 | 1048 | 1625076 | 421 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 10104 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005257 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE | 18477 | 20170109 | 1325 | 1631365 | 1278 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5112 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006208 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | JUMPER | OJ SS 14895 | 20170109 | 1511 | 1631695 | 4204 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 12612 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006220 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24918 | 20170109 | 1213 | 1632095 | 3104 | Distribution Circuit | Vegetation | Tree - fell into line | 171 | 433710 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006309 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | JUMPER | OJ'S 1/S/S/OF MTR500013313 TO EOL | 20170109 | 1815 | 1632044 | 2940 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2940 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006337 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
SONOMA | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE | 8859 | 20170109 | 941 | 1631664 | 4451 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8902 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006212 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1105 | 42271105 | FUSE | 2417 | 20170110 | 1244 | 1633282 | 2851 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 4255 | Partly Cloudy-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006689 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 36536 | 20170110 | 1739 | 1635033 | 1285 | Distribution Circuit | Equipment Failure/Involved | Overhead | 660 | 556009 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006875 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1105 | 42271105 | FUSE | 3287 | 20170110 | 1442 | 1633837 | 1324 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 65442 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007038 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 16739 | 20170110 | 1754 | 1635461 | 4071 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 77349 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007663 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
SONOMA | Tier 2 | LAKEVILLE-1102 | 43371102 | JUMPER | OJ'S 7 SPANS FROM 3793 | 20170110 | 2228 | 1638128 | 1272 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1272 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007408 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 1595 | 20170110 | 251 | 1632464 | 3605 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 18025 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006383 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 1939 | 20170110 | 1323 | 1633371 | 2647 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 23823 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006661 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 13491 | 20170110 | 1114 | 1633020 | 3407 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 59560 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006575 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 11721 | 20170110 | 1337 | 1634698 | 1843 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 18430 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0006855 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | JUMPER | O/J 1 SS OF MTR# G38872 | 20170110 | 1834 | 1636505 | 2906 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5812 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006988 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 3437 | 20170110 | 1752 | 1634972 | 1617 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 21221 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007321 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 64758 | 20170110 | 1238 | 1633280 | 3062 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 455556 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006657 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 240 | 20170110 | 1515 | 1634000 | 1609 | Distribution Circuit | Vegetation | Tree - fell into line | 620 | 670768 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006897 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 10183 | 20170110 | 1342 | 1640661 | 3260 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 22820 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008420 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 439 | 20170110 | 918 | 1632783 | 1778 | Distribution Circuit | Environmental/External | Water | 15 | 26670 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006503 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | JUMPER | WIRE DOWN 1 SPAN SOURCE SIDE OF 11757 HWY 116 | 20170110 | 836 | 1632922 | 1980 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 63888 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006513 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | RINCON-1103 | 43321103 | OCB | 1103/2 | 20170110 | 1414 | 1633660 | 579 | Distribution Circuit | Vegetation | Tree - fell into line | 2228 | 285114 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006680 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE | 3447 | 20170110 | 1600 | 1634189 | 2851 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 45616 | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006993 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1107 | 42151107 | OTHER | WIRE DOWN AT MTR1007528387 | 20170110 | 1752 | 1635207 | 2431 | Distribution Circuit | Vegetation | Tree - fell into line | 203 | 21678 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007304 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 779 | 20170111 | 1643 | 1640336 | 4042 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 74140 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007880 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | SONOMA-1103 | 42721103 | FUSE | 5543 | 20170111 | 540 | 1639122 | 2145 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 155705 | Partly Cloudy-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0007472 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 134 | 20170118 | 1315 | 1646247 | 1591 | Distribution Circuit | Vegetation | Tree - fell into line | 640 | 197059 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010035 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6229 | 20170118 | 2257 | 1649303 | 774 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 27090 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010587 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 669275 | 20170119 | 457 | 1649900 | 428 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3573 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010685 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1997 | 20170119 | 242 | 1649766 | 469 | Distribution Circuit | Vegetation | Tree - branch fell on line | 110 | 51590 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010643 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | SALMON CREEK-1101 | 43161101 | OTHER | 8859 | 20170119 | 1933 | 1651846 | 382 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 764 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011112 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
SONOMA | Tier 2 | MIRABEL-1102 | 42091102 | FUSE | 13669 | 20170120 | 338 | 1652166 | 464 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4176 | Partly Cloudy-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011202 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 9797 | 20170120 | 319 | 1652107 | 958 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 20118 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011215 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 12221 | 20170120 | 1203 | 1653404 | 230 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 2300 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0011535 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | Yes
SONOMA | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE | 8859 | 20170120 | 852 | 1653353 | 174 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 348 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011361 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 6751 | 20170121 | 2159 | 1657436 | 811 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 108674 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012557 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 134 | 20170121 | 1829 | 1657113 | 1519 | Distribution Circuit | Vegetation | Tree - fell into line | 232 | 289669 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0012165 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | MIRABEL-1102 | 42091102 | FUSE | 913 | 20170121 | 1028 | 1656267 | 1577 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5303 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012037 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | DUNBAR-1103 | 43071103 | OTHER | WIRE DOWN | 20170122 | 528 | 1659020 | 588 | Distribution Circuit | Vegetation | Tree - branch fell on line | 118 | 14224 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012991 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24918 | 20170122 | 609 | 1659460 | 425 | Distribution Circuit | Environmental/External | Flood/Erosion | 53 | 22525 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012894 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 18133 | 20170122 | 940 | 1660164 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1992 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012984 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | RECLOSER | 5040 | 20170122 | 449 | 1659021 | 755 | Distribution Circuit | Vegetation | Tree - fell into line | 386 | 291430 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0012820 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | COTATI-1104 | 42271104 | FUSE | 14645 | 20170207 | 804 | 1678601 | 506 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4048 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018514 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 4877 | 20170207 | 303 | 1677772 | 861 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 18942 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018291 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 6751 | 20170207 | 445 | 1679879 | 2090 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 280060 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018486 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4271 | 20170207 | 112 | 1677190 | 803 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11242 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018190 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4947 | 20170207 | 315 | 1678975 | 2156 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 118580 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018642 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | FULTON-1107 | 42561107 | OTHER | WIRE DOWN IRO 9108 LOCH HAVEN | 20170207 | 1417 | 1680804 | 1310 | Distribution Circuit | Vegetation | Tree - branch fell on line | 149 | 114666 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0018723 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 1071 | 20170207 | 907 | 1679369 | 4863 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 27917 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018519 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MIRABEL-1102 | 42091102 | FUSE | 13669 | 20170207 | 632 | 1678158 | 1796 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 19068 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018236 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 7951 | 20170207 | 629 | 1680184 | 950 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 16150 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018582 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6229 | 20170207 | 822 | 1680191 | 733 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 25655 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018586 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 12035 | 20170207 | 1218 | 1680588 | 2395 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 84538 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018720 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | OTHER | WIRE DOWN 3 S/S OF MTR1009647024 | 20170207 | 1507 | 1680503 | 1453 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 4359 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018737 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | JUMPER | WIRE DOWN | 20170207 | 1025 | 1681962 | 1925 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 38500 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019031 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | OTHER | 1995 | 20170207 | 904 | 1679352 | 1619 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 17809 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018556 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | JUMPER | 11 SPANS LD SIDE OF 2055 | 20170207 | 817 | 1678885 | 708 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 4248 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018630 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 208 | 20170207 | 224 | 1677412 | 721 | Distribution Circuit | Vegetation | Tree - fell into line | 182 | 81498 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018057 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE | 6119 | 20170207 | 309 | 1679273 | 2485 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 19172 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018332 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE | 15035 | 20170207 | 902 | 1679630 | 786 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5502 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018420 | OH | Sus | 0 | 2017 | FEB | Yes | Force Out | Yes | No
SONOMA | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE | 15553 | 20170207 | 456 | 1677976 | 1982 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3964 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018374 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 560 | 20170209 | 643 | 1682791 | 715 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 22165 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019307 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 79306 | 20170209 | 1216 | 1683342 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 26003 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019471 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 652 | 20170209 | 1243 | 1683406 | 497 | Distribution Circuit | Vegetation | Tree - fell into line | 312 | 125756 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019448 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | RINCON-1103 | 43321103 | OCB | 1103/2 | 20170209 | 1423 | 1683627 | 1100 | Distribution Circuit | Vegetation | Tree - fell into line | 458 | 419106 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0019503 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6233 | 20170217 | 2125 | 1698484 | 710 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 9230 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022769 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 23916 | 20170218 | 135 | 1698749 | 687 | Distribution Circuit | Environmental/External | Flood/Erosion | 689 | 258198 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0022844 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE | 4219 | 20170220 | 857 | 1702782 | 483 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1449 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023734 | OH | Sus | 0 | 2017 | FEB | Yes | Force Out | Yes | No
SONOMA | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 5531 | 20170220 | 2047 | 1705953 | 2393 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 39159 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0024531 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6917 | 20170220 | 2154 | 1706261 | 1004 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 16406 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024771 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 8139 | 20170220 | 2102 | 1706068 | 950 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 34200 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024718 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | JUMPER | WIRE DOWN @ 15383 | 20170220 | 1441 | 1703543 | 371 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 9897 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023876 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 4737 | 20170220 | 2049 | 1705997 | 978 | Distribution Circuit | Vegetation | Tree - branch fell on line | 53 | 51834 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0024348 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 15593 | 20170220 | 2230 | 1706267 | 731 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 73100 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024996 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 1621 | 20170220 | 2247 | 1706489 | 833 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 35819 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024829 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 3085 | 20170221 | 1410 | 1708756 | 411 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 8030 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025246 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | OTHER | WIRE DOWN 2 SPANS LD SIDE OF 9599 | 20170221 | 116 | 1707172 | 1090 | Distribution Circuit | Vegetation | Tree - fell into line | 171 | 137031 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024937 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 8347 | 20170221 | 1724 | 1709163 | 1251 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2502 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025268 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE | 15707 | 20170221 | 140 | 1707245 | 729 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 19683 | Overcast-Drizzle-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0024846 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | BELLEVUE-2103 | 43182103 | FUSE | 3789 | 20170406 | 2154 | 1748032 | 2290 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 84730 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037479 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | RECLOSER | 132 | 20170406 | 1907 | 1746115 | 883 | Distribution Circuit | Vegetation | Tree - fell into line | 1017 | 145509 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037238 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | OCB | 1121/2 | 20170406 | 2009 | 1746631 | 2878 | Distribution Circuit | Vegetation | Tree - fell into line | 523 | 818800 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0037273 | OH | Sus | 0 | 2017 | APR | Yes | Multi-Fault | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 560 | 20170406 | 2002 | 1750400 | 2893 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 89683 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037736 | OH | Sus | 0 | 2017 | APR | Yes | Multi-Fault | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 11011 | 20170406 | 2009 | 1750403 | 2878 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 20146 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037737 | OH | Sus | 0 | 2017 | APR | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 2027 | 20170406 | 1810 | 1745918 | 412 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 11536 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037250 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 4891 | 20170406 | 2125 | 1747741 | 1363 | Distribution Circuit | Equipment Failure/Involved | Overhead | 126 | 135174 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037460 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | COTATI-1102 | 42271102 | FUSE | 681 | 20170407 | 1553 | 1751214 | 188 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 10155 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038029 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 4703 | 20170407 | 1640 | 1751350 | 155 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 775 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038046 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | OTHER | WIRE DOWN @ 14950 BITTNER | 20170407 | 241 | 1749224 | 608 | Distribution Circuit | Vegetation | Tree - fell into line | 388 | 8532 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037613 | OH | Sus | 0 | 2017 | APR | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | OTHER | WIRE DOWN @ 4660 AUSTIN CREEK | 20170407 | 220 | 1749220 | 800 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 87211 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037575 | OH | Sus | 0 | 2017 | APR | Yes | Open Circuit | Yes | Yes
SONOMA | Tier 3 | CLOVERDALE-1102 | 42821102 | FUSE | 1381 | 20171008 | 2324 | 1906698 | 19846 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 27 | 535842 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0089338 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | DUNBAR-1101 | 43071101 | JUMPER | OJ'S HIGH SIDE OF FU 3749 | 20171008 | 2335 | 1900094 | 16805 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 33 | 539330 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087122 | OH | Sus | 0 | 2017 | OCT | Yes | None | Yes | No
SONOMA | Tier 3 | DUNBAR-1101 | 43071101 | JUMPER | OJ'S ON FIRST TO EAST LOADSIDE OF 1251 TO EO | 20171008 | 2154 | 1900167 | 19746 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 19746 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087147 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | DUNBAR-1101 | 43071101 | JUMPER | OJ'S IFO 352 GREEN ST @MTR 1009779560 | 20171008 | 2358 | 1900347 | 15332 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 33 | 468604 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087205 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | DUNBAR-1101 | 43071101 | JUMPER | OJ'S ON HARD TAP @MTR41L229 TO EOL | 20171008 | 2154 | 1901286 | 14034 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 7 | 98238 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087504 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | DUNBAR-1101 | 43071101 | JUMPER | OJ 1 SPAN SOURCE SIDE OF 18261 | 20171008 | 2358 | s1308557 | 19690 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 6 | 81458 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087580 | OH | Sus | 0 | 2017 | OCT | Yes | None | Yes | No
SONOMA | Tier 2 | DUNBAR-1101 | 43071101 | FUSE | 6597 | 20171008 | 2336 | 1901716 | 16517 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 198204 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087678 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | DUNBAR-1101 | 43071101 | FUSE | 4943 | 20171008 | 2335 | 1903260 | 16495 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 19 | 313405 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0088276 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 8857 | 20171008 | 2350 | 1898756 | 12720 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 5 | 51364 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086444 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | DUNBAR-1103 | 43071103 | JUMPER | OJ 1 P/N/OF MTR# 5000038774 | 20171008 | 2350 | 1899662 | 15147 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 4 | 60588 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086901 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FULTON-1102 | 42561102 | FUSE | 751 | 20171008 | 2150 | 1897466 | 2410 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 87406 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0085970 | OH | Sus | 0 | 2017 | OCT | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | TRIP-SAVER | 6917 | 20171008 | 2333 | 1894391 | 2437 | Distribution Circuit | Equipment Failure/Involved | Overhead | 77 | 187649 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085384 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | RINCON-1101 | 43321101 | JUMPER | OJ 1 SPAN S/OF 13169 | 20171008 | 2326 | 1896967 | 6704 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 60336 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085772 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE | 7207 | 20171008 | 2317 | 1900887 | 19569 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 19569 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0087394 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2225 | 20171008 | 2317 | 1901016 | 9687 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 90 | 871830 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087420 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 5152 | 20171008 | 2317 | 1901028 | 21108 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 53 | 136988 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087422 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | JUMPER | OJ ON TAP TO MTR 1007530457 | 20171008 | 2240 | 1900838 | 11229 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 11229 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087384 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 6891 | 20171008 | 2240 | 1901320 | 18032 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 11 | 198352 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087517 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 8765 | 20171008 | 2331 | 1901328 | 12595 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 25190 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087522 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 3679 | 20171008 | 2331 | 1901331 | 18409 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 46 | 846454 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087524 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | SANTA ROSA A-1104 | 42151104 | FUSE | 15173 | 20171008 | 2240 | 1901380 | 12560 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 37680 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087553 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 12107 | 20171008 | 2331 | 1901847 | 12669 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 19 | 240711 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087723 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 3451 | 20171008 | 2240 | 1902478 | 19435 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 57 | 1106870 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087940 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 8773 | 20171008 | 2240 | 1902794 | 15602 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 5 | 78010 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0088077 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 6583 | 20171008 | 2240 | 1903137 | 13945 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 27890 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0088207 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | JUMPER | OJ'S 5 SPANS S/W OF FUCO 1823 | 20171008 | 2240 | 1907299 | 19803 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 5 | 99015 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0089504 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | SONOMA-1102 | 42721102 | FUSE | 6939 | 20171008 | 2330 | 1894367 | 9843 | Distribution Circuit | Vegetation | Tree - bark fell into line | 15 | 50106 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085345 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | BELLEVUE-2103 | 43182103 | FUSE | 7197 | 20171009 | 313 | 1898660 | 13587 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 17 | 230979 | Clear-32-90 F | Pole-Wood | Broken, wire on object | 17-0086414 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | BELLEVUE-2103 | 43182103 | FUSE | 11331 | 20171009 | 313 | 1898790 | 13693 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 581551 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086452 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | CLOVERDALE-1102 | 42821102 | FUSE | 15705 | 20171009 | 30 | 1900344 | 7846 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 31384 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0087204 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 3 | DUNBAR-1102 | 43071102 | FUSE | 7015 | 20171009 | 136 | 1899587 | 16703 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 9 | 150327 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086872 | OH | Sus | 0 | 2017 | OCT | Yes | None | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | JUMPER | OPEN DDE@ 1/P/W/OF LINE & BUCK S/OF C2904 TWD | 20171009 | 417 | 1900182 | 19584 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 275 | 3394903 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087154 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 11177 | 20171009 | 417 | 1900920 | 12347 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 14 | 172858 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087154 | OH | Sus | 0 | 2017 | OCT | Yes | None | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | JUMPER | OJ'S 2 S/SS OF MTR#1006220457 | 20171009 | 412 | 1902088 | 17673 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 17673 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087779 | OH | Sus | 0 | 2017 | OCT | Yes | Multi-Fault | Yes | No
SONOMA | Tier 2 | PENNGROVE-1101 | 43471101 | FUSE | 4683 | 20171009 | 36 | 1894682 | 2251 | Distribution Circuit | Vegetation | Tree - branch fell on line | 49 | 66143 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085419 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | RINCON-1102 | 43321102 | FUSE | 15265 | 20171009 | 138 | 1896669 | 10977 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 19 | 208131 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086666 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE | 14985 | 20171009 | 17 | 1900801 | 19756 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 59268 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087371 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2223 | 20171009 | 17 | 1900803 | 19704 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 43 | 847272 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087372 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 69401 | 20171009 | 1605 | 1896824 | 2706 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 10824 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085746 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 7411 | 20171009 | 141 | 1901218 | 17881 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 18 | 321858 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087473 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 10107 | 20171009 | 211 | 1901335 | 13934 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 41802 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087527 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | SANTA ROSA A-1104 | 42151104 | FUSE | 12711 | 20171009 | 211 | 1901336 | 12122 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 5 | 60610 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087528 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | SANTA ROSA A-1104 | 42151104 | FUSE | 3943 | 20171009 | 211 | 1901338 | 20796 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 9 | 187164 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087529 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | SWITCH | 9267 | 20171009 | 141 | 1903332 | 25429 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 49 | 974037 | Clear-32-90 F | Other | Broken, wire on ground | 17-0088299 | OH | Sus | 0 | 2017 | OCT | Yes | Multi-Fault | Yes | No
SONOMA | Tier 2 | SONOMA-1105 | 42721105 | SWITCH | 532235 | 20171009 | 147 | 1902150 | 19500 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 132 | 2574000 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087806 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | DUNBAR-1101 | 43071101 | JUMPER | OJ'S NO HOME BEYOND | 20171020 | 1740 | 1906463 | 2767 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 5534 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0089267 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 81221 | 20171204 | 1131 | 1934989 | 424 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4240 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099652 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | TRIP-SAVER | 4947 | 20181121 | 521 | 219567 | 787 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 42298 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0101716 | OH | Sus | 43584951 | 2018 | NOV | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | TRIP-SAVER | 1285 | 20181129 | 1301 | 229048 | 720 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 40142 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105199 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | RINCON-1104 | 43321104 | FUSE | 2269 | 20181129 | 1611 | 229419 | 1329 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 31896 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105283 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4545 | 20190106 | 2009 | 257482 | 1021 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 9189 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005503 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | GEYSERVILLE-1102 | 42891102 | FUSE | 523 | 20190106 | 1230 | 255247 | 155 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 4340 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005073 | OH | Sus | 0 | 2019 | JAN | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE | 15035 | 20190106 | 1142 | 255169 | 378 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4158 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005082 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE | 2443 | 20190116 | 1434 | 267187 | 1531 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 13431 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009930 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | OTHER | WIRE DOWN @ 310 KING RD | 20190116 | 1904 | 271160 | 1200 | Distribution Circuit | Vegetation | Tree - fell into line | 227 | 260078 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010286 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | TRIP-SAVER | 6751 | 20190116 | 1450 | 267251 | 256 | Distribution Circuit | Vegetation | Tree - branch fell on line | 134 | 15145 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009868 | OH | Sus | 0 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 16211 | 20190116 | 1748 | 267899 | 2502 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 20397 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009997 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 6049 | 20190116 | 1900 | 269566 | 2454 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 9816 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010313 | OH | Sus | 0 | 2019 | JAN | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | OTHER | HOT WIRE DOWN 3 SS/OF 6263 | 20190116 | 1832 | 272312 | 1361 | Distribution Circuit | Vegetation | Tree - branch fell on line | 138 | 166097 | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0010519 | OH | Sus | 0 | 2019 | JAN | Yes | Open Circuit | Yes | Yes
SONOMA | Tier 3 | FULTON-1107 | 42561107 | FUSE | 11889 | 20190116 | 1829 | 269281 | 2483 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 27313 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0011389 | OH | Sus | 0 | 2019 | JAN | Yes | Force Out | Yes | No
SONOMA | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 5531 | 20190116 | 1455 | 267287 | 2980 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 51425 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009962 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | OTHER | 1/S/SS TO 12061 WIRE DOWN | 20190116 | 1519 | 267795 | 3913 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 114879 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009869 | OH | Sus | 0 | 2019 | JAN | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | MIRABEL-1101 | 42091101 | FUSE | 6485 | 20190116 | 2045 | 270806 | 2765 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 22120 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011618 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1335 | 20190116 | 2243 | 271679 | 2612 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 96644 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0011036 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 1761 | 20190116 | 1522 | 267478 | 1588 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 52404 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010090 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1101 | 42571101 | FUSE | 6051 | 20190116 | 1812 | 269199 | 1149 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 90771 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010428 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | TRIP-SAVER | 891 | 20190116 | 1825 | 269411 | 2684 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 53036 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010518 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 7317 | 20190116 | 1453 | 267275 | 265 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 7420 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009804 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 4899 | 20190116 | 1829 | 272008 | 2346 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 23028 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010411 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 11991 | 20190116 | 1626 | 272510 | 1658 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 46424 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010577 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 7183 | 20190116 | 1830 | 272660 | 1125 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 45000 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010594 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | TRIP-SAVER | 53477 | 20190116 | 1040 | 266734 | 343 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 18548 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009575 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 15399 | 20190116 | 1609 | 267714 | 226 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 11978 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0009960 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | OTHER | WIRE DOWN 1 SP LD SD 1581 | 20190116 | 1721 | 270517 | 1511 | Distribution Circuit | Vegetation | Tree - branch fell on line | 505 | 471427 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010284 | OH | Sus | 0 | 2019 | JAN | Yes | Open Circuit | Yes | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 74315 | 20190116 | 1741 | 270792 | 2570 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 51400 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011220 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 439 | 20190116 | 1958 | 270264 | 2894 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 43410 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011309 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 2027 | 20190116 | 1207 | 266854 | 264 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 7128 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009626 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 15609 | 20190116 | 1441 | 267208 | 324 | Distribution Circuit | Vegetation | Tree - branch fell on line | 98 | 31752 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009770 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1031 | 20190116 | 2025 | 270607 | 2543 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 61032 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010452 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER | 1067 | 20190116 | 2010 | 270390 | 1052 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 114668 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010992 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1993 | 20190116 | 2123 | 273321 | 1356 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 33900 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011011 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 7709 | 20190116 | 2112 | 270941 | 2438 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 19504 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011193 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 3331 | 20190116 | 1757 | 268867 | 2634 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 52680 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010085 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE | 4571 | 20190117 | 2022 | 275008 | 1004 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2008 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0011442 | OH | Sus | 0 | 2019 | JAN | Yes | Force Out | Yes | No
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | TRIP-SAVER | 2987 | 20190117 | 459 | 272558 | 1962 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 154998 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011665 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 11513 | 20190117 | 1629 | 274567 | 2630 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 26300 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011667 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 13477 | 20190117 | 806 | 272990 | 1923 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1923 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011668 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | OTHER | HOT WIRE DOWN 1/S/N/OF 6543 | 20190117 | 702 | 274066 | 678 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 24066 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011085 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 15455 | 20190117 | 823 | 273062 | 1680 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 8400 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010876 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER | 4859 | 20190117 | 802 | 272971 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 28800 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010966 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | Yes
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | OTHER | HOT WIRE DOWN 4/S/LS/OF 667 | 20190117 | 1052 | 274703 | 1455 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5820 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011322 | OH | Sus | 0 | 2019 | JAN | Yes | Open Circuit | Yes | Yes
SONOMA | Tier 3 | SALMON CREEK-1101 | 43161101 | FUSE | 615 | 20190117 | 2320 | 275085 | 1177 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3531 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011487 | OH | Sus | 0 | 2019 | JAN | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | DUNBAR-1101 | 43071101 | FUSE | 481459 | 20190204 | 1329 | 290547 | 365 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 730 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018037 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | RECLOSER | 132 | 20190209 | 1628 | 297191 | 1225 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1019 | 544883 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0020377 | OH | Sus | 43672759 | 2019 | FEB | Yes | Force Out | Yes | Yes
SONOMA | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4585 | 20190210 | 912 | 297225 | 206 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 412 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020629 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 134 | 20190212 | 1810 | 300950 | 1434 | Distribution Circuit | Vegetation | Tree - branch fell on line | 229 | 248170 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021884 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 12003 | 20190212 | 1520 | 300805 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 247 | 18338 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021522 | OH | Sus | 43678033 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 883 | 20190212 | 2254 | 301430 | 676 | Distribution Circuit | Vegetation | Tree - fell into line | 247 | 166972 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021683 | OH | Sus | 43678389 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24918 | 20190213 | 2208 | 305797 | 609 | Distribution Circuit | Vegetation | Tree - branch fell on line | 187 | 113883 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022647 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 1939 | 20190213 | 1748 | 305424 | 1705 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 15345 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022552 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 56225 | 20190213 | 1700 | 305331 | 1570 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 58090 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022539 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | COTATI-1102 | 42271102 | TRANSFORMER | 217930822751 | 20190214 | 1138 | 307125 | 545 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1090 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023156 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE | 3421 | 20190214 | 714 | 307326 | 1836 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 12852 | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023075 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE | 4571 | 20190214 | 1335 | 309444 | 1705 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 3410 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023305 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 99720 | 20190214 | 102 | 306093 | 1212 | Distribution Circuit | Vegetation | Tree - fell into line | 375 | 146016 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022725 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MIRABEL-1101 | 42091101 | FUSE | 2007 | 20190214 | 822 | 307730 | 1878 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9390 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023097 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 49587 | 20190214 | 243 | 307636 | 1896 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9480 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022908 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 12801 | 20190214 | 809 | 307621 | 1800 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7200 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023155 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 525 | 20190214 | 221 | 306375 | 519 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 19722 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022797 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 7499 | 20190214 | 1211 | 308918 | 1815 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5445 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023186 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 7927 | 20190214 | 201 | 307665 | 3328 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 49920 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023123 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 1113/2 | 20190214 | 2215 | 310977 | 3917 | Distribution Circuit | Vegetation | Tree - fell into line | 3897 | 403375 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023738 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 636 | 20190214 | 245 | 306425 | 847 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 36769 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022753 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | OTHER | WIRE DOWN 3 SPANS LD SIDE OF 7515 | 20190214 | 156 | 306893 | 916 | Distribution Circuit | Vegetation | Tree - fell into line | 138 | 86236 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022833 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 1627 | 20190214 | 21 | 306046 | 921 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 49734 | Overcast-Fog-Lightning-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022857 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 12217 | 20190214 | 711 | 307157 | 769 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2307 | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022889 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 12223 | 20190214 | 1630 | 310194 | 1465 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1465 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023589 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | PETALUMA C-1109 | 42631109 | FUSE | 2621 | 20190214 | 235 | 306411 | 743 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 11145 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022920 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 2 | SALMON CREEK-1101 | 43161101 | RECLOSER | 37368 | 20190214 | 1934 | 310741 | 1296 | Distribution Circuit | Equipment Failure/Involved | Overhead | 182 | 171819 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023646 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | CLOVERDALE-1101 | 42821101 | FUSE | 1231 | 20190226 | 2230 | 325553 | 705 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 61694 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028671 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE | 4139 | 20190226 | 2256 | 327079 | 2382 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 2382 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029041 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | RECLOSER | 70288 | 20190226 | 217 | 323781 | 1056 | Distribution Circuit | Vegetation | Tree - fell into line | 156 | 30950 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028067 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4271 | 20190226 | 1932 | 325162 | 2764 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 38696 | Clear-32-90 F | Conductor, Overhead | On Ground | 19-0029351 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 4523 | 20190226 | 1930 | 325158 | 5563 | Distribution Circuit | Environmental/External | Flood/Erosion | 16 | 89008 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0029861 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 2473 | 20190226 | 2220 | 325471 | 1214 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 43850 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 19-0028881 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 433 | 20190226 | 1635 | 324876 | 4209 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 138897 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028499 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MIRABEL-1102 | 42091102 | FUSE | 13669 | 20190226 | 1854 | 325128 | 4191 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 37719 | Partly Cloudy-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028600 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 8457 | 20190226 | 2115 | 325305 | 4064 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 52832 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 19-0029680 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 15399 | 20190226 | 1717 | 324909 | 1513 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 58874 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028903 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 2561 | 20190226 | 1949 | 325181 | 2726 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 57246 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028952 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 3043 | 20190226 | 1310 | 324525 | 3230 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 25840 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0029113 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 4001 | 20190226 | 339 | 323831 | 511 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 511 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028074 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 256 | 20190226 | 2248 | 325487 | 4178 | Distribution Circuit | Environmental/External | Flood/Erosion | 1431 | 4432998 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028605 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 2659 | 20190226 | 2229 | 327860 | 4131 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 152847 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029297 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 3895 | 20190226 | 2029 | 325251 | 4268 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 46948 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029299 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | TRIP-SAVER | 2987 | 20190226 | 1556 | 324897 | 4590 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 362610 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 19-0029429 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 2579 | 20190226 | 2236 | 325505 | 5126 | Distribution Circuit | Environmental/External | Flood/Erosion | 10 | 51260 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029858 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | RECLOSER | 120 | 20190226 | 1536 | 324785 | 5870 | Distribution Circuit | Environmental/External | Flood/Erosion | 492 | 300853 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028450 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 2035 | 20190226 | 605 | 323868 | 5260 | Distribution Circuit | Vegetation | Tree - fell into line | 144 | 160137 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028092 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 1621 | 20190226 | 2135 | 325329 | 2243 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 47603 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 19-0028795 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 204 | 20190227 | 543 | 326383 | 3763 | Distribution Circuit | Environmental/External | Flood/Erosion | 117 | 245153 | Clear-32-90 F | Conductor, Overhead | On Ground | 19-0028728 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MIRABEL-1102 | 42091102 | FUSE | 7711 | 20190227 | 1051 | 326672 | 4654 | Distribution Circuit | Environmental/External | Flood/Erosion | 35 | 23082 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029828 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 467555 | 20190227 | 100 | 326056 | 2204 | Distribution Circuit | Vegetation | Tree - fell into line | 253 | 23104 | Clear-32-90 F | Cutout, fuse holder | Broken, wire on ground | 19-0028695 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 4899 | 20190227 | 1336 | 327124 | 1377 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4081 | Clear-32-90 F | Conductor, Overhead | On Ground | 19-0029052 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 250 | 20190227 | 54 | 325997 | 3944 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 244528 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0029555 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SONOMA | Tier 2 | PETALUMA C-1109 | 42631109 | JUMPER | WIRE DOWN | 20190227 | 748 | 326533 | 244 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 788 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028857 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2223 | 20190227 | 40 | 326022 | 1092 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 48048 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028678 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | TRIP-SAVER | 6751 | 20190608 | 1848 | 401789 | 1065 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 44664 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0064689 | OH | Sus | 0 | 2019 | JUN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2225 | 20190608 | 1017 | 401355 | 241 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 21690 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0064576 | OH | Sus | 0 | 2019 | JUN | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | OTHER | WIRE DWN 4/SP/LD SIDE OF 2377 | 20190923 | 1452 | 607255 | 642 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 14 | 8708 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0102604 | OH | Sus | 43964302 | 2019 | SEP | Yes | Open Circuit | Yes | Yes
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 8287 | 20191009 | 1056 | 650876 | 357 | Distribution Circuit | 3rd Party | Vehicle | 11 | 1127 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0109622 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | SALMON CREEK-1101 | 43161101 | FUSE | 615 | 20191010 | 1439 | 653377 | 473 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 3 | 1419 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0110133 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 15463 | 20191120 | 1400 | 711702 | 488 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 4880 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0126948 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 840899 | 20191127 | 1103 | 721010 | 344 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1032 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0130309 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 694641 | 20200209 | 925 | 781601 | 669 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 40140 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0019030 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 246 | 20200209 | 1053 | 782348 | 456 | Distribution Circuit | Vegetation | Tree - fell into line | 352 | 67040 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0019132 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 4889 | 20200209 | 1020 | 785843 | 738 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 84132 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0019479 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 15441 | 20200209 | 1108 | 782144 | 284 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 2840 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0019175 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 1297 | 20200816 | 455 | 1010637 | 707 | Distribution Circuit | Vegetation | Tree - branch fell on line | 179 | 126553 | Partly Cloudy-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0084737 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 318 | 20200816 | 425 | 1010400 | 750 | Distribution Circuit | Vegetation | Tree - branch fell on line | 434 | 325500 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0084672 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 12111 | 20200816 | 448 | 1010564 | 860 | Distribution Circuit | Environmental/External | Lightning | 33 | 28380 | Overcast-Drizzle-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0084813 | OH | Sus | 0 | 2020 | AUG | Yes | Force Out | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 261774 | 20200927 | 1241 | 1095169 | 428 | Distribution Circuit | Vegetation | Tree - fell into line | 185 | 70828 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 20-0102103 | OH | Sus | 31514675 | 2020 | SEP | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | DUNBAR-1101 | 43071101 | FUSE | 4829 | 20210119 | 154 | 1214097 | 916 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2748 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0010120 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | DUNBAR-1103 | 43071103 | FUSE | 13499 | 20210119 | 439 | 1214692 | 475 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3325 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010240 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 140 | 20210119 | 522 | 1214841 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 143 | 22766 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010196 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 939 | 20210119 | 838 | 1215848 | 562 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 2811 | Clear-32-90 F | Transformer (OH) | Broken, wire on ground | 21-0010644 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER | 1989 | 20210119 | 28 | 1213521 | 551 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 23693 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0009976 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 7709 | 20210119 | 822 | 1215729 | 305 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2440 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010545 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 208 | 20210119 | 331 | 1214425 | 607 | Distribution Circuit | Vegetation | Tree - branch fell on line | 185 | 65855 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010122 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 1071 | 20210125 | 1130 | 1224312 | 588 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 4116 | Clear-32-90 F | Conductor, Overhead | On Ground | 21-0013978 | OH | Sus | 31528913 | 2021 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4543 | 20210127 | 1214 | 1229742 | 440 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 4400 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0016230 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1101 | 42571101 | SWITCH | 1617 | 20210127 | 1545 | 1236487 | 12 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 1140 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0015258 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE | 13193 | 20210128 | 1455 | 1239941 | 423 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2961 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0017757 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 3083 | 20210812 | 1137 | 1441120 | 636 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 23532 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0103653 | OH | Sus | 0 | 2021 | AUG | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 36536 | 20211024 | 717 | 1508260 | 787 | Distribution Circuit | Vegetation | Tree - fell into line | 802 | 316449 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135702 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 4566 | 20211024 | 619 | 1507973 | 723 | Distribution Circuit | Vegetation | Tree - fell into line | 303 | 149805 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135646 | OH | Sus | 0 | 2021 | OCT | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 5525 | 20211024 | 719 | 1508233 | 659 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 61287 | Clear-32-90 F | Conductor, Overhead | On Ground | 21-0135949 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 1297 | 20211024 | 1016 | 1509854 | 576 | Distribution Circuit | Vegetation | Tree - fell into line | 178 | 102528 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136056 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 7271 | 20211024 | 1853 | 1517481 | 1436 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 72004 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0137073 | OH | Sus | 0 | 2021 | OCT | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | TRIP-SAVER | 1703 | 20211024 | 451 | 1507492 | 1470 | Distribution Circuit | Vegetation | Tree - fell into line | 788 | 759376 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135611 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 2595 | 20211024 | 458 | 1510259 | 937 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 22488 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135611 | OH | Sus | 0 | 2021 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 2 | MONTE RIO-1111 | 42811111 | FUSE | 7385 | 20211024 | 902 | 1508971 | 601 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 11790 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136120 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 429 | 20211024 | 1125 | 1510626 | 274 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 8494 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136182 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER | 1067 | 20211024 | 732 | 1508323 | 798 | Distribution Circuit | Vegetation | Tree - branch fell on line | 109 | 86982 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135977 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER | 8299 | 20211024 | 809 | 1508688 | 589 | Distribution Circuit | Vegetation | Tree - branch fell on line | 51 | 30039 | Clear-32-90 F | Conductor, Overhead | On Ground | 21-0136068 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE | 2439 | 20211025 | 2235 | 1520550 | 994 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2982 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0137794 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 6697 | 20211025 | 1035 | 1518284 | 1632 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 14686 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0137537 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 64758 | 20211213 | 1746 | 1568275 | 318 | Distribution Circuit | Vegetation | Tree - branch fell on line | 813 | 139537 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0157492 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE | 1575 | 20211215 | 1345 | 1572745 | 240 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 798 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0158463 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 124 | 20211215 | 1752 | 1573229 | 304 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 19206 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0158550 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FULTON-1107 | 42561107 | RECLOSER | 145720 | 20211225 | 646 | 1581136 | 526 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 26068 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160527 | OH | Sus | 31588285 | 2021 | DEC | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | OTHER | WIRE DOWN SS OF CGC 217248127956 | 20211225 | 419 | 1581093 | 736 | Distribution Circuit | Vegetation | Tree - fell into line | 387 | 75749 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 21-0160519 | OH | Sus | 31588363 | 2021 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | DUNBAR-1101 | 43071101 | FUSE | 2107 | 20211227 | 756 | 1585081 | 326 | Distribution Circuit | Equipment Failure/Involved | Overhead | 105 | 34230 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0161018 | OH | Sus | 45102085 | 2021 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | RECLOSER | 120 | 20211229 | 315 | 1587694 | 56 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 5936 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0161473 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | RECLOSER | 5040 | 20211229 | 315 | 1587697 | 869 | Distribution Circuit | Vegetation | Tree - fell into line | 387 | 336303 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0161473 | OH | Sus | 35314365 | 2021 | DEC | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | SWITCH | 1011 | 20211229 | 2212 | 1589134 | 8 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 440 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0161595 | OH | Sus | 45103122 | 2021 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1104 | 42271104 | FUSE | 12145 | 20221210 | 945 | 1881318 | 574 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 4018 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0138295 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 969182 | 20221210 | 522 | 1880319 | 421 | Distribution Circuit | Vegetation | Tree - branch fell on line | 565 | 118993 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138054 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 37520 | 20221210 | 831 | 1881056 | 414 | Distribution Circuit | Vegetation | Tree - branch fell on line | 76 | 30558 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138172 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2225 | 20221210 | 936 | 1881312 | 688 | Distribution Circuit | Vegetation | Tree - branch fell on line | 92 | 63296 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138463 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 11121 | 20221231 | 1552 | 1904866 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2268 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0142690 | OH | Sus | 0 | 2022 | DEC | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | OTHER | 217436926073 | 20221231 | 1613 | 1904934 | 267 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 267 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0142684 | OH | Sus | 45612880 | 2022 | DEC | Yes | Line to Ground | Yes | Yes
SONOMA | Tier 2 | COTATI-1102 | 42271102 | RECLOSER | 464 | 20230104 | 859 | 1912851 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 5315 | 377617 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0005652 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | RINCON-1104 | 43321104 | OCB | 1104/2 | 20230104 | 1854 | 1917314 | 338 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4020 | 665256 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0006501 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | SONOMA-1104 | 42721104 | FUSE | 12407 | 20230104 | 500 | 1912232 | 706 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 21886 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0005559 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 202 | 20230110 | 833 | 1943811 | 451 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 48411 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0012060 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | JUMPER | WIRE DOWN SS OF CGC 217376729268 | 20230114 | 1048 | 1954369 | 362 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2534 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016194 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1112 | 42751112 | FUSE | 579 | 20230116 | 10 | 1956458 | 671 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 42944 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016861 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1112 | 42751112 | FUSE | 2345 | 20230221 | 1516 | 1992357 | 409 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 27403 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0031516 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1997 | 20230221 | 1345 | 1990934 | 379 | Distribution Circuit | Vegetation | Tree - branch fell on line | 112 | 42448 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0031364 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 10787 | 20230224 | 102 | 2001448 | 973 | Distribution Circuit | Environmental/External | Ice or snow | 28 | 27244 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0033601 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | GEYSERVILLE-1102 | 42891102 | FUSE | 3517 | 20230224 | 33 | 2001312 | 1109 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 16635 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0033786 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE | 2439 | 20230227 | 822 | 2011382 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1800 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0036236 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 612266 | 20230314 | 324 | 2035161 | 910 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 35490 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0044467 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | RECLOSER | 933786 | 20230314 | 945 | 2035725 | 120 | Distribution Circuit | Vegetation | Tree - bark fell into line | 27 | 3240 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0044670 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | TRIP-SAVER | 4859 | 20230314 | 1022 | 2036689 | 640 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 28160 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0045056 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 6399 | 20230314 | 618 | 2035193 | 743 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 23033 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0044508 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MIRABEL-1102 | 42091102 | FUSE | 913 | 20230314 | 1520 | 2042765 | 401 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 2601 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0045447 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 79306 | 20230314 | 1142 | 2037645 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 31266 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0044932 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | JUMPER | 4 LD SIDE OF 17803 WIRE DOWN | 20230321 | 2234 | 2062466 | 1299 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 10920 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on object | 23-0050587 | OH | Sus | 0 | 2023 | MAR | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | OTHER | 949673 | 20230321 | 1345 | 2056947 | 237 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 237 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0049718 | OH | Sus | 0 | 2023 | MAR | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER | B1101 | 20130408 | 302 | 768524 | 651 | Distribution Circuit | Equipment Failure/Involved | Other | 450 | 0 | Strong winds-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0022141 | OH | Sus | 41877870 | 2013 | APR | Yes |  | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 9181 | 20130408 | 218 | 768978 | 698 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 9772 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0022232 | OH | Sus | 41877941 | 2013 | APR | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 5465 | 20130408 | 503 | 769114 | 1137 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 53911 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022293 | OH | Sus | 30988000 | 2013 | APR | Yes |  | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 10025 | 20130408 | 428 | 769770 | 1122 | Distribution Circuit | Equipment Failure/Involved | Other | 36 | 40392 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0022442 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 9741 | 20130408 | 620 | 768938 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 17010 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0022451 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | OTHER |  | 20130408 | 1628 | 771123 | 1135 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 4136 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022792 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 2229 | 20130408 | 344 | 768597 | 1006 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 14084 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0022445 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 1909 | 20130408 | 134 | 768275 | 926 | Distribution Circuit | Equipment Failure/Involved | Other | 5 | 4630 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0022528 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 2835 | 20130408 | 1641 | 770758 | 47 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 3885 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0022729 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 2871 | 20130408 | 1652 | 770780 | 1356 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4068 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0022766 | OH | Sus | 0 | 2013 | APR | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | FUSE | 1275 | 20130408 | 652 | 769007 | 450 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 4050 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022423 | OH | Sus | 0 | 2013 | APR | Yes |  | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER | 10722 | 20130408 | 156 | 768329 | 941 | Distribution Circuit | Vegetation | Tree - branch fell on line | 798 | 371844 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0022130 | OH | Sus | 41877861 | 2013 | APR | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 7799 | 20130408 | 441 | 768950 | 1265 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 38703 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022550 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | OTHER |  | 20130408 | 850 | 769390 | 860 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 860 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022672 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | SEACLIFF-0401 | 83500401 | OTHER |  | 20130408 | 1951 | 771132 | 1089 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 7255 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0022825 | OH | Sus | 0 | 2013 | APR | Yes | Open Circuit | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5421 | 20130623 | 1650 | 815162 | 653 | Distribution Circuit | Equipment Failure/Involved | Other | 112 | 15520 | Overcast-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0041878 | OH | Sus | 31004714 | 2013 | JUN | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | OTHER |  | 20141203 | 758 | 1123048 | 1173 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 78210 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073443 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5183 | 20141203 | 808 | 1121957 | 696 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 15224 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073235 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5439 | 20141203 | 1352 | 1123312 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 228 | 33987 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073506 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 6215 | 20141203 | 939 | 1122157 | 1141 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 35371 | Heavy rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0073650 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 9307 | 20141203 | 2144 | 1123979 | 626 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 2504 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073666 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER | 10296 | 20141203 | 1031 | 1122359 | 793 | Distribution Circuit | Vegetation | Tree - fell into line | 629 | 360852 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073302 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5485 | 20141203 | 1047 | 1122408 | 1050 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 34650 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073586 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5487 | 20141203 | 1024 | 1122372 | 991 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 54505 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073596 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 7219 | 20141203 | 1706 | 1123757 | 1040 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 4478 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073610 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 12069 | 20141203 | 1115 | 1122605 | 945 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 31185 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073622 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 9763 | 20141203 | 134 | 1121585 | 436 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 6540 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073126 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 4259 | 20141203 | 204 | 1121602 | 1240 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 7440 | Heavy rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0073169 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER |  | 20141203 | 1029 | 1122328 | 735 | Distribution Circuit | Vegetation | Tree - branch fell on line | 94 | 64075 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073551 | OH | Sus | 0 | 2014 | DEC | Yes | Open Circuit | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER |  | 20141203 | 1202 | 1122943 | 1258 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1258 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073692 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 11965 | 20141203 | 708 | 1121833 | 1102 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8816 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073393 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 5335 | 20141203 | 630 | 1121772 | 761 | Distribution Circuit | Vegetation | Tree - branch fell on line | 74 | 56314 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073228 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10786 | 20141203 | 728 | 1121846 | 1361 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 97551 | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0073187 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | CAMP EVERS-2105 | 83622105 | FUSE | 5239 | 20141203 | 1155 | 1122911 | 680 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 27880 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073441 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9071 | 20141203 | 1055 | 1122594 | 996 | Distribution Circuit | Vegetation | Tree - branch fell on line | 122 | 121512 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073570 | OH | Sus | 42283952 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 10717 | 20141203 | 852 | 1122321 | 1973 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 45815 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073639 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9701 | 20141203 | 2322 | 1124051 | 536 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 536 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073680 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 37210 | 20141203 | 141 | 1121592 | 679 | Distribution Circuit | Vegetation | Tree - branch fell on line | 141 | 57808 | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0073131 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 2821 | 20141203 | 700 | 1121807 | 907 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2721 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073258 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 12055 | 20141203 | 1156 | 1122918 | 939 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4695 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073593 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8961 | 20141203 | 2353 | 1124060 | 362 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 724 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073661 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 2 | PACIFIC GROVE-0422 | 182440422 | SWITCH | 99040 | 20141203 | 1428 | 1123261 | 682 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 402 | 10854 | Drizzle-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0073476 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 3 | PAUL SWEET-2104 | 83252104 | OTHER |  | 20141203 | 1906 | 1123961 | 634 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5072 | Fog-32 - 90 F | Conductor, Overhead | On Ground | 14-0073642 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 5401 | 20141203 | 841 | 1123613 | 849 | Distribution Circuit | Vegetation | Tree - branch fell on line | 70 | 39732 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073514 | OH | Sus | 0 | 2014 | DEC | Yes | Open Circuit | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8359 | 20141203 | 728 | 1122195 | 752 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 11280 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073517 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 7371 | 20141203 | 1229 | 1123053 | 931 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 4655 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0073601 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 9005 | 20141203 | 1353 | 1123315 | 913 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 19173 | Heavy rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0073618 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | RECLOSER | 9698 | 20141203 | 514 | 1121721 | 796 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 17469 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073151 | OH | Sus | 31117940 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 40285 | 20141203 | 1058 | 1122509 | 392 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 17248 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073390 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER | 16010 | 20141211 | 921 | 1132222 | 1016 | Distribution Circuit | Vegetation | Tree - fell into line | 138 | 140208 | Heavy rain-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0075254 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 5143 | 20141211 | 948 | 1132445 | 2592 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 67392 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076289 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 9309 | 20141211 | 1035 | 1133007 | 2453 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 209809 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075698 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 7279 | 20141211 | 923 | 1132204 | 2997 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 17982 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076333 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5485 | 20141211 | 1352 | 1134064 | 743 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 24519 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076034 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5487 | 20141211 | 1259 | 1133756 | 1271 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 69905 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0076059 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER |  | 20141211 | 1417 | 1136990 | 1761 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7044 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076118 | OH | Sus | 0 | 2014 | DEC | Yes | Open Circuit | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 5066 | 20141211 | 654 | 1130234 | 813 | Distribution Circuit | Equipment Failure/Involved | Other | 108 | 78098 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075017 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 12779 | 20141211 | 540 | 1129530 | 740 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 11840 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075065 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | RECLOSER | 5300 | 20141211 | 940 | 1132406 | 935 | Distribution Circuit | Vegetation | Tree - branch fell on line | 347 | 235865 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075256 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 5219 | 20141211 | 852 | 1135792 | 849 | Distribution Circuit | Equipment Failure/Involved | Other | 21 | 17829 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075829 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 12887 | 20141211 | 817 | 1131784 | 735 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 89661 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075833 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 5217 | 20141211 | 2044 | 1135994 | 151 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 2265 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075973 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 6103 | 20141211 | 903 | 1131963 | 2085 | Distribution Circuit | Equipment Failure/Involved | Other | 54 | 112590 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075683 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | RECLOSER | 11056 | 20141211 | 2328 | 1136631 | 905 | Distribution Circuit | Vegetation | Tree - fell into line | 452 | 409060 | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0076002 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 9499 | 20141211 | 1115 | 1139312 | 2730 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5460 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076600 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6085 | 20141211 | 907 | 1133339 | 2020 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 20200 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075401 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | OTHER |  | 20141211 | 853 | 1133361 | 1749 | Distribution Circuit | Vegetation | Tree - fell into line | 514 | 188980 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075409 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 11929 | 20141211 | 2132 | 1136251 | 1636 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 81800 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076015 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 8883 | 20141211 | 954 | 1132524 | 2003 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 34336 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076307 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9435 | 20141211 | 1734 | 1135169 | 1845 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 25830 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076559 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | CAMP EVERS-2106 | 83622106 | RECLOSER | 5302 | 20141211 | 816 | 1131504 | 737 | Distribution Circuit | Vegetation | Tree - fell into line | 442 | 192760 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075138 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 7683 | 20141211 | 836 | 1131681 | 334 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 5344 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075286 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 8553 | 20141211 | 1316 | 1133871 | 2332 | Distribution Circuit | Equipment Failure/Involved | Other | 7 | 16324 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075642 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE | 8047 | 20141211 | 916 | 1135461 | 2354 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 21114 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075926 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | LAURELES-1111 | 182371111 | FUSE | 8407 | 20141211 | 721 | 1130936 | 3484 | Distribution Circuit | Equipment Failure/Involved | Other | 8 | 27872 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076240 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 3 | LOMPICO-0401 | 88880401 | RECLOSER | 11010 | 20141211 | 802 | 1131296 | 1100 | Distribution Circuit | Equipment Failure/Involved | Other | 106 | 113123 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0075102 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
CENTRAL COAST | Tier 3 | LOMPICO-0401 | 88880401 | FUSE | 5629 | 20141211 | 959 | 1132325 | 1925 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 38500 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076115 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | LOMPICO-0401 | 88880401 | FUSE | BXD7 | 20141211 | 802 | 1136351 | 2016 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2016 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075102 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | FUSE | 8833 | 20141211 | 838 | 1131698 | 2363 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 7089 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075424 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE | 2181 | 20141211 | 917 | 1132240 | 1717 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 112429 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075812 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | PACIFIC GROVE-0422 | 182440422 | FUSE | 2581 | 20141211 | 811 | 1131962 | 1310 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 36586 | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0075208 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER | 36516 | 20141211 | 642 | 1129620 | 1063 | Distribution Circuit | Vegetation | Tree - branch fell on line | 883 | 322996 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074992 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 83716 | 20141211 | 659 | 1130272 | 2059 | Distribution Circuit | Equipment Failure/Involved | Other | 30 | 54203 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075060 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 7371 | 20141211 | 702 | 1134590 | 1628 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 8140 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075619 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8515 | 20141211 | 1227 | 1133578 | 1106 | Distribution Circuit | Vegetation | Tree - fell into line | 103 | 92438 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075772 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 2979 | 20141211 | 1412 | 1135808 | 1068 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4272 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075834 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 5401 | 20141211 | 1814 | 1135597 | 1088 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 76160 | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0076138 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 1957 | 20141211 | 1407 | 1134196 | 1423 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5692 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075650 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 2199 | 20141211 | 2031 | 1135947 | 1100 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 31900 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075916 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 11835 | 20141211 | 1255 | 1133738 | 883 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 10864 | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075594 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | RECLOSER | 9698 | 20141211 | 730 | 1130893 | 3418 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 32886 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075054 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | RECLOSER | 9114 | 20141211 | 1005 | 1132798 | 2934 | Distribution Circuit | Vegetation | Tree - fell into line | 866 | 342914 | Overcast-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075329 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 7873 | 20141211 | 1242 | 1133648 | 3196 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 43320 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075820 | OH | Sus | 31120494 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 7879 | 20141211 | 1219 | 1133503 | 2860 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 42900 | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0076664 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER | 92792 | 20141211 | 751 | 1131212 | 2272 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 320352 | Drizzle-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075194 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER | 9118 | 20141211 | 900 | 1131664 | 1083 | Distribution Circuit | Vegetation | Tree - fell into line | 617 | 188759 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075217 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER | 9488 | 20141211 | 1004 | 1132789 | 3193 | Distribution Circuit | Vegetation | Tree - fell into line | 223 | 225105 | Drizzle-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075309 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 7537 | 20141211 | 837 | 1131693 | 1873 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9365 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076380 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 9125 | 20141212 | 631 | 1137634 | 599 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 25158 | Strong winds-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0076474 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 7299 | 20141212 | 648 | 1137234 | 647 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 7764 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076347 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 10717 | 20141212 | 448 | 1137063 | 552 | Distribution Circuit | Equipment Failure/Involved | Other | 25 | 13800 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076227 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 5020 | 20141212 | 43 | 1136771 | 1262 | Distribution Circuit | Vegetation | Tree - fell into line | 1183 | 307760 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076035 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8329 | 20141212 | 816 | 1137521 | 2002 | Distribution Circuit | Equipment Failure/Involved | Other | 7 | 14014 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076649 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | GREEN VALLEY-2101 | 83192101 | FUSE | 921 | 20141212 | 1326 | 1138416 | 1329 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2658 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076392 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 12129 | 20141212 | 1038 | 1138006 | 782 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 782 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076389 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | OTHER |  | 20141212 | 1423 | 1139224 | 1302 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1302 | Fog-32 - 90 F | Conductor, Underground | Broken, wire on ground | 14-0076574 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | RECLOSER | 10960 | 20141212 | 951 | 1137851 | 293 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2378 | 424771 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076271 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 40285 | 20141212 | 140 | 1138068 | 1310 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 39760 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076314 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 7537 | 20141212 | 1643 | 1138907 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1956 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076571 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 9125 | 20141230 | 2045 | 1156256 | 1245 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 52290 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079660 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5501 | 20141230 | 2013 | 1155425 | 1588 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 192492 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079594 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER |  | 20141230 | 2216 | 1155999 | 1404 | Distribution Circuit | Vegetation | Tree - branch fell on line | 279 | 81266 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079613 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 8471 | 20141230 | 2216 | 1157480 | 1454 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8724 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079773 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5435 | 20141230 | 2118 | 1155651 | 1327 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 9289 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0079775 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8403 | 20141230 | 2011 | 1155514 | 1594 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 138379 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079669 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 7295 | 20141230 | 1544 | 1153547 | 1546 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 37227 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079385 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 12887 | 20141230 | 1926 | 1155809 | 2123 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 197757 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079516 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 7301 | 20141230 | 1831 | 1155994 | 795 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 13515 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079565 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 3233 | 20141230 | 2036 | 1157188 | 1714 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 63418 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079726 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 6103 | 20141230 | 1214 | 1151785 | 1786 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 13234 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079212 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 5335 | 20141230 | 1916 | 1155163 | 875 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 64750 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079593 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9247 | 20141230 | 1832 | 1154816 | 1933 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 71521 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079560 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 7959 | 20141230 | 2011 | 1155388 | 2197 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 39546 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079598 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 1427 | 20141230 | 2001 | 1154731 | 1820 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 101920 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079607 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9033 | 20141230 | 1856 | 1157284 | 1804 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 41168 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079736 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 10718 | 20141230 | 2019 | 1155441 | 596 | Distribution Circuit | Vegetation | Tree - fell into line | 230 | 104984 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079465 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 1633 | 20141230 | 2206 | 1155751 | 1430 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 12870 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079779 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 11737 | 20141230 | 1342 | 1152371 | 1984 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 15936 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079403 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 1939 | 20141230 | 2057 | 1155593 | 1895 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 11370 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0002021 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10728 | 20150206 | 753 | 1173502 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 3019 | 259134 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009860 | OH | Sus | 31132982 | 2015 | FEB | Yes | Line to Line | Yes
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE | 1491 | 20150206 | 1621 | 1176829 | 548 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 14621 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010646 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 6625 | 20150206 | 218 | 1173086 | 672 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 10080 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009879 | OH | Sus | 42329112 | 2015 | FEB | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | LOMPICO-0401 | 88880401 | FUSE | 10457 | 20150206 | 1730 | 1176990 | 1610 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 25760 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011372 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | RECLOSER | 440 | 20150206 | 1510 | 1176124 | 694 | Distribution Circuit | Vegetation | Tree - fell into line | 368 | 79208 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0010398 | OH | Sus | 31132865 | 2015 | FEB | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 3459 | 20150206 | 2123 | 1178684 | 1275 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 67575 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010872 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 11305 | 20150207 | 1549 | 1181473 | 569 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7397 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011297 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 2453 | 20150207 | 653 | 1180209 | 387 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 2283 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011056 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 6185 | 20150207 | 652 | 1180206 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2160 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011130 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5421 | 20150208 | 1741 | 1183927 | 679 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 41006 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011779 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | BIG BASIN-1102 | 82841102 | FUSE | 11817 | 20150208 | 1751 | 1185409 | 1918 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 13963 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011919 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | OTHER |  | 20150208 | 1056 | 1182430 | 851 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 851 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011654 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7605 | 20150208 | 1506 | 1183040 | 431 | Distribution Circuit | Equipment Failure/Involved | Other | 16 | 6896 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011651 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | LOMPICO-0401 | 88880401 | FUSE | 5619 | 20150208 | 1829 | 1183478 | 760 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 60040 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011726 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | LOMPICO-0401 | 88880401 | FUSE | 5629 | 20150208 | 1738 | 1183996 | 848 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 16960 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011768 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | PAUL SWEET-2102 | 83252102 | FUSE | 11105 | 20150208 | 1125 | 1182507 | 1040 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6240 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011669 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 2453 | 20150208 | 1227 | 1182688 | 548 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 7672 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011638 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | JUMPER | OPEN JUMPERS 1 SPAN SS MTR | 20151018 | 49 | 1324491 | 508 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 3048 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 15-0071472 | OH | Sus | 0 | 2015 | OCT | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5507 | 20151213 | 1005 | 1361151 | 405 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 13770 | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084792 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 7219 | 20151213 | 1005 | 1361152 | 578 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 10982 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084839 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | JUMPER | OJ'S TO MTR# 1007590064 | 20151213 | 1010 | 1362302 | 673 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2019 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084876 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8259 | 20151213 | 1731 | 1362822 | 334 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 6012 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0085039 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 3233 | 20151213 | 957 | 1361120 | 758 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 21142 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084859 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 5577 | 20151213 | 1011 | 1361207 | 483 | Distribution Circuit | Equipment Failure/Involved | Overhead | 98 | 20928 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084823 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8427 | 20151213 | 944 | 1361640 | 101 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 4343 | Clear-32-90 F | Conductor, Overhead | On Ground | 15-0084752 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 6601 | 20151213 | 1044 | 1361445 | 1635 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 39921 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084936 | OH | Sus | 0 | 2015 | DEC | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 1945 | 20151213 | 1032 | 1361363 | 969 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4845 | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084858 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | JUMPER | OPEN JPRS 1 SPANS SS OF MTR 50001225809 | 20160217 | 1427 | 1405459 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1635 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013271 | OH | Sus | 0 | 2016 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 9545 | 20160217 | 1638 | 1405933 | 737 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1474 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013302 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | JUMPER | OJ HIGHSIDE OF 2293 | 20160217 | 1942 | 1407599 | 828 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 828 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013489 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 8033 | 20160217 | 1950 | 1406650 | 1327 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 9289 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013773 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5487 | 20160305 | 1556 | 1417015 | 322 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 15080 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017628 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5473 | 20160305 | 1930 | 1418526 | 250 | Distribution Circuit | Vegetation | Tree - branch fell on line | 90 | 22500 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017965 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5519 | 20160305 | 1933 | 1418557 | 1172 | Distribution Circuit | Vegetation | Tree - fell into line | 174 | 188631 | Overcast-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0018051 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 7773 | 20160305 | 1644 | 1417445 | 850 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 20206 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017976 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8501 | 20160305 | 1641 | 1417392 | 903 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 18060 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018033 | OH | Sus | 0 | 2016 | MAR | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 7289 | 20160305 | 2246 | 1421125 | 1055 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 14770 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018246 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | RECLOSER | 10946 | 20160305 | 1420 | 1416774 | 734 | Distribution Circuit | Vegetation | Tree - fell into line | 156 | 50664 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017498 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20160305 | 2049 | 1419389 | 1468 | Distribution Circuit | Vegetation | Tree - branch fell on line | 184 | 172095 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 16-0017987 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 287 | 20160305 | 1157 | 1416594 | 339 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 5424 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017465 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10728 | 20160305 | 1544 | 1416983 | 666 | Distribution Circuit | Vegetation | Tree - fell into line | 3432 | 251938 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017537 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 11929 | 20160305 | 1632 | 1418034 | 705 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 60572 | Clear-32-90 F | Conductor, Overhead | On Ground | 16-0017695 | OH | Sus | 0 | 2016 | MAR | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9251 | 20160305 | 1830 | 1418135 | 436 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3052 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 16-0018037 | OH | Sus | 0 | 2016 | MAR | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | OJ'S 1 SP SS 1 BROOKES LN | 20160305 | 1721 | 1421565 | 1374 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5496 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018345 | OH | Sus | 0 | 2016 | MAR | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7457 | 20160305 | 731 | 1416317 | 714 | Distribution Circuit | Equipment Failure/Involved | Overhead | 317 | 42327 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0017396 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 11323 | 20160305 | 1313 | 1416660 | 426 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2130 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017496 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 1117 | 20160305 | 1740 | 1421282 | 2843 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 56860 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018413 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE | 2875 | 20160305 | 2157 | 1419887 | 973 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 8757 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018197 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE | 8245 | 20160305 | 1753 | 1420877 | 1174 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 18886 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 16-0018103 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 5074 | 20160305 | 2045 | 1419193 | 1521 | Distribution Circuit | Vegetation | Tree - fell into line | 136 | 173554 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017828 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 5078 | 20160305 | 2049 | s1189817 | 246 | Distribution Circuit | Equipment Failure/Involved | Overhead | 808 | 138399 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0017955 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5539 | 20160305 | 2106 | 1423823 | 2609 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 5218 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018853 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6641 | 20160305 | 2058 | 1420902 | 1900 | Distribution Circuit | Vegetation | Tree - fell into line | 265 | 370817 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018136 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20160305 | 1616 | 1417182 | 805 | Distribution Circuit | Vegetation | Tree - fell into line | 429 | 71579 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017557 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 10421 | 20160305 | 1646 | 1417459 | 1329 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 19935 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0017667 | OH | Sus | 0 | 2016 | MAR | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20160305 | 2102 | 1419375 | 1071 | Distribution Circuit | Vegetation | Tree - fell into line | 6887 | 631240 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017873 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 9623 | 20160305 | 2142 | 1417491 | 548 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 21920 | Overcast-Rain-32-90 F | Conductor, Overhead | On Ground | 16-0018040 | OH | Sus | 0 | 2016 | MAR | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 2371 | 20160305 | 1628 | 1417245 | 552 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 21176 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017602 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2667 | 20161014 | 1515 | 1559890 | 195 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 975 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072262 | OH | Sus | 0 | 2016 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 5397 | 20161014 | 1805 | 1560193 | 680 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 15640 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072307 | OH | Sus | 0 | 2016 | OCT | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 6103 | 20170103 | 2303 | 1617210 | 2395 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 15274 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003363 | OH | Sus | 31292865 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 3307 | 20170103 | 1012 | 1615612 | 96 | Distribution Circuit | Vegetation | Tree - fell into line | 2034 | 147983 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0002955 | OH | Sus | 42908763 | 2017 | JAN | Yes | Three Phase Fault | Yes | Yes
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | OTHER | WIRE DOWN @ SW 461 | 20170103 | 1536 | 1615941 | 764 | Distribution Circuit | Equipment Failure/Involved | Overhead | 579 | 235871 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0003151 | OH | Sus | 42909923 | 2017 | JAN | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 5985 | 20170103 | 2141 | 1616979 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 9310 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003318 | OH | Sus | 42909935 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 12122 | 20170103 | 2247 | 1617172 | 1153 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 61170 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003317 | OH | Sus | 31292865 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN SUB | 8284 | OCB | 1101/2 | 20170108 | 650 | 1622844 | 3315 | Distribution Circuit | Vegetation | Tree - fell into line | 2942 | 3680039 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004942 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 8469 | 20170108 | 650 | 1625134 | 4839 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4839 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005147 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12758 | 20170108 | 956 | 1624575 | 1730 | Distribution Circuit | Vegetation | Tree - fell into line | 240 | 195317 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005095 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER | WIRE DOWN 3 SPANS S/SIDE OF 4367 | 20170108 | 811 | 1629928 | 4768 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 16784 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005852 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | JUMPER | WIRE DOWN 1 SPAN SOURCE SIDE 374675 | 20170108 | 10 | 1622372 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 7308 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004890 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE | 3307 | 20170108 | 709 | 1622950 | 444 | Distribution Circuit | Equipment Failure/Involved | Overhead | 617 | 57692 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004994 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | RECLOSER | 10728 | 20170108 | 1205 | 1626008 | 148 | Distribution Circuit | Vegetation | Tree - fell into line | 534 | 78536 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004989 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | JUMPER | OJ @ MTR 1007590761 | 20170108 | 935 | 1627443 | 1530 | Distribution Circuit | Vegetation | Tree - branch fell on line | 137 | 47202 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005411 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | RECLOSER | 10912 | 20170108 | 2249 | 1629739 | 2528 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 86560 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005772 | OH | Sus | 31294181 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 1143 | 20170108 | 940 | 1624286 | 361 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 5054 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005163 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 12525 | 20170108 | 1003 | 1624565 | 7247 | Distribution Circuit | Environmental/External | Flood/Erosion | 64 | 474176 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005274 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 4355 | 20170108 | 1504 | 1627581 | 2485 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 57155 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005600 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | OJ SS OF MTR 1008750940 | 20170108 | 1625 | 1629940 | 3075 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12300 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005828 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER | WIRE DOWN 1 SP SS/OF 839 | 20170108 | 1603 | 1630335 | 2962 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 167071 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005912 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER | WIRE DWN 2 SP LD SIDE OF 11929 | 20170108 | 1600 | 1630333 | 2925 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 90675 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005943 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 6037 | 20170108 | 200 | 1622468 | 870 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 14370 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0004900 | OH | Sus | 31294181 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 11006 | 20170108 | 902 | 1623885 | 2465 | Distribution Circuit | Vegetation | Tree - fell into line | 1634 | 308579 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005068 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 6043 | 20170108 | 1732 | 1628395 | 1588 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 25556 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005622 | OH | Sus | 31294181 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 11919 | 20170108 | 1851 | 1629523 | 1228 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 23332 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005736 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | OTHER | WIRE DOWN 1 SP S/S FUCO 5725 | 20170108 | 635 | 1622784 | 524 | Distribution Circuit | Vegetation | Tree - fell into line | 292 | 78433 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004936 | OH | Sus | 42912765 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE | 10189 | 20170108 | 748 | 1623241 | 372 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 1488 | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005039 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE | 40417 | 20170108 | 1248 | 1626423 | 212 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 636 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005379 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | FUSE | 633 | 20170108 | 1213 | 1626055 | 610 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 13420 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005484 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE | 457 | 20170108 | 1427 | 1628029 | 884 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 16796 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005511 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER | 39126 | 20170108 | 834 | 1623735 | 1721 | Distribution Circuit | Vegetation | Tree - fell into line | 136 | 168352 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005021 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 10139 | 20170108 | 1100 | 1626288 | 1648 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 6592 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005269 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | OTHER | WIRE DOWN 1 SPAN L/S OF METER # 1008412331 | 20170108 | 941 | 1624296 | 1887 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 18523 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005428 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 5409 | 20170108 | 1635 | 1628065 | 1828 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 10968 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005569 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 8033 | 20170108 | 1807 | 1628522 | 2033 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 14231 | Overcast-Rain-32-90 F | Conductor, Overhead | On Ground | 17-0006347 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 7989 | 20170108 | 942 | 1624468 | 4458 | Distribution Circuit | Vegetation | Tree - fell into line | 262 | 726569 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0005192 | OH | Sus | 31294181 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | OTHER | WIRE DOWN 2 SPANS LD S/O MTR#409498 | 20170108 | 1919 | 1628824 | 2888 | Distribution Circuit | Vegetation | Tree - fell into line | 335 | 98368 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005628 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 2705 | 20170108 | 1850 | 1628154 | 1782 | Distribution Circuit | Vegetation | Tree - fell into line | 144 | 255358 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005768 | OH | Sus | 31294181 | 2017 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 11305 | 20170108 | 2027 | 1629067 | 2493 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 32409 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0005774 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE | 6523 | 20170108 | 1508 | 1627637 | 1707 | Distribution Circuit | Equipment Failure/Involved | Overhead | 163 | 54934 | Overcast-Rain-32-90 F | Conductor, Overhead | On Ground | 17-0005642 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 7259 | 20170108 | 1523 | 1628439 | 1481 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 62202 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005644 | OH | Sus | 31293495 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5485 | 20170109 | 1852 | 1632090 | 923 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 30459 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006443 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9773 | 20170109 | 1609 | 1631724 | 1294 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 37526 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006517 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 12125 | 20170109 | 915 | 1630649 | 1845 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5535 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005975 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | SECTIONALIZER | 95394 | 20170109 | 524 | 1630158 | 1935 | Distribution Circuit | Vegetation | Tree - fell into line | 1896 | 163482 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005875 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | OJ LD SIDE OF TX#315371522847 | 20170109 | 1211 | 1631729 | 4651 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 13953 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006226 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 63868 | 20170109 | 901 | 1630615 | 1406 | Distribution Circuit | Environmental/External | Flood/Erosion | 416 | 579980 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005966 | OH | Sus | 31293495 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5043 | 20170109 | 1833 | 1632070 | 1122 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3366 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006272 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 737 | 20170109 | 332 | 1630264 | 2518 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 148562 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005898 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 1861 | 20170109 | 1240 | 1631241 | 460 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 460 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006258 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER | 5028 | 20170110 | 2046 | 1637013 | 985 | Distribution Circuit | Vegetation | Tree - fell into line | 636 | 565128 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0007048 | OH | Sus | 31294181 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12992 | 20170110 | 2047 | 1636280 | 1242 | Distribution Circuit | Vegetation | Tree - fell into line | 687 | 261630 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007046 | OH | Sus | 31294181 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 7301 | 20170110 | 1822 | 1635359 | 1278 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 21726 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007363 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE | 7199 | 20170110 | 1646 | 1634493 | 1485 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7425 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007608 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 6105 | 20170110 | 1731 | 1634710 | 2944 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 11776 | Overcast-Heavy Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0006906 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 33542 | 20170110 | 2325 | 1638064 | 2315 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 57579 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007254 | OH | Sus | 31294181 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 11929 | 20170110 | 1939 | 1638919 | 1301 | Distribution Circuit | Vegetation | Tree - fell into line | 382 | 164745 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007433 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | TRIP-SAVER | 5577 | 20170110 | 1442 | 1633788 | 1300 | Distribution Circuit | Vegetation | Tree - branch fell on line | 98 | 119344 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007445 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5587 | 20170110 | 2355 | 1638151 | 2160 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 17280 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007701 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER | OJ'S AT TAKE OFF POWER TO EOL | 20170110 | 837 | 1632698 | 578 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 578 | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006659 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2106 | 83622106 | FUSE | 1613 | 20170110 | 2105 | 1637179 | 1155 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 60500 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0007266 | OH | Sus | 31294181 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 10619 | 20170110 | 1909 | 1635973 | 2555 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 7665 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007737 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN @ 17230 LAUREL RD | 20170110 | 1933 | 1640082 | 2731 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 140889 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007742 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 6647 | 20170110 | 1956 | 1638665 | 1174 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 24654 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007411 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE | 1491 | 20170110 | 1428 | 1633754 | 982 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 16798 | Overcast-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006711 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 5985 | 20170110 | 1926 | 1636215 | 1194 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 108654 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007302 | OH | Sus | 42912765 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | RECLOSER | 10954 | 20170110 | 1442 | 1633797 | 1708 | Distribution Circuit | Vegetation | Tree - fell into line | 430 | 223903 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006697 | OH | Sus | 31294181 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN JUSTO-1101 | 183181101 | FUSE | 4245 | 20170110 | 1628 | 1634348 | 1077 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 4535 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006910 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 7805 | 20170111 | 233 | 1638504 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1024 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007359 | OH | Sus | 31294181 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 1827 | 20170111 | 1933 | 1640692 | 1182 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 14736 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007937 | OH | Sus | 31294181 | 2017 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | WIRE DOWN 1 LD SIDE OF 5151 | 20170111 | 656 | 1639979 | 2086 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 6258 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007828 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 6593 | 20170111 | 1627 | 1640341 | 1394 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 16728 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007938 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 1939 | 20170111 | 254 | 1638817 | 2081 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12486 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007507 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 11305 | 20170111 | 2357 | 1640886 | 2305 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 15995 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0008264 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE | 6773 | 20170111 | 333 | 1638560 | 625 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 54375 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007431 | OH | Sus | 42912765 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 10621 | 20170118 | 1814 | 1649117 | 1202 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 8414 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010460 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 11179 | 20170118 | 2030 | 1648889 | 1284 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 33384 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010554 | OH | Sus | 31297127 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5995 | 20170118 | 1951 | 1648711 | 989 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 6923 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010486 | OH | Sus | 31297127 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 5819 | 20170118 | 1922 | 1648649 | 1103 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 58322 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010455 | OH | Sus | 31297127 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 55781 | 20170118 | 2047 | 1648948 | 244 | Distribution Circuit | Vegetation | Tree - branch fell on line | 47 | 11468 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010572 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 2371 | 20170118 | 1959 | 1648748 | 899 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 32442 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010494 | OH | Sus | 42928578 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 7567 | 20170118 | 2047 | 1648956 | 1089 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 21780 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010570 | OH | Sus | 31297011 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | JUMPER | WIRE DOWN 1 SP S/SIDE OF 6133 | 20170119 | 1830 | 1651782 | 8395 | Distribution Circuit | Environmental/External | Flood/Erosion | 52 | 16696 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0011077 | OH | Sus | 31297011 | 2017 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 8461 | 20170120 | 805 | 1653163 | 1688 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 13504 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011441 | OH | Sus | 31297127 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 2945 | 20170120 | 1513 | 1654540 | 1287 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 64350 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0011739 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | JUMPER | JUMPERS IFO MTR# 100845729 | 20170120 | 724 | 1652973 | 3450 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7912 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011405 | OH | Sus | 31297127 | 2017 | JAN | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 4169 | 20170120 | 1115 | 1653882 | 1405 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1405 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0011563 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 3603 | 20170120 | 1035 | 1653756 | 1747 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 15723 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011631 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5151 | 20170120 | 941 | 1653546 | 1715 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 10290 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011650 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 5400 | 20170120 | 1531 | 1654594 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 6062 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011668 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER | WIRE DOWN | 20170120 | 1124 | 1653992 | 476 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2380 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011711 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 7681 | 20170120 | 544 | 1652565 | 1830 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 18300 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011627 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | GREEN VALLEY-2101 | 83192101 | JUMPER | WIRE DOWN 2 SP E/O 766683 | 20170120 | 1053 | 1653789 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3386 | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011510 | OH | Sus | 31297127 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | FUSE | 627 | 20170120 | 1319 | 1653046 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 13156 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011575 | OH | Sus | 31297011 | 2017 | JAN | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | FUSE | 8171 | 20170120 | 1407 | 1654407 | 1553 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 3106 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011712 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 5985 | 20170120 | 1315 | 1654294 | 1455 | Distribution Circuit | Equipment Failure/Involved | Overhead | 91 | 15651 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011629 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5995 | 20170120 | 553 | 1652605 | 1984 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 13888 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011558 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6605 | 20170120 | 1855 | 1655040 | 2745 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 19215 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013129 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20170120 | 1507 | 1654535 | 853 | Distribution Circuit | Vegetation | Tree - fell into line | 431 | 75682 | Overcast-Drizzle-32-90 F | Conductor, Overhead | On Ground | 17-0011658 | OH | Sus | 31297127 | 2017 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE | 775 | 20170120 | 1521 | 1654559 | 1849 | Distribution Circuit | Vegetation | Tree - fell into line | 103 | 35761 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011721 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 6975 | 20170120 | 528 | 1652469 | 725 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 36250 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011593 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 9123 | 20170120 | 1219 | 1654154 | 1545 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 21630 | Overcast-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0012016 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 5141 | 20170121 | 2020 | 1657228 | 1061 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 12732 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012315 | OH | Sus | 31297127 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5487 | 20170121 | 1959 | 1657227 | 4016 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 156718 | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012506 | OH | Sus | 42928924 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER | WIRE DOWN @ METER # 1007348651 | 20170121 | 1035 | 1656282 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 1640 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012093 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 12525 | 20170121 | 1644 | 1656979 | 1189 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 14482 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012166 | OH | Sus | 31297127 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | PAUL SWEET-2106 | 83252106 | FUSE | 7749 | 20170121 | 640 | 1655700 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 38296 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011921 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6641 | 20170121 | 912 | 1656099 | 3274 | Distribution Circuit | Vegetation | Tree - fell into line | 266 | 105470 | Overcast-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 17-0011931 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | OCB | 2202/2 | 20170121 | 900 | 1656047 | 278 | Distribution Circuit | 3rd Party | Vehicle | 6011 | 190342 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011934 | OH | Sus | 31297517 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9597 | 20170122 | 1057 | 1660473 | 193 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 965 | Overcast-Drizzle-32-90 F | Conductor, Overhead | On Ground | 17-0013047 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 12887 | 20170122 | 1222 | 1660882 | 1392 | Distribution Circuit | Vegetation | Tree - fell into line | 145 | 76914 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013142 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 11939 | 20170122 | 511 | 1658973 | 790 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 56090 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013194 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 11943 | 20170122 | 533 | 1659036 | 708 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 21471 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013280 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10294 | 20170122 | 317 | 1658375 | 4998 | Distribution Circuit | Environmental/External | Flood/Erosion | 522 | 970726 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 17-0012713 | OH | Sus | 42928924 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 5146 | 20170122 | 511 | 1658985 | 2074 | Distribution Circuit | Vegetation | Tree - fell into line | 178 | 42876 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0012789 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 5020 | 20170122 | 546 | 1659127 | 1765 | Distribution Circuit | Vegetation | Tree - fell into line | 1079 | 87210 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012819 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 10619 | 20170122 | 538 | 1659120 | 1942 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5826 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013302 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 11237 | 20170122 | 1100 | 1660485 | 3015 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12060 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013343 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 335 | 20170122 | 546 | 1659121 | 1904 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3808 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 17-0013656 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | RECLOSER | 2010 | 20170122 | 150 | 1658095 | 2376 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 195633 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012600 | OH | Sus | 31297011 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | RECLOSER | 9640 | 20170122 | 346 | s1251532 | 747 | Distribution Circuit | Vegetation | Tree - branch fell on line | 292 | 41531 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012709 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE | 2181 | 20170122 | 220 | 1660916 | 2155 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 175985 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013124 | OH | Sus | 31297011 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | TRIP-SAVER | 7611 | 20170122 | 248 | 1660992 | 2099 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 15055 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013144 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | FUSE | 40253 | 20170122 | 717 | 1660839 | 1807 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 7228 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013103 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | OTHER | 49899 | 20170122 | 1305 | 1660483 | 1673 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 6692 | Overcast-Drizzle-32-90 F | Connector or Splice (OH) | Broken, wire on object | 17-0013162 | OH | Sus | 31297011 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 8353 | 20170122 | 557 | 1659272 | 1748 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 7052 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013271 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | PAUL SWEET-2109 | 83252109 | RECLOSER | 12946 | 20170122 | 1957 | 1662249 | 853 | Distribution Circuit | Vegetation | Tree - fell into line | 212 | 172388 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on object | 17-0013395 | OH | Sus | 31297127 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | JUMPER | WIRE DOWN 3S/E/O 5411 | 20170122 | 204 | 1658252 | 609 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 10353 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012721 | OH | Sus | 31297127 | 2017 | JAN | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | OTHER | WIRE DOWN 843 CALABASAS | 20170122 | 626 | 1659254 | 2069 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 41425 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012952 | OH | Sus | 31297427 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 5819 | 20170122 | 732 | 1660089 | 1693 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 93087 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013074 | OH | Sus | 42928924 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 11835 | 20170122 | 1935 | 1662215 | 1865 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 26655 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013543 | OH | Sus | 31297127 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 1489 | 20170122 | 554 | 1659143 | 429 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4719 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012824 | OH | Sus | 42928578 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 6071 | 20170122 | 657 | 1659369 | 256 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 4864 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 17-0013005 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 6809 | 20170122 | 325 | 1658396 | 1805 | Distribution Circuit | Vegetation | Tree - branch fell on line | 180 | 148122 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0013085 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 2309 | 20170122 | 654 | 1659355 | 1711 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 32509 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0013721 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 8559 | 20170122 | 343 | 1660358 | 978 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 10758 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013021 | OH | Sus | 42928578 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | WIRE DWN @ 487 ON MAINLINE | 20170123 | 1011 | 1663596 | 1866 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 77148 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013809 | OH | Sus | 31297127 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8241 | 20170123 | 1108 | 1663734 | 202 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 1616 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0013748 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 5020 | 20170123 | 2215 | 1665069 | 1019 | Distribution Circuit | Environmental/External | Flood/Erosion | 1009 | 151850 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0014213 | OH | Sus | 31297127 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LOS OSITOS-2103 | 182082103 | FUSE | 7697 | 20170123 | 751 | 1663095 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 8050 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0013627 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5539 | 20170123 | 930 | 1663437 | 1720 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 3440 | Clear-32-90 F | Footings, Tower or Pole | Broken, wire on object | 17-0013857 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 125 | 20170123 | 1109 | 1663741 | 3156 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 80508 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013798 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 7537 | 20170123 | 302 | 1662909 | 583 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3010 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013596 | OH | Sus | 42928578 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5501 | 20170207 | 830 | 1678971 | 1827 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 92872 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018659 | OH | Sus | 42939797 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 5335 | 20170207 | 107 | 1677325 | 778 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 57572 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018045 | OH | Sus | 31304293 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 33542 | 20170207 | 747 | 1678755 | 1646 | Distribution Circuit | Vegetation | Tree - fell into line | 522 | 194099 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018264 | OH | Sus | 31304215 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | B1101 | 20170207 | 1123 | 1679930 | 4520 | Distribution Circuit | Environmental/External | Flood/Erosion | 289 | 192265 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018500 | OH | Sus | 31304215 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5151 | 20170207 | 1639 | 1680684 | 1410 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8460 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018693 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 6161 | 20170207 | 730 | 1679363 | 2071 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 41420 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0018748 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 11929 | 20170207 | 1128 | 1680927 | 1657 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 128686 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018812 | OH | Sus | 31304215 | 2017 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5901 | 20170207 | 130 | 1677332 | 1569 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 26673 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018325 | OH | Sus | 42939797 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7593 | 20170207 | 756 | 1679056 | 6047 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 57290 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018388 | OH | Sus | 31304215 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | JUMPER | OJ 1 LD SIDE OF 10705 | 20170207 | 1205 | 1680125 | 1662 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3324 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018633 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | JUMPER | WIRE DOWN LD SID EOF 7521 | 20170207 | 849 | 1680627 | 1811 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1811 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018675 | OH | Sus | 31304264 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | PAUL SWEET-2106 | 83252106 | FUSE | 7749 | 20170207 | 135 | 1677342 | 757 | Distribution Circuit | Environmental/External | Flood/Erosion | 102 | 52137 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018054 | OH | Sus | 42939835 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 10073 | 20170207 | 452 | 1677830 | 2748 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 10992 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018120 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 8353 | 20170207 | 1043 | 1680242 | 1497 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 13473 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018699 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5995 | 20170207 | 1001 | 1679617 | 3185 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 22295 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018795 | OH | Sus | 31304215 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 5819 | 20170207 | 104 | 1678178 | 2380 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 140420 | Overcast-Rain-32-90 F | Conductor, Overhead | On Ground | 17-0018273 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 3029 | 20170207 | 901 | 1679387 | 1849 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 83205 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | On Ground | 17-0018528 | OH | Sus | 42939797 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6647 | 20170207 | 1428 | 1680508 | 3073 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 64533 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018743 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | OTHER | WIRE DOWN TWD MTR 1006211444 | 20170207 | 2134 | 1681093 | 1162 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 16565 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018823 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 5781 | 20170207 | 1735 | 1680782 | 2450 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 24500 | Overcast-Drizzle-32-90 F | Conductor, Overhead | On Ground | 17-0018915 | OH | Sus | 42939797 | 2017 | FEB | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6651 | 20170207 | 345 | 1682634 | 3613 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 18065 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019368 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 487 | 20170209 | 2123 | 1684190 | 2263 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 77561 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019711 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8501 | 20170209 | 1557 | 1683829 | 1343 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 26860 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 17-0019614 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | OTHER | WIRE DOWN LD SIDE METER # 1008728481 | 20170209 | 1433 | 1683708 | 1580 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 12640 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019521 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5587 | 20170209 | 2316 | 1684351 | 1116 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8928 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019736 | OH | Sus | 42939797 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7351 | 20170209 | 1351 | 1684110 | 1539 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3078 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 17-0019626 | OH | Sus | 31304215 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2705 | 20170209 | 1243 | 1683403 | 1457 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 6410 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0019497 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 11739 | 20170209 | 824 | 1682868 | 1869 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 13083 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0019333 | OH | Sus | 31304215 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6647 | 20170209 | 1953 | 1684134 | 4087 | Distribution Circuit | Environmental/External | Flood/Erosion | 21 | 60427 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019710 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2105 | 83692105 | RECLOSER | 71630 | 20170209 | 1751 | 1684021 | 41 | Distribution Circuit | Vegetation | Tree - fell into line | 582 | 20334 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019491 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 5166 | 20170209 | 1957 | 1684137 | 1361 | Distribution Circuit | Vegetation | Tree - fell into line | 262 | 356582 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019632 | OH | Sus | 31304215 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20170209 | 2345 | 1684103 | 1067 | Distribution Circuit | Vegetation | Tree - fell into line | 393 | 133534 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019718 | OH | Sus | 42939797 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 1301 | 20170209 | 2345 | 1684396 | 655 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1965 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019731 | OH | Sus | 31304215 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5435 | 20170217 | 959 | 1693717 | 3159 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 22113 | Partly Cloudy-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022158 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER | WIRE DOWN 5 SP LD SD 4533 | 20170217 | 1556 | 1697014 | 1540 | Distribution Circuit | Equipment Failure/Involved | Overhead | 270 | 38337 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022552 | OH | Sus | 31306421 | 2017 | FEB | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 11967 | 20170217 | 1108 | 1694745 | 3135 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 97185 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023434 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | SECTIONALIZER | 12013 | 20170217 | 955 | 1694253 | 815 | Distribution Circuit | Vegetation | Tree - fell into line | 1368 | 1114746 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022411 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | OTHER | WIRE DOWN @ MTR#1008453916 | 20170217 | 1319 | 1698177 | 5865 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 17251 | Heavy Rain-Strong Winds-Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022601 | OH | Sus | 0 | 2017 | FEB | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | TRANSFORMER | 315479222480 | 20170217 | 1656 | 1697533 | 8145 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 8145 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022713 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 11010 | 20170217 | 848 | 1692567 | 4449 | Distribution Circuit | Vegetation | Tree - branch fell on line | 169 | 220685 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022832 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 10718 | 20170217 | 717 | 1691347 | 6542 | Distribution Circuit | Vegetation | Tree - fell into line | 745 | 156896 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021846 | OH | Sus | 42949498 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 3753 | 20170217 | 1711 | 1697612 | 7089 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 19017 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022966 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2104 | 182222104 | RECLOSER | 2624 | 20170217 | 500 | 1690890 | 9340 | Distribution Circuit | Vegetation | Tree - fell into line | 3187 | 5555655 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021790 | OH | Sus | 31306180 | 2017 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE | 8937 | 20170217 | 1836 | 1699433 | 1171 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 57379 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023064 | OH | Sus | 31306180 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE | 8245 | 20170217 | 804 | 1701693 | 3647 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 51902 | Heavy Rain-Strong Winds-Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 17-0023467 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 2943 | 20170217 | 631 | 1699372 | 4802 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 196882 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0023154 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1112 | 182371112 | FUSE | 435 | 20170217 | 552 | 1691210 | 1653 | Distribution Circuit | Vegetation | Tree - fell into line | 104 | 171912 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022220 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1112 | 182371112 | FUSE | 7091 | 20170217 | 527 | 1692398 | 4754 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 57048 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022660 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1112 | 182371112 | FUSE | 6703 | 20170217 | 529 | 1691021 | 6099 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 36594 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023841 | OH | Sus | 42949491 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE | 2181 | 20170217 | 823 | 1696697 | 4788 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 309033 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022386 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | FUSE | 633 | 20170217 | 1548 | 1698474 | 2836 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 62392 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022705 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2002 | 20170217 | 649 | 1691384 | 2004 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 248406 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021827 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | SWITCH | 467 | 20170217 | 716 | 1691491 | 1924 | Distribution Circuit | Vegetation | Tree - fell into line | 364 | 684593 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021997 | OH | Sus | 31306180 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2102 | 83252102 | FUSE | 11105 | 20170217 | 1306 | 1695836 | 5844 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 35064 | Overcast-Rain-32-90 F | Conductor, Overhead | On Ground | 17-0023155 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | PAUL SWEET-2109 | 83252109 | FUSE | 6137 | 20170217 | 750 | 1691606 | 3621 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 155703 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0021973 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | OTHER | WIRE DOWN BETWEEN 5413 & 823 | 20170217 | 501 | 1691237 | 1896 | Distribution Circuit | Vegetation | Tree - fell into line | 296 | 149623 |  | Conductor, Overhead | On Ground | 17-0021809 | OH | Sus | 31306188 | 2017 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8511 | 20170217 | 1231 | 1695769 | 3506 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 49084 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022263 | OH | Sus | 31306188 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 9827 | 20170217 | 1330 | 1696022 | 4272 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 136704 | Strong Winds-Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022361 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 7371 | 20170217 | 1633 | 1697398 | 102 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 510 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022567 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | RESERVATION ROAD-1101 | 182731101 | RECLOSER | 3026 | 20170217 | 505 | 1690928 | 9195 | Distribution Circuit | Vegetation | Tree - fell into line | 706 | 2064974 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021789 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 3889 | 20170217 | 843 | 1692466 | 5929 | Distribution Circuit | Vegetation | Tree - bark fell into line | 70 | 25157 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022014 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | RECLOSER | 10954 | 20170217 | 2147 | 1698528 | 1347 | Distribution Circuit | Vegetation | Tree - fell into line | 430 | 392418 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022724 | OH | Sus | 31306188 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 2199 | 20170217 | 825 | 1698735 | 4665 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 139950 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022903 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6647 | 20170217 | 901 | 1703506 | 5084 | Distribution Circuit | Environmental/External | Flood/Erosion | 8 | 40672 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023847 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 11305 | 20170217 | 901 | 1706770 | 5914 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 76882 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024741 | OH | Sus | 0 | 2017 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2105 | 83692105 | FUSE | 8595 | 20170217 | 824 | 1692151 | 3174 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 136482 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0023363 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 6121 | 20170217 | 828 | 1694719 | 3043 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 331687 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023367 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE | 6773 | 20170217 | 1837 | 1698283 | 2659 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 231333 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023299 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN JUSTO-1101 | 183181101 | FUSE | 4245 | 20170217 | 938 | 1693433 | 4621 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 90909 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022126 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN JUSTO-1101 | 183181101 | FUSE | 4097 | 20170217 | 606 | 1701681 | 4834 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 19336 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023463 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 10717 | 20170218 | 1009 | 1699415 | 5988 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 50478 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023008 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 11935 | 20170218 | 1613 | 1694376 | 1653 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 8265 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023150 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 2235 | 20170218 | 341 | 1698824 | 4932 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 83040 | Heavy Rain-Strong Winds-Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023082 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HOLLISTER-2106 | 182492106 | JUMPER | 50689 | 20170218 | 1853 | 1699622 | 2715 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 46155 | Heavy Rain-Strong Winds-Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023210 | OH | Sus | 0 | 2017 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1112 | 182371112 | FUSE | 6899 | 20170218 | 1421 | 1700097 | 1248 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 12587 | Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023212 | OH | Sus | 42949491 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | FUSE | 7791 | 20170218 | 1644 | 1701282 | 1492 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 20792 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023391 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 2155 | 20170218 | 536 | 1698931 | 6401 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 25604 | Strong Winds-Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025083 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 7567 | 20170218 | 620 | 1698967 | 720 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 13808 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022988 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER | 16010 | 20170220 | 1706 | 1704473 | 2784 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 343328 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023956 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | SECTIONALIZER | 8655 | 20170220 | 1738 | 1704199 | 2788 | Distribution Circuit | Vegetation | Tree - fell into line | 178 | 262858 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023976 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9725 | 20170220 | 1732 | 1704944 | 2812 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 41414 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024742 | OH | Sus | 42949498 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 12069 | 20170220 | 1730 | 1704907 | 1581 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 52173 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0025020 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8365 | 20170220 | 930 | 1703085 | 3162 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 91698 | Overcast-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0023764 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 9181 | 20170220 | 1651 | 1705811 | 3915 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 58725 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024995 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | TRIP-SAVER | 6219 | 20170220 | 1636 | 1704194 | 4137 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 91014 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025057 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 11995 | 20170220 | 1721 | 1704700 | 4164 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 33312 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0025275 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 7299 | 20170220 | 602 | 1702505 | 603 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 7236 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023669 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 4567 | 20170220 | 1622 | 1704031 | 2808 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 16848 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024753 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 4295 | 20170220 | 1658 | 1704416 | 3004 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 75100 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0025235 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20170220 | 1458 | 1703624 | 4146 | Distribution Circuit | Environmental/External | Flood/Erosion | 525 | 514596 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023913 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | RECLOSER | 5096 | 20170220 | 1637 | 1704223 | 2476 | Distribution Circuit | Vegetation | Tree - fell into line | 340 | 318650 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023930 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5155 | 20170220 | 1450 | 1703589 | 1665 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 123210 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023885 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10912 | 20170220 | 1607 | 1703838 | 2903 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 84526 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023910 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 8929 | 20170220 | 1603 | 1703886 | 2725 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 155325 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0023971 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5173 | 20170220 | 1550 | 1703807 | 3310 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 18440 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024011 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2105 | 83622105 | FUSE | 2943 | 20170220 | 1526 | 1704440 | 1599 | Distribution Circuit | Vegetation | Tree - fell into line | 193 | 118579 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024020 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5185 | 20170220 | 1831 | 1705173 | 2709 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 56889 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024059 | OH | Sus | 42949498 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5183 | 20170220 | 1631 | 1705165 | 2837 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 139013 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024073 | OH | Sus | 31306188 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | SECTIONALIZER | 10231 | 20170220 | 1651 | 1704367 | 1414 | Distribution Circuit | Equipment Failure/Involved | Overhead | 368 | 293972 | Overcast-Heavy Rain-Strong Winds-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0024404 | OH | Sus | 42949498 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 11929 | 20170220 | 1515 | 1707553 | 3113 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 305074 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024891 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5609 | 20170220 | 1515 | 1707556 | 3986 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 25557 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024894 | OH | Sus | 42949498 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2105 | 83622105 | FUSE | 5233 | 20170220 | 1716 | 1704611 | 2739 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 65736 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024935 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5443 | 20170220 | 1804 | 1705171 | 2951 | Distribution Circuit | Environmental/External | Flood/Erosion | 6 | 17706 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025037 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 10718 | 20170220 | 1621 | 1704077 | 3174 | Distribution Circuit | Vegetation | Tree - fell into line | 486 | 783560 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0023922 | OH | Sus | 42949498 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 12895 | 20170220 | 2044 | 1706188 | 2716 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 13312 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025224 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 6033 | 20170220 | 2020 | 1707804 | 2489 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 199120 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025282 | OH | Sus | 0 | 2017 | FEB | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 8555 | 20170220 | 1545 | 1703785 | 3021 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12084 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025754 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2104 | 182222104 | OTHER | WIRE DWN @ 9213 | 20170220 | 1725 | 1704787 | 2901 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 54295 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024683 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2705 | 20170220 | 1319 | 1703355 | 115 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 2875 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023864 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2667 | 20170220 | 1826 | 1705272 | 1613 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 9678 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025065 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 6483 | 20170220 | 1844 | 1705338 | 2589 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 28479 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025079 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE | 40419 | 20170220 | 1116 | 1703538 | 2012 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 74444 | Partly Cloudy-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0023852 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE | 8245 | 20170220 | 1115 | 1703542 | 2013 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 38247 | Partly Cloudy-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 17-0023853 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | OCB | 2654 | 20170220 | 1748 | 1705142 | 1620 | Distribution Circuit | Vegetation | Tree - fell into line | 2752 | 2776086 | Overcast-Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0024003 | OH | Sus | 31306180 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | RECLOSER | 2020 | 20170220 | 1900 | 1705434 | 1843 | Distribution Circuit | Vegetation | Tree - bark fell into line | 638 | 780630 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0024074 | OH | Sus | 31306180 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1112 | 182371112 | FUSE | 407 | 20170220 | 1524 | 1703915 | 1259 | Distribution Circuit | Vegetation | Tree - branch fell on line | 170 | 214030 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023933 | OH | Sus | 42949491 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1112 | 182371112 | FUSE | 6891 | 20170220 | 1740 | 1705093 | 1334 | Distribution Circuit | Equipment Failure/Involved | Overhead | 133 | 177422 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024044 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | OCB | 1101/2 | 20170220 | 1237 | 1703213 | 6129 | Distribution Circuit | Equipment Failure/Involved | Overhead | 191 | 375767 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023801 | OH | Sus | 0 | 2017 | FEB | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | FUSE | 8081 | 20170220 | 1953 | 1705762 | 5447 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 141622 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0025671 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2166 | 20170220 | 728 | 1703510 | 4938 | Distribution Circuit | Vegetation | Tree - fell into line | 423 | 2085732 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023848 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2102 | 83252102 | FUSE | 11103 | 20170220 | 2320 | 1706735 | 1251 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 40032 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024820 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | JUMPER | OJ'S 4 SPANS LOAD-SIDE OF 5411 | 20170220 | 1320 | 1703353 | 118 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 118 | Strong Winds-Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023819 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 12122 | 20170220 | 1523 | 1703714 | 3180 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 248040 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023886 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 5078 | 20170220 | 1620 | 1704033 | 4109 | Distribution Circuit | Vegetation | Tree - fell into line | 296 | 444914 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024598 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 2751 | 20170220 | 1928 | 1705546 | 1308 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 24852 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024949 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 9975 | 20170220 | 1800 | 1705140 | 4280 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 9698 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025305 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 5166 | 20170220 | 1243 | 1703277 | 2350 | Distribution Circuit | Vegetation | Tree - fell into line | 269 | 631989 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0023808 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 11327 | 20170220 | 2019 | 1708286 | 4106 | Distribution Circuit | Environmental/External | Flood/Erosion | 1 | 4106 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0025405 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE | 6773 | 20170220 | 506 | 1702455 | 679 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 7215 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023664 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE | 6773 | 20170220 | 713 | 1702729 | 776 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 8301 | Strong Winds-Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023693 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | RECLOSER | 88772 | 20170220 | 2045 | 1705987 | 1412 | Distribution Circuit | Environmental/External | Flood/Erosion | 1237 | 428435 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024104 | OH | Sus | 42949498 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | SAN JUSTO-1101 | 183181101 | JUMPER | WIRE DWN 4 S/OF 4091 | 20170220 | 836 | 1703223 | 1677 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 57018 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023796 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | RECLOSER | 9698 | 20170220 | 1429 | 1703515 | 2925 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 65946 | Overcast-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0023850 | OH | Sus | 31306180 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | SECTIONALIZER | 40017 | 20170220 | 1719 | 1704739 | 2973 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 115808 | Overcast-Drizzle-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0023965 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 8021 | 20170220 | 1615 | 1703988 | 2895 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 168930 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024025 | OH | Sus | 31306180 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | OCB | 2202/2 | 20170220 | 1905 | 1705431 | 492 | Distribution Circuit | Vegetation | Tree - fell into line | 2283 | 1090928 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024037 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 9127 | 20170220 | 1949 | 1705735 | 3160 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 37920 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025423 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 1445 | 20170220 | 1808 | 1705198 | 2947 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 29470 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024024 | OH | Sus | 31306180 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 10421 | 20170220 | 2023 | 1708955 | 3127 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 34165 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0025453 | OH | Sus | 31306180 | 2017 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 55781 | 20170220 | 1915 | 1706204 | 2561 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 120367 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024868 | OH | Sus | 31306180 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | JUMPER | OJ ON HARD TAP FEEDING MTR1008554001 | 20170220 | 1607 | 1710290 | 3106 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3106 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0025477 | OH | Sus | 42949491 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | OTHER | WIRE DOWN S/S OF 9559 | 20170220 | 1607 | 1710298 | 2978 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3942 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025481 | OH | Sus | 42949491 | 2017 | FEB | Yes | Line to Line | Yes | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 6295 | 20170221 | 325 | 1709172 | 2387 | Distribution Circuit | Vegetation | Tree - branch fell on line | 115 | 75425 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0025257 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5487 | 20170221 | 28 | 1707470 | 765 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 42840 | Heavy Rain-Strong Winds-32-90 F | Insulator | Broken, wire on object | 17-0025105 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 2323 | 20170221 | 1240 | 1704677 | 3053 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4141 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025377 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 5329 | 20170221 | 744 | 1704296 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 27720 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024911 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 3979 | 20170221 | 1936 | 1709418 | 1193 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 25053 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025313 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | WIRE DOWN 2 SP E/OF 7199 | 20170221 | 737 | 1709006 | 3473 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 14867 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025221 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9247 | 20170221 | 323 | 1709254 | 2257 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 41975 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025274 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9259 | 20170221 | 319 | 1709351 | 3731 | Distribution Circuit | Vegetation | Tree - fell into line | 412 | 1345108 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025283 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER | WIRE DOWN 1 SP LD SIDE OF MTR#1008739291 | 20170221 | 319 | 1710608 | 3336 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 32764 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025570 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2106 | 83622106 | RECLOSER | 12760 | 20170221 | 1256 | 1708585 | 1837 | Distribution Circuit | Vegetation | Tree - fell into line | 546 | 156387 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025114 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE | 54071 | 20170221 | 245 | 1704578 | 2293 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2293 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024835 | OH | Sus | 31306180 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 7807 | 20170221 | 29 | 1706890 | 3602 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 61234 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025137 | OH | Sus | 31306188 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 8643 | 20170221 | 1652 | 1709104 | 1464 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 19032 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025243 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | TRIP-SAVER | 6421 | 20170221 | 1657 | 1709110 | 1077 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 32310 | Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025248 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2104 | 83252104 | SWITCH | 1867 | 20170221 | 1617 | 1708985 | 1406 | Distribution Circuit | Vegetation | Tree - branch fell on line | 142 | 199652 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025218 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5043 | 20170221 | 930 | 1711917 | 3345 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10035 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025965 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 4431 | 20170221 | 1140 | 1707685 | 1907 | Distribution Circuit | Environmental/External | Flood/Erosion | 109 | 207863 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025073 | OH | Sus | 0 | 2017 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 2 | SAN JUSTO-1101 | 183181101 | SWITCH | 9975 | 20170221 | 1628 | 1708878 | 1478 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 32516 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025238 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | JUMPER | WIRE DOWN 1 SPAN LD SIDE OF 2143 | 20170221 | 1121 | 1708345 | 1818 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5454 | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 17-0025061 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5151 | 20170222 | 828 | 1710127 | 598 | Distribution Circuit | Environmental/External | Flood/Erosion | 6 | 3588 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025446 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 4731 | 20170222 | 1536 | 1710998 | 204 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 816 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025704 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 11929 | 20170222 | 2308 | 1711488 | 1002 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 98196 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025876 | OH | Sus | 42949498 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8361 | 20170222 | 1148 | 1710593 | 581 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7553 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025575 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | JUMPER | OJ @ MTR#1008725926 | 20170222 | 1638 | 1711090 | 1377 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 13770 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025936 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 4243 | 20170222 | 1801 | 1711260 | 1388 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 12492 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025769 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 7563 | 20170222 | 1543 | 1711006 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 332 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025710 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 11062 | 20170407 | 447 | 1749433 | 1980 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 50340 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037586 | OH | Sus | 42984110 | 2017 | APR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20170407 | 303 | 1749043 | 711 | Distribution Circuit | Vegetation | Tree - branch fell on line | 326 | 79963 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037547 | OH | Sus | 42984110 | 2017 | APR | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 6161 | 20170407 | 1538 | 1751184 | 1425 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 28500 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0038071 | OH | Sus | 31316813 | 2017 | APR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 6045 | 20170407 | 1604 | 1751262 | 1636 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 93252 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038119 | OH | Sus | 42984110 | 2017 | APR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE | 2811 | 20170407 | 223 | 1747995 | 677 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 12186 | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037521 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE | 1491 | 20170407 | 49 | 1749516 | 838 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 34358 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 17-0037604 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | OTHER | WIRE DOWN 1 SS/OF R813 | 20170407 | 628 | 1750338 | 546 | Distribution Circuit | Vegetation | Tree - branch fell on line | 198 | 59160 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037796 | OH | Sus | 42984159 | 2017 | APR | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | FELTON-0401 | 83140401 | OTHER | WIRE DOWN LD SD FCO 121 | 20170618 | 1315 | 1807762 | 685 | Distribution Circuit | Vegetation | Tree - fell into line | 1915 | 180924 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0056107 | OH | Sus | 0 | 2017 | JUN | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 9005 | 20170903 | 735 | 1867841 | 1091 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 24002 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0075541 | OH | Sus | 0 | 2017 | SEP | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 1301 | 20170903 | 2113 | 1869254 | 1098 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 3294 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0075732 | OH | Sus | 31348848 | 2017 | SEP | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | GABILAN-1101 | 182331101 | JUMPER | WIRE DOWN 1 SS OF 25027 | 20170911 | 1751 | 1875982 | 436 | Distribution Circuit | Environmental/External | Lightning | 36 | 13596 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0077860 | OH | Sus | 0 | 2017 | SEP | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | OTHER | WIRE DOWN @ MTR 100926211 | 20170911 | 626 | 1875124 | 404 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 19830 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0077544 | OH | Sus | 0 | 2017 | SEP | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | TRIP-SAVER | 6577 | 20171008 | 2151 | 1893977 | 559 | Distribution Circuit | Equipment Failure/Involved | Overhead | 48 | 26832 | Clear-32-90 F | Insulator | Broken, wire on object | 17-0085312 | OH | Sus | 43169679 | 2017 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7593 | 20171009 | 131 | 1894906 | 984 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 50249 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085482 | OH | Sus | 31355742 | 2017 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER | WIRE DOWN MTR 1007590728 | 20171020 | 715 | 1905815 | 433 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 9010 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0089038 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8501 | 20171020 | 412 | 1906576 | 2175 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 43500 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0089318 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | FELTON-0401 | 83140401 | JUMPER | WIRE DOWN @ 519075 | 20171020 | 313 | 1905181 | 408 | Distribution Circuit | Vegetation | Tree - fell into line | 1912 | 52596 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0088877 | OH | Sus | 43198596 | 2017 | OCT | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | RECLOSER | 88772 | 20171020 | 440 | 1905242 | 339 | Distribution Circuit | 3rd Party | Vehicle | 135 | 37765 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0088903 | OH | Sus | 31361694 | 2017 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER | 5028 | 20171204 | 1352 | 1935401 | 494 | Distribution Circuit | Vegetation | Tree - fell into line | 2200 | 442980 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099694 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 96986 | 20171204 | 1359 | 1935552 | 1604 | Distribution Circuit | Vegetation | Tree - fell into line | 750 | 355891 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0099716 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2161 | 20171204 | 1444 | 1935590 | 664 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2656 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099755 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 5415 | 20171204 | 1927 | 1936047 | 463 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 28243 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0099837 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12758 | 20171216 | 1225 | 1944818 | 1396 | Distribution Circuit | Vegetation | Tree - fell into line | 295 | 28283 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102088 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 6161 | 20171216 | 919 | 1944344 | 683 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 14343 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102009 | OH | Sus | 1370082 | 2017 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 12518 | 20171216 | 935 | 1944224 | 1352 | Distribution Circuit | Vegetation | Tree - fell into line | 527 | 38602 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0101957 | OH | Sus | 31370082 | 2017 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 11737 | 20171216 | 931 | 1944249 | 570 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 6946 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102065 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 9125 | 20180316 | 1202 | 45737 | 334 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 8196 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023410 | OH | Sus | 43302840 | 2018 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2705 | 20180316 | 629 | 45299 | 249 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 3924 | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023295 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 7989 | 20180316 | 205 | 45189 | 678 | Distribution Circuit | Vegetation | Tree - branch fell on line | 263 | 73608 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023231 | OH | Sus | 43301937 | 2018 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 6625 | 20180728 | 108 | 142200 | 688 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 19264 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0064531 | OH | Sus | 43422806 | 2018 | JUL | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 4355 | 20181108 | 1202 | 211662 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 10810 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0098292 | OH | Sus | 43534781 | 2018 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 2949 | 20181108 | 1239 | 211702 | 89 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 848 | 51106 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0098270 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 10717 | 20181121 | 1051 | 219955 | 634 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 16484 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0101851 | OH | Sus | 43584947 | 2018 | NOV | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 5977 | 20181121 | 1541 | 220657 | 570 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 5700 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102192 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 5076 | 20181121 | 1505 | 220593 | 4167 | Distribution Circuit | Equipment Failure/Involved | Overhead | 123 | 216927 | Overcast-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0101966 | OH | Sus | 31416550 | 2018 | NOV | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9723 | 20181129 | 753 | 228017 | 2045 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 22495 | Overcast-Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0104854 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8015 | 20181129 | 754 | 228179 | 1646 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 106771 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105021 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 66253 | 20181129 | 959 | 228569 | 1815 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 21780 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105322 | OH | Sus | 43586641 | 2018 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 6053 | 20181129 | 659 | 227935 | 1626 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 85596 | Strong Winds-Heavy Rain-Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104884 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5587 | 20181129 | 1031 | 228670 | 429 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3432 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105107 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | FELTON-0401 | 83140401 | FUSE | 5215 | 20181129 | 819 | 228367 | 1711 | Distribution Circuit | Equipment Failure/Involved | Overhead | 60 | 102660 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105156 | OH | Sus | 43586641 | 2018 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | FELTON-0401 | 83140401 | FUSE | 7309 | 20181129 | 1512 | 229261 | 1268 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 20288 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105440 | OH | Sus | 43586641 | 2018 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 63868 | 20181129 | 48 | 227377 | 1118 | Distribution Circuit | Vegetation | Tree - fell into line | 417 | 462449 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104665 | OH | Sus | 31416754 | 2018 | NOV | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2105 | 83252105 | FUSE | 5559 | 20181129 | 854 | 228337 | 2268 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 49896 | Overcast-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0105146 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | RECLOSER | 5178 | 20181129 | 740 | 227969 | 1778 | Distribution Circuit | Vegetation | Tree - fell into line | 267 | 117726 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104810 | OH | Sus | 31416754 | 2018 | NOV | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | TRIP-SAVER | 6577 | 20181129 | 1026 | 228660 | 1759 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 84432 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105091 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | JUMPER | FUCO 27429 | 20181129 | 1213 | 228898 | 1555 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1555 | Partly Cloudy-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105438 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 3459 | 20181129 | 210 | 227530 | 2695 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 63343 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105138 | OH | Sus | 31416754 | 2018 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 9421 | 20190106 | 1336 | 255338 | 1181 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 35430 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005120 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5443 | 20190106 | 1133 | 255153 | 396 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2772 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005074 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER | 5028 | 20190106 | 1507 | 255478 | 1258 | Distribution Circuit | Vegetation | Tree - fell into line | 638 | 46169 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005117 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 3005 | 20190106 | 1806 | 257734 | 1202 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3606 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0005408 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER | WIRE DOWN. | 20190106 | 1839 | 258408 | 1241 | Distribution Circuit | Vegetation | Tree - fell into line | 473 | 200329 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005550 | OH | Sus | 31420594 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | TRANSFORMER | 315133224442 | 20190106 | 2239 | 258320 | 1077 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1077 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005780 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | SECTIONALIZER | 12013 | 20190106 | 1818 | 256412 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 2129 | 376381 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005332 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 8315 | 20190106 | 1418 | 255311 | 1323 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 33075 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005092 | OH | Sus | 0 | 2019 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 10457 | 20190106 | 1353 | 255363 | 1262 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 20192 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005150 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | TRIP-SAVER | 5577 | 20190106 | 1808 | 256225 | 1181 | Distribution Circuit | Equipment Failure/Involved | Overhead | 97 | 101519 | Overcast-Heavy Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0005652 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | FELTON-0401 | 83140401 | OCB | 401/2 | 20190106 | 1917 | 258251 | 1003 | Distribution Circuit | Vegetation | Tree - branch fell on line | 912 | 632115 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005486 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | HATTON-1101 | 182291101 | FUSE | 9302 | 20190106 | 2124 | 258155 | 1208 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 118384 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005554 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2104 | 83252104 | OTHER | WIRE DOWN ON MAINLINE 2 SPANS S/SIDE 857 TAP | 20190106 | 1713 | 255929 | 425 | Distribution Circuit | Vegetation | Tree - fell into line | 295 | 58445 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005263 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | PAUL SWEET-2105 | 83252105 | FUSE | 12119 | 20190106 | 1743 | 256015 | 1202 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4808 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005466 | OH | Sus | 0 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 711 | 20190106 | 1735 | 255942 | 1123 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 23583 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005357 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER | 39126 | 20190106 | 1906 | 256877 | 1223 | Distribution Circuit | Vegetation | Tree - branch fell on line | 136 | 143283 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005378 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 6465 | 20190106 | 1830 | 256499 | 2370 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2370 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005932 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | TRIP-SAVER | 6577 | 20190106 | 1736 | 255948 | 2696 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 133985 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005454 | OH | Sus | 31420894 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 1003 | 20190106 | 1726 | 255878 | 1457 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 85963 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005797 | OH | Sus | 0 | 2019 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 5166 | 20190106 | 1944 | 257358 | 1633 | Distribution Circuit | Equipment Failure/Involved | Overhead | 269 | 262292 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0005363 | OH | Sus | 31420586 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE | 6523 | 20190106 | 2038 | 258732 | 1422 | Distribution Circuit | Vegetation | Tree - fell into line | 163 | 72469 | Overcast-32-90 F | Conductor, Overhead | On Ground | 19-0005661 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | SECTIONALIZER | 40017 | 20190106 | 1814 | 256397 | 1422 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 55681 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005268 | OH | Sus | 0 | 2019 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | JUMPER | WIRE DOWN SOURCE SIDE OF 7625 | 20190106 | 1658 | 255732 | 1448 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1448 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005269 | OH | Sus | 0 | 2019 | JAN | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 495039 | 20190106 | 1657 | 255730 | 2988 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 42633 | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0005401 | OH | Sus | 31420586 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 5131 | 20190116 | 1844 | 269526 | 1334 | Distribution Circuit | Equipment Failure/Involved | Overhead | 112 | 143805 | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010150 | OH | Sus | 31422113 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER | 5144 | 20190116 | 2104 | 270974 | 1195 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 25015 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010253 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 9125 | 20190116 | 1830 | 274100 | 3274 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 65580 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011197 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5443 | 20190116 | 1743 | 271848 | 1127 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 7889 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | On Ground | 19-0010389 | OH | Sus | 0 | 2019 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5501 | 20190116 | 49 | 266427 | 688 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 67211 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009363 | OH | Sus | 31422113 | 2019 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 12383 | 20190116 | 1410 | 267804 | 4130 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 167220 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009903 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8259 | 20190116 | 1518 | 272507 | 2684 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 48312 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010576 | OH | Sus | 43634211 | 2019 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 5511 | 20190116 | 1822 | 272725 | 3034 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 127428 | Overcast-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0010606 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 7949 | 20190116 | 1609 | 267716 | 2762 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 49716 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010978 | OH | Sus | 0 | 2019 | JAN | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 7289 | 20190116 | 1809 | 267626 | 3989 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 26518 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011376 | OH | Sus | 43634211 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20190116 | 1925 | 272969 | 1414 | Distribution Circuit | Vegetation | Tree - branch fell on line | 184 | 260176 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010673 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | RECLOSER | 5020 | 20190116 | 2025 | 276631 | 4153 | Distribution Circuit | Vegetation | Tree - fell into line | 219 | 909507 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012097 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2106 | 83622106 | RECLOSER | 5302 | 20190116 | 2302 | 271783 | 1047 | Distribution Circuit | Vegetation | Tree - fell into line | 517 | 294924 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010224 | OH | Sus | 31422113 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 2487 | 20190116 | 2301 | 273141 | 1215 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 21870 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010731 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 8553 | 20190116 | 2142 | 274260 | 2732 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 19124 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011129 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 6753 | 20190116 | 2142 | 275017 | 2725 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 84475 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011468 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 8557 | 20190116 | 2142 | 275690 | 3843 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 23058 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011728 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE | 9509 | 20190116 | 2300 | 271781 | 1301 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 171732 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011094 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | FELTON-0401 | 83140401 | OCB | 401/2 | 20190116 | 2308 | 271960 | 2049 | Distribution Circuit | Vegetation | Tree - fell into line | 912 | 639550 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010481 | OH | Sus | 31422113 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | OCB | 1101/2 | 20190116 | 1608 | 267368 | 1702 | Distribution Circuit | Vegetation | Tree - fell into line | 2026 | 1063227 | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0009860 | OH | Sus | 0 | 2019 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE | 2181 | 20190116 | 1553 | 267639 | 1703 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 133721 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009950 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | OTHER | WIRE DOWN 1 SPAN SOURCE SIDE 40283 | 20190116 | 2147 | 271259 | 2308 | Distribution Circuit | Equipment Failure/Involved | Overhead | 442 | 215330 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010513 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2002 | 20190116 | 1922 | 269755 | 2778 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 256680 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010102 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER | 39126 | 20190116 | 1408 | 267109 | 1452 | Distribution Circuit | Vegetation | Tree - branch fell on line | 136 | 28333 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009718 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 4355 | 20190116 | 1313 | 266969 | 1283 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 29509 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009760 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER | 11010 | 20190116 | 1945 | 270127 | 1231 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 42967 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010133 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 7799 | 20190116 | 1817 | 273676 | 2738 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 167018 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010922 | OH | Sus | 0 | 2019 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 11929 | 20190116 | 1949 | 274220 | 2966 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 118074 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011118 | OH | Sus | 43634211 | 2019 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 10433 | 20190116 | 1918 | 269709 | 2478 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 11190 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011144 | OH | Sus | 43634211 | 2019 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 9251 | 20190116 | 2119 | 271061 | 2783 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 19481 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011278 | OH | Sus | 31422113 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | RECLOSER | 2064 | 20190116 | 1616 | 267767 | 1243 | Distribution Circuit | Equipment Failure/Involved | Overhead | 600 | 198534 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009896 | OH | Sus | 43634200 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 6973 | 20190116 | 2036 | 270730 | 984 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 35424 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010516 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER | 9488 | 20190116 | 1439 | 267213 | 1794 | Distribution Circuit | Vegetation | Tree - fell into line | 380 | 79995 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0009754 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER | 9104 | 20190116 | 1947 | 270139 | 1468 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1193 | 406884 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010136 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 55781 | 20190116 | 1907 | 269626 | 2702 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 62354 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011063 | OH | Sus | 31422108 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | OCB | 2203/2 | 20190116 | 2123 | 270492 | 2667 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5206 | 4928972 | Overcast-Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0010273 | OH | Sus | 0 | 2019 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 1489 | 20190116 | 1559 | 275086 | 4111 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 45221 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011489 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 10421 | 20190116 | 2123 | 275097 | 2666 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 39990 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011497 | OH | Sus | 0 | 2019 | JAN | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 1653 | 20190117 | 1520 | 274412 | 1244 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 14928 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011333 | OH | Sus | 43634211 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 2887 | 20190117 | 1520 | 274413 | 1367 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2734 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011417 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER | OJ @ CGC 315145724442 | 20190117 | 557 | 272838 | 2207 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 17656 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010638 | OH | Sus | 0 | 2019 | JAN | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 9779 | 20190117 | 634 | 274135 | 2101 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12606 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011078 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | RECLOSER | 12990 | 20190117 | 723 | 272664 | 2214 | Distribution Circuit | Vegetation | Tree - fell into line | 277 | 268878 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010628 | OH | Sus | 0 | 2019 | JAN | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 177 | 20190117 | 1139 | 274879 | 3071 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 6142 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011375 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2161 | 20190117 | 1500 | 275004 | 1282 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1282 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011432 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | JUMPER | OJ AT HARD 6 POLES TO EOL TWD N/E | 20190117 | 2112 | 275005 | 2237 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 6711 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011498 | OH | Sus | 0 | 2019 | JAN | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE | 8937 | 20190117 | 712 | 272776 | 677 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 32496 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011238 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | OTHER | WIRE DOWN | 20190117 | 1513 | 274401 | 659 | Distribution Circuit | Vegetation | Tree - branch fell on line | 116 | 8044 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011306 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | SWITCH | 794081 | 20190117 | 829 | 273472 | 541 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 52477 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010915 | OH | Sus | 0 | 2019 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20190117 | 59 | 272227 | 463 | Distribution Circuit | Vegetation | Tree - fell into line | 209 | 86031 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010474 | OH | Sus | 43634200 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 5151 | 20190202 | 748 | 286838 | 517 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3102 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017058 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 12383 | 20190202 | 543 | 286625 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 15017 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017082 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 6355 | 20190202 | 1434 | 287731 | 1176 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 50568 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017233 | OH | Sus | 43665416 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8239 | 20190202 | 2327 | 288286 | 1123 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 14599 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 19-0017469 | OH | Sus | 31424211 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 6743 | 20190202 | 242 | 286104 | 844 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 29540 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016957 | OH | Sus | 31424211 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE | 2811 | 20190202 | 55 | 286920 | 3747 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 71193 | Overcast-Heavy Rain-Strong Winds-32-90 F | Insulator | Broken, wire on ground | 19-0017100 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2105 | 182222105 | FUSE | 6029 | 20190202 | 437 | 286379 | 3581 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 89931 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017264 | OH | Sus | 31424211 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | FUSE | 2283 | 20190202 | 338 | 286281 | 1847 | Distribution Circuit | Vegetation | Tree - fell into line | 383 | 707401 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016919 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | HATTON-1101 | 182291101 | FUSE | 9302 | 20190202 | 1306 | 287423 | 2931 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 287238 | Heavy Rain-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017244 | OH | Sus | 43665416 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | RECLOSER | 2654 | 20190202 | 1702 | 287895 | 1602 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 26675 | Partly Cloudy-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017292 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | TRANSFORMER | 411370744360 | 20190202 | 1315 | 287507 | 1900 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 9525 | Overcast-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0017178 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | RECLOSER | 2010 | 20190202 | 357 | 287686 | 2807 | Distribution Circuit | Vegetation | Tree - fell into line | 104 | 160135 | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017217 | OH | Sus | 31424211 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE | 8937 | 20190202 | 258 | 286135 | 2199 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 52824 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017224 | OH | Sus | 43665408 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | FUSE | 637 | 20190202 | 2 | 285892 | 1050 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 75600 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016851 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE | 2181 | 20190202 | 103 | 285962 | 2331 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 77094 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016970 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE | 40411 | 20190202 | 243 | 286316 | 1149 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 70861 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016999 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | FUSE | 1279 | 20190202 | 834 | 286973 | 3086 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 15430 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017171 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2012 | 20190202 | 322 | 286174 | 4108 | Distribution Circuit | Equipment Failure/Involved | Overhead | 441 | 1790658 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0016877 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | RECLOSER | 5178 | 20190202 | 425 | 286360 | 415 | Distribution Circuit | Vegetation | Tree - branch fell on line | 267 | 110805 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016908 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 8351 | 20190202 | 1804 | 288221 | 1189 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 10701 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017371 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | TRIP-SAVER | 5401 | 20190202 | 1411 | 287808 | 1207 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 13657 | Partly Cloudy-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017259 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | SEACLIFF-0401 | 83500401 | JUMPER | WIRE DOWN @ 997 MESA GRANDE CT | 20190202 | 1714 | 287911 | 1103 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 7721 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017333 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20190202 | 330 | 286230 | 3602 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5926 | 1943971 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016884 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 7257 | 20190202 | 724 | 287587 | 2126 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 174332 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017265 | OH | Sus | 43665408 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 9655 | 20190202 | 1416 | 287589 | 1794 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 20673 | Partly Cloudy-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017327 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 6409 | 20190202 | 354 | 286363 | 2295 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 139500 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017123 | OH | Sus | 31424211 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 11929 | 20190204 | 601 | 289532 | 637 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1274 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017748 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 1655 | 20190204 | 1100 | 290040 | 1668 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 16680 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018007 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 5873 | 20190204 | 1208 | 290216 | 1416 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2832 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018112 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | TRIP-SAVER | 5401 | 20190204 | 730 | 289633 | 471 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 32499 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017871 | OH | Sus | 31424216 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 1003 | 20190204 | 636 | 289615 | 324 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 19116 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017769 | OH | Sus | 31424216 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 6209 | 20190205 | 1258 | 292704 | 497 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1491 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018645 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER | 65444 | 20190209 | 2250 | 297547 | 980 | Distribution Circuit | Vegetation | Tree - fell into line | 985 | 191758 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020495 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 12377 | 20190210 | 642 | 298482 | 951 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 22824 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0020625 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | SEACLIFF-0401 | 83500401 | FUSE | 6005 | 20190210 | 1343 | 298992 | 484 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 9196 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020758 | OH | Sus | 43676142 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | OTHER | WIRE DOWN @ MTR# 1009698877 | 20190213 | 1713 | 305362 | 1743 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 50714 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022562 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 12383 | 20190213 | 2122 | 305747 | 4208 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 260896 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022695 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 12125 | 20190213 | 2359 | 309562 | 3912 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 11736 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023339 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 7773 | 20190213 | 2359 | 311485 | 4193 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 142562 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023837 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | TRIP-SAVER | 6219 | 20190213 | 2359 | 311487 | 3990 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 87780 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023839 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 1607 | 20190213 | 2359 | 311495 | 4134 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 53742 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023843 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 5066 | 20190213 | 2359 | 311558 | 4051 | Distribution Circuit | Environmental/External | Flood/Erosion | 44 | 178244 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023855 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 12055 | 20190213 | 1544 | 305134 | 276 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1380 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022520 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 8405 | 20190213 | 1308 | 304574 | 3103 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 118965 | Partly Cloudy-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023266 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 2233 | 20190213 | 1918 | 305568 | 2918 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 32098 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023378 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | JUMPER | OJS SS/OF CGC 411493846296 | 20190213 | 1926 | 312811 | 2995 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 8175 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024243 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE | 2845 | 20190213 | 1327 | 304621 | 2899 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 201986 | Partly Cloudy-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023655 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | OCB | 1101/2 | 20190213 | 1052 | 303879 | 2058 | Distribution Circuit | Vegetation | Tree - fell into line | 1959 | 957728 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022134 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | FUSE | 723499 | 20190213 | 1058 | 305177 | 2051 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 28714 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022432 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE | 10187 | 20190213 | 734 | 308658 | 6298 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 37788 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0023140 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE | 1491 | 20190213 | 734 | 311893 | 3494 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 139760 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023961 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE | 8045 | 20190213 | 734 | 312465 | 6099 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 6099 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024150 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | OTHER | WIRE DOWN 1 LD SIDE OF MTR#1008500619 | 20190213 | 1427 | 305024 | 4666 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 37826 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0022470 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 2 | LAURELES-1112 | 182371112 | FUSE | 407 | 20190213 | 838 | 304618 | 2003 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 324263 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022271 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE | 40419 | 20190213 | 532 | 307974 | 4890 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 180930 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022988 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE | 40411 | 20190213 | 532 | 310107 | 3680 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 353280 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023478 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE | 457 | 20190213 | 532 | 311922 | 5076 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 96444 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023971 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8513 | 20190213 | 649 | 302920 | 752 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 12032 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021958 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 7369 | 20190213 | 848 | 303431 | 1922 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 21322 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021965 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 5409 | 20190213 | 650 | 302922 | 670 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3445 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022151 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 12122 | 20190213 | 2248 | 305833 | 5541 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 437093 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022690 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20190213 | 817 | 303177 | 4793 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 221714 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021880 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 8917 | 20190213 | 729 | 305708 | 3582 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 75222 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022583 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 7259 | 20190213 | 729 | 305820 | 4969 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 109318 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022677 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 2453 | 20190213 | 729 | 308941 | 4969 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 64597 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023191 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 766491 | 20190213 | 739 | 309175 | 5058 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 60696 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023248 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 2451 | 20190213 | 729 | 314849 | 6124 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 42868 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024691 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 7873 | 20190213 | 739 | 314852 | 6184 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 179336 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024692 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER | 2606 | 20190213 | 807 | 303128 | 7714 | Distribution Circuit | Vegetation | Tree - fell into line | 327 | 1074917 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021875 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 8167 | 20190213 | 1731 | 308454 | 5450 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 87200 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023117 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 45255 | 20190213 | 511 | 310350 | 4940 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 192660 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023555 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 1421 | 20190213 | 710 | 310527 | 4978 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 104538 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023595 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | TRIP-SAVER | 9089 | 20190213 | 828 | 303242 | 3206 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 327012 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023894 | OH | Sus | 43677321 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 8187 | 20190213 | 828 | 312287 | 6415 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 301505 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024100 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 1445 | 20190213 | 1816 | 305595 | 2790 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 21423 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023084 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 83339 | 20190213 | 1009 | 303622 | 6204 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 55836 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022936 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 6931 | 20190213 | 1131 | 304147 | 2073 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 43896 | Overcast-Drizzle-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023065 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER | 5144 | 20190214 | 1229 | 308769 | 1857 | Distribution Circuit | Vegetation | Tree - fell into line | 146 | 234460 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023219 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 5131 | 20190214 | 337 | 306960 | 1941 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 83440 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023290 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 5141 | 20190214 | 419 | 306746 | 2028 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 24336 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024032 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 3603 | 20190214 | 558 | 308250 | 3342 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 30078 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023421 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9779 | 20190214 | 508 | 306959 | 3502 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 21012 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024523 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 5465 | 20190214 | 629 | 307462 | 467 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 25685 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022890 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | JUMPER | WIRE DOWN 2 SPANS PAST MT# 1007328258 | 20190214 | 606 | 308087 | 1808 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 23868 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023017 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20190214 | 414 | 306780 | 2092 | Distribution Circuit | Vegetation | Tree - fell into line | 666 | 531645 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023038 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 9733 | 20190214 | 739 | 307463 | 884 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 36244 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023166 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 11645 | 20190214 | 213 | 306350 | 3865 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 12540 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023587 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 7799 | 20190214 | 1419 | 310290 | 2096 | Distribution Circuit | Vegetation | Tree - branch fell on line | 61 | 32428 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023672 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 5225 | 20190214 | 216 | 306571 | 3514 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 35140 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024449 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10294 | 20190214 | 415 | 306745 | 2392 | Distribution Circuit | Vegetation | Tree - fell into line | 430 | 670999 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022802 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 3753 | 20190214 | 227 | 306382 | 2088 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7464 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023080 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | FELTON-0401 | 83140401 | FUSE | 5217 | 20190214 | 1243 | 309139 | 1547 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 23205 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023240 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | FELTON-0401 | 83140401 | TRANSFORMER | 315427019690 | 20190214 | 1635 | 310209 | 4229 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 4229 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024114 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2102 | 83252102 | FUSE | 11829 | 20190214 | 1803 | 310520 | 2587 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 12935 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024520 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 1033 | 20190214 | 950 | 308325 | 1900 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 11400 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023331 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 4431 | 20190214 | 1235 | 309634 | 2300 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 248400 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023424 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | JUMPER | WIRE DOWN SS OF 6445 | 20190214 | 658 | 307269 | 3482 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 24374 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023087 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | OCB | 2202/2 | 20190214 | 507 | 306671 | 4892 | Distribution Circuit | Vegetation | Tree - fell into line | 4847 | 1473842 | Partly Cloudy-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022824 | OH | Sus | 31425388 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 6117 | 20190214 | 601 | 307620 | 2069 | Distribution Circuit | Equipment Failure/Involved | Overhead | 156 | 271244 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023034 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 8895 | 20190214 | 552 | s1417125 | 1900 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 199500 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024014 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 5331 | 20190215 | 1359 | 312294 | 1681 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 33620 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024654 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 9237 | 20190215 | 1032 | 311864 | 356 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1068 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023950 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 7601 | 20190215 | 913 | 311642 | 1927 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3854 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024123 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 8353 | 20190215 | 1650 | 312641 | 1208 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 9664 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024197 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | OTHER | WIRE DOWN CGC 315933018430 | 20190215 | 1737 | 312721 | 1408 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 11881 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024269 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 1655 | 20190216 | 1721 | 314835 | 1226 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 12260 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024742 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 2233 | 20190216 | 556 | 313437 | 238 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2142 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024443 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8503 | 20190217 | 1302 | 315896 | 215 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 430 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025152 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 2949 | 20190217 | 620 | 315261 | 820 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 50840 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025123 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 3603 | 20190226 | 2132 | 325323 | 946 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 8514 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028597 | OH | Sus | 43685094 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5515 | 20190227 | 1332 | 327115 | 1321 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 48747 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029083 | OH | Sus | 43687242 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | TRIP-SAVER | 8403 | 20190227 | 221 | 326153 | 631 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 20772 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028703 | OH | Sus | 43685094 | 2019 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5995 | 20190227 | 518 | 326347 | 2097 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5079 | Overcast-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0028797 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20190227 | 43 | 325967 | 455 | Distribution Circuit | Vegetation | Tree - fell into line | 849 | 165487 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028656 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2107 | 83252107 | OTHER | WIRE DOWN | 20190608 | 1043 | 401447 | 29267 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 65606 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0064604 | OH | Sus | 0 | 2019 | JUN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE | 23665 | 20190610 | 436 | 403105 | 708 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 8889 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0065104 | OH | Sus | 0 | 2019 | JUN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 5985 | 20190815 | 1444 | 513553 | 72 | Distribution Circuit | Equipment Failure/Involved | Overhead | 88 | 6336 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0088407 | OH | Sus | 0 | 2019 | AUG | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7969 | 20191026 | 2042 | 692818 | 4436 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 8872 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0118288 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | JUMPER | OJ 2 S/SS OF 90 CARTER | 20200116 | 904 | 763185 | 658 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1316 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010232 | OH | Sus | 44157208 | 2020 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 2233 | 20200116 | 1436 | 763116 | 139 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1529 | Overcast-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0010080 | OH | Sus | 0 | 2020 | JAN | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 5078 | 20200116 | 906 | 762422 | 494 | Distribution Circuit | Vegetation | Tree - branch fell on line | 800 | 171201 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009638 | OH | Sus | 44157208 | 2020 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 5411 | 20200116 | 906 | 763040 | 549 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 9333 | Partly Cloudy-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009991 | OH | Sus | 31486501 | 2020 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 6911 | 20200209 | 816 | 781532 | 335 | Distribution Circuit | Vegetation | Tree - branch fell on line | 94 | 31490 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0019015 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 12455 | 20200315 | 100 | 851642 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 5760 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032166 | OH | Sus | 31495831 | 2020 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20200315 | 934 | 852139 | 86 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 5732 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0032258 | OH | Sus | 0 | 2020 | MAR | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20200316 | 7 | 853030 | 182 | Distribution Circuit | Vegetation | Tree - bark fell into line | 181 | 32942 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032480 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 2969 | 20200316 | 7 | 853308 | 698 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2094 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032481 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5477 | 20200816 | 2103 | 1014188 | 1305 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 67744 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0085566 | OH | Sus | 0 | 2020 | AUG | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 6161 | 20200816 | 252 | 1012937 | 898 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 20654 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0085007 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2106 | 83622106 | RECLOSER | 12760 | 20200816 | 434 | 1010524 | 749 | Distribution Circuit | Equipment Failure/Involved | Overhead | 397 | 68445 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0084687 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8137 | 20200816 | 252 | 1010502 | 1000 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 14000 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0084706 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 1159 | 20200816 | 241 | 1011479 | 1260 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 42840 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0084775 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 6121 | 20200816 | 239 | 1011539 | 1015 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 109620 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0084611 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 3459 | 20200816 | 1146 | 1013115 | 364 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 33545 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0085160 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20200817 | 322 | 1014489 | 1061 | Distribution Circuit | Vegetation | Tree - fell into line | 181 | 141530 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0085524 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 2 | RIO DEL MAR-0401 | 83260401 | FUSE | 7075 | 20200908 | 653 | 1060599 | 783 | Distribution Circuit | Vegetation | Tree - fell into line | 244 | 54525 | Clear-32-90 F | Transformer (OH) | Broken, wire on ground | 20-0094801 | OH | Sus | 0 | 2020 | SEP | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7593 | 20210118 | 1001 | 1212381 | 532 | Distribution Circuit | Vegetation | Tree - branch fell on line | 85 | 37226 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0009704 | OH | Sus | 44628039 | 2021 | JAN | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 764889 | 20210119 | 512 | 1214819 | 815 | Distribution Circuit | Equipment Failure/Involved | Overhead | 344 | 169471 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0010780 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 3279 | 20210119 | 1025 | 1217223 | 499 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 10479 | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0011105 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 3537 | 20210119 | 17 | 1221136 | 5263 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 105260 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0012724 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | FUSE | 7793 | 20210119 | 853 | 1215368 | 282 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 1692 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0010509 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | JUMPER | FUSE 11739 | 20210119 | 41 | 1221607 | 6799 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 61191 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013207 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8259 | 20210125 | 2240 | 1225431 | 835 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 12482 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 21-0014252 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 11384 | 20210125 | 759 | 1223696 | 343 | Distribution Circuit | Vegetation | Tree - fell into line | 2398 | 306988 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013669 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 35874 | 20210125 | 7 | 1222992 | 703 | Distribution Circuit | Vegetation | Tree - branch fell on line | 558 | 164396 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013541 | OH | Sus | 44633345 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 12377 | 20210127 | 1027 | 1234876 | 388 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 3262 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0016196 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER | 5028 | 20210127 | 2049 | 1237733 | 89 | Distribution Circuit | Vegetation | Tree - fell into line | 584 | 51976 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0016912 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5339 | 20210127 | 245 | 1232391 | 637 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 8281 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0015778 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | RECLOSER | 2000 | 20210127 | 128 | 1231910 | 844 | Distribution Circuit | Vegetation | Tree - fell into line | 217 | 183148 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0015501 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | SWITCH | 8687 | 20210127 | 112 | 1233712 | 1106 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 99540 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 21-0015454 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 7349 | 20210127 | 2356 | 1238548 | 676 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2704 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0017127 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 5411 | 20210127 | 46 | 1231559 | 703 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 11951 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0015710 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8097 | 20210127 | 614 | 1233126 | 698 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 11866 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0016234 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 11333 | 20210127 | 121 | 1234911 | 909 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4545 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0016057 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 8643 | 20210127 | 126 | 1231867 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 22680 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0016100 | OH | Sus | 0 | 2021 | JAN | Yes |  | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 8313 | 20210128 | 631 | 1238626 | 516 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 8772 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0017284 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 95050 | 20210804 | 755 | 1433409 | 610 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1970 | 512625 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0099476 | OH | Sus | 44932682 | 2021 | AUG | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 243760 | 20211011 | 1034 | 1492771 | 391 | Distribution Circuit | Vegetation | Tree - fell into line | 1682 | 559642 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0128730 | OH | Sus | 31554589 | 2021 | OCT | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 5143 | 20211024 | 932 | 1509231 | 238 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 6426 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136028 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5743 | 20211024 | 744 | 1508408 | 508 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2540 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135836 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER | WIRE DOWN 6868 SAN LARENZO WY | 20211024 | 1459 | 1514519 | 209 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 3647 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136517 | OH | Sus | 0 | 2021 | OCT | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | OTHER | WIRE DOWN 5 SP LD SD OF 7565 | 20211024 | 1323 | 1513778 | 348 | Distribution Circuit | Vegetation | Tree - fell into line | 271 | 39604 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136413 | OH | Sus | 0 | 2021 | OCT | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20211024 | 723 | 1508276 | 493 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1798 | 90303 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135694 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1102 | 182941102 | OTHER | WIRE DOWN E/OF 6939 | 20211025 | 521 | 1516997 | 682 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 47368 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0137039 | OH | Sus | 0 | 2021 | OCT | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER | WIRE DOWN @ 391980 | 20211213 | 37 | 1565601 | 980 | Distribution Circuit | Vegetation | Tree - fell into line | 175 | 118292 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0156934 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 2923 | 20211213 | 705 | 1565815 | 625 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 30625 | Clear-32-90F | Conductor, Overhead | Broken, wire on object | 21-0157313 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20211213 | 426 | 1565708 | 406 | Distribution Circuit | Vegetation | Tree - branch fell on line | 186 | 75516 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0156952 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9463 | 20211213 | 559 | 1565765 | 278 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 16680 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0156949 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER | 16010 | 20211225 | 1124 | 1581319 | 304 | Distribution Circuit | Vegetation | Tree - branch fell on line | 140 | 24056 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160562 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5225 | 20211227 | 142 | 1583811 | 944 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 7235 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161049 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | TRIP-SAVER | 6601 | 20211227 | 420 | 1584296 | 455 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 15925 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161023 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | RECLOSER | 2020 | 20220906 | 1033 | 1801698 | 293 | Distribution Circuit | Vegetation | Tree - fell into line | 849 | 87909 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0106392 | OH | Sus | 31615345 | 2022 | SEP | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12758 | 20220907 | 547 | 1803969 | 161 | Distribution Circuit | Vegetation | Tree - fell into line | 279 | 44919 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0107132 | OH | Sus | 0 | 2022 | SEP | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5435 | 20221210 | 1044 | 1881626 | 375 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 2625 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0138371 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9769 | 20221210 | 1158 | 1881941 | 322 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 10626 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0138456 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 5066 | 20221210 | 849 | 1880962 | 628 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 20724 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138154 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 2923 | 20221210 | 953 | 1881335 | 537 | Distribution Circuit | Vegetation | Tree - branch fell on line | 45 | 24165 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0138442 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE | 1995 | 20221210 | 700 | 1880720 | 400 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 800 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138126 | OH | Sus | 0 | 2022 | DEC | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | OTHER | WIRE DOWN 1 SPAN LD SIDE OF CFC# 315508318685 | 20221210 | 844 | 1880911 | 145 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 1595 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138226 | OH | Sus | 0 | 2022 | DEC | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | OJ 1 SPAN LD SIDE OF CGCG 315455021192 | 20221210 | 824 | 1881394 | 688 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3440 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138235 | OH | Sus | 0 | 2022 | DEC | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE | 1491 | 20221210 | 922 | 1881113 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 23400 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0138296 | OH | Sus | 0 | 2022 | DEC | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 5955 | 20221231 | 12 | 1902898 | 933 | Distribution Circuit | Vegetation | Tree - fell into line | 167 | 155811 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142448 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | OTHER | 12122 | 20221231 | 450 | 1902999 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 39186 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142481 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 796388 | 20221231 | 529 | 1903038 | 539 | Distribution Circuit | Vegetation | Tree - fell into line | 269 | 118531 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0142489 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | OCB | 2203/2 | 20221231 | 309 | 1902974 | 849 | Distribution Circuit | Vegetation | Tree - fell into line | 4856 | 1942256 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142449 | OH | Sus | 0 | 2022 | DEC | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5219 | 20230105 | 1435 | 1922791 | 327 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 6213 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0007591 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 6409 | 20230105 | 230 | 1920381 | 1032 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 111456 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0007028 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9769 | 20230107 | 1249 | 1926605 | 282 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 9306 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0008847 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2002 | 20230107 | 901 | 1926203 | 29 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 870 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0006449 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 1143 | 20230108 | 129 | 1931781 | 998 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 13972 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0010216 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 7681 | 20230108 | 1355 | 1933716 | 276 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 2760 | Clear-32-90 F | Conductor, Overhead | On Ground | 23-0010256 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE | 2811 | 20230108 | 948 | 1932990 | 160 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 3200 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0010081 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 8895 | 20230108 | 106 | 1931497 | 816 | Distribution Circuit | Vegetation | Tree - branch fell on line | 144 | 99272 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0009843 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 1445 | 20230108 | 7 | 1930410 | 1109 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 13308 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0009789 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER | 5400 | 20230109 | 518 | 1935806 | 570 | Distribution Circuit | Environmental/External | Flood/Erosion | 9 | 5130 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0010784 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | JUMPER | OPEN/CREATE FOR LR 698634 | 20230109 | 519 | 1938059 | 543 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 43440 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0010782 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10996 | 20230109 | 518 | 1935780 | 435 | Distribution Circuit | Environmental/External | Flood/Erosion | 257 | 111795 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0010784 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | FUSE | 627 | 20230109 | 337 | 1935465 | 1060 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 23320 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0011010 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | PANOCHE-1103 | 253671103 | RECLOSER | 4008 | 20230109 | 531 | 1935817 | 558 | Distribution Circuit | Vegetation | Tree - branch fell on line | 118 | 42833 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0010788 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | RECLOSER | 5178 | 20230109 | 524 | 1935790 | 480 | Distribution Circuit | Vegetation | Tree - fell into line | 267 | 99296 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0010785 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 68191 | 20230109 | 1156 | 1937988 | 205 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 3895 | Clear-32-90 F | Conductor, Overhead | On Ground | 23-0011143 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20230109 | 216 | 1935800 | 1244 | Distribution Circuit | Vegetation | Tree - fell into line | 1289 | 1601657 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0010786 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | SWITCH | 80069 | 20230110 | 202 | 1942969 | 767 | Distribution Circuit | Vegetation | Tree - branch fell on line | 423 | 129242 | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0011726 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | SWITCH | 11025 | 20230110 | 202 | 1943868 | 531 | Distribution Circuit | Company Initiated | Return Circuit Normal | 172 | 91332 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0011726 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE | 10189 | 20230110 | 1528 | 1945741 | 129 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 516 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0012684 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 2 | HATTON SUB | 18229 | OCB | 1101/2 | 20230114 | 836 | 1953363 | 930 | Distribution Circuit | Vegetation | Tree - fell into line | 505 | 136405 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 23-0015922 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE | 1491 | 20230114 | 1015 | 1953903 | 715 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 15088 | Clear-32-90 F | Conductor, Overhead | On Ground | 23-0016178 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 11384 | 20230116 | 518 | 1956858 | 769 | Distribution Circuit | Vegetation | Tree - fell into line | 416 | 88568 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0016929 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7593 | 20230116 | 250 | 1956601 | 655 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 44540 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0017049 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2105 | 83692105 | JUMPER | WIRE DOWN | 20230116 | 211 | 1956542 | 450 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 27288 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0017031 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 11327 | 20230116 | 538 | 1956873 | 682 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 682 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0017064 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SEACLIFF-0401 | 83500401 | RECLOSER | 929132 | 20230116 | 240 | 1956588 | 837 | Distribution Circuit | Vegetation | Tree - fell into line | 127 | 106299 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0016880 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | SEACLIFF-0401 | 83500401 | RECLOSER | 12946 | 20230116 | 324 | 1956683 | 662 | Distribution Circuit | Vegetation | Tree - fell into line | 213 | 136302 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0016893 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 8917 | 20230116 | 342 | 1956737 | 551 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 11571 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0016911 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20230221 | 1407 | 1991279 | 38 | Distribution Circuit | Equipment Failure/Involved | Overhead | 325 | 12350 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0031165 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 6121 | 20230221 | 1407 | 1991849 | 559 | Distribution Circuit | Equipment Failure/Involved | Overhead | 109 | 60931 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0031165 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | OCB | 2101/2 | 20230224 | 500 | 2002630 | 959 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1264 | 1179857 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0033657 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS SUB | 18358 | SWITCH | BURNS | 20230228 | 1205 | 2015200 | 87 | Distribution Circuit | Vegetation | Tree - fell into line | 2568 | 223416 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0036162 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI SUB | 8293 | SWITCH | POINT MORETTI | 20230228 | 1206 | 2015195 | 86 | Distribution Circuit | Vegetation | Tree - fell into line | 636 | 54696 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0036162 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 9005 | 20230314 | 912 | 2035418 | 522 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 11484 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0044704 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8097 | 20230314 | 1022 | 2035864 | 368 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 6256 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0044931 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 737 | 20230314 | 1821 | 2044095 | 202 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 11568 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0045877 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20230314 | 1613 | 2042186 | 255 | Distribution Circuit | Vegetation | Tree - fell into line | 428 | 109140 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0045535 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 6753 | 20230321 | 1426 | 2056682 | 419 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 15922 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0049798 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | FUSE | 627 | 20230321 | 1255 | 2054707 | 401 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 8822 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0049710 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER |  | 20130408 | 1421 | 770356 | 596 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 596 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0022721 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH | SB15 | 20130408 | 1555 | 770621 | 167 | Distribution Circuit | Equipment Failure/Involved | Other | 170 | 28390 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0022728 | OH | Sus | 0 | 2013 | APR | Yes | None | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH | SB15 | 20141203 | 1707 | 1123765 | 1242 | Distribution Circuit | Vegetation | Tree - fell into line | 167 | 51262 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073571 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER | 60114 | 20141203 | 245 | 1121657 | 1157 | Distribution Circuit | Vegetation | Tree - fell into line | 291 | 274737 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073128 | OH | Sus | 42284329 | 2014 | DEC | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 17431 | 20141203 | 344 | 1121676 | 766 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 24512 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073146 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 6947 | 20141203 | 1225 | 1123091 | 1055 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 9245 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073409 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
DE ANZA | Tier 2 | SARATOGA-1106 | 83371106 | OTHER |  | 20141203 | 1528 | 1123621 | 1153 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1153 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073519 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
DE ANZA | Tier 2 | SARATOGA-1106 | 83371106 | FUSE | 5089 | 20141203 | 1129 | 1122897 | 1068 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 54353 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073545 | OH | Sus | 3118510 | 2014 | DEC | Yes | Three Phase Fault | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER | 60124 | 20141211 | 859 | 1131925 | 596 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1574 | 548748 | Strong winds-32 - 90 F | Other | Broken, wire on ground | 14-0075200 | OH | Sus | 42293239 | 2014 | DEC | Yes |  | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 9125 | 20141211 | 927 | 1132231 | 812 | Distribution Circuit | Equipment Failure/Involved | Other | 476 | 105949 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075306 | OH | Sus | 42293239 | 2014 | DEC | Yes | Line to Line | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 7651 | 20141211 | 1122 | 1133222 | 618 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 4326 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075384 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER |  | 20141211 | 1427 | 1134340 | 678 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 20400 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075669 | OH | Sus | 31120396 | 2014 | DEC | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 5203 | 20141211 | 852 | 1133449 | 899 | Distribution Circuit | Equipment Failure/Involved | Other | 99 | 35300 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075428 | OH | Sus | 42293239 | 2014 | DEC | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 15767 | 20141211 | 1536 | 1134656 | 69 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 621 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075630 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
DE ANZA | Tier 3 | STELLING-1110 | 83481110 | RECLOSER | 60094 | 20141211 | 917 | 1131873 | 853 | Distribution Circuit | Vegetation | Tree - fell into line | 270 | 47238 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075295 | OH | Sus | 31120421 | 2014 | DEC | Yes |  | Yes
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5617 | 20141230 | 1605 | 1153765 | 1695 | Distribution Circuit | Equipment Failure/Involved | Other | 12 | 20340 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079406 | OH | Sus | 42304600 | 2014 | DEC | Yes | Line to Line | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH | SA07 | 20141230 | 2034 | 1155873 | 2945 | Distribution Circuit | Vegetation | Tree - fell into line | 491 | 291402 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079551 | OH | Sus | 31124019 | 2014 | DEC | Yes | Line to Ground | Yes
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 15771 | 20141230 | 2000 | 1156062 | 1808 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 33308 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079668 | OH | Sus | 31124019 | 2014 | DEC | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | STELLING-1110 | 83481110 | FUSE | 8051 | 20141230 | 1940 | 1155271 | 1605 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 40125 | Strong winds-32 - 90 F | Conductor, Underground | Broken, wire on ground | 14-0079733 | OH | Sus | 42304601 | 2014 | DEC | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 18597 | 20150206 | 2056 | 1178468 | 1324 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 9584 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010831 | OH | Sus | 42328658 | 2015 | FEB | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER | 60092 | 20150206 | 2113 | 1178840 | 3338 | Distribution Circuit | Equipment Failure/Involved | Other | 204 | 52093 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010837 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 3721 | 20150206 | 1535 | 1176037 | 520 | Distribution Circuit | Equipment Failure/Involved | Other | 5 | 2600 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0010384 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
DE ANZA | Tier 2 | STELLING-1110 | 83481110 | FUSE | 1251 | 20150206 | 1408 | 1175762 | 122 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 652 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010269 | OH | Sus | 31132912 | 2015 | FEB | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 31331 | 20150207 | 2130 | 1181937 | 2086 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 16688 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011415 | OH | Sus | 31132912 | 2015 | FEB | Yes | Line to Line | Yes
DE ANZA | Tier 2 | SARATOGA-1105 | 83371105 | SWITCH |  | 20150207 | 331 | 1179973 | 30 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 0 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0010269 | OH | Sus | 31132912 | 2015 | FEB | Yes |  | Yes
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 15769 | 20150207 | 634 | 1180520 | 1236 | Distribution Circuit | Vegetation | Tree - fell into line | 496 | 47618 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011044 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4417 | 20150208 | 1419 | 1182959 | 2351 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 6851 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011611 | OH | Sus | 31132912 | 2015 | FEB | Yes | Line to Line | Yes
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 15771 | 20150208 | 1219 | 1182674 | 963 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 18784 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011548 | OH | Sus | 31132916 | 2015 | FEB | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | OTHER | WIRE DOWN 5P LOAD SIDE 23069 | 20151213 | 1023 | 1361691 | 911 | Distribution Circuit | Vegetation | Tree - fell into line | 500 | 125830 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084768 | OH | Sus | 42588469 | 2015 | DEC | Yes | Force Out | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4451 | 20160217 | 1612 | 1405976 | 633 | Distribution Circuit | Vegetation | Tree - fell into line | 337 | 135477 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013277 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 8349 | 20160217 | 2137 | 1407390 | 1838 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1838 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013459 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER | WIRE DOWN ONE SPAN NORTH OF METER 5000058672 | 20160217 | 2129 | 1407539 | 1006 | Distribution Circuit | Vegetation | Tree - branch fell on line | 129 | 111744 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013647 | OH | Sus | 42632627 | 2016 | FEB | Yes | Open Circuit | Yes | Yes
DE ANZA | Tier 2 | SARATOGA-1104 | 83371104 | FUSE | 3571 | 20160217 | 1552 | 1405667 | 652 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 4564 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013316 | OH | Sus | 42632627 | 2016 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 29951 | 20160217 | 1909 | 1406369 | 1157 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2314 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 16-0013596 | OH | Sus | 42632627 | 2016 | FEB | Yes | None | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 60124 | 20160305 | 1347 | 1416718 | 1151 | Distribution Circuit | Vegetation | Tree - fell into line | 789 | 117853 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0017487 | OH | Sus | 31222889 | 2016 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 60124 | 20160305 | 1727 | 1419060 | 1390 | Distribution Circuit | Equipment Failure/Involved | Overhead | 716 | 339716 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017809 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | 60116 | 20160305 | 1124 | 1416563 | 656 | Distribution Circuit | Vegetation | Tree - fell into line | 612 | 34496 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017451 | OH | Sus | 0 | 2016 | MAR | Yes | Multi-Fault | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LB44 | 20160305 | 1624 | 1417274 | 2291 | Distribution Circuit | Vegetation | Tree - fell into line | 328 | 185751 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017573 | OH | Sus | 31222889 | 2016 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 1429 | 20160305 | 1810 | 1418995 | 759 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 5184 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017815 | OH | Sus | 42646371 | 2016 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | STELLING-1110 | 83481110 | FUSE | 9265 | 20160305 | 1839 | 1418253 | 1211 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 70238 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017840 | OH | Sus | 42646371 | 2016 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | STELLING-1110 | 83481110 | JUMPER | 1 SPAN OF WIRE DOWN @ 7653 TWD 4985 | 20160305 | 2229 | 1420792 | 2916 | Distribution Circuit | Equipment Failure/Involved | Overhead | 171 | 227228 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018071 | OH | Sus | 42646371 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 9125 | 20170103 | 1547 | 1615982 | 660 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 26457 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003164 | OH | Sus | 42909755 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 7163 | 20170103 | 40 | 1615236 | 787 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 30724 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0002877 | OH | Sus | 31292530 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | JUMPER | WIRE DOWN 1 SPAN SSD OF 11239 | 20170103 | 2130 | 1616948 | 1280 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1280 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003333 | OH | Sus | 42909755 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4451 | 20170108 | 1318 | 1627251 | 1197 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 34713 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005385 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER | 60092 | 20170108 | 1842 | 1627933 | 1149 | Distribution Circuit | Vegetation | Tree - fell into line | 843 | 919162 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005604 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | OTHER | WIRE DOWN 2 P/W/O 23069 | 20170108 | 1018 | 1624830 | 1922 | Distribution Circuit | Vegetation | Tree - fell into line | 494 | 174739 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005263 | OH | Sus | 31294278 | 2017 | JAN | Yes | Force Out | Yes | Yes
DE ANZA | Tier 2 | STELLING-1110 | 83481110 | OTHER | WIRE DOWN 1 P/S/O 33481 | 20170108 | 42 | 1622449 | 643 | Distribution Circuit | Vegetation | Tree - branch fell on line | 63 | 6018 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004885 | OH | Sus | 42913015 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4533 | 20170109 | 1529 | 1631634 | 4281 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 10369 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006375 | OH | Sus | 31294361 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 11753 | 20170109 | 2002 | 1632193 | 4058 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 36522 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006326 | OH | Sus | 31294278 | 2017 | JAN | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER | TAPS @ 26199 PIERCE RD, LG | 20170110 | 1028 | 1632615 | 2661 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 7626 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0006519 | OH | Sus | 31294361 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 12741 | 20170110 | 27 | 1632419 | 852 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 8470 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006382 | OH | Sus | 31294278 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH | SA07 | 20170110 | 1954 | 1636576 | 4017 | Distribution Circuit | Vegetation | Tree - fell into line | 469 | 208453 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007001 | OH | Sus | 31294278 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4415 | 20170110 | 2046 | 1637006 | 4293 | Distribution Circuit | Environmental/External | Flood/Erosion | 104 | 446472 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007211 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 949 | 20170110 | 1040 | 1632952 | 412 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1236 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006576 | OH | Sus | 42913015 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 21117 | 20170110 | 1328 | 1633397 | 3142 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 95536 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006882 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | SARATOGA-1106 | 83371106 | FUSE | 5089 | 20170110 | 1545 | 1634134 | 1509 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 60903 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006848 | OH | Sus | 31294278 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 15769 | 20170110 | 1448 | 1634151 | 1717 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 25755 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0006782 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | JUMPER | WIRE DOWN @ 2897 | 20170111 | 856 | 1639138 | 3289 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 16445 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007514 | OH | Sus | 31294278 | 2017 | JAN | Yes | Force Out | Yes | Yes
DE ANZA | Tier 2 | SARATOGA-1106 | 83371106 | FUSE | 7419 | 20170111 | 913 | 1639242 | 1664 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 99102 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007560 | OH | Sus | 42913015 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | STELLING-1110 | 83481110 | FUSE | 4417 | 20170120 | 1210 | 1654124 | 3401 | Distribution Circuit | Environmental/External | Flood/Erosion | 31 | 25753 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011564 | OH | Sus | 31297028 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 17345 | 20170122 | 1127 | 1660580 | 3234 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 19404 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013294 | OH | Sus | 31297030 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 21295 | 20170122 | 2317 | 1662576 | 890 | Distribution Circuit | Environmental/External | Flood/Erosion | 20 | 17800 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013552 | OH | Sus | 42928670 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 11753 | 20170122 | 716 | 1659461 | 2384 | Distribution Circuit | Environmental/External | Flood/Erosion | 9 | 21456 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012915 | OH | Sus | 31297028 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 4469 | 20170123 | 408 | 1662752 | 937 | Distribution Circuit | Vegetation | Tree - branch fell on line | 71 | 61407 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013603 | OH | Sus | 31297030 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LA64 | 20170207 | 629 | 1678191 | 1906 | Distribution Circuit | Vegetation | Tree - fell into line | 338 | 175889 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018174 | OH | Sus | 31304239 | 2017 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LB48 | 20170207 | 833 | 1679023 | 178 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 16554 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0018321 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | TRIP-SAVER | 12041 | 20170207 | 848 | 1679132 | 381 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 29718 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018469 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 12371 | 20170207 | 639 | 1680008 | 2298 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 11490 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018532 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 2 | SARATOGA-1105 | 83371105 | SWITCH | SC01 | 20170207 | 1512 | 1680535 | 2008 | Distribution Circuit | Vegetation | Tree - branch fell on line | 310 | 35608 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018656 | OH | Sus | 31304239 | 2017 | FEB | Yes | Force Out | Yes | No
DE ANZA | Tier 2 | STELLING-1110 | 83481110 | TRIP-SAVER | 9265 | 20170207 | 512 | 1678870 | 1929 | Distribution Circuit | Equipment Failure/Involved | Overhead | 461 | 309020 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018379 | OH | Sus | 42939926 | 2017 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER | WIRE DOWN 23400 OLD SANTA CRUZ HWY | 20170209 | 1918 | 1684101 | 1853 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 17557 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019734 | OH | Sus | 31304342 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 5387 | 20170217 | 923 | 1695077 | 2239 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 17912 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022859 | OH | Sus | 31306421 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 30547 | 20170217 | 1540 | 1693227 | 1771 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 8855 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023041 | OH | Sus | 31306421 | 2017 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 60124 | 20170220 | 1503 | 1703629 | 5850 | Distribution Circuit | Vegetation | Tree - fell into line | 718 | 3670876 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023867 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | HICKS-1116 | 83431116 | OTHER | WIRE DOWN 1 SP S/S OF 18667 | 20170220 | 1706 | 1704476 | 4028 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 108756 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025621 | OH | Sus | 42950074 | 2017 | FEB | Yes | None | Yes | Yes
DE ANZA | Tier 2 | LOS GATOS-1101 | 82021101 | FUSE | 1425 | 20170220 | 1642 | 1705251 | 2916 | Distribution Circuit | Environmental/External | Flood/Erosion | 84 | 244944 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025632 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LA64 | 20170220 | 1550 | 1703743 | 7049 | Distribution Circuit | Vegetation | Tree - fell into line | 338 | 1772057 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023898 | OH | Sus | 31306421 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LA46 | 20170220 | 1552 | 1703842 | 1649 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 222615 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023899 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH | SA07 | 20170220 | 1620 | 1704048 | 4331 | Distribution Circuit | Vegetation | Tree - fell into line | 160 | 694083 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023924 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LB44 | 20170220 | 1748 | 1704704 | 7629 | Distribution Circuit | Equipment Failure/Involved | Overhead | 508 | 2696073 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023990 | OH | Sus | 31306421 | 2017 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | 60116 | 20170220 | 2111 | 1704263 | 3968 | Distribution Circuit | Vegetation | Tree - fell into line | 309 | 1136634 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024200 | OH | Sus | 31306421 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH | SB19 | 20170220 | 1859 | 1705660 | 5715 | Distribution Circuit | Environmental/External | Flood/Erosion | 9 | 51435 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024916 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 2909 | 20170220 | 1634 | 1704184 | 1676 | Distribution Circuit | Vegetation | Tree - fell into line | 207 | 346932 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024730 | OH | Sus | 31306426 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 19887 | 20170220 | 1737 | 1704989 | 4245 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 12735 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0024806 | OH | Sus | 31306426 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 2915 | 20170220 | 1619 | 1704013 | 3142 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 78385 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025464 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 21117 | 20170220 | 1707 | 1704480 | 4216 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 139104 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025761 | OH | Sus | 31306421 | 2017 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 15771 | 20170220 | 1747 | 1705726 | 5799 | Distribution Circuit | Environmental/External | Flood/Erosion | 35 | 124357 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024892 | OH | Sus | 31306421 | 2017 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | STELLING-1110 | 83481110 | FUSE | 22639 | 20170220 | 1543 | 1704777 | 9909 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 56984 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0026749 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER | OJ'S | 20170222 | 640 | 1711513 | 992 | Distribution Circuit | Environmental/External | Flood/Erosion | 8 | 7936 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025874 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 17431 | 20170222 | 1652 | 1711126 | 308 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 9856 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025855 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 12371 | 20170406 | 2018 | 1751187 | 4365 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 21825 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038433 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | SARATOGA-1103 | 83371103 | JUMPER | CUT IN CLERAR | 20170911 | 327 | 1874784 | 713 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 7184 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0077619 | OH | Sus | 0 | 2017 | SEP | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 22529 | 20170911 | 314 | 1875033 | 805 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 15295 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0077592 | OH | Sus | 0 | 2017 | SEP | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 9125 | 20171008 | 2221 | 1894126 | 928 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 24464 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085291 | OH | Sus | 31355577 | 2017 | OCT | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 17499 | 20171204 | 1826 | 1935939 | 753 | Distribution Circuit | Vegetation | Tree - branch fell on line | 36 | 27108 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099810 | OH | Sus | 43227153 | 2017 | DEC | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 60120 | 20171204 | 2006 | 1936048 | 2249 | Distribution Circuit | Vegetation | Tree - fell into line | 685 | 35805 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0099811 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4417 | 20171204 | 2152 | 1936115 | 1058 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 17876 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099865 | OH | Sus | 31368279 | 2017 | DEC | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | 60116 | 20171216 | 924 | 1944237 | 3342 | Distribution Circuit | Vegetation | Tree - fell into line | 2232 | 3670529 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0101950 | OH | Sus | 31370183 | 2017 | DEC | Yes | Multi-Fault | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER | 60118 | 20171216 | 646 | 1944042 | 3186 | Distribution Circuit | Vegetation | Tree - fell into line | 908 | 1847418 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0101910 | OH | Sus | 31370181 | 2017 | DEC | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | OTHER | WIRE DOWN 1 POLE S/OF 13831 | 20180728 | 838 | 142285 | 394 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2321 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 18-0064573 | OH | Sus | 43422814 | 2018 | JUL | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 21063 | 20181108 | 931 | 211438 | 902 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 8118 | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0098245 | OH | Sus | 0 | 2018 | NOV | Yes | Force Out | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LB48 | 20181129 | 822 | 228166 | 509 | Distribution Circuit | Vegetation | Tree - branch fell on line | 143 | 53737 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104832 | OH | Sus | 31416747 | 2018 | NOV | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER | WIRE DOWN | 20181129 | 818 | 228121 | 1752 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1752 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105018 | OH | Sus | 31416745 | 2018 | NOV | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 4461 | 20181129 | 837 | 228279 | 562 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 21356 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104981 | OH | Sus | 43586552 | 2018 | NOV | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 31297 | 20190106 | 1632 | 255654 | 382 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 6494 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005194 | OH | Sus | 31420581 | 2019 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER | WIRE DOWN @ C/OUT 4421 TWD WEST | 20190106 | 1748 | 256034 | 426 | Distribution Circuit | Equipment Failure/Involved | Overhead | 172 | 40440 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005341 | OH | Sus | 43625028 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 11401 | 20190106 | 1815 | 256332 | 2071 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 84994 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005414 | OH | Sus | 31420535 | 2019 | JAN | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 15777 | 20190106 | 1111 | 255170 | 1893 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 11358 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005084 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LB48 | 20190116 | 2022 | 270595 | 5229 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 392405 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010191 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4451 | 20190116 | 1950 | 271687 | 1522 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 44138 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010569 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | LOS GATOS-1106 | 82021106 | FUSE | 1573 | 20190116 | 1954 | 270207 | 4091 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 46585 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010970 | OH | Sus | 43634152 | 2019 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 17121 | 20190116 | 2045 | 274832 | 3055 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 113035 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011363 | OH | Sus | 31422106 | 2019 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER | LA60 | 20190116 | 1548 | 267619 | 2838 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 263305 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009835 | OH | Sus | 43634152 | 2019 | JAN | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | TRIP-SAVER | 2917 | 20190116 | 2100 | 275113 | 2476 | Distribution Circuit | Vegetation | Tree - fell into line | 117 | 224036 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010265 | OH | Sus | 43634154 | 2019 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | RECLOSER | 167792 | 20190116 | 1705 | 268225 | 2921 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 93472 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009938 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 15769 | 20190116 | 2010 | 270659 | 1369 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 127275 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0010340 | OH | Sus | 31422104 | 2019 | JAN | Yes | Force Out | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 7651 | 20190117 | 614 | 273173 | 850 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 36238 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0010840 | OH | Sus | 43634152 | 2019 | JAN | Yes | Open Circuit | Yes | No
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 6757 | 20190213 | 802 | 303116 | 358 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 14678 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021961 | OH | Sus | 31425395 | 2019 | FEB | Yes | Open Circuit | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4421 | 20190214 | 605 | 307160 | 1345 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 69940 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0023198 | OH | Sus | 43677333 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER | 60092 | 20190214 | 6 | 306012 | 2619 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 50318 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0022717 | OH | Sus | 31425395 | 2019 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | RECLOSER | 167792 | 20190214 | 143 | 306368 | 2432 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 77824 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022748 | OH | Sus | 31425395 | 2019 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 15777 | 20190227 | 541 | 326371 | 664 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3984 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028735 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4421 | 20190608 | 519 | 401182 | 941 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 21392 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0064523 | OH | Sus | 43832032 | 2019 | JUN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | STELLING-1110 | 83481110 | JUMPER | OJ'S | 20191023 | 130 | 677261 | 879 | Distribution Circuit | 3rd Party | Vehicle | 1 | 879 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0114891 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER | 8051 | 20191029 | 1945 | 694583 | 349 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 8725 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0118769 | OH | Sus | 44082355 | 2019 | OCT | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 1579 | 20200116 | 934 | 763363 | 1811 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1811 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0010328 | OH | Sus | 31486644 | 2020 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4435 | 20200816 | 254 | 1011258 | 1101 | Distribution Circuit | Environmental/External | Lightning | 34 | 37434 | Lightning-Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0084746 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LA64 | 20210118 | 950 | 1212195 | 493 | Distribution Circuit | Vegetation | Tree - branch fell on line | 337 | 30511 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0009632 | OH | Sus | 31528401 | 2021 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | OTHER | 15775 | 20210125 | 115 | 1223103 | 609 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 12931 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013574 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER | 60114 | 20210127 | 132 | 1231923 | 2381 | Distribution Circuit | Equipment Failure/Involved | Overhead | 248 | 176225 | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0015496 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 6947 | 20211024 | 558 | 1508380 | 527 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 10540 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135727 | OH | Sus | 45018624 | 2021 | OCT | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER | WIRE DOWN 195 MILLER CUTOFF RD | 20211024 | 1028 | 1510046 | 554 | Distribution Circuit | Vegetation | Tree - fell into line | 292 | 23572 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0135958 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 2 | STELLING-1110 | 83481110 | OTHER | WIRE DOWN 17294 STEVENS CANYON RD | 20211024 | 2201 | 1520704 | 2701 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 26742 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0137836 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 10003 | 20211025 | 2208 | 1520448 | 1232 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 28336 | Clear-Strong Winds-Rain-Combination-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0138270 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | 60116 | 20221210 | 821 | 1880745 | 613 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1136 | 161962 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138134 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LA64 | 20230116 | 229 | 1956566 | 976 | Distribution Circuit | Vegetation | Tree - fell into line | 338 | 76656 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016872 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | SARATOGA-1105 | 83371105 | FUSE | 15767 | 20230116 | 639 | 1957030 | 641 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1986 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0017111 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
DE ANZA | Tier 2 | STELLING-1110 | 83481110 | FUSE | 18351 | 20230116 | 250 | 1957333 | 800 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3200 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0017028 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 7163 | 20230221 | 1457 | 1992038 | 653 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 52240 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0031709 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | AUBERRY-1101 | 254151101 | FUSE | D133 | 20130408 | 741 | 769174 | 464 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 5104 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022304 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
FRESNO | Tier 2 | AUBERRY-1101 | 254151101 | FUSE | D13006 | 20160305 | 2022 | 1418915 | 459 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2295 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017870 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
FRESNO | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER | 7080 | 20170111 | 20 | 1638345 | 854 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 240828 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007485 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
FRESNO | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER | 7080 | 20170120 | 1825 | 1653783 | 1523 | Distribution Circuit | Vegetation | Tree - branch fell on line | 282 | 426086 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011753 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
FRESNO | Tier 2 | SAND CREEK-1103 | 254601103 | FUSE | 7995F | 20170121 | 101 | 1655384 | 481 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 40885 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0011886 | OH | Sus | 42930433 | 2017 | JAN | Yes | Line to Ground | Yes | No
FRESNO | Tier 3 | AUBERRY-1101 | 254151101 | FUSE | D5467 | 20170122 | 427 | 1658745 | 1938 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 6971 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013060 | OH | Sus | 31297701 | 2017 | JAN | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | AUBERRY-1101 | 254151101 | RECLOSER | R314 | 20170122 | 1140 | 1660681 | 204 | Distribution Circuit | Vegetation | Tree - fell into line | 421 | 43624 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013127 | OH | Sus | 42930604 | 2017 | JAN | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | SWITCH | 3084D | 20170122 | 1453 | 1661368 | 123 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 7995 | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0012500 | OH | Sus | 42930533 | 2017 | JAN | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER | 7080 | 20170122 | 1048 | 1660448 | 1494 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 413458 | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013043 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
FRESNO | Tier 3 | AUBERRY-1101 | 254151101 | FUSE | 37429 | 20170123 | 1715 | 1664724 | 155 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 310 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013985 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | FUSE | 7997F | 20170123 | 1620 | 1664590 | 1232 | Distribution Circuit | Environmental/External | Ice or snow | 61 | 75152 | Overcast-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0013043 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
FRESNO | Tier 3 | AUBERRY-1101 | 254151101 | JUMPER | WIRE DOWN 1 W/OF MTR# 1004704399 | 20170407 | 542 | 1749536 | 453 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1812 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0037721 | OH | Sus | 0 | 2017 | APR | Yes | None | Yes | No
FRESNO | Tier 2 | AUBERRY-1102 | 254151102 | FUSE | D2748 | 20190106 | 2018 | 257577 | 363 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 21054 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005476 | OH | Sus | 43626773 | 2019 | JAN | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | RECLOSER | 7173 | 20190204 | 1359 | 290490 | 7414 | Distribution Circuit | Equipment Failure/Involved | Overhead | 303 | 1040880 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0018005 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | FUSE | 7684F | 20190204 | 506 | 289478 | 3701 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 111030 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018401 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | FUSE | 3201F | 20190204 | 1359 | 296545 | 8250 | Distribution Circuit | Environmental/External | Ice or snow | 4 | 40636 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0018005 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER | 7170 | 20190204 | 256 | 289407 | 10624 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 150788 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017740 | OH | Sus | 43669499 | 2019 | FEB | Yes | Line to Line | Yes | No
FRESNO | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER | 7080 | 20190204 | 256 | 292038 | 3518 | Distribution Circuit | Environmental/External | Ice or snow | 354 | 969928 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017740 | OH | Sus | 43669499 | 2019 | FEB | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-1103 | 254061103 | FUSE | 3767F | 20190209 | 955 | 296826 | 375 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 375 | Overcast-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0020277 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
FRESNO | Tier 3 | AUBERRY-1101 | 254151101 | FUSE | D325 | 20190214 | 1357 | 309515 | 1625 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 63402 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0023635 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | AUBERRY-1102 | 254151102 | FUSE | D9404 | 20190217 | 2247 | 317102 | 693 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 24255 | Partly Cloudy-Fog-Below 32 F | Connector or Splice (OH) | Broken, wire on ground | 19-0025522 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
FRESNO | Tier 2 | DUNLAP-0001 | 254060001 | FUSE | 7985F | 20200817 | 1452 | 1017281 | 370 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 5507 | Partly Cloudy-Heat Wave-Above 90 | Crossarm, Wood | Broken, wire on ground | 20-0086152 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | AUBERRY-1101 | 254151101 | RECLOSER | R2845 | 20211011 | 2112 | 1495296 | 1171 | Distribution Circuit | Vegetation | Tree - fell into line | 823 | 842904 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0129469 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
FRESNO | Tier 2 | AUBERRY-1102 | 254151102 | FUSE | D10394 | 20211213 | 1217 | 1567063 | 214 | Distribution Circuit | 3rd Party | Other | 20 | 4280 | Clear-32-90F | Conductor, Overhead | On Ground | 21-0157266 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
FRESNO | Tier 2 | AUBERRY-1101 | 254151101 | RECLOSER | R2838 | 20230109 | 755 | 1936604 | 754 | Distribution Circuit | Vegetation | Tree - fell into line | 418 | 255427 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0010866 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
FRESNO | Tier 2 | AUBERRY-1102 | 254151102 | OTHER | D8323 | 20230116 | 708 | 1957161 | 664 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 3016 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0017068 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | AUBERRY-1101 | 254151101 | RECLOSER | 49122 | 20230224 | 2120 | 2007220 | 1100 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 1100 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 23-0034521 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
FRESNO | Tier 2 | KERCKHOFF-1101 | 252561101 | FUSE | D2818 | 20230225 | 119 | 2007461 | 1080 | Distribution Circuit | Environmental/External | Ice or snow | 49 | 52920 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0035155 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
FRESNO | Tier 2 | SAND CREEK-1103 | 254601103 | FUSE | 7485F | 20230225 | 211 | 2008658 | 922 | Distribution Circuit | Environmental/External | Ice or snow | 51 | 47022 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0035280 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | AUBERRY-1102 | 254151102 | OCB | 1102/2 | 20230314 | 1122 | 2036982 | 563 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1657 | 124963 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 23-0044810 | OH | Sus | 35431654 | 2023 | MAR | Yes | Line to Ground | Yes | No
KERN | Tier 2 | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 3990 | 20141211 | 2342 | 1136682 | 2368 | Distribution Circuit | Equipment Failure/Involved | Other | 27 | 63936 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0076008 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | OCB | W14 | 20130408 | 2246 | 771246 | 874 | Distribution Circuit | 3rd Party | Vehicle | 3591 | 204109 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0022826 | OH | Sus | 30988253 | 2013 | APR | Yes | Line to Ground | Yes
LOS PADRES | Tier 2 | CAMBRIA-1102 | 182771102 | FUSE | 3865 | 20141211 | 1732 | 1135157 | 1822 | Distribution Circuit | Equipment Failure/Involved | Other | 80 | 120108 | Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 14-0075760 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
LOS PADRES | Tier 2 | CAMBRIA-1102 | 182771102 | RECLOSER | W50 | 20141211 | 1919 | 1135720 | 769 | Distribution Circuit | Vegetation | Tree - fell into line | 611 | 79832 | Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 14-0075837 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
LOS PADRES | Tier 2 | FOOTHILL-1101 | 182951101 | FUSE | 10549 | 20141211 | 1928 | 1139274 | 2084 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 18756 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076586 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | V74 | 20141211 | 1901 | 1135524 | 547 | Distribution Circuit | Vegetation | Tree - fell into line | 522 | 160563 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075784 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
LOS PADRES | Tier 2 | PURISIMA-1101 | 182971101 | OTHER |  | 20141211 | 1139 | 1133323 | 518 | Distribution Circuit | Equipment Failure/Involved | Other | 14 | 7186 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075587 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
LOS PADRES | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 4391 | 20141211 | 2157 | 1136947 | 1484 | Distribution Circuit | Vegetation | Tree - branch fell on line | 77 | 135674 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076103 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
LOS PADRES | Tier 3 | SANTA MARIA-1108 | 182671108 | RECLOSER | M80 | 20141211 | 2110 | 1136342 | 2755 | Distribution Circuit | 3rd Party | Vehicle | 319 | 561161 | Drizzle-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0075934 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
LOS PADRES | Tier 3 | SANTA MARIA-1108 | 182671108 | FUSE | 2175 | 20141211 | 1920 | 1139430 | 3600 | Distribution Circuit | Equipment Failure/Involved | Other | 58 | 208800 | Rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0076665 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
LOS PADRES | Tier 2 | SANTA YNEZ-1104 | 182721104 | FUSE | 6205 | 20141211 | 2047 | 1136032 | 3398 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 190288 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0076098 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
LOS PADRES | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE | 7147 | 20141211 | 1558 | 1134769 | 592 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 20802 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075708 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
LOS PADRES | Tier 3 | TEMPLETON-2113 | 183052113 | FUSE | 6343 | 20141211 | 1838 | 1135375 | 1688 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 28696 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0076201 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
LOS PADRES | Tier 2 | BUELLTON-1101 | 183041101 | FUSE | 20149 | 20141212 | 634 | 1137198 | 1781 | Distribution Circuit | Equipment Failure/Involved | Other | 33 | 65822 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076296 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
LOS PADRES | Tier 2 | SANTA YNEZ-1102 | 182721102 | FUSE | 20195 | 20141212 | 621 | 1138040 | 2410 | Distribution Circuit | Equipment Failure/Involved | Other | 21 | 50610 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076453 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
LOS PADRES | Tier 3 | TEMPLETON-2113 | 183052113 | RECLOSER | A10 | 20150206 | 1932 | 1177984 | 773 | Distribution Circuit | Vegetation | Tree - fell into line | 406 | 54085 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0010615 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
LOS PADRES | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 10895 | 20150207 | 1429 | 1181338 | 281 | Distribution Circuit | Vegetation | Tree - fell into line | 179 | 11149 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011274 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
LOS PADRES | Tier 2 | OCEANO-1108 | 182601108 | FUSE | 9589 | 20150719 | 1354 | 1272537 | 946 | Distribution Circuit | Environmental/External | Lightning | 32 | 30272 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0048930 | OH | Sus | 0 | 2015 | JUL | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | OTHER | WIRE DOWN SS 14843 | 20150719 | 735 | 1272189 | 1535 | Distribution Circuit | Environmental/External | Lightning | 96 | 97605 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0048751 | OH | Sus | 0 | 2015 | JUL | Yes | Open Circuit | Yes | No
LOS PADRES | Tier 2 | OCEANO-1104 | 182601104 | RECLOSER | Q06 | 20151018 | 2159 | 1325661 | 291 | Distribution Circuit | Equipment Failure/Involved | Overhead | 819 | 155970 | Overcast-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0071600 | OH | Sus | 42521324 | 2015 | OCT | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | GOLDTREE-1107 | 182581107 | OCB | 1107/2 | 20160217 | 2242 | 1407584 | 364 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 9169 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013484 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | CAYUCOS-1101 | 182551101 | FUSE | 9217 | 20160305 | 2337 | 1420675 | 425 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 10200 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 16-0018118 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2111 | 183052111 | RECLOSER | A66 | 20160305 | 2310 | 1420581 | 800 | Distribution Circuit | Vegetation | Tree - fell into line | 959 | 131092 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018035 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | ATASCADERO-1103 | 182541103 | FUSE | 4617 | 20170108 | 1004 | 1624576 | 369 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 2302 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005110 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE | 7581 | 20170108 | 1859 | 1628888 | 206 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 13999 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005667 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2110 | 183052110 | FUSE | 30185 | 20170109 | 210 | 1629943 | 610 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 4310 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0005865 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | ATASCADERO-1101 | 182541101 | FUSE | 30459 | 20170111 | 14 | 1638172 | 306 | Distribution Circuit | Vegetation | Tree - branch fell on line | 62 | 14072 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007344 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | OTHER | 14851 | 20170111 | 957 | 1639368 | 790 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2370 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 17-0007581 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | FOOTHILL-1101 | 182951101 | FUSE | 3561 | 20170118 | 1453 | 1646560 | 186 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 2046 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010071 | OH | Sus | 42929062 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | SANTA MARIA-1108 | 182671108 | OTHER | WIRE DOWN 2 LD SD SW 7345 | 20170118 | 1248 | 1646173 | 950 | Distribution Circuit | Equipment Failure/Involved | Overhead | 439 | 105340 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0009934 | OH | Sus | 42929077 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE | 9179 | 20170120 | 540 | 1652521 | 443 | Distribution Circuit | Vegetation | Tree - fell into line | 303 | 48013 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011234 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE | 5581 | 20170120 | 728 | 1653008 | 663 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 26520 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0011615 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | ATASCADERO-1101 | 182541101 | RECLOSER | A02 | 20170122 | 339 | 1658478 | 770 | Distribution Circuit | Vegetation | Tree - fell into line | 487 | 40648 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012685 | OH | Sus | 42929174 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 3 | ATASCADERO-1101 | 182541101 | SWITCH | 2793 | 20170122 | 831 | 1659777 | 300 | Distribution Circuit | Vegetation | Tree - fell into line | 175 | 37389 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012925 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | ATASCADERO-1103 | 182541103 | FUSE | 4617 | 20170122 | 435 | 1658770 | 1047 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 26938 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0013079 | OH | Sus | 31297289 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | FOOTHILL-1101 | 182951101 | FUSE | 2815 | 20170122 | 626 | 1659255 | 896 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 9856 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013034 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | FOOTHILL-1101 | 182951101 | JUMPER | OJ'S 1 SPAN S/OF 1008717736 | 20170122 | 831 | 1659776 | 3109 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6218 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013259 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | MESA-1101 | 182821101 | FUSE | 6119 | 20170122 | 820 | 1660464 | 2124 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 36108 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0013341 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 9347 | 20170122 | 734 | 1659529 | 346 | Distribution Circuit | Vegetation | Tree - branch fell on line | 32 | 11072 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013038 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | OCEANO-1104 | 182601104 | JUMPER | WIRE DOWN 3 N/E OF 9407 | 20170122 | 703 | 1660466 | 3312 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1449 | 260666 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013045 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE | 9547 | 20170122 | 647 | 1659311 | 267 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2136 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012852 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE | 9179 | 20170122 | 748 | 1659595 | 466 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 8388 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012934 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE | 4747 | 20170122 | 638 | 1659420 | 552 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 44712 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0012998 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | SANTA YNEZ-1101 | 182721101 | RECLOSER | Y52 | 20170122 | 2045 | 1662536 | 1585 | Distribution Circuit | Equipment Failure/Involved | Overhead | 190 | 259226 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013523 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 3 | TEMPLETON-2113 | 183052113 | SWITCH | 858255 | 20170122 | 1456 | 1661588 | 2377 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 52294 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0013257 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | CABRILLO-1104 | 183101104 | FUSE | 6085 | 20170123 | 813 | 1663170 | 1799 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1799 | Overcast-Drizzle-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0013854 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE | 6095 | 20170123 | 649 | 1662990 | 1801 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 30547 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013804 | OH | Sus | 31297289 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 3 | TEMPLETON-2113 | 183052113 | FUSE | 6343 | 20170123 | 123 | 1662645 | 822 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 13974 | Rain-Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0013600 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | CAMBRIA-1101 | 182771101 | OTHER | WIRE DOWN @ 19019 HWY 1 | 20170207 | 1651 | 1680705 | 1344 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 37965 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018731 | OH | Sus | 0 | 2017 | FEB | Yes | Open Circuit | Yes | Yes
LOS PADRES | Tier 2 | ATASCADERO-1103 | 182541103 | RECLOSER | A18 | 20170217 | 1806 | 1697994 | 1478 | Distribution Circuit | Vegetation | Tree - fell into line | 1613 | 415250 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022620 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 10485 | 20170217 | 925 | 1698372 | 6020 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 355180 | Partly Cloudy-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0022640 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 11007 | 20170217 | 930 | 1701241 | 3896 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 27272 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023378 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 11005 | 20170217 | 930 | 1701361 | 4380 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 13140 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023411 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | OCEANO-1105 | 182601105 | OCB | V02 | 20170217 | 959 | 1693522 | 3576 | Distribution Circuit | Vegetation | Tree - fell into line | 9178 | 3700800 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022024 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | OCEANO-1108 | 182601108 | FUSE | 58417 | 20170217 | 957 | 1694172 | 4458 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 4458 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022227 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | OCEANO-1108 | 182601108 | FUSE | 77699 | 20170217 | 1029 | 1696511 | 3010 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6020 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022333 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | OCEANO-1108 | 182601108 | SWITCH | 8511 | 20170217 | 1750 | 1696038 | 10 | Distribution Circuit | Vegetation | Tree - fell into line | 890 | 8900 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0022557 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | OCEANO-1108 | 182601108 | FUSE | 15239 | 20170217 | 1015 | 1694221 | 2918 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 145900 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022828 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2113 | 183052113 | FUSE | 6323 | 20170217 | 1101 | 1694781 | 2092 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 18828 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023187 | OH | Sus | 42949651 | 2017 | FEB | Yes | Multi-Fault | Yes | No
LOS PADRES | Tier 2 | CABRILLO-1103 | 183101103 | FUSE | 11221 | 20170218 | 744 | 1699093 | 289 | Distribution Circuit | Equipment Failure/Involved | Overhead | 163 | 7093 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023007 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 9313 | 20170218 | 2344 | 1700964 | 1225 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 18375 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023308 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE | 9211 | 20170218 | 953 | 1699402 | 1834 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 18340 | Overcast-Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0022979 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE | 15567 | 20170218 | 1321 | 1699925 | 3013 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 123533 | Strong Winds-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0023111 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE | 9547 | 20170218 | 1345 | 1699960 | 1214 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 9712 | Strong Winds-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023115 | OH | Sus | 42949651 | 2017 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2113 | 183052113 | FUSE | 30877 | 20170218 | 1118 | 1699608 | 1447 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1447 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023038 | OH | Sus | 31306099 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE | 5429 | 20170220 | 1553 | 1703819 | 512 | Distribution Circuit | Equipment Failure/Involved | Overhead | 107 | 54784 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023909 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | Q08 | 20170220 | 534 | 1702489 | 450 | Distribution Circuit | Vegetation | Tree - fell into line | 183 | 46692 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0023646 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 10895 | 20170220 | 1120 | 1703107 | 766 | Distribution Circuit | Vegetation | Tree - fell into line | 1179 | 166918 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023599 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 3 | ATASCADERO-1103 | 182541103 | RECLOSER | A12 | 20170221 | 746 | 1707754 | 1054 | Distribution Circuit | Equipment Failure/Involved | Overhead | 131 | 21824 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0024923 | OH | Sus | 31306099 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE | 15567 | 20170221 | 1134 | 1708392 | 412 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 8906 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025179 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE | 4479 | 20170221 | 833 | 1708645 | 412 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2060 | Heavy Rain-Strong Winds-Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025134 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE | 2521 | 20170407 | 1729 | 1751417 | 1229 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 13519 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0038104 | OH | Sus | 31318406 | 2017 | APR | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | CABRILLO-1103 | 183101103 | FUSE | 6085 | 20171020 | 1610 | 1906380 | 173 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 173 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0089249 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | SANTA MARIA-1108 | 182671108 | FUSE | 6461 | 20171204 | 930 | 1934673 | 813 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2439 | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099678 | OH | Sus | 43227091 | 2017 | DEC | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | MESA-1103 | 182821103 | SWITCH | 12047 | 20180316 | 1653 | 46189 | 11 | Distribution Circuit | Company Initiated | Return Circuit Normal | 1 | 11 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0023230 | OH | Sus | 31384355 | 2018 | MAR | Yes | None | Yes | No
LOS PADRES | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 9313 | 20181129 | 222 | 227529 | 855 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 12825 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104799 | OH | Sus | 43587912 | 2018 | NOV | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2113 | 183052113 | RECLOSER | A08 | 20190116 | 2011 | 270405 | 1008 | Distribution Circuit | Equipment Failure/Involved | Overhead | 924 | 414175 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0010176 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V02 | 20190117 | 1713 | 274695 | 429 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2706 | 679889 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0011313 | OH | Sus | 31422124 | 2019 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | ATASCADERO-1101 | 182541101 | FUSE | 81595 | 20190202 | 331 | 286221 | 704 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3803 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0016901 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | ATASCADERO-1101 | 182541101 | JUMPER | LINE & BUCK AT 10500 SAN MARCOS RD | 20190202 | 1230 | 287402 | 1511 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1511 | Strong Winds-Heavy Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0017307 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
LOS PADRES | Tier 2 | BUELLTON-1102 | 183041102 | FUSE | 20391 | 20190202 | 428 | 287123 | 2218 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 17744 | Overcast-Fog-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0017067 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
LOS PADRES | Tier 2 | CABRILLO-1104 | 183101104 | FUSE | 8695 | 20190202 | 830 | 286967 | 2061 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 20610 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017199 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | FOOTHILL-1101 | 182951101 | FUSE | 3229 | 20190202 | 559 | 286585 | 3592 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 8978 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017515 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | PALMER-1101 | 183031101 | RECLOSER | M82 | 20190202 | 236 | 286085 | 622 | Distribution Circuit | Vegetation | Tree - branch fell on line | 787 | 74114 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016863 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE | 14851 | 20190202 | 151 | 286027 | 1164 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3492 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016882 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | V74 | 20190202 | 2039 | 288120 | 1208 | Distribution Circuit | Vegetation | Tree - fell into line | 382 | 212654 | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0017348 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | SANTA YNEZ-1104 | 182721104 | FUSE | 7973 | 20190202 | 1413 | 288255 | 2828 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 121604 | Strong Winds-Rain-Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0017374 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
LOS PADRES | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE | 6289 | 20190202 | 901 | 287046 | 1664 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 13312 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017271 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE | 6023 | 20190202 | 533 | 286526 | 975 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 13650 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017042 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 3 | TEMPLETON-2113 | 183052113 | RECLOSER | A12 | 20190202 | 611 | 286610 | 1670 | Distribution Circuit | Vegetation | Tree - fell into line | 130 | 106171 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016944 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | ZACA-1102 | 182681102 | OCB | 1102/2 | 20190202 | 327 | 286215 | 1176 | Distribution Circuit | Vegetation | Tree - fell into line | 1427 | 751030 | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0016880 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 3 | BUELLTON-1102 | 183041102 | FUSE | 6075 | 20190204 | 1326 | 290380 | 1433 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 7165 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0017961 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | CAMBRIA-1101 | 182771101 | FUSE | 789803 | 20190213 | 1044 | 303783 | 836 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 7539 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022150 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | MORRO BAY-1102 | 183011102 | FUSE | 10573 | 20190213 | 709 | 302969 | 436 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 3052 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021876 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
LOS PADRES | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE | 5581 | 20190227 | 1606 | 327387 | 1373 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 11864 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0029173 | OH | Sus | 31426870 | 2019 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE | 30099 | 20200315 | 851 | 852090 | 507 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4563 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032262 | OH | Sus | 44258655 | 2020 | MAR | Yes | Multi-Fault | Yes | No
LOS PADRES | Tier 2 | BUELLTON-1101 | 183041101 | FUSE | 8673 | 20210119 | 1223 | 1217455 | 382 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 2674 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0010922 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | W12 | 20210119 | 1142 | 1216804 | 589 | Distribution Circuit | Vegetation | Tree - fell into line | 783 | 64893 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 21-0010709 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | V72 | 20210127 | 251 | 1232418 | 436 | Distribution Circuit | Vegetation | Tree - fell into line | 1579 | 233641 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0015564 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | CAMBRIA-1102 | 182771102 | FUSE | 3865 | 20210812 | 1618 | 1441321 | 356 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 29548 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0103873 | OH | Sus | 44945723 | 2021 | AUG | Yes | Line to Ground | Yes | Yes
LOS PADRES | Tier 2 | PASO ROBLES-1104 | 182611104 | OTHER | WIRE DOWN TWD CGC 511598579063 | 20211025 | 14 | 1516133 | 1016 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2032 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136963 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V18 | 20211025 | 455 | 1516952 | 853 | Distribution Circuit | Vegetation | Tree - fell into line | 1042 | 316084 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0136878 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | V74 | 20221210 | 1222 | 1882329 | 387 | Distribution Circuit | Vegetation | Tree - fell into line | 382 | 64752 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138378 | OH | Sus | 31630223 | 2022 | DEC | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 15185 | 20230105 | 421 | 1920579 | 548 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 15892 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0007093 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | CABRILLO-1104 | 183101104 | FUSE | 6345 | 20230108 | 1258 | 1933594 | 519 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 6607 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0010233 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | OCEANO-1102 | 182601102 | FUSE | 8631 | 20230114 | 1421 | 1954545 | 254 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 5588 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016277 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
LOS PADRES | Tier 2 | PURISIMA-1101 | 182971101 | FUSE | 20139 | 20230224 | 511 | 2003221 | 424 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 4240 | Overcast-Drizzle-Strong Winds-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 23-0033704 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE | 9211 | 20230314 | 1028 | 2035944 | 464 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4640 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0044832 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | V74 | 20230314 | 1140 | 2037502 | 392 | Distribution Circuit | Vegetation | Tree - fell into line | 372 | 66360 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0044881 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
SAN JOSE | Tier 2 | LLAGAS-2103 | 83182103 | FUSE | 14201 | 20141211 | 2140 | 1136215 | 620 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 1240 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075959 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SAN JOSE | Tier 2 | MILPITAS-1109 | 82831109 | OTHER |  | 20141212 | 1115 | 1138128 | 150 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 300 | Drizzle-32 - 90 F | Conductor, Overhead | On Ground | 14-0076326 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
SAN JOSE | Tier 2 | SWIFT-2110 | 83392110 | FUSE | 6263 | 20141230 | 1843 | 1156068 | 1342 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 22396 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079602 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SAN JOSE | Tier 2 | MORGAN HILL-2105 | 83242105 | FUSE | 28315 | 20170110 | 2051 | 1637040 | 2529 | Distribution Circuit | Vegetation | Tree - branch fell on line | 86 | 15704 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007155 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SAN JOSE | Tier 2 | MORGAN HILL-2111 | 83242111 | FUSE | 3761 | 20170110 | 2002 | 1636629 | 2428 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 246744 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0007249 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SAN JOSE | Tier 2 | SWIFT-2110 | 83392110 | RECLOSER | XR254 | 20170119 | 1010 | 1650603 | 1664 | Distribution Circuit | Environmental/External | Lightning | 194 | 189436 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0010809 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SAN JOSE | Tier 2 | LLAGAS-2101 | 83182101 | FUSE | 3843 | 20170207 | 736 | 1678652 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 6146 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018354 | OH | Sus | 0 | 2017 | FEB | Yes | None | Yes | No
SAN JOSE | Tier 2 | MORGAN HILL-2105 | 83242105 | OTHER | WIRE DOWN 1/S/S/O FUCO'S 4889 | 20170207 | 1126 | 1679934 | 664 | Distribution Circuit | Equipment Failure/Involved | Overhead | 98 | 17648 | Strong Winds-Rain-Heavy Rain-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018660 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
SAN JOSE | Tier 3 | MORGAN HILL-2111 | 83242111 | TRIP-SAVER | 4461 | 20170207 | 1723 | 1680858 | 4728 | Distribution Circuit | Environmental/External | Flood/Erosion | 63 | 297864 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018740 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | Yes
SAN JOSE | Tier 2 | MC KEE-1111 | 83531111 | FUSE | 14289 | 20170217 | 827 | 1693487 | 1969 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 11814 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023138 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SAN JOSE | Tier 3 | MORGAN HILL-2111 | 83242111 | FUSE | 2153 | 20190106 | 1954 | 257386 | 1536 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 18432 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005517 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SAN JOSE | Tier 2 | MILPITAS-1109 | 82831109 | FUSE | 25457 | 20190202 | 1352 | 287562 | 4368 | Distribution Circuit | Vegetation | Tree - bark fell into line | 4 | 17472 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0018584 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SAN JOSE | Tier 3 | LLAGAS-2107 | 83182107 | FUSE | 4459 | 20190213 | 1319 | 304628 | 546 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 8736 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0022427 | OH | Sus | 31425399 | 2019 | FEB | Yes | Line to Ground | Yes | No
SAN JOSE | Tier 2 | HICKS-2101 | 83432101 | FUSE | 25065 | 20190216 | 1743 | 314870 | 448 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 23744 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0024737 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SAN JOSE | Tier 3 | MORGAN HILL-2105 | 83242105 | OTHER | OJ'S NW/O 73299 | 20200817 | 645 | 1015257 | 316 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 13858 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0085670 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | Yes
SAN JOSE | Tier 2 | MORGAN HILL-2105 | 83242105 | FUSE | 27285 | 20211227 | 1446 | 1585919 | 390 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 16380 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161149 | OH | Sus | 45102203 | 2021 | DEC | Yes | Force Out | Yes | No
SAN JOSE | Tier 2 | MORGAN HILL-2111 | 83242111 | FUSE | 2501 | 20221210 | 1103 | 1881688 | 412 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 11967 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138452 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 3889 | 20240204 | 740 | 2334985 | 565 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 39550 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019291 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20240301 | 235 | 2391724 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 1939 | 115078 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0035822 | OH | Sus | 31685408 | 2024 | MAR | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | SWITCH | 216684 | 20241105 | 2311 | 2615125 | 1072 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 59 | 63248 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0131208 | OH | Sus | 0 | 2024 | NOV | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 543817 | 20241105 | 2311 | 2617170 | 1436 | Distribution Circuit | Vegetation | Tree - branch fell on line | 49 | 70364 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0131208 | OH | Sus | 0 | 2024 | NOV | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE | 1491 | 20241214 | 629 | 2658690 | 681 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 27921 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145635 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | OTHER | WIRE DOWN1 N/OF 7213 | 20241214 | 650 | 2657781 | 625 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 40338 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145495 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 19949 | 20241214 | 641 | 2659609 | 789 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 17358 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145151 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4451 | 20241214 | 642 | 2659236 | 750 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 21000 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145151 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER | 60114 | 20241214 | 649 | 2653738 | 612 | Distribution Circuit | Vegetation | Tree - fell into line | 290 | 70203 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145146 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | SWITCH | SA11 | 20241214 | 1703 | 2660250 | 126 | Distribution Circuit | Vegetation | Tree - branch fell on line | 132 | 13592 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145146 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | PALO SECO-0401 | 13180401 | FUSE | 5500 | 20240204 | 29 | 2334153 | 1039 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 59223 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019093 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | SAN LEANDRO-1109 | 13111109 | FUSE | 1608 | 20241214 | 1013 | 2657171 | 503 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 29174 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145614 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | EL CERRITO G-1105 | 12501105 | FUSE | R3383 | 20241214 | 1358 | 2659592 | 387 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 8127 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145772 | OH | Sus | 0 | 2024 | DEC | Yes | Force Out | Yes | No
EAST BAY | Tier 2 | EL CERRITO G-1105 | 12501105 | RECLOSER | BR304 | 20241214 | 1505 | 2659823 | 313 | Distribution Circuit | Equipment Failure/Involved | Overhead | 594 | 185922 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146059 | OH | Sus | 0 | 2024 | DEC | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 2933 | 20240204 | 443 | 2334363 | 485 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3395 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019266 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOPLAND-1101 | 42251101 | FUSE | 8017 | 20240204 | 616 | 2334597 | 278 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 20025 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019360 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3091 | 20240204 | 1119 | 2338099 | 385 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 23870 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019718 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 4239 | 20240204 | 1318 | 2339952 | 128 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 1280 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019944 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 1593 | 20240204 | 1912 | 2371528 | 7019 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 119323 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026940 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER | 694680 | 20240301 | 1019 | 2391944 | 538 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 21442 | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0035998 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOPLAND-1101 | 42251101 | OTHER | WIRE DOWN SS/OF CGC# 216756550525 | 20241214 | 450 | 2653922 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 306 | 7214 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145158 | OH | Sus | 0 | 2024 | DEC | Yes | Open Circuit | Yes | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | JUMPER | WIRE DOWN 2 SPANS LD SIDE 1793 | 20241214 | 829 | 2655150 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4630 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145434 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE | 2613 | 20241214 | 922 | 2656452 | 475 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2375 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145547 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | REDBUD-1102 | 43191102 | OTHER | WIRE DOWN 2 CGC# 218017648327 | 20241214 | 1227 | 2658883 | 274 | Distribution Circuit | Vegetation | Tree - fell into line | 485 | 7050 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145715 | OH | Sus | 0 | 2024 | DEC | Yes | Open Circuit | Yes | No
LOS PADRES | Tier 2 | OCEANO-1104 | 182601104 | RECLOSER | 891294 | 20240204 | 857 | 2335801 | 572 | Distribution Circuit | Vegetation | Tree - fell into line | 859 | 264012 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019340 | OH | Sus | 0 | 2024 | FEB | Yes | Multi-Fault | Yes | No
LOS PADRES | Tier 2 | ATASCADERO-1101 | 182541101 | FUSE | 2553 | 20240204 | 1240 | 2339282 | 537 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 6444 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020617 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2110 | 183052110 | FUSE | 5935 | 20241214 | 924 | 2656522 | 316 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 5372 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145464 | OH | Sus | 0 | 2024 | DEC | Yes | Three Phase Fault | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE | 2911 | 20241214 | 927 | 2656434 | 293 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 6895 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145525 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE | 81595 | 20241214 | 940 | 2656811 | 298 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 3278 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145591 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | SILVERADO-2102 | 43432102 | RECLOSER | 636 | 20241214 | 1157 | 2658584 | 509 | Distribution Circuit | Equipment Failure/Involved | Overhead | 131 | 30823 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145686 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER | 13026 | 20240301 | 2345 | 2394078 | 4000 | Distribution Circuit | Vegetation | Tree - fell into line | 174 | 246286 | Overcast-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0036609 | OH | Sus | 0 | 2024 | MAR | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 27019 | 20241214 | 40 | 2652760 | 731 | Distribution Circuit | Vegetation | Tree - fell into line | 165 | 120615 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145049 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | RECLOSER | 1646 | 20241214 | 146 | 2652835 | 815 | Distribution Circuit | Vegetation | Tree - fell into line | 542 | 396143 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145039 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CLARK ROAD-1102 | 103091102 | RECLOSER | 90548 | 20241214 | 827 | 2655264 | 707 | Distribution Circuit | Equipment Failure/Involved | Overhead | 163 | 94721 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145292 | OH | Sus | 0 | 2024 | DEC | Yes | Multi-Fault | Yes | No
SAN JOSE | Tier 3 | MORGAN HILL-2111 | 83242111 | RECLOSER | 944636 | 20241214 | 838 | 2655380 | 650 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 11700 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145677 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1346 | 20240301 | 2139 | 2393678 | 1177 | Distribution Circuit | Vegetation | Tree - fell into line | 294 | 243443 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036523 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER | 32536 | 20240301 | 2331 | 2394708 | 1101 | Distribution Circuit | Vegetation | Tree - fell into line | 460 | 313184 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036531 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 21933 | 20240301 | 2337 | 2394556 | 841 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 9251 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 24-0036750 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 5825 | 20241214 | 37 | 2652746 | 769 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5383 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145048 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER | 51484 | 20241214 | 202 | 2652870 | 961 | Distribution Circuit | Vegetation | Tree - fell into line | 990 | 339382 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145044 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | FUSE | 9447 | 20241214 | 445 | 2652959 | 556 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7228 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145106 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | TRIP-SAVER | 3907 | 20241214 | 728 | 2654378 | 743 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 105506 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145252 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER | 1030 | 20241214 | 820 | 2655015 | 442 | Distribution Circuit | Vegetation | Tree - fell into line | 1239 | 117978 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145281 | OH | Sus | 0 | 2024 | DEC | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9351 | 20241214 | 828 | 2655156 | 536 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2680 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145638 | OH | Sus | 0 | 2024 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 61892 | 20241214 | 1025 | 2657539 | 483 | Distribution Circuit | Vegetation | Tree - fell into line | 410 | 54815 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145471 | OH | Sus | 0 | 2024 | DEC | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 22367 | 20241214 | 1157 | 2658363 | 373 | Distribution Circuit | Vegetation | Tree - bark fell into line | 18 | 6714 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145710 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | JUMPER | WIRE DOWN @ CGC#223394349585 | 20241214 | 1205 | 2660003 | 280 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 840 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145901 | OH | Sus | 0 | 2024 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 5873 | 20241214 | 1215 | 2658779 | 344 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1720 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145774 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE | 6113 | 20240204 | 404 | 2334328 | 706 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 13686 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019171 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 616 | 20240204 | 425 | 2334350 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 229 | 88805 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019124 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FULTON-1107 | 42561107 | FUSE | 13741 | 20240204 | 559 | 2334608 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5325 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019203 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 579 | 20240204 | 733 | 2337630 | 787 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 49581 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019546 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 104 | 20240301 | 2103 | 2393564 | 147 | Distribution Circuit | Vegetation | Tree - fell into line | 1571 | 219604 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036495 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 560 | 20241214 | 559 | 2653182 | 775 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 18937 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145105 | OH | Sus | 0 | 2024 | DEC | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | RECLOSER | 148 | 20241214 | 950 | 2656927 | 288 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 29088 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145418 | OH | Sus | 0 | 2024 | DEC | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE | 4131 | 20241214 | 950 | 2659444 | 684 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 16416 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145754 | OH | Sus | 0 | 2024 | DEC | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 134 | 20241214 | 1025 | 2657454 | 498 | Distribution Circuit | Vegetation | Tree - branch fell on line | 234 | 89492 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145497 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER | 696442 | 20241214 | 722 | 2654320 | 522 | Distribution Circuit | Vegetation | Tree - branch fell on line | 245 | 51210 | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0145179 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L1641 | 20241214 | 727 | 2658192 | 763 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 95375 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145303 | OH | Sus | 0 | 2024 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 1509 | 20241214 | 727 | 2659777 | 925 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 15725 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145303 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | SWITCH | 488279 | 20241214 | 756 | 2657987 | 674 | Distribution Circuit | Vegetation | Tree - fell into line | 246 | 165804 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145217 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | JUMPER | L5155 | 20241214 | 811 | 2654826 | 576 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 9216 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145406 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | Yes
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | SWITCH | L4141 | 20241214 | 824 | 2657588 | 0 | Distribution Circuit | Vegetation | Tree - fell into line | 1405 | 202039 | Overcast-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0145310 | OH | Sus | 0 | 2024 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | MARTELL-1101 | 163011101 | FUSE | L2775 | 20241214 | 841 | 2657561 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 13386 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145723 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1701 | 163451701 | OTHER | WIRE DOWN 1 N/OF CGC #319905857158 | 20241214 | 914 | 2659818 | 474 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 474 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145848 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L2049 | 20241214 | 1845 | 2660458 | 1418 | Distribution Circuit | Equipment Failure/Involved | Overhead | 118 | 167324 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146061 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 1509 | 20241214 | 2345 | 2660783 | 0 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 12597 | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0146236 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1705 | 163781705 | FUSE | 36849 | 20240204 | 1424 | 2341467 | 276 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1380 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020198 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 88393 | 20240301 | 1413 | 2392273 | 317 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 6023 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036232 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | FUSE | 20299 | 20241214 | 639 | 2653535 | 476 | Distribution Circuit | Vegetation | Tree - branch fell on line | 148 | 70448 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145243 | OH | Sus | 0 | 2024 | DEC | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 20363 | 20241214 | 645 | 2653633 | 564 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 17484 | Overcast-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0145300 | OH | Sus | 0 | 2024 | DEC | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | OTHER | WIRE DOWN C/O CRESTA & MANZINITA | 20241214 | 653 | 2653764 | 0 | Distribution Circuit | Vegetation | Tree - branch fell on line | 610 | 119910 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145263 | OH | Sus | 0 | 2024 | DEC | Yes | None | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER | 767890 | 20241214 | 739 | 2654596 | 880 | Distribution Circuit | Vegetation | Tree - fell into line | 1241 | 260047 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145203 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | FUSE | 23334 | 20241214 | 802 | 2654736 | 479 | Distribution Circuit | Equipment Failure/Involved | Overhead | 232 | 108712 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145582 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | FUSE | 796199 | 20241214 | 802 | 2658937 | 617 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 51211 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145671 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20241214 | 831 | 2655404 | 836 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 56808 | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0145295 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | FUSE | 23334 | 20241214 | 2211 | 2660707 | 1065 | Distribution Circuit | Vegetation | Tree - fell into line | 315 | 237555 | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146172 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No

## Metric 3.01
Metric 3.01: Wires Down MEDs (Distribution)
Definition | (# Events/HFTD Circuit Miles (D))*1000
2022 HFTD Circuit Miles (D) | 25270.5
2023 HFTD Circuit Miles (D) | 25059.94
2024 HFTD Circuit Miles (D) | 24878.17
2023 Target | 65.9426
Year | WD Events | WD Events/1,000 Miles
2013 | 131 | 5.1839
2014 | 443 | 17.5303
2015 | 389 | 15.3934
2016 | 181 | 7.1625
2017 | 1739 | 68.8154
2018 | 116 | 4.5903
2019 | 1405 | 55.5984
2020 | 130 | 5.1443
2021 | 277 | 10.9614
2022 | 48 | 1.8994
2023 | 257 | 10.2554
2024 | 77 | 3.0951
|  | 23.1037 | STD
|  | 19.7351 | Average
|  | 42.8388 | 1 STD
|  | 65.9426 | 2 STD

## HFTD WD MED Summary
HFTD WIRE-DOWN OUTAGE DETAILS (2013 - 2024)
DISTRIBUTION CIRCUIT & TRANSFORMER-ONLY OUTAGES
(2.5b ME Days Only)
System | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
SYSTEM | 2013 | 0 | 0 | 0 | 40 | 0 | 1 | 0 | 0 | 0 | 0 | 90 | 0 | 131
SYSTEM | 2014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 441 | 443
SYSTEM | 2015 | 0 | 285 | 0 | 1 | 0 | 5 | 7 | 0 | 0 | 2 | 0 | 89 | 389
SYSTEM | 2016 | 0 | 49 | 120 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 181
SYSTEM | 2017 | 939 | 486 | 0 | 112 | 0 | 2 | 0 | 0 | 12 | 139 | 0 | 49 | 1739
SYSTEM | 2018 | 0 | 0 | 55 | 0 | 0 | 0 | 8 | 0 | 0 | 5 | 48 | 0 | 116
SYSTEM | 2019 | 329 | 1022 | 0 | 0 | 0 | 11 | 0 | 1 | 5 | 15 | 22 | 0 | 1405
SYSTEM | 2020 | 60 | 19 | 22 | 0 | 0 | 0 | 0 | 24 | 4 | 1 | 0 | 0 | 130
SYSTEM | 2021 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 2 | 58 | 0 | 79 | 277
SYSTEM | 2022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 44 | 48
SYSTEM | 2023 | 143 | 70 | 43 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 257
SYSTEM | 2024 | 0 | 14 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 53 | 77
System | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
10-Year Averages (2014-2023) | Count of Events | 160.5 | 193.1 | 24 | 11.3 | 0 | 1.8 | 1.5 | 3.1 | 2.8 | 23.2 | 7 | 70.2 | 498.5
| Monthly Percentage | 32.2% | 38.74% | 4.814% | 2.267% | 0% | 0.3611% | 0.3009% | 0.6219% | 0.5617% | 4.654% | 1.404% | 14.08% | 100%
System | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Targets | 2024 | 21.2313 | 25.5437 | 3.1748 | 1.4948 | 0 | 0.23811 | 0.19842 | 0.41007 | 0.37039 | 3.0689 | 0.92597 | 9.2862 | 65.9426
System | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Events | 2024 | 0 | 14 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 53 | 77
Monthly Metric | 2024 | 0 | 0.56274 | 0.32157 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.080392 | 2.1304 | 3.0951
YTD Metric | 2024 | 0 | 0.56274 | 0.88431 | 0.88431 | 0.88431 | 0.88431 | 0.88431 | 0.88431 | 0.88431 | 0.88431 | 0.9647 | 3.0951

## OH Dlines in HFTD
Source: Extracted from EDGIS as of 1/1/2024.
CIRCUITNAME | CIRCUITID | TOTALMILES | T3MILES | T2MILES | Z1MILES | T1MILES
18TH STREET 0401 | 22390401 | 1.28 |  |  |  | 1.28
18TH STREET 0402 | 22390402 | 1.82 |  |  |  | 1.82
21ST AVENUE 0401 | 22550401 | 1.91 |  |  |  | 1.91
21ST AVENUE 0402 | 22550402 | 3.34 |  |  |  | 3.34
21ST AVENUE 0403 | 22550403 | 1.9 |  |  |  | 1.9
6TH AVENUE 0401 | 22530401 | 1.27 |  |  |  | 1.27
6TH AVENUE 0402 | 22530402 | 1.21 |  |  |  | 1.21
6TH AVENUE 0403 | 22530403 | 1.79 |  |  |  | 1.79
7TH STANDARD 2101 | 254582101 | 2.58 |  |  |  | 2.58
7TH STANDARD 2102 | 254582102 | 16.91 |  |  |  | 16.91
7TH STANDARD 2103 | 254582103 | 22.47 |  |  |  | 22.47
7TH STANDARD 2104 | 254582104 | 0.04 |  |  |  | 0.04
8TH AVENUE 0401 | 12670401 | 4.92 |  |  |  | 4.92
ACTON 0401 | 22470401 | 3.88 |  |  |  | 3.88
ACTON 0402 | 22470402 | 4.47 |  |  |  | 4.47
AIRWAYS 1101 | 252041101 | 1.11 |  |  |  | 1.11
AIRWAYS 1102 | 252041102 | 7.59 |  |  |  | 7.59
AIRWAYS 1103 | 252041103 | 7.67 |  |  |  | 7.67
AIRWAYS 1104 | 252041104 | 1.77 |  |  |  | 1.77
AIRWAYS 1105 | 252041105 | 1.37 |  |  |  | 1.37
AIRWAYS 1106 | 252041106 | 7.66 |  |  |  | 7.66
AIRWAYS 1107 | 252041107 | 43.72 |  |  |  | 43.72
AIRWAYS 1108 | 252041108 | 11.68 |  |  |  | 11.68
ALHAMBRA 1101 | 14101101 | 8.41 |  |  |  | 8.41
ALHAMBRA 1102 | 14101102 | 14.19 |  | 0.13 |  | 14.06
ALHAMBRA 1105 | 14101105 | 44.8 | 0.85 | 36.58 |  | 7.37
ALLEGHANY 1101 | 152101101 | 76.31 | 31.65 | 27.11 | 7.07 | 10.48
ALLEGHANY 1102 | 152101102 | 17.69 | 17.69 |  |  | 0
ALMADEN 1101 | 82311101 | 18.43 |  |  |  | 18.43
ALMADEN 1102 | 82311102 | 21.92 |  |  |  | 21.92
ALMADEN 1110 | 82311110 | 8.5 |  |  |  | 8.5
ALMADEN 1111 | 82311111 | 9.82 |  |  |  | 9.82
ALPAUGH 1103 | 254001103 | 26.68 |  |  |  | 26.68
ALPAUGH 1104 | 254001104 | 55.93 |  |  |  | 55.93
ALPAUGH 1106 | 254001106 | 52.47 |  |  |  | 52.47
ALPINE 1101 | 163561101 | 0.87 |  |  |  | 0.87
ALTO 1120 | 42031120 | 20.43 |  | 3.89 |  | 16.54
ALTO 1121 | 42031121 | 15.4 |  |  | 0.34 | 15.06
ALTO 1122 | 42031122 | 22.39 | 9.15 | 3.72 | 0.18 | 9.34
ALTO 1123 | 42031123 | 10.36 |  | 0.47 |  | 9.89
ALTO 1124 | 42031124 | 35.04 | 27.97 |  |  | 7.07
ALTO 1125 | 42031125 | 44.87 | 26.4 | 10.98 |  | 7.49
AMES 1101 | 83901101 | 0.12 |  |  |  | 0.12
AMES 1102 | 83901102 | 3.3 |  |  |  | 3.3
ANDERSON 1101 | 103261101 | 19.99 |  | 10.93 |  | 9.06
ANDERSON 1102 | 103261102 | 3.29 |  |  |  | 3.29
ANDERSON 1103 | 103261103 | 28.38 |  | 4.86 |  | 23.52
ANGIOLA 1102 | 252151102 | 35.84 |  |  |  | 35.84
ANGIOLA 1103 | 252151103 | 45.62 |  |  |  | 45.62
ANGIOLA 1104 | 252151104 | 19.63 |  |  |  | 19.63
ANITA 1101 | 102841101 | 34.52 |  |  |  | 34.52
ANITA 1102 | 102841102 | 34.84 |  |  |  | 34.84
ANITA 1105 | 102841105 | 16.85 |  |  |  | 16.85
ANITA 1106 | 102841106 | 90.58 |  | 0.48 |  | 90.1
ANNAPOLIS 1101 | 42861101 | 51 |  | 51 |  | 0
ANTELOPE 1101 | 252021101 | 40.48 |  | 0.92 |  | 39.56
ANTELOPE 1102 | 252021102 | 25.34 |  |  |  | 25.34
ANTLER 1101 | 103271101 | 61.17 | 8.17 | 51.9 |  | 1.1
APPLE HILL 1103 | 153661103 | 59.83 | 14.79 | 35.1 |  | 9.94
APPLE HILL 1104 | 153661104 | 95.4 | 55.38 | 35.39 |  | 4.63
APPLE HILL 2102 | 153662102 | 364.69 | 123.29 | 228.62 |  | 12.78
ARANA 0401 | 83010401 | 3.49 |  |  |  | 3.49
ARANA 0402 | 83010402 | 2.99 |  |  |  | 2.99
ARBUCKLE 1101 | 62081101 | 60.06 |  |  |  | 60.06
ARBUCKLE 1102 | 62081102 | 59.15 |  |  |  | 59.15
ARBUCKLE 1103 | 62081103 | 0.04 |  |  |  | 0.04
ARBUCKLE 1104 | 62081104 | 56.63 |  |  |  | 56.63
ARCATA 1105 | 192021105 | 44.02 |  |  |  | 44.02
ARCATA 1106 | 192021106 | 10.27 |  |  |  | 10.27
ARCATA 1121 | 192021121 | 29.05 |  | 6.84 |  | 22.21
ARCATA 1122 | 192021122 | 68.17 |  | 20.45 |  | 47.72
ARCATA 1123 | 192021123 | 5.99 |  |  |  | 5.99
ARCATA 1124 | 192021124 | 0 |  |  |  | 0
ARLINGTON 0401 | 13700401 | 4.18 |  | 0.94 |  | 3.24
ARVIN 1101 | 253801101 | 27.63 |  | 0.1 |  | 27.53
ARVIN 1102 | 253801102 | 17.54 |  |  |  | 17.54
ARVIN 1103 | 253801103 | 20.62 |  |  |  | 20.62
ASHLAN AVE 1102 | 252051102 | 13.28 |  |  |  | 13.28
ASHLAN AVE 1103 | 252051103 | 9.33 |  |  |  | 9.33
ASHLAN AVE 1104 | 252051104 | 13.91 |  |  |  | 13.91
ASHLAN AVE 1106 | 252051106 | 17.1 |  |  |  | 17.1
ASHLAN AVE 1107 | 252051107 | 8.35 |  |  |  | 8.35
ASHLAN AVE 1108 | 252051108 | 11.14 |  |  |  | 11.14
ASHLAN AVE 1109 | 252051109 | 14.67 |  |  |  | 14.67
ASHLAN AVE 1111 | 252051111 | 7.96 |  |  |  | 7.96
ASHLAN AVE 1112 | 252051112 | 9.19 |  |  |  | 9.19
ASHLAN AVE 1113 | 252051113 | 9.86 |  |  |  | 9.86
ASHLAN AVE 1114 | 252051114 | 8.39 |  |  |  | 8.39
ASHLAN AVE 1116 | 252051116 | 19.15 |  |  |  | 19.15
ASHLAN AVE 2101 | 252052101 | 2.23 |  |  |  | 2.23
ASHLAN AVE 2105 | 252052105 | 16.4 |  |  |  | 16.4
ASHLAN AVE 2110 | 252052110 | 6.75 |  |  |  | 6.75
ASHLAN AVE 2115 | 252052115 | 5.53 |  |  |  | 5.53
ASHLAN AVE 2117 | 252052117 | 1.88 |  |  |  | 1.88
ASHLAN AVE 2118 | 252052118 | 9.58 |  |  |  | 9.58
ASHLAN AVE 2119 | 252052119 | 14.09 |  |  |  | 14.09
ATASCADERO 1101 | 182541101 | 33.56 | 0.79 | 16.93 |  | 15.84
ATASCADERO 1102 | 182541102 | 17.45 |  | 3.41 |  | 14.04
ATASCADERO 1103 | 182541103 | 127.93 | 37.15 | 56.1 |  | 34.68
ATWATER 1102 | 253611102 | 84.6 |  |  |  | 84.6
ATWATER 1103 | 253611103 | 23.23 |  |  |  | 23.23
ATWATER 1104 | 253611104 | 12.93 |  |  |  | 12.93
ATWATER 1105 | 253611105 | 6.84 |  |  |  | 6.84
ATWATER 1106 | 253611106 | 36.75 |  |  |  | 36.75
ATWATER 1107 | 253611107 | 30.46 |  |  |  | 30.46
ATWATER 1108 | 253611108 | 61.1 |  |  |  | 61.1
AUBERRY 1101 | 254151101 | 241.42 | 32.39 | 206.66 |  | 2.37
AUBERRY 1102 | 254151102 | 129.09 |  | 129.09 |  | 0
AUBURN 1101 | 152161101 | 4.93 |  | 3.14 |  | 1.79
AUBURN 1102 | 152161102 | 8.95 |  | 2.96 |  | 5.99
AVENA 1701 | 163571701 | 90.85 |  |  |  | 90.85
AVENA 1702 | 163571702 | 80.44 |  |  |  | 80.44
AVENAL 2101 | 255002101 | 68.53 |  |  |  | 68.53
AVENAL 2102 | 255002102 | 2.46 |  |  |  | 2.46
AVENAL 2103 | 255002103 | 2.45 |  |  |  | 2.45
BABEL 0401 | 13850401 | 3.09 |  |  |  | 3.09
BAHIA 1101 | 43251101 | 3.06 |  |  |  | 3.06
BAHIA 1102 | 43251102 | 14.22 |  |  |  | 14.22
BAHIA 1103 | 43251103 | 11.07 |  |  |  | 11.07
BAHIA 1104 | 43251104 | 18.34 |  |  |  | 18.34
BAHIA 1105 | 43251105 | 14.07 |  |  |  | 14.07
BAIR 1103 | 24261103 | 0.53 |  |  |  | 0.53
BAIR 1105 | 24261105 | 2.23 |  |  |  | 2.23
BAKERSFIELD 1101 | 253371101 | 7.46 |  |  |  | 7.46
BAKERSFIELD 1102 | 253371102 | 17.7 |  |  |  | 17.7
BAKERSFIELD 1105 | 253371105 | 6.48 |  |  |  | 6.48
BAKERSFIELD 1106 | 253371106 | 11.83 |  |  |  | 11.83
BAKERSFIELD 1107 | 253371107 | 3.69 |  |  |  | 3.69
BAKERSFIELD 1110 | 253371110 | 5.97 |  |  |  | 5.97
BAKERSFIELD 1114 | 253371114 | 15.8 |  |  |  | 15.8
BAKERSFIELD 1115 | 253371115 | 5.7 |  |  |  | 5.7
BAKERSFIELD 1116 | 253371116 | 16.82 |  |  |  | 16.82
BAKERSFIELD 1118 | 253371118 | 11.45 |  |  |  | 11.45
BAKERSFIELD 2104 | 253372104 | 37.65 |  |  |  | 37.65
BAKERSFIELD 2106 | 253372106 | 31.56 |  |  |  | 31.56
BAKERSFIELD 2107 | 253372107 | 0 |  |  |  | 0
BAKERSFIELD 2109 | 253372109 | 27.53 |  |  |  | 27.53
BALCH NO 1 1101 | 252501101 | 14.56 |  | 14.56 |  | 0
BALFOUR 1101 | 14321101 | 50.03 |  |  |  | 50.03
BANCROFT 0401 | 13030401 | 8.43 |  | 0 |  | 8.43
BANCROFT 0402 | 13030402 | 4.59 |  | 0.12 |  | 4.47
BANGOR 1101 | 103191101 | 197.64 | 1.73 | 187.68 |  | 8.23
BANTA 1101 | 162471101 | 32.96 |  |  |  | 32.96
BANTA 1102 | 162471102 | 15.35 |  |  |  | 15.35
BANTA 1103 | 162471103 | 60.49 |  |  |  | 60.49
BARRETT 0401 | 13020401 | 6.63 |  |  |  | 6.63
BARRETT 0402 | 13020402 | 5.97 |  |  |  | 5.97
BARRY 1101 | 152111101 | 32.05 |  |  |  | 32.05
BARRY 1102 | 152111102 | 17.82 |  |  |  | 17.82
BARRY 1103 | 152111103 | 33.13 |  |  |  | 33.13
BARTON 1101 | 253571101 | 6 |  |  |  | 6
BARTON 1102 | 253571102 | 5.6 |  |  |  | 5.6
BARTON 1104 | 253571104 | 9.4 |  |  |  | 9.4
BARTON 1105 | 253571105 | 4.79 |  |  |  | 4.79
BARTON 1106 | 253571106 | 5.96 |  |  |  | 5.96
BARTON 1108 | 253571108 | 19.07 |  |  |  | 19.07
BARTON 1109 | 253571109 | 4.48 |  |  |  | 4.48
BARTON 1110 | 253571110 | 16.48 |  |  |  | 16.48
BARTON 1111 | 253571111 | 15.67 |  |  |  | 15.67
BARTON 1112 | 253571112 | 3.35 |  |  |  | 3.35
BARTON 1114 | 253571114 | 12.87 |  |  |  | 12.87
BARTON 1115 | 253571115 | 13.02 |  |  |  | 13.02
BARTON 1116 | 253571116 | 8.26 |  |  |  | 8.26
BASALT 1101 | 42461101 | 10.86 |  |  |  | 10.86
BASALT 1104 | 42461104 | 0.67 |  |  |  | 0.67
BASALT 1105 | 42461105 | 1.59 |  |  |  | 1.59
BASALT 1106 | 42461106 | 69.16 |  | 2.01 |  | 67.15
BAY MEADOWS 1102 | 24011102 | 4.99 |  |  |  | 4.99
BAY MEADOWS 1103 | 24011103 | 6.88 |  |  |  | 6.88
BAY MEADOWS 1104 | 24011104 | 16.81 |  |  |  | 16.81
BAY MEADOWS 1105 | 24011105 | 6.68 |  |  |  | 6.68
BAY MEADOWS 1106 | 24011106 | 0.86 |  |  |  | 0.86
BAY MEADOWS 1107 | 24011107 | 3.18 |  |  |  | 3.18
BAY MEADOWS 1108 | 24011108 | 1.05 |  |  |  | 1.05
BAY MEADOWS 2101 | 24012101 | 17.96 |  |  |  | 17.96
BAY MEADOWS 2102 | 24012102 | 14.32 |  | 3.99 |  | 10.33
BAY MEADOWS 2103 | 24012103 | 0 |  |  |  | 0
BAYWOOD 1101 | 182801101 | 29.03 |  | 3.37 |  | 25.66
BEACH (Q) 0402 | 22340402 | 2.03 |  |  |  | 2.03
BEAR VALLEY 2101 | 252192101 | 167.05 |  | 100.93 |  | 66.12
BEAR VALLEY 2105 | 252192105 | 157.22 | 7.51 | 149.71 |  | 0
BECK STREET 0401 | 12640401 | 1.59 |  |  |  | 1.59
BELL 1107 | 152701107 | 50.55 |  | 42.65 |  | 7.9
BELL 1108 | 152701108 | 66.72 |  | 54.77 |  | 11.95
BELL 1109 | 152701109 | 18.1 |  | 13.97 |  | 4.13
BELL 1110 | 152701110 | 11.24 |  | 0.16 |  | 11.08
BELLE HAVEN 0401 | 24020401 | 9.44 |  |  |  | 9.44
BELLE HAVEN 0402 | 24020402 | 4.69 |  |  |  | 4.69
BELLE HAVEN 0403 | 24020403 | 5.53 |  |  |  | 5.53
BELLE HAVEN 0404 | 24020404 | 8.66 |  |  |  | 8.66
BELLE HAVEN 0405 | 24020405 | 7.4 |  |  |  | 7.4
BELLE HAVEN 0406 | 24020406 | 9.32 |  |  |  | 9.32
BELLE HAVEN 0407 | 24020407 | 6.36 |  |  |  | 6.36
BELLE HAVEN 0408 | 24020408 | 5.2 |  |  |  | 5.2
BELLE HAVEN 0409 | 24020409 | 3.64 |  |  |  | 3.64
BELLE HAVEN 1101 | 24021101 | 1.59 |  |  |  | 1.59
BELLE HAVEN 1102 | 24021102 | 1.63 |  |  |  | 1.63
BELLE HAVEN 1103 | 24021103 | 1.85 |  |  |  | 1.85
BELLE HAVEN 1104 | 24021104 | 5.69 |  |  |  | 5.69
BELLE HAVEN 1105 | 24021105 | 10.58 |  |  |  | 10.58
BELLE HAVEN 1106 | 24021106 | 15.66 |  |  |  | 15.66
BELLE HAVEN 1107 | 24021107 | 1.27 |  |  |  | 1.27
BELLEVUE 1102 | 43181102 | 62.99 |  | 0.16 |  | 62.83
BELLEVUE 1104 | 43181104 | 12.5 |  |  |  | 12.5
BELLEVUE 2101 | 43182101 | 66.02 | 7.03 | 19.04 |  | 39.95
BELLEVUE 2103 | 43182103 | 5.71 |  |  |  | 5.71
BELLEVUE 2105 | 43182105 | 4.02 |  |  |  | 4.02
BELLEVUE 2107 | 43182107 | 11.35 |  |  |  | 11.35
BELMONT 0401 | 24030401 | 5.91 |  |  |  | 5.91
BELMONT 0402 | 24030402 | 7 |  |  |  | 7
BELMONT 0403 | 24030403 | 4.65 |  |  |  | 4.65
BELMONT 0406 | 24030406 | 5.03 |  |  |  | 5.03
BELMONT 1102 | 24031102 | 15.22 |  |  |  | 15.22
BELMONT 1103 | 24031103 | 18.67 |  | 3.38 |  | 15.29
BELMONT 1104 | 24031104 | 7.05 |  |  |  | 7.05
BELMONT 1105 | 24031105 | 0.64 |  |  |  | 0.64
BELMONT 1106 | 24031106 | 1.64 |  |  |  | 1.64
BELMONT 1107 | 24031107 | 0.97 |  |  |  | 0.97
BELMONT 1110 | 24031110 | 24.28 |  | 0.11 |  | 24.17
BELRIDGE 1A 1101 | 254371101 | 0.09 |  |  |  | 0.09
BELRIDGE 1B 1101 | 254381101 | 0.01 |  |  |  | 0.01
BEN LOMOND 0401 | 83040401 | 23.09 | 23.09 |  |  | 0
BEN LOMOND 1101 | 83041101 | 15.16 | 15.16 |  |  | 0
BERESFORD 0401 | 24040401 | 1.09 |  |  |  | 1.09
BERESFORD 0402 | 24040402 | 2.38 |  |  |  | 2.38
BERESFORD 0403 | 24040403 | 12.22 |  | 5.4 |  | 6.82
BERESFORD 0404 | 24040404 | 5.78 |  |  |  | 5.78
BERKELEY F 0401 | 12060401 | 0 |  |  |  | 0
BERKELEY F 0402 | 12060402 | 2.14 |  | 0.14 |  | 2
BERKELEY F 0403 | 12060403 | 2.19 |  |  |  | 2.19
BERKELEY F 0404 | 12060404 | 3.72 |  |  |  | 3.72
BERKELEY F 0405 | 12060405 | 0.97 |  |  |  | 0.97
BERKELEY F 0406 | 12060406 | 3.86 |  |  |  | 3.86
BERKELEY F 0407 | 12060407 | 0 |  |  |  | 0
BERKELEY F 0408 | 12060408 | 0.8 |  |  |  | 0.8
BERKELEY F 0409 | 12060409 | 3.66 |  |  |  | 3.66
BERKELEY F 0410 | 12060410 | 2.91 |  |  |  | 2.91
BERKELEY F 0411 | 12060411 | 4.46 |  |  |  | 4.46
BERKELEY F 1102 | 12061102 | 0.28 |  |  |  | 0.28
BERKELEY F 1103 | 12061103 | 5.27 | 1.97 |  |  | 3.3
BERKELEY F 1104 | 12061104 | 2.05 |  |  |  | 2.05
BERKELEY F 1105 | 12061105 | 11.4 |  | 1.78 |  | 9.62
BERKELEY T 0401 | 12660401 | 2.68 |  |  |  | 2.68
BERKELEY T 0402 | 12660402 | 1.36 |  |  |  | 1.36
BERKELEY T 0403 | 12660403 | 0.87 |  |  |  | 0.87
BERKELEY T 0404 | 12660404 | 0.35 |  |  |  | 0.35
BERRENDA A 1101 | 254261101 | 0.02 |  |  |  | 0.02
BERRENDA C 0401 | 254480401 | 0.02 |  |  |  | 0.02
BETHEL BANK 0401 | 18150401 | 0.78 |  |  |  | 0.78
BIG BASIN 1101 | 82841101 | 55.12 | 55.12 |  |  | 0
BIG BASIN 1102 | 82841102 | 63.73 | 60.69 | 3.04 |  | 0
BIG BEND 1101 | 103751101 | 56.94 | 42.43 | 14.51 |  | 0
BIG BEND 1102 | 103751102 | 18.18 | 18.07 |  |  | 0.11
BIG MEADOWS 2101 | 102812101 | 139.52 |  | 85.08 |  | 54.44
BIG RIVER 1101 | 43081101 | 86 |  | 70.01 |  | 15.99
BIOLA 1101 | 252211101 | 90.23 |  |  |  | 90.23
BIOLA 1102 | 252211102 | 32.42 |  |  |  | 32.42
BIOLA 1103 | 252211103 | 80.27 |  |  |  | 80.27
BIOLA 1104 | 252211104 | 50.19 |  |  |  | 50.19
BLACKWELL 1102 | 254681102 | 30.42 |  |  |  | 30.42
BLACKWELL 2101 | 254682101 | 22.77 |  |  |  | 22.77
BLUE LAKE 1101 | 192181101 | 7.32 |  |  | 0.31 | 7.01
BLUE LAKE 1102 | 192181102 | 68.86 |  |  | 0.02 | 68.84
BOGARD 1101 | 103301101 | 0.51 |  | 0.51 |  | 0
BOGUE 1102 | 153781102 | 17.88 |  |  |  | 17.88
BOGUE 1103 | 153781103 | 16.24 |  |  |  | 16.24
BOGUE 1104 | 153781104 | 8.69 |  |  |  | 8.69
BOGUE 1105 | 153781105 | 10.51 |  |  |  | 10.51
BOGUE 1106 | 153781106 | 28.18 |  |  |  | 28.18
BOGUE 1107 | 153781107 | 15.83 |  |  |  | 15.83
BOGUE 1108 | 153781108 | 32.65 |  |  |  | 32.65
BOLINAS 1101 | 42261101 | 51.67 | 27.2 | 7.49 |  | 16.98
BOLTHOUSE FARMS 1101 | 258181101 | 0.02 |  |  |  | 0.02
BONITA 1101 | 255391101 | 59.36 |  |  |  | 59.36
BONITA 1102 | 255391102 | 30.59 |  |  |  | 30.59
BONITA 1103 | 255391103 | 39.3 |  |  |  | 39.3
BONNIE NOOK 1101 | 152301101 | 14.47 | 14.47 |  |  | 0
BONNIE NOOK 1102 | 152301102 | 34.05 | 34.05 |  |  | 0
BONNIE NOOK 1103 | 152301103 | 0.33 | 0.33 |  |  | 0
BORDEN 1101 | 255121101 | 68.21 |  |  |  | 68.21
BORDEN 1102 | 255121102 | 22.98 |  |  |  | 22.98
BORDEN 1103 | 255121103 | 86.3 |  |  |  | 86.3
BORONDA 1101 | 182461101 | 7.95 |  |  |  | 7.95
BORONDA 1102 | 182461102 | 4.35 |  |  |  | 4.35
BOWLES 1101 | 253531101 | 69.27 |  |  |  | 69.27
BOWLES 1102 | 253531102 | 33.35 |  |  |  | 33.35
BOWLES 1103 | 253531103 | 26.75 |  |  |  | 26.75
BOWLES 1104 | 253531104 | 41.66 |  |  |  | 41.66
BRENTWOOD 2104 | 14592104 | 4.27 |  |  |  | 4.27
BRENTWOOD 2105 | 14592105 | 79.11 |  | 10.38 |  | 68.73
BRENTWOOD 2106 | 14592106 | 5.72 |  |  |  | 5.72
BRENTWOOD 2108 | 14592108 | 6.1 |  |  |  | 6.1
BRENTWOOD 2109 | 14592109 | 1.28 |  |  |  | 1.28
BRENTWOOD 2110 | 14592110 | 3.44 |  |  |  | 3.44
BRENTWOOD 2111 | 14592111 | 7.33 |  |  |  | 7.33
BRENTWOOD 2112 | 14592112 | 94.47 |  |  |  | 94.47
BRENTWOOD 2113 | 14592113 | 8.18 |  |  |  | 8.18
BRIDGEVILLE 1101 | 192461101 | 24.81 | 4.67 | 17.9 |  | 2.24
BRIDGEVILLE 1102 | 192461102 | 43.31 | 20.65 | 10.34 |  | 12.32
BRITTON 1104 | 83611104 | 1.19 |  |  |  | 1.19
BRITTON 1105 | 83611105 | 4.96 |  |  |  | 4.96
BRITTON 1106 | 83611106 | 3.78 |  |  |  | 3.78
BRITTON 1107 | 83611107 | 5.47 |  |  |  | 5.47
BRITTON 1108 | 83611108 | 1.73 |  |  |  | 1.73
BRITTON 1109 | 83611109 | 2.44 |  |  |  | 2.44
BRITTON 1110 | 83611110 | 11.68 |  |  |  | 11.68
BRITTON 1111 | 83611111 | 1.26 |  |  |  | 1.26
BRITTON 1112 | 83611112 | 1.84 |  |  |  | 1.84
BRITTON 1113 | 83611113 | 1.35 |  |  |  | 1.35
BRITTON 1114 | 83611114 | 5.03 |  |  |  | 5.03
BRITTON 1115 | 83611115 | 1.12 |  |  |  | 1.12
BROOKSIDE 0401 | 13210401 | 3.69 |  |  |  | 3.69
BROWNS VALLEY 1101 | 152921101 | 66.5 |  | 44.24 |  | 22.26
BRUNSWICK 1102 | 152481102 | 54.35 | 47.05 | 4.71 |  | 2.59
BRUNSWICK 1103 | 152481103 | 66.13 | 40.54 | 17.97 |  | 7.62
BRUNSWICK 1104 | 152481104 | 58.06 | 26.28 | 29.76 |  | 2.02
BRUNSWICK 1105 | 152481105 | 118.48 | 114.03 | 4.2 |  | 0.25
BRUNSWICK 1106 | 152481106 | 172.65 | 114.24 | 48.9 |  | 9.51
BRUNSWICK 1107 | 152481107 | 19.55 | 3.12 | 5.72 |  | 10.71
BRUNSWICK 1110 | 152481110 | 32.91 |  | 22.82 |  | 10.09
BUCKS CREEK 1102 | 102211102 | 0.03 | 0.03 |  |  | 0
BUCKS CREEK 1103 | 102211103 | 12.88 | 9.91 | 2.67 |  | 0.3
BUELLTON 1101 | 183041101 | 104.38 | 4.82 | 72.66 |  | 26.9
BUELLTON 1102 | 183041102 | 28.26 |  | 16.05 |  | 12.21
BUENA VISTA 1101 | 182261101 | 0.71 |  |  |  | 0.71
BUENA VISTA 1102 | 182261102 | 11.15 |  |  |  | 11.15
BUENA VISTA 1103 | 182261103 | 7.6 |  |  |  | 7.6
BUENA VISTA 1104 | 182261104 | 3.98 |  |  |  | 3.98
BUENA VISTA 1106 | 182261106 | 12.95 |  |  |  | 12.95
BULLARD 1101 | 253961101 | 14.39 |  |  |  | 14.39
BULLARD 1102 | 253961102 | 4.05 |  |  |  | 4.05
BULLARD 1103 | 253961103 | 8.16 |  |  |  | 8.16
BULLARD 1104 | 253961104 | 8.06 |  |  |  | 8.06
BULLARD 1105 | 253961105 | 3.47 |  |  |  | 3.47
BULLARD 1106 | 253961106 | 3.69 |  |  |  | 3.69
BULLARD 1107 | 253961107 | 2.42 |  |  |  | 2.42
BULLARD 1108 | 253961108 | 1.63 |  |  |  | 1.63
BULLARD 1109 | 253961109 | 5.43 |  |  |  | 5.43
BULLARD 1110 | 253961110 | 4.23 |  |  |  | 4.23
BULLARD 1113 | 253961113 | 5.24 |  |  |  | 5.24
BULLARD 2111 | 253962111 | 4.45 |  |  |  | 4.45
BULLARD 2112 | 253962112 | 11.14 |  |  |  | 11.14
BULLARD 2114 | 253962114 | 4.96 |  |  |  | 4.96
BURLINGAME 0401 | 24050401 | 3.18 |  |  |  | 3.18
BURLINGAME 0402 | 24050402 | 5.89 |  |  |  | 5.89
BURLINGAME 0403 | 24050403 | 3.93 |  |  |  | 3.93
BURLINGAME 0404 | 24050404 | 4.02 |  |  |  | 4.02
BURLINGAME 0405 | 24050405 | 3.31 |  |  |  | 3.31
BURLINGAME 2101 | 24052101 | 6.83 |  |  |  | 6.83
BURNEY 1101 | 103311101 | 49.69 |  | 40.82 |  | 8.87
BURNEY 1102 | 103311102 | 4.09 |  | 0.65 |  | 3.44
BURNS 2101 | 183582101 | 29.1 | 29.1 |  |  | 0
BUTTE 1103 | 103081103 | 60.58 |  |  |  | 60.58
BUTTE 1104 | 103081104 | 52.09 |  |  |  | 52.09
BUTTE 1105 | 103081105 | 37.87 | 26.69 | 3.43 |  | 7.75
BUTTE 1106 | 103081106 | 11.92 |  |  |  | 11.92
BUTTE 1107 | 103081107 | 109.6 |  |  |  | 109.6
CABRILLO 1103 | 183101103 | 101.98 |  | 57.32 |  | 44.66
CABRILLO 1104 | 183101104 | 75.86 |  | 30.03 |  | 45.83
CADET 1101 | 254821101 | 0.03 |  |  |  | 0.03
CAL WATER 1102 | 255451102 | 26.43 |  | 3.72 |  | 22.71
CAL WATER 1103 | 255451103 | 7.96 |  |  |  | 7.96
CALAVERAS CEMENT 1101 | 162211101 | 242.92 | 7.78 | 218.35 |  | 16.79
CALFLAX 1101 | 253441101 | 27.48 |  |  |  | 27.48
CALFLAX 1102 | 253441102 | 20.45 |  |  |  | 20.45
CALFLAX 1103 | 253441103 | 29.01 |  |  |  | 29.01
CALFLAX 1104 | 253441104 | 18.62 |  |  |  | 18.62
CALIFORNIA AVE 1102 | 252281102 | 11.47 |  |  |  | 11.47
CALIFORNIA AVE 1103 | 252281103 | 7.74 |  |  |  | 7.74
CALIFORNIA AVE 1104 | 252281104 | 4.76 |  |  |  | 4.76
CALIFORNIA AVE 1106 | 252281106 | 9.83 |  |  |  | 9.83
CALIFORNIA AVE 1108 | 252281108 | 9.57 |  |  |  | 9.57
CALIFORNIA AVE 1110 | 252281110 | 11.12 |  |  |  | 11.12
CALIFORNIA AVE 1111 | 252281111 | 6.78 |  |  |  | 6.78
CALIFORNIA AVE 1112 | 252281112 | 4.93 |  |  |  | 4.93
CALIFORNIA AVE 1113 | 252281113 | 6.52 |  |  |  | 6.52
CALIFORNIA AVE 1114 | 252281114 | 19.45 |  |  |  | 19.45
CALIFORNIA AVE 1116 | 252281116 | 11.79 |  |  |  | 11.79
CALIFORNIA AVE 1117 | 252281117 | 1.27 |  |  |  | 1.27
CALISTOGA 1101 | 42711101 | 115.2 | 82.93 | 15.46 |  | 16.81
CALISTOGA 1102 | 42711102 | 45.63 | 22.29 | 1.54 |  | 21.8
CALPELLA 1101 | 43411101 | 101.44 | 4.03 | 78.01 |  | 19.4
CALPELLA 1102 | 43411102 | 7.55 |  | 1.79 |  | 5.76
CALPINE 1144 | 48011144 | 29.57 | 27.36 | 2.22 |  | -0.01
CALPINE 1146 | 48011146 | 5.61 | 5.61 |  |  | 0
CAMDEN 1102 | 252301102 | 40.21 |  |  |  | 40.21
CAMDEN 1103 | 252301103 | 127.81 |  |  |  | 127.81
CAMDEN 1104 | 252301104 | 77.5 |  |  |  | 77.5
CAMDEN 1105 | 252301105 | 58.77 |  |  |  | 58.77
CAMP EVERS 2103 | 83622103 | 61.32 | 44.88 | 0.83 |  | 15.61
CAMP EVERS 2104 | 83622104 | 36.54 | 26.69 | 0.58 |  | 9.27
CAMP EVERS 2105 | 83622105 | 78.58 | 73.57 | 2.12 |  | 2.89
CAMP EVERS 2106 | 83622106 | 145.85 | 132.89 | 2.99 |  | 9.97
CAMPHORA 0401 | 182070401 | 0.43 |  |  |  | 0.43
CAMPHORA 1101 | 182071101 | 51.87 |  | 3.88 |  | 47.99
CANAL 1101 | 252091101 | 47.07 |  |  |  | 47.07
CANAL 1102 | 252091102 | 15.37 |  |  |  | 15.37
CANAL 1103 | 252091103 | 53.72 |  |  |  | 53.72
CANAL 1104 | 252091104 | 10.57 |  |  |  | 10.57
CANAL 1105 | 252091105 | 16.78 |  |  |  | 16.78
CANAL 1106 | 252091106 | 7.89 |  |  |  | 7.89
CANTUA 1101 | 253591101 | 24.07 |  |  |  | 24.07
CANTUA 1102 | 253591102 | 47.77 |  |  |  | 47.77
CANTUA 1103 | 253591103 | 35.78 |  |  |  | 35.78
CANTUA 1104 | 253591104 | 0.17 |  |  |  | 0.17
CANTUA 1105 | 253591105 | 15.13 |  |  |  | 15.13
CANTUA 1106 | 253591106 | 0.16 |  |  |  | 0.16
CAPAY 1101 | 102111101 | 48.88 |  |  |  | 48.88
CAPAY 1102 | 102111102 | 74.57 |  |  |  | 74.57
CARLOTTA 1121 | 192291121 | 52.07 |  | 21.12 |  | 30.95
CARNATION 2101 | 255282101 | 0.01 |  |  |  | 0.01
CARNERAS 1102 | 252321102 | 16.82 |  |  |  | 16.82
CARNERAS 1103 | 252321103 | 41.57 |  |  |  | 41.57
CAROLANDS 0401 | 24060401 | 4.56 |  |  |  | 4.56
CAROLANDS 0402 | 24060402 | 0.03 |  |  |  | 0.03
CAROLANDS 0403 | 24060403 | 13.35 |  |  |  | 13.35
CAROLANDS 0404 | 24060404 | 10.23 |  | 4.17 |  | 6.06
CARQUINEZ 1103 | 43281103 | 14.78 |  |  |  | 14.78
CARQUINEZ 1104 | 43281104 | 0.38 |  |  |  | 0.38
CARQUINEZ 1105 | 43281105 | 5.7 |  |  |  | 5.7
CARRIZO PLAINS 1101 | 253461101 | 106.2 |  |  |  | 106.2
CARUTHERS 1101 | 252371101 | 82.02 |  |  |  | 82.02
CARUTHERS 1102 | 252371102 | 69.74 |  |  |  | 69.74
CARUTHERS 1104 | 252371104 | 80.66 |  |  |  | 80.66
CARUTHERS 1105 | 252371105 | 56.49 |  |  |  | 56.49
CASSERLY 0401 | 83110401 | 3.08 |  |  |  | 3.08
CASSIDY 2107 | 254272107 | 59.51 |  |  |  | 59.51
CASSIDY 2108 | 254272108 | 33.65 |  |  |  | 33.65
CASTRO 0401 | 22480401 | 2.94 |  |  |  | 2.94
CASTRO 0402 | 22480402 | 2.63 |  |  |  | 2.63
CASTRO VALLEY 1102 | 14091102 | 22.12 |  | 1.15 |  | 20.97
CASTRO VALLEY 1103 | 14091103 | 15.74 |  |  |  | 15.74
CASTRO VALLEY 1104 | 14091104 | 7.39 |  |  |  | 7.39
CASTRO VALLEY 1105 | 14091105 | 30.3 |  | 2.18 |  | 28.12
CASTRO VALLEY 1107 | 14091107 | 16.13 |  |  |  | 16.13
CASTRO VALLEY 1108 | 14091108 | 38.87 | 12.59 | 4.17 |  | 22.11
CASTRO VALLEY 1109 | 14091109 | 10.09 |  |  |  | 10.09
CASTRO VALLEY 1110 | 14091110 | 24.85 | 15.61 | 6.7 |  | 2.54
CASTRO VALLEY 1111 | 14091111 | 8.56 | 1.9 | 3.92 |  | 2.74
CASTROVILLE 2103 | 182352103 | 81.48 |  |  |  | 81.48
CASTROVILLE 2104 | 182352104 | 50.55 |  |  |  | 50.55
CATLETT 1101 | 153761101 | 0.03 |  |  |  | 0.03
CATLETT 1102 | 153761102 | 106.11 |  |  |  | 106.11
CATLETT 1105 | 153761105 | 54.06 |  |  |  | 54.06
CAWELO B 1101 | 252621101 | 0.01 |  |  |  | 0.01
CAWELO C 1101 | 252631101 | 0.02 |  |  |  | 0.02
CAYETANO 2109 | 14422109 | 49.6 | 12.08 | 21.65 |  | 15.87
CAYETANO 2111 | 14422111 | 12.31 |  | 5.41 |  | 6.9
CAYUCOS 1101 | 182551101 | 46.16 |  | 0.46 |  | 45.7
CAYUCOS 1102 | 182551102 | 57.39 | 9.06 | 4.99 |  | 43.34
CEDAR CREEK 1101 | 103321101 | 109.79 | 20.99 | 88.8 |  | 0
CELERON 1101 | 255271101 | 0.15 |  |  |  | 0.15
CHALLENGE 1101 | 103201101 | 48.27 | 48.04 | 0.23 |  | 0
CHALLENGE 1102 | 103201102 | 62.94 | 60.3 | 2.64 |  | 0
CHANNEL 1101 | 163071101 | 9.98 |  |  |  | 9.98
CHANNEL 1102 | 163071102 | 8.39 |  |  |  | 8.39
CHARCA 1102 | 254501102 | 60.55 |  |  |  | 60.55
CHARCA 1103 | 254501103 | 41.39 |  |  |  | 41.39
CHARCA 1106 | 254501106 | 18.23 |  |  |  | 18.23
CHEROKEE 1101 | 163651101 | 19.81 |  |  |  | 19.81
CHEROKEE 1102 | 163651102 | 36.34 |  |  |  | 36.34
CHESTER 1101 | 103181101 | 8.22 |  | 2.12 |  | 6.1
CHESTER 1102 | 103181102 | 5.32 |  | 2.31 |  | 3.01
CHICO A 0401 | 102050401 | 2.21 |  |  |  | 2.21
CHICO A 0402 | 102050402 | 5.67 |  |  |  | 5.67
CHICO A 1101 | 102051101 | 2.99 |  |  |  | 2.99
CHICO A 1102 | 102051102 | 9.36 |  |  |  | 9.36
CHICO A 1103 | 102051103 | 4.89 |  |  |  | 4.89
CHICO B 1101 | 102491101 | 4.59 |  |  |  | 4.59
CHICO B 1103 | 102491103 | 7.33 |  |  |  | 7.33
CHICO B 1105 | 102491105 | 9.67 |  |  |  | 9.67
CHICO B 1106 | 102491106 | 2.03 |  |  |  | 2.03
CHICO C 0401 | 102650401 | 2.78 |  |  |  | 2.78
CHOLAME 1101 | 182561101 | 97.28 |  |  |  | 97.28
CHOLAME 2102 | 182562102 | 215.02 |  | 59.02 |  | 156
CHOWCHILLA 1101 | 254101101 | 63.1 |  |  |  | 63.1
CHOWCHILLA 1102 | 254101102 | 13.16 |  |  |  | 13.16
CHOWCHILLA 1103 | 254101103 | 49.08 |  |  |  | 49.08
CHOWCHILLA 1104 | 254101104 | 80.35 |  |  |  | 80.35
CHOWCHILLA 1105 | 254101105 | 9.75 |  |  |  | 9.75
CHOWCHILLA 1106 | 254101106 | 54.55 |  |  |  | 54.55
CLARK ROAD 1101 | 103091101 | 0 |  |  |  | 0
CLARK ROAD 1102 | 103091102 | 122.41 | 32.85 | 76.79 |  | 12.77
CLARKSVILLE 2103 | 153612103 | 49.95 | 19.62 | 10.52 |  | 19.81
CLARKSVILLE 2104 | 153612104 | 75.67 | 41.35 | 21.7 |  | 12.62
CLARKSVILLE 2105 | 153612105 | 13.07 | 5.52 | 4.76 |  | 2.79
CLARKSVILLE 2106 | 153612106 | 1.4 |  | 0.48 |  | 0.92
CLARKSVILLE 2109 | 153612109 | 12.26 | 1.99 | 1.96 |  | 8.31
CLARKSVILLE 2110 | 153612110 | 7.84 |  |  |  | 7.84
CLAY 1101 | 163341101 | 40.63 |  | 26.37 |  | 14.26
CLAY 1102 | 163341102 | 2.04 |  | 0.82 |  | 1.22
CLAY 1103 | 163341103 | 113.09 |  | 49.85 |  | 63.24
CLAYTON 1103 | 12021103 | 4.36 |  |  |  | 4.36
CLAYTON 1104 | 12021104 | 13.44 |  |  |  | 13.44
CLAYTON 2211 | 12022211 | 10.47 |  |  |  | 10.47
CLAYTON 2212 | 12022212 | 57.29 | 27.54 | 18.68 |  | 11.07
CLAYTON 2213 | 12022213 | 4.84 |  | 2.51 |  | 2.33
CLAYTON 2214 | 12022214 | 5.93 |  |  |  | 5.93
CLAYTON 2215 | 12022215 | 29.12 | 2.92 | 3.78 |  | 22.42
CLAYTON 2216 | 12022216 | 18.77 |  |  |  | 18.77
CLAYTON 2217 | 12022217 | 19.94 |  |  |  | 19.94
CLAYTON 2218 | 12022218 | 8.35 |  |  |  | 8.35
CLEAR LAKE 1101 | 42141101 | 112.83 | 6.05 | 12.3 |  | 94.48
CLEAR LAKE 1102 | 42141102 | 36.71 |  | 3.98 |  | 32.73
CLOVERDALE 1101 | 42821101 | 36.62 |  | 24.27 |  | 12.35
CLOVERDALE 1102 | 42821102 | 104.04 | 47.27 | 28.29 |  | 28.48
CLOVIS 1101 | 254081101 | 3.98 |  |  |  | 3.98
CLOVIS 1102 | 254081102 | 24.12 |  |  |  | 24.12
CLOVIS 1103 | 254081103 | 1.96 |  |  |  | 1.96
CLOVIS 1104 | 254081104 | 0.43 |  |  |  | 0.43
CLOVIS 1105 | 254081105 | 7.74 |  |  |  | 7.74
CLOVIS 1106 | 254081106 | 5 |  |  |  | 5
CLOVIS 1107 | 254081107 | 9.87 |  |  |  | 9.87
CLOVIS 1108 | 254081108 | 12.91 |  |  |  | 12.91
CLOVIS 2109 | 254082109 | 3.89 |  |  |  | 3.89
CLOVIS 2110 | 254082110 | 11.53 |  |  |  | 11.53
CLOVIS 2111 | 254082111 | 8.76 |  |  |  | 8.76
CMC 1101 | 183111101 | 2.01 |  | 2.01 |  | 0
CMC 1102 | 183111102 | 0.49 |  | 0.49 |  | 0
COALINGA NO 1 1106 | 252161106 | 9.01 |  |  |  | 9.01
COALINGA NO 1 1107 | 252161107 | 4.04 |  |  |  | 4.04
COALINGA NO 1 1108 | 252161108 | 60 |  |  |  | 60
COALINGA NO 1 1109 | 252161109 | 26.26 |  |  |  | 26.26
COALINGA NO 2 1104 | 252381104 | 0.16 |  |  |  | 0.16
COALINGA NO 2 1105 | 252381105 | 76.43 |  |  |  | 76.43
COALINGA NO 2 1106 | 252381106 | 42.53 |  |  |  | 42.53
COALINGA NO 2 1107 | 252381107 | 38.51 |  |  |  | 38.51
COARSEGOLD 2102 | 254432102 | 73 | 58.17 | 14.83 |  | 0
COARSEGOLD 2103 | 254432103 | 122.61 |  | 93.26 |  | 29.35
COARSEGOLD 2104 | 254432104 | 264.82 | 2.83 | 243.1 |  | 18.89
COLONY 1101 | 162231101 | 29.03 |  |  |  | 29.03
COLONY 1102 | 162231102 | 47.74 |  |  |  | 47.74
COLUMBIA HILL 1101 | 152471101 | 89.72 | 72.07 | 17.65 |  | 0
COLUMBUS 1103 | 253951103 | 7.88 |  |  |  | 7.88
COLUMBUS 1104 | 253951104 | 10.25 |  |  |  | 10.25
COLUMBUS 1105 | 253951105 | 16.08 |  |  |  | 16.08
COLUMBUS 1106 | 253951106 | 14.34 |  |  |  | 14.34
COLUMBUS 1109 | 253951109 | 5.58 |  |  |  | 5.58
COLUMBUS 1110 | 253951110 | 13.21 |  |  |  | 13.21
COLUSA 1100 | 62021100 | 0.02 |  |  |  | 0.02
COLUSA 1101 | 62021101 | 112.92 |  |  |  | 112.92
COLUSA JUNCTION 1101 | 62071101 | 29.04 |  |  |  | 29.04
CONCORD NO 1 0401 | 12960401 | 4.77 |  |  |  | 4.77
CONCORD NO 1 0402 | 12960402 | 3.79 |  |  |  | 3.79
CONTRA COSTA 2103 | 13652103 | 16.38 |  |  |  | 16.38
CONTRA COSTA 2104 | 13652104 | 10.79 |  |  |  | 10.79
CONTRA COSTA 2105 | 13652105 | 14.32 |  |  |  | 14.32
CONTRA COSTA 2106 | 13652106 | 0.83 |  |  |  | 0.83
CONTRA COSTA 2107 | 13652107 | 12.76 |  |  |  | 12.76
CONTRA COSTA 2108 | 13652108 | 0.88 |  |  |  | 0.88
CONTRA COSTA 2109 | 13652109 | 13.87 |  |  |  | 13.87
CONTRA COSTA 2110 | 13652110 | 0.39 |  |  |  | 0.39
CONTRA COSTA 2112 | 13652112 | 0.04 |  |  |  | 0.04
CONTRA COSTA 2113 | 13652113 | 15.07 |  |  |  | 15.07
CONTRA COSTA 2114 | 13652114 | 1.91 |  |  |  | 1.91
CONTRA COSTA 2115 | 13652115 | 7.62 |  |  |  | 7.62
CONTRA COSTA 2116 | 13652116 | 14.12 |  |  |  | 14.12
COPPERMINE 1104 | 252411104 | 103.43 |  | 9.04 |  | 94.39
COPPERMINE 1106 | 252411106 | 7.97 |  |  |  | 7.97
COPPERMINE 1112 | 252411112 | 15.89 |  |  |  | 15.89
COPPERMINE 2110 | 252412110 | 0 |  |  |  | 0
COPUS 1102 | 253871102 | 30.95 |  |  |  | 30.95
COPUS 1103 | 253871103 | 24.41 |  |  |  | 24.41
COPUS 1104 | 253871104 | 39.17 |  |  |  | 39.17
CORCORAN 1101 | 252171101 | 0.52 |  |  |  | 0.52
CORCORAN 1102 | 252171102 | 0.04 |  |  |  | 0.04
CORCORAN 1104 | 252171104 | 26.73 |  |  |  | 26.73
CORCORAN 1106 | 252171106 | 44.59 |  |  |  | 44.59
CORCORAN 1108 | 252171108 | 23.58 |  |  |  | 23.58
CORCORAN 1112 | 252171112 | 44.97 |  |  |  | 44.97
CORCORAN 1116 | 252171116 | 56.82 |  |  |  | 56.82
CORCORAN 1117 | 252171117 | 0.54 |  |  |  | 0.54
CORCORAN 1118 | 252171118 | 52.34 |  |  |  | 52.34
CORDELIA 1101 | 62701101 | 0.02 |  |  |  | 0.02
CORDELIA 1102 | 62701102 | 0.04 |  |  |  | 0.04
CORDELIA 1104 | 62701104 | 62 |  |  |  | 62
CORDELIA 1110 | 62701110 | 8.96 |  |  |  | 8.96
CORDELIA 1112 | 62701112 | 16.12 |  |  |  | 16.12
CORNING 1101 | 103331101 | 143.53 |  | 49.56 |  | 93.97
CORNING 1102 | 103331102 | 163.49 |  | 65.08 |  | 98.41
CORNING 1103 | 103331103 | 66.67 |  |  |  | 66.67
CORNING 1104 | 103331104 | 113.1 |  |  |  | 113.1
CORNING REMOTE 0001 0001 | 197040001 | 0.01 |  | 0.01 |  | 0
CORNING REMOTE 0002 0002 | 193330002 | 0.01 |  | 0.01 |  | 0
CORONA 1101 | 43491101 | 22.86 |  |  |  | 22.86
CORONA 1102 | 43491102 | 1.38 |  |  |  | 1.38
CORONA 1103 | 43491103 | 17.53 |  | 0.46 |  | 17.07
CORRAL 1101 | 162991101 | 172.25 |  | 119.57 |  | 52.68
CORRAL 1102 | 162991102 | 62.87 |  | 47.63 |  | 15.24
CORRAL 1103 | 162991103 | 80.7 |  | 17.72 |  | 62.98
CORTINA 1101 | 63121101 | 59.42 |  | 1.32 |  | 58.1
COTATI 1102 | 42271102 | 34.71 |  | 15.65 |  | 19.06
COTATI 1103 | 42271103 | 110.97 |  | 84.08 |  | 26.89
COTATI 1104 | 42271104 | 19.36 |  | 8.45 |  | 10.91
COTATI 1105 | 42271105 | 112.18 |  | 43.05 |  | 69.13
COTTLE 1701 | 163711701 | 89.99 |  |  |  | 89.99
COTTLE 1702 | 163711702 | 36.99 |  |  |  | 36.99
COTTLE 1703 | 163711703 | 27.21 |  |  |  | 27.21
COTTLE 1704 | 163711704 | 14.67 |  |  |  | 14.67
COTTLE 1707 | 163711707 | 47.14 |  |  |  | 47.14
COTTLE 1708 | 163711708 | 129.34 |  |  |  | 129.34
COTTONWOOD 1101 | 102931101 | 101.05 |  | 70.06 |  | 30.99
COTTONWOOD 1102 | 102931102 | 67.82 |  | 41.65 |  | 26.17
COTTONWOOD 1103 | 102931103 | 160.63 |  | 133.86 |  | 26.77
COUNTRY CLUB 0401 | 163120401 | 2.16 |  |  |  | 2.16
COUNTRY CLUB 0402 | 163120402 | 4.67 |  |  |  | 4.67
COUNTRY CLUB 0403 | 163120403 | 2.7 |  |  |  | 2.7
COUNTRY CLUB 1101 | 163121101 | 12.07 |  |  |  | 12.07
COUNTRY CLUB 1102 | 163121102 | 1.34 |  |  |  | 1.34
COUNTRY CLUB 1103 | 163121103 | 6.27 |  |  |  | 6.27
COUNTRY CLUB 1104 | 163121104 | 7.21 |  |  |  | 7.21
COUNTRY CLUB 1105 | 163121105 | 1.65 |  |  |  | 1.65
COUNTRY CLUB 1106 | 163121106 | 9.01 |  |  |  | 9.01
COVELO 1101 | 43061101 | 120.69 |  | 17.54 |  | 103.15
CRESSEY 2103 | 254702103 | 152.82 |  |  |  | 152.82
CRESSEY 2104 | 254702104 | 87.73 |  |  |  | 87.73
CRESTA 1101 | 102251101 | 1.65 | 0.38 | 1.28 |  | -0.01
CROWS LANDING 1101 | 163251101 | 44.57 |  |  |  | 44.57
CROWS LANDING 1102 | 163251102 | 3.17 |  |  |  | 3.17
CURTIS 1701 | 163351701 | 19.84 |  | 11.96 |  | 7.88
CURTIS 1702 | 163351702 | 117.9 | 22.48 | 87.25 |  | 8.17
CURTIS 1703 | 163351703 | 198.1 | 17.43 | 177.37 |  | 3.3
CURTIS 1704 | 163351704 | 84.55 | 25.62 | 58.36 |  | 0.57
CURTIS 1705 | 163351705 | 88.39 | 14.4 | 69.9 |  | 4.09
CUYAMA 1103 | 253141103 | 79.81 |  | 2.58 |  | 77.23
CUYAMA 1104 | 253141104 | 17.88 |  |  |  | 17.88
CUYAMA 2101 | 253142101 | 63.24 |  | 3.32 |  | 59.92
CUYAMA 2102 | 253142102 | 35.72 |  |  |  | 35.72
DAIRYLAND 1102 | 252421102 | 81.49 |  |  |  | 81.49
DAIRYLAND 1105 | 252421105 | 64.82 |  |  |  | 64.82
DAIRYLAND 1109 | 252421109 | 46.7 |  |  |  | 46.7
DAIRYLAND 1110 | 252421110 | 37.73 |  |  |  | 37.73
DAIRYLAND 1111 | 252421111 | 26.78 |  |  |  | 26.78
DAIRYLAND 1112 | 252421112 | 62.39 |  |  |  | 62.39
DAIRYLAND 1113 | 252421113 | 83.52 |  |  |  | 83.52
DAIRYVILLE 1101 | 103341101 | 43.02 |  |  |  | 43.02
DALY CITY 0401 | 22640401 | 5.66 |  |  |  | 5.66
DALY CITY 1101 | 22641101 | 3.43 |  |  |  | 3.43
DALY CITY 1102 | 22641102 | 7.55 |  |  |  | 7.55
DALY CITY 1103 | 22641103 | 4.75 |  |  |  | 4.75
DALY CITY 1104 | 22641104 | 10.98 |  |  |  | 10.98
DALY CITY 1105 | 22641105 | 10.67 |  |  |  | 10.67
DALY CITY 1106 | 22641106 | 10.01 |  |  |  | 10.01
DALY CITY 1107 | 22641107 | 5.33 |  |  |  | 5.33
DALY CITY 1108 | 22641108 | 2.94 |  |  |  | 2.94
DALY CITY 1109 | 22641109 | 6.25 |  |  |  | 6.25
DALY CITY 1110 | 22641110 | 1.8 |  |  |  | 1.8
DALY CITY 1111 | 22641111 | 7.05 |  |  |  | 7.05
DALY CITY 1112 | 22641112 | 14.06 |  |  |  | 14.06
DALY CITY 1115 | 22641115 | 0.03 |  |  |  | 0.03
DAVIS 1101 | 62041101 | 37.44 |  |  |  | 37.44
DAVIS 1102 | 62041102 | 6.48 |  |  |  | 6.48
DAVIS 1103 | 62041103 | 5.86 |  |  |  | 5.86
DAVIS 1104 | 62041104 | 5.75 |  |  |  | 5.75
DAVIS 1105 | 62041105 | 8.04 |  |  |  | 8.04
DAVIS 1106 | 62041106 | 42.85 |  |  |  | 42.85
DAVIS 1107 | 62041107 | 84.27 |  |  |  | 84.27
DAVIS 1108 | 62041108 | 3.34 |  |  |  | 3.34
DAVIS 1109 | 62041109 | 4.45 |  |  |  | 4.45
DAVIS 1110 | 62041110 | 1.88 |  |  |  | 1.88
DAVIS 1111 | 62041111 | 7.25 |  |  |  | 7.25
DAVIS 1112 | 62041112 | 46.59 |  |  |  | 46.59
DAYTON ROAD 0401 | 102940401 | 2.11 |  |  |  | 2.11
DEEPWATER 1105 | 63621105 | 5.53 |  |  |  | 5.53
DEEPWATER 1106 | 63621106 | 0.06 |  |  |  | 0.06
DEEPWATER 1107 | 63621107 | 24.83 |  |  |  | 24.83
DEEPWATER 1108 | 63621108 | 0.09 |  |  |  | 0.09
DEEPWATER 1109 | 63621109 | 4.8 |  |  |  | 4.8
DEEPWATER 1110 | 63621110 | 6.21 |  |  |  | 6.21
DEER CREEK PH 0401 | 158450401 | 1.12 | 1.12 |  |  | 0
DEL MAR 1103 | 152581103 | 12.74 |  |  |  | 12.74
DEL MAR 1104 | 152581104 | 4.72 |  |  |  | 4.72
DEL MAR 2105 | 152582105 | 13.9 |  |  |  | 13.9
DEL MAR 2106 | 152582106 | 3.1 |  |  |  | 3.1
DEL MAR 2109 | 152582109 | 6.88 |  | 2.03 |  | 4.85
DEL MAR 2110 | 152582110 | 1.77 |  |  |  | 1.77
DEL MONTE 1101 | 182221101 | 14.95 |  | 0.49 |  | 14.46
DEL MONTE 2102 | 182222102 | 16.25 |  | 0.66 |  | 15.59
DEL MONTE 2103 | 182222103 | 36.87 |  | 12.31 |  | 24.56
DEL MONTE 2104 | 182222104 | 59.34 |  | 43.92 |  | 15.42
DEL MONTE 2105 | 182222105 | 20.19 |  | 1.05 |  | 19.14
DELEVAN 1101 | 69551101 | 0.6 |  |  |  | 0.6
DELEVAN 1102 | 69551102 | 0.61 |  |  |  | 0.61
DESCHUTES 1101 | 103351101 | 130.52 | 7.49 | 99.46 |  | 23.57
DESCHUTES 1104 | 103351104 | 112.61 |  | 60.08 |  | 52.53
DEVILS DEN 1101 | 253451101 | 44.63 |  |  |  | 44.63
DEVILS DEN 1102 | 253451102 | 32.94 |  |  |  | 32.94
DIAMOND SPRINGS 1103 | 152261103 | 53.35 | 10.21 | 22.95 |  | 20.19
DIAMOND SPRINGS 1104 | 152261104 | 18.2 | 7.58 | 4.87 |  | 5.75
DIAMOND SPRINGS 1105 | 152261105 | 131.4 | 75.07 | 47.85 |  | 8.48
DIAMOND SPRINGS 1106 | 152261106 | 120.23 |  | 109.82 |  | 10.41
DIAMOND SPRINGS 1107 | 152261107 | 56.83 | 33.81 | 17.85 |  | 5.17
DINUBA 1102 | 254091102 | 22.15 |  |  |  | 22.15
DINUBA 1104 | 254091104 | 85.48 |  |  |  | 85.48
DINUBA 1105 | 254091105 | 100.18 |  |  |  | 100.18
DINUBA 1106 | 254091106 | 10.39 |  |  |  | 10.39
DIVIDE 1101 | 182571101 | 14.98 |  |  |  | 14.98
DIVIDE 1102 | 182571102 | 47.81 |  |  |  | 47.81
DIVIDE 1103 | 182571103 | 20.68 |  | 2.39 |  | 18.29
DIXON 1102 | 62061102 | 10.86 |  |  |  | 10.86
DIXON 1103 | 62061103 | 120.37 |  |  |  | 120.37
DIXON 1104 | 62061104 | 11.69 |  |  |  | 11.69
DIXON 1105 | 62061105 | 23.82 |  |  |  | 23.82
DIXON 1106 | 62061106 | 9.76 |  |  |  | 9.76
DIXON LANDING 2101 | 14722101 | 10.69 |  |  |  | 10.69
DIXON LANDING 2102 | 14722102 | 10.83 |  |  |  | 10.83
DIXON LANDING 2103 | 14722103 | 2.81 |  |  |  | 2.81
DIXON LANDING 2105 | 14722105 | 1.68 |  |  |  | 1.68
DIXON LANDING 2109 | 14722109 | 10.6 |  |  |  | 10.6
DIXON LANDING 2111 | 14722111 | 0.13 |  |  |  | 0.13
DOBBINS 1101 | 153741101 | 81.73 | 26.59 | 54.07 |  | 1.07
DOLAN ROAD 1101 | 182381101 | 69.1 |  | 2.77 |  | 66.33
DOLAN ROAD 1102 | 182381102 | 0.45 |  |  |  | 0.45
DOLAN ROAD 1103 | 182381103 | 3.01 |  |  |  | 3.01
DOLAN ROAD 1104 | 182381104 | 5.06 |  |  |  | 5.06
DOS PALOS 1101 | 254041101 | 75.74 |  |  |  | 75.74
DOS PALOS 1102 | 254041102 | 0.21 |  |  |  | 0.21
DRUM 1101 | 152321101 | 18.38 | 18.34 | 0.04 |  | 0
DUMBARTON 1102 | 14471102 | 16.57 |  |  |  | 16.57
DUMBARTON 1103 | 14471103 | 1.48 |  |  |  | 1.48
DUMBARTON 1104 | 14471104 | 11.57 |  |  |  | 11.57
DUMBARTON 1106 | 14471106 | 7.25 |  |  |  | 7.25
DUMBARTON 1107 | 14471107 | 10.44 |  |  |  | 10.44
DUMBARTON 1108 | 14471108 | 3.94 |  |  |  | 3.94
DUMBARTON 1109 | 14471109 | 3.73 |  |  |  | 3.73
DUMBARTON 1110 | 14471110 | 6.98 |  |  |  | 6.98
DUMBARTON 2111 | 14472111 | 6.41 |  |  |  | 6.41
DUNBAR 1101 | 43071101 | 53.65 | 26.69 | 2.54 |  | 24.42
DUNBAR 1102 | 43071102 | 62 | 7.08 | 42.27 |  | 12.65
DUNBAR 1103 | 43071103 | 60.19 | 20.74 | 14.72 |  | 24.73
DUNLAP 1102 | 254061102 | 55.31 |  | 55.31 |  | 0
DUNLAP 1103 | 254061103 | 71.24 |  | 71.24 |  | 0
DUNNIGAN 1101 | 63811101 | 36.43 |  |  |  | 36.43
DUNNIGAN 1102 | 63811102 | 39.28 |  |  |  | 39.28
DUNNIGAN 1103 | 63811103 | 46.97 |  | 1.92 |  | 45.05
EAST GRAND 0401 | 22570401 | 4.76 |  |  |  | 4.76
EAST GRAND 0404 | 22570404 | 3.85 |  |  |  | 3.85
EAST GRAND 1101 | 22571101 | 7.95 |  |  |  | 7.95
EAST GRAND 1102 | 22571102 | 2.25 |  |  |  | 2.25
EAST GRAND 1103 | 22571103 | 1.51 |  |  |  | 1.51
EAST GRAND 1104 | 22571104 | 15.59 |  |  |  | 15.59
EAST GRAND 1105 | 22571105 | 5.58 |  |  |  | 5.58
EAST GRAND 1106 | 22571106 | 3.71 |  |  |  | 3.71
EAST GRAND 1107 | 22571107 | 13.58 |  |  |  | 13.58
EAST GRAND 1108 | 22571108 | 3.88 |  |  |  | 3.88
EAST GRAND 1109 | 22571109 | 2.08 |  |  |  | 2.08
EAST GRAND 1110 | 22571110 | 3.35 |  |  |  | 3.35
EAST GRAND 1111 | 22571111 | 0.88 |  |  |  | 0.88
EAST GRAND 1114 | 22571114 | 0 |  |  |  | 0
EAST GRAND 1115 | 22571115 | 0 |  |  |  | 0
EAST MARYSVILLE 1105 | 152331105 | 48.19 |  |  |  | 48.19
EAST MARYSVILLE 1107 | 152331107 | 8.06 |  |  |  | 8.06
EAST MARYSVILLE 1108 | 152331108 | 67.89 |  |  |  | 67.89
EAST NICOLAUS 1101 | 152151101 | 68.94 |  |  |  | 68.94
EAST NICOLAUS 1102 | 152151102 | 58.36 |  |  |  | 58.36
EAST NICOLAUS 1103 | 152151103 | 93.4 |  |  |  | 93.4
EAST QUINCY 1101 | 102551101 | 17.52 | 1.69 | 2.06 |  | 13.77
EAST STOCKTON 0401 | 163130401 | 8.46 |  |  |  | 8.46
EAST STOCKTON 0402 | 163130402 | 9.83 |  |  |  | 9.83
EAST STOCKTON 1101 | 163131101 | 14.66 |  |  |  | 14.66
EAST STOCKTON 1102 | 163131102 | 16.16 |  |  |  | 16.16
ECHO SUMMIT 1101 | 158031101 | 14.68 |  | 5.92 | 0.04 | 8.72
EDENVALE 1101 | 82951101 | 9.68 |  |  |  | 9.68
EDENVALE 1102 | 82951102 | 5.72 |  | 0.52 |  | 5.2
EDENVALE 1103 | 82951103 | 0.31 |  |  |  | 0.31
EDENVALE 2105 | 82952105 | 37.24 |  | 2.32 |  | 34.92
EDENVALE 2106 | 82952106 | 16.96 |  |  |  | 16.96
EDENVALE 2107 | 82952107 | 0.07 |  |  |  | 0.07
EDENVALE 2108 | 82952108 | 2.87 |  |  |  | 2.87
EDENVALE 2109 | 82952109 | 2.47 |  |  |  | 2.47
EDENVALE 2110 | 82952110 | 0 |  |  |  | 0
EDENVALE 2112 | 82952112 | 1.34 |  |  |  | 1.34
EDENVALE 2113 | 82952113 | 2.42 |  | 0.02 |  | 2.4
EDES 1101 | 13681101 | 8.66 |  |  |  | 8.66
EDES 1103 | 13681103 | 12.55 |  |  |  | 12.55
EDES 1105 | 13681105 | 3.62 |  |  |  | 3.62
EDES 1110 | 13681110 | 4.97 |  |  |  | 4.97
EDES 1111 | 13681111 | 4.22 |  |  |  | 4.22
EDES 1112 | 13681112 | 17.1 | 0.58 | 14.66 |  | 1.86
EDES 1113 | 13681113 | 4.45 |  |  |  | 4.45
EDES 1114 | 13681114 | 10.47 |  |  |  | 10.47
EEL RIVER 1102 | 192381102 | 144.73 |  | 40.04 |  | 104.69
EEL RIVER 1103 | 192381103 | 59.43 |  | 3.2 |  | 56.23
EIGHT MILE 2101 | 163912101 | 73.19 |  |  |  | 73.19
EIGHT MILE 2102 | 163912102 | 29.41 |  |  |  | 29.41
EIGHT MILE 2103 | 163912103 | 0 |  |  |  | 0
EIGHT MILE 2104 | 163912104 | 1.36 |  |  |  | 1.36
EIGHT MILE 2105 | 163912105 | 0.49 |  |  |  | 0.49
EIGHT MILE 2106 | 163912106 | 30.18 |  |  |  | 30.18
EL CAPITAN 0004 | 253880004 | 0.01 |  |  |  | 0.01
EL CAPITAN 1102 | 253881102 | 9.33 |  |  |  | 9.33
EL CAPITAN 1103 | 253881103 | 67.79 |  |  |  | 67.79
EL CAPITAN 1104 | 253881104 | 49.51 |  |  |  | 49.51
EL CAPITAN 1105 | 253881105 | 4.84 |  |  |  | 4.84
EL CAPITAN 1106 | 253881106 | 17.65 |  |  |  | 17.65
EL CAPITAN 2109 | 253882109 | 7.43 |  |  |  | 7.43
EL CAPITAN 2110 | 253882110 | 8.88 |  |  |  | 8.88
EL CERRITO G 1101 | 12501101 | 10.17 |  |  |  | 10.17
EL CERRITO G 1102 | 12501102 | 7.79 |  |  |  | 7.79
EL CERRITO G 1103 | 12501103 | 9.13 |  |  |  | 9.13
EL CERRITO G 1104 | 12501104 | 7.88 |  |  |  | 7.88
EL CERRITO G 1105 | 12501105 | 31.81 | 5.58 | 18.99 |  | 7.24
EL CERRITO G 1106 | 12501106 | 4.69 |  |  |  | 4.69
EL CERRITO G 1107 | 12501107 | 3.6 |  |  |  | 3.6
EL CERRITO G 1108 | 12501108 | 14.49 |  | 0 |  | 14.49
EL CERRITO G 1109 | 12501109 | 8.04 |  |  |  | 8.04
EL CERRITO G 1110 | 12501110 | 16.6 |  | 0.69 |  | 15.91
EL CERRITO G 1111 | 12501111 | 16.3 |  | 0.2 |  | 16.1
EL CERRITO G 1112 | 12501112 | 24.62 | 1.65 | 0.35 |  | 22.62
EL CERRITO G 1113 | 12501113 | 11.46 |  | 0.1 |  | 11.36
EL CERRITO G 1114 | 12501114 | 6.8 |  |  |  | 6.8
EL DORADO PH 2101 | 152762101 | 135.03 | 99.11 | 25.44 | 0.74 | 9.74
EL DORADO PH 2102 | 152762102 | 33.98 | 33.98 |  |  | 0
EL NIDO 1101 | 252451101 | 57.54 |  |  |  | 57.54
EL NIDO 1102 | 252451102 | 59.29 |  |  |  | 59.29
EL NIDO 1103 | 252451103 | 60.07 |  |  |  | 60.07
EL NIDO 1104 | 252451104 | 86.9 |  |  |  | 86.9
EL PATIO 1101 | 82921101 | 0.77 |  |  |  | 0.77
EL PATIO 1102 | 82921102 | 1.64 |  |  |  | 1.64
EL PATIO 1103 | 82921103 | 13.15 |  |  |  | 13.15
EL PATIO 1104 | 82921104 | 12 |  |  |  | 12
EL PATIO 1105 | 82921105 | 6.97 |  |  |  | 6.97
EL PATIO 1107 | 82921107 | 15.68 |  |  |  | 15.68
EL PATIO 1108 | 82921108 | 6.74 |  |  |  | 6.74
EL PATIO 1109 | 82921109 | 10.6 |  |  |  | 10.6
EL PATIO 1111 | 82921111 | 0.03 |  |  |  | 0.03
EL PATIO 1112 | 82921112 | 19.54 |  |  |  | 19.54
EL PATIO 1113 | 82921113 | 4.76 |  |  |  | 4.76
EL PATIO 1114 | 82921114 | 0.53 |  |  |  | 0.53
EL PATIO 1116 | 82921116 | 8.75 |  |  |  | 8.75
EL PATIO 1117 | 82921117 | 4.19 |  |  |  | 4.19
EL PATIO 1118 | 82921118 | 10.94 |  |  |  | 10.94
EL PATIO 1119 | 82921119 | 8.29 |  |  |  | 8.29
EL PECO 1102 | 253981102 | 52.32 |  |  |  | 52.32
EL PECO 1105 | 253981105 | 90.24 |  |  |  | 90.24
EL PECO 1106 | 253981106 | 50.32 |  |  |  | 50.32
ELECTRA 1101 | 162161101 | 85.18 |  | 81.65 |  | 3.53
ELECTRA 1102 | 162161102 | 19.56 |  | 16.98 |  | 2.58
ELK 1101 | 42981101 | 106.71 |  | 73.23 |  | 33.48
ELK CREEK 1101 | 102781101 | 158.69 |  | 68.16 |  | 90.53
ELK HILLS 1104 | 252441104 | 57.68 |  |  |  | 57.68
ELK HILLS 1106 | 252441106 | 21.2 |  |  |  | 21.2
EMBARCADERO (Z) 1112 | 22871112 | 0 |  |  |  | 0
EMBARCADERO (Z) 1113 | 22871113 | 0.32 |  |  |  | 0.32
EMBARCADERO (Z) 1114 | 22871114 | 0 |  |  |  | 0
EMBARCADERO (Z) 1115 | 22871115 | 0.24 |  |  |  | 0.24
EMBARCADERO (Z) 1116 | 22871116 | 1.02 |  |  |  | 1.02
EMBARCADERO (Z) 1118 | 22871118 | 0.31 |  |  |  | 0.31
EMBARCADERO (Z) 1119 | 22871119 | 0 |  |  |  | 0
EMBARCADERO (Z) 1120 | 22871120 | 0.32 |  |  |  | 0.32
EMBARCADERO (Z) 1122 | 22871122 | 0.01 |  |  |  | 0.01
EMBARCADERO (Z) 1123 | 22871123 | 0.36 |  |  |  | 0.36
EMERALD LAKE 0401 | 24080401 | 12.93 | 2.1 | 6.87 |  | 3.96
EMERALD LAKE 0402 | 24080402 | 6.57 |  | 6.57 |  | 0
ERTA 0403 | 83510403 | 2.99 |  |  |  | 2.99
ERTA 0404 | 83510404 | 6.52 |  |  |  | 6.52
ESQUON 1101 | 102171101 | 70.1 |  |  |  | 70.1
ESQUON 1102 | 102171102 | 50.82 |  |  |  | 50.82
ESQUON 1103 | 102171103 | 20.36 |  |  |  | 20.36
ESTUDILLO 0401 | 13480401 | 4.81 |  | 0.79 |  | 4.02
EUREKA A 1103 | 192121103 | 10.55 |  |  |  | 10.55
EUREKA A 1106 | 192121106 | 1.82 |  |  |  | 1.82
EUREKA A 1107 | 192121107 | 4.52 |  |  |  | 4.52
EUREKA E 1101 | 192331101 | 13.38 |  |  |  | 13.38
EUREKA E 1104 | 192331104 | 26.99 |  | 0.03 |  | 26.96
EUREKA E 1105 | 192331105 | 7.34 |  |  |  | 7.34
EVERGREEN 2101 | 82012101 | 2.53 |  |  |  | 2.53
EVERGREEN 2102 | 82012102 | 10.76 |  |  |  | 10.76
EVERGREEN 2103 | 82012103 | 19.17 |  |  |  | 19.17
EVERGREEN 2104 | 82012104 | 3.55 |  |  |  | 3.55
EVERGREEN 2105 | 82012105 | 4.64 |  |  |  | 4.64
FAIRHAVEN 1103 | 192451103 | 9.43 |  |  |  | 9.43
FAIRHAVEN 1104 | 192451104 | 3.33 |  |  |  | 3.33
FAIRMOUNT 0401 | 12650401 | 5.65 |  | 1.34 |  | 4.31
FAIRMOUNT 0402 | 12650402 | 5.15 |  |  |  | 5.15
FAIRVIEW 2206 | 13432206 | 14.27 |  |  |  | 14.27
FAIRVIEW 2207 | 13432207 | 50.58 |  | 20.94 |  | 29.64
FAIRVIEW 2208 | 13432208 | 10.08 |  |  |  | 10.08
FAIRWAY 1103 | 182061103 | 6.8 |  |  |  | 6.8
FAIRWAY 1104 | 182061104 | 22.91 |  |  |  | 22.91
FAIRWAY 1106 | 182061106 | 4.54 |  |  |  | 4.54
FAIRWAY 1107 | 182061107 | 19.02 |  |  |  | 19.02
FAIRWAY 1108 | 182061108 | 11.33 |  |  |  | 11.33
FAMOSO 1101 | 252461101 | 39.04 |  |  |  | 39.04
FAMOSO 1102 | 252461102 | 27.39 |  |  |  | 27.39
FAMOSO 1103 | 252461103 | 28.9 |  |  |  | 28.9
FAMOSO 1105 | 252461105 | 10.05 |  |  |  | 10.05
FAMOSO 1107 | 252461107 | 18.75 |  |  |  | 18.75
FELLOWS 2103 | 254242103 | 26.79 |  |  |  | 26.79
FELLOWS 2104 | 254242104 | 77.37 |  |  |  | 77.37
FIGARDEN 2102 | 254552102 | 23.9 |  |  |  | 23.9
FIGARDEN 2103 | 254552103 | 5.49 |  |  |  | 5.49
FIGARDEN 2104 | 254552104 | 1.81 |  |  |  | 1.81
FIGARDEN 2105 | 254552105 | 12.66 |  |  |  | 12.66
FIGARDEN 2107 | 254552107 | 5.43 |  |  |  | 5.43
FIGARDEN 2108 | 254552108 | 4.95 |  |  |  | 4.95
FIGARDEN 2109 | 254552109 | 3.91 |  |  |  | 3.91
FIGARDEN 2110 | 254552110 | 16.52 |  |  |  | 16.52
FIGARDEN 2111 | 254552111 | 4.83 |  |  |  | 4.83
FIGARDEN 2112 | 254552112 | 31.41 |  |  |  | 31.41
FIGARDEN 2113 | 254552113 | 11.29 |  |  |  | 11.29
FIREBAUGH 1101 | 253471101 | 92.42 |  |  |  | 92.42
FIREBAUGH 1102 | 253471102 | 52.74 |  |  |  | 52.74
FIREBAUGH 1103 | 253471103 | 75.53 |  |  |  | 75.53
FITCH MOUNTAIN 1111 | 42751111 | 30.48 |  | 0.29 |  | 30.19
FITCH MOUNTAIN 1112 | 42751112 | 0.01 |  |  |  | 0.01
FITCH MOUNTAIN 1113 | 42751113 | 145.72 | 30.79 | 46.32 |  | 68.61
FLINT 1101 | 152531101 | 18.66 |  | 6.27 |  | 12.39
FLINT 1102 | 152531102 | 0.12 |  | 0.12 |  | 0
FLORENCE 0401 | 12690401 | 4.29 |  | 0.82 |  | 3.47
FMC 1105 | 83871105 | 16.58 |  |  |  | 16.58
FMC 1108 | 83871108 | 1.36 |  |  |  | 1.36
FMC 1109 | 83871109 | 1.03 |  |  |  | 1.03
FMC 1111 | 83871111 | 1.39 |  |  |  | 1.39
FOOTHILL 1101 | 182951101 | 39.49 |  | 18.92 |  | 20.57
FOOTHILL 1102 | 182951102 | 15.62 |  | 7.61 |  | 8.01
FORESTHILL 1101 | 152181101 | 64.36 | 64.32 | 0.05 |  | -0.01
FORESTHILL 1102 | 152181102 | 29.49 | 21.72 | 7.77 |  | 0
FORT BRAGG A 1101 | 42761101 | 81.19 |  | 70.52 |  | 10.67
FORT BRAGG A 1102 | 42761102 | 81.65 |  | 66.1 |  | 15.55
FORT BRAGG A 1103 | 42761103 | 2.68 |  | 0.07 |  | 2.61
FORT BRAGG A 1104 | 42761104 | 39.14 |  | 25.05 |  | 14.09
FORT ORD 1101 | 182401101 | 16.95 |  |  |  | 16.95
FORT ORD 2105 | 182402105 | 7.22 |  |  |  | 7.22
FORT ORD 2106 | 182402106 | 24.04 |  | 2.2 |  | 21.84
FORT ORD 2107 | 182402107 | 19.45 |  | 3.78 |  | 15.67
FORT ORD 2108 | 182402108 | 0.9 |  |  |  | 0.9
FORT ROSS 1121 | 42851121 | 93.71 | 21.98 | 70.02 |  | 1.71
FORT SEWARD 1121 | 192321121 | 48.12 |  | 36.16 |  | 11.96
FORT SEWARD 1122 | 192321122 | 21.85 |  | 17.45 |  | 4.4
FRANKLIN 1101 | 13921101 | 9.3 |  | 1.27 |  | 8.03
FRANKLIN 1102 | 13921102 | 4.44 |  |  |  | 4.44
FRANKLIN 1103 | 13921103 | 12.27 |  |  |  | 12.27
FRANKLIN 1104 | 13921104 | 14.69 |  | 7.42 |  | 7.27
FREMONT 1103 | 14351103 | 3.25 |  |  |  | 3.25
FREMONT 1104 | 14351104 | 21.67 |  | 1.08 |  | 20.59
FREMONT 1107 | 14351107 | 15.11 |  |  |  | 15.11
FREMONT 1108 | 14351108 | 4.89 |  |  |  | 4.89
FREMONT 1109 | 14351109 | 13.65 |  |  |  | 13.65
FREMONT 1110 | 14351110 | 10.36 |  |  |  | 10.36
FREMONT 1112 | 14351112 | 0.18 |  |  |  | 0.18
FRENCH CAMP 1101 | 163291101 | 15.51 |  |  |  | 15.51
FRENCH CAMP 1102 | 163291102 | 87.11 |  |  |  | 87.11
FRENCH CAMP 1103 | 163291103 | 1.23 |  |  |  | 1.23
FRENCH CAMP 1104 | 163291104 | 5.63 |  |  |  | 5.63
FRENCH GULCH 1101 | 103381101 | 15.99 |  | 15.99 |  | 0
FRENCH GULCH 1102 | 103381102 | 18.78 |  | 18.68 |  | 0.1
FROGTOWN 1701 | 163451701 | 71.45 | 6.65 | 63.55 |  | 1.25
FROGTOWN 1702 | 163451702 | 230.08 |  | 204.89 |  | 25.19
FRUITLAND 1141 | 192311141 | 26.41 |  | 23.43 |  | 2.98
FRUITLAND 1142 | 192311142 | 67.22 |  | 57.14 | 0.03 | 10.05
FRUITVALE 1101 | 253391101 | 3.34 |  |  |  | 3.34
FRUITVALE 1103 | 253391103 | 11.75 |  |  |  | 11.75
FRUITVALE 1104 | 253391104 | 11.25 |  |  |  | 11.25
FRUITVALE 1105 | 253391105 | 3.41 |  |  |  | 3.41
FRUITVALE 1106 | 253391106 | 9.52 |  |  |  | 9.52
FRUITVALE 1108 | 253391108 | 9.13 |  |  |  | 9.13
FULTON 1101 | 42561101 | 4.17 |  |  |  | 4.17
FULTON 1102 | 42561102 | 61.66 | 1.64 | 26.35 |  | 33.67
FULTON 1103 | 42561103 | 0.01 |  |  |  | 0.01
FULTON 1104 | 42561104 | 8.48 |  | 0.41 |  | 8.07
FULTON 1105 | 42561105 | 41.65 |  |  |  | 41.65
FULTON 1106 | 42561106 | 5.35 |  |  |  | 5.35
FULTON 1107 | 42561107 | 47.37 | 34.19 | 0.01 |  | 13.17
GABILAN 1101 | 182331101 | 72.82 |  | 4.55 |  | 68.27
GABILAN 1102 | 182331102 | 9.8 |  |  |  | 9.8
GALLO 1101 | 254901101 | 0.72 |  |  |  | 0.72
GALLO 1102 | 254901102 | 0.08 |  |  |  | 0.08
GANSNER 1101 | 103021101 | 44.15 | 3 | 30.46 |  | 10.69
GANSO 1103 | 254541103 | 39.46 |  |  |  | 39.46
GANSO 1104 | 254541104 | 37.41 |  |  |  | 37.41
GARBERVILLE 1101 | 192221101 | 145.81 |  | 66.33 |  | 79.48
GARBERVILLE 1102 | 192221102 | 136.76 |  | 122.15 |  | 14.61
GARBERVILLE 1103 | 192221103 | 2.24 |  | 0.48 |  | 1.76
GARCIA 0401 | 43040401 | 2.46 |  | 2.46 |  | 0
GARDNER 0401 | 254930401 | 0.02 |  |  |  | 0.02
GATES 1101 | 253931101 | 15.29 |  |  |  | 15.29
GATES 1102 | 253931102 | 41.83 |  |  |  | 41.83
GATES 1104 | 253931104 | 26.79 |  |  |  | 26.79
GATES 1105 | 253931105 | 39.31 |  |  |  | 39.31
GATES 1106 | 253931106 | 45.56 |  |  |  | 45.56
GATES 1107 | 253931107 | 2.52 |  |  |  | 2.52
GATES 1108 | 253931108 | 2.57 |  |  |  | 2.57
GATES 1109 | 253931109 | 0.3 |  |  |  | 0.3
GATES 1110 | 253931110 | 42.79 |  |  |  | 42.79
GERBER 1101 | 103391101 | 43.3 |  |  |  | 43.3
GERBER 1102 | 103391102 | 75.04 |  |  |  | 75.04
GEYSERVILLE 1101 | 42891101 | 142.75 |  | 72.34 |  | 70.41
GEYSERVILLE 1102 | 42891102 | 118.8 | 20.32 | 33.89 |  | 64.59
GIFFEN 1102 | 253151102 | 41.36 |  |  |  | 41.36
GIFFEN 1103 | 253151103 | 50.47 |  |  |  | 50.47
GIFFEN 1106 | 253151106 | 2.17 |  |  |  | 2.17
GIFFEN 1107 | 253151107 | 2.65 |  |  |  | 2.65
GILL 0401 | 13550401 | 3.26 |  |  |  | 3.26
GILL 0402 | 13550402 | 3.93 |  |  |  | 3.93
GIRVAN 1101 | 103401101 | 106.52 | 42.18 | 58.95 |  | 5.39
GIRVAN 1102 | 103401102 | 76.29 | 33.66 | 10.86 |  | 31.77
GLENN 1101 | 102601101 | 137.11 |  | 0.26 |  | 136.85
GLENWOOD 0404 | 24090404 | 6.08 |  |  |  | 6.08
GLENWOOD 0405 | 24090405 | 5.72 |  |  |  | 5.72
GLENWOOD 0406 | 24090406 | 2.32 |  |  |  | 2.32
GLENWOOD 1101 | 24091101 | 5.43 |  |  |  | 5.43
GLENWOOD 1102 | 24091102 | 7.19 |  |  |  | 7.19
GOLDTREE 1105 | 182581105 | 11.83 |  | 6.84 |  | 4.99
GOLDTREE 1107 | 182581107 | 3.53 |  | 0.94 |  | 2.59
GOLDTREE 1108 | 182581108 | 21.62 |  | 3.45 |  | 18.17
GONZALES 1101 | 182131101 | 26 |  | 3.89 |  | 22.11
GONZALES 1102 | 182131102 | 0.73 |  |  |  | 0.73
GONZALES 1103 | 182131103 | 5.46 |  |  |  | 5.46
GONZALES 1104 | 182131104 | 54.37 |  | 0.74 |  | 53.63
GOOSE LAKE 1101 | 254201101 | 0.54 |  |  |  | 0.54
GOOSE LAKE 1103 | 254201103 | 74.04 |  |  |  | 74.04
GOOSE LAKE 1106 | 254201106 | 66.33 |  |  |  | 66.33
GOOSE LAKE 2104 | 254202104 | 47.73 |  |  |  | 47.73
GRAND ISLAND 2223 | 62462223 | 96.51 |  |  |  | 96.51
GRAND ISLAND 2224 | 62462224 | 65.27 |  |  |  | 65.27
GRAND ISLAND 2225 | 62462225 | 65.8 |  |  |  | 65.8
GRAND ISLAND 2226 | 62462226 | 20.92 |  |  |  | 20.92
GRAND ISLAND 2227 | 62462227 | 157.82 |  |  |  | 157.82
GRANT 1102 | 14381102 | 4.43 |  |  |  | 4.43
GRANT 1103 | 14381103 | 3.04 |  |  |  | 3.04
GRANT 1104 | 14381104 | 23.77 |  |  |  | 23.77
GRANT 1105 | 14381105 | 14.01 |  |  |  | 14.01
GRANT 1106 | 14381106 | 17.06 |  |  |  | 17.06
GRANT 1107 | 14381107 | 5.38 |  |  |  | 5.38
GRANT 1108 | 14381108 | 22.76 |  |  |  | 22.76
GRASS VALLEY 1101 | 152031101 | 24.84 | 7.72 | 14.39 |  | 2.73
GRASS VALLEY 1102 | 152031102 | 5.82 |  | 0.06 |  | 5.76
GRASS VALLEY 1103 | 152031103 | 87.69 |  | 86.09 |  | 1.6
GRAYS FLAT 0401 | 102530401 | 10.64 |  | 10.64 |  | 0
GREEN VALLEY 2101 | 83192101 | 156.02 | 32.66 | 7.64 |  | 115.72
GREEN VALLEY 2102 | 83192102 | 45.91 |  |  |  | 45.91
GREEN VALLEY 2103 | 83192103 | 68.73 |  |  |  | 68.73
GREEN VALLEY 2104 | 83192104 | 30.29 |  |  |  | 30.29
GREENBRAE 1101 | 43091101 | 1.84 |  |  |  | 1.84
GREENBRAE 1102 | 43091102 | 13.47 | 5.79 |  |  | 7.68
GREENBRAE 1103 | 43091103 | 7.2 |  | 0.75 |  | 6.45
GREENBRAE 1104 | 43091104 | 18.4 |  | 0.18 |  | 18.22
GUALALA 1111 | 42841111 | 37.89 |  | 33.24 |  | 4.65
GUALALA 1112 | 42841112 | 47.36 |  | 42.9 |  | 4.46
GUERNSEY 1101 | 252661101 | 43.66 |  |  |  | 43.66
GUERNSEY 1102 | 252661102 | 40.78 |  |  |  | 40.78
GUERNSEY 1103 | 252661103 | 31.77 |  |  |  | 31.77
GUERNSEY 1104 | 252661104 | 29.99 |  |  |  | 29.99
GUERNSEY 1105 | 252661105 | 2.17 |  |  |  | 2.17
GUERNSEY 1106 | 252661106 | 37.03 |  |  |  | 37.03
GUERNSEY 1108 | 252661108 | 2.17 |  |  |  | 2.17
GUSTINE 1101 | 163111101 | 67.91 |  |  |  | 67.91
GUSTINE 1102 | 163111102 | 136.97 |  |  |  | 136.97
HAAS 2101 | 259932101 | 12.23 |  | 3.79 | 0.49 | 7.95
HALF MOON BAY 1101 | 24101101 | 47.11 | 12.61 | 12.36 |  | 22.14
HALF MOON BAY 1102 | 24101102 | 48.17 | 5.57 | 2.87 |  | 39.73
HALF MOON BAY 1103 | 24101103 | 166.69 | 1.42 | 122.45 |  | 42.82
HALLS FLAT 1101 | 108011101 | 0.01 |  | 0.01 |  | 0
HALSEY 1101 | 152241101 | 68.48 |  | 68.48 |  | 0
HALSEY 1102 | 152241102 | 59.55 |  | 49.22 |  | 10.33
HAMILTON A 1101 | 102121101 | 36.77 |  |  |  | 36.77
HAMILTON A 1102 | 102121102 | 40.43 |  |  |  | 40.43
HAMILTON BRANCH 1101 | 102361101 | 34.41 |  | 24.29 |  | 10.12
HAMMER 1101 | 163301101 | 5.54 |  |  |  | 5.54
HAMMER 1102 | 163301102 | 2.76 |  |  |  | 2.76
HAMMER 1103 | 163301103 | 3.78 |  |  |  | 3.78
HAMMER 1104 | 163301104 | 10.69 |  |  |  | 10.69
HAMMER 1105 | 163301105 | 10.87 |  |  |  | 10.87
HAMMER 1106 | 163301106 | 7.25 |  |  |  | 7.25
HAMMER 1108 | 163301108 | 6.03 |  |  |  | 6.03
HAMMER 1109 | 163301109 | 3.86 |  |  |  | 3.86
HAMMONDS 1101 | 253401101 | 35.08 |  |  |  | 35.08
HAMMONDS 1102 | 253401102 | 72.89 |  |  |  | 72.89
HAMMONDS 1104 | 253401104 | 25.14 |  |  |  | 25.14
HARDING 0401 | 163310401 | 1.03 |  |  |  | 1.03
HARDING 0402 | 163310402 | 3.91 |  |  |  | 3.91
HARDING 0403 | 163310403 | 1.56 |  |  |  | 1.56
HARDING 0404 | 163310404 | 2.72 |  |  |  | 2.72
HARDING 0405 | 163310405 | 2.94 |  |  |  | 2.94
HARDING 0406 | 163310406 | 3.19 |  |  |  | 3.19
HARDWICK 1101 | 253711101 | 72.23 |  |  |  | 72.23
HARDWICK 1102 | 253711102 | 97.68 |  |  |  | 97.68
HARRIS 1108 | 192431108 | 32.73 |  | 1.71 |  | 31.02
HARRIS 1109 | 192431109 | 50.18 |  | 14.43 |  | 35.75
HARTER 1102 | 152851102 | 4.34 |  |  |  | 4.34
HARTER 1104 | 152851104 | 7.29 |  |  |  | 7.29
HARTER 1105 | 152851105 | 23.61 |  |  |  | 23.61
HARTER 1106 | 152851106 | 2.03 |  |  |  | 2.03
HARTER 1107 | 152851107 | 10.29 |  |  |  | 10.29
HARTLEY 1101 | 43211101 | 72.28 |  | 37.24 |  | 35.04
HARTLEY 1102 | 43211102 | 31.13 |  | 5.27 |  | 25.86
HATTON 1101 | 182291101 | 33.02 | 2.68 | 17.72 |  | 12.62
HATTON 1102 | 182291102 | 22.53 |  | 11.41 |  | 11.12
HAYWARD O 0401 | 12240401 | 3.31 |  |  |  | 3.31
HAYWARD O 0402 | 12240402 | 3.71 |  |  |  | 3.71
HENRIETTA 1104 | 252681104 | 35.96 |  |  |  | 35.96
HENRIETTA 1106 | 252681106 | 46.12 |  |  |  | 46.12
HENRIETTA 1108 | 252681108 | 22.64 |  |  |  | 22.64
HENRIETTA 1110 | 252681110 | 85.71 |  |  |  | 85.71
HERDLYN 1102 | 163741102 | 78.93 |  |  |  | 78.93
HERDLYN 1103 | 163741103 | 99.22 |  |  |  | 99.22
HICKS 1108 | 83431108 | 12.15 |  |  |  | 12.15
HICKS 1109 | 83431109 | 15.03 |  |  |  | 15.03
HICKS 1110 | 83431110 | 8.04 |  |  |  | 8.04
HICKS 1111 | 83431111 | 21.94 |  |  |  | 21.94
HICKS 1112 | 83431112 | 4.43 |  |  |  | 4.43
HICKS 1113 | 83431113 | 19.25 |  |  |  | 19.25
HICKS 1114 | 83431114 | 9.56 |  |  |  | 9.56
HICKS 1115 | 83431115 | 15.47 |  | 0.05 |  | 15.42
HICKS 1116 | 83431116 | 34.37 |  | 13.99 |  | 20.38
HICKS 2101 | 83432101 | 40.52 | 2.24 | 10.16 |  | 28.12
HICKS 2102 | 83432102 | 3.9 |  |  |  | 3.9
HICKS 2103 | 83432103 | 21.57 | 5.28 | 2.08 |  | 14.21
HICKS 2105 | 83432105 | 11.61 |  |  |  | 11.61
HICKS 2111 | 83432111 | 4.58 |  |  |  | 4.58
HIGGINS 1103 | 152691103 | 148.51 |  | 143.69 |  | 4.82
HIGGINS 1104 | 152691104 | 88.14 |  | 72.64 |  | 15.5
HIGGINS 1107 | 152691107 | 32.62 |  | 17.95 |  | 14.67
HIGGINS 1108 | 152691108 | 0.02 |  |  |  | 0.02
HIGGINS 1109 | 152691109 | 87.11 |  | 83.31 |  | 3.8
HIGGINS 1110 | 152691110 | 57.29 |  | 48.92 |  | 8.37
HIGHLANDS 1101 | 43361101 | 0.03 |  | 0.03 |  | 0
HIGHLANDS 1102 | 43361102 | 62.75 | 10.51 | 27.96 |  | 24.28
HIGHLANDS 1103 | 43361103 | 121.58 |  | 107.99 |  | 13.59
HIGHLANDS 1104 | 43361104 | 30.67 |  | 13.35 |  | 17.32
HIGHWAY 1101 | 42651101 | 11.19 |  |  |  | 11.19
HIGHWAY 1102 | 42651102 | 18.4 |  |  |  | 18.4
HIGHWAY 1103 | 42651103 | 6.31 |  |  |  | 6.31
HIGHWAY 1104 | 42651104 | 9.58 |  |  |  | 9.58
HIGHWAY 1105 | 42651105 | 1.04 |  |  |  | 1.04
HIGHWAY 1106 | 42651106 | 15.31 |  |  |  | 15.31
HIGHWAY 1107 | 42651107 | 3.38 |  |  |  | 3.38
HILLSDALE 0401 | 24110401 | 7.48 |  |  |  | 7.48
HILLSDALE 0402 | 24110402 | 8.07 |  |  |  | 8.07
HILLSDALE 0403 | 24110403 | 3.29 |  |  |  | 3.29
HILLSDALE 0404 | 24110404 | 5.72 |  |  |  | 5.72
HILLSDALE 0405 | 24110405 | 5.93 |  |  |  | 5.93
HOLLISTER 2101 | 182492101 | 25.61 |  |  |  | 25.61
HOLLISTER 2102 | 182492102 | 108.32 |  | 27.73 |  | 80.59
HOLLISTER 2103 | 182492103 | 13.6 |  |  |  | 13.6
HOLLISTER 2104 | 182492104 | 122.87 |  | 6.34 |  | 116.53
HOLLISTER 2105 | 182492105 | 166.22 |  | 65.53 |  | 100.69
HOLLISTER 2106 | 182492106 | 39.34 |  | 8.1 |  | 31.24
HOLLYWOOD 0401 | 13170401 | 5.36 |  | 2.78 |  | 2.58
HONCUT 1101 | 103211101 | 99.13 |  |  |  | 99.13
HONCUT 1102 | 103211102 | 140.63 |  | 2.57 |  | 138.06
HOOPA 1101 | 192401101 | 136.75 | 4.9 | 99.36 |  | 32.49
HOPLAND 1101 | 42251101 | 130.5 |  | 81.62 |  | 48.88
HORSESHOE 1101 | 152571101 | 35.08 |  | 3.86 |  | 31.22
HORSESHOE 1102 | 152571102 | 14.84 |  |  |  | 14.84
HORSESHOE 1103 | 152571103 | 5.26 |  |  |  | 5.26
HORSESHOE 1104 | 152571104 | 11.67 |  | 1.98 |  | 9.69
HORSESHOE 1105 | 152571105 | 2.27 |  |  |  | 2.27
HORSESHOE 1106 | 152571106 | 15.37 |  |  |  | 15.37
HUMBOLDT BAY 1101 | 192341101 | 12.98 |  |  |  | 12.98
HUMBOLDT BAY 1102 | 192341102 | 41.6 |  | 6.35 |  | 35.25
HUNTERS POINT (P) 1101 | 22331101 | 3.75 |  |  |  | 3.75
HUNTERS POINT (P) 1102 | 22331102 | 8.31 |  |  |  | 8.31
HUNTERS POINT (P) 1103 | 22331103 | 5.81 |  |  |  | 5.81
HUNTERS POINT (P) 1104 | 22331104 | 3.61 |  |  |  | 3.61
HUNTERS POINT (P) 1105 | 22331105 | 10.45 |  |  |  | 10.45
HUNTERS POINT (P) 1106 | 22331106 | 1.54 |  |  |  | 1.54
HUNTERS POINT (P) 1107 | 22331107 | 5.25 |  |  |  | 5.25
HUNTERS POINT (P) 1108 | 22331108 | 5.6 |  |  |  | 5.6
HUNTERS POINT (P) 1109 | 22331109 | 1.61 |  |  |  | 1.61
HURON 1106 | 253161106 | 17.08 |  |  |  | 17.08
HURON 1107 | 253161107 | 0.35 |  |  |  | 0.35
HURON 1108 | 253161108 | 10.27 |  |  |  | 10.27
HURON 1109 | 253161109 | 0.35 |  |  |  | 0.35
HURON 1112 | 253161112 | 13.79 |  |  |  | 13.79
HURON 1116 | 253161116 | 19.97 |  |  |  | 19.97
IGNACIO 1101 | 42481101 | 11.68 | 0.5 | 5.76 |  | 5.42
IGNACIO 1102 | 42481102 | 8.48 |  |  |  | 8.48
IGNACIO 1103 | 42481103 | 2.78 |  | 0.62 |  | 2.16
IGNACIO 1104 | 42481104 | 57.26 |  | 6.33 |  | 50.93
IGNACIO 1105 | 42481105 | 20.24 |  | 4.72 |  | 15.52
INDIAN FLAT 1104 | 252691104 | 16.1 |  | 16.1 |  | 0
INDUSTRIAL ACRES 0411 | 182300411 | 2.04 |  |  |  | 2.04
INDUSTRIAL ACRES 0412 | 182300412 | 9.8 |  |  |  | 9.8
INDUSTRIAL ACRES 0413 | 182300413 | 3.78 |  |  |  | 3.78
INDUSTRIAL ACRES 0415 | 182300415 | 1.43 |  |  |  | 1.43
IONE 1101 | 163881101 | 29.02 |  | 14.91 |  | 14.11
JACINTO 1101 | 102851101 | 76.85 |  |  |  | 76.85
JACINTO 1102 | 102851102 | 80.86 |  |  |  | 80.86
JACOBS CORNER 1101 | 254771101 | 62.41 |  |  |  | 62.41
JACOBS CORNER 1102 | 254771102 | 51.64 |  |  |  | 51.64
JAMESON 1101 | 63801101 | 0.01 |  |  |  | 0.01
JAMESON 1102 | 63801102 | 19.8 |  | 7.85 |  | 11.95
JAMESON 1103 | 63801103 | 10.83 |  | 2.19 |  | 8.64
JAMESON 1104 | 63801104 | 0.08 |  |  |  | 0.08
JAMESON 1105 | 63801105 | 53.53 |  | 6.69 |  | 46.84
JANES CREEK 1101 | 192391101 | 29.39 |  |  |  | 29.39
JANES CREEK 1102 | 192391102 | 6.28 |  |  |  | 6.28
JANES CREEK 1103 | 192391103 | 41.76 |  |  |  | 41.76
JANES CREEK 1104 | 192391104 | 2.59 |  |  |  | 2.59
JARVIS 1101 | 13501101 | 13.75 |  | 0.58 |  | 13.17
JARVIS 1103 | 13501103 | 3.43 |  |  |  | 3.43
JARVIS 1104 | 13501104 | 4.43 |  |  |  | 4.43
JARVIS 1105 | 13501105 | 7.99 |  |  |  | 7.99
JARVIS 1106 | 13501106 | 4.8 |  |  |  | 4.8
JARVIS 1108 | 13501108 | 17.76 |  | 0.7 |  | 17.06
JARVIS 1109 | 13501109 | 4.17 |  |  |  | 4.17
JARVIS 1110 | 13501110 | 5.96 |  |  |  | 5.96
JARVIS 1111 | 13501111 | 19.01 | 0.87 | 0.03 |  | 18.11
JARVIS 1112 | 13501112 | 7.28 |  |  |  | 7.28
JERSEY ISLAND 0401 | 18320401 | 2.77 |  |  |  | 2.77
JESSUP 1101 | 103441101 | 79.74 | 0.2 | 63.76 |  | 15.78
JESSUP 1102 | 103441102 | 70.7 |  | 38.1 |  | 32.6
JESSUP 1103 | 103441103 | 36.92 |  | 2.77 |  | 34.15
JOLON 1102 | 182981102 | 105.97 |  | 65.47 |  | 40.5
JOLON 1103 | 182981103 | 18.59 |  | 12.51 |  | 6.08
JUDAH 0401 | 22400401 | 3.72 |  |  |  | 3.72
JUDAH 0402 | 22400402 | 2.16 |  |  |  | 2.16
KANAKA 1101 | 103221101 | 70.58 | 45.46 | 25.13 |  | -0.01
KEARNEY 1104 | 252701104 | 73.23 |  |  |  | 73.23
KEARNEY 1106 | 252701106 | 39.3 |  |  |  | 39.3
KEARNEY 1110 | 252701110 | 50.58 |  |  |  | 50.58
KEARNEY 1113 | 252701113 | 0.63 |  |  |  | 0.63
KEARNEY 1114 | 252701114 | 13.37 |  |  |  | 13.37
KERCKHOFF 1101 | 252561101 | 34.07 |  | 34.07 |  | 0
KERMAN 1101 | 252711101 | 145.52 |  |  |  | 145.52
KERMAN 1102 | 252711102 | 58.54 |  |  |  | 58.54
KERMAN 1103 | 252711103 | 56.54 |  |  |  | 56.54
KERMAN 1104 | 252711104 | 66.04 |  |  |  | 66.04
KERMAN 1106 | 252711106 | 75.53 |  |  |  | 75.53
KERMAN 1108 | 252711108 | 28.17 |  |  |  | 28.17
KERN OIL 1103 | 252721103 | 11.46 |  |  |  | 11.46
KERN OIL 1104 | 252721104 | 39.15 |  |  |  | 39.15
KERN OIL 1106 | 252721106 | 43.12 |  | 1.31 |  | 41.81
KERN OIL 1107 | 252721107 | 23.9 |  |  |  | 23.9
KERN OIL 1108 | 252721108 | 7.28 |  |  |  | 7.28
KERN OIL 1109 | 252721109 | 11.31 |  |  |  | 11.31
KERN OIL 1110 | 252721110 | 8.62 |  |  |  | 8.62
KERN OIL 1112 | 252721112 | 0.07 |  |  |  | 0.07
KERN OIL 1114 | 252721114 | 21.56 |  |  |  | 21.56
KERN OIL 1116 | 252721116 | 2.08 |  |  |  | 2.08
KERN POWER 2101 | 255262101 | 1.99 |  |  |  | 1.99
KERN POWER 2102 | 255262102 | 4.37 |  |  |  | 4.37
KERN POWER 2103 | 255262103 | 12.52 |  |  |  | 12.52
KERN POWER 2104 | 255262104 | 5.06 |  |  |  | 5.06
KERN POWER 2105 | 255262105 | 12.06 |  |  |  | 12.06
KESWICK 1101 | 103451101 | 51.43 | 48.06 | 3.31 |  | 0.06
KETTLEMAN HILLS 1101 | 252731101 | 34.52 |  |  |  | 34.52
KETTLEMAN HILLS 2104 | 252732104 | 29.31 |  |  |  | 29.31
KING CITY 1101 | 182031101 | 6.97 |  |  |  | 6.97
KING CITY 1102 | 182031102 | 21.49 |  |  |  | 21.49
KING CITY 1103 | 182031103 | 27.81 |  | 17.75 |  | 10.06
KING CITY 1104 | 182031104 | 13.94 |  |  |  | 13.94
KING CITY 1105 | 182031105 | 3.05 |  |  |  | 3.05
KING CITY 1106 | 182031106 | 71.86 |  |  |  | 71.86
KING CITY 1107 | 182031107 | 0.02 |  |  |  | 0.02
KING CITY 1108 | 182031108 | 0.02 |  |  |  | 0.02
KINGSBURG 1102 | 252241102 | 15.63 |  |  |  | 15.63
KINGSBURG 1108 | 252241108 | 41.16 |  |  |  | 41.16
KINGSBURG 1110 | 252241110 | 86.24 |  |  |  | 86.24
KINGSBURG 1111 | 252241111 | 81.99 |  |  |  | 81.99
KINGSBURG 1112 | 252241112 | 14.2 |  |  |  | 14.2
KINGSBURG 1113 | 252241113 | 51.59 |  |  |  | 51.59
KINGSBURG 1114 | 252241114 | 18.4 |  |  |  | 18.4
KINGSBURG 1116 | 252241116 | 113.91 |  |  |  | 113.91
KIRKER 2103 | 14452103 | 7.37 |  |  |  | 7.37
KIRKER 2104 | 14452104 | 17.24 |  | 4.01 |  | 13.23
KIRKER 2105 | 14452105 | 9.61 |  |  |  | 9.61
KIRKER 2106 | 14452106 | 18.12 |  |  |  | 18.12
KIRKER 2107 | 14452107 | 7.77 |  |  |  | 7.77
KIRKER 2108 | 14452108 | 10.22 |  |  |  | 10.22
KIRKER 2109 | 14452109 | 8.63 |  |  |  | 8.63
KNIGHTS LANDING 1101 | 62721101 | 45.14 |  |  |  | 45.14
KNIGHTS LANDING 1102 | 62721102 | 119.07 |  |  |  | 119.07
KONOCTI 1102 | 43311102 | 145.98 | 63.98 | 61.39 |  | 20.61
KONOCTI 1108 | 43311108 | 33.13 |  | 20.44 |  | 12.69
LAKEVIEW 1102 | 253411102 | 52.39 |  |  |  | 52.39
LAKEVIEW 1103 | 253411103 | 22.68 |  |  |  | 22.68
LAKEVIEW 1106 | 253411106 | 36.35 |  |  |  | 36.35
LAKEVIEW 1107 | 253411107 | 26.08 |  |  |  | 26.08
LAKEVILLE 1101 | 43371101 | 19.67 |  |  |  | 19.67
LAKEVILLE 1102 | 43371102 | 50.43 | 0.07 | 18.07 |  | 32.29
LAKEVILLE 1105 | 43371105 | 4.22 |  |  |  | 4.22
LAKEWOOD 1101 | 13531101 | 0.72 |  |  |  | 0.72
LAKEWOOD 1102 | 13531102 | 9.58 |  | 0.1 |  | 9.48
LAKEWOOD 1103 | 13531103 | 2.57 |  |  |  | 2.57
LAKEWOOD 1104 | 13531104 | 11.79 |  |  |  | 11.79
LAKEWOOD 2107 | 13532107 | 33.32 |  | 7.77 |  | 25.55
LAKEWOOD 2108 | 13532108 | 0.53 |  |  |  | 0.53
LAKEWOOD 2109 | 13532109 | 7.3 | 0.42 |  |  | 6.88
LAKEWOOD 2110 | 13532110 | 22.76 |  |  |  | 22.76
LAKEWOOD 2111 | 13532111 | 2.31 |  |  |  | 2.31
LAKEWOOD 2112 | 13532112 | 8.92 |  |  |  | 8.92
LAKEWOOD 2223 | 13532223 | 9.18 |  |  |  | 9.18
LAKEWOOD 2224 | 13532224 | 31.62 | 0.82 |  |  | 30.8
LAKEWOOD 2225 | 13532225 | 3.36 |  |  |  | 3.36
LAKEWOOD 2226 | 13532226 | 8.03 |  |  |  | 8.03
LAKEWOOD 2227 | 13532227 | 7.93 | 0.03 |  |  | 7.9
LAMMERS 1101 | 162771101 | 9.67 |  |  |  | 9.67
LAMMERS 1102 | 162771102 | 3.57 |  |  |  | 3.57
LAMMERS 1103 | 162771103 | 6.48 |  |  |  | 6.48
LAMMERS 1104 | 162771104 | 2.88 |  |  |  | 2.88
LAMMERS 1105 | 162771105 | 1.77 |  |  |  | 1.77
LAMMERS 1106 | 162771106 | 2.29 |  |  |  | 2.29
LAMMERS 1107 | 162771107 | 9.11 |  |  |  | 9.11
LAMMERS 1108 | 162771108 | 1.11 |  |  |  | 1.11
LAMONT 1102 | 253911102 | 44.95 |  |  |  | 44.95
LAMONT 1103 | 253911103 | 26.85 |  |  |  | 26.85
LAMONT 1104 | 253911104 | 76.74 |  | 4.88 |  | 71.86
LAMONT 1105 | 253911105 | 37.11 |  |  |  | 37.11
LAMONT 1106 | 253911106 | 22.56 |  |  |  | 22.56
LAMONT 1107 | 253911107 | 46.15 |  |  |  | 46.15
LARKIN (Y) 1107 | 22801107 | 2.35 |  |  |  | 2.35
LARKIN (Y) 1108 | 22801108 | 0.11 |  |  |  | 0.11
LARKIN (Y) 1109 | 22801109 | 0.3 |  |  |  | 0.3
LARKIN (Y) 1110 | 22801110 | 0.23 |  |  |  | 0.23
LARKIN (Y) 1111 | 22801111 | 0.12 |  |  |  | 0.12
LARKIN (Y) 1119 | 22801119 | 1.76 |  |  |  | 1.76
LARKIN (Y) 1120 | 22801120 | 2.12 |  |  |  | 2.12
LARKIN (Y) 1127 | 22801127 | 1.53 |  |  |  | 1.53
LARKIN (Y) 1128 | 22801128 | 0.11 |  |  |  | 0.11
LARKIN (Y) 1135 | 22801135 | 1.66 |  |  |  | 1.66
LARKIN (Y) 1136 | 22801136 | 1.3 |  |  |  | 1.3
LARKIN (Y) 1137 | 22801137 | 0.01 |  |  |  | 0.01
LARKIN (Y) 1138 | 22801138 | 1.48 |  |  |  | 1.48
LARKIN (Y) 1140 | 22801140 | 0.1 |  |  |  | 0.1
LARKIN (Y) 1141 | 22801141 | 0.03 |  |  |  | 0.03
LAS GALLINAS A 1103 | 42991103 | 5.28 |  |  |  | 5.28
LAS GALLINAS A 1104 | 42991104 | 12.96 |  | 0.28 |  | 12.68
LAS GALLINAS A 1105 | 42991105 | 20.37 | 7.19 | 2.93 |  | 10.25
LAS GALLINAS A 1106 | 42991106 | 15.86 | 0.02 | 1.16 |  | 14.68
LAS GALLINAS A 1107 | 42991107 | 8.06 |  | 0.02 |  | 8.04
LAS PALMAS 1101 | 254921101 | 0.27 |  |  |  | 0.27
LAS POSITAS 2103 | 14402103 | 2.99 |  |  |  | 2.99
LAS POSITAS 2104 | 14402104 | 11.42 |  |  |  | 11.42
LAS POSITAS 2105 | 14402105 | 3.76 |  |  |  | 3.76
LAS POSITAS 2106 | 14402106 | 18.08 |  |  |  | 18.08
LAS POSITAS 2107 | 14402107 | 11.24 |  |  |  | 11.24
LAS POSITAS 2108 | 14402108 | 20.05 |  | 6.8 |  | 13.25
LAS POSITAS 2109 | 14402109 | 11.55 |  |  |  | 11.55
LAS POSITAS 2110 | 14402110 | 19.73 |  |  |  | 19.73
LAS PULGAS 0401 | 24120401 | 8.91 |  | 1.98 |  | 6.93
LAS PULGAS 0402 | 24120402 | 2.58 |  |  |  | 2.58
LAS PULGAS 0403 | 24120403 | 7.86 |  |  |  | 7.86
LAS PULGAS 0404 | 24120404 | 4.08 |  |  |  | 4.08
LATHROP 0402 | 163030402 | 0.04 |  |  |  | 0.04
LAURELES 1111 | 182371111 | 106.28 | 5.72 | 99.48 |  | 1.08
LAURELES 1112 | 182371112 | 43.17 |  | 33.05 |  | 10.12
LAWNDALE 0401 | 22440401 | 4.75 |  |  |  | 4.75
LAWNDALE 0402 | 22440402 | 4.77 |  |  |  | 4.77
LAWRENCE 1102 | 83421102 | 0.08 |  |  |  | 0.08
LAWRENCE 1103 | 83421103 | 0.23 |  |  |  | 0.23
LAWRENCE 1104 | 83421104 | 9.35 |  |  |  | 9.35
LAWRENCE 1105 | 83421105 | 1.07 |  |  |  | 1.07
LAWRENCE 1106 | 83421106 | 2.77 |  |  |  | 2.77
LAWRENCE 1107 | 83421107 | 4.64 |  |  |  | 4.64
LAWRENCE 1108 | 83421108 | 0.86 |  |  |  | 0.86
LAWRENCE 1109 | 83421109 | 1.98 |  |  |  | 1.98
LAWRENCE 1110 | 83421110 | 4.93 |  |  |  | 4.93
LAWRENCE 1111 | 83421111 | 3.71 |  |  |  | 3.71
LAWRENCE 1112 | 83421112 | 11.12 |  |  |  | 11.12
LAWRENCE 1113 | 83421113 | 5.67 |  |  |  | 5.67
LAYTONVILLE 1101 | 42681101 | 93.78 |  | 65.96 |  | 27.82
LAYTONVILLE 1102 | 42681102 | 125.44 | 3.4 | 107.17 |  | 14.87
LE GRAND 1104 | 255361104 | 56.79 |  |  |  | 56.79
LE GRAND 1106 | 255361106 | 59.92 |  |  |  | 59.92
LE GRAND 1110 | 255361110 | 91.96 |  |  |  | 91.96
LE GRAND 1112 | 255361112 | 68.88 |  |  |  | 68.88
LEMOORE 1101 | 253601101 | 41.63 |  |  |  | 41.63
LEMOORE 1102 | 253601102 | 11.58 |  |  |  | 11.58
LEMOORE 1103 | 253601103 | 14.46 |  |  |  | 14.46
LEMOORE 1104 | 253601104 | 49.94 |  |  |  | 49.94
LEMOORE 1105 | 253601105 | 12.09 |  |  |  | 12.09
LERDO 1110 | 253491110 | 12.01 |  |  |  | 12.01
LERDO 1111 | 253491111 | 35.93 |  |  |  | 35.93
LERDO 1112 | 253491112 | 38.53 |  |  |  | 38.53
LERDO 1113 | 253491113 | 38.52 |  |  |  | 38.52
LERDO 1114 | 253491114 | 9.95 |  |  |  | 9.95
LERDO 1115 | 253491115 | 15.98 |  |  |  | 15.98
LERDO 1116 | 253491116 | 31.85 |  |  |  | 31.85
LINCOLN 1101 | 153701101 | 50.59 |  | 16.39 |  | 34.2
LINCOLN 1102 | 153701102 | 9.59 |  |  |  | 9.59
LINCOLN 1104 | 153701104 | 132.93 |  | 30.42 |  | 102.51
LINCOLN 1105 | 153701105 | 32.27 |  |  |  | 32.27
LINCOLN 2108 | 153702108 | 1.63 |  |  |  | 1.63
LINCOLN 2109 | 153702109 | 0.82 |  |  |  | 0.82
LINDEN 1101 | 162071101 | 34.79 |  |  |  | 34.79
LINDEN 1103 | 162071103 | 60.1 |  |  |  | 60.1
LINDEN 1104 | 162071104 | 72.27 |  |  |  | 72.27
LIVE OAK 1101 | 153771101 | 44.62 |  |  |  | 44.62
LIVE OAK 1102 | 153771102 | 25.75 |  |  |  | 25.75
LIVE OAK 1104 | 153771104 | 113.48 |  |  |  | 113.48
LIVERMORE 1101 | 12141101 | 6.06 |  |  |  | 6.06
LIVERMORE 1102 | 12141102 | 4.24 |  |  |  | 4.24
LIVERMORE 1103 | 12141103 | 4.66 |  |  |  | 4.66
LIVERMORE 1104 | 12141104 | 8.63 |  |  |  | 8.63
LIVINGSTON 1101 | 252261101 | 103.24 |  |  |  | 103.24
LIVINGSTON 1102 | 252261102 | 13.63 |  |  |  | 13.63
LIVINGSTON 1104 | 252261104 | 50.67 |  |  |  | 50.67
LIVINGSTON 1105 | 252261105 | 88.72 |  |  |  | 88.72
LIVINGSTON 1106 | 252261106 | 62.3 |  |  |  | 62.3
LLAGAS 2101 | 83182101 | 102.13 |  | 21.38 |  | 80.75
LLAGAS 2102 | 83182102 | 12.7 |  |  |  | 12.7
LLAGAS 2103 | 83182103 | 16.74 |  |  |  | 16.74
LLAGAS 2104 | 83182104 | 30.02 |  | 2.68 |  | 27.34
LLAGAS 2105 | 83182105 | 17.66 | 0.12 | 0.46 |  | 17.08
LLAGAS 2106 | 83182106 | 32.26 |  | 1.18 |  | 31.08
LLAGAS 2107 | 83182107 | 22.35 | 3.63 | 2.65 |  | 16.07
LOCKEFORD 2101 | 163682101 | 90.81 |  |  |  | 90.81
LOCKEFORD 2102 | 163682102 | 242.58 |  |  |  | 242.58
LOCKHEED NO 2 1103 | 83001103 | 0.52 |  |  |  | 0.52
LOCKHEED NO 2 1106 | 83001106 | 0.37 |  |  |  | 0.37
LOCKHEED NO 2 1107 | 83001107 | 0.77 |  |  |  | 0.77
LOCKHEED NO 2 1108 | 83001108 | 1.25 |  |  |  | 1.25
LODI 1101 | 162111101 | 44.34 |  |  |  | 44.34
LODI 1102 | 162111102 | 97.2 |  |  |  | 97.2
LOGAN CREEK 2101 | 103142101 | 163.39 |  |  |  | 163.39
LOGAN CREEK 2102 | 103142102 | 241.65 |  | 3.48 |  | 238.17
LOGAN CREEK 2103 | 103142103 | 3.17 |  |  |  | 3.17
LOGAN CREEK 2199 | 103142199 | 0.03 |  |  |  | 0.03
LONE TREE 2101 | 13232101 | 1.11 |  |  |  | 1.11
LONE TREE 2102 | 13232102 | 14.75 |  |  |  | 14.75
LONE TREE 2105 | 13232105 | 21.74 |  | 10.65 |  | 11.09
LOS ALTOS 1103 | 82241103 | 6.82 |  |  |  | 6.82
LOS ALTOS 1104 | 82241104 | 12.93 |  |  |  | 12.93
LOS ALTOS 1105 | 82241105 | 1.82 |  |  |  | 1.82
LOS ALTOS 1106 | 82241106 | 9.98 |  |  |  | 9.98
LOS ALTOS 1107 | 82241107 | 2.97 |  |  |  | 2.97
LOS COCHES 1101 | 182151101 | 24.5 |  | 2.3 |  | 22.2
LOS COCHES 1102 | 182151102 | 29.13 |  |  |  | 29.13
LOS GATOS 1101 | 82021101 | 20.99 |  | 11.8 |  | 9.19
LOS GATOS 1102 | 82021102 | 6.16 |  | 1.09 |  | 5.07
LOS GATOS 1106 | 82021106 | 70.72 | 67.45 | 2.43 |  | 0.84
LOS GATOS 1107 | 82021107 | 94.15 | 80.66 | 12.72 |  | 0.77
LOS GATOS 1108 | 82021108 | 6.2 | 1.13 | 3.29 |  | 1.78
LOS MOLINOS 1101 | 103481101 | 55.89 |  | 0.19 |  | 55.7
LOS MOLINOS 1102 | 103481102 | 59.17 |  |  |  | 59.17
LOS OSITOS 2101 | 182082101 | 110.05 |  |  |  | 110.05
LOS OSITOS 2102 | 182082102 | 51.61 |  | 2.48 |  | 49.13
LOS OSITOS 2103 | 182082103 | 102.7 |  | 44.33 |  | 58.37
LOST HILLS 1101 | 254281101 | 0.01 |  |  |  | 0.01
LOW GAP 1101 | 192411101 | 72.34 |  | 70.63 |  | 1.71
LOYOLA 0401 | 82160401 | 8.3 |  |  |  | 8.3
LOYOLA 0403 | 82160403 | 8.93 |  |  |  | 8.93
LOYOLA 1101 | 82161101 | 19.37 |  |  |  | 19.37
LOYOLA 1102 | 82161102 | 51 |  | 0.02 |  | 50.98
LUCERNE 1103 | 43351103 | 52.94 |  | 26.84 |  | 26.1
LUCERNE 1106 | 43351106 | 47.7 |  | 36.83 |  | 10.87
MABURY 1103 | 82191103 | 7.95 |  |  |  | 7.95
MABURY 1104 | 82191104 | 13.9 |  |  |  | 13.9
MABURY 1105 | 82191105 | 5.04 |  |  |  | 5.04
MABURY 1106 | 82191106 | 15.13 |  |  |  | 15.13
MADERA 1102 | 252761102 | 0.02 |  |  |  | 0.02
MADERA 1104 | 252761104 | 12.86 |  |  |  | 12.86
MADERA 1106 | 252761106 | 8.73 |  |  |  | 8.73
MADERA 1112 | 252761112 | 12.31 |  |  |  | 12.31
MADERA 1114 | 252761114 | 11.56 |  |  |  | 11.56
MADERA 1116 | 252761116 | 19.96 |  |  |  | 19.96
MADERA 1118 | 252761118 | 8.88 |  |  |  | 8.88
MADERA 1119 | 252761119 | 111.93 |  |  |  | 111.93
MADISON 1103 | 63171103 | 73.12 |  |  |  | 73.12
MADISON 1105 | 63171105 | 84.75 |  | 0.35 |  | 84.4
MADISON 2101 | 63172101 | 167.26 |  | 5.25 |  | 162.01
MAGUNDEN 1101 | 252771101 | 19.61 |  |  |  | 19.61
MAGUNDEN 1104 | 252771104 | 8.12 |  |  |  | 8.12
MAGUNDEN 1105 | 252771105 | 11.73 |  |  |  | 11.73
MAGUNDEN 1106 | 252771106 | 7.4 |  |  |  | 7.4
MAGUNDEN 1108 | 252771108 | 30.64 |  | 3.86 |  | 26.78
MAGUNDEN 2108 | 252772108 | 42.52 |  |  |  | 42.52
MAGUNDEN 2109 | 252772109 | 14.47 |  |  |  | 14.47
MAINE PRAIRIE 0401 | 68670401 | 0.06 |  |  |  | 0.06
MALAGA 1101 | 254251101 | 3.52 |  |  |  | 3.52
MALAGA 1102 | 254251102 | 55.53 |  |  |  | 55.53
MALAGA 1103 | 254251103 | 19.84 |  |  |  | 19.84
MALAGA 1104 | 254251104 | 15.41 |  |  |  | 15.41
MALAGA 1105 | 254251105 | 0.64 |  |  |  | 0.64
MALAGA 1106 | 254251106 | 8.97 |  |  |  | 8.97
MALAGA 1107 | 254251107 | 2.67 |  |  |  | 2.67
MALAGA 1108 | 254251108 | 21.92 |  |  |  | 21.92
MALAGA 1109 | 254251109 | 3.35 |  |  |  | 3.35
MALAGA 1110 | 254251110 | 15.45 |  |  |  | 15.45
MALAGA 1111 | 254251111 | 7.08 |  |  |  | 7.08
MANCHESTER 1101 | 253921101 | 11.88 |  |  |  | 11.88
MANCHESTER 1102 | 253921102 | 13.66 |  |  |  | 13.66
MANCHESTER 1103 | 253921103 | 12.17 |  |  |  | 12.17
MANCHESTER 1104 | 253921104 | 3.98 |  |  |  | 3.98
MANCHESTER 1105 | 253921105 | 9.1 |  |  |  | 9.1
MANCHESTER 1106 | 253921106 | 15.01 |  |  |  | 15.01
MANCHESTER 1107 | 253921107 | 8.73 |  |  |  | 8.73
MANCHESTER 1108 | 253921108 | 14.83 |  |  |  | 14.83
MANCHESTER 1109 | 253921109 | 15.79 |  |  |  | 15.79
MANCHESTER 1110 | 253921110 | 14.49 |  |  |  | 14.49
MANCHESTER 1111 | 253921111 | 13.27 |  |  |  | 13.27
MANCHESTER 1112 | 253921112 | 16 |  |  |  | 16
MANTECA 1701 | 162611701 | 6.17 |  |  |  | 6.17
MANTECA 1702 | 162611702 | 14.15 |  |  |  | 14.15
MANTECA 1703 | 162611703 | 15.73 |  |  |  | 15.73
MANTECA 1704 | 162611704 | 7.59 |  |  |  | 7.59
MANTECA 1705 | 162611705 | 34.89 |  |  |  | 34.89
MANTECA 1706 | 162611706 | 7.52 |  |  |  | 7.52
MANTECA 1707 | 162611707 | 7.97 |  |  |  | 7.97
MANTECA 1708 | 162611708 | 9.53 |  |  |  | 9.53
MAPLE 0401 | 13520401 | 3.67 |  |  |  | 3.67
MAPLE CREEK 1101 | 192101101 | 32.82 |  | 9.29 |  | 23.53
MARICOPA 1101 | 254211101 | 37.74 |  |  |  | 37.74
MARICOPA 1102 | 254211102 | 37.81 |  |  |  | 37.81
MARINA (F) 0401 | 22780401 | 0.53 |  |  |  | 0.53
MARINA (F) 0402 | 22780402 | 0.49 |  |  |  | 0.49
MARINA (F) 0403 | 22780403 | 0.04 |  |  |  | 0.04
MARINA (F) 0404 | 22780404 | 0.37 |  |  |  | 0.37
MARINA (F) 0405 | 22780405 | 0.14 |  |  |  | 0.14
MARINA (F) 0407 | 22780407 | 1.42 |  |  |  | 1.42
MARINA (F) 0408 | 22780408 | 0.53 |  |  |  | 0.53
MARINA (F) 1101 | 22781101 | 0 |  |  |  | 0
MARINA (F) 1102 | 22781102 | 0 |  |  |  | 0
MARINA (F) 1103 | 22781103 | 0.98 |  |  |  | 0.98
MARIPOSA 2101 | 254452101 | 253.04 | 71.56 | 176.54 |  | 4.94
MARIPOSA 2102 | 254452102 | 257.5 | 56.88 | 187.67 |  | 12.95
MARIPOSA REMOTE 0001 0001 | 257010001 | 0.01 |  | 0.01 |  | 0
MARIPOSA REMOTE 0002 0002 | 257010002 | 0.01 | 0.01 |  |  | 0
MARTELL 1101 | 163011101 | 82.14 |  | 69.85 |  | 12.29
MARTELL 1102 | 163011102 | 12.12 |  | 6.89 |  | 5.23
MARTELL 1103 | 163011103 | 29.35 |  | 20.32 |  | 9.03
MARYSVILLE 1102 | 152011102 | 7.48 |  |  |  | 7.48
MARYSVILLE 1103 | 152011103 | 12.43 |  |  |  | 12.43
MARYSVILLE 1104 | 152011104 | 5.59 |  |  |  | 5.59
MARYSVILLE 1105 | 152011105 | 8.62 |  |  |  | 8.62
MARYSVILLE 1106 | 152011106 | 3.56 |  |  |  | 3.56
MARYSVILLE 1107 | 152011107 | 8.56 |  |  |  | 8.56
MARYSVILLE 1108 | 152011108 | 51.59 |  |  |  | 51.59
MAXWELL 1102 | 62881102 | 60.6 |  |  |  | 60.6
MAXWELL 1105 | 62881105 | 88.74 |  | 3.9 |  | 84.84
MAXWELL 1106 | 62881106 | 29.61 |  |  |  | 29.61
MC ARTHUR 1101 | 103491101 | 179.76 |  | 64.86 |  | 114.9
MC ARTHUR 1102 | 103491102 | 30.23 |  | 1.1 |  | 29.13
MC CALL 1101 | 254121101 | 95.15 |  |  |  | 95.15
MC CALL 1102 | 254121102 | 25.18 |  |  |  | 25.18
MC CALL 1103 | 254121103 | 17.29 |  |  |  | 17.29
MC CALL 1104 | 254121104 | 16.72 |  |  |  | 16.72
MC CALL 1105 | 254121105 | 15.22 |  |  |  | 15.22
MC CALL 1106 | 254121106 | 73.85 |  |  |  | 73.85
MC CALL 1107 | 254121107 | 82.56 |  |  |  | 82.56
MC CALL 1108 | 254121108 | 58.49 |  |  |  | 58.49
MC FARLAND 1101 | 253181101 | 14.02 |  |  |  | 14.02
MC FARLAND 1102 | 253181102 | 42.08 |  |  |  | 42.08
MC FARLAND 1104 | 253181104 | 37.96 |  |  |  | 37.96
MC FARLAND 1105 | 253181105 | 19.86 |  |  |  | 19.86
MC KEE 1103 | 83531103 | 22.1 |  | 0.58 |  | 21.52
MC KEE 1104 | 83531104 | 15.51 |  |  |  | 15.51
MC KEE 1105 | 83531105 | 8.39 |  |  |  | 8.39
MC KEE 1106 | 83531106 | 15.26 |  |  |  | 15.26
MC KEE 1107 | 83531107 | 38.23 |  | 2.68 |  | 35.55
MC KEE 1108 | 83531108 | 10.46 |  | 0.66 |  | 9.8
MC KEE 1109 | 83531109 | 1.77 |  |  |  | 1.77
MC KEE 1110 | 83531110 | 1.67 |  |  |  | 1.67
MC KEE 1111 | 83531111 | 26.76 |  | 8.71 |  | 18.05
MC KEE 1112 | 83531112 | 16.75 |  |  |  | 16.75
MC MULLIN 1104 | 254411104 | 62.27 |  |  |  | 62.27
MC MULLIN 1105 | 254411105 | 58 |  |  |  | 58
MC MULLIN 1106 | 254411106 | 94.05 |  |  |  | 94.05
MCKITTRICK 1101 | 252781101 | 51.1 |  |  |  | 51.1
MEADOW LANE 2102 | 14302102 | 0.01 |  |  |  | 0.01
MEADOW LANE 2103 | 14302103 | 18.88 |  |  |  | 18.88
MEADOW LANE 2104 | 14302104 | 4.19 |  |  |  | 4.19
MEADOW LANE 2105 | 14302105 | 14.39 |  |  |  | 14.39
MEADOW LANE 2106 | 14302106 | 23.29 | 0.74 | 0.11 |  | 22.44
MEADOW LANE 2107 | 14302107 | 8.48 |  |  |  | 8.48
MEADOW LANE 2108 | 14302108 | 23.99 |  |  |  | 23.99
MEADOW LANE 2109 | 14302109 | 0.58 |  |  |  | 0.58
MEADOW LANE 2110 | 14302110 | 6.57 |  |  |  | 6.57
MENDOCINO 1101 | 42951101 | 74.7 | 13.34 | 18.78 |  | 42.58
MENDOCINO 1102 | 42951102 | 0.05 |  |  |  | 0.05
MENDOTA 1101 | 252311101 | 14.82 |  |  |  | 14.82
MENDOTA 1102 | 252311102 | 98.29 |  |  |  | 98.29
MENDOTA 1103 | 252311103 | 15.32 |  |  |  | 15.32
MENDOTA 1104 | 252311104 | 54.69 |  |  |  | 54.69
MENLO 0401 | 24130401 | 7.16 |  |  |  | 7.16
MENLO 0402 | 24130402 | 7.57 |  |  |  | 7.57
MENLO 0403 | 24130403 | 7.62 |  |  |  | 7.62
MENLO 0404 | 24130404 | 8.21 |  |  |  | 8.21
MENLO 1101 | 24131101 | 1.51 |  |  |  | 1.51
MENLO 1102 | 24131102 | 63.75 | 0.01 | 28.28 |  | 35.46
MENLO 1103 | 24131103 | 56.45 |  | 39.13 |  | 17.32
MENLO 1104 | 24131104 | 16.83 |  |  |  | 16.83
MERCED 1108 | 252801108 | 69.53 |  |  |  | 69.53
MERCED 1114 | 252801114 | 58.11 |  |  |  | 58.11
MERCED 1116 | 252801116 | 77.62 |  |  |  | 77.62
MERCED 2101 | 252802101 | 40.16 |  |  |  | 40.16
MERCED 2102 | 252802102 | 26 |  |  |  | 26
MERCED FALLS 1102 | 252811102 | 153.39 |  | 93.49 |  | 59.9
MERIDIAN 1101 | 62541101 | 57.79 |  |  |  | 57.79
MERIDIAN 1102 | 62541102 | 71.93 |  |  |  | 71.93
MESA 1101 | 182821101 | 82.23 | 11.15 | 37.59 |  | 33.49
MESA 1102 | 182821102 | 35.33 |  |  |  | 35.33
MESA 1103 | 182821103 | 75.94 |  | 9.99 |  | 65.95
MESA 1104 | 182821104 | 35.06 |  |  |  | 35.06
METTLER 1109 | 163701109 | 20.41 |  |  |  | 20.41
METTLER 1110 | 163701110 | 38.03 |  |  |  | 38.03
MIDDLE RIVER 1101 | 162091101 | 31.37 |  |  |  | 31.37
MIDDLE RIVER 1102 | 162091102 | 32.1 |  |  |  | 32.1
MIDDLE RIVER 1103 | 162091103 | 28.63 |  |  |  | 28.63
MIDDLETOWN 1101 | 43141101 | 100.89 | 75.54 | 9.22 |  | 16.13
MIDDLETOWN 1102 | 43141102 | 48.15 | 0.04 | 36.22 |  | 11.89
MIDDLETOWN 1103 | 43141103 | 38.53 | 4.85 | 13.86 |  | 19.82
MIDWAY 1101 | 252611101 | 60.32 |  |  |  | 60.32
MIDWAY 1102 | 252611102 | 52.64 |  |  |  | 52.64
MIDWAY 1103 | 252611103 | 30.77 |  |  |  | 30.77
MIDWAY 1104 | 252611104 | 36.86 |  |  |  | 36.86
MILLBRAE 0401 | 22690401 | 2.82 |  |  |  | 2.82
MILLBRAE 0403 | 22690403 | 4.93 |  |  |  | 4.93
MILLBRAE 0404 | 22690404 | 7.11 |  |  |  | 7.11
MILLBRAE 1101 | 22691101 | 4.01 |  |  |  | 4.01
MILLBRAE 1102 | 22691102 | 4.78 |  |  |  | 4.78
MILLBRAE 1103 | 22691103 | 0.18 |  |  |  | 0.18
MILLBRAE 1104 | 22691104 | 15.86 |  |  |  | 15.86
MILLBRAE 1105 | 22691105 | 0.26 |  |  |  | 0.26
MILLBRAE 1106 | 22691106 | 3.62 |  |  |  | 3.62
MILLBRAE 1107 | 22691107 | 4.76 |  |  |  | 4.76
MILLBRAE 1108 | 22691108 | 14.21 |  |  |  | 14.21
MILPITAS 1101 | 82831101 | 4.1 |  |  |  | 4.1
MILPITAS 1103 | 82831103 | 0.07 |  |  |  | 0.07
MILPITAS 1104 | 82831104 | 1.04 |  |  |  | 1.04
MILPITAS 1105 | 82831105 | 4.83 |  | 0.07 |  | 4.76
MILPITAS 1106 | 82831106 | 3.14 |  |  |  | 3.14
MILPITAS 1108 | 82831108 | 13.34 |  | 0.02 |  | 13.32
MILPITAS 1109 | 82831109 | 49.33 |  | 29.7 |  | 19.63
MILPITAS 2110 | 82832110 | 10.39 |  |  |  | 10.39
MILPITAS 2111 | 82832111 | 0.58 |  |  |  | 0.58
MILPITAS 2112 | 82832112 | 0.87 |  |  |  | 0.87
MILPITAS 2113 | 82832113 | 0.12 |  |  |  | 0.12
MILPITAS 2114 | 82832114 | 0.17 |  |  |  | 0.17
MIRA VISTA 0401 | 12330401 | 8.85 |  |  |  | 8.85
MIRA VISTA 0403 | 12330403 | 7.14 |  |  |  | 7.14
MIRABEL 1101 | 42091101 | 51.33 | 19.92 | 8.95 |  | 22.46
MIRABEL 1102 | 42091102 | 57.62 | 31.85 | 4.83 |  | 20.94
MISSION (X) 0401 | 22010401 | 1.64 |  |  |  | 1.64
MISSION (X) 1102 | 22011102 | 0.17 |  |  |  | 0.17
MISSION (X) 1108 | 22011108 | 5.29 |  |  |  | 5.29
MISSION (X) 1109 | 22011109 | 1.13 |  |  |  | 1.13
MISSION (X) 1110 | 22011110 | 5.74 |  |  |  | 5.74
MISSION (X) 1113 | 22011113 | 2.66 |  |  |  | 2.66
MISSION (X) 1116 | 22011116 | 3.04 |  |  |  | 3.04
MISSION (X) 1118 | 22011118 | 0.6 |  |  |  | 0.6
MISSION (X) 1124 | 22011124 | 0.71 |  |  |  | 0.71
MISSION (X) 1125 | 22011125 | 1.07 |  |  |  | 1.07
MISSION (X) 1127 | 22011127 | 0.56 |  |  |  | 0.56
MISSION (X) 1128 | 22011128 | 0.77 |  |  |  | 0.77
MIWUK 1701 | 163661701 | 76.19 | 74.65 | 1.54 |  | 0
MIWUK 1702 | 163661702 | 74.57 | 71.93 | 2.64 |  | 0
MOLINO 1101 | 42571101 | 90.12 | 7.16 | 26.49 |  | 56.47
MOLINO 1102 | 42571102 | 161.55 | 90.08 | 19.89 |  | 51.58
MOLINO 1103 | 42571103 | 78.42 |  |  |  | 78.42
MOLINO 1104 | 42571104 | 61.24 |  | 2.38 |  | 58.86
MONARCH 0401 | 162300401 | 3.26 |  |  |  | 3.26
MONARCH 0402 | 162300402 | 2.87 |  |  |  | 2.87
MONARCH 0403 | 162300403 | 4.67 |  |  |  | 4.67
MONROE 1104 | 43301104 | 5.24 |  |  |  | 5.24
MONROE 1105 | 43301105 | 10.7 |  |  |  | 10.7
MONROE 1106 | 43301106 | 13.51 |  |  |  | 13.51
MONROE 2102 | 43302102 | 4.76 |  |  |  | 4.76
MONROE 2103 | 43302103 | 11.53 | 0.45 |  |  | 11.08
MONROE 2107 | 43302107 | 10.39 | 0.61 |  |  | 9.78
MONTAGUE 2101 | 83892101 | 0.87 |  |  |  | 0.87
MONTAGUE 2102 | 83892102 | 0.81 |  |  |  | 0.81
MONTAGUE 2103 | 83892103 | 0.94 |  |  |  | 0.94
MONTAGUE 2104 | 83892104 | 0.84 |  |  |  | 0.84
MONTAGUE 2105 | 83892105 | 0.78 |  |  |  | 0.78
MONTAGUE 2106 | 83892106 | 0 |  |  |  | 0
MONTAGUE 2108 | 83892108 | 2.14 |  |  |  | 2.14
MONTAGUE 2109 | 83892109 | 0.81 |  |  |  | 0.81
MONTE RIO 1111 | 42811111 | 63.98 | 43.71 | 13.46 |  | 6.81
MONTE RIO 1112 | 42811112 | 19.7 | 19.7 |  |  | 0
MONTE RIO 1113 | 42811113 | 61.11 | 61.11 |  |  | 0
MONTICELLO 1101 | 43051101 | 123.2 |  | 107.82 |  | 15.38
MORAGA 1101 | 13801101 | 37.71 | 19.7 | 11.31 |  | 6.7
MORAGA 1102 | 13801102 | 13.35 | 2.91 | 2.12 |  | 8.32
MORAGA 1103 | 13801103 | 17.53 | 0.12 | 2.04 |  | 15.37
MORAGA 1104 | 13801104 | 21.22 | 0.01 | 13.67 |  | 7.54
MORAGA 1105 | 13801105 | 19.74 | 6.87 | 0.81 |  | 12.06
MORGAN HILL 2104 | 83242104 | 20.83 |  | 5.75 |  | 15.08
MORGAN HILL 2105 | 83242105 | 82.23 | 14.12 | 35.87 |  | 32.24
MORGAN HILL 2106 | 83242106 | 39.1 |  | 0.12 |  | 38.98
MORGAN HILL 2108 | 83242108 | 13.12 |  |  |  | 13.12
MORGAN HILL 2109 | 83242109 | 26.36 |  | 2.48 |  | 23.88
MORGAN HILL 2110 | 83242110 | 32.64 |  | 2.21 |  | 30.43
MORGAN HILL 2111 | 83242111 | 72.25 | 16.45 | 34.85 |  | 20.95
MORMON 1101 | 163211101 | 65.53 |  |  |  | 65.53
MORMON 1102 | 163211102 | 68.66 |  |  |  | 68.66
MORMON 1103 | 163211103 | 23.52 |  |  |  | 23.52
MORRO BAY 1101 | 183011101 | 46.27 | 0.49 | 4.89 |  | 40.89
MORRO BAY 1102 | 183011102 | 57.89 | 4.03 | 17.89 |  | 35.97
MOSHER 2104 | 163722104 | 0.01 |  |  |  | 0.01
MOSHER 2107 | 163722107 | 3.13 |  |  |  | 3.13
MOSHER 2108 | 163722108 | 1.88 |  |  |  | 1.88
MOSHER 2110 | 163722110 | 2.19 |  |  |  | 2.19
MOSHER 2111 | 163722111 | 17.51 |  |  |  | 17.51
MOUNTAIN QUARRIES 2101 | 152282101 | 215.93 | 22.72 | 192.26 |  | 0.95
MOUNTAIN VIEW 1102 | 82031102 | 14.33 |  |  |  | 14.33
MOUNTAIN VIEW 1103 | 82031103 | 2.87 |  |  |  | 2.87
MOUNTAIN VIEW 1104 | 82031104 | 8.08 |  |  |  | 8.08
MOUNTAIN VIEW 1105 | 82031105 | 9.54 |  |  |  | 9.54
MOUNTAIN VIEW 1106 | 82031106 | 7.37 |  |  |  | 7.37
MOUNTAIN VIEW 1107 | 82031107 | 19.33 |  |  |  | 19.33
MOUNTAIN VIEW 1108 | 82031108 | 14.7 |  |  |  | 14.7
MOUNTAIN VIEW 1109 | 82031109 | 10.03 |  |  |  | 10.03
MOUNTAIN VIEW 1110 | 82031110 | 9.38 |  |  |  | 9.38
MOUNTAIN VIEW 1111 | 82031111 | 1.74 |  |  |  | 1.74
MOUNTAIN VIEW 1112 | 82031112 | 0.97 |  |  |  | 0.97
MOUNTAIN VIEW 1113 | 82031113 | 4.03 |  |  |  | 4.03
MOUNTAIN VIEW 1114 | 82031114 | 6.62 |  |  |  | 6.62
MT EDEN 1101 | 13761101 | 6.71 |  |  |  | 6.71
MT EDEN 1102 | 13761102 | 9 |  |  |  | 9
MT EDEN 1103 | 13761103 | 13.12 |  |  |  | 13.12
MT EDEN 1104 | 13761104 | 14.05 |  |  |  | 14.05
MT EDEN 1105 | 13761105 | 7.05 |  |  |  | 7.05
MT EDEN 1106 | 13761106 | 5.64 |  |  |  | 5.64
MT EDEN 1107 | 13761107 | 6.08 |  |  |  | 6.08
MT EDEN 1108 | 13761108 | 23.57 |  |  |  | 23.57
MT EDEN 1109 | 13761109 | 17.04 |  |  |  | 17.04
MT EDEN 1110 | 13761110 | 1.77 |  |  |  | 1.77
MT EDEN 1111 | 13761111 | 3.24 |  |  |  | 3.24
MT EDEN 1112 | 13761112 | 16.51 |  |  |  | 16.51
MT EDEN 1113 | 13761113 | 2.66 |  |  |  | 2.66
MT EDEN 1114 | 13761114 | 4.78 |  |  |  | 4.78
NAPA 1102 | 42021102 | 32.58 |  | 0.27 |  | 32.31
NAPA 1103 | 42021103 | 14.94 |  |  |  | 14.94
NAPA 1105 | 42021105 | 15.61 |  |  |  | 15.61
NAPA 1106 | 42021106 | 1.26 |  |  |  | 1.26
NAPA 1109 | 42021109 | 11.65 |  |  |  | 11.65
NAPA 1110 | 42021110 | 13.32 |  |  |  | 13.32
NAPA 1112 | 42021112 | 52 |  | 19.29 |  | 32.71
NARROWS 2101 | 153132101 | 61.48 |  | 61.48 |  | 0
NARROWS 2102 | 153132102 | 117.75 |  | 93.7 |  | 24.05
NARROWS 2104 | 153132104 | 0 |  | 0 |  | 0
NARROWS 2105 | 153132105 | 196.49 |  | 176.85 |  | 19.64
NARROWS PH 1151 | 153131151 | 0.2 |  | 0.2 |  | 0
NEW HOPE 1101 | 162081101 | 38.16 |  |  |  | 38.16
NEW HOPE 1102 | 162081102 | 50.76 |  |  |  | 50.76
NEWARK 12KV 1101 | 12221101 | 1.44 |  |  |  | 1.44
NEWARK 12KV 1102 | 12221102 | 8.44 |  |  |  | 8.44
NEWARK 12KV 1103 | 12221103 | 18.16 |  |  |  | 18.16
NEWARK 12KV 1104 | 12221104 | 0.22 |  |  |  | 0.22
NEWARK 12KV 1105 | 12221105 | 3.19 |  |  |  | 3.19
NEWARK 12KV 1106 | 12221106 | 18.36 |  |  |  | 18.36
NEWARK 12KV 1107 | 12221107 | 21.49 |  |  |  | 21.49
NEWARK 12KV 1108 | 12221108 | 0.95 |  |  |  | 0.95
NEWARK 21KV 2102 | 12232102 | 2.69 |  |  |  | 2.69
NEWARK 21KV 2103 | 12232103 | 17.87 |  |  |  | 17.87
NEWARK 21KV 2104 | 12232104 | 4.99 |  |  |  | 4.99
NEWARK 21KV 2105 | 12232105 | 2.52 |  |  |  | 2.52
NEWARK 21KV 2107 | 12232107 | 7.06 |  |  |  | 7.06
NEWARK 21KV 2108 | 12232108 | 4.82 |  |  |  | 4.82
NEWARK 21KV 2109 | 12232109 | 0 |  |  |  | 0
NEWARK 21KV 2110 | 12232110 | 3.14 |  |  |  | 3.14
NEWARK 21KV 2111 | 12232111 | 0 |  |  |  | 0
NEWBURG 1131 | 192151131 | 31.03 |  | 5.66 |  | 25.37
NEWBURG 1132 | 192151132 | 22.38 |  | 1.28 |  | 21.1
NEWBURG 1133 | 192151133 | 16.95 |  | 2.38 |  | 14.57
NEWHALL 1109 | 254461109 | 73.55 |  |  |  | 73.55
NEWHALL 1111 | 254461111 | 54.02 |  |  |  | 54.02
NEWMAN 1101 | 162741101 | 41.04 |  |  |  | 41.04
NEWMAN 1102 | 162741102 | 9.55 |  |  |  | 9.55
NEWMAN 1105 | 162741105 | 42.75 |  |  |  | 42.75
NEWMAN 1106 | 162741106 | 44.36 |  |  |  | 44.36
NORCO 1101 | 254691101 | 33.91 |  |  |  | 33.91
NORCO 1102 | 254691102 | 7.67 |  |  |  | 7.67
NORD 1103 | 103071103 | 18.58 |  |  |  | 18.58
NORD 1104 | 103071104 | 51.15 |  |  |  | 51.15
NORD 1105 | 103071105 | 7 |  |  |  | 7
NORD 1106 | 103071106 | 10.87 |  |  |  | 10.87
NORIEGA 0401 | 22510401 | 1.5 |  |  |  | 1.5
NORIEGA 0402 | 22510402 | 1.77 |  |  |  | 1.77
NORTECH 2107 | 82462107 | 0.1 |  |  |  | 0.1
NORTECH 2109 | 82462109 | 3.13 |  |  |  | 3.13
NORTECH 2110 | 82462110 | 9.49 |  |  |  | 9.49
NORTECH 2111 | 82462111 | 0.71 |  |  |  | 0.71
NORTH BRANCH 1101 | 163231101 | 12.92 |  | 11.65 |  | 1.27
NORTH DUBLIN 2101 | 14052101 | 1.87 |  | 1.4 |  | 0.47
NORTH DUBLIN 2103 | 14052103 | 21.74 |  | 18.67 |  | 3.07
NORTH TOWER 1102 | 42041102 | 18.76 |  |  |  | 18.76
NORTH TOWER 1103 | 42041103 | 13.11 |  |  |  | 13.11
NORTH TOWER 1104 | 42041104 | 19.89 |  |  |  | 19.89
NORTH TOWER 1108 | 42041108 | 13.33 |  |  |  | 13.33
NORTH TOWER 2101 | 42042101 | 4.42 |  | 0.52 |  | 3.9
NORTH TOWER 2104 | 42042104 | 4.21 |  |  |  | 4.21
NOTRE DAME 1101 | 102041101 | 1.6 |  |  |  | 1.6
NOTRE DAME 1102 | 102041102 | 13.93 |  |  |  | 13.93
NOTRE DAME 1103 | 102041103 | 7.83 |  | 0.54 |  | 7.29
NOTRE DAME 1104 | 102041104 | 37.72 | 17.96 | 9.74 |  | 10.02
NOVATO 1101 | 42211101 | 3.47 |  | 0.6 |  | 2.87
NOVATO 1102 | 42211102 | 0.59 |  |  |  | 0.59
NOVATO 1103 | 42211103 | 2.96 |  |  |  | 2.96
NOVATO 1104 | 42211104 | 24.39 |  | 3.45 |  | 20.94
OAK 0401 | 12600401 | 5.45 |  | 3.46 |  | 1.99
OAK PARK 0401 | 163270401 | 2.52 |  |  |  | 2.52
OAK PARK 0402 | 163270402 | 0.51 |  |  |  | 0.51
OAKHURST 1101 | 254421101 | 91.86 | 2.56 | 88.45 |  | 0.85
OAKHURST 1102 | 254421102 | 16.34 | 1.18 | 11.33 |  | 3.83
OAKHURST 1103 | 254421103 | 123.52 | 80.67 | 40.21 |  | 2.64
OAKLAND C 1108 | 12011108 | 2.05 |  |  |  | 2.05
OAKLAND C 1109 | 12011109 | 3.3 |  |  |  | 3.3
OAKLAND C 1110 | 12011110 | 1.25 |  |  |  | 1.25
OAKLAND C 1112 | 12011112 | 1.17 |  |  |  | 1.17
OAKLAND C 1113 | 12011113 | 3.28 |  |  |  | 3.28
OAKLAND C 1114 | 12011114 | 3.39 |  |  |  | 3.39
OAKLAND C 1115 | 12011115 | 1.19 |  |  |  | 1.19
OAKLAND C 1116 | 12011116 | 2.49 |  |  |  | 2.49
OAKLAND C 1117 | 12011117 | 2.98 |  |  |  | 2.98
OAKLAND C 1118 | 12011118 | 3.32 |  |  |  | 3.32
OAKLAND C 1119 | 12011119 | 0.43 |  |  |  | 0.43
OAKLAND C 1120 | 12011120 | 2.97 |  |  |  | 2.97
OAKLAND C 1121 | 12011121 | 1.93 |  |  |  | 1.93
OAKLAND C 1132 | 12011132 | 1.22 |  |  |  | 1.22
OAKLAND C 1133 | 12011133 | 0.03 |  |  |  | 0.03
OAKLAND C 1134 | 12011134 | 1.4 |  |  |  | 1.4
OAKLAND D 0406 | 12040406 | 3.18 |  |  |  | 3.18
OAKLAND D 0407 | 12040407 | 0.33 |  |  |  | 0.33
OAKLAND D 0408 | 12040408 | 4.03 |  |  |  | 4.03
OAKLAND D 0410 | 12040410 | 2.76 |  |  |  | 2.76
OAKLAND D 1101 | 12041101 | 0.16 |  |  |  | 0.16
OAKLAND D 1102 | 12041102 | 2.86 |  |  |  | 2.86
OAKLAND D 1103 | 12041103 | 0.44 |  |  |  | 0.44
OAKLAND D 1104 | 12041104 | 5.92 |  |  |  | 5.92
OAKLAND D 1105 | 12041105 | 8.59 |  |  |  | 8.59
OAKLAND D 1106 | 12041106 | 8.82 |  |  |  | 8.82
OAKLAND D 1107 | 12041107 | 2.51 |  |  |  | 2.51
OAKLAND D 1110 | 12041110 | 5.49 |  |  |  | 5.49
OAKLAND D 1111 | 12041111 | 7.84 |  |  |  | 7.84
OAKLAND D 1112 | 12041112 | 10.67 | 1.96 | 0.41 |  | 8.3
OAKLAND D 1115 | 12041115 | 2.65 |  |  |  | 2.65
OAKLAND D 1116 | 12041116 | 2.82 |  |  |  | 2.82
OAKLAND D 1117 | 12041117 | 0.5 |  |  |  | 0.5
OAKLAND D 1130 | 12041130 | 6.45 |  |  |  | 6.45
OAKLAND D 1131 | 12041131 | 7.76 |  |  |  | 7.76
OAKLAND D 1132 | 12041132 | 2.79 |  |  |  | 2.79
OAKLAND D 1133 | 12041133 | 2.98 |  |  |  | 2.98
OAKLAND D 1134 | 12041134 | 9.32 |  |  |  | 9.32
OAKLAND D 1202 | 12041202 | 0.24 |  |  |  | 0.24
OAKLAND I 0401 | 12080401 | 3.31 |  |  |  | 3.31
OAKLAND I 0402 | 12080402 | 5.13 |  |  |  | 5.13
OAKLAND J 0401 | 12090401 | 4.65 |  |  |  | 4.65
OAKLAND J 0403 | 12090403 | 6.35 |  |  |  | 6.35
OAKLAND J 0408 | 12090408 | 4.59 |  |  |  | 4.59
OAKLAND J 0409 | 12090409 | 3.01 |  |  |  | 3.01
OAKLAND J 1101 | 12091101 | 10.53 |  |  |  | 10.53
OAKLAND J 1102 | 12091102 | 18.4 |  | 6.02 |  | 12.38
OAKLAND J 1103 | 12091103 | 2.78 |  |  |  | 2.78
OAKLAND J 1104 | 12091104 | 6.91 |  |  |  | 6.91
OAKLAND J 1105 | 12091105 | 20.38 |  | 1.53 |  | 18.85
OAKLAND J 1106 | 12091106 | 18.13 |  | 1.89 |  | 16.24
OAKLAND J 1108 | 12091108 | 9.31 |  |  |  | 9.31
OAKLAND J 1109 | 12091109 | 0.04 |  |  |  | 0.04
OAKLAND J 1110 | 12091110 | 2.12 |  |  |  | 2.12
OAKLAND J 1111 | 12091111 | 4.7 |  |  |  | 4.7
OAKLAND J 1112 | 12091112 | 5.52 |  |  |  | 5.52
OAKLAND J 1114 | 12091114 | 0 |  |  |  | 0
OAKLAND J 1115 | 12091115 | 3.91 |  |  |  | 3.91
OAKLAND J 1116 | 12091116 | 23.59 |  | 0.48 |  | 23.11
OAKLAND J 1117 | 12091117 | 13.2 |  |  |  | 13.2
OAKLAND J 1118 | 12091118 | 13.99 |  | 0.31 |  | 13.68
OAKLAND K 1101 | 12101101 | 7.27 | 1.09 | 1.46 |  | 4.72
OAKLAND K 1102 | 12101102 | 14.94 | 14.94 |  |  | 0
OAKLAND K 1103 | 12101103 | 10.77 | 1.13 | 4.84 |  | 4.8
OAKLAND K 1104 | 12101104 | 14.9 | 9.55 | 5.35 |  | 0
OAKLAND L 1101 | 12111101 | 5.79 |  |  |  | 5.79
OAKLAND L 1102 | 12111102 | 1.29 |  |  |  | 1.29
OAKLAND L 1103 | 12111103 | 4.71 |  |  |  | 4.71
OAKLAND L 1105 | 12111105 | 2.48 |  |  |  | 2.48
OAKLAND L 1106 | 12111106 | 0.35 |  |  |  | 0.35
OAKLAND L 1107 | 12111107 | 1.47 |  |  |  | 1.47
OAKLAND L 1108 | 12111108 | 0 |  |  |  | 0
OAKLAND X 0401 | 12540401 | 5.55 |  |  |  | 5.55
OAKLAND X 0402 | 12540402 | 1.77 |  |  |  | 1.77
OAKLAND X 1101 | 12541101 | 5.29 |  | 0.5 |  | 4.79
OAKLAND X 1102 | 12541102 | 6.39 |  |  |  | 6.39
OAKLAND X 1103 | 12541103 | 7.78 |  |  |  | 7.78
OAKLAND X 1104 | 12541104 | 13.25 | 10.73 | 1.35 |  | 1.17
OAKLAND X 1105 | 12541105 | 19.51 |  | 2.52 |  | 16.99
OAKLAND X 1106 | 12541106 | 22.92 | 4.14 | 10.82 |  | 7.96
OAKLAND X 1107 | 12541107 | 12.93 |  |  |  | 12.93
OAKLAND X 1109 | 12541109 | 7.13 |  |  |  | 7.13
OAKLAND X 1110 | 12541110 | 0.43 |  |  |  | 0.43
OAKLAND X 1111 | 12541111 | 1.09 |  |  |  | 1.09
OAKLAND X 1112 | 12541112 | 3.93 |  |  |  | 3.93
OAKLAND X 1114 | 12541114 | 5.11 |  |  |  | 5.11
OAKLAND X 1115 | 12541115 | 12.65 |  |  |  | 12.65
OCEAN 0401 | 22580401 | 3.72 |  |  |  | 3.72
OCEAN 0402 | 22580402 | 2.99 |  |  |  | 2.99
OCEANO 1102 | 182601102 | 54.22 |  | 37.18 |  | 17.04
OCEANO 1103 | 182601103 | 11.36 |  | 1.11 |  | 10.25
OCEANO 1104 | 182601104 | 112.44 | 6.75 | 78.99 |  | 26.7
OCEANO 1105 | 182601105 | 22.26 |  | 0.04 |  | 22.22
OCEANO 1106 | 182601106 | 29.49 |  | 1.96 |  | 27.53
OCEANO 1108 | 182601108 | 11.1 |  |  |  | 11.1
OILFIELDS 1102 | 182391102 | 39.26 |  |  |  | 39.26
OILFIELDS 1103 | 182391103 | 144.23 |  | 116.46 |  | 27.77
OLD RIVER 1101 | 252821101 | 42.02 |  |  |  | 42.02
OLD RIVER 1102 | 252821102 | 49.46 |  |  |  | 49.46
OLD RIVER 1103 | 252821103 | 35.38 |  |  |  | 35.38
OLD RIVER 1104 | 252821104 | 58.27 |  |  |  | 58.27
OLD RIVER 1105 | 252821105 | 15.45 |  |  |  | 15.45
OLEMA 1101 | 42291101 | 123.15 | 15.44 | 55.44 |  | 52.27
OLETA 1101 | 163541101 | 116.84 | 4.66 | 84.74 |  | 27.44
OLETA 1102 | 163541102 | 98.83 |  | 56.22 |  | 42.61
OLIVEHURST 1101 | 152901101 | 21.88 |  |  |  | 21.88
OLIVEHURST 1102 | 152901102 | 6.05 |  |  |  | 6.05
OLIVEHURST 1103 | 152901103 | 47.39 |  |  |  | 47.39
OLIVEHURST 1104 | 152901104 | 11.43 |  |  |  | 11.43
OLIVEHURST 1105 | 152901105 | 54.04 |  |  |  | 54.04
OREGON TRAIL 1102 | 103521102 | 49.26 |  | 44.93 |  | 4.33
OREGON TRAIL 1103 | 103521103 | 112.03 |  | 109.09 |  | 2.94
OREGON TRAIL 1104 | 103521104 | 73.46 |  | 60.61 |  | 12.85
ORICK 1101 | 192261101 | 7.99 |  |  |  | 7.99
ORICK 1102 | 192261102 | 23.27 |  |  |  | 23.27
ORLAND B 1101 | 102701101 | 29.25 |  |  |  | 29.25
ORLAND B 1102 | 102701102 | 20.12 |  |  |  | 20.12
ORLAND B 1103 | 102701103 | 94.76 |  |  |  | 94.76
ORO FINO 1101 | 103031101 | 31.45 | 31.45 |  |  | 0
ORO FINO 1102 | 103031102 | 109.41 | 83.13 | 26.28 |  | 0
ORO LOMA 1102 | 255371102 | 1.07 |  |  |  | 1.07
ORO LOMA 1103 | 255371103 | 1.1 |  |  |  | 1.1
ORO LOMA 1106 | 255371106 | 73.04 |  |  |  | 73.04
ORO LOMA 1108 | 255371108 | 55.51 |  |  |  | 55.51
ORO LOMA 1115 | 255371115 | 74.35 |  |  |  | 74.35
ORO LOMA 1116 | 255371116 | 24.71 |  |  |  | 24.71
ORO LOMA 1117 | 255371117 | 49.55 |  |  |  | 49.55
ORO LOMA 1118 | 255371118 | 42.77 |  |  |  | 42.77
OROSI 1101 | 252841101 | 50.42 |  |  |  | 50.42
OROSI 1102 | 252841102 | 34.92 |  | 0.8 |  | 34.12
OROSI 1103 | 252841103 | 37.83 |  |  |  | 37.83
OROSI 1104 | 252841104 | 56.07 |  |  |  | 56.07
OROVILLE 0402 | 102520402 | 1.59 |  |  |  | 1.59
OROVILLE 0403 | 102520403 | 2.06 |  |  |  | 2.06
OROVILLE 1101 | 102521101 | 23.53 |  |  |  | 23.53
OROVILLE 1102 | 102521102 | 6.31 |  |  |  | 6.31
OROVILLE 1103 | 102521103 | 8.89 |  |  |  | 8.89
OROVILLE 1104 | 102521104 | 9.91 |  |  |  | 9.91
ORTIGA 1105 | 254311105 | 42.48 |  |  |  | 42.48
ORTIGA 1106 | 254311106 | 53.75 |  |  |  | 53.75
OTTER 1101 | 182941101 | 26.95 | 14.55 | 7.1 |  | 5.3
OTTER 1102 | 182941102 | 53.62 | 4.38 | 48.14 |  | 1.1
PACIFIC GROVE 0421 | 182440421 | 3.37 |  |  |  | 3.37
PACIFIC GROVE 0422 | 182440422 | 6.93 |  | 0.13 |  | 6.8
PACIFIC GROVE 0423 | 182440423 | 1.72 |  |  |  | 1.72
PACIFIC GROVE 0424 | 182440424 | 9.07 |  |  |  | 9.07
PACIFIC PIPE GRAPEVI 1101 | 255441101 | 0.02 |  |  |  | 0.02
PACIFICA 1101 | 22811101 | 9.23 | 0.07 | 0.74 |  | 8.42
PACIFICA 1102 | 22811102 | 20.13 | 1.34 | 1.37 |  | 17.42
PACIFICA 1103 | 22811103 | 14.15 | 0.19 | 0.77 |  | 13.19
PACIFICA 1104 | 22811104 | 7.23 |  | 0.7 |  | 6.53
PALMER 1101 | 183031101 | 62.71 |  | 39.5 |  | 23.21
PALO SECO 0401 | 13180401 | 4.73 |  | 4.71 |  | 0.02
PANAMA 2101 | 253422101 | 38.62 |  |  |  | 38.62
PANAMA 2102 | 253422102 | 32.73 |  |  |  | 32.73
PANOCHE 1101 | 253671101 | 32.13 |  |  |  | 32.13
PANOCHE 1102 | 253671102 | 42.73 |  |  |  | 42.73
PANOCHE 1103 | 253671103 | 122.16 |  | 44.24 |  | 77.92
PANORAMA 1101 | 103461101 | 38.6 |  | 12.44 |  | 26.16
PANORAMA 1102 | 103461102 | 84.93 |  | 30.01 |  | 54.92
PARADISE 1102 | 102831102 | 0.44 | 0.33 |  |  | 0.11
PARADISE 1103 | 102831103 | 22.06 | 7.9 | 13.97 |  | 0.19
PARADISE 1104 | 102831104 | 17.2 | 13.3 | 1.2 |  | 2.7
PARADISE 1105 | 102831105 | 34.91 | 34.3 |  |  | 0.61
PARADISE 1106 | 102831106 | 7.05 | 6.48 |  |  | 0.57
PARKWAY 1101 | 42051101 | 7.12 |  |  |  | 7.12
PARKWAY 1102 | 42051102 | 0 |  |  |  | 0
PARKWAY 1103 | 42051103 | 6.72 |  |  |  | 6.72
PARLIER 1102 | 252291102 | 28.08 |  |  |  | 28.08
PARLIER 1103 | 252291103 | 40.95 |  |  |  | 40.95
PARLIER 1104 | 252291104 | 49.92 |  |  |  | 49.92
PARLIER 1105 | 252291105 | 21.55 |  |  |  | 21.55
PARSONS 0401 | 13660401 | 1.32 |  |  |  | 1.32
PARSONS 0402 | 13660402 | 3.43 |  |  |  | 3.43
PASO ROBLES 1101 | 182611101 | 6.65 |  |  |  | 6.65
PASO ROBLES 1102 | 182611102 | 4.93 |  |  |  | 4.93
PASO ROBLES 1103 | 182611103 | 62.04 |  | 38.59 |  | 23.45
PASO ROBLES 1104 | 182611104 | 65.63 |  | 37.16 |  | 28.47
PASO ROBLES 1106 | 182611106 | 8.6 |  |  |  | 8.6
PASO ROBLES 1107 | 182611107 | 36.34 |  | 0.27 |  | 36.07
PASO ROBLES 1108 | 182611108 | 14.54 |  |  |  | 14.54
PAUL SWEET 2101 | 83252101 | 28.41 |  |  |  | 28.41
PAUL SWEET 2102 | 83252102 | 18.05 | 3.72 | 0.73 |  | 13.6
PAUL SWEET 2103 | 83252103 | 16.95 |  |  |  | 16.95
PAUL SWEET 2104 | 83252104 | 38.46 | 17.22 |  |  | 21.24
PAUL SWEET 2105 | 83252105 | 40.98 | 6.8 | 0.8 |  | 33.38
PAUL SWEET 2106 | 83252106 | 51.71 | 30.48 | 5.21 |  | 16.02
PAUL SWEET 2107 | 83252107 | 49.65 | 4.04 | 4.24 |  | 41.37
PAUL SWEET 2108 | 83252108 | 20.86 |  |  |  | 20.86
PAUL SWEET 2109 | 83252109 | 23.69 | 0.85 | 2.02 |  | 20.82
PEABODY 2102 | 63642102 | 7.56 |  |  |  | 7.56
PEABODY 2104 | 63642104 | 6.77 |  |  |  | 6.77
PEABODY 2105 | 63642105 | 61.11 |  |  |  | 61.11
PEABODY 2106 | 63642106 | 1.08 |  | 0.39 |  | 0.69
PEABODY 2107 | 63642107 | 192.91 |  |  |  | 192.91
PEABODY 2108 | 63642108 | 2.54 |  |  |  | 2.54
PEABODY 2109 | 63642109 | 3.63 |  |  |  | 3.63
PEABODY 2112 | 63642112 | 3.45 |  |  |  | 3.45
PEABODY 2113 | 63642113 | 8.1 |  | 1.36 |  | 6.74
PEACHTON 1101 | 103241101 | 68.97 |  |  |  | 68.97
PEACHTON 1102 | 103241102 | 67.71 |  |  |  | 67.71
PEACHTON 1103 | 103241103 | 61.41 |  |  |  | 61.41
PEASE 1101 | 153751101 | 6.86 |  |  |  | 6.86
PEASE 1102 | 153751102 | 4 |  |  |  | 4
PEASE 1103 | 153751103 | 97.74 |  |  |  | 97.74
PEASE 1104 | 153751104 | 62.61 |  |  |  | 62.61
PEASE 1105 | 153751105 | 8.29 |  |  |  | 8.29
PENNGROVE 1101 | 43471101 | 41.98 |  | 20.3 |  | 21.68
PENRYN 1103 | 152561103 | 80.37 |  | 67.28 |  | 13.09
PENRYN 1105 | 152561105 | 91.61 |  | 33.88 |  | 57.73
PENRYN 1106 | 152561106 | 25.91 |  | 0.81 |  | 25.1
PENRYN 1107 | 152561107 | 84.09 |  | 35.99 |  | 48.1
PENTLAND 1101 | 255311101 | 0.02 |  |  |  | 0.02
PEORIA 1701 | 163781701 | 112.31 |  | 101.03 |  | 11.28
PEORIA 1704 | 163781704 | 117.99 |  | 58.71 |  | 59.28
PEORIA 1705 | 163781705 | 42.4 |  | 34.18 |  | 8.22
PERRY 1101 | 183071101 | 83.64 | 7.19 | 58.31 |  | 18.14
PERRY 1104 | 183071104 | 62.34 |  | 43.91 |  | 18.43
PETALUMA A 0411 | 42120411 | 3.09 |  |  |  | 3.09
PETALUMA A 0413 | 42120413 | 2.41 |  |  |  | 2.41
PETALUMA C 1101 | 42631101 | 0.51 |  |  |  | 0.51
PETALUMA C 1102 | 42631102 | 4.23 |  |  |  | 4.23
PETALUMA C 1105 | 42631105 | 10.67 |  |  |  | 10.67
PETALUMA C 1106 | 42631106 | 9 |  |  |  | 9
PETALUMA C 1108 | 42631108 | 118.59 |  | 75.82 |  | 42.77
PETALUMA C 1109 | 42631109 | 66.66 |  | 48.77 |  | 17.89
PETALUMA C 1110 | 42631110 | 0.25 |  |  |  | 0.25
PETROL 1101 | 252541101 | 0.03 |  |  |  | 0.03
PHILO 1101 | 42601101 | 96.16 |  | 76.49 |  | 19.67
PHILO 1102 | 42601102 | 106.01 |  | 88.33 |  | 17.68
PIERCY 2109 | 83912109 | 19.91 |  |  |  | 19.91
PIERCY 2110 | 83912110 | 27.53 |  | 19.66 |  | 7.87
PIERCY 2111 | 83912111 | 0.91 |  |  |  | 0.91
PIKE CITY 1101 | 152201101 | 34.07 | 34.07 |  |  | 0
PIKE CITY 1102 | 152201102 | 9.52 | 9.52 |  |  | 0
PINE GROVE 1101 | 163751101 | 71.84 |  | 71.84 |  | 0
PINE GROVE 1102 | 163751102 | 176.11 | 85.27 | 90.83 |  | 0.01
PINECREST 0401 | 163160401 | 3.16 | 1.12 | 1.95 |  | 0.09
PINEDALE 2101 | 252852101 | 1.43 |  |  |  | 1.43
PINEDALE 2102 | 252852102 | 2.77 |  |  |  | 2.77
PINEDALE 2103 | 252852103 | 2 |  |  |  | 2
PINEDALE 2105 | 252852105 | 1.76 |  |  |  | 1.76
PINEDALE 2106 | 252852106 | 6.87 |  |  |  | 6.87
PINEDALE 2107 | 252852107 | 1.6 |  |  |  | 1.6
PINEDALE 2109 | 252852109 | 5.74 |  |  |  | 5.74
PINEDALE 2110 | 252852110 | 0.18 |  |  |  | 0.18
PINEDALE 2111 | 252852111 | 0.76 |  |  |  | 0.76
PIPER BANK 0401 | 18120401 | 1.57 |  |  |  | 1.57
PIT NO 1 1101 | 103721101 | 52.98 |  | 29.58 |  | 23.4
PIT NO 3 2101 | 103732101 | 48.47 |  | 47.43 |  | 1.04
PIT NO 5 1101 | 101321101 | 23.57 |  | 23.57 |  | 0
PIT NO 7 1101 | 103501101 | 2.84 |  | 2.84 |  | 0
PITTSBURG 0401 | 12160401 | 1.04 |  |  |  | 1.04
PITTSBURG 0402 | 12160402 | 1.88 |  |  |  | 1.88
PLACER 1101 | 152461101 | 7.71 |  | 1.26 |  | 6.45
PLACER 1102 | 152461102 | 2.08 |  | 1.87 |  | 0.21
PLACER 1103 | 152461103 | 29.67 |  | 12.22 |  | 17.45
PLACER 1104 | 152461104 | 13.46 |  | 0.52 |  | 12.94
PLACERVILLE 1109 | 153081109 | 11.07 |  | 10.78 |  | 0.29
PLACERVILLE 1110 | 153081110 | 34.51 | 0.76 | 32.74 |  | 1.01
PLACERVILLE 1111 | 153081111 | 16.87 |  | 14.9 |  | 1.97
PLACERVILLE 1112 | 153081112 | 30.04 |  | 27.71 |  | 2.33
PLACERVILLE 2106 | 153082106 | 273.21 | 179.03 | 93.92 |  | 0.26
PLAINFIELD 1101 | 63441101 | 33.5 |  |  |  | 33.5
PLAINFIELD 1105 | 63441105 | 50.78 |  |  |  | 50.78
PLAINFIELD 1106 | 63441106 | 32.65 |  |  |  | 32.65
PLEASANT GROVE 2103 | 152442103 | 1.88 |  |  |  | 1.88
PLEASANT GROVE 2104 | 152442104 | 2.42 |  |  |  | 2.42
PLEASANT GROVE 2107 | 152442107 | 0.02 |  |  |  | 0.02
PLEASANT GROVE 2108 | 152442108 | 2.1 |  |  |  | 2.1
PLEASANT GROVE 2110 | 152442110 | 34.69 |  |  |  | 34.69
PLUMAS 1101 | 153731101 | 32.26 |  |  |  | 32.26
PLUMAS 1102 | 153731102 | 5.67 |  |  |  | 5.67
PLUMAS 2106 | 153732106 | 31.96 |  |  |  | 31.96
PLUMAS 2107 | 153732107 | 39.5 |  |  |  | 39.5
PLYMOUTH 0401 | 22680401 | 4.73 |  |  |  | 4.73
POINT ARENA 1101 | 43381101 | 66.13 |  | 44.26 |  | 21.87
POINT MORETTI 1101 | 82931101 | 53.9 | 29.94 | 17.24 |  | 6.72
POINT PINOLE 1101 | 14261101 | 21.06 |  |  |  | 21.06
POINT PINOLE 1102 | 14261102 | 14.18 |  |  |  | 14.18
POINT PINOLE 1103 | 14261103 | 0.01 |  |  |  | 0.01
PORTOLA 0401 | 22610401 | 2.45 |  |  |  | 2.45
PORTOLA 0402 | 22610402 | 3.5 |  |  |  | 3.5
POSO MOUNTAIN 2101 | 253642101 | 59.21 |  | 48.64 |  | 10.57
POSO MOUNTAIN 2103 | 253642103 | 20.39 |  | 18.37 |  | 2.02
POSO MOUNTAIN 2104 | 253642104 | 12.56 |  | 8.04 |  | 4.52
POTRERO PP (A) 1101 | 22031101 | 7.23 |  |  |  | 7.23
POTRERO PP (A) 1102 | 22031102 | 0.47 |  |  |  | 0.47
POTRERO PP (A) 1103 | 22031103 | 1.81 |  |  |  | 1.81
POTRERO PP (A) 1104 | 22031104 | 0.3 |  |  |  | 0.3
POTRERO PP (A) 1105 | 22031105 | 1.53 |  |  |  | 1.53
POTRERO PP (A) 1107 | 22031107 | 0.98 |  |  |  | 0.98
POTRERO PP (A) 1108 | 22031108 | 3.39 |  |  |  | 3.39
POTRERO PP (A) 1109 | 22031109 | 5.27 |  |  |  | 5.27
POTRERO PP (A) 1110 | 22031110 | 6.2 |  |  |  | 6.2
POTRERO PP (A) 1112 | 22031112 | 0.93 |  |  |  | 0.93
POTRERO PP (A) 1113 | 22031113 | 1.37 |  |  |  | 1.37
POTRERO PP (A) 1114 | 22031114 | 0.07 |  |  |  | 0.07
POTRERO PP (A) 1115 | 22031115 | 0.08 |  |  |  | 0.08
POTRERO PP (A) 1116 | 22031116 | 2.22 |  |  |  | 2.22
POTRERO PP (A) 1117 | 22031117 | 4.95 |  |  |  | 4.95
POTRERO PP (A) 1118 | 22031118 | 4.33 |  |  |  | 4.33
POTRERO PP (A) 1119 | 22031119 | 3.26 |  |  |  | 3.26
POTRERO PP (A) 1121 | 22031121 | 0.17 |  |  |  | 0.17
POTTER VALLEY P H 1104 | 42281104 | 0.02 |  | 0.02 |  | 0
POTTER VALLEY P H 1105 | 42281105 | 90.53 | 3.98 | 47.06 |  | 39.49
PRUNEDALE 1107 | 182961107 | 47.09 |  |  |  | 47.09
PRUNEDALE 1110 | 182961110 | 79.93 |  | 0.24 |  | 79.69
PUEBLO 1102 | 43291102 | 8.99 |  |  | 0.09 | 8.9
PUEBLO 1103 | 43291103 | 8.11 |  |  |  | 8.11
PUEBLO 1104 | 43291104 | 51.02 |  | 28.43 | 0.05 | 22.54
PUEBLO 1105 | 43291105 | 70.02 |  | 20.63 | 0.05 | 49.34
PUEBLO 2101 | 43292101 | 11.64 |  |  |  | 11.64
PUEBLO 2102 | 43292102 | 97.65 | 21.14 | 0.74 |  | 75.77
PUEBLO 2103 | 43292103 | 77.51 | 37.65 | 8.12 |  | 31.74
PURISIMA 1101 | 182971101 | 57.13 |  | 17.63 |  | 39.5
PUTAH CREEK 1102 | 63681102 | 50.78 |  | 26.46 |  | 24.32
PUTAH CREEK 1103 | 63681103 | 36.56 |  | 3.76 |  | 32.8
PUTAH CREEK 1105 | 63681105 | 82.87 |  | 1.78 |  | 81.09
RACETRACK 1703 | 163761703 | 53.47 |  | 47.33 |  | 6.14
RACETRACK 1704 | 163761704 | 45.4 |  | 45.4 |  | 0
RADUM 1101 | 13151101 | 1.63 |  |  |  | 1.63
RADUM 1102 | 13151102 | 1.15 |  |  |  | 1.15
RADUM 1105 | 13151105 | 11.82 | 1.14 | 1.91 |  | 8.77
RAINBOW 1103 | 254441103 | 11.06 |  |  |  | 11.06
RAINBOW 1105 | 254441105 | 23.75 |  |  |  | 23.75
RAINBOW 1106 | 254441106 | 122.17 |  |  |  | 122.17
RALSTON 1101 | 24141101 | 14.48 | 0.41 | 8.53 |  | 5.54
RALSTON 1102 | 24141102 | 10.72 |  | 3.77 |  | 6.95
RANCHERS COTTON 1000 | 254801000 | 0.01 |  |  |  | 0.01
RANCHERS COTTON 1101 | 254801101 | 14.17 |  |  |  | 14.17
RANDOLPH 0401 | 22590401 | 0 |  |  |  | 0
RANDOLPH 0402 | 22590402 | 1.27 |  |  |  | 1.27
RANDOLPH 0403 | 22590403 | 3.15 |  |  |  | 3.15
RAWSON 1103 | 103531103 | 40.18 |  | 2.75 |  | 37.43
RED BLUFF 1101 | 103541101 | 74.72 |  | 47.86 |  | 26.86
RED BLUFF 1102 | 103541102 | 1.49 |  |  |  | 1.49
RED BLUFF 1103 | 103541103 | 38.11 |  | 16.84 |  | 21.27
RED BLUFF 1104 | 103541104 | 93.41 |  | 66.14 |  | 27.27
RED BLUFF 1105 | 103541105 | 37.77 |  | 13.63 |  | 24.14
REDBUD 1101 | 43191101 | 63.02 | 18.4 | 20.53 |  | 24.09
REDBUD 1102 | 43191102 | 58.5 | 0.65 | 27.85 |  | 30
REDWOOD CITY 0402 | 24160402 | 1.26 |  |  |  | 1.26
REDWOOD CITY 0403 | 24160403 | 2.13 |  |  |  | 2.13
REDWOOD CITY 0404 | 24160404 | 1.63 |  |  |  | 1.63
REDWOOD CITY 0405 | 24160405 | 3.39 |  |  |  | 3.39
REDWOOD CITY 0406 | 24160406 | 6.62 |  |  |  | 6.62
REDWOOD CITY 0408 | 24160408 | 5.66 |  |  |  | 5.66
REDWOOD CITY 0409 | 24160409 | 4.93 |  |  |  | 4.93
REDWOOD CITY 0410 | 24160410 | 5.45 |  |  |  | 5.45
REDWOOD CITY 1101 | 24161101 | 1.95 |  |  |  | 1.95
REDWOOD CITY 1102 | 24161102 | 1.63 |  |  |  | 1.63
REDWOOD CITY 1103 | 24161103 | 1.6 |  |  |  | 1.6
REDWOOD CITY 1104 | 24161104 | 0.98 |  |  |  | 0.98
REDWOOD CITY 1105 | 24161105 | 7.3 |  |  |  | 7.3
REEDLEY 1101 | 252341101 | 26.5 |  |  |  | 26.5
REEDLEY 1104 | 252341104 | 82.5 |  | 1.69 |  | 80.81
REEDLEY 1106 | 252341106 | 123.35 |  |  |  | 123.35
REEDLEY 1110 | 252341110 | 42.26 |  |  |  | 42.26
REEDLEY 1112 | 252341112 | 90.06 |  | 0.78 |  | 89.28
RENFRO 2101 | 254572101 | 31.47 |  |  |  | 31.47
RENFRO 2102 | 254572102 | 4.41 |  |  |  | 4.41
RENFRO 2103 | 254572103 | 26.52 |  |  |  | 26.52
RENFRO 2105 | 254572105 | 10.08 |  |  |  | 10.08
RENFRO 2107 | 254572107 | 8 |  |  |  | 8
RESEARCH 2101 | 14692101 | 7.78 |  |  |  | 7.78
RESEARCH 2102 | 14692102 | 20.77 | 2.18 |  |  | 18.59
RESEARCH 2103 | 14692103 | 0 |  |  |  | 0
RESERVATION ROAD 1101 | 182731101 | 36.99 |  | 29.12 |  | 7.87
RESERVATION ROAD 1102 | 182731102 | 58.38 |  | 19.67 |  | 38.71
RESERVE OIL 1101 | 254181101 | 2.19 |  |  |  | 2.19
RICE 1101 | 62831101 | 53.74 |  |  |  | 53.74
RICE 1102 | 62831102 | 62.32 |  |  |  | 62.32
RICE 1103 | 62831103 | 78.39 |  |  |  | 78.39
RICE 1104 | 62831104 | 33.18 |  |  |  | 33.18
RICHMOND R 1118 | 13471118 | 2.98 |  |  |  | 2.98
RICHMOND R 1119 | 13471119 | 3.65 |  |  |  | 3.65
RICHMOND R 1120 | 13471120 | 2.98 |  |  |  | 2.98
RICHMOND R 1121 | 13471121 | 4.47 |  |  |  | 4.47
RICHMOND R 1122 | 13471122 | 3.87 |  |  |  | 3.87
RICHMOND R 1123 | 13471123 | 1.33 |  |  |  | 1.33
RICHMOND R 1124 | 13471124 | 6.76 |  |  |  | 6.76
RICHMOND R 1125 | 13471125 | 10.63 |  |  |  | 10.63
RICHMOND R 1126 | 13471126 | 13.13 |  |  |  | 13.13
RICHMOND R 1127 | 13471127 | 20.33 |  |  |  | 20.33
RICHMOND R 1128 | 13471128 | 7.57 |  |  |  | 7.57
RICHMOND R 1129 | 13471129 | 13.64 |  |  |  | 13.64
RICHMOND R 1130 | 13471130 | 16.09 |  |  |  | 16.09
RIDGE 0401 | 12840401 | 2.65 |  | 2.65 |  | 0
RIDGE 0402 | 12840402 | 2.41 |  | 1.75 |  | 0.66
RINCON 1101 | 43321101 | 37.98 | 16.3 | 5.75 |  | 15.93
RINCON 1102 | 43321102 | 17.89 | 0.01 | 2.62 |  | 15.26
RINCON 1103 | 43321103 | 47.7 | 40.38 | 4.36 |  | 2.96
RINCON 1104 | 43321104 | 8.9 | 1.92 |  |  | 6.98
RIO BRAVO 1101 | 252861101 | 20.94 |  |  |  | 20.94
RIO BRAVO 1102 | 252861102 | 36.83 |  |  |  | 36.83
RIO BRAVO 1103 | 252861103 | 26.97 |  |  |  | 26.97
RIO BRAVO 1104 | 252861104 | 4.99 |  |  |  | 4.99
RIO BRAVO 1106 | 252861106 | 63.05 |  |  |  | 63.05
RIO DELL 1101 | 192251101 | 61.91 |  | 14.57 | 0.76 | 46.58
RIO DELL 1102 | 192251102 | 39.11 |  | 34.63 |  | 4.48
RIPON 1701 | 163801701 | 64.73 |  |  |  | 64.73
RIPON 1702 | 163801702 | 24.37 |  |  |  | 24.37
RIPON 1703 | 163801703 | 83.53 |  |  |  | 83.53
RIPON 1704 | 163801704 | 9.66 |  |  |  | 9.66
RISING RIVER 1101 | 103551101 | 68.86 |  | 53.69 |  | 15.17
RIVER ROCK 1101 | 255251101 | 0.02 |  |  |  | 0.02
RIVERBANK 1711 | 163191711 | 35.99 |  |  |  | 35.99
RIVERBANK 1712 | 163191712 | 54.5 |  |  |  | 54.5
RIVERBANK 1713 | 163191713 | 54.04 |  |  |  | 54.04
RIVERBANK 1714 | 163191714 | 33.66 |  |  |  | 33.66
RIVERBANK 1715 | 163191715 | 92.1 |  |  |  | 92.1
RIVERBANK 1716 | 163191716 | 26.83 |  |  |  | 26.83
ROB ROY 2104 | 83692104 | 159.84 | 39.37 | 62.05 |  | 58.42
ROB ROY 2105 | 83692105 | 66.31 | 26.89 | 11.35 |  | 28.07
ROCKLIN 1102 | 152061102 | 18.67 |  |  |  | 18.67
ROCKLIN 1103 | 152061103 | 5.12 |  |  |  | 5.12
ROCKLIN 1104 | 152061104 | 3.31 |  |  |  | 3.31
ROSEDALE 1101 | 254761101 | 12.1 |  |  |  | 12.1
ROSEDALE 2102 | 254762102 | 3.72 |  |  |  | 3.72
ROSSMOOR 1101 | 14161101 | 30.62 | 2.13 | 10.75 |  | 17.74
ROSSMOOR 1102 | 14161102 | 1.45 | 0.45 |  |  | 1
ROSSMOOR 1103 | 14161103 | 2.58 |  |  |  | 2.58
ROSSMOOR 1104 | 14161104 | 19.25 |  | 0.3 |  | 18.95
ROSSMOOR 1105 | 14161105 | 4.29 |  |  |  | 4.29
ROSSMOOR 1106 | 14161106 | 16.16 | 0.58 | 2.84 |  | 12.74
ROSSMOOR 1107 | 14161107 | 10.58 | 0.03 |  |  | 10.55
ROSSMOOR 1108 | 14161108 | 13.15 | 1.97 | 3.14 |  | 8.04
ROSSMOOR 1109 | 14161109 | 14.03 | 6.39 | 1.14 |  | 6.5
ROUGH AND READY ISLA 1102 | 163081102 | 54.3 |  |  |  | 54.3
ROUND MOUNTAIN 1101 | 109001101 | 0.02 |  | 0.02 |  | 0
RUSS RANCH 1101 | 192471101 | 0.22 |  |  |  | 0.22
RUSSELL (SMUD) 2101 | 63142101 | 5.13 |  |  |  | 5.13
RUSSELL 0401 | 13310401 | 3.44 |  |  |  | 3.44
RUSSELL 0402 | 13310402 | 3.36 |  |  |  | 3.36
SALINAS 1101 | 182011101 | 8.34 |  |  |  | 8.34
SALINAS 1102 | 182011102 | 21.28 |  |  |  | 21.28
SALINAS 1103 | 182011103 | 10.83 |  |  |  | 10.83
SALINAS 1104 | 182011104 | 32.45 |  |  |  | 32.45
SALINAS 1105 | 182011105 | 10.9 |  |  |  | 10.9
SALINAS 1106 | 182011106 | 17.76 |  |  |  | 17.76
SALINAS 1107 | 182011107 | 7.21 |  |  |  | 7.21
SALINAS 1108 | 182011108 | 2.75 |  |  |  | 2.75
SALINAS 1109 | 182011109 | 20.42 |  |  |  | 20.42
SALMON CREEK 1101 | 43161101 | 47.36 | 7.21 | 15 |  | 25.15
SALT SPRINGS 2101 | 163692101 | 21.95 |  | 17.06 | 1.36 | 3.53
SALT SPRINGS 2102 | 163692102 | 51.96 | 42.08 | 9.8 |  | 0.08
SAN ARDO 1101 | 182191101 | 56.5 |  | 2.67 |  | 53.83
SAN ARDO 1102 | 182191102 | 123.85 |  |  |  | 123.85
SAN BENITO 2101 | 182742101 | 48.38 |  | 4.28 |  | 44.1
SAN BENITO 2102 | 182742102 | 12.95 |  |  |  | 12.95
SAN BENITO 2103 | 182742103 | 0.59 |  |  |  | 0.59
SAN BENITO 2104 | 182742104 | 51.15 |  | 26.68 |  | 24.47
SAN BERNARD 1101 | 253191101 | 41.68 |  | 1.13 |  | 40.55
SAN BERNARD 1102 | 253191102 | 11.98 |  |  |  | 11.98
SAN BERNARD 1104 | 253191104 | 9.27 |  |  |  | 9.27
SAN BRUNO 0401 | 22700401 | 3.7 |  |  |  | 3.7
SAN BRUNO 0402 | 22700402 | 3.14 |  |  |  | 3.14
SAN BRUNO 0403 | 22700403 | 5.13 |  |  |  | 5.13
SAN CARLOS 0401 | 24180401 | 1.66 |  |  |  | 1.66
SAN CARLOS 0402 | 24180402 | 4.32 |  |  |  | 4.32
SAN CARLOS 0403 | 24180403 | 6.95 |  |  |  | 6.95
SAN CARLOS 0404 | 24180404 | 8.83 |  |  |  | 8.83
SAN CARLOS 0405 | 24180405 | 8.22 |  |  |  | 8.22
SAN CARLOS 0406 | 24180406 | 6.6 |  |  |  | 6.6
SAN CARLOS 1101 | 24181101 | 1.46 |  |  |  | 1.46
SAN CARLOS 1102 | 24181102 | 0.46 |  |  |  | 0.46
SAN CARLOS 1103 | 24181103 | 16.61 |  | 3.83 |  | 12.78
SAN CARLOS 1104 | 24181104 | 22.09 |  | 10.63 |  | 11.46
SAN JOAQUIN #2 1103 | 252521103 | 79.95 | 10.34 | 69.61 |  | 0
SAN JOAQUIN #3 1101 | 252531101 | 24.35 | 22.77 | 1.57 |  | 0.01
SAN JOAQUIN #3 1102 | 252531102 | 11.41 | 5.46 | 5.95 |  | 0
SAN JOAQUIN #3 1103 | 252531103 | 56.09 | 30.4 | 25.69 |  | 0
SAN JOAQUIN 1106 | 252361106 | 52.1 |  |  |  | 52.1
SAN JOAQUIN 1108 | 252361108 | 41.18 |  |  |  | 41.18
SAN JOAQUIN 1112 | 252361112 | 42.34 |  |  |  | 42.34
SAN JOSE A 0403 | 82250403 | 3.99 |  |  |  | 3.99
SAN JOSE A 0404 | 82250404 | 1.66 |  |  |  | 1.66
SAN JOSE A 0405 | 82250405 | 1.85 |  |  |  | 1.85
SAN JOSE A 0407 | 82250407 | 1.76 |  |  |  | 1.76
SAN JOSE A 0408 | 82250408 | 2.41 |  |  |  | 2.41
SAN JOSE A 0410 | 82250410 | 4.57 |  |  |  | 4.57
SAN JOSE A 1109 | 82251109 | 0.59 |  |  |  | 0.59
SAN JOSE A 1110 | 82251110 | 9.1 |  |  |  | 9.1
SAN JOSE A 1111 | 82251111 | 0.13 |  |  |  | 0.13
SAN JOSE A 1112 | 82251112 | 10.63 |  |  |  | 10.63
SAN JOSE B 1101 | 82261101 | 0.16 |  |  |  | 0.16
SAN JOSE B 1102 | 82261102 | 0.25 |  |  |  | 0.25
SAN JOSE B 1104 | 82261104 | 0.48 |  |  |  | 0.48
SAN JOSE B 1105 | 82261105 | 8.68 |  |  |  | 8.68
SAN JOSE B 1106 | 82261106 | 0.7 |  |  |  | 0.7
SAN JOSE B 1107 | 82261107 | 9.15 |  |  |  | 9.15
SAN JOSE B 1108 | 82261108 | 8.11 |  |  |  | 8.11
SAN JOSE B 1109 | 82261109 | 0.39 |  |  |  | 0.39
SAN JOSE B 1110 | 82261110 | 13.32 |  |  |  | 13.32
SAN JOSE B 1111 | 82261111 | 0.08 |  |  |  | 0.08
SAN JOSE B 1112 | 82261112 | 12.66 |  |  |  | 12.66
SAN JOSE B 1113 | 82261113 | 0.1 |  |  |  | 0.1
SAN JOSE B 1114 | 82261114 | 0.68 |  |  |  | 0.68
SAN JOSE B 1115 | 82261115 | 0.78 |  |  |  | 0.78
SAN JOSE B 1116 | 82261116 | 4.36 |  |  |  | 4.36
SAN JOSE B 1117 | 82261117 | 3.65 |  |  |  | 3.65
SAN JUSTO 1101 | 183181101 | 56.49 |  | 37.23 |  | 19.26
SAN LEANDRO U 1101 | 13111101 | 3.91 |  |  |  | 3.91
SAN LEANDRO U 1102 | 13111102 | 12.46 |  |  |  | 12.46
SAN LEANDRO U 1103 | 13111103 | 1.94 |  |  |  | 1.94
SAN LEANDRO U 1104 | 13111104 | 6.21 |  |  |  | 6.21
SAN LEANDRO U 1105 | 13111105 | 7.75 |  |  |  | 7.75
SAN LEANDRO U 1106 | 13111106 | 12.43 |  |  |  | 12.43
SAN LEANDRO U 1107 | 13111107 | 15.09 |  |  |  | 15.09
SAN LEANDRO U 1108 | 13111108 | 8.58 |  |  |  | 8.58
SAN LEANDRO U 1109 | 13111109 | 19.87 | 0.86 | 11.61 |  | 7.4
SAN LEANDRO U 1110 | 13111110 | 19.02 |  |  |  | 19.02
SAN LEANDRO U 1111 | 13111111 | 2.31 |  |  |  | 2.31
SAN LEANDRO U 1112 | 13111112 | 4.07 |  |  |  | 4.07
SAN LEANDRO U 1113 | 13111113 | 9.83 |  |  |  | 9.83
SAN LEANDRO U 1114 | 13111114 | 29.14 |  | 9.54 |  | 19.6
SAN LEANDRO U 1115 | 13111115 | 1.47 |  |  |  | 1.47
SAN LEANDRO U 1116 | 13111116 | 3.82 |  |  |  | 3.82
SAN LEANDRO U 1151 | 13111151 | 5.97 |  |  |  | 5.97
SAN LUIS OBISPO 1101 | 182631101 | 39.66 | 10.18 | 15.38 |  | 14.1
SAN LUIS OBISPO 1102 | 182631102 | 12.3 |  | 0.63 |  | 11.67
SAN LUIS OBISPO 1103 | 182631103 | 38.99 |  | 20.23 |  | 18.76
SAN LUIS OBISPO 1104 | 182631104 | 84.64 | 21.33 | 37.33 |  | 25.98
SAN LUIS OBISPO 1105 | 182631105 | 15.89 |  | 1.43 |  | 14.46
SAN LUIS OBISPO 1107 | 182631107 | 52.31 | 24.64 | 22.65 |  | 5.02
SAN LUIS OBISPO 1108 | 182631108 | 7.24 |  | 1.56 |  | 5.68
SAN MATEO 0404 | 24190404 | 5.11 |  |  |  | 5.11
SAN MATEO 0407 | 24190407 | 3.62 |  |  |  | 3.62
SAN MATEO 0408 | 24190408 | 5.68 |  |  |  | 5.68
SAN MATEO 0409 | 24190409 | 3.15 |  |  |  | 3.15
SAN MATEO 0410 | 24190410 | 5.18 |  |  |  | 5.18
SAN MATEO 2101 | 24192101 | 7.26 |  |  |  | 7.26
SAN MATEO 2102 | 24192102 | 13.08 |  |  |  | 13.08
SAN MIGUEL 1104 | 182661104 | 143.94 |  | 23.8 |  | 120.14
SAN MIGUEL 1105 | 182661105 | 20.21 |  | 1.39 |  | 18.82
SAN MIGUEL 1106 | 182661106 | 74.35 |  | 37.81 |  | 36.54
SAN MIGUEL 1107 | 182661107 | 5.72 |  |  |  | 5.72
SAN PABLO 1105 | 14371105 | 18.68 |  |  |  | 18.68
SAN PABLO 1106 | 14371106 | 0.65 |  |  |  | 0.65
SAN RAFAEL 1101 | 42011101 | 27.48 | 12.24 | 1.17 |  | 14.07
SAN RAFAEL 1102 | 42011102 | 4.87 |  |  |  | 4.87
SAN RAFAEL 1103 | 42011103 | 5.89 |  |  |  | 5.89
SAN RAFAEL 1104 | 42011104 | 25.12 | 2.08 | 9.76 |  | 13.28
SAN RAFAEL 1105 | 42011105 | 23.1 |  | 1.63 |  | 21.47
SAN RAFAEL 1106 | 42011106 | 21.16 |  | 2.8 |  | 18.36
SAN RAFAEL 1107 | 42011107 | 29.19 | 18.27 | 2.98 |  | 7.94
SAN RAFAEL 1108 | 42011108 | 29.18 | 26.18 | 0.44 |  | 2.56
SAN RAFAEL 1109 | 42011109 | 26.46 |  | 9.82 |  | 16.64
SAN RAFAEL 1110 | 42011110 | 13.16 | 7.94 |  |  | 5.22
SAN RAMON 2101 | 14232101 | 1.08 |  | 0.61 |  | 0.47
SAN RAMON 2102 | 14232102 | 2.32 |  | 1.51 |  | 0.81
SAN RAMON 2103 | 14232103 | 2.79 |  |  |  | 2.79
SAN RAMON 2104 | 14232104 | 20.69 |  |  |  | 20.69
SAN RAMON 2105 | 14232105 | 3.44 |  |  |  | 3.44
SAN RAMON 2106 | 14232106 | 5.1 | 0.45 |  |  | 4.65
SAN RAMON 2107 | 14232107 | 27.42 | 14.29 | 0.17 |  | 12.96
SAN RAMON 2108 | 14232108 | 17.34 | 16.41 |  |  | 0.93
SAN RAMON 2110 | 14232110 | 0.1 |  |  |  | 0.1
SAN RAMON 2111 | 14232111 | 9.44 |  |  |  | 9.44
SAN RAMON 2114 | 14232114 | 1.61 |  |  |  | 1.61
SAN RAMON 2116 | 14232116 | 0 |  |  |  | 0
SAN RAMON 2117 | 14232117 | 1.67 |  | 0.56 |  | 1.11
SAN RAMON 2118 | 14232118 | 0.82 |  |  |  | 0.82
SAN RAMON 2119 | 14232119 | 3.03 |  | 0.59 |  | 2.44
SAND CREEK 1103 | 254601103 | 150.21 |  | 148.5 |  | 1.71
SANGER 1104 | 252351104 | 9.62 |  |  |  | 9.62
SANGER 1106 | 252351106 | 8.59 |  |  |  | 8.59
SANGER 1108 | 252351108 | 81.35 |  |  |  | 81.35
SANGER 1110 | 252351110 | 33.64 |  |  |  | 33.64
SANGER 1112 | 252351112 | 11.57 |  |  |  | 11.57
SANGER 1114 | 252351114 | 62.91 |  |  |  | 62.91
SANGER 1116 | 252351116 | 8.04 |  |  |  | 8.04
SANGER 1118 | 252351118 | 29.28 |  |  |  | 29.28
SANTA MARIA 1105 | 182671105 | 28.99 |  |  |  | 28.99
SANTA MARIA 1106 | 182671106 | 19.05 |  |  |  | 19.05
SANTA MARIA 1107 | 182671107 | 7.5 |  |  |  | 7.5
SANTA MARIA 1108 | 182671108 | 93.93 | 43.74 | 28.52 |  | 21.67
SANTA MARIA 1109 | 182671109 | 21.04 |  |  |  | 21.04
SANTA MARIA 1110 | 182671110 | 52.78 |  |  |  | 52.78
SANTA MARIA 1111 | 182671111 | 14.03 |  |  |  | 14.03
SANTA MARIA 1112 | 182671112 | 10.48 |  |  |  | 10.48
SANTA NELLA 1101 | 254051101 | 22.89 |  |  |  | 22.89
SANTA NELLA 1103 | 254051103 | 15.67 |  |  |  | 15.67
SANTA NELLA 1104 | 254051104 | 52.34 |  |  |  | 52.34
SANTA RITA 1102 | 253541102 | 98.64 |  |  |  | 98.64
SANTA RITA 1105 | 253541105 | 61.46 |  |  |  | 61.46
SANTA ROSA A 1101 | 42151101 | 4.56 |  |  |  | 4.56
SANTA ROSA A 1102 | 42151102 | 12.11 |  |  |  | 12.11
SANTA ROSA A 1103 | 42151103 | 10.19 |  |  |  | 10.19
SANTA ROSA A 1104 | 42151104 | 56.23 | 37.55 | 5.25 |  | 13.43
SANTA ROSA A 1105 | 42151105 | 9.43 |  |  |  | 9.43
SANTA ROSA A 1106 | 42151106 | 10.04 |  |  |  | 10.04
SANTA ROSA A 1107 | 42151107 | 18.07 | 2.9 |  |  | 15.17
SANTA ROSA A 1108 | 42151108 | 6.62 |  | 0.14 |  | 6.48
SANTA ROSA A 1109 | 42151109 | 5.93 |  |  |  | 5.93
SANTA ROSA A 1110 | 42151110 | 16.56 |  |  |  | 16.56
SANTA ROSA A 1111 | 42151111 | 26.5 |  | 5.68 |  | 20.82
SANTA ROSA A 1112 | 42151112 | 12.74 |  |  |  | 12.74
SANTA TERESA 2101 | 82962101 | 0.3 |  |  |  | 0.3
SANTA YNEZ 1101 | 182721101 | 58.88 | 14.55 | 14.08 |  | 30.25
SANTA YNEZ 1102 | 182721102 | 34 | 4.99 | 9.02 |  | 19.99
SANTA YNEZ 1104 | 182721104 | 84.65 | 4.59 | 37.49 |  | 42.57
SARANAP 0401 | 13560401 | 2.47 |  |  |  | 2.47
SARATOGA 1103 | 83371103 | 10.51 |  | 4.61 |  | 5.9
SARATOGA 1104 | 83371104 | 18.21 |  | 2.93 |  | 15.28
SARATOGA 1105 | 83371105 | 16.78 |  | 10.16 |  | 6.62
SARATOGA 1106 | 83371106 | 26.82 | 1.38 | 14.1 |  | 11.34
SARATOGA 1107 | 83371107 | 45.56 | 20.54 | 13.97 |  | 11.05
SARATOGA 1108 | 83371108 | 18.63 |  |  |  | 18.63
SARATOGA 1109 | 83371109 | 25.39 |  |  |  | 25.39
SARATOGA 1110 | 83371110 | 20.1 |  |  |  | 20.1
SARATOGA 1111 | 83371111 | 23.96 |  |  |  | 23.96
SARATOGA 1112 | 83371112 | 8.46 |  |  |  | 8.46
SARATOGA 1113 | 83371113 | 25.8 |  |  |  | 25.8
SARATOGA 1114 | 83371114 | 21.18 |  |  |  | 21.18
SARATOGA 1115 | 83371115 | 13.85 |  | 2.83 |  | 11.02
SAUSALITO 0401 | 42490401 | 2.03 |  |  |  | 2.03
SAUSALITO 0402 | 42490402 | 2.94 |  |  |  | 2.94
SAUSALITO 1101 | 42491101 | 6.01 |  | 1.25 |  | 4.76
SAUSALITO 1102 | 42491102 | 18.84 |  | 9.13 |  | 9.71
SCE MCFARLAND 1101 | 258111101 | 0.5 |  |  |  | 0.5
SCE REFUGIO 1701 | 188071701 | 0.08 | 0.08 |  |  | 0
SCE TEHACHAPI 1101 | 258131101 | 1.44 |  | 1.44 |  | 0
SCE TEJON TIE 1101 | 258191101 | 0.06 |  | 0.06 |  | 0
SCE VEGAS 1701 | 188881701 | 0.17 | 0.17 |  |  | 0
SCHINDLER 1104 | 252891104 | 0.01 |  |  |  | 0.01
SCHINDLER 1105 | 252891105 | 41.89 |  |  |  | 41.89
SCHINDLER 1107 | 252891107 | 1.38 |  |  |  | 1.38
SCHINDLER 1108 | 252891108 | 2.16 |  |  |  | 2.16
SCHINDLER 1109 | 252891109 | 1.67 |  |  |  | 1.67
SCHINDLER 1110 | 252891110 | 48.7 |  |  |  | 48.7
SCHINDLER 1111 | 252891111 | 41.64 |  |  |  | 41.64
SCHINDLER 1112 | 252891112 | 48.85 |  |  |  | 48.85
SCHINDLER 1114 | 252891114 | 58.52 |  |  |  | 58.52
SCHINDLER 1116 | 252891116 | 25.73 |  |  |  | 25.73
SEACLIFF 0401 | 83500401 | 9.18 | 6.53 | 1.24 |  | 1.41
SEACLIFF 0402 | 83500402 | 1.57 | 0.07 | 0.01 |  | 1.49
SEMITROPIC 1104 | 252901104 | 27.78 |  |  |  | 27.78
SEMITROPIC 1106 | 252901106 | 27.39 |  |  |  | 27.39
SEMITROPIC 1108 | 252901108 | 2.28 |  |  |  | 2.28
SEMITROPIC 1110 | 252901110 | 37.2 |  |  |  | 37.2
SEMITROPIC 1112 | 252901112 | 26.75 |  |  |  | 26.75
SERRAMONTE 1103 | 22861103 | 13.2 |  |  |  | 13.2
SERRAMONTE 1104 | 22861104 | 12.67 |  |  |  | 12.67
SF E 0401 | 22070401 | 3.53 |  |  |  | 3.53
SF E 0405 | 22070405 | 2.21 |  |  |  | 2.21
SF E 0406 | 22070406 | 1.48 |  |  |  | 1.48
SF E 0407 | 22070407 | 0.94 |  |  |  | 0.94
SF E 0408 | 22070408 | 2.7 |  |  |  | 2.7
SF E 0409 | 22070409 | 1.82 |  |  |  | 1.82
SF E 0410 | 22070410 | 1.88 |  |  |  | 1.88
SF E 1101 | 22071101 | 1.16 |  |  |  | 1.16
SF E 1103 | 22071103 | 3.15 |  |  |  | 3.15
SF E 1105 | 22071105 | 2.43 |  |  |  | 2.43
SF E 1107 | 22071107 | 3.8 |  |  |  | 3.8
SF G 0401 | 22090401 | 0.67 |  |  |  | 0.67
SF G 0402 | 22090402 | 1.57 |  |  |  | 1.57
SF G 0403 | 22090403 | 0.71 |  |  |  | 0.71
SF G 0404 | 22090404 | 0.98 |  |  |  | 0.98
SF G 0405 | 22090405 | 1.47 |  |  |  | 1.47
SF G 0406 | 22090406 | 1.28 |  |  |  | 1.28
SF G 0407 | 22090407 | 1.36 |  |  |  | 1.36
SF G 0408 | 22090408 | 1.19 |  |  |  | 1.19
SF G 0409 | 22090409 | 0.99 |  |  |  | 0.99
SF G 0410 | 22090410 | 0.58 |  |  |  | 0.58
SF G 0412 | 22090412 | 1.1 |  |  |  | 1.1
SF G 0413 | 22090413 | 0.98 |  |  |  | 0.98
SF G 0414 | 22090414 | 0.89 |  |  |  | 0.89
SF G 1101 | 22091101 | 1.03 |  |  |  | 1.03
SF G 1102 | 22091102 | 0.56 |  |  |  | 0.56
SF H 0401 | 22100401 | 4.7 |  |  |  | 4.7
SF H 0402 | 22100402 | 4.1 |  |  |  | 4.1
SF H 0403 | 22100403 | 1.08 |  |  |  | 1.08
SF H 0404 | 22100404 | 2.75 |  |  |  | 2.75
SF H 0405 | 22100405 | 2.46 |  |  |  | 2.46
SF H 1101 | 22101101 | 6.45 |  |  |  | 6.45
SF H 1102 | 22101102 | 6.95 |  |  |  | 6.95
SF H 1103 | 22101103 | 8.69 |  |  |  | 8.69
SF H 1104 | 22101104 | 0.65 |  |  |  | 0.65
SF H 1105 | 22101105 | 14.98 |  |  |  | 14.98
SF H 1106 | 22101106 | 7.97 |  |  |  | 7.97
SF H 1107 | 22101107 | 3.81 |  |  |  | 3.81
SF H 1108 | 22101108 | 13.5 |  |  |  | 13.5
SF H 1109 | 22101109 | 4.76 |  |  |  | 4.76
SF H 1110 | 22101110 | 13.18 |  |  |  | 13.18
SF H 1111 | 22101111 | 4.23 |  |  |  | 4.23
SF J 0402 | 22220402 | 0.87 |  |  |  | 0.87
SF J 0404 | 22220404 | 0.52 |  |  |  | 0.52
SF J 0406 | 22220406 | 0.52 |  |  |  | 0.52
SF J 0407 | 22220407 | 0 |  |  |  | 0
SF J 0409 | 22220409 | 0.15 |  |  |  | 0.15
SF J 1108 | 22221108 | 0 |  |  |  | 0
SF K 0401 | 22130401 | 2.49 |  |  |  | 2.49
SF K 0402 | 22130402 | 3.32 |  |  |  | 3.32
SF K 0403 | 22130403 | 2.52 |  |  |  | 2.52
SF K 0404 | 22130404 | 0.98 |  |  |  | 0.98
SF K 0405 | 22130405 | 2.83 |  |  |  | 2.83
SF K 0406 | 22130406 | 1.72 |  |  |  | 1.72
SF K 0407 | 22130407 | 1.29 |  |  |  | 1.29
SF K 0408 | 22130408 | 1.36 |  |  |  | 1.36
SF K 0409 | 22130409 | 2.4 |  |  |  | 2.4
SF K 0410 | 22130410 | 2.13 |  |  |  | 2.13
SF K 0411 | 22130411 | 2.28 |  |  |  | 2.28
SF K 1101 | 22131101 | 6.78 |  |  |  | 6.78
SF L 0401 | 22260401 | 2.53 |  |  |  | 2.53
SF L 0402 | 22260402 | 0 |  |  |  | 0
SF L 0403 | 22260403 | 0.25 |  |  |  | 0.25
SF L 0404 | 22260404 | 0.81 |  |  |  | 0.81
SF L 0405 | 22260405 | 2.31 |  |  |  | 2.31
SF L 0406 | 22260406 | 2.14 |  |  |  | 2.14
SF L 0407 | 22260407 | 0.55 |  |  |  | 0.55
SF L 0408 | 22260408 | 2.41 |  |  |  | 2.41
SF L 0409 | 22260409 | 0.15 |  |  |  | 0.15
SF L 1101 | 22261101 | 2.39 |  |  |  | 2.39
SF L 1102 | 22261102 | 8.06 |  |  |  | 8.06
SF L 1103 | 22261103 | 1.98 |  |  |  | 1.98
SF M 0401 | 22270401 | 3.73 |  |  |  | 3.73
SF M 0402 | 22270402 | 1.98 |  |  |  | 1.98
SF M 0403 | 22270403 | 3.7 |  |  |  | 3.7
SF M 0404 | 22270404 | 3.58 |  |  |  | 3.58
SF M 0405 | 22270405 | 2.41 |  |  |  | 2.41
SF M 0406 | 22270406 | 2.92 |  |  |  | 2.92
SF N 0401 | 22280401 | 3.15 |  |  |  | 3.15
SF N 0402 | 22280402 | 1.01 |  |  |  | 1.01
SF N 0403 | 22280403 | 2.46 |  |  |  | 2.46
SF N 0405 | 22280405 | 1.07 |  |  |  | 1.07
SF N 0406 | 22280406 | 0.81 |  |  |  | 0.81
SF N 0408 | 22280408 | 3.11 |  |  |  | 3.11
SF N 1101 | 22281101 | 0.27 |  |  |  | 0.27
SF N 1102 | 22281102 | 6.17 |  |  |  | 6.17
SHADY GLEN 1101 | 152431101 | 39.56 |  | 33.18 |  | 6.38
SHADY GLEN 1102 | 152431102 | 51.51 | 24.11 | 25.6 |  | 1.8
SHAFTER 1101 | 253651101 | 0.03 |  |  |  | 0.03
SHAFTER 1102 | 253651102 | 27.74 |  |  |  | 27.74
SHAFTER 1103 | 253651103 | 39.56 |  |  |  | 39.56
SHAFTER 1104 | 253651104 | 9.64 |  |  |  | 9.64
SHAFTER 1111 | 253651111 | 24.37 |  |  |  | 24.37
SHAFTER 1112 | 253651112 | 47.92 |  |  |  | 47.92
SHARON 1101 | 255331101 | 1.55 |  |  |  | 1.55
SHEPHERD 2109 | 252062109 | 3.12 |  |  |  | 3.12
SHEPHERD 2110 | 252062110 | 8.44 |  |  |  | 8.44
SHEPHERD 2111 | 252062111 | 69.13 |  | 29.59 |  | 39.54
SHEPHERD 2112 | 252062112 | 7.25 |  |  |  | 7.25
SHINGLE SPRINGS 1103 | 153651103 | 13.67 | 4.61 | 3.1 |  | 5.96
SHINGLE SPRINGS 1104 | 153651104 | 60.19 | 37.4 | 6.67 |  | 16.12
SHINGLE SPRINGS 2105 | 153652105 | 32.78 | 26.07 | 4.39 |  | 2.32
SHINGLE SPRINGS 2108 | 153652108 | 29.78 | 7.18 | 7.81 |  | 14.79
SHINGLE SPRINGS 2109 | 153652109 | 207.46 | 107.4 | 99.42 |  | 0.64
SHINGLE SPRINGS 2110 | 153652110 | 65.29 | 55.53 | 7.38 |  | 2.38
SILVER 0401 | 22670401 | 5.1 |  |  |  | 5.1
SILVERADO 2102 | 43432102 | 108.64 | 32.83 | 24.58 |  | 51.23
SILVERADO 2103 | 43432103 | 32.6 | 10.78 | 0.03 |  | 21.79
SILVERADO 2104 | 43432104 | 138.87 | 75.06 | 36.11 |  | 27.7
SILVERADO 2105 | 43432105 | 63.67 | 34.91 | 1.72 |  | 27.04
SISQUOC 1101 | 182811101 | 26.7 |  |  |  | 26.7
SISQUOC 1102 | 182811102 | 111.54 | 31.35 | 19.59 |  | 60.6
SISQUOC 1103 | 182811103 | 50.2 | 22.65 | 2.83 |  | 24.72
SISQUOC 1104 | 182811104 | 36.38 |  |  |  | 36.38
SKAGGS ISLAND 1101 | 43341101 | 0.05 |  |  |  | 0.05
SMARTVILLE 1101 | 153791101 | 16.18 |  | 15.91 |  | 0.27
SMYRNA 1101 | 253551101 | 43.39 |  |  |  | 43.39
SMYRNA 1102 | 253551102 | 66.8 |  |  |  | 66.8
SMYRNA 1104 | 253551104 | 44.49 |  |  |  | 44.49
SMYRNA 1105 | 253551105 | 51.97 |  |  |  | 51.97
SMYRNA 1106 | 253551106 | 46.75 |  |  |  | 46.75
SNEATH LANE 1101 | 22721101 | 9.43 |  | 2.26 |  | 7.17
SNEATH LANE 1102 | 22721102 | 10.55 |  | 1.24 |  | 9.31
SNEATH LANE 1106 | 22721106 | 11.65 |  | 2.62 |  | 9.03
SNEATH LANE 1107 | 22721107 | 10.48 |  | 0.91 |  | 9.57
SO. CAL. EDISON #3 1101 | 258861101 | 8.58 | 6.13 | 2.29 |  | 0.16
SO. CAL. EDISON 1001 | 258881001 | 2.02 |  |  |  | 2.02
SOBRANTE 1101 | 14671101 | 21.4 |  | 15.01 |  | 6.39
SOBRANTE 1102 | 14671102 | 27.69 | 1.26 | 26.07 |  | 0.36
SOBRANTE 1103 | 14671103 | 11.37 | 1.83 | 7.7 |  | 1.84
SOLEDAD 2101 | 182052101 | 41.52 |  | 17.33 |  | 24.19
SOLEDAD 2102 | 182052102 | 49.07 |  | 11.64 |  | 37.43
SOLEDAD 2104 | 182052104 | 25.1 |  | 1.22 |  | 23.88
SOLEDAD 2105 | 182052105 | 49.1 |  | 4.47 |  | 44.63
SONOMA 1102 | 42721102 | 18.16 | 6.02 |  |  | 12.14
SONOMA 1103 | 42721103 | 25.53 | 12.7 |  |  | 12.83
SONOMA 1104 | 42721104 | 55.58 |  | 19.65 |  | 35.93
SONOMA 1105 | 42721105 | 63.18 | 3.47 | 9.93 |  | 49.78
SONOMA 1106 | 42721106 | 10.73 | 0.74 |  |  | 9.99
SONOMA 1107 | 42721107 | 52.06 |  | 3.87 |  | 48.19
SOQUEL 0402 | 83300402 | 6.63 |  |  |  | 6.63
SPAULDING 1101 | 152251101 | 23.95 | 1.19 | 19.15 | 0.37 | 3.24
SPENCE 1101 | 182201101 | 52.34 |  | 9.05 |  | 43.29
SPENCE 1102 | 182201102 | 33.26 |  | 2.36 |  | 30.9
SPENCE 1103 | 182201103 | 12.62 |  |  |  | 12.62
SPENCE 1105 | 182201105 | 7.18 |  |  |  | 7.18
SPRING GAP 1702 | 162831702 | 42.21 | 39.56 | 0.77 |  | 1.88
STAFFORD 1101 | 43201101 | 19.24 |  | 2.81 |  | 16.43
STAFFORD 1102 | 43201102 | 37.44 | 1.54 | 19.68 |  | 16.22
STAGG 1101 | 162421101 | 19.65 |  |  |  | 19.65
STAGG 1103 | 162421103 | 6.09 |  |  |  | 6.09
STAGG 1105 | 162421105 | 12.1 |  |  |  | 12.1
STAGG 1106 | 162421106 | 1.86 |  |  |  | 1.86
STAGG 2104 | 162422104 | 24.57 |  |  |  | 24.57
STAGG 2105 | 162422105 | 4.5 |  |  |  | 4.5
STAGG 2106 | 162422106 | 5.41 |  |  |  | 5.41
STAGG 2107 | 162422107 | 6.02 |  |  |  | 6.02
STAGG 2108 | 162422108 | 5.84 |  |  |  | 5.84
STANISLAUS 1701 | 162821701 | 74.51 | 22.67 | 51.59 |  | 0.25
STANISLAUS 1702 | 162821702 | 83.84 | 78.32 | 5.52 |  | 0
STELLING 1102 | 83481102 | 0.69 |  |  |  | 0.69
STELLING 1103 | 83481103 | 2.87 |  |  |  | 2.87
STELLING 1104 | 83481104 | 11.04 |  |  |  | 11.04
STELLING 1105 | 83481105 | 0.4 |  |  |  | 0.4
STELLING 1106 | 83481106 | 0 |  |  |  | 0
STELLING 1107 | 83481107 | 8.23 |  |  |  | 8.23
STELLING 1108 | 83481108 | 31.86 |  |  |  | 31.86
STELLING 1109 | 83481109 | 16.64 |  | 0.89 |  | 15.75
STELLING 1110 | 83481110 | 53.39 | 14.11 | 22.08 |  | 17.2
STELLING 1111 | 83481111 | 26.85 |  |  |  | 26.85
STELLING 1112 | 83481112 | 2.2 |  |  |  | 2.2
STELLING 1113 | 83481113 | 17.2 |  |  |  | 17.2
STILLWATER 1101 | 103561101 | 35.15 |  | 34.43 |  | 0.72
STILLWATER 1102 | 103561102 | 78.33 |  | 78.23 |  | 0.1
STOCKDALE 1105 | 254071105 | 5.05 |  |  |  | 5.05
STOCKDALE 1106 | 254071106 | 5.63 |  |  |  | 5.63
STOCKDALE 1108 | 254071108 | 3.85 |  |  |  | 3.85
STOCKDALE 1109 | 254071109 | 4.49 |  |  |  | 4.49
STOCKDALE 1110 | 254071110 | 6.33 |  |  |  | 6.33
STOCKDALE 1111 | 254071111 | 8.66 |  |  |  | 8.66
STOCKDALE 2105 | 254072105 | 5.01 |  |  |  | 5.01
STOCKDALE 2106 | 254072106 | 8.98 |  |  |  | 8.98
STOCKDALE 2107 | 254072107 | 1.84 |  |  |  | 1.84
STOCKDALE 2108 | 254072108 | 2.96 |  |  |  | 2.96
STOCKDALE 2109 | 254072109 | 8.59 |  |  |  | 8.59
STOCKDALE 2110 | 254072110 | 8.83 |  |  |  | 8.83
STOCKDALE 2111 | 254072111 | 2.88 |  |  |  | 2.88
STOCKDALE 2112 | 254072112 | 29.52 |  |  |  | 29.52
STOCKDALE 2113 | 254072113 | 20.47 |  |  |  | 20.47
STOCKDALE 2114 | 254072114 | 10.49 |  |  |  | 10.49
STOCKDALE 2115 | 254072115 | 0.45 |  |  |  | 0.45
STOCKTON A 0404 | 162370404 | 5.2 |  |  |  | 5.2
STOCKTON A 0405 | 162370405 | 0.39 |  |  |  | 0.39
STOCKTON A 0406 | 162370406 | 3.29 |  |  |  | 3.29
STOCKTON A 0410 | 162370410 | 6.32 |  |  |  | 6.32
STOCKTON A 1101 | 162371101 | 4.13 |  |  |  | 4.13
STOCKTON A 1102 | 162371102 | 6.52 |  |  |  | 6.52
STOCKTON A 1103 | 162371103 | 0.21 |  |  |  | 0.21
STOCKTON A 1104 | 162371104 | 15.92 |  |  |  | 15.92
STOCKTON A 1105 | 162371105 | 12.39 |  |  |  | 12.39
STOCKTON A 1106 | 162371106 | 17.15 |  |  |  | 17.15
STOCKTON A 1107 | 162371107 | 11.31 |  |  |  | 11.31
STOCKTON A 1108 | 162371108 | 9.39 |  |  |  | 9.39
STOCKTON A 1109 | 162371109 | 11.96 |  |  |  | 11.96
STOCKTON A 1110 | 162371110 | 9.65 |  |  |  | 9.65
STOCKTON A 1111 | 162371111 | 0.07 |  |  |  | 0.07
STOCKTON ACRES 0401 | 163220401 | 2.87 |  |  |  | 2.87
STOCKTON ACRES 0402 | 163220402 | 3.03 |  |  |  | 3.03
STONE 1101 | 83701101 | 20.05 |  |  |  | 20.05
STONE 1104 | 83701104 | 5.58 |  |  |  | 5.58
STONE 1107 | 83701107 | 12.05 |  |  |  | 12.05
STONE 1108 | 83701108 | 4.4 |  |  |  | 4.4
STONE 1109 | 83701109 | 8.19 |  |  |  | 8.19
STONE 1110 | 83701110 | 11.89 |  |  |  | 11.89
STONE CORRAL 1108 | 252921108 | 76.32 |  | 1.87 |  | 74.45
STONE CORRAL 1109 | 252921109 | 16.46 |  |  |  | 16.46
STONE CORRAL 1110 | 252921110 | 62.53 |  | 2.01 |  | 60.52
STOREY 1104 | 254611104 | 75.65 |  |  |  | 75.65
STOREY 1105 | 254611105 | 14.4 |  |  |  | 14.4
STOREY 1106 | 254611106 | 13.63 |  |  |  | 13.63
STOREY 1107 | 254611107 | 19.13 |  |  |  | 19.13
STOREY 1108 | 254611108 | 72.37 |  |  |  | 72.37
STOREY 1109 | 254611109 | 177.22 |  |  |  | 177.22
STOREY 1111 | 254611111 | 29.63 |  |  |  | 29.63
STROUD 1101 | 253661101 | 31.55 |  |  |  | 31.55
STROUD 1102 | 253661102 | 34.55 |  |  |  | 34.55
STROUD 1104 | 253661104 | 31.12 |  |  |  | 31.12
STUART 0401 | 13840401 | 2.96 |  |  |  | 2.96
STUART 0402 | 13840402 | 1.81 |  |  |  | 1.81
STUART 0403 | 13840403 | 3.1 |  |  |  | 3.1
STUART 0404 | 13840404 | 0.49 |  |  |  | 0.49
STUART 0405 | 13840405 | 2.56 |  |  |  | 2.56
STUART 0406 | 13840406 | 2.94 |  |  |  | 2.94
SUISUN 1101 | 62131101 | 5.92 |  |  |  | 5.92
SUISUN 1102 | 62131102 | 11.97 |  |  |  | 11.97
SUISUN 1103 | 62131103 | 2.73 |  |  |  | 2.73
SUISUN 1104 | 62131104 | 4.84 |  |  |  | 4.84
SUISUN 1105 | 62131105 | 5.37 |  |  |  | 5.37
SUISUN 1106 | 62131106 | 5 |  |  |  | 5
SUISUN 1107 | 62131107 | 9.68 |  |  |  | 9.68
SUISUN 1108 | 62131108 | 6.62 |  |  |  | 6.62
SUISUN 1109 | 62131109 | 8.08 |  |  |  | 8.08
SUISUN 1110 | 62131110 | 2.91 |  |  |  | 2.91
SUISUN 1111 | 62131111 | 0.63 |  |  |  | 0.63
SUISUN 1112 | 62131112 | 2.85 |  |  |  | 2.85
SULLIVAN 0402 | 22850402 | 3.21 |  |  |  | 3.21
SUMMIT 1101 | 152591101 | 15.23 |  | 7.22 | 2.05 | 5.96
SUMMIT 1102 | 152591102 | 5.04 |  | 5.04 |  | 0
SUNOL 1101 | 14241101 | 55.12 | 9.57 | 23.25 |  | 22.3
SWIFT 2102 | 83392102 | 2.95 |  | 0.35 |  | 2.6
SWIFT 2106 | 83392106 | 21.33 |  |  |  | 21.33
SWIFT 2107 | 83392107 | 11.89 |  | 1.9 |  | 9.99
SWIFT 2108 | 83392108 | 4.92 |  |  |  | 4.92
SWIFT 2109 | 83392109 | 5.47 |  | 0.15 |  | 5.32
SWIFT 2110 | 83392110 | 86.35 |  | 81.48 |  | 4.87
SWIFT 2111 | 83392111 | 8.6 |  |  |  | 8.6
SYCAMORE CREEK 1101 | 102971101 | 4.57 |  |  |  | 4.57
SYCAMORE CREEK 1102 | 102971102 | 7.57 |  |  |  | 7.57
SYCAMORE CREEK 1103 | 102971103 | 3.16 |  |  |  | 3.16
SYCAMORE CREEK 1104 | 102971104 | 8.15 |  |  |  | 8.15
SYCAMORE CREEK 1105 | 102971105 | 16.45 |  |  |  | 16.45
SYCAMORE CREEK 1107 | 102971107 | 6.04 |  |  |  | 6.04
SYCAMORE CREEK 1109 | 102971109 | 13.44 |  | 0.13 |  | 13.31
SYCAMORE CREEK 1110 | 102971110 | 8.47 |  |  |  | 8.47
SYCAMORE CREEK 1111 | 102971111 | 65.09 | 27.39 | 24.92 |  | 12.78
TAFT 1101 | 252081101 | 14.26 |  |  |  | 14.26
TAFT 1102 | 252081102 | 0.05 |  |  |  | 0.05
TAFT 1103 | 252081103 | 27.53 |  |  |  | 27.53
TAFT 1104 | 252081104 | 11.24 |  |  |  | 11.24
TAFT 1106 | 252081106 | 7.19 |  |  |  | 7.19
TAFT 1108 | 252081108 | 9.33 |  |  |  | 9.33
TAMARACK 1101 | 152291101 | 19.66 |  | 18.77 | 0.13 | 0.76
TAMARACK 1102 | 152291102 | 7.89 |  |  | 0.31 | 7.58
TAR FLAT 0401 | 163240401 | 3.63 | 0 | 3.16 |  | 0.47
TAR FLAT 0402 | 163240402 | 6.72 | 0.88 | 4.53 |  | 1.31
TARAVAL 0401 | 22500401 | 1.83 |  |  |  | 1.83
TARAVAL 0402 | 22500402 | 3.05 |  |  |  | 3.05
TARAVAL 0403 | 22500403 | 3.49 |  |  |  | 3.49
TASSAJARA 2103 | 14662103 | 19.68 | 0.18 | 0.3 |  | 19.2
TASSAJARA 2104 | 14662104 | 9.68 | 1.57 | 4.37 |  | 3.74
TASSAJARA 2106 | 14662106 | 2.92 |  | 0.35 |  | 2.57
TASSAJARA 2107 | 14662107 | 8.55 |  |  |  | 8.55
TASSAJARA 2108 | 14662108 | 24.23 | 1.7 |  |  | 22.53
TASSAJARA 2109 | 14662109 | 4.02 |  | 2.89 |  | 1.13
TASSAJARA 2112 | 14662112 | 18.63 | 6.79 | 3.6 |  | 8.24
TASSAJARA 2113 | 14662113 | 4.93 | 3.82 |  |  | 1.11
TECUYA 1101 | 254511101 | 0.04 |  |  |  | 0.04
TEJON 1102 | 252931102 | 60.89 |  | 36.83 |  | 24.06
TEJON 1103 | 252931103 | 32.72 |  | 2.97 |  | 29.75
TEJON 1105 | 252931105 | 31.13 |  |  |  | 31.13
TEJON 1106 | 252931106 | 36 |  |  |  | 36
TEJON 1107 | 252931107 | 0.54 |  |  |  | 0.54
TEMBLOR 1104 | 252551104 | 49.23 |  |  |  | 49.23
TEMBLOR 2103 | 252552103 | 30.36 |  |  |  | 30.36
TEMPLETON 2108 | 183052108 | 36 |  | 5.36 |  | 30.64
TEMPLETON 2109 | 183052109 | 215.37 |  |  |  | 215.37
TEMPLETON 2110 | 183052110 | 173.13 | 33.55 | 93.88 |  | 45.7
TEMPLETON 2111 | 183052111 | 92.71 | 13.85 | 61.07 |  | 17.79
TEMPLETON 2112 | 183052112 | 37.93 |  | 2.66 |  | 35.27
TEMPLETON 2113 | 183052113 | 324.21 | 53.22 | 143.12 |  | 127.87
TEMPORARY CARBONA 1101 | 169951101 | 39.09 |  |  |  | 39.09
TEMPORARY CARBONA 1102 | 169951102 | 3.44 |  |  |  | 3.44
TEMPORARY CARBONA 1104 | 169951104 | 31.69 |  |  |  | 31.69
TEMPORARY CARBONA 1105 | 169951105 | 5.3 |  |  |  | 5.3
TERMINOUS 1102 | 163021102 | 23.78 |  |  |  | 23.78
TERMINOUS 1103 | 163021103 | 40.06 |  |  |  | 40.06
TEVIS 2101 | 255322101 | 23.82 |  |  |  | 23.82
TEVIS 2102 | 255322102 | 2.14 |  |  |  | 2.14
TEVIS 2103 | 255322103 | 3.29 |  |  |  | 3.29
TEVIS 2104 | 255322104 | 17.27 |  |  |  | 17.27
TEVIS 2105 | 255322105 | 2.1 |  |  |  | 2.1
TEXACO EMIDIO 1101 | 255421101 | 0.02 |  |  |  | 0.02
TIDEWATER 2104 | 14652104 | 25.32 |  |  |  | 25.32
TIDEWATER 2105 | 14652105 | 14.07 |  |  |  | 14.07
TIDEWATER 2106 | 14652106 | 35.33 |  | 2.29 |  | 33.04
TIDEWATER 2107 | 14652107 | 21.68 |  |  |  | 21.68
TIDEWATER 2108 | 14652108 | 9.61 |  |  |  | 9.61
TIDEWATER 2109 | 14652109 | 33.14 |  |  |  | 33.14
TIDEWATER 2110 | 14652110 | 10.2 |  |  |  | 10.2
TIGER CREEK 0201 | 161380201 | 3.77 | 1.73 | 2.04 |  | 0
TIVY VALLEY 1106 | 252941106 | 27.01 |  |  |  | 27.01
TIVY VALLEY 1107 | 252941107 | 174.48 |  | 116.51 |  | 57.97
TOCALOMA 0241 | 43150241 | 0.04 |  | 0.04 |  | 0
TOKAY 1101 | 168881101 | 12.31 |  |  |  | 12.31
TRACY 0402 | 162880402 | 2.93 |  |  |  | 2.93
TRACY 0405 | 162880405 | 3.27 |  |  |  | 3.27
TRACY 1102 | 162881102 | 4.72 |  |  |  | 4.72
TRACY 1103 | 162881103 | 4.44 |  |  |  | 4.44
TRACY 1104 | 162881104 | 4.77 |  |  |  | 4.77
TRACY 1105 | 162881105 | 4.73 |  |  |  | 4.73
TRACY 1106 | 162881106 | 36.31 |  |  |  | 36.31
TRACY 1107 | 162881107 | 6.18 |  |  |  | 6.18
TRACY 1108 | 162881108 | 23.1 |  |  |  | 23.1
TRACY 1109 | 162881109 | 5.06 |  |  |  | 5.06
TRACY 1110 | 162881110 | 9.16 |  |  |  | 9.16
TRACY 1111 | 162881111 | 7.27 |  |  |  | 7.27
TRACY 1112 | 162881112 | 4.71 |  |  |  | 4.71
TRES PINOS 1111 | 183221111 | 32.92 |  | 0.11 |  | 32.81
TRES VIAS 1101 | 103251101 | 68.49 |  |  |  | 68.49
TRIDAM POWERHOUSE 2101 | 168152101 | 0.05 | 0.05 |  |  | 0
TRIMBLE 1103 | 83801103 | 2.74 |  |  |  | 2.74
TRIMBLE 1104 | 83801104 | 0.46 |  |  |  | 0.46
TRIMBLE 1105 | 83801105 | 1.44 |  |  |  | 1.44
TRIMBLE 1106 | 83801106 | 0.65 |  |  |  | 0.65
TRIMBLE 1107 | 83801107 | 1.05 |  |  |  | 1.05
TRIMBLE 1110 | 83801110 | 0.34 |  |  |  | 0.34
TRIMBLE 2114 | 83802114 | 0 |  |  |  | 0
TRIMBLE 2115 | 83802115 | 0.31 |  |  |  | 0.31
TRIMBLE 2116 | 83802116 | 3.39 |  |  |  | 3.39
TRIMBLE 2118 | 83802118 | 0.39 |  |  |  | 0.39
TRINIDAD 1101 | 192231101 | 26.56 |  |  |  | 26.56
TRINIDAD 1102 | 192231102 | 24.29 |  |  | 0.25 | 24.04
TUDOR 1101 | 153711101 | 31.54 |  |  |  | 31.54
TUDOR 1102 | 153711102 | 23.17 |  |  |  | 23.17
TULARE LAKE 1104 | 252951104 | 14.59 |  |  |  | 14.59
TULARE LAKE 1106 | 252951106 | 53.29 |  |  |  | 53.29
TULARE LAKE 1108 | 252951108 | 48.8 |  |  |  | 48.8
TULUCAY 1101 | 42301101 | 18.04 |  | 3.77 |  | 14.27
TUPMAN 1103 | 254561103 | 45.48 |  |  |  | 45.48
TUPMAN 1104 | 254561104 | 53.39 |  |  |  | 53.39
TUPMAN 1105 | 254561105 | 23.11 |  |  |  | 23.11
TUPMAN 1106 | 254561106 | 36.62 |  |  |  | 36.62
TWISSELMAN 1101 | 254401101 | 0.02 |  |  |  | 0.02
TWISSELMAN 1102 | 254401102 | 49.2 |  |  |  | 49.2
TWISSELMAN 1104 | 254401104 | 0.02 |  |  |  | 0.02
TWISSELMAN 2105 | 254402105 | 88.98 |  |  |  | 88.98
TYLER 1103 | 103571103 | 4.24 |  |  |  | 4.24
TYLER 1104 | 103571104 | 35.52 |  |  |  | 35.52
TYLER 1105 | 103571105 | 114.16 |  | 60.2 |  | 53.96
UKIAH 1111 | 42771111 | 31.96 |  | 7.84 |  | 24.12
UKIAH 1113 | 42771113 | 15.91 |  | 7.53 |  | 8.38
UKIAH 1114 | 42771114 | 103.89 |  | 53.87 |  | 50.02
UKIAH 1115 | 42771115 | 50.67 |  | 35.18 |  | 15.49
UPPER LAKE 1101 | 42871101 | 73.85 | 1.44 | 35.12 |  | 37.29
VACA DIXON 1101 | 63591101 | 50.26 |  | 22.19 |  | 28.07
VACA DIXON 1102 | 63591102 | 1.96 |  |  |  | 1.96
VACA DIXON 1103 | 63591103 | 127.04 |  |  |  | 127.04
VACA DIXON 1104 | 63591104 | 7.49 |  |  |  | 7.49
VACA DIXON 1105 | 63591105 | 49.88 |  | 1.41 |  | 48.47
VACA DIXON 1106 | 63591106 | 11.12 |  |  |  | 11.12
VACA DIXON 1109 | 63591109 | 2.13 |  |  |  | 2.13
VACAVILLE 1102 | 63601102 | 1 |  |  |  | 1
VACAVILLE 1103 | 63601103 | 11.22 |  |  |  | 11.22
VACAVILLE 1104 | 63601104 | 13.7 |  | 11.46 |  | 2.24
VACAVILLE 1105 | 63601105 | 2.87 |  |  |  | 2.87
VACAVILLE 1106 | 63601106 | 1.76 |  |  |  | 1.76
VACAVILLE 1107 | 63601107 | 1.91 |  |  |  | 1.91
VACAVILLE 1108 | 63601108 | 41.46 |  | 20.22 |  | 21.24
VACAVILLE 1109 | 63601109 | 5.66 |  | 0.81 |  | 4.85
VACAVILLE 1110 | 63601110 | 2.36 |  |  |  | 2.36
VACAVILLE 1111 | 63601111 | 12.15 |  | 9.27 |  | 2.88
VACAVILLE 1112 | 63601112 | 3.33 |  | 0.19 |  | 3.14
VALLEJO B 0411 | 42450411 | 7.09 |  |  |  | 7.09
VALLEJO B 0413 | 42450413 | 6.48 |  |  |  | 6.48
VALLEJO B 0414 | 42450414 | 8.31 |  |  |  | 8.31
VALLEJO B 0415 | 42450415 | 7.62 |  |  |  | 7.62
VALLEJO B 1101 | 42451101 | 16.36 |  |  |  | 16.36
VALLEJO B 1102 | 42451102 | 2.5 |  |  |  | 2.5
VALLEJO C 0401 | 42550401 | 2.84 |  |  |  | 2.84
VALLEY HOME 1702 | 162981702 | 56.31 |  |  |  | 56.31
VALLEY HOME 1703 | 162981703 | 127.56 |  |  |  | 127.56
VALLEY HOME 1704 | 162981704 | 38.85 |  |  |  | 38.85
VALLEY VIEW 1103 | 14341103 | 18.14 | 0.59 |  |  | 17.55
VALLEY VIEW 1105 | 14341105 | 15.09 |  | 3.97 |  | 11.12
VALLEY VIEW 1106 | 14341106 | 21.32 | 1.99 | 6.77 |  | 12.56
VASCO 1101 | 13751101 | 2.56 |  |  |  | 2.56
VASCO 1102 | 13751102 | 88.13 |  | 45.57 |  | 42.56
VASCO 1103 | 13751103 | 14.81 |  |  |  | 14.81
VASONA 1101 | 83771101 | 9.97 |  |  |  | 9.97
VASONA 1102 | 83771102 | 15.45 |  | 0.12 |  | 15.33
VASONA 1103 | 83771103 | 15.56 |  |  |  | 15.56
VASONA 1104 | 83771104 | 3.78 |  |  |  | 3.78
VASONA 1105 | 83771105 | 11.7 |  |  |  | 11.7
VASONA 1108 | 83771108 | 10.99 |  |  |  | 10.99
VICTOR 1101 | 163281101 | 18.3 |  |  |  | 18.3
VICTOR 1102 | 163281102 | 87.97 |  |  |  | 87.97
VIEJO 2201 | 182852201 | 17.34 |  | 14.63 |  | 2.71
VIEJO 2202 | 182852202 | 44.28 |  | 14.18 |  | 30.1
VIEJO 2203 | 182852203 | 22.9 |  | 3.04 |  | 19.86
VIEJO 2204 | 182852204 | 24.64 |  | 4.39 |  | 20.25
VIERRA 1701 | 162701701 | 9.75 |  |  |  | 9.75
VIERRA 1702 | 162701702 | 6.92 |  |  |  | 6.92
VIERRA 1703 | 162701703 | 5.57 |  |  |  | 5.57
VIERRA 1706 | 162701706 | 6.89 |  |  |  | 6.89
VIERRA 1707 | 162701707 | 46.98 |  |  |  | 46.98
VINA 1101 | 103581101 | 49.71 |  |  |  | 49.71
VINEYARD 2104 | 14502104 | 3.75 |  |  |  | 3.75
VINEYARD 2105 | 14502105 | 3.94 |  |  |  | 3.94
VINEYARD 2106 | 14502106 | 5.51 |  |  |  | 5.51
VINEYARD 2107 | 14502107 | 13.91 |  | 3 |  | 10.91
VINEYARD 2108 | 14502108 | 13.41 | 5.17 |  |  | 8.24
VINEYARD 2109 | 14502109 | 4.73 |  |  |  | 4.73
VINEYARD 2110 | 14502110 | 10.3 |  | 5 |  | 5.3
VIRGINIA 0401 | 13780401 | 4.07 |  |  |  | 4.07
VOLTA 1101 | 102541101 | 146.78 | 6.29 | 138.37 |  | 2.12
VOLTA 1102 | 102541102 | 129.72 | 86.93 | 41.97 |  | 0.82
Valley Springs 1101 | 168891101 | 79.1 |  | 51.37 |  | 27.73
WAHTOKE 1106 | 254531106 | 13.96 |  |  |  | 13.96
WAHTOKE 1107 | 254531107 | 19.24 |  |  |  | 19.24
WAHTOKE 1108 | 254531108 | 108.56 |  |  |  | 108.56
WAHTOKE 1109 | 254531109 | 6.99 |  |  |  | 6.99
WAHTOKE 1110 | 254531110 | 16.12 |  |  |  | 16.12
WAHTOKE 1111 | 254531111 | 29.97 |  |  |  | 29.97
WALDO 0401 | 13350401 | 5.74 |  | 1.6 |  | 4.14
WALDO 0402 | 13350402 | 5.19 |  | 2.96 |  | 2.23
WALL 0401 | 13740401 | 5.39 |  |  |  | 5.39
WALNUT CREEK 0403 | 12200403 | 0.51 |  |  |  | 0.51
WALNUT CREEK 0404 | 12200404 | 6.43 |  |  |  | 6.43
WARD 0401 | 12980401 | 4.54 |  |  |  | 4.54
WASCO 1101 | 252961101 | 12.22 |  |  |  | 12.22
WASCO 1102 | 252961102 | 7.81 |  |  |  | 7.81
WASCO 1104 | 252961104 | 9.95 |  |  |  | 9.95
WATERLOO 1101 | 163151101 | 58.08 |  |  |  | 58.08
WATERLOO 1102 | 163151102 | 21.76 |  |  |  | 21.76
WATERSHED 0402 | 24240402 | 1.19 | 0.02 |  |  | 1.17
WATSONVILLE 0411 | 83330411 | 2.32 |  |  |  | 2.32
WATSONVILLE 0413 | 83330413 | 1.22 |  |  |  | 1.22
WATSONVILLE 0414 | 83330414 | 1.28 |  |  |  | 1.28
WATSONVILLE 2101 | 83332101 | 102.61 |  |  |  | 102.61
WEBER 1101 | 163481101 | 3.16 |  |  |  | 3.16
WEBER 1102 | 163481102 | 31.75 |  |  |  | 31.75
WEBER 1103 | 163481103 | 1.8 |  |  |  | 1.8
WEBER 1105 | 163481105 | 21.01 |  |  |  | 21.01
WEBER 1107 | 163481107 | 0.04 |  |  |  | 0.04
WEBER 1108 | 163481108 | 0.44 |  |  |  | 0.44
WEBER 1109 | 163481109 | 53.25 |  |  |  | 53.25
WEBER 1110 | 163481110 | 12.1 |  |  |  | 12.1
WEBER 1111 | 163481111 | 20.07 |  |  |  | 20.07
WEBER 1112 | 163481112 | 0.02 |  |  |  | 0.02
WEBER 1113 | 163481113 | 2.13 |  |  |  | 2.13
WEBER 1114 | 163481114 | 9.85 |  |  |  | 9.85
WEBER 1115 | 163481115 | 14.4 |  |  |  | 14.4
WEEDPATCH 1101 | 252971101 | 21.76 |  |  |  | 21.76
WEEDPATCH 1102 | 252971102 | 18.82 |  |  |  | 18.82
WEEDPATCH 1103 | 252971103 | 18.4 |  |  |  | 18.4
WEEDPATCH 1105 | 252971105 | 0.88 |  |  |  | 0.88
WEEDPATCH 1106 | 252971106 | 64.49 |  |  |  | 64.49
WEIMAR 1101 | 152491101 | 78.55 |  | 78.55 |  | 0
WEIMAR 1102 | 152491102 | 36.71 |  | 36.71 |  | 0
WELLFIELD 1102 | 254291102 | 37.91 |  |  |  | 37.91
WELLFIELD 1103 | 254291103 | 0.32 |  |  |  | 0.32
WELLFIELD 1104 | 254291104 | 5.27 |  |  |  | 5.27
WEST FRESNO 1101 | 253731101 | 16.04 |  |  |  | 16.04
WEST FRESNO 1102 | 253731102 | 4.18 |  |  |  | 4.18
WEST FRESNO 1103 | 253731103 | 5.93 |  |  |  | 5.93
WEST FRESNO 1104 | 253731104 | 15.39 |  |  |  | 15.39
WEST FRESNO 1105 | 253731105 | 6.07 |  |  |  | 6.07
WEST FRESNO 1106 | 253731106 | 5.94 |  |  |  | 5.94
WEST FRESNO 1107 | 253731107 | 4.35 |  |  |  | 4.35
WEST FRESNO 1108 | 253731108 | 2.48 |  |  |  | 2.48
WEST FRESNO 1109 | 253731109 | 20.35 |  |  |  | 20.35
WEST FRESNO 1110 | 253731110 | 5.26 |  |  |  | 5.26
WEST FRESNO 1111 | 253731111 | 27.98 |  |  |  | 27.98
WEST FRESNO 1112 | 253731112 | 29.43 |  |  |  | 29.43
WEST LANE 1101 | 163621101 | 10.07 |  |  |  | 10.07
WEST LANE 1102 | 163621102 | 14.68 |  |  |  | 14.68
WEST LANE 1103 | 163621103 | 4.92 |  |  |  | 4.92
WEST POINT 1101 | 163201101 | 63.11 | 63.07 | 0.04 |  | 0
WEST POINT 1102 | 163201102 | 252.12 | 184.18 | 67.43 |  | 0.51
WEST SACRAMENTO 1104 | 63131104 | 10.62 |  |  |  | 10.62
WEST SACRAMENTO 1105 | 63131105 | 6.33 |  |  |  | 6.33
WEST SACRAMENTO 1106 | 63131106 | 2.03 |  |  |  | 2.03
WEST SACRAMENTO 1107 | 63131107 | 15.65 |  |  |  | 15.65
WEST SACRAMENTO 1108 | 63131108 | 9.97 |  |  |  | 9.97
WEST SACRAMENTO 1109 | 63131109 | 39.15 |  |  |  | 39.15
WEST SACRAMENTO 1110 | 63131110 | 7.25 |  |  |  | 7.25
WEST SACRAMENTO 1111 | 63131111 | 0.01 |  |  |  | 0.01
WESTLAKE 0401 | 22600401 | 0.82 |  |  |  | 0.82
WESTLAKE 0403 | 22600403 | 1.76 |  |  |  | 1.76
WESTLEY 1101 | 162671101 | 87.11 |  |  |  | 87.11
WESTLEY 1102 | 162671102 | 0.07 |  |  |  | 0.07
WESTLEY 1103 | 162671103 | 96.08 |  | 0.43 |  | 95.65
WESTPARK 1101 | 253701101 | 11.36 |  |  |  | 11.36
WESTPARK 1102 | 253701102 | 3.77 |  |  |  | 3.77
WESTPARK 1103 | 253701103 | 16.97 |  |  |  | 16.97
WESTPARK 1104 | 253701104 | 10.44 |  |  |  | 10.44
WESTPARK 1105 | 253701105 | 2.29 |  |  |  | 2.29
WESTPARK 1106 | 253701106 | 2.77 |  |  |  | 2.77
WESTPARK 1107 | 253701107 | 5.4 |  |  |  | 5.4
WESTPARK 1108 | 253701108 | 19.87 |  |  |  | 19.87
WESTPARK 1109 | 253701109 | 9.84 |  |  |  | 9.84
WESTPARK 1110 | 253701110 | 13.06 |  |  |  | 13.06
WESTPARK 1111 | 253701111 | 5.25 |  |  |  | 5.25
WESTPARK 1112 | 253701112 | 6.93 |  |  |  | 6.93
WHEATLAND 1101 | 152811101 | 0 |  |  |  | 0
WHEATLAND 1102 | 152811102 | 30.12 |  |  |  | 30.12
WHEATLAND 1104 | 152811104 | 113.93 |  |  |  | 113.93
WHEATLAND 1105 | 152811105 | 75.14 |  | 10.8 |  | 64.34
WHEELER RIDGE 1101 | 253481101 | 73.91 |  |  |  | 73.91
WHEELER RIDGE 1102 | 253481102 | 34.41 |  |  |  | 34.41
WHEELER RIDGE 1103 | 253481103 | 39.08 |  |  |  | 39.08
WHISMAN 1101 | 83631101 | 5.09 |  |  |  | 5.09
WHISMAN 1102 | 83631102 | 1.77 |  |  |  | 1.77
WHISMAN 1103 | 83631103 | 2.68 |  |  |  | 2.68
WHISMAN 1104 | 83631104 | 0 |  |  |  | 0
WHISMAN 1105 | 83631105 | 0.94 |  |  |  | 0.94
WHISMAN 1106 | 83631106 | 7.18 |  |  |  | 7.18
WHISMAN 1107 | 83631107 | 0.13 |  |  |  | 0.13
WHISMAN 1108 | 83631108 | 7.09 |  |  |  | 7.09
WHISMAN 1110 | 83631110 | 1.92 |  |  |  | 1.92
WHISMAN 1111 | 83631111 | 2.2 |  |  |  | 2.2
WHITMORE 1101 | 103601101 | 91.21 | 31.9 | 59.31 |  | 0
WILDWOOD 1101 | 103611101 | 32.01 |  | 32.01 |  | 0
WILKINS SLOUGH 1101 | 62771101 | 52.84 |  |  |  | 52.84
WILKINS SLOUGH 1102 | 62771102 | 62.23 |  |  |  | 62.23
WILKINS SLOUGH 1103 | 62771103 | 34.46 |  |  |  | 34.46
WILLIAMS 1101 | 62051101 | 32.68 |  |  |  | 32.68
WILLIAMS 1102 | 62051102 | 98.77 |  |  |  | 98.77
WILLITS 1102 | 42661102 | 11.32 |  | 4.8 |  | 6.52
WILLITS 1103 | 42661103 | 154.71 | 50 | 91.47 |  | 13.24
WILLITS 1104 | 42661104 | 95.98 | 50.96 | 36.39 |  | 8.63
WILLOW CREEK 1101 | 192171101 | 56.58 | 25.96 | 20.08 |  | 10.54
WILLOW CREEK 1102 | 192171102 | 9.58 | 5.32 | 4.26 |  | 0
WILLOW CREEK 1103 | 192171103 | 77.15 | 0.54 | 75.45 |  | 1.16
WILLOW PASS 1101 | 13911101 | 7.07 |  | 1.12 |  | 5.95
WILLOW PASS 1102 | 13911102 | 5.11 |  |  |  | 5.11
WILLOW PASS 2107 | 13912107 | 3.07 |  | 0.66 |  | 2.41
WILLOW PASS 2108 | 13912108 | 21.23 |  | 0.23 |  | 21
WILLOWS A 1101 | 102741101 | 4.29 |  |  |  | 4.29
WILLOWS A 1103 | 102741103 | 9.91 |  |  |  | 9.91
WILLOWS A 1104 | 102741104 | 9.44 |  |  |  | 9.44
WILSON 1101 | 254301101 | 13.27 |  |  |  | 13.27
WILSON 1102 | 254301102 | 31.31 |  |  |  | 31.31
WILSON 1103 | 254301103 | 115.54 |  |  |  | 115.54
WINDSOR 1101 | 43501101 | 8.5 |  |  |  | 8.5
WINDSOR 1102 | 43501102 | 14.76 |  |  |  | 14.76
WINDSOR 1103 | 43501103 | 11.22 |  | 2 |  | 9.22
WINTERS 1101 | 63321101 | 12.9 |  |  |  | 12.9
WINTERS 1102 | 63321102 | 35.51 |  |  |  | 35.51
WISE 1101 | 152271101 | 12.87 |  | 5.69 |  | 7.18
WISE 1102 | 152271102 | 119.15 |  | 114.13 |  | 5.02
WISHON 1101 | 251511101 | 7.6 | 3.48 | 4.13 |  | -0.01
WOLFE 1104 | 83671104 | 6.81 |  |  |  | 6.81
WOLFE 1105 | 83671105 | 7.29 |  |  |  | 7.29
WOLFE 1106 | 83671106 | 9.16 |  |  |  | 9.16
WOLFE 1107 | 83671107 | 10.41 |  |  |  | 10.41
WOLFE 1109 | 83671109 | 8.93 |  |  |  | 8.93
WOLFE 1110 | 83671110 | 2.04 |  |  |  | 2.04
WOLFE 1113 | 83671113 | 17.33 |  |  |  | 17.33
WOLFE 1114 | 83671114 | 2.93 |  |  |  | 2.93
WOOD 0401 | 13380401 | 3.32 |  | 0.17 |  | 3.15
WOODACRE 1101 | 43021101 | 38.24 | 22.84 | 7.8 |  | 7.6
WOODACRE 1102 | 43021102 | 31.11 | 19.35 | 11.4 |  | 0.36
WOODLAND 1101 | 62031101 | 7.23 |  |  |  | 7.23
WOODLAND 1102 | 62031102 | 13.61 |  |  |  | 13.61
WOODLAND 1103 | 62031103 | 1.23 |  |  |  | 1.23
WOODLAND 1104 | 62031104 | 5.95 |  |  |  | 5.95
WOODLAND 1105 | 62031105 | 2.64 |  |  |  | 2.64
WOODLAND 1106 | 62031106 | 28.06 |  |  |  | 28.06
WOODLAND 1107 | 62031107 | 11.23 |  |  |  | 11.23
WOODLAND 1108 | 62031108 | 21.29 |  |  |  | 21.29
WOODLAND 1109 | 62031109 | 10.78 |  |  |  | 10.78
WOODLAND 1110 | 62031110 | 10.95 |  |  |  | 10.95
WOODLAND 1111 | 62031111 | 0.26 |  |  |  | 0.26
WOODLAND 1112 | 62031112 | 12.89 |  |  |  | 12.89
WOODLAND 1113 | 62031113 | 20.95 |  |  |  | 20.95
WOODSIDE 1101 | 24251101 | 61.92 | 42.67 | 0.5 |  | 18.75
WOODSIDE 1102 | 24251102 | 17.09 |  | 0.06 |  | 17.03
WOODSIDE 1104 | 24251104 | 44.02 | 7.16 | 13.02 |  | 23.84
WOODSIDE 1105 | 24251105 | 6.22 |  |  |  | 6.22
WOODWARD 2101 | 255292101 | 25.85 |  |  |  | 25.85
WOODWARD 2102 | 255292102 | 1.41 |  |  |  | 1.41
WOODWARD 2104 | 255292104 | 3.61 |  |  |  | 3.61
WOODWARD 2105 | 255292105 | 0.36 |  |  |  | 0.36
WOODWARD 2106 | 255292106 | 0.26 |  |  |  | 0.26
WOODWARD 2107 | 255292107 | 8.87 |  |  |  | 8.87
WOODWARD 2108 | 255292108 | 91.92 |  | 18.51 |  | 73.41
WOODWARD 2109 | 255292109 | 1.82 |  |  |  | 1.82
WRIGHT 1110 | 254641110 | 87.67 |  |  |  | 87.67
WYANDOTTE 1102 | 102911102 | 40.63 |  | 4.33 |  | 36.3
WYANDOTTE 1103 | 102911103 | 68.12 | 38.52 | 16.13 |  | 13.47
WYANDOTTE 1105 | 102911105 | 37.22 | 0.68 | 25.29 |  | 11.25
WYANDOTTE 1106 | 102911106 | 94.45 |  | 0.55 |  | 93.9
WYANDOTTE 1107 | 102911107 | 155.32 | 9.93 | 101.73 |  | 43.66
WYANDOTTE 1109 | 102911109 | 117.25 |  | 51.68 |  | 65.57
WYANDOTTE 1110 | 102911110 | 35.42 |  | 8.88 |  | 26.54
YOSEMITE 0401 | 22490401 | 3.56 |  |  |  | 3.56
YOSEMITE 0402 | 22490402 | 2.41 |  |  |  | 2.41
YOSEMITE 0403 | 22490403 | 0 |  |  |  | 0
ZACA 1101 | 182681101 | 26.16 | 1.27 | 16.64 |  | 8.25
ZACA 1102 | 182681102 | 80.42 | 22.36 | 40.69 |  | 17.37
ZAMORA 1105 | 63191105 | 45.69 |  |  |  | 45.69
ZAMORA 1106 | 63191106 | 52.99 |  |  |  | 52.99
ZAMORA 1107 | 63191107 | 76.99 |  |  |  | 76.99
|  | 80312.87 | 6875.14 | 18003.03 | 14.64 | 55420.06
|  |  | HFTD Mileage | 24878.17