## ET-WD Details
kV Cls | kV | SAP FL | LINE NO | FACILITY NAME | YEAR | Date Out | Time Out | MED | ET Wire Down | Auto Reclose Disabled | Durn (hr:min) | Durn (mins) | Date In | Time In | Out Cls | Cause Category | Cause Detail | Secondary Cause | Comments | CAP | REGION | TOTL | Customers Affected | CESO Event | CMIN Event | SAIFI Contr | SAIDI Contr | CAIDI | System Customer Count | Fault Type | Fault Estimate | AUTO EFO SCHD | Outage Mode | HFTD | County | Division | LAT | LONG | Actual Location | Weather | Conductor | ETGIS Location | BS GS SD
115 | 115 | ETL.2400 | 10166 | MELONES-RACETRACK | 2024 | 2024-01-10 22:22 | 45301.9319 | No | YES | No | 1900-01-03 16:15 | 6735 | 2024-01-15 14:37 | 45306.609 | C | Equipment Failure | Equip Fail-structure-line | NONE | Relayed - 1/10/24, 2222 Melones-Racetrack 115kV line relayed and tested NG. Sustained interruption to Racetrack. Weather storm. Estimated return 01/11/24. 1/11/24, 0024 Melones-Racetrack 115kV line (Melones to Racetrack SW 125 section) tested NG. 0040 Racetrack restored from alternate source. 0813 Melones SW STA to Racetrack SW 125 section cleared for crew to replace NG poles 007/016 and 007/017 damaged by storm. Estimated return 10/13/23. From trouble on 01/10/24 at 2222. 1/15/24, 1437 Melones-Racetrack 115kV line returned to service normal after crews replaced downed poles 7/16 and 7/17. From trouble on 01/10/24 at 2222. ET-WD | NONE | CENTRAL VALLEY | INT-17835 | 3802 | 3802 | 597443 | 0.00066112 | 0.10389 | 157.1391 | 5750834 | A-B-C | 007/001 | AUTO | Single Mode | Tier 2 | Tuolumne | Yosemite | 37.971 | -120.4454 | Melones-Racetrack 115kV line STR 007/016 | Storm | 397.5 AAC | Lat: 37.97105, Long: -120.44539 | SD
69 | 70 | ETL.8720 | 70031 | GUERNSEY-HENRIETTA | 2024 | 2024-01-28 01:06 | 45319.0458 | No | YES | No | 0.90764 | 1307 | 2024-01-28 22:53 | 45319.9535 | F | External Contact | Ext Cont-car pole | COND | Relayed - 1/28/24, 0106 Guernsey-Henrietta 70kV line relayed and tested NG. Sustained interruption to Jacobs Corner and Kansas South Solar (offline). Momentary interruption to Guernsey, Guernsey Solar STA (offline), Faraday Future and Reserve Oil. Weather clear. 0117 Guernsey to Kansas South JCT section manually tested NG. 0207 Jacobs Corner JCT to Henrietta section manually tested OK, restoring Jacobs Corner and Kansas South Solar. 2101 Guernsey-Henrietta 70kV line (Guernsey to Jacobs Corner JCT) returned to service after crew replaced structure 018/007B and repaired 2 spans of down wire. 2253 Line returned normal. ET-WD | NONE | CENTRAL VALLEY | INT-17862 | 1710 | 1690 | 131650 | 0.00029387 | 0.022892 | 77.8994 | 5750834 | N/A | Electromechanical | AUTO | Single Mode | Non-HFTD | Kings | Fresno | 36.2682 | -119.6549 | Guernsey-Henrietta 70kV line STR ;018/007 | Clear | 3/0 CU | Lat: 36.26822, Long: -119.65494 | BS
69 | 60 | ETL.6980 | 60430 | FORT ROSS-GUALALA | 2024 | 2024-01-31 11:45 | 45322.4896 | No | YES | No | 1900-01-01 06:28 | 3268 | 2024-02-02 18:13 | 45324.759 | F | Tree | Tree-failure | COND | Relayed - 1/31/24, 1145 Fort Ross-Gualala 60kV line relayed and tested NG. Momentary interruption to Gualala. Sustained interruption to Annapolis. Weather rain. 1450 Reports of 3-phase wire down and tree in the line at pole 048/002 between Gualala to Annapolis section. 1628 Reports of 1-phase wire down between poles 039/011 to 039/012 between Annapolis to Fort Ross section. Estimated return 02/01/24 at 1800. 1941 Fort Ross-Gualala 60kV line, (Annapolis to Gualala section) returned to service after crew repaired three phases of downed conductor at pole 048/002. Estimated return of 02/02/24 for Fort Ross-Gualala 60kV line (Fort Ross to Annapolis section). 1813 Fort Ross-Gualala 60kV line (Fort Ross to Annapolis section) returned to service after crew repaired one phase of downed conductor between poles 039/011 and 039/012. ET-WD | NONE | NORTH COAST | INT-17883 | 229 | 229 | 468600 | 3.982e-05 | 0.081484 | 2046.2882 | 5750834 | A-B | 048/009 | AUTO | Single Mode | Tier 2 | Sonoma | Humboldt | 38.7188 | -123.38 | Fort Ross-Gualala 60kV line STR 048/002 | Rain | 4/0 AAC | Lat: 38.7188, Long: -123.38001 | SD
69 | 60 | ETL.6979 | 60429 | MONTE RIO-FORT ROSS | 2024 | 2024-02-04 00:05 | 45326.0035 | YES | YES | No | 0.05 | 72 | 2024-02-04 01:17 | 45326.0535 | F | Equipment Failure | Equip Fail-structure-line | NONE | Relayed - 2/4/24, 0005 Monte Rio-Fort Ross 60kV line relayed and tested NG. On the trouble the Fort Ross-Gualala 60kV line de-energized. Sustained interruption to Salmon Creek, Fort Ross, Annapolis and Gualala. Weather is rain. 0018 Gualala restored via alternate source. 0019 Fort Ross-Gualala 60kV line energized, restoring Annapolis. 0020 Fort Ross restored. 0033 Monte Rio to Salmon Creek section tested NG. 0055 Salmon Creek 60kV Tap isolated. Patrol of Salmon 60kV tap found NG broken pole 2/7. 0109 Monte Rio to Salmon Creek JCT section manually tested OK. 0112 Salmon Creek JCT to Fort Ross section manually tested OK. 0117 Monte Rio to Fort Ross path restored. No estimated return. ET-WD | NONE | NORTH COAST | INT-17902-1 | 5889 | 5889 | 3708687 | 0.001024 | 0.6449 | 629.7652 | 5750834 | A-C | 024/003 | AUTO | Dependent Mode Initiating | Non-HFTD | Sonoma | Sonoma | 38.443 | -123.107 | Salmon Creek 60kV Tap STR 002/007 | Storm | 4/0 AAC | Lat: 38.44296, Long: -123.107 | SD
69 | 60 | ETL.6980 | 60430 | FORT ROSS-GUALALA | 2024 | 2024-02-04 04:57 | 45326.2063 | YES | YES | No | 1900-01-07 13:46 | 12346 | 2024-02-12 18:43 | 45334.7799 | C | Tree | Tree-failure | COND | Relayed - 2/4/24, 0457 Fort Ross-Gualala 60kV line relayed and tested NG. Momentary interruption to Gualala. Sustained interruption to Annapolis. Weather storm. 0633 Fort Ross to Annapolis section tested NG. 0636 Gualala to Annapolis section tested OK restoring Annapolis. 1030 Fort Ross to Annapolis section cleared for crews to repair 3 phases of downed conductor at pole 41/05. No estimated return. 2/7/24, 2008 Elk-Gualala 60kV line de-energized to operate Gualala switch 57 dead. 2008 Elk-Gualala 60kV line energized and Fort Ross-Gualala 60kV line (Gualala to Annapolis section) returned to service after crew removed trees from structure 046/009, 048/005, replumed structure 047/001, repaired down conductor at structure 047/000, 047/001, 047/002 and replaced structure 047/001. Momentary interruption to Point Arena and Gualala, and restoring Annapolis. From trouble on 02/04/24 at 0457. 2/12/24, 1843 Fort Ross-Gualala 60kV line (Fort Ross to Annapolis section) returned to service after crews replaced structures 033/009, 039/009, 039/010, 039/011, 039/12, 040/000, 041/001, repaired down wire at structures 030/010, 033/012, 035/004, 041/005, 041/007 and removed tree from line at 030/005. From trouble on 02/04/24 at 0457. ET-WD | NONE | NORTH COAST | INT-17905 | 229 | 229 | 22671 | 3.982e-05 | 0.0039422 | 99 | 5750834 | A-B-C | 041/009 | AUTO | Single Mode | Tier 2 | Sonoma | Humboldt | 38.6613 | -123.309 | Fort Ross-Gualala 60kV line STR 041/005 | Storm | 4/0 AAC | Lat: 38.6613, Long: -123.309 | SD
69 | 70 | ETL.8880 | 70048 | KERN-MAGUNDEN | 2024 | 2024-02-04 08:54 | 45326.3708 | YES | YES | No | 1900-01-01 12:30 | 3630 | 2024-02-06 21:24 | 45328.8917 | F | Equipment Failure | Equip Fail-structure-line | NONE | Relayed - 2/4/24, 0854 Kern-Magunden 70kV line relayed and tested NG. Sustained interruption to Golden State Metals. Weather storm. 1252 Kern to Golden State Metals JCT section energized, restoring Golden State Metals. 1252 Golden State Metals JCT to Magunden section cleared for crews to repair multiple broken poles between 12/162 and 12/169. No estimated return. 2/6/24, 2124 Kern-Magunden 70kV line (Bakersfield JCT to Magunden section) returned to service after crew repaired down conductor and replaced structures at 012/161, 012/162, 012/164, 012/165, 012/166, 012/167, 012/168 and reframed cross arms on structures 012/163 and 012/169. From trouble on 02/04/24 at 0854. ET-WD | 128167034 | CENTRAL VALLEY | INT-17913 | 1 | 1 | 238 | 1.7389e-07 | 4.1385e-05 | 238 | 5750834 | A-B-C | 012/164 | AUTO | Single Mode | Non-HFTD | Kern | Kern | 35.3824 | -118.923 | Kern-Magunden 70kV line STR 012/162 | Storm | 3/0 CU | Lat: 35.38244, Long: -118.923 | SD
69 | 60 | ETL.7550 | 60151 | MENDOCINO-WILLITS-FORT BRAGG | 2024 | 2024-02-04 09:33 | 45326.3979 | YES | YES | No | 1899-12-31 03:36 | 1656 | 2024-02-05 13:09 | 45327.5479 | F | Tree | Tree-failure | COND | Relayed - 2/4/24, 0933 Mendocino-Willits-Fort Bragg 60kV line relayed and tested NG. No customer interruption. Weather storm. 0939 Mendocino-Willits JCT section tested OK. 1729 Fort Bragg to Willits JCT section cleared for crews to repair one phase of down conductor at structure 034/003. No estimated return. 2/5/24, 1309 Mendocino-Willits-Fort Bragg 60kV line (Fort Bragg to Willits JCT section) returned to service restoring transmission service to Fort Bragg after crew repaired one phase of downed conductor at pole 034/003 due to tree contact. From trouble on 02/04/24 at 0929. ET-WD | NONE | NORTH COAST | INT-17915 | 0 | 0 | 0 | 0 | 0 | 0 | 5750834 | A-C | 034/009 | AUTO | Single Mode | Tier 2 | Mendocino | Humboldt | 39.3669 | -123.677 | Mendocino-Willits-Fort Bragg 60kV line STR 034/003 | Storm | 397.5 AAC | Lat: 39.36692, Long: -123.677 | SD
69 | 60 | ETL.6220 | 60010 | BRIDGEVILLE-GARBERVILLE | 2024 | 2024-02-04 09:50 | 45326.4097 | YES | YES | No | 0.53194 | 766 | 2024-02-04 22:36 | 45326.9417 | F | Tree | Tree-failure | COND | Relayed - 2/4/24, 0950 Bridgeville-Garberville 60kV line relayed and tested NG. Sustained interruption to Fruitland and Fort Seward. Weather storm. 0954 Fruitland JCT to Garberville section manually tested OK, restoring Fruitland and Fort Seward. 1423 to 2236 Bridgeville to Fruitland JCT section cleared for crew to remove tree and repair down conductor between poles 4/12 and 4/13. Line returned to service normal. ET-WD | NONE | NORTH COAST | INT-17919 | 1437 | 1437 | 5748 | 0.00024988 | 0.00099951 | 4 | 5750834 | B-C | 004/011 | AUTO | Single Mode | Tier 3 | Humboldt | Humboldt | 40.4356 | -123.767 | Bridgeville-Garberville 60kV line STR 004/012 | Storm | 4/0 AAC | Lat: 40.43557, Long: -123.767 | SD
69 | 60 | ETL.8410 | 60244 | ELK-GUALALA | 2024 | 2024-02-04 09:55 | 45326.4132 | YES | YES | No | 1899-12-31 09:58 | 2038 | 2024-02-05 19:53 | 45327.8285 | F | Tree | Tree-failure | COND | Relayed - 2/4/24, 0955 Elk-Gualala 60kV line relayed and tested NG. Sustained interruption to Point Arena, Gualala and Annapolis. 1009 Line manually tested NG. Line patrol found 3 phases of down conductor between 48/7 and 48/8. No estimated return. 2/5/24, 1953 Elk-Gualala 60kV returned to service restoring Point Arena and Gualala following conductor repair between structures 48/8 and 48/7. From trouble on 02/04/24 at 0955. ET-WD | NONE | NORTH COAST | INT-17918 | 761 | 761 | 1550918 | 0.00013233 | 0.26969 | 2038 | 5750834 | A-C | 048/006 | AUTO | Single Mode | Non-HFTD | Mendocino | Humboldt | 38.9763 | -123.68 | Elk-Gualala 60kV line STR 048/007 | Storm | 397.5 AAC | Lat: 38.97632, Long: -123.68 | SD
69 | 70 | ETL.8970 | 70115 | COPUS-OLD RIVER | 2024 | 2024-02-04 10:11 | 45326.4243 | YES | YES | No | 0.5 | 720 | 2024-02-04 22:11 | 45326.9243 | F | Equipment Failure | Equip Fail-conductor | NONE | Relayed - 2/4/24, 1011 Copus-Old River 70kV line open-ended at Old River. Old River CB 12 tripped, reclosed by automatics and tripped open. No customer interruption. Weather storm. 1208 Copus-Old River 70kV line forced out of service due to down conductor at structure 18/301. Sustained interruption to South Kern Solar. 1251 Copus to San Emidio JCT section energized, restoring South Kern Solar. 2011 Old River to San Emidio JCT section returned to service after single phase conductor repaired at 018/301. Line returned normal. ET-WD | 128167663 | CENTRAL VALLEY | INT-17921 | 0 | 0 | 0 | 0 | 0 | 0 | 5750834 | B-G | 018/302 | AUTO | Single Mode | Non-HFTD | Kern | Kern | 35.1129 | -119.11 | Copus-Old River 70kV line STR 018/301 | Storm | 3/0 AAC | Lat: 35.11292, Long: -119.11 | SD
69 | 70 | ETL.9300 | 70090 | WHEELER RIDGE-SAN BERNARD | 2024 | 2024-02-04 12:56 | 45326.5389 | YES | YES | No | 1900-01-03 05:54 | 6114 | 2024-02-08 18:50 | 45330.7847 | C | Equipment Failure | Equip Fail-structure-line | STRU | Relayed - 2/4/24, 1256 Wheeler Ridge-San Bernard 70kV line relayed and tested NG. No customer interruption. Weather storm. Patrol reports Wheeler-Ridge San Bernard has 14 poles down. 4/55 to 5/68. Estimating has been contacted. 2/8/24, 1850 Wheeler Ridge-San Bernard 70kV line returned to service after crews replaced down poles 004/055, 004/056, 004/057, 004/058, 004/059, 004/060, 004/061, 005/063, 005/064, 005/065, 005/066, 005/067 and 005/068. From trouble on 02/04/24 at 1256. ET-WD | 128168988 | CENTRAL VALLEY | INT-17936 | 0 | 0 | 0 | 0 | 0 | 0 | 5750834 | A-B-C | 004/052 | AUTO | Single Mode | Non-HFTD | Kern | Kern | 35.0891 | -118.899 | Wheeler Ridge-San Bernard 70kV line STRs 004/055-005/068 | Storm | 397.5 ACSR | Lat: 35.08907, Long: -118.899 | SD
69 | 60 | ETL.7212 | 60424 | SNEATH LANE-HALF MOON BAY | 2024 | 2024-02-04 14:40 | 45326.6111 | YES | YES | No | 1900-01-04 02:57 | 7377 | 2024-02-09 17:37 | 45331.734 | C | Equipment Failure | Equip Fail-structure-line | NONE | Relayed - 2/4/24, 1440 Sneath Lane-Half Moon Bay 60kV line relayed and tested NG. No customer interruption. Weather storm. 1615 Sneath Lane to Pacifica section manually tested OK, restoring Pacifica. No estimated return. 2/6/24, Line patrol of the Sneath Lane-Half Moon Bay 60kV line found broken pole ?004/003. 1239 Sneath Lane-Half Moon Bay 60kV line (Sneath Lane to Pacifica section) manually tested OK, restoring alternate source to Pacifica. From trouble on 02/04/24 at 1440. 2/9/24, 1737 Sneath Lane-Half Moon Bay 60kV line (Pacifica to Half Moon Bay section) returned to service after crews replaced pole ?004/003. From trouble on 02/04/24 at 1440. ET-WD | NONE | BAY AREA | INT-17950 | 0 | 0 | 0 | 0 | 0 | 0 | 5750834 | A-C | ?006/008 | AUTO | Single Mode | Tier 3 | San Mateo | Peninsula | 37.5509 | -122.47 | Sneath Lane-Half Moon Bay 60kV line STR ?004/003 | Storm | 397.5 AAC | Lat: 37.55094, Long: -122.47 | SD
69 | 60 | ETL.7180 | 60113 | IGNACIO-BOLINAS #2 | 2024 | 2024-02-04 14:45 | 45326.6146 | YES | YES | No | 1900-01-03 22:46 | 7126 | 2024-02-09 13:31 | 45331.5632 | C | Tree | Tree-failure | COND | Relayed - 2/4/24, 1445 Ignacio-Bolinas #2-60kV line relayed and tested OK. Bolinas to Olema section tested NG. Momentary interruption to Olema and Tocaloma. Weather storm. No estimated return. T-Line patrol of the Ignacio-Bolinas #2-60kV line (Bolinas to Olema section) found all 3 phases of both transmission and distribution wire down between structures 023/265 and 023/266. 2/9/24, 1331 Ignacio-Bolinas #2-60kV line (Bolinas to Olema section) returned to service, after crew repaired 2 phases of downed conductor between structures 023/265 and 023/266 and also between 019/224 and 019/223, damaged by storm. From trouble 02/04/24 at 1445. ET-WD | NONE | NORTH COAST | INT-17951 | 2221 | 0 | 0 | 0 | 0 | 0 | 5750834 | A-B-C | 024/270 | AUTO | Single Mode | Tier 3 | Marin | North Bay | 37.9748 | -122.727 | Ignacio-Bolinas #2-60kV line STR 023/265 | Storm | 1/0 CU | Lat: 37.97479, Long: -122.727 | SD
69 | 60 | ETL.6240 | 60012 | BURNS-LONE STAR #2 | 2024 | 2024-02-04 14:56 | 45326.6222 | YES | YES | YES | 1900-01-02 07:39 | 4779 | 2024-02-07 22:35 | 45329.941 | C | Tree | Tree-failure | NONE | Relayed - 2/4/24, 1456 Burns-Lonestar #2-60kV line relayed and did not test. Sustained interruption to Point Moretti, Crusher, and CEMEX. Weather storm. No estimated return. Line patrol found tree on all three phases of conductor between structures 0/11 and 0/12. 2/7/24, 2235 Burns Lone Star #2-60kV line returned to service, restoring Crusher, Point Moretti and CEMEX. From trouble on 02/04/24 at 1456. ET-WD | NONE | SOUTH BAY AND CENTRAL COAST | INT-17953 | 816 | 816 | 3899664 | 0.00014189 | 0.6781 | 4779 | 5750834 | A-B-C | 000/014 | AUTO | Single Mode | Tier 3 | Santa Cruz | Central Coast | 37.0884 | -122.142 | Burns-Lone Star #2-60kV line STR 000/011 | Storm | 3/0 CU | Lat: 37.08842, Long: -122.142 | SD
69 | 60 | ETL.8010 | 60201 | SOLEDAD #1 | 2024 | 2024-02-04 15:59 | 45326.666 | YES | YES | No | 1899-12-31 04:04 | 1684 | 2024-02-05 20:03 | 45327.8354 | F | Equipment Failure | Equip Fail-structure-line | NONE | Relayed - 2/4/24, 1559 Soledad #1 60kV Line relayed and tested NG. Sustained Interruption to Gonzales. Weather storm. 2/5/24, 2003 Soledad #1-60kV line returned to service following cross arm repair on structures 012/237 and 012/239. From trouble on 02/04/24 at 1559. ET-WD | NONE | SOUTH BAY AND CENTRAL COAST | INT-17965 | 2620 | 2620 | 331564 | 0.00045559 | 0.057655 | 126.5511 | 5750834 | A-G | 012/235 | AUTO | Single Mode | Non-HFTD | Monterey | Central Coast | 36.55 | -121.499 | Soledad #1 60kV Line STR 012/238 | Storm | 4/0 AAC | Lat: 36.54995, Long: -121.499 | SD
69 | 60 | ETL.7590 | 60156 | MONTA VISTA-BURNS | 2024 | 2024-02-04 16:06 | 45326.6708 | YES | YES | No | 1900-01-02 06:11 | 4691 | 2024-02-07 22:17 | 45329.9285 | C | Tree | Tree-failure | COND | Relayed - 2/4/24, 1606 Monta Vista-Burns 60kV line relayed and tested NG. On the trouble Burns 60kV bus and Burns-Lonestar #1-60kV line de-energized. Sustained interruption to Burns. Weather storm. No estimated return. Air patrol found two spans of wire down and NG pole at 11/91. 2/7/24, 2217 Monta Vista-Burns 60kV line returned to service after crew replaced NG structure 011/091. Restoring Big Basin and Burns. 2236 Burns Lone Star #1-60kV line returned to service. From trouble on 02/04/24 at 1606. ET-WD | NONE | SOUTH BAY AND CENTRAL COAST | INT-17967-1 | 156 | 156 | 738972 | 2.7127e-05 | 0.1285 | 4737 | 5750834 | B-C-G | 012/102 | AUTO | Dependent Mode Initiating | Tier 3 | Santa Cruz | Central Coast | 37.172 | -122.165 | Monta Vista-Burns 60kV line STR 011/091 | Storm | 397.5 AAC | Lat: 37.17205, Long: -122.165 | SD
69 | 60 | ETL.6910 | 60085 | FULTON-MOLINO-COTATI | 2024 | 2024-02-04 16:17 | 45326.6785 | YES | YES | No | 1900-01-01 04:25 | 3145 | 2024-02-06 20:42 | 45328.8625 | F | Tree | Tree-failure | STRU | Relayed - 2/4/24, 1617 Fulton-Molino-Cotati 60kV line relayed and tested NG. Momentary interruption to Molino. Sustained interruption to Laguna, Sonoma County Landfill, and Cotati. Weather storm. 1631 Cotati restored. 2/5/24, 1429 Fulton to Laguna JCT section energized, restoring Laguna and transmission service to Molino. Laguna JCT to Cotati section to be cleared, for crew to repair downed conductor at structure 16/304. From trouble 0n 02/04/24 at 1617. 2/6/24, 2042 Fulton-Molino-Cotati 60kV line (Laguna to Cotati section) returned to service after crews replaced pole 016/303 and repaired down conductor at 016/303, 016/304 and 016/305, restoring Sonoma County Land Fill. From trouble on 02/04/24 at 1617. Veg management confirmed tree contact. ET-WD | NONE | NORTH COAST | INT-17972 | 29764 | 12293 | 16374276 | 0.0021376 | 2.8473 | 1332 | 5750834 | A-B | 016/310 | AUTO | Single Mode | Tier 2 | Sonoma | Sonoma | 38.3122 | -122.736 | Fulton-Molino-Cotati 60kV line STR 016/304 | Storm | 715 AAC | Lat: 38.31224, Long: -122.736 | SD
69 | 60 | ETL.6170 | 60397 | DEL MAR-ATLANTIC #2 | 2024 | 2024-02-04 16:26 | 45326.6847 | YES | YES | No | 1900-01-23 17:48 | 35628 | 2024-02-29 10:14 | 45351.4264 | C | Equipment Failure | Equip Fail-structure-line | NONE | Relayed - 2/4/24, 1626 Del Mar-Atlantic #2-60kV line relayed and tested NG. Sustained interruption to Kinder Morgan and Rocklin. Weather storm. No estimated return. 2/5/24, 0654 Del Mar-Atlantic #2-60kV line (Del Mar to Kinder Morgan JCT section) energized, restoring transmission to Kinder Morgan and Rocklin. Kinder Morgan JCT to Atlantic section is cleared for repairs, estimated time of return is 02/08 at 1800. From trouble on 02/04/24 at 1626. 2/5/24, 0654 Del Mar-Atlantic #2-60kV line (Del Mar to Kinder Morgan JCT section) energized, restoring transmission to Kinder Morgan and Rocklin. Kinder Morgan JCT to Atlantic section is cleared for repairs, estimated time of return is 02/08 at 1800. From trouble on 02/04/24 at 1626. 2/29/24, 1014 Del Mar-Atlantic #2-60kV line (Kinder Morgan JCT to Atlantic section) returned to service after crews replaced poles 002/076, 002/078, 003/079, 003/080, 003/081, 003/082, 003/083, 003/084, 003/085, 003/086, guy pole 003/084 and replaced conductor between structures 002/077 and 002/078. From trouble on 02/04/24 at 1626. ET-WD | NONE | NORTH VALLEY AND SIERRA | INT-17973 | 4609 | 4609 | 4000612 | 0.00080145 | 0.69566 | 868 | 5750834 | A-B-C | 003/085 | AUTO | Single Mode | Non-HFTD | Placer | Sierra | 38.7733 | -121.25 | Del Mar-Atlantic #2 60kV line STR 002/076 | Storm | 715 AAC | Lat: 38.77327, Long: -121.25 | SD
69 | 60 | ETL.7770 | 60176 | PEASE-MARYSVILLE-HARTER | 2024 | 2024-02-04 18:55 | 45326.7882 | YES | YES | No | 1900-01-03 03:14 | 5954 | 2024-02-08 22:09 | 45330.9229 | C | Equipment Failure | Equip Fail-structure-line | NONE | Relayed - 2/4/24, 1855 Pease-Marysville-Harter 60kV line relayed and tested NG. Sustained interruption to Harter, Yuba City Cogen (offline) and YCEC (offline). Weather storm. 2034 Harter restored via alternate source. No estimated return. 2/5/24, 1605 Pease-Marysville-Harter 60kV line (Harter to Yuba City Co-gen section returned to service restoring transmission service to YCEC (offline) and Yuba City Cogen (offline) after full patrol of line section complete with no trouble found. From trouble on 02/04/24 at 1855.Estimated return of 02/09/24 for Pease-Marysville section. Multiple structures broken and condcutor down on Pease-Marysville Section 005/106-005/111. 2/8/24, 2209 Pease-Marysville-Harter 60kV line returned to service after crews replaced NG structures 005/105, 005/106, 005/107, 005/108, 005/109, 005/110 and 005/111. From trouble on 02/04/24 at 1855. ET-WD | NONE | NORTH VALLEY AND SIERRA | INT-17997 | 7666 | 7666 | 758934 | 0.001333 | 0.13197 | 99 | 5750834 | A-B-C | 001/035 | AUTO | Single Mode | Non-HFTD | Yuba | Sierra | 39.1653 | -121.564 | Pease-Marysville-Harter 60kV line STR 005/106 | Storm | 477 ACSS | Lat: 39.16526, Long: -121.564 | SD
69 | 60 | ETL.2060 | 60389 | FORT BRAGG-ELK | 2024 | 2024-02-04 19:12 | 45326.8 | YES | YES | No | 0.077083 | 111 | 2024-02-04 21:03 | 45326.8771 | F | Tree | Tree-failure | COND | Relayed - 2/4/24, 1912 Fort Bragg-Elk 60kV line relayed and tested NG. On the trouble Big River SVC tripped. Sustained interruption to Big River and Fort Bragg STA “A”. Weather storm. 2103 Big River to Elk section manually tested OK and returned to service restoring transmission to Big River. 2/6/24, 1447 Fort Bragg-Elk 60kV line (Fort Bragg to Big River section) returned to service after crews replaced pole 21/9, re-framed pole 21/8 and repaired three phases of downed conductor between poles 21/8 and 21/9. Momentary interruption to Big River (2,628) and Big River SVC. From trouble on 02/04/24 at 1912. ET-WD | NONE | NORTH COAST | INT-18001 | 11176 | 11176 | 1240536 | 0.0019434 | 0.21571 | 111 | 5750834 | A-B-C | 022/008 | AUTO | Single Mode | Tier 2 | Mendocino | Humboldt | 39.3996 | -123.801 | Fort Bragg-Elk 60kV Line STR 021/008 | Storm | 397.5 AAC | Lat: 39.39958, Long: -123.801 | SD
69 | 60 | ETL.6930 | 60088 | GLENN #2 | 2024 | 2024-02-04 19:13 | 45326.8007 | YES | YES | No | 0.030556 | 44 | 2024-02-04 19:57 | 45326.8313 | F | Equipment Failure | Equip Fail-conductor | NONE | Relayed - 2/4/24, 1913 Glenn #2-60kV line relayed and tested NG. Sustained interruption to Hamilton "A" and Jacinto. Weather storm. 1923 Glenn to Hamilton “A” line section manually tested OK, restoring Hamiton “A”. 2144 Hamilton “A” to Jacinto line section manually tested OK, restoring Jacinto. No estimated return. Line patrol of the Glenn #2-60kV line (Jacinto to Rice section) found one phase of down conductor between structures 034/656 and 034/657. 2/5/24, 1957 Glenn #2-60kV line (Jacinto to Rice section) returned to service after crew repaired 1 phase of down conductor between structures 034/656 and 034/657. From trouble 02/04/24 at 1913. ET-WD | NONE | NORTH VALLEY AND SIERRA | INT-18000 | 2120 | 2120 | 93280 | 0.00036864 | 0.01622 | 44 | 5750834 | A-B-G | 034/652 | AUTO | Single Mode | Non-HFTD | Colusa | Sacramento | 39.4079 | -122.012 | Glenn #2-60kV line STR 034/656 | Storm | 715 AAC | Lat: 39.40795, Long: -122.012 | SD
69 | 60 | ETL.7980 | 60198 | SMARTVILLE-MARYSVILLE | 2024 | 2024-02-04 19:16 | 45326.8028 | YES | YES | YES | 1899-12-31 23:51 | 2871 | 2024-02-06 19:07 | 45328.7965 | F | Equipment Failure | Equip Fail-structure-line | NONE | Relayed - 2/4/24, 1916 Smartville-Marysville 60kV line relayed and did not test. Sustained interruption to Yuba and Browns Valley. 1924 Smartville to Browns Valley section tested OK, restoring Yuba. 1925 Browns Valley restored. No estimated return. Patrol of Browns Valley to Marysville section found poles and conductor down at 18/367, 18/368, 18/369 & 18/370. 2/6/24, 1907 Smartville-Marysville 60kV line (Browns Valley to Marysville section) returned to service after crew repaired/replaced poles 018/367, 018/368, 018/369 & 018/370 including downed conductors. From trouble on 02/04/24 at 1916. ET-WD | NONE | NORTH VALLEY AND SIERRA | INT-18004 | 615 | 615 | 5535 | 0.00010694 | 0.00096247 | 9 | 5750834 | A-C-G | 019/386 | AUTO | Single Mode | Non-HFTD | Yuba | Sierra | 39.1566 | -121.566 | Smartville-Marysville 60kV line STR 018/367 | Storm | 266.8 AAC | Lat: 39.15664, Long: -121.566 | SD
115 | 115 | ETL.1190 | 10026 | BUTTE-SYCAMORE CREEK | 2024 | 2024-02-04 19:42 | 45326.8208 | YES | YES | No | 0.69583 | 1002 | 2024-02-05 12:24 | 45327.5167 | F | Tree | Tree-failure | COND | Relayed - 2/4/24, 1942 Butte-Sycamore Creek 115kV line relayed and tested NG. Sustained interruption to Nord. Weather storm. 2/5/24, 1224 Butte-Sycamore Creek 115kV line returned to service normal, after crew replaced downed conductor between structures 15/314 & 15/315. From trouble on 02/04/24 at 1942. ET-WD | NONE | NORTH VALLEY AND SIERRA | INT-18007 | 8233 | 8233 | 8249466 | 0.0014316 | 1.4345 | 1002 | 5750834 | C-G | 015/309 | AUTO | Single Mode | Non-HFTD | Butte | North Valley | 39.7737 | -121.848 | Butte-Sycamore Creek 115kV line STR 015/314 | Storm | 715 AAC | Lat: 39.77367, Long: -121.848 | SD
115 | 115 | ETL.4396 | 10399 | PARADISE-BUTTE | 2024 | 2024-02-04 19:59 | 45326.8326 | YES | YES | No | 1899-12-31 00:46 | 1486 | 2024-02-05 20:45 | 45327.8646 | F | Tree | Tree-failure | HDWR | Relayed - 2/4/24, 1959 Paradise-Butte 115kV line relayed and tested NG. Weather storm. Initial patrol found 3 phases of wire down on the Paradise-Butte 115kV line, 1 phase of wire down on the Paradise-Table Mountain 115kV line both between shared structures 002/025 and 002/026, along with damaged insulators and bent brackets at structures 001/023, 001/024 and 002/025. 2/5/24, 2045 Paradise-Butte 115kV line returned to service after crew repaired multiple phases of wire down one phase of wire down between structures 2/25 and 2/26, restoring transmission service to Paradise. From trouble on 02/04/24 at 1959. ET-WD | NONE | NORTH VALLEY AND SIERRA | INT-18008 | 0 | 0 | 0 | 0 | 0 | 0 | 5750834 | A-G | 002/034 | AUTO | Single Mode | Tier 2 | Butte | North Valley | 39.7462 | -121.644 | Paradise-Butte 115kV line STR 002/025 | Storm | 715 AAC | Lat: 39.74615, Long: -121.644 | SD
115 | 115 | ETL.4316 | 10400 | PARADISE-TABLE MTN | 2024 | 2024-02-04 19:59 | 45326.8326 | YES | YES | YES | 1899-12-31 00:57 | 1497 | 2024-02-05 20:56 | 45327.8722 | F | Tree | Tree-failure | HDWR | Relayed - 2/4/24, 1959 Paradise-Table Mountain 115kV line relayed and did not test. 2006 Paradise-Table Mountain 115kV line manually tested NG. Sustained interruption to Paradise. Weather storm. 2/5/24, 0014 Paradise-Table Mountain 115kV line (Table Mountain to Big Bend to Wyandotte section) energized, restoring alternate source to Wyandotte. From trouble on 02/04/24 at 2006. Initial patrol found 3 phases of wire down on the Paradise-Butte 115kV line, 1 phase of wire down on the Paradise-Table Mountain 115kV line both between shared structures 002/025 and 002/026, along with damaged insulators and bent brackets at structures 001/023, 001/024 and 002/025. 2/5/24, 2056 Paradise-Table Mountain 115kV line returned to service after crew repaired multiple phases of wire down phase of wire down between structures 2/25 and 2/26. From trouble on 02/04/24 at 1959. ET-WD | NONE | NORTH VALLEY AND SIERRA | INT-18011 | 7496 | 7496 | 11221512 | 0.0013035 | 1.9513 | 1497 | 5750834 | A-B-C | 000/003 | AUTO | Single Mode | Tier 2 | Butte | North Valley | 39.7462 | -121.644 | Paradise-Table Mountain 115kV line STR 002/025 | Storm | 715 AAC | Lat: 39.74615, Long: -121.644 | SD
115 | 115 | ETL.2140 | 10140 | LIVE OAK-KERN OIL | 2024 | 2024-02-04 21:21 | 45326.8896 | YES | YES | No | 1900-01-01 21:25 | 4165 | 2024-02-07 18:46 | 45329.7819 | F | Equipment Failure | Equip Fail-structure-line | COND | Relayed - 2/4/24, 2121 Live Oak-Kern Oil 115kV line relayed and tested NG. 2/7/24, 1837 Live Oak-Kern Oil 115kV line de-energized to operate Vedder JCT switch 145 dead. Sustained interruption to Oxy Kern-Front. 1846 Live Oak-Kern Oil 115kV line returned to service after crews replaced NG insulators at structures 004/056, 004/060, 005/064 and replaced NG poles at 007/086, 007/087 and 007/088. Restoring Vedder, Poso Mountain and Oxy Kern-Front. From trouble on 02/04/24 at 2121. ET-WD | 128168875 | CENTRAL VALLEY | INT-18017 | 1 | 1 | 4165 | 1.7389e-07 | 0.00072424 | 4165 | 5750834 | A-G | 002/029 | AUTO | Single Mode | Tier 2 | Kern | Kern | 35.5512 | -118.97 | Vedder 115kV Tap STR 007/086 | Storm | 3/0 AAC | Lat: 35.55116, Long: -118.97 | SD
69 | 60 | ETL.6880 | 60082 | FULTON-CALISTOGA | 2024 | 2024-02-05 17:48 | 45327.7417 | No | YES | No | 1899-12-31 22:20 | 2780 | 2024-02-07 16:08 | 45329.6722 | F | Tree | Tree-failure | COND | Forced - 2/5/24, 1748 Fulton-Calistoga 60kV line (Calistoga to Middle Town section) deenergized for down tree found between poles B002/002 and B002/001. No Customer interruption. No estimated return. 2/7/24, 1608 Fulton-Calistoga 60kV line (Calistoga to Middle Town section) returned to service after crews removed a tree and replaced 3 phases of downed conductors between structures B002/001 and B002/002. From trouble on 02/05/24 at 1748. ET-WD | NONE | CENTRAL VALLEY | T24-004522 | 0 | 0 | 0 | 0 | 0 | 0 | 5750834 | N/A | N/A | EFO | Emergency Forced Outage | Tier 3 | Napa | North Bay | 38.6238 | -122.587 | Fulton-Calistoga 60kV line STR B002/002 | Storm | 4/0 AAC | Lat: 38.62381, Long: -122.587 | SD
69 | 60 | ETL.6910 | 60085 | FULTON-MOLINO-COTATI | 2024 | 2024-02-07 07:00 | 45329.2917 | No | YES | No | 0.67569 | 973 | 2024-02-07 23:13 | 45329.9674 | F | External Contact | Ext Cont-car pole | COND | Relayed - 2/7/24, 0700 Fulton-Molino-Cotati 60kV line relayed and tested NG. Sustained interruption to Laguna, Sonoma County Landfill and Cotati. Momentary interruption to Molino (17471). Weather is clear. 0706 Cotati transferred to alternate source. 0707 Fulton to Laguna JCT section manually tested OK restoring Laguna. 1135 Fulton-Molino-Cotati 60kV line (Laguna JCT to Cotati section) cleared for crew to repair 3 phases of wire down and replace pole 015/287 damaged by car pole. ET-WD | NONE | NORTH COAST | INT-18051 | 25051 | 7635 | 45810 | 0.0013276 | 0.0079658 | 6 | 5750834 | A-B-C | 015/289 | AUTO | Single Mode | Tier 2 | Sonoma | Sonoma | 38.3253 | -122.736 | Fulton-Molino-Cotati 60kV line STR 015/287 | Clear | 4/0 AAC | Lat: 38.32527, Long: -122.736 | SD
69 | 60 | ETL.7850 | 60184 | RIO DELL JCT-BRIDGEVILLE | 2024 | 2024-02-29 08:11 | 45351.341 | No | YES | No | 0.00069444 | 1 | 2024-02-29 08:12 | 45351.3417 | F | Tree | Tree-failure | COND | Relayed - 2/29/24, 0811 Rio Dell JCT-Bridgeville 60kV line (Rio Dell JCT to Carlotta section) relayed and tested OK. Carlotta to Bridgeville section tested NG. Momentary interruption to Humboldt Redwood (1) and Carlotta (1143). Weather storm. Line patrol of the Carlotta to Bridgeville section found a tree through all 3 phases of transmission and distribution conductor between poles 038/006 and 038/007 and broken pole 038/006. Line will be cleared for repairs. 3/2/24, 1208 Rio Dell JCT-Bridgeville 60kV line (Carlotta to Bridgeville section) returned to service after crew replaced NG structure 038/006 and repaired conductor between structures 038/006 and 038/007. From trouble on 02/29/24 at 0811. ET-WD | NONE | NORTH COAST | INT-18116 | 1144 | 0 | 0 | 0 | 0 | 0 | 5750834 | B-C-G | 038/008 | AUTO | Single Mode | Tier 2 | Humboldt | Humboldt | 40.4699 | -123.8161 | Rio Dell JCT-Bridgeville 60kV line STR 038/006 | Rain | 4/0 AAC | Lat: 40.46994, Long: -123.81612 | GS
69 | 60 | ETL.6470 | 60038 | COLGATE-ALLEGHANY | 2024 | 2024-03-01 17:27 | 45352.7271 | YES | YES | No | 0.93819 | 1351 | 2024-03-02 15:58 | 45353.6653 | F | Tree | Tree-failure | COND | Relayed - 3/1/24, 1727 Colgate-Alleghany 60kV line relayed and tested NG. Sustained interruption to Alleghany, Pike City and Columbia Hill. Weather storm. 1733 Colgate to Columbia Hill JCT section tested OK, restoring Columbia Hill. Estimated return 03/03/24. 3/2/24, 1056 Colgate-Alleghany 60kV line (Colgate SW STA to Columbia Hill section) de-energized to close Columbia Hill JCT switch 17 dead. Momentary interruption to Columbia Hill (1164). 1057 Colgate-Alleghany 60kV line (Colgate SW STA to Pike City section) energized restoring Columbia Hill and Pike City after T-Line patrolled with no trouble found. Pike City to Alleghany section patrol found down conductor at structure 017/461. Estimated return 03/03/24 at 1600. 3/2/24, 1549 Colgate-Alleghany 60kV line (Colgate SW STA to Pike City section) de-energized to close Pike City JCT switch 77 dead. Sustained interruption to Columbia Hill (1164) and Pike City (438). 1558 Colgate-Alleghany 60kV line energized restoring Columbia Hill, Pike City and Alleghany after T-Line removed down tree and repaired conductor between structures 017/460 and 17/461. ET-WD | NONE | NORTH VALLEY AND SIERRA | INT-18128 | 1657 | 1657 | 483254 | 0.00028813 | 0.084032 | 291.6439 | 5750834 | B-G | 012/313 | AUTO | Single Mode | Tier 3 | Sierra | Sierra | 39.4496 | -120.9581 | Colgate-Alleghany 60kV line STR 017/461 | Storm | 2 CU | Lat: 39.44955, Long: -120.95807 | SD
69 | 60 | ETL.8060 | 60206 | SPAULDING-SUMMIT | 2024 | 2024-03-01 19:21 | 45352.8063 | YES | YES | No | 1900-01-01 01:41 | 2981 | 2024-03-03 21:02 | 45354.8764 | F | Tree | Tree-failure | COND | Relayed - 3/1/24, 1921 Spaulding-Summit 60kV line relayed and tested NG. Sustained interruption to Cisco Grove, Tamarack and Summit. Weather storm. 1922 Spaulding to Summit section manually tested NG. 1926 Spaulding to Tamarack section manually tested NG. Estimated return 03/02/24. 3/2/24, 0520 Spaulding-Summit 60kV line (Summit section) energized, restoring Summit via NV Energy source. 0947 Spaulding-Summit 60kV line (Spaulding to Tamarack section) manually tested OK restoring Cisco Grove and Tamarack after T-Line patrolled with no trouble found. 3/3/24, 2102 Spaulding-Summit 60kV line (Tamarack to Summit section) returned to service after crew removed tree and reframed pole 011/397, installed splice and re-sagged conductor from poles 011/396 to 011/398. From trouble on 03/01/24 at 1921. ET-WD | NONE | NORTH VALLEY AND SIERRA | INT-18132 | 1292 | 1292 | 810052 | 0.00022466 | 0.14086 | 626.9752 | 5750834 | A-B | 012/419 | AUTO | Single Mode | Tier 2 | Nevada | Sierra | 39.3175 | -120.4485 | Spaulding-Summit 60kV line STR 011/397 | Snow | 397.5 ACSR | Lat: 39.31753, Long: -120.44849 | SD
69 | 60 | ETL.7560 | 60152 | WEIMAR #1 | 2024 | 2024-03-01 20:56 | 45352.8722 | YES | YES | No | 1900-01-01 03:02 | 3062 | 2024-03-03 23:58 | 45354.9986 | F | Weather | Weather-snow/ ice | COND | Relayed - 3/1/24, 2056 Weimar #1-60kV line relayed and tested NG. On the trouble, Middle Fork #1-60kV line de-energized. Weimar to Forest Hill JCT manually tested OK. Oxbow PH separated on the trouble. Momentary interruption to Forest Hill. Estimated return 03/03/24. 3/2/24, 1410 Weimar #1-60kV line (Weimar to Forest Hill section) de-energized to close Forest Hill JCT switch 37 dead. Momentary interruption to Forest Hill. 1411 Weimar #1-60kV line manually tested NG after T-Line patrolled with no trouble found. 1412 Weimar #1-60kV line (Weimar to Forest Hill section) manually tested OK restoring Forest Hill. 3/3/24, 1834 Weimar to Forest Hill JCT section de-energized to close Forest Hill JCT switch 37 dead. 1835 Weimar #1 and a section of the Middle Fork #1-60kV line manually tested OK. Restoring Oxbow PH. Momentary interruption to Forest Hill. Middle Fork #1-60kV line (Ralston PH JCT to Middle Fork section) cleared for crews to reframe poles 003/52, 003/053 and repair 1 phase of wire down between structures 003/051 and 003/052. Estimated return 03/04/23. 3/4/24, 2252 Weimar #1-60kV line de-energized to close Middle Fork 17 and Ralston 19 (dead operation). Sustained interruption to Forest Hill and Oxbow PH (offline). 2337 Weimar to Forest Hill section energized, restoring Forest Hill. 2357 Weimar to Forest Hill section de-energized. Momentary interruption to Forest Hill. 2358 Weimar #1-60kV line (Ralston PH JCT to Middle Fork section) returned to service after crew repaired 1 phase of wire down at structures 3/51 & 3/52 and reframed structures 3/52 & 3/53, restoring Forest Hill and Oxbow PH. From trouble on 03/01/24 at 2056. ET-WD | NONE | NORTH VALLEY AND SIERRA | INT-18135-1 | 2704 | 0 | 0 | 0 | 0 | 0 | 5750834 | A-C | 011/169 | AUTO | Dependent Mode Initiating | Tier 2 | Placer | Sierra | 39.0199 | -120.9399 | Middle Fork #1-60kV line STR 003/052 | Storm | 2 ACSR | Lat: 39.01992, Long: -120.93986 | SD
69 | 60 | ETL.6220 | 60010 | BRIDGEVILLE-GARBERVILLE | 2024 | 2024-03-03 07:34 | 45354.3153 | No | YES | No | 0.80069 | 1153 | 2024-03-04 02:47 | 45355.116 | F | Tree | Tree-failure | COND | Relayed - 3/3/24, 0734 Bridgeville-Garberville 60kV line relayed and tested NG. Sustained interruption to Fruitland and Fort Seward. Weather storm. 0741 Fruitland JCT - Garberville section energized after isolating Fort Seward, restoring Fruitland. 0743 Bridgeville - Fruitland JCT section energized. 0744 Line restored normal. 1202 Patrol reports a downed tree across all 3 conductors between structures 2/6 and 2/7, on the Fort Seward tap. Fort Seward 60kV tap to be cleared for crew to remove tree. No estimated return. 3/4/24, 0244 to 0246 Bridgeville-Garberville 60kV line (Garberville to Fort Seward JCT section) de-energized to close Fort Seward JCT switch 71 dead. No customer interruption. 0246 Fort Seward 60kV tap returned to service after crew removed tree from 3 phases of conductor between poles 002/006 and 002/007. Restoring Fort Seward. 0247 Bridgeville-Garberville 60kV line returned to service normal. From trouble on 03/03/24 at 0734. ET-WD | NONE | NORTH COAST | INT-18154 | 1480 | 1480 | 14800 | 0.00025735 | 0.0025735 | 10 | 5750834 | A-C | 002/005 | AUTO | Single Mode | Non-HFTD | Humboldt | Humboldt | 40.2126 | -123.6658 | Fort Seward 60kV Tap STR 002/006 | Storm | 4/0 ACSR | Lat: 40.21258, Long: -123.66579 | SD
69 | 70 | ETL.9020 | 70062 | ORO LOMA-CANAL #1 | 2024 | 2024-03-11 23:26 | 45362.9764 | No | YES | YES | 0.62222 | 896 | 2024-03-12 14:22 | 45363.5986 | F | External Contact | Ext Cont-car pole | COND | Relayed - 3/11/24, 2326 Oro Loma-Canal #1-70kV line relayed and did not test. Sustained interruption to Dos Palos and Santa Rita. Weather rain. 2333 line manually tested NG. 2343 Canal to Santa Rita section manually tested OK, restoring Santa Rita. 2355 Oro Loma to Dos Palos JCT section manually tested OK, restoring Dos Palos. 2355 Oro Loma 70kV CB 7022 failed to close after trouble on Oro Loma-Canal #1-70kV line. T-Line went to the hazard and found car pole at 11/13, crew will replace pole on LC 128274777, all conductors broke on ground for the 70KV and 12KV. 3/12/24, 1422 Oro Loma-Canal #1-70kV line (Dos Palos JCT to Santa Rita section) returned to service after crew replaced structure 011/013 and repaired all 3 phases of conductor. ET-WD | 128274787 | CENTRAL VALLEY | INT-18173 | 3601 | 3601 | 721124 | 0.00062617 | 0.12539 | 200.2566 | 5750834 | A-B-C | 012/009 | AUTO | Single Mode | Non-HFTD | Merced | Yosemite | 37.0231 | -120.6355 | Oro Loma-Canal #1-70kV line STR 011/013 | Clear | 397.5 AAC | Lat: 37.02308, Long: -120.63554 | GS
69 | 60 | ETL.7575 | 60422 | SNEATH LANE-PACIFICA | 2024 | 2024-03-15 01:16 | 45366.0528 | No | YES | No | 0.77639 | 1118 | 2024-03-15 19:54 | 45366.8292 | F | Equipment Failure | Equip Fail-connector/ hardware | NONE | Relayed - 3/15/24, 0116 Sneath Lane-Pacifica 60kV line relayed and tested NG. Momentary interruption to Pacifica. Weather clear. 1954 Line returned to service after crew repaired 1 phase of downed conductor between structures 005/062 and 006/063. Tman confirmed that wire broke at or near the attachment point of Pole 5/62 towards Pole 6/63 (sheared right at the armor rod). No signs of ignition found. Dispatching crew ASAP. ET-WD | NONE | BAY AREA | INT-18178 | 10044 | 0 | 0 | 0 | 0 | 0 | 5750834 | A-C | 006/063 | AUTO | Single Mode | Tier 3 | San Mateo | Peninsula | 37.6029 | -122.4646 | Sneath Lane-Pacifica 60kV line STR 005/062 | Clear | 715 AAC | Lat: 37.60288, Long: -122.46463 | SD
69 | 60 | ETL.8310 | 60231 | WATSONVILLE-SALINAS | 2024 | 2024-03-16 08:23 | 45367.3493 | No | YES | No | 0.36389 | 524 | 2024-03-16 17:07 | 45367.7132 | F | Equipment Failure | Equip Fail-conductor | NONE | Forced - 3/16/24, 0823 to 1707 Watsonville-Salinas 60kV line (Brigatano JCT to Lagunitas tap section) forced out of service for crew to repair downed conductor at structure 020/251. No customer interruption. As you mentioned below, Lagunitas 60kV Tap has a normally open SW 19 on pole 0/11, and the phase conductor that hit the ground was on the side of the line with the normally open switch. Since there is no power source from the normally open switch, the phase conductor is de-energized when it hits the ground. From the pictures, the energized jumper at structure 20/251 was in contact with the ungrounded wooden pole causing the pole to burn/smoke. Ungrounded wood poles are known to be highly resistive, and high resistive faults result in low fault currents. Since the line relays at Salinas and Watsonville did not record any information for this event, it means the fault current was less than the pickup setting of 120 amps. Due to the high resistive fault caused by the ungrounded wood pole, the fault current was low enough to not be detectable by the relays. Our standard protection guidelines do not capture these types of faults. ET-WD | NONE | SOUTH BAY AND CENTRAL COAST | T24-006657 | 0 | 0 | 0 | 0 | 0 | 0 | 5750834 | N/A | N/A | EFO | Emergency Forced Outage | Non-HFTD | Monterey | Central Coast | 36.7571 | -121.6111 | Watsonville-Salinas 60kV line STR 020/251 | Clear | 397.5 AAC | Lat: 36.75707, Long: -121.61111 | BS
69 | 70 | ETL.8850 | 70045 | KERN CANYON-MAGUNDEN-WEEDPATCH | 2024 | 2024-03-24 00:57 | 45375.0396 | No | YES | YES | 0.82361 | 1186 | 2024-03-24 20:43 | 45375.8632 | X | Other | Other-distribution caused | STRU | Relayed - 3/24/24, 0057 Kern Canyon-Magunden-Weedpatch70kV line relayed and tested NG. On the trouble Kern-Magunden 70kV line de-energized. Sustained interruption to Golden State Metals, Kern Canyon PH (offline) and Rio Bravo PH (offline). Weather storm. 0300 Kern-Magunden 70kV line returned to service, restoring Golden State Metals. 2043 Kern Canyon-Magunden-Weedpatch 70kV line returned to service after crew repaired NG pole 4/71, replaced downed conductor between poles 4/70 and 4/72 and NG cross arms on the underbuilt between poles 4/70 to 4/67. ET-WD | NONE | CENTRAL VALLEY | INT-18198-1 | 1 | 1 | 1186 | 1.7389e-07 | 0.00020623 | 1186 | 5750834 | A-G | 004/072 | AUTO | Dependent Mode Initiating | Non-HFTD | Kern | Kern | 35.4103 | -118.8668 | Kern Canyon-Magunden-Weedpatch 70kV line STR 004/071 distribution underbuild | Storm | 397.5 AAC | Lat: 35.41028, Long: -118.86683 | GS
69 | 60 | ETL.7550 | 60151 | MENDOCINO-WILLITS-FORT BRAGG | 2024 | 2024-03-24 01:17 | 45375.0535 | No | YES | YES | 0.94583 | 1362 | 2024-03-24 23:59 | 45375.9993 | F | Tree | Tree-failure | STRU | Relayed - 3/24/24, 0117 Mendocino-Willits-Fort Bragg 60kV line relayed and tested NG. No customer interruption. Weather storm. 0546 Mendocino to Willits to Willits JCT section returned to service after isolating trouble between Fort Bragg and Willits JCT. 2359 Fort Bragg to Willits JCT section returned to service after crew replaced downed conductor and NG pole 028/007. ET-WD | NONE | NORTH COAST | INT-18199 | 0 | 0 | 0 | 0 | 0 | 0 | 5750834 | A-B-C | 029/006 | AUTO | Single Mode | Tier 2 | Mendocino | Humboldt | 39.3484 | -123.5778 | Mendocino-Willits-Fort Bragg 60kV line STR 028/007 | Storm | 397.5 AAC | Lat: 39.34838, Long: -123.5778 | GS
69 | 60 | ETL.7851 | 60105B | RIO DELL TAP | 2024 | 2024-03-25 03:27 | 45376.1438 | No | YES | No | 0.59444 | 856 | 2024-03-25 17:43 | 45376.7382 | X | Disaster | Disaster-flood | COND | Relayed - 3/25/24, 0327 Rio Dell 60kV tap relayed and tested NG. Sustained interruption to Rio Dell and Humboldt Redwood Scotia. Weather rain. 3/25/24, 1743 Rio Dell 60kV tap returned to service after crew replaced 3 phases of downed conductors between structures 002/003 and 002/004. Multiple trees and land movement cause. ET-WD | NONE | NORTH COAST | INT-18201 | 3031 | 3031 | 1180004 | 0.00052705 | 0.20519 | 389.3118 | 5750834 | A-B | 002/006 | AUTO | Single Mode | Non-HFTD | Humboldt | Humboldt | 40.5313 | -124.1072 | Rio Dell 60kV Tap STR 002/003 | Storm | 4/0 AAC | Lat: 40.53129, Long: -124.10718 | GS
115 | 115 | ETL.3830 | 10317 | STANISLAUS-MELONES SW STA-MANTECA #1 | 2024 | 2024-04-04 02:48 | 45386.6167 | No | YES | No | 1899-12-31 11:56 | 2156 | 2024-04-05 14:44 | 45387.6139 | F | Equipment Failure | Equip Fail-conductor | NONE | Relayed - 4/4/24, 1448 Stanislaus-Melones SW STA-Manteca #1-115kV line relayed and tested NG. Sustained interruption to Avena and Frogtown. Weather snow. 1522 Melones to Frogtown JCT section manually tested OK, restoring Avena and Frogtown. Frogtown JCT to Stanislaus section cleared to repair 1 phase of down conductor between structures 003/023 and 003/024. Estimated return 04/05/24. 4/5/24, 1443 Stanislaus-Manteca #1-115kV line (Frogtown to Manteca section) de-energized to close Frogtown JCT 137 dead. Momentary interruption to Frogtown and Avena. 1444 Stanislaus-Manteca #1-115kV line manually tested OK, after crews repaired down conductor between structures 003/023 and 003/024, restoring Stanislaus and Stanislaus PH. From trouble on 04/04/24 at 1448. ET-WD | NONE | CENTRAL VALLEY | INT-18234 | 7620 | 7620 | 262436 | 0.001325 | 0.045634 | 34.4404 | 5750834 | B-C | 003/023 | AUTO | Dependent Mode Initiating | Tier 2 | Calveras | Stockton | 38.1156 | -120.4298 | Stanislaus-Melones SW STA-Manteca #1-115kV line STR 003/023 | Snow | 2/0 CU | Lat: 38.115596, Long: -120.429824 | GS
115 | 115 | ETL.1950 | 10464 | LERDO-KERN OIL-7TH STANDARD | 2024 | 2024-04-05 19:33 | 45387.8146 | No | YES | YES | 0.56319 | 811 | 2024-04-06 09:04 | 45388.3778 | X | Other | Other-distribution caused | STRU | Relayed - 4/5/24, 1933 Lerdo-Kern Oil-7th Standard 115kV line relayed and did not test due to pole fire at structure F002/003. No customer interruption. Weather rain. Estimated return 04/06/24. 4/6/24, 0904 Lerdo-Kern Oil-7th Standard 115kV line returned to service after crew replaced NG pole F002/003 and repaired NG conductor. From trouble on 04/05/24 at 1933. Fire at distribution level caused pole failure. ET-WD | 128468141 | CENTRAL VALLEY | T24-007567 | 0 | 0 | 0 | 0 | 0 | 0 | 5750834 | C-G | F002/003 | AUTO | Single Mode | Non-HFTD | Kern | Kern | 35.4886 | -119.0857 | Lerdo-Kern Oil-7th Standard 115kV line STR F0002/003 | Rain | TBD | Lat: 35.488554, Long: -119.085697 | SD
115 | 115 | ETL.4393 | 10459 | DRUM-HIGGINS | 2024 | 2024-05-04 18:32 | 45416.7722 | No | YES | No | 0.59167 | 852 | 2024-05-05 08:44 | 45417.3639 | F | Weather | Weather-lightning | COND | Relayed - 5/4/24, 1832 Drum-Higgins 115kV line relayed and tested NG. Sustained interruption to Dutch Flat #1 PH (online) and Chicago Park PH (online). Weather lightning. 1850 Drum PH to Chicago Park JCT section manually tested OK, restoring Chicago Park PH and Dutch Flat #1 PH. Estimated return 05/05/24 at 0800. 5/5/24, 0844 Drum-Higgins 115kV line (Chicago Park JCT to Higgins section) returned to service after crew repaired down conductor between towers 027/206 and 027/207. From trouble on 05/04/24 at 1832. | NONE | NORTH VALLEY AND SIERRA | INT-18324 | 2 | 0 | 0 | 0 | 0 | 0 | 5750834 | A-G | 026/204 | AUTO | Single Mode | Tier 2 | Nevada | Sierra | 39.0524 | -121.0955 | Drum-Higgins 115kV line 027/206 | Lightning | 397.5 ACSR | Lat: 39.05243, Long: -121.09553 | SD
69 | 60 | ETL.8330 | 60234 | WEBER-MORMON JCT | 2024 | 2024-05-20 23:28 | 45432.9778 | No | YES | No | 1899-12-31 05:15 | 1755 | 2024-05-22 04:43 | 45434.1965 | F | Work Procedure Error | Work Procedure-not following prescribed procedures | STRU | Relayed - 5/20/24, 2328 Weber-Mormon JCT 60kV line relayed and tested NG. Sustained interruption to Mormon and Linden. Weather clear. 2345 Weber to Mormon JCT section tested NG. 5/21/24, 0012 Weber-Mormon JCT 60kV line (Linden Section) returned to service from alternate source. Restoring Linden. 0111 Mormon restored from the Stockton “A”-Weber #3 60kV line. After isolating trouble between Weber and Mormon JCT switch 37. Trouble found NG pole at 3/49 Weber Mormon jct No cause at this time. 5/22/24, 0443 Weber-Mormon JCT 60kV line returned service normal after crew replaced structure 003/049 and restrung all 3 phases of conductor between 003/049 and 003/050. From trouble on 05/20/24 at 2328. | NONE | CENTRAL VALLEY | INT-18364 | 6347 | 6347 | 598344 | 0.0011037 | 0.10404 | 94.2719 | 5750834 | A-C-G | 003/052 | AUTO | Single Mode | Non-HFTD | San Joaquin | Stockton | 37.9334 | -121.1842 | Weber-Mormon JCT 60kV line STR 003/049 | Clear | 715 AAC | Lat: 37.93336, Long: -121.1842 | GS
69 | 60 | ETL.6240 | 60012 | BURNS-LONE STAR #2 | 2024 | 2024-06-01 16:12 | 45444.675 | No | YES | YES | 0.77292 | 1113 | 2024-06-02 10:45 | 45445.4479 | F | Tree | Tree-failure | COND | Relayed - 6/1/24, 1612 Burns-Lone Star #2-60kV line (HFRA) (EPSS) relayed and did not test as directed by Operations. Sustained interruption to Point Moretti, Crusher and Cemex. Weather clear. 2154 Burns to Point Moretti section cleared for crew to replace three phases of downed conductor at structure 002/043. Estimated return 06/02/24. 6/2/24, 1045 Burns-Lone Star #2-60kV line (HFRA) (EPSS) (Burns to Point Moretti section) returned to service after crew replaced three phases of downed conductor at structure 002/043 due to tree contact. From trouble on 06/01/24 at 1612. | NONE | SOUTH BAY AND CENTRAL COAST | INT-18382 | 815 | 815 | 273284 | 0.00014172 | 0.047521 | 335.3178 | 5750834 | A-B | 002/049 | AUTO | Single Mode | Tier 3 | Santa Cruz | Central Coast | 37.0704 | -122.1431 | Burns-Lone Star #2-60kV line STR 002/043 | Clear | 2 CU | Lat: 37.070391, Long: -122.143079 | BS
69 | 60 | ETL.6410 | 60032 | COBURN-OIL FIELDS #1 | 2024 | 2024-07-13 17:28 | 45486.7278 | No | YES | No | 0.91111 | 1312 | 2024-07-14 15:20 | 45487.6389 | F | Disaster | Disaster-fire | STRU | Relayed - 7/13/24, 1728 Coburn-Oil Fields #1-60kV line relayed and tested NG. Sustained interruption to San Ardo. Weather clear. 2025 Coburn-Oil Fields #1-60kV line (Oil Fields to San Ardo JCT SW 17 section) returned to service restoring San Ardo. Estimated return 07/14/24. 7/14/24, 1520 Coburn-Oil Fields #1-60kV line (Coburn to San Ardo JCT section) returned to service after crew repaired downed conductor and replaced NG pole 004/097. From trouble on 07/13/24 at 1728. TSAFE identified as Third Party caused fire. | NONE | SOUTH BAY AND CENTRAL COAST | INT-18494 | 795 | 795 | 172338 | 0.00013824 | 0.029967 | 218 | 5750834 | B-G | 003/072 | AUTO | Single Mode | Non-HFTD | Monterey | Central Coast | 36.2093 | -121.1175 | Coburn-Oil Fields #1-60kV line STR 004/097 | Clear | 715 AAC | Lat: 36.209346, Long: -121.117456 | SD
69 | 60 | ETL.6870 | 60081 | FRENCH MEADOWS-MIDDLE FORK | 2024 | 2024-08-12 12:53 | 45516.5368 | No | YES | YES | 0.83403 | 1201 | 2024-08-13 08:54 | 45517.3708 | F | Tree | Tree-3rd party | COND | Relayed - 8/12/24, 1253 French Meadows-Middle Fork 60kV line (HFRA) relayed and did not test as directed by operations. On the trouble, French Meadows PH and Hell Hole PH separated. Weather clear. 8/13/24, 0854 French Meadows-Middle Fork 60kV line (HFRA) returned to service after crew reframed, replaced insulators and repaired single phase of wire down between structures 008/150 and 008/151, restoring French Meadows PH and Hell Hole PH. From trouble on 08/12/24 at 1253. | NONE | NORTH VALLEY AND SIERRA | INT-18572 | 0 | 0 | 0 | 0 | 0 | 0 | 5750834 | Fault locating not available | N/A | AUTO | Single Mode | Tier 3 | Placer | Sierra | 39.0266 | -120.5323 | French Meadows-Middle Fork 60kV line (HFRA) STR 008/150 | Clear | 4/0 ACSR | Lat: 39.026617, Long: -120.532252 | BS
69 | 60 | ETL.7460 | 60141 | MANTECA #1 | 2024 | 2024-08-22 11:00 | 45526.4583 | No | YES | No | 0.46944 | 676 | 2024-08-22 22:16 | 45526.9278 | F | Equipment Failure | Equip Fail-conductor | COND | Forced - 8/22/24, 1100 to 2216 Manteca #1-60kV line (Manteca to Lee JCT section) forced out of service to replace downed conductor between structures 002/035 and 002/036. No customer interruption. I believe the Manteca #1 60kV on 8/22 did not result in automatic de-energization. I’ve copied the area protection engineers, but I believe the reason was the broken conductor fell on the load side (not source side) of the radial line, and therefore did not result in an electrical fault. - Ben Nie | NONE | CENTRAL VALLEY | T24-014316 | 4337 | 4337 | 300324 | 0.00075415 | 0.052223 | 69 | 5750834 | N/A | N/A | EFO | Emergency Forced Outage | Non-HFTD | San Joaquin | Stockton | 37.7768 | -121.2342 | Manteca #1-60kV line (Manteca to Lee JCT section) STR 002/035 | Clear | 4/0 AAC | Lat: 37.776818, Long: -121.234186 | SD
69 | 70 | ETL.9250 | 70085 | TEJON-LEBEC | 2024 | 2024-08-26 17:00 | 45530.7083 | No | YES | YES | 0.57778 | 832 | 2024-08-27 06:52 | 45531.2861 | F | External Contact | Ext Cont-car pole | STRU | Relayed - 8/26/24, 1700 Tejon-Lebec 70kV line (EPSS) relayed and did not test as directed by Operations. Sustained interruption to Rose, Pacific Pipeline, Grapevine, Castaic and Lebec. Caused by carpole at 5/99. Estimated return 08/27/24 at 0600. 8/27/24, 0652 Tejon-Lebec 70kV line (Rose JCT to Pacific Pipeline JCT section) returned to service restoring Rose, Pacific Pipeline, Grapevine, Castaic and Lebec after crew repaired downed conductor and replaced NG pole 05/99 damaged by car pole. From trouble on 08/26/24 at 1700. | 129441112 | CENTRAL VALLEY | INT-18596 | 717 | 717 | 160516 | 0.00012468 | 0.027912 | 224 | 5750834 | C-A | 004/083 | AUTO | Single Mode | Non-HFTD | Kern | Kern | 34.9488 | -118.9331 | Tejon-Lebec 70kV line (EPSS) STR 5/99 | Clear | 1/0 ACSR | Lat: 34.948818, Long: -118.93309 | SD
69 | 60 | ETL.7490 | 60145 | MAPLE CREEK-HOOPA | 2024 | 2024-11-13 17:46 | 45609.7403 | No | YES | YES | 0.60625 | 873 | 2024-11-14 08:19 | 45610.3465 | F | Tree | Tree-failure | COND | Relayed - 11/13/24, 1746 Maple Creek-Hoopa 60kV line (HFRA) (EPSS) relayed and did not test as directed by Operations. Sustained interruption to Russ Ranch, Willow Creek and Hoopa. Weather rain. 1848 Maple Creek to Russ Ranch section manually tested OK, restoring Russ Ranch. 2117 Berry Summit to Willow Creek section cleared to reframe pole 15/4 and repair/replace 1 phase of broken conductor between poles 15/4 to 15/5 caused by downed tree. Estimated return 11/14/24 at 0800. 11/14/24, 0815 Maple Creek-Hoopa 60kV line (Maple Creek to Berry Summit section) de-energized to close Berry Summit switch 27 on a dead operation. Momentary interruption to Russ Ranch. 0819 Maple Creek-Hoopa 60kV line (EPSS) (HFRA) returned to service after crew replaced 1 span of down conductor between structures 015/004 and 015/005 and reframed structure 015/004, restoring Willow Creek and Hoopa. From trouble on 11/13/24 at 1746. | NONE | NORTH COAST | INT-18742 | 4449 | 4449 | 3929115 | 0.00077363 | 0.68323 | 1828 | 5750834 | C-A | 015/002 | AUTO | Single Mode | Tier 3 | Humboldt | Humboldt | 40.9125 | -123.7045 | Maple Creek-Hoopa 60kV line (HFRA) (EPSS) STR 15/4 | Rain | 4/0 ACSR | Lat: 40.912455, Long: -123.70449
69 | 70 | ETL.8550 | 70113 | CARUTHERS-LEMOORE NAS-CAMDEN | 2024 | 2024-11-19 10:53 | 45615.4535 | No | YES | No | 0.15764 | 227 | 2024-11-19 14:40 | 45615.6111 | F | Equipment Failure | Equip Fail-conductor | COND | Forced - 11/19/24, 1053 to 1440 Caruthers-Lemoore NAS-Camden 70kV line (Camden-Camden JCT section) forced out of service for crew to repair downed conductor on structure 15/15. No customer interruption. Weather clear.T-Line went to the hazard and found 1 phase (road side) broke at pole 15/15, conductor broke to the ground towards Camden sub which has an open breaker that is way line did not relay….at pole 15/15 to SW 25 stay hot, crew will repair conductor and install dampeners on LC 129835232 (PM 46393946)….conductor will go to ATS. | NONE | CENTRAL VALLEY | T24-017087 | 0 | 0 | 0 | 0 | 0 | 0 | 5750834 | N/A | N/A | EFO | Emergency Forced Outage | Non-HFTD | Fresno | Fresno | 36.4455 | -119.8263 | Caruthers-Lemoore NAS-Camden 70kV line (Camden-Camden JCT section) STR 15/15 | Clear | 3/0 AAC | Lat: 36.445507, Long: -119.826252
69 | 60 | ETL.2060 | 60389 | FORT BRAGG-ELK | 2024 | 2024-11-20 15:28 | 45616.6444 | No | YES | No | 1899-12-31 02:10 | 1570 | 2024-11-21 17:38 | 45617.7347 | F | Tree | Tree-failure | COND | Relayed - 11/20/24, 1528 Fort Bragg-Elk 60kV line relayed and tested NG. Sustained interruption to Big River (2,613). Weather storm. 2015 Big River to Elk section cleared to repair three phases of downed conductor between poles 013/002 and 013/003. Patrol found all 3 phases down between 13/2-13/3-Fur tree.No estimated return. 11/21/24, 1738 Fort Bragg-Elk 60kV line returned to service, restoring Big River after crew repaired three phases of downed conductor between poles 13/2 and 13/3. 1836 Big River 60kV SVC returned to service. From trouble on 11/20/24 at 1528. | NONE | NORTH COAST | INT-18769 | 1113 | 1113 | 330639 | 0.00019354 | 0.057494 | 618 | 5750834 | A-B | 014/004 | AUTO | Single Mode | Tier 2 | Mendocino | Humboldt | 39.2948 | -123.7893 | Fort Bragg-Elk 60kV line STR 013/002 | Storm | 397.5 AAC | Lat: 39.294805, Long: -123.789315
69 | 60 | ETL.6470 | 60038 | COLGATE-ALLEGHANY | 2024 | 2024-11-22 18:50 | 45618.7847 | No | YES | No | 0.97292 | 1401 | 2024-11-23 18:11 | 45619.7576 | F | Tree | Tree-failure | COND | Relayed - 11/22/24, 1850 Colegate-Alleghany 60kV line relayed and tested NG. 1855 Colgate to Pike City JCT section manually tested NG. Sustained interruption to Columbia Hill, Pike City and Alleghany. Weather Storm. 2212 Colgate to Columbia Hill section manually tested OK, restoring transmission service to Columbia Hill. Estimated return 11/23/24. 11/23/24, 1811 Colgate-Alleghany 60kV line (Columbia Hill to Pike City section) tested OK, after crew removed tree and repaired 3 phases of wire down between structures 010/271 and 010/272, restoring transmission service to Pike City. 1812 Transmission service restored to Alleghany. From trouble on 11/22/24 at 1850. | NONE | NORTH VALLEY AND SIERRA | INT-18785 | 1242 | 1242 | 1531291 | 0.00021597 | 0.26627 | 1233 | 5750834 | A-B-C | 010/072 | AUTO | Single Mode | Tier 3 | Nevada | Sierra | 39.3823 | -121.0351 | Colegate-Alleghany 60kV line STR 010/271 | Storm | 4/0 ACSR | Lat: 39.382327, Long: -121.035124
69 | 60 | ETL.7212 | 60424 | SNEATH LANE-HALF MOON BAY | 2024 | 2024-12-09 09:08 | 45635.3806 | No | YES | No | 1900-01-03 01:45 | 5865 | 2024-12-13 10:53 | 45639.4535 | C | Equipment Failure | Equip Fail-conductor | COND | Forced - 12/9/24, 0908 Sneath Lane-Half Moon Bay 60kV line forced out of service to repair down conductor at structure ;000/006. No customer interruption. Estimated return 12/11/24. 12/13/24, 1053 Sneath Lane-Half Moon Bay 60kV line returned to service after crew repaired downed conductor at structure ;000/006, added spacers at structures ?004/000, ?004/001, ?002/000 and ?001/013. From trouble on 12/09/24 at 0908. | 129911042 | SOUTH BAY AND CENTRAL COAST | T24-017364 | 0 | 0 | 0 | 0 | 0 | 0 | 5750834 | N/A | N/A | EFO | Emergency Forced Outage | Tier 2 | San Mateo | Peninsula | 37.6184 | -122.4499 | Sneath Lane-Half Moon Bay 60kV line STR ;000/006 | Clear | 3/0 AAC | Lat: 37.61838, Long: -122.449875
69 | 60 | ETL.7820 | 60181 | POTTER VALLEY-WILLITS | 2024 | 2024-12-13 20:27 | 45639.8521 | No | YES | No | 0.65139 | 938 | 2024-12-14 12:05 | 45640.5035 | F | Tree | Tree-failure | COND | Relayed - 12/13/24, 2027 Potter Valley-Willits 60kV line relayed and tested NG. No customer interruption. Weather storm. 2242 Line cleared to repair 3 phases of downed conductor between structures 009/002 and 009/003. Estimated return 12/14/24. 12/14/24, 1205 Potter Valley-Willits 60kV line returned to service after crew repaired three phases of downed conductor between structures 009/002 and 009/003. From trouble on 12/13/24 at 2027. | NONE | NORTH COAST | INT-18834 | 0 | 0 | 0 | 0 | 0 | 0 | 5750834 | B-C | 008/006 | AUTO | Single Mode | Tier 3 | Mendocino | Humboldt | 39.3737 | -123.2767 | Potter Valley-Willits 60kV line STR 009/002 | Storm | 1/0 ACSR | Lat: 39.373653, Long: -123.276743
69 | 60 | ETL.8365 | 60393 | GARBERVILLE-LAYTONVILLE | 2024 | 2024-12-13 20:48 | 45639.8667 | No | YES | No | 0.84931 | 1223 | 2024-12-14 17:11 | 45640.716 | F | Tree | Tree-failure | COND | Relayed - 12/13/24, 2048 Garberville-Laytonville 60kV line relayed and tested NG. No customer interruption. Weather storm. Line Patrol found a downed tree across 3 downed conductors between structures 23/8 and 23/9. Estimated return 12/14/24. 12/14/24, 0038 Garberville-Laytonville 60kV line (Garberville to Farmhouse JCT section) energized. 1711 Farmhouse JCT to Laytonville section returned to service after crew repaired three phases of downed conductors between structures 023/008 and 023/009. Line returned to service normal. From trouble on 12/13/24 at 2048. | NONE | NORTH COAST | INT-18835 | 0 | 0 | 0 | 0 | 0 | 0 | 5750834 | B-C | 023/009 | AUTO | Single Mode | Tier 2 | Mendocino | Humboldt | 39.6979 | -123.4809 | Garberville-Laytonville 60kV line STR 023/008 | Storm | 4/0 ACAR | Lat: 39.697891, Long: -123.480861
69 | 60 | ETL.6700 | 60063 | DEL MONTE-MONTEREY | 2024 | 2024-12-14 06:56 | 45640.2889 | YES | YES | YES | 1899-12-31 15:22 | 2362 | 2024-12-15 22:18 | 45641.9292 | F | Tree | Tree-failure | STRU | Relayed - 12/14/24, 0656 Del Monte-Monterey and Monterey-Viejo 60kV lines (HFRA) relayed and did not test as directed by operations. Line manually tested NG. Sustained interruption to Navy School. Weather storm. 1312 Line clear for crew to repaired broken structures 000/011, 000/012, 000/013 and 000/014. Estimated return 12/15/24. 12/15/24, 2218 Del Monte-Monterey and Monterey-Viejo 60kV lines returned to service restoring Navy School after crew repaired structure 000/010, replaced downed conductors, and replaced NG poles 000/011, 000/012, 000/013 and 000/014, damaged by the storm. From trouble on 12/14/24 at 0656. | NONE | SOUTH BAY AND CENTRAL COAST | INT-18843-1 | 1 | 0 | 0 | 0 | 0 | 0 | 5750834 | C-A | 000/012 | AUTO | Dependent Mode Initiating | Non-HFTD | Monterey | Central Coast | 36.6015 | -121.8568 | Del Monte-Monterey 60kV line STR 000/011 | Storm | 715 AAC | Lat: 36.601545, Long: -121.8568
69 | 60 | ETL.7180 | 60113 | IGNACIO-BOLINAS #2 | 2024 | 2024-12-14 09:35 | 45640.3993 | YES | YES | No | 1899-12-31 06:46 | 1846 | 2024-12-15 16:21 | 45641.6813 | F | Tree | Tree-failure | COND | Relayed - 12/14/24, 0935 Ignacio-Bolinas #2-60kV line relayed. Ignacio to Olema section tested OK. Bolinas to Olema section tested NG. Momentary to Tocaloma and Olema. Weather storm. 1552 Stafford JCT to Tocaloma JCT section cleared to repair one phase of down conductor at structure 013/155. Estimated return 12/15/24. 12/15/24, 1446 Ignacio-Bolinas #2-60kV line (Stafford JCT to Tocaloma JCT section) returned to service after crew replaced 2 NG insulators and repaired a downed conductor between structures 013/155 and 013/156, restoring transmission service to Tocaloma and Olema. 12/15/24, 1621 Ignacio-Bolinas #2-60kV line (Olema to Bolinas section) returned to service after crew repaired 1 phase of downed conductor between structures 021/240 and 021/241. From trouble on 12/14/24 at 0935. | NONE | BAY AREA | INT-18851 | [7 empty] | C-G | 016/253 | AUTO | Single Mode | Tier 3 | Marin | North Bay | 38.0074 | -122.7539 | Ignacio-Bolinas #2-60kV line STR 021/240 | Storm | 397.5 AAC | Lat: 38.007406, Long: -122.753899
115 | 115 | ETL.2580 | 10185 | MIDSUN-MIDWAY | 2024 | 2024-12-14 11:51 | 45640.4938 | YES | YES | YES | 1899-12-31 06:08 | 1808 | 2024-12-15 17:59 | 45641.7493 | F | Equipment Failure | Equip Fail-structure-line | STRU | Relayed - 12/14/24, 1151 Midsun-Midway 115kV line relayed and did not test as designed. Sustained interruption to Cymric Co-generator and Texaco North Midway. Weather storm. 2103 Midway to Cymric JCT section energized, restoring Cymric Co-generator. Cymric JCT to Midsun SW STA section cleared for crew to replace multiple downed poles. Estimated return 12/16/24. | 130114317 | CENTRAL VALLEY | INT-18863 | 2 | 0 | 0 | 0 | 0 | 0 | 5750834 | A-B-C | 016/181 | AUTO | Single Mode | Non-HFTD | Kern | Kern | 35.276 | -119.6248 | Midsun-Midway 115kV line near STR 016/181 | Storm | 715 AAC | Lat: 35.276019, Long: -119.624785
115 | 115 | ETL.1070 | 10013 | BELLOTA-RIVERBANK-MELONES SW STA | 2024 | 2024-12-15 05:28 | 45641.2278 | No | YES | No | 0.093056 | 134 | 2024-12-15 07:42 | 45641.3208 | F | Equipment Failure | Equip Fail-conductor | COND | Relayed - 12/15/24, 0528 Bellota-Riverbank-Melones SW STA 115kV line relayed and manually tested NG. Sustained interruption to Tulloch PH (online). Weather wind. 0742 Bellota-Riverbank-Melones SW STA 115kV line (Melones SW STA to Tulloch PH JCT section) returned to service after isolating fault location given at structure 013/003, restoring transmission service to Tulloch PH. 1900 Bellota-Riverbank-Melones SW STA 115kV line (Bellota to Tulloch section) returned to service, after crew replaced NG top phase conductor between structures 015/004 and 015/005. | NONE | CENTRAL VALLEY | INT-18865 | 0 | 0 | 0 | 0 | 0 | 0 | 5750834 | B-G | 013/003 | AUTO | Single Mode | Non-HFTD | Stanislaus | Yosemite | 37.8246 | -120.8904 | Bellota-Riverbank-Melones SW STA 115kV line STR 015/004 | Wind | 397.5 AAC | Lat: 37.824561, Long: -120.890414

## 3.6 WD RFW HFTD
County | inRFW | datetime | NWS_FireZone | RFW_ISSUED_local | RFW_EXPIRED_local
Tehama | 1 | 2017-10-08 13:11 | CAZ215 | 2017-10-08 11:00 | 2017-10-09 17:00
Sonoma | 1 | 2017-10-08 23:15 | CAZ507 | 2017-10-08 11:00 | 2017-10-10 05:00
Sonoma | 1 | 2017-10-09 02:01 | CAZ506 | 2017-10-08 11:00 | 2017-10-10 05:00
Marin | 1 | 2020-08-17 09:56 | CAZ505 | 2020-08-15 23:00 | 2020-08-17 11:00
Metric 3.6
Wire Down Events in HFTD on Red Flag Warning Days
[6 empty] | Year | WD Events | RFW OH CKT Mile-Days | WD / CKT Mile-Days
[6 empty] | 2013 | 0 | 24219.8893 | 0
[6 empty] | 2014 | 0 | 22115.1095 | 0
[6 empty] | 2015 | 0 | 8576.4054 | 0
[6 empty] | 2016 | 0 | 17315.6816 | 0
[6 empty] | 2017 | 3 | 55361.8287 | 5.4189e-05
[6 empty] | 2018 | 0 | 44290.6168 | 0
[6 empty] | 2019 | 0 | 36237.9327 | 0
[6 empty] | 2020 | 1 | 60675.43 | 1.6481e-05
[6 empty] | 2021 | 0 | 27334.9208 | 0
[6 empty] | 2022 | 0 | 13337 | 0
[6 empty] | 2023 | 0 | 9979.98 | 0
[6 empty] | 2024 | 0 | 22686 | 0
¹ 2022 RFW OH CKT Mile-Days was corrected from 16,578 in our March filing to 13,337 in our September 2023 filing. This correction only impacted the data file. It did not impact the narrative. The performance result was not impacted with this correction. It remains zero.
SOMs 3.6 | 0
¹

## RFW OH CKT Mile-Days
| 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024
| OH Tx | OH Tx | OH Tx | OH Tx | OH Tx | OH Tx | OH Tx | OH Tx | OH Tx | OH Tx | OH Tx | OH Tx
Tier2 | 16860.5621 | 16274.942 | 6818.5806 | 13218.3469 | 38017.0768 | 32991.4315 | 26812.6387 | 44686.1 | 22903.3895 | 11071.1 | 7435.97 | 16757
Tier3 | 7359.3272 | 5840.1675 | 1757.8248 | 4097.3346 | 17344.7519 | 11299.1853 | 9425.294 | 15989.33 | 4431.5313 | 2265.9 | 2544.01 | 5929
TOTAL | 24219.8893 | 22115.1095 | 8576.4054 | 17315.6816 | 55361.8287 | 44290.6168 | 36237.9327 | 60675.43 | 27334.9208 | 13337 | 9979.98 | 22686

## Cause Translation
PG&E Outage Cause Category-Details | ISO Outage Primary Cause Code | ISO Outage Primary Cause Code Description | PG&E and ISO Outage Secondary Cause Code | ISO Outage Secondary Cause Code Description |  | Cause Category (10 categories) | Cause Details | Outage Mode
Animal-bird | ANIM | Animal Contact | ARRS | Arrestor | 1 | Animal | Animal-bird | Common Mode
Animal-ground | ANIM | Animal Contact | AUX | Station auxiliary equip (e.g., CT, PT, CCVT) | 2 | Contamination | Animal-ground | Common Mode-initiating
Contamination-agriculture | CNTM | Contamination | BATT | Battery system | 3 | Disaster | Cntmn-agriculture | Dependent Mode
Contamination-animal waste | CNTM | Contamination | BUSH | Bushing | 4 | Equipment Failure | Cntmn-animal waste | Dependent Mode-initiating
Contamination-environmental | CNTM | Contamination | CB | Circuit breaker/Circuit switch | 5 | External Contact | Cntmn-environmental | Emergency Forced Outage
Contamination-industrial waste | CNTM | Contamination | COMM | Communication facility (no relay) | 6 | Other | Cntmn-industrial waste | Scheduled Outage
Disaster-earthquake | ND | Natural Disaster | COND | Conductor/shield wire/splice | 7 | Tree | Disaster-earthquake | Single Mode
Disaster-fire | FIRE | Fire | DISC | Disconnect | 8 | Unknown | Disaster-fire
Disaster-flood | ND | Natural Disaster | ENCR | Encroachment | 9 | Weather | Disaster-flood
Disaster-other | ND | Natural Disaster | GUYS | Guy/anchor | 10 | Work Procedure Error | Disaster-other
Equipment Failure-arrestor | SEQP | Substation Equipment Problem | HDWR | Hardware, fittings, accessories |  |  | Equip Fail-arrestor
Equipment Failure-bus | SEQP | Substation Equipment Problem | INSL | Insulator (station/line) |  |  | Equip Fail-bus
Equipment Failure-bushing | SEQP | Substation Equipment Problem | LS | Line switch |  |  | Equip Fail-bushing
Equipment Failure-ccvt | SEQP | Substation Equipment Problem | NONE | None |  |  | Equip Fail-ccvt
Equipment Failure-circuit breaker | CB | Circuit Breaker Trouble | REAC | Reactive device (e.g., capacitors, condenser) |  |  | Equip Fail-circuit breaker
Equipment Failure-conductor | LEQP | Line Equipment Problem | REG | Regulator |  |  | Equip Fail-conductor
Equipment Failure-connector/hardware | LEQP | Line Equipment Problem | RELY | Relay/communicatons for relay |  |  | Equip Fail-connector/ hardware
Equipment Failure-CT | SEQP | Substation Equipment Problem | STRU | Structure/foundation |  |  | Equip Fail-CT
Equipment Failure-insulator-line | LEQP | Line Equipment Problem | XFRM | dre56] |  |  | Equip Fail-insulator-line
Equipment Failure-insulator-station | SEQP | Substation Equipment Problem | UG | Underground transmission component |  |  | Equip Fail-insulator-station
Equipment Failure-other-line | LEQP | Line Equipment Problem | PROC | Work Procedure/Human Error |  |  | Equip Fail-other-line
Equipment Failure-other-station | SEQP | Substation Equipment Problem | PSPS | Public Safety Power Shutoff |  |  | Equip Fail-other-station
Equipment Failure-PT | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-PT
Equipment Failure-reactive equipment | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-reactive equipment
Equipment Failure-regulator/LTC | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-regulator/ LTC
Equipment Failure-relay | PROT | Protection |  |  |  |  | Equip Fail-relay
Equipment Failure-structure-line | LEQP | Line Equipment Problem |  |  |  |  | Equip Fail-structure-line
Equipment Failure-structure-station | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-structure-station
Equipment Failure-switch-line | LEQP | Line Equipment Problem |  |  |  |  | Equip Fail-switch-line
Equipment Failure-switch-station | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-switch-station
Equipment Failure-transformer | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-transformer
External Contact-aircraft | AIR | Aircraft |  |  |  |  | Ext Cont-aircraft
External Contact-car pole | VEH | Vehicle Contact |  |  |  |  | Ext Cont-car pole
External Contact-foreign object | OTHR | Other |  |  |  |  | Ext Cont-foreign object
External Contact-system disturbance | DIST | System Disturbance |  |  |  |  | Ext Cont-system disturbance
External Contact-vandalism | OTHR | Other |  |  |  |  | Ext Cont-vandalism
Other-customer/IPP caused | OTHR | Other |  |  |  |  | Other-customer/ IPP caused
Other-distribution caused | UC | Utility Contact |  |  |  |  | Other-distribution caused
Other-generation caused | GEN | Generation Trouble |  |  |  |  | Other-generation caused
Other-overload situation | DIST | System Disturbance |  |  |  |  | Other-load control
Other-safety clearance | OTHR | Other |  |  |  |  | Other-safety clearance
Scheduled-approved | SCHD | Scheduled Outage |  |  |  |  | Other-scheduled-approved
Scheduled-disapproved | LATE | Late Notification |  |  |  |  | Other-scheduled-disapproved
Scheduled-extended | LATE | Late Notification |  |  |  |  | Other-scheduled-extended
Tree-3rd party | OTHR | Other |  |  |  |  | Tree-3rd party
Tree-failure | VEGA | Vegetation |  |  |  |  | Tree-failure
Tree-tree contact | VEGA | Vegetation |  |  |  |  | Tree-tree contact
Unknown-no patrol conducted | UNKN | Unknown |  |  |  |  | Unk-no patrol conducted
Unknown-patrol found nothing | UNKN | Unknown |  |  |  |  | Unk-patrol found nothing
Weather-lightning | LIGT | Lightning |  |  |  |  | Weather-lightning
Weather-rain | WEAT | Weather |  |  |  |  | Weather-rain
Weather-snow/ice | WEAT | Weather |  |  |  |  | Weather-snow/ ice
Weather-wind | WEAT | Weather |  |  |  |  | Weather-wind
Work Procedure-design error | OPER | Operating error |  |  |  |  | Work Procedure-design error
Work Procedure-equipment incorrectly set | OPER | Operating error |  |  |  |  | Work Procedure-equip incorrectly set
Work Procedure-inattention or carelessness | OPER | Operating error |  |  |  |  | Work Procedure-inattention or carelessness
Work Procedure-miscommunications or unclear expectations | OPER | Operating error |  |  |  |  | Work Procedure-miscommunications or unclear expectations
Work Procedure-not following prescribed procedures | OPER | Operating error |  |  |  |  | Work Procedure-not following prescribed procedures
SGS CAUSE CODE CATEGORIES
Description | SGS Category No | Examples
Equipment | 1 | Terminal equipment: breakers, switches, transformers, cap bks, busses, etc. ("inside the fence")
System Protection | 2 | Relay equipment failure, misoperation, incorrect settings or scheme, "over-reaching", communications
Lines | 3 | Failed hardware "outside the fence"; structures, conductors, cable cable hardware, insulators, static wire
Weather, other than lightning | 4 | Severe weather conditions, usually beyond design capabilities of facilities, exclusive of lightning
Lightning Only | 5 | Verified or suspected outages resulting from lightning
Unknown | 6 | Diligent attempts to verify cause were unsuccessful
Vegetation | 7 | Vegetation and trees which directly cause an outage
External | 8 | Causes outside control of ET system (e.g., foreign utilities, customer equip, generation, UF, instability)
Other | 9 | Operating errors, contractors, dig-ins, loggers, birds, animals, public damage, contamination, autos
Excludable Outage, Natural Causes Only | 10 | Major events (extreme), system disturbances associated w/ cascading
Excludable Outage, System Causes Only | 11 | Operational Outage for safety, voltage control or stability, System Disturbances, Unusual Configurations
Human Factors | 12 | WPE/ HPE

## ILIS Causes
Basic Cause Field | Supplemental Cause Field | [13 empty] | Equipment Condition
3rd Party* 00 | Aircraft | Aircraft-Crop Dusting | Contact with High Voltage, 3rd Party | Customer Equipment | Dig In, 3rd Party | Fire, house or bldg | Gun Shot | Kite | Metallic Balloon | Thrown Object | Vandalism | Vehicle | Other | tree - cutting 3rd party | Annealed
Animal* 02 | Bird Found | Other | Squirrel | [11 empty] | Arcing
Company Initiated* 05 | Construction Activity/equip, company | Contact with High Voltage, company | Coordination Failure | Dig in, company | Improper Construction | Insulator washing | Operating error | Other Circuits | Personnel, company | Planned, capital | Planned, customer | Planned, maintenance | Rotating Outage | Return circuit normal | Bent or Twisted
Equipment Failure/Involved* 03 | Electrical Overload | Fire, pole | overhead | Substation | underground | [9 empty] | Blown / exploded
Vegatation* 01 | Other Ground Vegetation | Tree - bark fell into line | Tree - branch fell on line | Tree - cutting PG&E contractor | Tree - fell into line | Tree - grew into line | Tree - palm frond fell into line | [7 empty] | Broken
Unknown 04 | Patrol - Found Nothing | Patrol - Not Conducted | [12 empty] | Broken, wire on ground
(Environmental)External influence * 06 | Earthquake | Fire, forest/grass | Flood/ errosion | Ice or snow | Lightning | water | [8 empty] | Burned Open
Burned / flashed
* These type outages require "Equipment Involved" & "Equipment Condition" field be populated. See available selection below | [14 empty] | Contaminated
Deteriorated
Equipment Involved | Anchor or Guy | Booster | Bus | Bushing | PT/CCVT | CT/PT | Capacitor | Circuit Breaker | Conductor, Overhead | Conductor, Underground | Connector or Splice (OH) | Connector or Splice (UG) | Crossarm, Steel |  | Leaking
See also next tabs | Crossarm, Wood | Customer Equipment | Cutout, Fused, Distribution | Cutout fuse holder | Elbow | Footings, Tower or Pole | Fuse | Insulator | Interrupter | Jumper | Lightning Arrestor | Manhole, primary box | Metering Equipment |  | Malfunctioning
| Other | PGs, Kearneys | Pole - Tower, steel | Pole - Wood | Pothead or Cable Termination | Reactive Equipment | Recloser | Regulator | Regulator, LTC substation | Relay, substation | Riser | Secondary | Sectionalizer |  | Normal
| Service Conductor | Splice Box | Stepdown | Street Light Equipment | Switch | Transformer | Transformer, Station Bank, Power | Woodpin | Generator | SCADA |  |  |  |  | Together
Equipment Condition | Annealed | Arcing | Bent or Twisted | Blown / exploded | Broken | Broken, wire on ground | Burned Open | Burned / flashed | Contaminated | Deteriorated | Leaking | Malfunctioning | Normal
see also next tabs | On Ground | Together |  |  |  | Broken, wire on object
Outage Level | Distribution Circuit | Substation Distribution | Substation Transmission | Transmission Line | Transformer Only | Generation | secondary | service
[7 empty] | FAS only | FAS only

## 2024 HFTD Miles
TLINE_NAME | RATEDKV | SAP_FL | OWNER_STATUS | STATUS | TLINEMILES | T3MILES | T2MILES | Z1MILES | T1MILES | Exclude | 2024 ALL | 2024 Exclude | 2024 HFTD Miles
230KV CAP BANK TIE LINE | 230 | 0 |  | ACT | 0.27 |  |  |  | 0.27 |  | 5441.88 | 39.6 | 5402.28
7TH STANDARD-KERN | 115 | ETL.1981 |  | ACT | 6.76 |  |  |  | 6.76
ADOBE SW STA #1 TAP | 115 | ETL.1145 |  | ACT | 14.25 |  |  |  | 14.25
AEC SITE #1 TAP | 115 | ETL.3982 |  | ACT | 1.6 |  |  |  | 1.6
AEC SITE #2 TAP | 115 | ETL.3983 |  | ACT | 2.16 |  |  |  | 2.16
AERA ENERGY TAP | 70 | ETL.7727 |  | ACT | 0.35 |  |  |  | 0.35
AIR PRODUCTS TAP | 115 | ETL.2314 |  | ACT | 0.29 |  |  |  | 0.29
ALMADEN-LOS GATOS | 60 | ETL.6825 |  | ACT | 6.35 |  |  |  | 6.35
ALMENDRA JCT-NICOLAUS | 60 | ETL.6150 |  | ACT | 24.9 |  |  |  | 24.9
AMERIGAS TAP | 115 | ETL.1591 |  | ACT | 0.49 |  |  |  | 0.49
AMES DISTRIBUTION-AMES | 115 | ETL.2482 |  | ACT | 0.1 |  |  |  | 0.1
AMES-MOUNTAIN VIEW | 115 | ETL.1174 |  | ACT | 2.57 |  |  |  | 2.57
AMES-WHISMAN | 115 | ETL.4150 |  | ACT | 0.97 |  |  |  | 0.97
AMFOR TAP | 60 | ETL.8241 |  | ACT | 1.04 |  |  |  | 1.04
ANTELOPE TAP | 70 | ETL.8442 |  | ACT | 4.28 |  |  |  | 4.28
APPLE HILL #1 TAP | 115 | ETL.1531 |  | ACT | 1.42 |  | 1.42 |  | 0
APPLE HILL #2 TAP | 115 | ETL.1541 |  | ACT | 1.43 |  | 1.43 |  | 0
APPLIED MATERIALS-BRITTON | 115 | ETL.4300 |  | ACT | 0.47 |  |  |  | 0.47
ARBUCKLE TAP | 60 | ETL.6591 |  | ACT | 0.82 |  |  |  | 0.82
ARBURUA TAP | 70 | ETL.8932 |  | ACT | 3.57 |  |  |  | 3.57
ARCATA-HUMBOLDT | 60 | ETL.7110 |  | ACT | 7.28 |  |  |  | 7.28
ARCO-CARNERAS | 70 | ETL.8430 |  | ACT | 18.02 |  |  |  | 18.02
ARCO-CHOLAME | 70 | ETL.8440 |  | ACT | 26.74 |  | 4.8 |  | 21.94
ARCO-MIDWAY | 230 | ETL.4320 |  | ACT | 43.36 |  |  |  | 43.36
ARCO-POLONIO PASS PP | 70 | ETL.8450 |  | ACT | 21.27 |  | 7.26 |  | 14.01
ARCO-TULARE LAKE | 70 | ETL.8460 |  | ACT | 16.11 |  |  |  | 16.11
ARCO-TWISSELMAN | 70 | ETL.8470 |  | ACT | 6.46 |  |  |  | 6.46
ARMSTRONG TAP | 70 | ETL.8722 |  | ACT | 0.44 |  |  |  | 0.44
ARVIN EDISON TAP | 115 | ETL.4141 |  | ACT | 1.06 |  |  |  | 1.06
ATASCADERO-CAYUCOS | 70 | ETL.8480 |  | ACT | 11.79 | 5.36 | 3.59 |  | 2.84
ATASCADERO-SAN LUIS OBISPO | 70 | ETL.8490 |  | ACT | 15.52 | 3.3 | 7.86 |  | 4.36
ATLANTIC-GOLD HILL | 230 | ETL.4330 |  | ACT | 11.11 |  |  |  | 11.11
ATLANTIC-PLEASANT GROVE #1 | 115 | ETL.6190 |  | ACT | 5.33 |  |  |  | 5.33
ATLANTIC-PLEASANT GROVE #2 | 115 | ETL.9420 |  | ACT | 5.36 |  |  |  | 5.36
ATWATER-CRESSEY | 115 | ETL.1033 |  | ACT | 5.91 |  |  |  | 5.91
ATWATER-EL CAPITAN | 115 | ETL.1020 |  | ACT | 7.31 |  |  |  | 7.31
ATWATER-LIVINGSTON-MERCED | 115 | ETL.1030 |  | ACT | 24.26 |  |  |  | 24.26
AUBERRY TAP | 70 | ETL.9331 |  | ACT | 2.28 |  | 2.28 |  | 0
AUBURN TAP | 60 | ETL.6992 |  | ACT | 0.75 |  |  |  | 0.75
AVENAL TAP | 70 | ETL.8702 |  | ACT | 5.4 |  |  |  | 5.4
BADGER CREEK (PSE) TAP | 115 | ETL.1932 |  | ACT | 1.07 |  |  |  | 1.07
BADGER HILL TAP | 70 | ETL.8452 |  | ACT | 1.56 |  |  |  | 1.56
BAHIA-MORAGA | 230 | ETL.4340 |  | ACT | 26.92 | 4.3 | 12.25 |  | 10.37
BAIR-BELMONT | 115 | ETL.1040 |  | ACT | 3.64 |  |  |  | 3.64
BAIR-COOLEY LANDING #1 | 60 | ETL.6200 |  | ACT | 5.56 |  |  |  | 5.56
BAIR-COOLEY LANDING #2 | 60 | ETL.6210 |  | ACT | 5.6 |  |  |  | 5.6
BAKERSFIELD #2 TAP | 230 | ETL.5171 |  | ACT | 6.97 |  |  |  | 6.97
BALCH-MCCALL | 230 | ETL.4350 |  | ACT | 39.76 |  | 20.2 |  | 19.56
BALCH-SANGER | 115 | ETL.1050 |  | ACT | 35.62 |  | 19.85 |  | 15.77
BARKER SLOUGH TAP | 115 | ETL.1141 |  | ACT | 1.63 |  |  |  | 1.63
BARTON-AIRWAYS-SANGER | 115 | ETL.1060 |  | ACT | 11.57 |  |  |  | 11.57
BASALT #1 TAP | 60 | ETL.8181 |  | ACT | 1.18 |  |  |  | 1.18
BEALE AFB (WAPA) #1 TAP | 60 | ETL.8001 |  | ACT | 0.11 |  | 0.11 |  | 0
BEALE AFB (WAPA) #2 TAP | 60 | ETL.7971 |  | ACT | 0.14 |  | 0.14 |  | 0
BEAR CANYON TAP | 230 | ETL.1182 |  | ACT | 0.02 | 0.02 |  |  | 0
BEAR MTN TAP | 115 | ETL.4131 |  | ACT | 1.27 |  |  |  | 1.27
BEARDSLEY TAP | 115 | ETL.1401 |  | ACT | 2.2 | 2.15 | 0.02 |  | 0.03
BELDEN TAP | 230 | ETL.4441 |  | ACT | 0.02 |  | 0.02 |  | 0
BELL-PLACER | 115 | ETL.4395 |  | ACT | 7.94 |  | 2.86 |  | 5.08
BELLE HAVEN #1 TAP | 60 | ETL.6201 |  | ACT | 0.42 |  |  |  | 0.42
BELLE HAVEN #2 TAP | 60 | ETL.6211 |  | ACT | 0.41 |  |  |  | 0.41
BELLOTA-COTTLE | 230 | ETL.4360 |  | ACT | 19.86 |  |  |  | 19.86
BELLOTA-RIVERBANK | 115 | ETL.3480 |  | ACT | 18.87 |  |  |  | 18.87
BELLOTA-RIVERBANK-MELONES SW STA | 115 | ETL.1070 |  | ACT | 44.65 |  | 11.19 |  | 33.46
BELLOTA-TESLA #2 | 230 | ETL.4370 |  | ACT | 37.94 |  |  |  | 37.94
BELLOTA-WARNERVILLE | 230 | ETL.4380 |  | ACT | 22.47 |  |  |  | 22.47
BELLOTA-WEBER | 230 | ETL.4390 |  | ACT | 14.26 |  |  |  | 14.26
BELRIDGE TAP | 115 | ETL.2631 |  | ACT | 6.94 |  |  |  | 6.94
BERRENDA A TAP | 70 | ETL.8441 |  | ACT | 2.3 |  |  |  | 2.3
BERRENDA C TAP | 70 | ETL.8443 |  | ACT | 1.87 |  |  |  | 1.87
BIOLA-GLASS-MADERA | 70 | ETL.9350 |  | ACT | 18.8 |  |  |  | 18.8
BIRDS LANDING SW STA-CONTRA COSTA PP | 230 | ETL.5830 |  | ACT | 10.2 |  |  |  | 10.2
BIRDS LANDING SW STA-CONTRA COSTA SUB | 230 | ETL.6161 |  | ACT | 9.46 |  |  |  | 9.46
BIRDS LANDING SW STA-RUSSELL | 230 | ETL.6602 |  | ACT | 0.11 |  |  |  | 0.11
BIRDS LANDING SW STA-SHILOH | 230 | ETL.1413 |  | ACT | 0.11 |  |  |  | 0.11
BIXLER TAP | 60 | ETL.7056 |  | ACT | 0.55 |  |  |  | 0.55
BLACK TAP | 230 | ETL.5431 | POWERGEN | ACT | 0.51 |  | 0.51 |  | 0
BLUE CHIP MILLING TAP | 60 | ETL.6802 |  | ACT | 0.42 |  |  |  | 0.42
BLUE LAKE TAP | 60 | ETL.6801 |  | ACT | 3.7 |  |  |  | 3.7
BOGUE-RIO OSO | 115 | ETL.1100 |  | ACT | 21.24 |  |  |  | 21.24
BOLLMAN #1 TAP | 115 | ETL.3321 |  | ACT | 2.14 |  |  |  | 2.14
BOLLMAN #2 TAP | 115 | ETL.3331 |  | ACT | 2.19 |  |  |  | 2.19
BOLTHOUSE FARMS TAP | 115 | ETL.4132 |  | ACT | 0.11 |  |  |  | 0.11
BONITA TAP | 70 | ETL.9352 |  | ACT | 3.03 |  |  |  | 3.03
BORDEN-COPPERMINE | 70 | ETL.8500 |  | ACT | 19.92 |  |  |  | 19.92
BORDEN-GLASS | 70 | ETL.8510 |  | ACT | 6.64 |  |  |  | 6.64
BORDEN-GREGG #1 | 230 | ETL.1082 |  | ACT | 6.21 |  |  |  | 6.21
BORDEN-GREGG #2 | 230 | ETL.4400 |  | ACT | 6.21 |  |  |  | 6.21
BORDEN-LOTUS PV | 70 | ETL.1122 |  | ACT | 0.16 |  |  |  | 0.16
BORDEN-MADERA #1 | 70 | ETL.8710 |  | ACT | 4.92 |  |  |  | 4.92
BORDEN-MADERA #2 | 70 | ETL.8520 |  | ACT | 5.8 |  |  |  | 5.8
BOTTLE ROCK TAP D.W.R. | 230 | ETL.4771 |  | ACT | 1.07 | 1.07 |  |  | 0
BRENTWOOD-KELSO | 230 | ETL.4410 |  | ACT | 16.41 |  | 5.2 |  | 11.21
BRICEBURG JCT-MARIPOSA TAP | 70 | ETL.8651 |  | ACT | 7.78 |  | 7.78 |  | 0
BRIDGEVILLE-COTTONWOOD | 115 | ETL.1110 |  | ACT | 86.08 | 1 | 79.04 |  | 6.04
BRIDGEVILLE-GARBERVILLE | 60 | ETL.6220 |  | ACT | 36.15 | 9.8 | 7.13 |  | 19.22
BRIGHTON-BELLOTA | 230 | ETL.4420 |  | ACT | 42.51 |  |  |  | 42.51
BRIGHTON-DAVIS | 115 | ETL.1140 |  | ACT | 42.72 |  |  |  | 42.72
BRIGHTON-DAVIS | 115 | ETL.1140 |  | IDL | 17.36 |  |  |  | 17.36
BRIGHTON-GRAND ISLAND #1 | 115 | ETL.1150 |  | ACT | 24.99 |  |  |  | 24.99
BRIGHTON-GRAND ISLAND #1 | 115 | ETL.1150 |  | IDL | 0.14 |  |  |  | 0.14
BRIGHTON-GRAND ISLAND #2 | 115 | ETL.1160 |  | ACT | 25.04 |  |  |  | 25.04
BRIGHTON-GRAND ISLAND #2 | 115 | ETL.1160 |  | IDL | 0.14 |  |  |  | 0.14
BRIGHTON-OLEUM JCT | 0 | ETL.1162 |  | IDL | 1.5 |  | 0.8 |  | 0.7
BRIONES TAP | 60 | ETL.7055 |  | ACT | 6.99 | 0.22 | 4.28 |  | 2.49
BRITTON-MONTA VISTA | 115 | ETL.1170 |  | ACT | 7.17 |  |  |  | 7.17
BRUNSWICK #1 TAP | 115 | ETL.1422 |  | ACT | 6.98 | 5.95 | 0.61 |  | 0.42
BRUNSWICK #2 TAP | 115 | ETL.1431 |  | ACT | 7 | 5.97 | 0.63 |  | 0.4
BUCKS CREEK-ROCK CREEK-CRESTA | 230 | ETL.4430 |  | ACT | 9.37 | 0.07 | 9.3 |  | 0
BUELLTON TAP | 115 | ETL.1201 |  | ACT | 1.75 |  | 1.39 |  | 0.36
BUENA VISTA BIOMASS POWER TAP | 60 | ETL.8252 |  | ACT | 1.01 |  | 0.32 |  | 0.69
BUENA VISTA PUMPING PLANT #1 TAP | 230 | ETL.5191 |  | ACT | 1.18 |  |  |  | 1.18
BUENA VISTA PUMPING PLANT #2 TAP | 230 | ETL.5201 |  | ACT | 1.21 |  |  |  | 1.21
BURNEY FOREST PRODUCTS TAP | 230 | ETL.5391 |  | ACT | 0.04 |  |  |  | 0.04
BURNEY TAP | 60 | ETL.7041 |  | ACT | 1.07 |  |  |  | 1.07
BURNS-LONE STAR #1 | 60 | ETL.6230 |  | ACT | 5.44 | 3.23 | 2.21 |  | 0
BURNS-LONE STAR #2 | 60 | ETL.6240 |  | ACT | 6.31 | 4.9 | 1.4 |  | 0.01
BUTTE VALLEY-CARIBOU | 115 | ETL.1180 | POWERGEN | ACT | 7.44 |  | 7.09 |  | 0.35
BUTTE-CHICO #1 | 60 | ETL.6250 |  | ACT | 0.79 |  |  |  | 0.79
BUTTE-CHICO #2 | 60 | ETL.6260 |  | ACT | 0.74 |  |  |  | 0.74
BUTTE-ESQUON | 60 | ETL.6270 |  | ACT | 9.87 |  |  |  | 9.87
BUTTE-SYCAMORE CREEK | 115 | ETL.1190 |  | ACT | 18.14 |  |  |  | 18.14
Bellota-North Central Valley | 115 | ETL.1374 |  | ACT | 0.03 |  |  |  | 0.03
CABRILLO-SANTA YNEZ SW STA | 115 | ETL.1200 |  | ACT | 14.59 |  | 13.18 |  | 1.41
CACHE SLOUGH TAP | 60 | ETL.6741 |  | ACT | 6.82 |  |  |  | 6.82
CADET TAP | 70 | ETL.9232 |  | ACT | 0.06 |  |  |  | 0.06
CAL PEAK-VACA | 115 | ETL.4230 |  | ACT | 0.11 |  |  |  | 0.11
CAL WATER TAP | 115 | ETL.3951 |  | ACT | 2.15 |  |  |  | 2.15
CALIENTE SW STA-MIDWAY #1 | 230 | ETL.5216 |  | ACT | 27.17 |  |  |  | 27.17
CALIENTE SW STA-MIDWAY #2 | 230 | ETL.5226 |  | ACT | 27.16 |  |  |  | 27.16
CALIFORNIA AVE-KEARNEY | 70 | ETL.8530 |  | IDL | 3.21 |  |  |  | 3.21
CALIFORNIA AVE-MCCALL | 115 | ETL.2360 |  | ACT | 23.66 |  |  |  | 23.66
CALIFORNIA FLATS SW STA-GATES | 230 | ETL.5281 |  | ACT | 22.57 |  | 1.5 |  | 21.07
CALLENDER SW STA-MESA | 115 | ETL.1210 |  | ACT | 13.76 |  | 5.61 |  | 8.15
CALPINE-WEST FORD FLAT | 230 | ETL.1183 |  | ACT | 0.05 | 0.05 |  |  | 0
CALVO TAP | 60 | ETL.7251 |  | ACT | 0.54 |  |  |  | 0.54
CAMANCHE PUMPING PLANT TAP | 230 | ETL.1230 |  | ACT | 0.45 |  |  |  | 0.45
CAMANCHE TAP | 115 | ETL.1691 |  | ACT | 6.71 |  |  |  | 6.71
CAMDEN-KINGSBURG | 70 | ETL.8653 |  | ACT | 14.93 |  |  |  | 14.93
CAMP EVERS-PAUL SWEET | 115 | ETL.1220 |  | ACT | 5.22 | 4.59 |  |  | 0.63
CANANDAIGUA WINERY TAP | 70 | ETL.9351 |  | ACT | 0.29 |  |  |  | 0.29
CANTUA TAP | 115 | ETL.3251 |  | ACT | 1.83 |  |  |  | 1.83
CAPE HORN TAP | 60 | ETL.6761 |  | ACT | 0.31 |  | 0.31 |  | 0
CARBERRY SW STA-ROUND MTN | 230 | ETL.5410 |  | ACT | 12.61 | 0.25 | 12.36 |  | 0
CARBONA #2 TAP | 60 | ETL.7233 |  | ACT | 5.6 |  |  |  | 5.6
CARIBOU #2 | 60 | ETL.6280 |  | ACT | 30.62 |  | 27.77 |  | 2.85
CARIBOU-PALERMO | 115 | ETL.3190 |  | IDL | 1.48 |  | 1.09 |  | 0.39
CARIBOU-PLUMAS JCT | 60 | ETL.6290 |  | ACT | 21.26 |  | 16.4 |  | 4.86
CARIBOU-TABLE MTN | 230 | ETL.4440 |  | ACT | 54.34 | 9.09 | 39.35 |  | 5.9
CARIBOU-WESTWOOD | 60 | ETL.6300 |  | ACT | 20.99 |  | 20 |  | 0.99
CARIBOU-WESTWOOD | 60 | ETL.6300 |  | IDL | 0.06 |  |  |  | 0.06
CARNATION TAP | 70 | ETL.8901 |  | ACT | 0.54 |  |  |  | 0.54
CARNERAS-TAFT | 70 | ETL.8540 |  | ACT | 34.8 |  |  |  | 34.8
CARQUINEZ #1 TAP | 115 | ETL.1831 |  | ACT | 0.51 |  |  |  | 0.51
CARQUINEZ #2 TAP | 115 | ETL.1841 |  | ACT | 0.52 |  |  |  | 0.52
CARRIZO PLAINS TAP | 115 | ETL.3961 |  | ACT | 0.04 |  |  |  | 0.04
CARUTHERS-LEMOORE NAS-CAMDEN | 70 | ETL.8550 |  | ACT | 25.1 |  |  |  | 25.1
CASCADE-BENTON-DESCHUTES | 60 | ETL.6310 |  | ACT | 15.97 |  | 9.56 |  | 6.41
CASCADE-COTTONWOOD | 115 | ETL.1240 |  | ACT | 19.47 |  | 12.18 |  | 7.29
CASTAIC TAP | 70 | ETL.9253 |  | ACT | 0.02 |  | 0.02 |  | 0
CASTRO VALLEY-NEWARK | 230 | ETL.4450 |  | ACT | 22.71 | 5.6 | 5.96 |  | 11.15
CAWELO B TAP | 70 | ETL.8871 |  | ACT | 0.4 |  |  |  | 0.4
CAWELO C TAP | 115 | ETL.2122 |  | ACT | 1.33 |  |  |  | 1.33
CAYUCOS-CAMBRIA | 70 | ETL.8560 |  | ACT | 17.73 |  | 7.7 |  | 10.03
CELERON TAP | 70 | ETL.8541 |  | ACT | 0.04 |  |  |  | 0.04
CENTERVILLE-TABLE MTN | 60 | ETL.6320 |  | ACT | 21.51 | 4.1 | 3.81 |  | 13.6
CENTERVILLE-TABLE MTN-OROVILLE | 60 | ETL.6330 |  | ACT | 26.1 | 3.85 | 6.34 |  | 15.91
CERTAINTEED TAP | 115 | ETL.2111 |  | ACT | 2.52 |  |  |  | 2.52
CHARCA-FAMOSO | 115 | ETL.2621 |  | ACT | 7.15 |  |  |  | 7.15
CHCF TAP | 115 | ETL.7011 |  | ACT | 3 |  |  |  | 3
CHENEY #1 TAP | 115 | ETL.3231 |  | ACT | 4.1 |  |  |  | 4.1
CHENEY #2 TAP | 115 | ETL.3261 |  | ACT | 1.97 |  |  |  | 1.97
CHEVRON (LOST HILLS) TAP | 70 | ETL.8472 |  | ACT | 14.75 |  |  |  | 14.75
CHEVRON PIPELINE KETTLEMAN TAP | 70 | ETL.8703 |  | ACT | 1.17 |  |  |  | 1.17
CHINESE CAMP (ULTRA POWER) TAP | 115 | ETL.2392 |  | ACT | 2.1 |  | 1.54 |  | 0.56
CHOWCHILLA #1 TAP | 115 | ETL.2112 |  | ACT | 1.24 |  |  |  | 1.24
CHOWCHILLA-KERCKHOFF | 115 | ETL.1250 |  | ACT | 42.52 |  | 9.5 |  | 33.02
CHRISTIE-FRANKLIN #1 | 60 | ETL.6350 |  | ACT | 3.45 |  | 1.85 |  | 1.6
CHRISTIE-FRANKLIN #1 | 60 | ETL.6350 |  | IDL | 1.56 |  |  |  | 1.56
CHRISTIE-FRANKLIN #2 | 60 | ETL.6360 |  | ACT | 3.45 |  | 1.84 |  | 1.61
CHRISTIE-FRANKLIN #2 (12KV) | 60 | ETL.6360 |  | IDL | 1.62 |  |  |  | 1.62
CHRISTIE-SOBRANTE | 115 | ETL.1260 |  | ACT | 7.84 |  | 7.74 |  | 0.1
CHRISTIE-WILLOW PASS | 60 | ETL.6370 |  | ACT | 15.93 |  | 3.83 |  | 12.1
CHUALAR TAP | 60 | ETL.8012 |  | IDL | 1.47 |  |  |  | 1.47
CISCO GROVE TAP | 60 | ETL.8061 |  | ACT | 0.34 |  |  |  | 0.34
CITY #1 TAP | 115 | ETL.1382 |  | ACT | 0.07 |  |  |  | 0.07
CITY #2 TAP | 115 | ETL.1371 |  | ACT | 1.37 |  |  |  | 1.37
CLAY-MARTEL | 60 | ETL.8250 |  | ACT | 16.98 |  | 14.52 |  | 2.46
CLAYTON-MEADOW LANE | 115 | ETL.1270 |  | ACT | 7.06 |  |  |  | 7.06
CLEAR LAKE-HOPLAND | 60 | ETL.6390 |  | ACT | 11.53 |  | 7.33 |  | 4.2
CLEAR LAKE-KONOCTI | 60 | ETL.6852 |  | ACT | 10.99 |  | 4.94 |  | 6.05
CLOVER CREEK TAP | 60 | ETL.7291 |  | ACT | 0.02 | 0.02 |  |  | 0
COALINGA #1-COALINGA #2 | 70 | ETL.8570 |  | ACT | 8.61 |  |  |  | 8.61
COALINGA #1-SAN MIGUEL | 70 | ETL.8580 |  | ACT | 38.01 |  | 17.45 |  | 20.56
COALINGA COGEN TAP | 70 | ETL.8571 |  | ACT | 4.91 |  |  |  | 4.91
COBURN-BASIC ENERGY | 60 | ETL.6400 |  | ACT | 3.39 |  |  |  | 3.39
COBURN-LAS AGUILAS SW STA | 230 | ETL.4460 |  | ACT | 63.97 |  | 41.16 |  | 22.81
COBURN-OIL FIELDS #1 | 60 | ETL.6410 |  | ACT | 29.46 |  |  |  | 29.46
COBURN-OIL FIELDS #2 | 60 | ETL.6420 |  | ACT | 31.05 |  |  |  | 31.05
COGENERATION NATIONAL TAP | 60 | ETL.8323 |  | ACT | 0.56 |  |  |  | 0.56
COLEMAN HATCHERY TAP | 60 | ETL.8428 |  | ACT | 0.56 |  |  |  | 0.56
COLEMAN-COTTONWOOD | 60 | ETL.6430 |  | ACT | 8.58 |  | 1.11 |  | 7.47
COLEMAN-RED BLUFF | 60 | ETL.6440 |  | ACT | 48.31 |  | 20.25 |  | 28.06
COLEMAN-SOUTH | 60 | ETL.6450 |  | ACT | 13.39 |  | 13.39 |  | 0
COLES LEVEE TAP | 115 | ETL.2593 |  | ACT | 0.22 |  |  |  | 0.22
COLGATE PH-COLGATE SW STA | 60 | ETL.6460 |  | ACT | 0.19 |  | 0.19 |  | 0
COLGATE-ALLEGHANY | 60 | ETL.6470 |  | ACT | 24.53 | 19.92 | 4.61 |  | 0
COLGATE-CHALLENGE | 60 | ETL.6480 |  | ACT | 13.04 | 11.62 | 1.43 |  | -0.01
COLGATE-GRASS VALLEY | 60 | ETL.6490 |  | ACT | 13.17 | 1.87 | 10.04 |  | 1.26
COLGATE-PALERMO | 60 | ETL.6500 |  | ACT | 22.65 |  | 21.72 |  | 0.93
COLGATE-RIO OSO | 230 | ETL.5900 |  | ACT | 40.89 |  | 11.86 |  | 29.03
COLGATE-SMARTVILLE #1 | 60 | ETL.6510 |  | ACT | 11.26 |  | 11.26 |  | 0
COLGATE-SMARTVILLE #2 | 60 | ETL.6520 |  | ACT | 11.19 |  | 11.19 |  | 0
COLLINS PINE TAP | 60 | ETL.7001 |  | ACT | 1 |  | 0.08 |  | 0.92
COLUMBIA SOLAR 115kV TAP | 115 | ETL.3301 |  | ACT | 0.51 |  |  |  | 0.51
COLUMBUS-MAGUNDEN | 115 | ETL.1233 |  | ACT | 3.69 |  |  |  | 3.69
COLUSA JCT #1 | 60 | ETL.8390 |  | ACT | 16.98 |  |  |  | 16.98
CONTRA COSTA #1 | 115 | ETL.1280 |  | ACT | 11.15 |  |  |  | 11.15
CONTRA COSTA #2 | 115 | ETL.1290 |  | ACT | 1.43 |  |  |  | 1.43
CONTRA COSTA PP-CONTRA COSTA SUB | 230 | ETL.4470 |  | ACT | 1.89 |  |  |  | 1.89
CONTRA COSTA-BALFOUR | 60 | ETL.8420 |  | ACT | 11.54 |  |  |  | 11.54
CONTRA COSTA-BRENTWOOD | 230 | ETL.4480 |  | ACT | 10.06 |  |  |  | 10.06
CONTRA COSTA-DELTA SWITCHYARD | 230 | ETL.4490 |  | ACT | 18.46 |  | 5.19 |  | 13.27
CONTRA COSTA-DU PONT | 60 | ETL.6530 |  | ACT | 2.14 |  |  |  | 2.14
CONTRA COSTA-LAS POSITAS | 230 | ETL.4510 |  | ACT | 23.83 | 0.88 | 10.98 |  | 11.97
CONTRA COSTA-LONE TREE | 230 | ETL.4535 |  | ACT | 5.61 |  |  |  | 5.61
CONTRA COSTA-MORAGA #1 | 230 | ETL.5452 |  | ACT | 26.76 | 4.3 | 11.36 |  | 11.1
CONTRA COSTA-MORAGA #1 | 230 | ETL.5452 |  | IDL | 0.13 |  |  |  | 0.13
CONTRA COSTA-MORAGA #2 | 230 | ETL.5453 |  | ACT | 26.84 | 4.38 | 11.32 |  | 11.14
CONTRA COSTA-PITTSBURG | 60 | ETL.6540 |  | ACT | 6.28 |  |  |  | 6.28
CONTRA COSTA-SHELL CHEMICAL#1(21KV) | 60 | ETL.6550 |  | IDL | 9.55 |  |  |  | 9.55
COOLEY LANDING-LOS ALTOS | 60 | ETL.6560 |  | ACT | 14.93 |  |  |  | 14.93
COOLEY LANDING-LOS ALTOS (I2KV) | 60 | ETL.6560 |  | IDL | 1.4 |  |  |  | 1.4
COOLEY LANDING-PALO ALTO | 115 | ETL.1300 |  | ACT | 2.72 |  |  |  | 2.72
COOLEY LANDING-STANFORD | 60 | ETL.6570 |  | ACT | 6.02 |  |  |  | 6.02
COPPERMINE-TIVY VALLEY | 70 | ETL.8590 |  | ACT | 24.01 |  | 0.89 |  | 23.12
COPUS-OLD RIVER | 70 | ETL.8970 |  | ACT | 19.62 |  |  |  | 19.62
CORCORAN-ANGIOLA | 70 | ETL.8600 |  | ACT | 8.95 |  |  |  | 8.95
CORCORAN-GUERNSEY | 70 | ETL.9360 |  | ACT | 13.49 |  |  |  | 13.49
CORCORAN-OLIVE SW STA | 115 | ETL.1310 |  | ACT | 18.43 |  |  |  | 18.43
CORCORAN-OLIVE SW STA | 115 | ETL.1310 |  | IDL | 0.02 |  |  |  | 0.02
CORDELIA #1 TAP | 60 | ETL.8182 |  | ACT | 7.69 |  | 4.56 |  | 3.13
CORDELIA #2 TAP | 60 | ETL.8184 |  | ACT | 6.87 |  | 2.99 |  | 3.88
CORONA-LAKEVILLE | 115 | ETL.4311 |  | ACT | 5.79 |  |  |  | 5.79
CORTINA #1 | 60 | ETL.6580 |  | ACT | 26.28 |  |  |  | 26.28
CORTINA #2 | 60 | ETL.6590 |  | ACT | 26.61 |  |  |  | 26.61
CORTINA #3 | 60 | ETL.6600 |  | ACT | 24.8 |  |  |  | 24.8
CORTINA #4 | 60 | ETL.6610 |  | ACT | 45.24 |  |  |  | 45.24
CORTINA-MENDOCINO #1 | 115 | ETL.1330 |  | ACT | 60.95 | 4.56 | 48.77 |  | 7.62
CORTINA-VACA | 230 | ETL.4540 |  | ACT | 53.22 |  | 2.25 |  | 50.97
COTTLE-MELONES | 230 | ETL.4530 |  | ACT | 25.94 |  | 5.29 |  | 20.65
COTTONWOOD #1 | 60 | ETL.6620 |  | ACT | 48.17 |  | 9.72 |  | 38.45
COTTONWOOD #2 | 60 | ETL.6630 |  | ACT | 23.63 |  | 9.72 |  | 13.91
COTTONWOOD-BENTON #1 | 60 | ETL.6640 |  | ACT | 15.54 |  | 5.53 |  | 10.01
COTTONWOOD-BENTON #2 | 60 | ETL.6650 |  | ACT | 14.67 | 2.99 | 9.6 |  | 2.08
COTTONWOOD-DELEVAN #1 | 230 | ETL.4550 |  | ACT | 71.55 |  | 9.71 |  | 61.84
COTTONWOOD-DELEVAN #2 | 230 | ETL.4580 |  | ACT | 71.54 |  | 9.71 |  | 61.83
COTTONWOOD-GLENN | 230 | ETL.4560 |  | ACT | 48.33 |  | 9.71 |  | 38.62
COTTONWOOD-LOGAN CREEK | 230 | ETL.4570 |  | ACT | 59.28 |  | 9.71 |  | 49.57
COTTONWOOD-PANORAMA | 115 | ETL.1340 |  | ACT | 2.95 |  | 2.08 |  | 0.87
COTTONWOOD-RED BLUFF | 60 | ETL.6660 |  | ACT | 16.78 |  | 10.54 |  | 6.24
COVE ROAD TAP | 230 | ETL.5421 |  | ACT | 0.11 |  | 0.11 |  | 0
COYOTE SW STA-METCALF | 230 | ETL.5092 |  | ACT | 0.88 |  |  |  | 0.88
CRAG VIEW-CASCADE | 115 | ETL.1350 |  | ACT | 21.61 | 2.41 | 17.96 |  | 1.24
CRAZY HORSE CANYON-HOLLISTER | 115 | ETL.2153 |  | ACT | 17.18 |  | 2.7 |  | 14.48
CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | 115 | ETL.2900 |  | ACT | 35.34 |  | 15.82 |  | 19.52
CRAZY HORSE CANYON-SALINAS-SOLEDAD #2 | 115 | ETL.2910 |  | ACT | 35.42 |  | 15.84 |  | 19.58
CRAZY HORSE CANYON-SAN BENITO | 115 | ETL.2152 |  | ACT | 8.94 |  | 2.64 |  | 6.3
CRESCENT SW STA-SCHINDLER | 70 | ETL.9180 |  | ACT | 10.8 |  |  |  | 10.8
CRESCENT SW STA-SCULPIN PV | 70 | ETL.1038 |  | ACT | 0.04 |  |  |  | 0.04
CRESCENT SW STA-STROUD | 70 | ETL.9190 |  | ACT | 3.61 |  |  |  | 3.61
CRESTA-RIO OSO | 230 | ETL.4590 |  | ACT | 64.79 | 8.93 | 18.2 |  | 37.66
CROW CREEK SW STA-FRONTIER SOLAR PV | 60 | ETL.7859 |  | ACT | 0.02 |  |  |  | 0.02
CROW CREEK SW STA-NEWMAN | 60 | ETL.7860 |  | ACT | 11.14 |  |  |  | 11.14
CROWS LANDING TAP | 60 | ETL.7871 |  | ACT | 5.28 |  |  |  | 5.28
CRUSHER TAP | 60 | ETL.6241 |  | ACT | 1.94 |  | 1.94 |  | 0
CRYSTAL SPRINGS TAP | 60 | ETL.7211 |  | ACT | 0.28 |  | 0.28 |  | 0
CYMRIC TAP | 115 | ETL.2582 |  | ACT | 0.18 |  |  |  | 0.18
DAIRYLAND-MENDOTA | 115 | ETL.1360 |  | ACT | 28.69 |  |  |  | 28.69
DANISH CREAMERY TAP | 115 | ETL.2362 |  | ACT | 1.2 |  |  |  | 1.2
DE FRANCESCO TAP | 115 | ETL.3245 |  | ACT | 1.03 |  |  |  | 1.03
DEEPWATER #1 TAP | 115 | ETL.4121 |  | ACT | 2.29 |  |  |  | 2.29
DEEPWATER #2 TAP | 115 | ETL.4111 |  | ACT | 2.45 |  |  |  | 2.45
DEER CREEK-DRUM | 60 | ETL.6690 | PGE | ACT | 6.27 | 6.27 |  |  | 0
DEL MAR-ATLANTIC #1 | 60 | ETL.1410 |  | ACT | 2.78 |  |  |  | 2.78
DEL MAR-ATLANTIC #2 | 60 | ETL.6170 |  | ACT | 4.39 |  |  |  | 4.39
DEL MONTE-FORT ORD #1 | 60 | ETL.8400 |  | ACT | 6.13 |  | 0.25 |  | 5.88
DEL MONTE-FORT ORD #2 | 60 | ETL.8422 |  | ACT | 5.6 |  | 0.06 |  | 5.54
DEL MONTE-MONTEREY | 60 | ETL.6700 |  | ACT | 2.53 |  |  |  | 2.53
DEL MONTE-VIEJO | 60 | ETL.6710 |  | ACT | 8.67 |  | 5.29 |  | 3.38
DELEVAN-CORTINA | 230 | ETL.4384 |  | ACT | 17.89 |  |  |  | 17.89
DELEVAN-VACA #1 | 230 | ETL.5010 |  | ACT | 71.04 |  | 2.06 |  | 68.98
DELEVAN-VACA #2 | 230 | ETL.4231 |  | ACT | 71.07 |  | 1.67 |  | 69.4
DELEVAN-VACA #3 | 230 | ETL.4790 |  | ACT | 71.09 |  | 1.49 |  | 69.6
DELTA SWITCHING YARD-TESLA | 230 | ETL.4600 |  | ACT | 7.7 |  |  |  | 7.7
DELTA-MTN GATE JCT | 60 | ETL.6750 |  | ACT | 15.11 | 2.18 | 11.65 |  | 1.28
DERRICK TAP | 70 | ETL.8573 |  | ACT | 0.85 |  |  |  | 0.85
DESABLA-CENTERVILLE | 60 | ETL.6720 |  | ACT | 5.89 | 5.89 |  |  | 0
DIABLO PP STANDBY SUPPLY | 230 | ETL.4610 |  | ACT | 0.48 | 0.48 |  |  | 0
DIABLO UNIT #1 | 500 | ETL.5940 |  | ACT | 0.54 | 0.54 |  |  | 0
DIABLO UNIT #2 | 500 | ETL.5950 |  | ACT | 0.57 | 0.57 |  |  | 0
DIABLO-GATES #1 | 500 | ETL.5960 |  | ACT | 79.23 | 10.56 | 16.5 |  | 52.17
DIABLO-MESA | 230 | ETL.4620 |  | ACT | 40.34 | 7.65 | 27.83 |  | 4.86
DIABLO-MIDWAY #2 | 500 | ETL.5970 |  | ACT | 84.09 | 15.47 | 29.47 |  | 39.15
DIABLO-MIDWAY #3 | 500 | ETL.5980 |  | ACT | 84.67 | 15.56 | 29.34 |  | 39.77
DINOSAUR POINT TAP | 70 | ETL.8961 |  | ACT | 2 |  | 0.51 |  | 1.49
DINUBA ENERGY TAP | 70 | ETL.9051 |  | ACT | 3.16 |  |  |  | 3.16
DINUBA-OROSI | 70 | ETL.8610 |  | ACT | 9.83 |  |  |  | 9.83
DISCOVERY TAP | 115 | ETL.1921 |  | ACT | 2.1 |  |  |  | 2.1
DISTRICT 1001 TAP | 60 | ETL.7701 |  | ACT | 1.45 |  |  |  | 1.45
DISTRICT 1500 TAP | 60 | ETL.7711 |  | ACT | 3.61 |  |  |  | 3.61
DIVIDE-CABRILLO #1 | 115 | ETL.1380 |  | ACT | 14.6 |  | 6.29 |  | 8.31
DIVIDE-CABRILLO #2 | 115 | ETL.1370 |  | ACT | 11.55 |  | 6.05 |  | 5.5
DIVIDE-VANDENBERG #1 | 70 | ETL.8620 |  | ACT | 6.64 |  | 5.51 |  | 1.13
DIVIDE-VANDENBERG #2 | 70 | ETL.8630 |  | ACT | 6.57 |  | 5.45 |  | 1.12
DIXON LANDING-MCKEE | 115 | ETL.1390 |  | ACT | 8.3 |  |  |  | 8.3
DIXON-VACA #1 | 60 | ETL.6730 |  | ACT | 18.35 |  |  |  | 18.35
DIXON-VACA #2 | 60 | ETL.6740 |  | ACT | 26.77 |  |  |  | 26.77
DOLAN RD #1 TAP | 115 | ETL.2881 |  | ACT | 0.32 |  |  |  | 0.32
DOLAN RD #2 TAP | 115 | ETL.2891 |  | ACT | 0.33 |  |  |  | 0.33
DONNELLS-MI-WUK | 115 | ETL.1400 |  | ACT | 18.46 | 18.46 |  |  | 0
DOS AMIGOS PUMPING PLANT-PANOCHE | 230 | ETL.4630 |  | ACT | 23.68 |  |  |  | 23.68
DOUBLE C (PSE) TAP | 115 | ETL.1931 |  | ACT | 0.06 |  |  |  | 0.06
DRUM PH #2 TAP | 115 | ETL.6375 | POWERGEN | ACT | 0.09 | 0.09 |  |  | 0
DRUM-GRASS VALLEY-WEIMAR | 60 | ETL.6760 |  | ACT | 31.17 | 17.19 | 12.72 |  | 1.26
DRUM-HIGGINS | 115 | ETL.4393 |  | ACT | 43.53 | 19.01 | 23.87 |  | 0.65
DRUM-RIO OSO #1 | 115 | ETL.1420 |  | ACT | 44.64 | 14.06 | 17.9 |  | 12.68
DRUM-RIO OSO #2 | 115 | ETL.1430 |  | ACT | 44.65 | 14.08 | 17.87 |  | 12.7
DRUM-SPAULDING | 60 | ETL.6770 |  | ACT | 9.36 | 6.88 | 2.48 |  | 0
DRUM-SUMMIT #1 | 115 | ETL.1440 |  | ACT | 27.36 | 6.49 | 15.1 | 0.62 | 5.15
DRUM-SUMMIT #2 | 115 | ETL.1450 |  | ACT | 28.36 | 6.49 | 16.36 | 0.44 | 5.07
DUMBARTON-NEWARK | 115 | ETL.1460 |  | ACT | 7.14 |  |  |  | 7.14
DUNLAP TAP | 70 | ETL.9061 |  | ACT | 16.21 |  | 13.79 |  | 2.42
DUTCH FLAT #2 TAP | 115 | ETL.1421 |  | ACT | 0.43 | 0.43 |  |  | 0
EAGLE ROCK-CORTINA | 115 | ETL.1470 |  | ACT | 43.39 | 14.63 | 23 |  | 5.76
EAGLE ROCK-FULTON-SILVERADO | 115 | ETL.4392 |  | ACT | 46.62 | 41.49 | 2.45 |  | 2.68
EAGLE ROCK-FULTON-SILVERADO | 115 | ETL.4392 |  | IDL | 0.33 | 0.33 |  |  | 0
EAGLE ROCK-REDBUD | 115 | ETL.1480 |  | ACT | 23.31 | 9.94 | 13.05 |  | 0.32
EAST DUBLIN (BART) TAP | 60 | ETL.7962 |  | ACT | 0.04 |  |  |  | 0.04
EAST GRAND - SOUTH SAN FRANSICO TRACTION POWER #1 | 115 | ETL.1302 |  | ACT | 0.09 |  |  |  | 0.09
EAST GRAND - SOUTH SAN FRANSICO TRACTION POWER #2 | 115 | ETL.1304 |  | ACT | 0.05 |  |  |  | 0.05
EAST GRAND-SAN MATEO | 115 | ETL.1490 |  | ACT | 7.89 |  |  |  | 7.89
EASTSHORE-CERBERUS | 115 | ETL.7252 |  | ACT | 0.48 |  |  |  | 0.48
EASTSHORE-CLAWITER #1 | 230 | ETL.1335 |  | ACT | 0.11 |  |  |  | 0.11
EASTSHORE-CLAWITER #2 | 230 | ETL.1333 |  | ACT | 0.11 |  |  |  | 0.11
EASTSHORE-DUMBARTON | 115 | ETL.1495 |  | ACT | 12.38 |  |  |  | 12.38
EASTSHORE-MT EDEN #1 | 115 | ETL.1500 |  | ACT | 1.04 |  |  |  | 1.04
EASTSHORE-MT EDEN #2 | 115 | ETL.1501 |  | ACT | 1 |  |  |  | 1
EASTSHORE-SAN MATEO | 230 | ETL.4650 |  | ACT | 12.43 |  |  |  | 12.43
EBMUD TAP | 115 | ETL.2081 |  | ACT | 0.02 |  |  |  | 0.02
EDES #1 TAP | 115 | ETL.3521 |  | ACT | 0.04 |  |  |  | 0.04
EDES #2 TAP | 115 | ETL.3142 |  | ACT | 0.04 |  |  |  | 0.04
EEL RIVER TAP | 60 | ETL.7101 |  | ACT | 2.31 |  |  |  | 2.31
EIGHT MILE ROAD-STAGG | 230 | ETL.5002 |  | ACT | 7.2 |  |  |  | 7.2
EIGHT MILE ROAD-TESLA | 230 | ETL.4660 |  | ACT | 26.64 |  |  |  | 26.64
EISEN TAP | 70 | ETL.8883 |  | ACT | 1.86 |  |  |  | 1.86
EL CAPITAN-WILSON | 115 | ETL.1510 |  | ACT | 8.12 |  |  |  | 8.12
EL DORADO-MISSOURI FLAT #1 | 115 | ETL.1530 |  | ACT | 14.43 | 3.84 | 8.91 |  | 1.68
EL DORADO-MISSOURI FLAT #2 | 115 | ETL.1540 |  | ACT | 14.4 | 3.84 | 8.85 |  | 1.71
EL PATIO-SAN JOSE A | 115 | ETL.1520 |  | ACT | 7.08 |  |  |  | 7.08
EL PECO TAP | 70 | ETL.9353 |  | ACT | 3.02 |  |  |  | 3.02
ELECTRA-BELLOTA | 230 | ETL.4670 |  | ACT | 29.23 |  | 12.78 |  | 16.45
ELK CREEK TAP | 60 | ETL.6921 |  | ACT | 20.44 |  | 3.58 |  | 16.86
ELK-GUALALA | 60 | ETL.8410 |  | ACT | 29.02 |  | 22.59 |  | 6.43
ELLIS TAP | 115 | ETL.4021 |  | ACT | 0.17 |  |  |  | 0.17
EMIDIO TAP | 70 | ETL.9291 |  | ACT | 3.07 |  |  |  | 3.07
ENCINAL TAP | 60 | ETL.7751 |  | ACT | 1.43 |  |  |  | 1.43
ESSEX JCT-ARCATA-FAIRHAVEN | 60 | ETL.6800 |  | ACT | 16.06 |  |  |  | 16.06
ESSEX JCT-ORICK | 60 | ETL.6810 |  | ACT | 31.29 |  |  | 1.57 | 29.72
EUREKA-STA A | 60 | ETL.6820 |  | ACT | 0.22 |  |  |  | 0.22
EVERGREEN-ALMADEN | 60 | ETL.6830 |  | ACT | 4.96 |  |  |  | 4.96
EVERGREEN-MABURY | 60 | ETL.6840 |  | ACT | 5.48 |  |  |  | 5.48
EXCELSIOR SW STA-CRE FIVE POINTS PV | 115 | ETL.3247 | PGE | ACT | 0.03 |  |  |  | 0.03
EXCELSIOR SW STA-SCHINDLER #1 | 115 | ETL.3248 |  | ACT | 5.24 |  |  |  | 5.24
EXCELSIOR SW STA-SCHINDLER #2 | 115 | ETL.3249 |  | ACT | 5.23 |  |  |  | 5.23
EXCHEQUER-INDIAN FLAT | 70 | ETL.8650 | PGE | ACT | 29.89 | 4 | 25.17 |  | 0.72
EXCHEQUER-LE GRAND | 115 | ETL.1560 |  | ACT | 29.75 |  |  |  | 29.75
EXCHEQUER-MARIPOSA | 70 | ETL.8640 |  | ACT | 19.48 |  | 10.62 |  | 8.86
FAIRHAVEN #1 | 60 | ETL.6850 |  | ACT | 0.47 |  |  |  | 0.47
FAIRHAVEN POWER CO TAP | 60 | ETL.6853 |  | ACT | 0.5 |  |  |  | 0.5
FAIRHAVEN-HUMBOLDT | 60 | ETL.6860 |  | ACT | 15.44 |  |  |  | 15.44
FAIRVIEW-MARTINEZ SW STA | 115 | ETL.2275 |  | ACT | 0.1 |  |  |  | 0.1
FAIRWAY #1 TAP | 115 | ETL.2451 |  | ACT | 2.83 |  |  |  | 2.83
FAIRWAY #2 TAP | 115 | ETL.3611 |  | ACT | 1.52 |  |  |  | 1.52
FELLOWS-MIDSUN | 115 | ETL.1570 |  | ACT | 4.92 |  |  |  | 4.92
FELLOWS-TAFT | 115 | ETL.1580 |  | ACT | 7.93 |  |  |  | 7.93
FIBREBOARD STANDARD TAP | 115 | ETL.1404 |  | ACT | 0.02 |  | 0.02 |  | 0
FIBREBOARD TAP | 115 | ETL.1291 |  | ACT | 0.96 |  |  |  | 0.96
FITCH MTN #1 TAP | 60 | ETL.6891 |  | ACT | 0.85 |  | 0.15 |  | 0.7
FITCH MTN #2 TAP | 60 | ETL.6901 |  | ACT | 0.06 |  |  |  | 0.06
FIVE POINTS SW STA-HURON-GATES | 70 | ETL.9160 |  | ACT | 19.78 |  |  |  | 19.78
FIVE POINTS SW-WHITNEY POINT PV | 70 | ETL.1053 |  | ACT | 0.05 |  |  |  | 0.05
FLINT TAP | 115 | ETL.3341 |  | ACT | 1.96 |  | 1.48 |  | 0.48
FMC - SAN JOSE TRACTION POWER #1 | 115 | ETL.1344 |  | ACT | 0.21 |  |  |  | 0.21
FMC - SAN JOSE TRACTION POWER #2 | 115 | ETL.1346 |  | ACT | 0.19 |  |  |  | 0.19
FMC-SAN JOSE B | 115 | ETL.2021 |  | ACT | 1.61 |  |  |  | 1.61
FORBESTOWN TAP | 115 | ETL.4222 |  | ACT | 0.22 | 0.22 |  |  | 0
FORKS OF THE BUTTE TAP | 60 | ETL.6722 |  | ACT | 0.25 | 0.25 |  |  | 0
FORT BRAGG-ELK | 60 | ETL.2060 |  | ACT | 24.03 |  | 21.59 |  | 2.44
FORT ROSS-GUALALA | 60 | ETL.6980 |  | ACT | 29.76 |  | 29.61 |  | 0.15
FORT SEWARD TAP | 60 | ETL.6222 |  | ACT | 7.69 |  | 2.9 |  | 4.79
FRENCH MEADOWS-MIDDLE FORK | 60 | ETL.6870 |  | ACT | 13.15 | 13.15 |  |  | 0
FRESH EXPRESS TAP | 60 | ETL.7901 |  | ACT | 0.56 |  |  |  | 0.56
FRESNO COGEN (AGRICO) TAP | 70 | ETL.8741 |  | ACT | 3.17 |  |  |  | 3.17
FRIANT-COPPERMINE | 70 | ETL.8660 |  | ACT | 8.3 |  |  |  | 8.3
FRITO LAY TAP | 115 | ETL.2602 |  | ACT | 0.51 |  |  |  | 0.51
FROGTOWN #1 TAP | 115 | ETL.3831 |  | ACT | 0.12 |  | 0.12 |  | 0
FROGTOWN #2 TAP | 115 | ETL.3843 |  | ACT | 0.11 |  | 0.11 |  | 0
FRUITLAND TAP | 60 | ETL.6221 |  | ACT | 4.26 |  | 3.85 |  | 0.41
FRUITVALE TAP | 70 | ETL.8881 |  | ACT | 0.12 |  |  |  | 0.12
FULTON JCT-VACA | 115 | ETL.1590 |  | ACT | 11.93 |  | 2.83 |  | 9.1
FULTON-CALISTOGA | 60 | ETL.6880 |  | ACT | 50.35 | 41.39 | 2.9 |  | 6.06
FULTON-HOPLAND | 60 | ETL.6890 |  | ACT | 41.04 | 6.72 | 26.21 |  | 8.11
FULTON-IGNACIO #1 | 230 | ETL.4680 |  | ACT | 40.73 | 14.88 | 7.55 |  | 18.3
FULTON-LAKEVILLE | 230 | ETL.4950 |  | ACT | 25.51 | 15.24 | 6.43 |  | 3.84
FULTON-LAKEVILLE-IGNACIO | 230 | ETL.2823 |  | IDL | 1.59 | 0.44 | 0.54 |  | 0.61
FULTON-MOLINO-COTATI | 60 | ETL.6910 |  | ACT | 20.52 |  | 1.77 |  | 18.75
FULTON-MOLINO-COTATI | 60 | ETL.6910 |  | IDL | 0.34 |  |  |  | 0.34
FULTON-PUEBLO | 115 | ETL.1600 |  | ACT | 59.95 | 18.66 | 18.92 | 0.05 | 22.32
FULTON-SANTA ROSA #1 | 115 | ETL.1620 |  | ACT | 6.69 |  |  |  | 6.69
FULTON-SANTA ROSA #2 | 115 | ETL.1630 |  | ACT | 6.29 |  |  |  | 6.29
FULTON-WINDSOR | 60 | ETL.1024 |  | ACT | 6.59 |  |  |  | 6.59
GALLO-CRESSEY | 115 | ETL.1036 |  | ACT | 14.42 |  |  |  | 14.42
GALLO-LIVINGSTON | 115 | ETL.1032 |  | ACT | 4.2 |  |  |  | 4.2
GARBERVILLE-LAYTONVILLE | 60 | ETL.8365 |  | ACT | 39.98 |  | 10.29 |  | 29.69
GARCIA TAP | 60 | ETL.8411 |  | ACT | 3.04 |  | 3.04 |  | 0
GARDNER TAP | 70 | ETL.8971 |  | ACT | 3.77 |  |  |  | 3.77
GATES BK-12 | 230 | ETL.1222 |  | ACT | 0.29 |  |  |  | 0.29
GATES-ARCO | 230 | ETL.4690 |  | ACT | 35.02 |  |  |  | 35.02
GATES-CASTANEA | 230 | ETL.1223 |  | ACT | 0.42 |  |  |  | 0.42
GATES-COALINGA #2 | 70 | ETL.8680 |  | ACT | 17.33 |  |  |  | 17.33
GATES-FIFTH STANDARD SOLAR PV | 230 | ETL.1313 | PGE | ACT | 0.3 |  |  |  | 0.3
GATES-HURON | 70 | ETL.8690 |  | ACT | 4.5 |  |  |  | 4.5
GATES-JAYNE SW STA | 70 | ETL.8652 |  | ACT | 0.68 |  |  |  | 0.68
GATES-MIDWAY | 230 | ETL.4891 |  | ACT | 63.68 |  |  |  | 63.68
GATES-MIDWAY | 500 | ETL.5990 |  | ACT | 63.78 |  |  |  | 63.78
GATES-MUSTANG SW STA #1 | 230 | ETL.2604 |  | ACT | 12.96 |  |  |  | 12.96
GATES-MUSTANG SW STA #2 | 230 | ETL.2605 |  | ACT | 12.99 |  |  |  | 12.99
GATES-PANOCHE #1 | 230 | ETL.4720 |  | ACT | 43.59 |  |  |  | 43.59
GATES-PANOCHE #2 | 230 | ETL.4730 |  | ACT | 43.57 |  |  |  | 43.57
GATES-TULARE LAKE | 70 | ETL.8700 |  | ACT | 18.34 |  |  |  | 18.34
GEYSERS #11-EAGLE ROCK | 115 | ETL.4391 |  | ACT | 0.64 | 0.64 |  |  | 0
GEYSERS #12-FULTON | 230 | ETL.4750 |  | ACT | 24.1 | 18.9 | 3.57 |  | 1.63
GEYSERS #13 TAP | 230 | ETL.4781 |  | ACT | 2.06 | 2.06 |  |  | 0
GEYSERS #16 TAP | 230 | ETL.4760 |  | ACT | 1.29 | 1.29 |  |  | 0
GEYSERS #17-FULTON | 230 | ETL.4770 |  | ACT | 25.8 | 20.68 | 3.56 |  | 1.56
GEYSERS #17-FULTON | 230 | ETL.4770 |  | IDL | 0.33 | 0.33 |  |  | 0
GEYSERS #18 TAP | 230 | ETL.4784 |  | ACT | 0.74 | 0.74 |  |  | 0
GEYSERS #20 TAP | 230 | ETL.4783 |  | ACT | 0.03 | 0.03 |  |  | 0
GEYSERS #3-CLOVERDALE | 115 | ETL.1650 |  | ACT | 12.06 | 10.88 | 0.02 |  | 1.16
GEYSERS #3-EAGLE ROCK | 115 | ETL.1660 |  | ACT | 1.77 | 1.77 |  |  | 0
GEYSERS #5-GEYSERS #3 | 115 | ETL.1670 |  | ACT | 0.49 | 0.49 |  |  | 0
GEYSERS #7-EAGLE ROCK | 115 | ETL.1680 | PGE | ACT | 1.16 | 1.16 |  |  | 0
GEYSERS #9-LAKEVILLE | 230 | ETL.4780 |  | ACT | 41.08 | 31.96 | 7.03 |  | 2.09
GIFFEN TAP | 70 | ETL.8985 |  | ACT | 4.95 |  |  |  | 4.95
GIFFEN-BURFORD | 70 | ETL.1352 |  | ACT | 0.04 |  |  |  | 0.04
GILL RANCH TAP | 115 | ETL.1742 |  | ACT | 9.15 |  |  |  | 9.15
GILROY ENERGY TAP | 115 | ETL.2151 |  | ACT | 0.28 |  |  |  | 0.28
GISH TAP | 115 | ETL.4031 |  | IDL | 0.96 |  |  |  | 0.96
GLENN #1 | 60 | ETL.6920 |  | ACT | 33.38 |  |  |  | 33.38
GLENN #2 | 60 | ETL.6930 |  | ACT | 34.68 |  |  |  | 34.68
GLENN #3 | 60 | ETL.6940 |  | ACT | 28.51 |  |  |  | 28.51
GLENN #4 | 60 | ETL.8424 |  | ACT | 12.54 |  |  |  | 12.54
GLENN #5 | 60 | ETL.8427 |  | ACT | 7.41 |  |  |  | 7.41
GLENN-DELEVAN | 230 | ETL.7042 |  | ACT | 37.42 |  |  |  | 37.42
GOLD HILL #1 | 60 | ETL.6950 |  | ACT | 32.36 | 8.54 | 13.08 |  | 10.74
GOLD HILL-BELLOTA-LOCKEFORD | 115 | ETL.1690 |  | ACT | 86.17 |  |  |  | 86.17
GOLD HILL-BELLOTA-LOCKEFORD | 115 | ETL.1690 |  | IDL | 1.1 |  |  |  | 1.1
GOLD HILL-CLARKSVILLE | 115 | ETL.9430 |  | ACT | 5.77 |  |  |  | 5.77
GOLD HILL-EIGHT MILE ROAD | 230 | ETL.4800 |  | ACT | 48.8 |  |  |  | 48.8
GOLD HILL-LODI STIG | 230 | ETL.4810 |  | ACT | 46.67 |  |  |  | 46.67
GOLDEN VALLEY TAP | 115 | ETL.2603 |  | ACT | 1.59 |  |  |  | 1.59
GOLDTREE TAP | 115 | ETL.2821 |  | ACT | 2.3 |  | 1.05 |  | 1.25
GONZALES #1 TAP | 60 | ETL.8011 |  | ACT | 0.19 |  |  |  | 0.19
GONZALES #2 TAP | 60 | ETL.8021 |  | ACT | 0.3 |  |  |  | 0.3
GRANITE ROCK TAP | 60 | ETL.8311 |  | ACT | 2.39 |  | 2.35 |  | 0.04
GRANT-EASTSHORE #1 | 115 | ETL.1700 |  | ACT | 4.34 |  |  |  | 4.34
GRANT-EASTSHORE #2 | 115 | ETL.1701 |  | ACT | 4.21 |  |  |  | 4.21
GRAPEVINE TAP | 70 | ETL.9252 |  | ACT | 0.14 |  | 0.14 |  | 0
GREEN VALLEY-CAMP EVERS | 115 | ETL.1710 |  | ACT | 18.56 | 10.39 | 3.03 |  | 5.14
GREEN VALLEY-LLAGAS | 115 | ETL.1720 |  | ACT | 24.74 | 6.14 | 8.41 |  | 10.19
GREEN VALLEY-PAUL SWEET | 115 | ETL.1730 |  | ACT | 15.82 | 7.14 | 4.24 |  | 4.44
GREEN VALLEY-WATSONVILLE | 60 | ETL.6970 |  | ACT | 4.79 |  |  |  | 4.79
GREENLEAF #1 TAP | 115 | ETL.1101 |  | ACT | 4.84 |  |  |  | 4.84
GREENLEAF #2 TAP | 60 | ETL.7761 |  | ACT | 0.62 |  |  |  | 0.62
GREGG-ASHLAN | 230 | ETL.4820 |  | ACT | 7 |  |  |  | 7
GREGG-HERNDON #1 | 230 | ETL.4830 |  | ACT | 0.6 |  |  |  | 0.6
GREGG-HERNDON #2 | 230 | ETL.4840 |  | ACT | 0.63 |  |  |  | 0.63
GRONEMEYER TAP | 60 | ETL.7471 |  | ACT | 0.83 |  |  |  | 0.83
GUARDIAN #1 TAP | 115 | ETL.2301 |  | ACT | 0.75 |  |  |  | 0.75
GUARDIAN #2 TAP | 115 | ETL.2292 |  | ACT | 0.13 |  |  |  | 0.13
GUERNSEY-HENRIETTA | 70 | ETL.8720 |  | ACT | 18.44 |  |  |  | 18.44
GUSTINE #1 TAP | 60 | ETL.7862 |  | ACT | 7.51 |  |  |  | 7.51
GUSTINE #2 TAP | 60 | ETL.7872 |  | ACT | 4.44 |  |  |  | 4.44
GWF #4 TAP | 60 | ETL.6531 |  | IDL | 0.01 |  |  |  | 0.01
GWF HANFORD COGEN TAP | 70 | ETL.8723 |  | IDL | 0.31 |  |  |  | 0.31
GWF-HENRIETTA | 70 | ETL.8774 |  | ACT | 0.12 |  |  |  | 0.12
GWF-KINGSBURG | 115 | ETL.1743 |  | ACT | 21.64 |  |  |  | 21.64
H-P #3 | 115 | ETL.1555 |  | ACT | 0.17 |  |  |  | 0.17
HAAS-MCCALL | 230 | ETL.4850 |  | ACT | 44.21 |  | 24.67 |  | 19.54
HAAS-WOODCHUCK | 0 | ETL.8730 |  | IDL | 6.79 |  | 3.79 |  | 3
HALSEY-PLACER | 60 | ETL.6990 |  | ACT | 4.94 |  | 1.58 |  | 3.36
HAMILTON BRANCH-CHESTER | 60 | ETL.7000 |  | ACT | 12.27 |  | 10.09 |  | 2.18
HAMMER-COUNTRY CLUB | 60 | ETL.7010 |  | ACT | 8.82 |  |  |  | 8.82
HARDWICK TAP | 70 | ETL.8911 |  | ACT | 2.74 |  |  |  | 2.74
HARRINGTON TAP | 60 | ETL.6581 |  | ACT | 0.53 |  |  |  | 0.53
HARTLEY-CLEARLAKE | 60 | ETL.7515 |  | ACT | 6.62 |  | 3.14 |  | 3.48
HAT CREEK #1-PIT #1 | 60 | ETL.7020 |  | ACT | 6.01 |  | 6.01 |  | 0
HAT CREEK #1-WESTWOOD | 60 | ETL.7030 |  | ACT | 55.63 |  | 46.54 |  | 9.09
HEADGATE TAP | 60 | ETL.6941 |  | ACT | 0.97 |  |  |  | 0.97
HEALDSBURG #1 TAP | 60 | ETL.6892 |  | ACT | 0.25 |  |  |  | 0.25
HEALDSBURG #2 TAP | 60 | ETL.6902 |  | ACT | 0.16 |  |  |  | 0.16
HEINZ TAP (12KV) | 115 | ETL.2193 |  | IDL | 0.78 |  |  |  | 0.78
HELM-CRESCENT SW STA | 70 | ETL.8750 |  | ACT | 4.92 |  |  |  | 4.92
HELM-KERMAN | 70 | ETL.8740 |  | ACT | 13.25 |  |  |  | 13.25
HELM-MCCALL | 230 | ETL.4860 |  | ACT | 30.84 |  |  |  | 30.84
HELM-STROUD | 70 | ETL.8760 |  | ACT | 7.43 |  |  |  | 7.43
HELMS-GREGG #1 | 230 | ETL.4870 | POWERGEN | ACT | 60.67 |  | 25.11 | 1.66 | 33.9
HELMS-GREGG #2 | 230 | ETL.4880 | POWERGEN | ACT | 60.68 |  | 25.12 | 1.44 | 34.12
HENRIETTA-AMERICAN KINGS | 70 | ETL.1243 | PGE | ACT | 0.21 |  |  |  | 0.21
HENRIETTA-KENT SW STA | 70 | ETL.8791 |  | ACT | 1.47 |  |  |  | 1.47
HENRIETTA-LEMOORE | 70 | ETL.8770 |  | ACT | 9.36 |  |  |  | 9.36
HENRIETTA-LEMOORE NAS | 70 | ETL.8780 |  | ACT | 1.75 |  |  |  | 1.75
HENRIETTA-LEPRINO SW STA | 115 | ETL.1737 |  | ACT | 6.03 |  |  |  | 6.03
HERDLYN-BALFOUR | 60 | ETL.7050 |  | ACT | 16.33 |  |  |  | 16.33
HERDLYN-BALFOUR | 60 | ETL.7050 |  | IDL | 4.17 |  |  |  | 4.17
HERDLYN-TRACY | 70 | ETL.8800 |  | ACT | 2.06 |  |  |  | 2.06
HERNDON-ASHLAN | 230 | ETL.4890 |  | ACT | 6.39 |  |  |  | 6.39
HERNDON-BARTON | 115 | ETL.1750 |  | ACT | 12.69 |  |  |  | 12.69
HERNDON-BULLARD #1 | 115 | ETL.1760 |  | ACT | 11.44 |  |  |  | 11.44
HERNDON-BULLARD #2 | 115 | ETL.1770 |  | ACT | 11.43 |  |  |  | 11.43
HERNDON-KEARNEY | 230 | ETL.4900 |  | ACT | 10.83 |  |  |  | 10.83
HERNDON-MANCHESTER | 115 | ETL.1780 |  | ACT | 9.29 |  |  |  | 9.29
HERNDON-WOODWARD | 115 | ETL.1790 |  | ACT | 13.04 |  |  |  | 13.04
HICKS-METCALF | 230 | ETL.4910 |  | ACT | 9.07 |  | 3.38 |  | 5.69
HIGGINS-BELL | 115 | ETL.1412 |  | ACT | 18.77 |  | 15.04 |  | 3.73
HILLSDALE JCT-HALF MOON BAY | 60 | ETL.7060 |  | ACT | 6.81 | 1.42 | 3.25 |  | 2.14
HONCUT TAP | 115 | ETL.3201 |  | ACT | 1.65 |  |  |  | 1.65
HOWLAND ROAD TAP | 115 | ETL.2191 |  | ACT | 0.9 |  |  |  | 0.9
HUMBOLDT #1 | 60 | ETL.7113 |  | ACT | 11.08 |  |  |  | 11.08
HUMBOLDT BAY-EUREKA | 60 | ETL.7070 |  | ACT | 5.61 |  |  |  | 5.61
HUMBOLDT BAY-HUMBOLDT #1 | 60 | ETL.7080 |  | ACT | 8.41 |  |  |  | 8.41
HUMBOLDT BAY-HUMBOLDT #1 | 115 | ETL.1800 |  | ACT | 6.31 |  | 2.47 | 0.1 | 3.74
HUMBOLDT BAY-HUMBOLDT #2 | 60 | ETL.7090 |  | ACT | 6.5 |  | 2.46 | 0.11 | 3.93
HUMBOLDT BAY-RIO DELL JCT | 60 | ETL.7100 |  | ACT | 18.41 |  | 1.99 |  | 16.42
HUMBOLDT-BRIDGEVILLE | 115 | ETL.1810 |  | ACT | 30.28 |  | 7.15 |  | 23.13
HUMBOLDT-EUREKA | 60 | ETL.7120 |  | ACT | 4.74 |  |  |  | 4.74
HUMBOLDT-MAPLE CREEK | 60 | ETL.7130 |  | ACT | 14.09 |  | 8 |  | 6.09
HUMBOLDT-TRINITY | 115 | ETL.1820 |  | ACT | 68.58 |  | 63.09 |  | 5.49
IBM BAILEY AVE TAP | 115 | ETL.2491 |  | ACT | 2 |  |  |  | 2
IBM HARRY RD #1 TAP | 115 | ETL.2501 |  | ACT | 0.58 |  | 0.58 |  | 0
IBM HARRY RD #2 TAP | 115 | ETL.2481 |  | ACT | 0.58 |  | 0.58 |  | 0
IGNACIO-ALTO | 60 | ETL.7150 |  | ACT | 17.79 | 1.01 | 3.06 |  | 13.72
IGNACIO-ALTO-SAUSALITO #1 | 60 | ETL.7160 |  | ACT | 17.95 |  | 4.85 |  | 13.1
IGNACIO-ALTO-SAUSALITO #2 | 60 | ETL.7170 |  | ACT | 17.95 |  | 4.82 |  | 13.13
IGNACIO-BOLINAS #1 | 60 | ETL.7140 |  | ACT | 15.02 | 10.25 | 4.65 |  | 0.12
IGNACIO-BOLINAS #2 | 60 | ETL.7180 |  | ACT | 28.21 | 12.46 | 13.66 |  | 2.09
IGNACIO-LAS GALLINAS | 115 | ETL.1860 |  | ACT | 4.15 |  | 0.08 |  | 4.07
IGNACIO-MARE ISLAND #1 | 115 | ETL.1830 |  | ACT | 39.46 |  |  |  | 39.46
IGNACIO-MARE ISLAND #2 | 115 | ETL.1840 |  | ACT | 43.07 |  |  |  | 43.07
IGNACIO-SAN RAFAEL #1 | 115 | ETL.1850 |  | ACT | 11.54 | 0.62 | 2.45 |  | 8.47
IGNACIO-SOBRANTE | 230 | ETL.4920 |  | ACT | 42.49 |  | 11.94 |  | 30.55
IGNACIO-STAFFORD | 60 | ETL.1042 |  | ACT | 6.13 |  | 0.6 |  | 5.53
IMHOFF TAP | 115 | ETL.3322 |  | ACT | 1.43 |  |  |  | 1.43
INDIAN FLAT-YOSEMITE | 70 | ETL.1112 |  | ACT | 5 |  | 5 |  | 0
INDUSTRIAL TAP | 60 | ETL.7441 |  | ACT | 0.97 |  |  |  | 0.97
INGRAM CREEK TAP | 115 | ETL.4001 |  | ACT | 0.5 |  |  |  | 0.5
IONE TAP | 60 | ETL.8253 |  | ACT | 4.09 |  | 3 |  | 1.09
IUKA TAP | 60 | ETL.8281 |  | ACT | 0.49 |  |  |  | 0.49
JAMESON CANYON PUMPING PLANT TAP | 115 | ETL.1833 |  | ACT | 0.19 |  |  |  | 0.19
JANES CREEK TAP | 60 | ETL.6805 |  | ACT | 1.78 |  |  |  | 1.78
JARVIS-CRYOGENICS | 115 | ETL.1870 |  | IDL | 0.03 |  |  |  | 0.03
JAYNE SW STA-COALINGA | 70 | ETL.8670 |  | ACT | 12.25 |  |  |  | 12.25
JEFFERSON #1 | 60 | ETL.6831 |  | ACT | 8.97 |  | 2.31 |  | 6.66
JEFFERSON-HILLSDALE JCT | 60 | ETL.7190 |  | ACT | 14.78 |  | 2.3 |  | 12.48
JEFFERSON-LAS PULGAS | 60 | ETL.7200 |  | ACT | 5.99 |  | 0.11 |  | 5.88
JEFFERSON-MARTIN | 230 | ETL.5710 |  | ACT | 3.3 |  | 1.04 |  | 2.26
JEFFERSON-STANFORD | 60 | ETL.7220 |  | ACT | 7.57 |  | 2.53 |  | 5.04
JENNINGS TAP | 60 | ETL.6842 |  | ACT | 0.14 |  |  |  | 0.14
JESSUP TAP | 115 | ETL.4041 |  | ACT | 0.86 |  | 0.33 |  | 0.53
JOLON TAP | 60 | ETL.7321 |  | ACT | 15.87 |  | 15.42 |  | 0.45
KAMM TAP | 115 | ETL.3253 |  | ACT | 0.52 |  |  |  | 0.52
KANAKA TAP | 115 | ETL.4223 |  | ACT | 2.59 | 0.71 | 1.88 |  | 0
KANSAS PV-LEPRINO SW STA | 115 | ETL.1739 |  | ACT | 0.17 |  |  |  | 0.17
KASSON #1 | 60 | ETL.7230 |  | ACT | 0.19 |  |  |  | 0.19
KASSON-BANTA #1 | 60 | ETL.7240 |  | ACT | 1.05 |  |  |  | 1.05
KASSON-CARBONA | 60 | ETL.7231 |  | ACT | 7.32 |  |  |  | 7.32
KASSON-LOUISE | 60 | ETL.7250 |  | ACT | 9.12 |  |  |  | 9.12
KEARNEY ALTERNATE TIE | 70 | ETL.9380 |  | ACT | 0.3 |  |  |  | 0.3
KEARNEY TIE | 70 | ETL.9370 |  | ACT | 0.15 |  |  |  | 0.15
KEARNEY-BIOLA | 70 | ETL.8810 |  | ACT | 19.14 |  |  |  | 19.14
KEARNEY-BOWLES | 70 | ETL.8820 |  | ACT | 9.29 |  |  |  | 9.29
KEARNEY-CARUTHERS | 70 | ETL.8830 |  | ACT | 12.05 |  |  |  | 12.05
KEARNEY-KERMAN | 70 | ETL.8840 |  | ACT | 10.98 |  |  |  | 10.98
KELLEY TAP | 70 | ETL.9293 |  | ACT | 2.79 |  |  |  | 2.79
KELSO-TESLA | 230 | ETL.4930 |  | ACT | 7.95 |  |  |  | 7.95
KENT SW STA-TULARE LAKE | 70 | ETL.8790 |  | ACT | 15.93 |  |  |  | 15.93
KERCKHOFF #1-KERCKHOFF #2 | 115 | ETL.1880 |  | ACT | 1.58 |  | 1.58 |  | 0
KERCKHOFF-CLOVIS-SANGER #1 | 115 | ETL.1890 |  | ACT | 36.93 |  | 7.85 |  | 29.08
KERCKHOFF-CLOVIS-SANGER #2 | 115 | ETL.1900 |  | ACT | 32.08 |  | 7.85 |  | 24.23
KERN CANYON-MAGUNDEN-WEEDPATCH | 70 | ETL.8850 |  | ACT | 20.68 |  |  |  | 20.68
KERN OIL-DEXZEL | 115 | ETL.1910 |  | ACT | 0.44 |  |  |  | 0.44
KERN OIL-MT POSO | 70 | ETL.1212 |  | IDL | 1.08 |  |  |  | 1.08
KERN OIL-WITCO | 115 | ETL.1920 |  | ACT | 4.2 |  |  |  | 4.2
KERN-BAKERSFIELD | 230 | ETL.5151 |  | ACT | 7.04 |  |  |  | 7.04
KERN-FRUITVALE | 70 | ETL.8860 |  | ACT | 0.16 |  |  |  | 0.16
KERN-KERN FRONT | 115 | ETL.1930 |  | ACT | 12.47 |  |  |  | 12.47
KERN-KERN OIL-FAMOSO | 70 | ETL.8870 |  | ACT | 19.67 |  |  |  | 19.67
KERN-KERN OIL-FAMOSO | 70 | ETL.8870 |  | IDL | 6.53 |  |  |  | 6.53
KERN-LIVE OAK | 115 | ETL.1960 |  | ACT | 10.83 |  |  |  | 10.83
KERN-MAGUNDEN | 70 | ETL.8880 |  | ACT | 17.35 |  |  |  | 17.35
KERN-MAGUNDEN-WITCO | 115 | ETL.1970 |  | ACT | 19.57 |  |  |  | 19.57
KERN-OLD RIVER #1 | 70 | ETL.8890 |  | ACT | 11.97 |  |  |  | 11.97
KERN-OLD RIVER #2 | 70 | ETL.8900 |  | ACT | 26.33 |  |  |  | 26.33
KERN-ROSEDALE | 115 | ETL.1980 |  | ACT | 1.77 |  |  |  | 1.77
KERN-STOCKDALE #1 | 230 | ETL.5152 |  | ACT | 6.35 |  |  |  | 6.35
KERN-STOCKDALE #2 | 230 | ETL.5161 |  | ACT | 6.32 |  |  |  | 6.32
KERN-STOCKDALE-LAMONT #1 | 115 | ETL.1990 |  | ACT | 19.66 |  |  |  | 19.66
KERN-STOCKDALE-LAMONT #1 (21KV) | 115 | ETL.1990 |  | IDL | 3.71 |  |  |  | 3.71
KERN-STOCKDALE-LAMONT #2 | 115 | ETL.1940 |  | ACT | 18.23 |  |  |  | 18.23
KERN-WESTPARK #1 | 115 | ETL.2000 |  | ACT | 3.83 |  |  |  | 3.83
KERN-WESTPARK #2 | 115 | ETL.2010 |  | ACT | 3.81 |  |  |  | 3.81
KERNWATER TAP | 115 | ETL.1971 |  | ACT | 0.67 |  |  |  | 0.67
KESWICK-CASCADE | 60 | ETL.7260 |  | ACT | 9.35 | 0.56 | 8.46 |  | 0.33
KESWICK-TRINITY | 60 | ETL.7270 |  | ACT | 30.4 | 5.47 | 23.62 |  | 1.31
KETTLEMAN HILLS TAP | 70 | ETL.8701 |  | ACT | 1.02 |  |  |  | 1.02
KIFER-FMC | 115 | ETL.2020 |  | ACT | 6.02 |  |  |  | 6.02
KILARC-CEDAR CREEK | 60 | ETL.7290 |  | ACT | 13.33 | 13.33 |  |  | 0
KILARC-DESCHUTES | 60 | ETL.7300 |  | ACT | 23.41 | 0.67 | 19.94 |  | 2.8
KILARC-DESCHUTES | 60 | ETL.7300 |  | IDL | 3.26 |  | 2.73 |  | 0.53
KILARC-VOLTA TIE | 60 | ETL.7310 |  | ACT | 1.93 |  | 0.66 |  | 1.27
KING CITY-COBURN #1 | 60 | ETL.7320 |  | ACT | 21.76 |  |  |  | 21.76
KING CITY-COBURN #2 | 60 | ETL.7330 |  | ACT | 15.76 |  |  |  | 15.76
KINGS RIVER-SANGER-REEDLEY | 115 | ETL.2030 |  | ACT | 43.37 |  | 14.47 |  | 28.9
KINGSBURG COGEN TAP | 115 | ETL.2291 |  | ACT | 1.22 |  |  |  | 1.22
KINGSBURG-CORCORAN #1 | 115 | ETL.2040 |  | ACT | 27.46 |  |  |  | 27.46
KINGSBURG-LEMOORE | 70 | ETL.8910 |  | ACT | 27.57 |  |  |  | 27.57
KINGSBURG-WAUKENA SW STA | 115 | ETL.2050 |  | ACT | 25.25 |  |  |  | 25.25
KM GREEN TAP | 115 | ETL.3505 |  | ACT | 1.6 |  | 1.6 |  | 0
KONOCTI-EAGLE ROCK | 60 | ETL.6861 |  | ACT | 9.66 | 7.53 | 0.23 |  | 1.9
KONOCTI-MIDDLETOWN | 60 | ETL.6380 |  | ACT | 19.87 | 0.87 | 15.42 |  | 3.58
KYOHO TAP | 115 | ETL.3891 |  | ACT | 2.2 |  |  |  | 2.2
LAGUNA TAP | 60 | ETL.6912 |  | ACT | 1.68 |  |  |  | 1.68
LAGUNITAS TAP | 60 | ETL.8312 |  | ACT | 0.56 |  |  |  | 0.56
LAKEVILLE #1 | 60 | ETL.7360 |  | ACT | 11.15 | 1.16 | 7.42 |  | 2.57
LAKEVILLE #2 | 60 | ETL.7340 |  | ACT | 21.62 |  | 6.2 |  | 15.42
LAKEVILLE-IGNACIO #1 | 230 | ETL.4940 |  | ACT | 15.49 |  | 0.89 |  | 14.6
LAKEVILLE-IGNACIO #2 | 230 | ETL.3745 |  | ACT | 14.54 |  | 0.71 |  | 13.83
LAKEVILLE-PETALUMA C | 60 | ETL.7350 |  | ACT | 5.36 |  |  |  | 5.36
LAKEVILLE-SOBRANTE #2 | 230 | ETL.4960 |  | ACT | 47.89 |  | 11.02 |  | 36.87
LAKEVILLE-SONOMA #1 | 115 | ETL.2063 |  | ACT | 6.68 |  | 2.54 |  | 4.14
LAKEVILLE-SONOMA #2 | 115 | ETL.2070 |  | ACT | 7.18 |  | 2.54 |  | 4.64
LAKEVILLE-TULUCAY | 230 | ETL.4970 |  | ACT | 17.22 |  | 1.8 |  | 15.42
LAKEWOOD-CLAYTON | 115 | ETL.2082 |  | ACT | 5.52 |  | 1.13 |  | 4.39
LAKEWOOD-MEADOW LANE-CLAYTON | 115 | ETL.2080 |  | ACT | 9.55 |  | 1.13 |  | 8.42
LAKEWOOD-MEADOW LANE-CLAYTON | 115 | ETL.2080 |  | IDL | 0.06 |  |  |  | 0.06
LAMBIE SW STA-BIRDS LANDING SW STA | 230 | ETL.5820 |  | ACT | 7.04 |  |  |  | 7.04
LAMMERS-KASSON | 115 | ETL.3972 |  | ACT | 8.23 |  |  |  | 8.23
LAMONT-GRIMMWAY MALAGA | 115 | ETL.1942 |  | ACT | 3.55 |  |  |  | 3.55
LAS AGUILAS SW STA-PANOCHE #1 | 230 | ETL.1003 |  | ACT | 17.44 |  |  |  | 17.44
LAS AGUILAS SW STA-PANOCHE #2 | 230 | ETL.1002 |  | ACT | 17.44 |  |  |  | 17.44
LAS GALLINAS-SAN RAFAEL | 115 | ETL.1103 |  | ACT | 4.46 |  |  |  | 4.46
LAS PALMAS TAP | 115 | ETL.2181 |  | ACT | 0.85 |  |  |  | 0.85
LAS PERILLAS TAP | 70 | ETL.8463 |  | ACT | 0.39 |  |  |  | 0.39
LAS PLUMAS TAP | 115 | ETL.2653 |  | ACT | 0.48 |  |  |  | 0.48
LAS POSITAS-NEWARK | 230 | ETL.4980 |  | ACT | 20.93 |  | 4.34 |  | 16.59
LAS POSITAS-VASCO | 60 | ETL.7370 |  | ACT | 1.5 |  |  |  | 1.5
LAURELES-OTTER | 60 | ETL.7380 |  | ACT | 15.56 | 12.23 | 3.12 |  | 0.21
LAWRENCE-MONTA VISTA | 115 | ETL.2090 |  | ACT | 9.5 |  |  |  | 9.5
LAYTONVILLE-COVELO | 60 | ETL.7390 |  | ACT | 16.09 |  | 6.59 |  | 9.5
LAYTONVILLE-WILLITS | 60 | ETL.8360 |  | ACT | 22.95 |  | 15.23 |  | 7.72
LE GRAND-CHOWCHILLA | 115 | ETL.2110 |  | ACT | 10.94 |  |  |  | 10.94
LE GRAND-DAIRYLAND | 115 | ETL.2100 |  | ACT | 11.4 |  |  |  | 11.4
LEE TAP | 60 | ETL.7461 |  | IDL | 2.47 |  |  |  | 2.47
LEPRINO FOODS (TRACY) TAP | 115 | ETL.1283 |  | ACT | 0.02 |  |  |  | 0.02
LEPRINO FOODS-LEPRINO SW STA | 115 | ETL.1741 |  | ACT | 6.41 |  |  |  | 6.41
LEPRINO SW STA-GWF HANFORD SW STA | 115 | ETL.1740 |  | ACT | 12.4 |  |  |  | 12.4
LEPRINO SW STA-HENRIETTA PV | 115 | ETL.1738 |  | ACT | 0.06 |  |  |  | 0.06
LEPRINO TAP | 70 | ETL.8771 |  | ACT | 0.47 |  |  |  | 0.47
LERDO-FAMOSO | 115 | ETL.2120 |  | ACT | 13.45 |  |  |  | 13.45
LERDO-KERN OIL-7TH STANDARD | 115 | ETL.1950 |  | ACT | 16.35 |  |  |  | 16.35
LIGHTNER TAP | 70 | ETL.8542 |  | IDL | 2.88 |  |  |  | 2.88
LINCOLN-PLEASANT GROVE | 115 | ETL.7400 |  | ACT | 7.39 |  |  |  | 7.39
LINDE TAP | 115 | ETL.3302 |  | ACT | 0.62 |  |  |  | 0.62
LIVE OAK TAP | 115 | ETL.2130 |  | ACT | 3.97 |  |  |  | 3.97
LIVE OAK-KERN OIL | 115 | ETL.2140 |  | ACT | 4.4 |  |  |  | 4.4
LIVERMORE-LAS POSITAS | 60 | ETL.7410 |  | ACT | 3.63 |  |  |  | 3.63
LIVINGSTON-LIVINGSTON JCT | 70 | ETL.8920 |  | ACT | 23.36 |  |  |  | 23.36
LLAGAS-GILROY FOODS | 115 | ETL.2150 |  | ACT | 1.98 |  |  |  | 1.98
LLAGAS-HOLLISTER | 115 | ETL.2911 |  | ACT | 19.85 |  |  |  | 19.85
LLAGAS-HOLLISTER | 115 | ETL.2911 |  | IDL | 1.71 |  |  |  | 1.71
LOCKEFORD #1 | 60 | ETL.9461 |  | ACT | 12.91 |  |  |  | 12.91
LOCKEFORD-BELLOTA | 230 | ETL.4990 |  | ACT | 12.32 |  |  |  | 12.32
LOCKEFORD-INDUSTRIAL | 60 | ETL.7420 |  | ACT | 6.03 |  |  |  | 6.03
LOCKEFORD-LODI #2 | 60 | ETL.7440 |  | ACT | 9.49 |  |  |  | 9.49
LOCKEFORD-LODI #3 | 60 | ETL.7450 |  | ACT | 15.36 |  |  |  | 15.36
LOCKHEED #1 TAP | 115 | ETL.3051 |  | ACT | 1.71 |  |  |  | 1.71
LOCKHEED #2 TAP | 115 | ETL.2981 |  | ACT | 1.3 |  |  |  | 1.3
LODI STIG-EIGHT MILE ROAD | 230 | ETL.5001 |  | ACT | 2.18 |  |  |  | 2.18
LODI-INDUSTRIAL | 60 | ETL.6755 |  | ACT | 0.98 |  |  |  | 0.98
LOGAN CREEK-DELEVAN | 230 | ETL.6331 |  | ACT | 12.35 |  |  |  | 12.35
LONE STAR TAP | 60 | ETL.6231 |  | ACT | 1.18 |  | 0.76 |  | 0.42
LONE TREE-CAYETANO | 230 | ETL.6160 |  | ACT | 15.4 | 0.86 | 10.68 |  | 3.86
LOS BANOS-DOS AMIGOS | 230 | ETL.5020 |  | ACT | 14.31 |  |  |  | 14.31
LOS BANOS-GATES #1 | 500 | ETL.6000 |  | ACT | 80.85 |  |  |  | 80.85
LOS BANOS-LIVINGSTON JCT-CANAL | 70 | ETL.8940 |  | ACT | 14.32 |  |  |  | 14.32
LOS BANOS-MERCY SPRINGS SW STA | 70 | ETL.8929 |  | ACT | 14.7 |  |  |  | 14.7
LOS BANOS-MIDWAY #2 | 500 | ETL.6010 |  | ACT | 144.6 |  |  |  | 144.6
LOS BANOS-O'NEILL PGP | 70 | ETL.8950 |  | ACT | 3.87 |  |  |  | 3.87
LOS BANOS-PACHECO | 70 | ETL.8960 |  | ACT | 16.31 |  |  |  | 16.31
LOS BANOS-PACHECO | 70 | ETL.8960 |  | IDL | 4.46 |  |  |  | 4.46
LOS BANOS-PADRE FLAT SW STA | 230 | ETL.1092 |  | ACT | 3.67 |  |  |  | 3.67
LOS BANOS-PANOCHE #2 | 230 | ETL.5040 |  | ACT | 37.13 |  |  |  | 37.13
LOS BANOS-QUINTO SW STA | 230 | ETL.5071 |  | ACT | 12.06 |  |  |  | 12.06
LOS BANOS-SAN LUIS PUMPS #1 | 230 | ETL.5050 |  | ACT | 3.43 |  |  |  | 3.43
LOS BANOS-SAN LUIS PUMPS #2 | 230 | ETL.5060 |  | ACT | 3.43 |  |  |  | 3.43
LOS COCHES TAP | 60 | ETL.7331 |  | ACT | 1.32 |  |  |  | 1.32
LOS ESTEROS-AGNEW | 115 | ETL.2690 |  | ACT | 1.37 |  |  |  | 1.37
LOS ESTEROS-METCALF | 230 | ETL.5353 |  | ACT | 63.25 |  | 51.47 |  | 11.78
LOS ESTEROS-MONTAGUE | 115 | ETL.2380 |  | ACT | 4.64 |  |  |  | 4.64
LOS ESTEROS-NORTECH | 115 | ETL.4032 |  | ACT | 2 |  |  |  | 2
LOS ESTEROS-TRIMBLE | 115 | ETL.2550 |  | ACT | 3.73 |  |  |  | 3.73
LOST HILLS TAP | 70 | ETL.8451 |  | ACT | 2.89 |  |  |  | 2.89
LOUISIANA PACIFIC (OROVILLE) TAP | 60 | ETL.7732 |  | ACT | 0.16 |  |  |  | 0.16
LOWER LAKE-HOMESTAKE | 115 | ETL.1481 |  | ACT | 16.08 |  | 15.36 |  | 0.72
LP FLAKEBOARD TAP | 60 | ETL.7111 |  | ACT | 0.51 |  |  |  | 0.51
LUCERNE #1 TAP | 115 | ETL.1331 |  | ACT | 0.23 |  | 0.23 |  | 0
LUCERNE #2 TAP | 115 | ETL.2411 |  | ACT | 0.23 |  | 0.23 |  | 0
LYOTH TAP | 60 | ETL.7232 |  | ACT | 1.34 |  |  |  | 1.34
MABURY TAP | 115 | ETL.2651 |  | ACT | 2.81 |  |  |  | 2.81
MADISON-VACA | 115 | ETL.2170 |  | ACT | 22.99 |  | 2.84 |  | 20.15
MALACHA TAP | 230 | ETL.5910 |  | ACT | 0.12 |  | 0.12 |  | 0
MALAGA-KRCD | 115 | ETL.2294 |  | ACT | 0.99 |  |  |  | 0.99
MALIN-ROUND MTN #2 | 500 | ETL.6020 |  | ACT | 46.9 |  | 46.9 |  | 0
MANCHESTER-AIRWAYS-SANGER | 115 | ETL.2180 |  | ACT | 15.02 |  |  |  | 15.02
MANTECA #1 | 60 | ETL.7460 |  | ACT | 34.52 |  |  |  | 34.52
MANTECA-LOUISE | 60 | ETL.7470 |  | ACT | 12.53 |  |  |  | 12.53
MANTECA-VIERRA | 115 | ETL.2190 |  | ACT | 3.97 |  |  |  | 3.97
MANVILLE TAP | 115 | ETL.1372 |  | ACT | 5.53 |  | 2.73 |  | 2.8
MAPLE CREEK-HOOPA | 60 | ETL.7490 |  | ACT | 29.13 | 13.53 | 11.39 |  | 4.21
MARICOPA-COPUS | 70 | ETL.8851 |  | ACT | 7.86 |  |  |  | 7.86
MARSH TAP | 60 | ETL.7054 |  | ACT | 3.97 |  |  |  | 3.97
MARTIN-DALY CITY #1 | 115 | ETL.2200 |  | ACT | 3.93 |  |  |  | 3.93
MARTIN-DALY CITY #2 | 115 | ETL.2210 |  | ACT | 3.93 |  |  |  | 3.93
MARTIN-EAST GRAND | 115 | ETL.2220 |  | ACT | 3.96 |  |  |  | 3.96
MARTIN-MILLBRAE #1 | 115 | ETL.2230 |  | ACT | 7.28 |  |  |  | 7.28
MARTIN-SF AIRPORT | 115 | ETL.2240 |  | ACT | 5.43 |  |  |  | 5.43
MARTIN-SNEATH LANE | 60 | ETL.7210 |  | ACT | 7.23 |  | 0.79 |  | 6.44
MARTINEZ-SOBRANTE | 115 | ETL.2270 |  | ACT | 16.4 |  | 13.61 |  | 2.79
MCCALL-KINGSBURG #1 | 115 | ETL.2290 |  | ACT | 11.65 |  |  |  | 11.65
MCCALL-KINGSBURG #2 | 115 | ETL.2300 |  | ACT | 11.57 |  |  |  | 11.57
MCCALL-MALAGA | 115 | ETL.2310 |  | ACT | 10.96 |  |  |  | 10.96
MCCALL-REEDLEY | 115 | ETL.2320 |  | ACT | 15.19 |  |  |  | 15.19
MCCALL-SANGER #1 | 115 | ETL.2330 |  | ACT | 9.22 |  |  |  | 9.22
MCCALL-SANGER #2 | 115 | ETL.2340 |  | ACT | 9.21 |  |  |  | 9.21
MCCALL-SANGER #3 | 115 | ETL.2350 |  | ACT | 8.58 |  |  |  | 8.58
MCCALL-WEST FRESNO #2 | 115 | ETL.2370 |  | ACT | 19.61 |  |  |  | 19.61
MCDONALD TAP | 60 | ETL.7053 |  | ACT | 5.88 |  |  |  | 5.88
MCFARLAND TAP | 70 | ETL.9171 |  | ACT | 6 |  |  |  | 6
MCKEE-PIERCY | 115 | ETL.2379 |  | ACT | 7.75 |  |  |  | 7.75
MCSWAIN TAP | 70 | ETL.8991 |  | ACT | 1.38 |  | 0.57 |  | 0.81
MELONES-CURTIS | 115 | ETL.2390 |  | ACT | 14.8 |  | 14.07 |  | 0.73
MELONES-RACETRACK | 115 | ETL.2400 |  | ACT | 10.2 |  | 10.2 |  | 0
MELONES-WILSON | 230 | ETL.5080 |  | ACT | 61.61 |  | 5.23 |  | 56.38
MENDOCINO #1 | 60 | ETL.7530 |  | IDL | 9.1 |  | 8.18 |  | 0.92
MENDOCINO-HARTLEY | 60 | ETL.7510 |  | ACT | 23.21 |  | 21.8 |  | 1.41
MENDOCINO-PHILO JCT-HOPLAND | 60 | ETL.7520 |  | ACT | 21.87 |  | 16.15 |  | 5.72
MENDOCINO-REDBUD | 115 | ETL.2410 |  | ACT | 34.83 |  | 32.61 |  | 2.22
MENDOCINO-UKIAH | 115 | ETL.2420 |  | ACT | 9.83 |  | 7.49 |  | 2.34
MENDOCINO-WILLITS | 60 | ETL.7540 |  | ACT | 14.52 | 3.77 | 8.33 |  | 2.42
MENDOCINO-WILLITS-FORT BRAGG | 60 | ETL.7550 |  | ACT | 43.77 | 3.78 | 36.76 |  | 3.23
MENDOTA BIOMASS TAP | 70 | ETL.8981 |  | ACT | 3.84 |  |  |  | 3.84
MENDOTA-NORTH STAR SOLAR | 115 | ETL.2113 |  | ACT | 0.03 |  |  |  | 0.03
MENDOTA-SAN JOAQUIN-HELM | 70 | ETL.8980 |  | ACT | 26.94 |  |  |  | 26.94
MENLO TAP | 60 | ETL.6571 |  | ACT | 0.37 |  |  |  | 0.37
MERCED #1 | 70 | ETL.9000 |  | ACT | 39.89 |  |  |  | 39.89
MERCED FALLS-EXCHEQUER | 70 | ETL.8990 | PGE | ACT | 6.51 |  | 4.34 |  | 2.17
MERCED-MERCED FALLS | 70 | ETL.9010 |  | ACT | 20.93 |  |  |  | 20.93
MERCY SPRINGS SW STA-CANAL-ORO LOMA | 70 | ETL.8930 |  | ACT | 23.31 |  |  |  | 23.31
MESA-DIVIDE #1 | 115 | ETL.2430 |  | ACT | 14.71 |  |  |  | 14.71
MESA-DIVIDE #2 | 115 | ETL.2440 |  | ACT | 14.72 |  |  |  | 14.72
MESA-SANTA MARIA | 115 | ETL.2450 |  | ACT | 4.36 |  | 0.07 |  | 4.29
MESA-SISQUOC | 115 | ETL.2460 |  | ACT | 17.6 |  | 1.05 |  | 16.55
METCALF SUB INTER-TIE 230KV | 230 | 0.1 |  | ACT | 0.21 |  |  |  | 0.21
METCALF SUB INTER-TIE 230KV | 230 | 0.2 |  | ACT | 0.11 |  |  |  | 0.11
METCALF SUB INTER-TIE 230KV | 230 | 0.3 |  | ACT | 0.15 |  |  |  | 0.15
METCALF-COYOTE PUMPING PLANT | 115 | ETL.2470 |  | ACT | 7.86 |  |  |  | 7.86
METCALF-EDENVALE #2 | 115 | ETL.2490 |  | ACT | 5.6 |  | 1.3 |  | 4.3
METCALF-EL PATIO #1 | 115 | ETL.2500 |  | ACT | 14.38 |  | 3.38 |  | 11
METCALF-EL PATIO #2 | 115 | ETL.2510 |  | ACT | 14.41 |  | 3.38 |  | 11.03
METCALF-EVERGREEN #1 | 115 | ETL.2520 |  | ACT | 10.63 |  |  |  | 10.63
METCALF-GREEN VALLEY | 115 | ETL.2540 |  | ACT | 25.27 | 5.75 | 4.6 |  | 14.92
METCALF-HICKS 1 & 2 | 115 | ETL.4317 |  | IDL | 6.62 |  | 2.83 |  | 3.79
METCALF-MONTA VISTA #3 | 230 | ETL.5091 |  | ACT | 28.59 | 13.12 | 9.59 |  | 5.88
METCALF-MORGAN HILL | 115 | ETL.2570 |  | ACT | 9.72 |  | 1.2 |  | 8.52
METCALF-MOSS LANDING #1 | 230 | ETL.5100 |  | ACT | 35.76 | 7.17 | 9.86 |  | 18.73
METCALF-MOSS LANDING #2 | 230 | ETL.5110 |  | ACT | 35.76 | 7.17 | 9.87 |  | 18.72
METCALF-SALINAS #1 | 115 | ETL.1721 |  | IDL | 1.93 |  |  |  | 1.93
METCALF-SALINAS #2 (12KV) | 115 | ETL.1731 |  | IDL | 6.8 |  |  |  | 6.8
METCALF-SANTA TERESA | 115 | ETL.2480 |  | ACT | 5.4 |  | 1.29 |  | 4.11
MI-WUK-CURTIS | 115 | ETL.1073 |  | ACT | 8.4 | 4.62 | 3.69 |  | 0.09
MIDDLE FORK #1 | 60 | ETL.8405 |  | ACT | 9.45 | 9.45 |  |  | 0
MIDDLE FORK-GOLD HILL | 230 | ETL.5140 |  | ACT | 44.08 | 25.41 | 12.02 |  | 6.65
MIDDLE RIVER TAP | 60 | ETL.7052 |  | ACT | 7.02 |  |  |  | 7.02
MIDSET TAP | 115 | ETL.1581 |  | ACT | 0.72 |  |  |  | 0.72
MIDSUN-MIDWAY | 115 | ETL.2580 |  | ACT | 19.05 |  |  |  | 19.05
MIDWAY-KERN #1 | 230 | ETL.5150 |  | ACT | 41.07 |  |  |  | 41.07
MIDWAY-KERN #3 | 230 | ETL.5160 |  | ACT | 20.74 |  |  |  | 20.74
MIDWAY-KERN #4 | 230 | ETL.5170 |  | ACT | 20.78 |  |  |  | 20.78
MIDWAY-RENFRO-TUPMAN | 115 | ETL.2590 |  | ACT | 22.6 |  |  |  | 22.6
MIDWAY-SANTA MARIA (12KV) | 115 | ETL.9240 |  | IDL | 31.58 | 16.68 | 1.9 |  | 13 | Distribution Transferred
MIDWAY-SANTA MARIA (21KV) | 115 | ETL.9240 |  | IDL | 14.65 |  |  |  | 14.65
MIDWAY-SHAFTER | 115 | ETL.2610 |  | ACT | 13.63 |  |  |  | 13.63
MIDWAY-SUNSET | 230 | ETL.5194 |  | ACT | 0.57 |  |  |  | 0.57
MIDWAY-TAFT | 115 | ETL.2620 |  | ACT | 19.33 |  |  |  | 19.33
MIDWAY-TEMBLOR | 115 | ETL.2630 |  | ACT | 14.7 |  |  |  | 14.7
MIDWAY-TUPMAN-RIO BRAVO-RENFRO | 115 | ETL.2600 |  | ACT | 26.59 |  |  |  | 26.59
MIDWAY-WHEELER RIDGE #1 | 230 | ETL.5190 |  | ACT | 52.68 |  |  |  | 52.68
MIDWAY-WHEELER RIDGE #2 | 230 | ETL.5200 |  | ACT | 52.65 |  |  |  | 52.65
MIDWAY-WHIRLWIND | 500 | ETL.6030 |  | ACT | 52.77 |  | 8.6 |  | 44.17
MILLBRAE-SAN MATEO #1 | 115 | ETL.2640 |  | ACT | 4.71 |  |  |  | 4.71
MILLBRAE-SNEATH LANE | 60 | ETL.7570 |  | ACT | 6.72 |  | 2.15 |  | 4.57
MILLER #1 TAP | 115 | ETL.3992 |  | ACT | 21.28 |  |  |  | 21.28
MILLER #2 TAP | 115 | ETL.4002 |  | ACT | 12.32 |  |  |  | 12.32
MILPITAS-SWIFT | 115 | ETL.2650 |  | ACT | 8.86 |  |  |  | 8.86
MISSION POWER TAP | 115 | ETL.1651 |  | ACT | 1.93 | 1.93 |  |  | 0
MISSOURI FLAT-GOLD HILL #1 | 115 | ETL.2660 |  | ACT | 19.7 | 5.95 | 4.73 |  | 9.02
MISSOURI FLAT-GOLD HILL #2 | 115 | ETL.2670 |  | ACT | 19.69 | 5.91 | 4.76 |  | 9.02
MOCO TAP | 70 | ETL.9233 |  | ACT | 1.64 |  |  |  | 1.64
MOFFETT FIELD TAP | 115 | ETL.3052 |  | ACT | 0.16 |  |  |  | 0.16
MONTA VISTA-BURNS | 60 | ETL.7590 |  | ACT | 18.07 | 12.46 | 4.53 |  | 1.08
MONTA VISTA-COYOTE SW STA | 230 | ETL.5090 |  | ACT | 27.83 | 13.13 | 9.6 |  | 5.1
MONTA VISTA-HICKS | 230 | ETL.5210 |  | ACT | 13.21 |  | 0.38 |  | 12.83
MONTA VISTA-JEFFERSON #1 | 230 | ETL.5220 |  | ACT | 19.72 | 6.35 | 10.5 |  | 2.87
MONTA VISTA-JEFFERSON #2 | 230 | ETL.5230 |  | ACT | 19.73 | 6.36 | 10.5 |  | 2.87
MONTA VISTA-LOS ALTOS | 60 | ETL.7600 |  | ACT | 7.11 |  |  |  | 7.11
MONTA VISTA-LOS GATOS | 60 | ETL.7610 |  | ACT | 10.88 |  | 1.97 |  | 8.91
MONTA VISTA-PERMANENTE | 60 | ETL.7620 |  | ACT | 1.19 |  | 0.11 |  | 1.08
MONTA VISTA-SARATOGA | 230 | ETL.5240 |  | ACT | 5.49 |  | 0.37 |  | 5.12
MONTA VISTA-WOLFE | 115 | ETL.3870 |  | ACT | 2.72 |  |  |  | 2.72
MONTAGUE-TRIMBLE | 115 | ETL.2560 |  | ACT | 2.07 |  |  |  | 2.07
MONTE RIO-FORT ROSS | 60 | ETL.6979 |  | ACT | 14.3 | 7.21 | 4.73 |  | 2.36
MONTE RIO-FULTON | 60 | ETL.7630 |  | ACT | 22.56 | 7.11 | 0.13 |  | 15.32
MONTEZUMA SW STA-BIRDS LANDING SW STA | 230 | ETL.7973 |  | ACT | 0.54 |  |  |  | 0.54
MONTICELLO PH TAP | 115 | ETL.1602 |  | ACT | 0.62 |  | 0.61 |  | 0.01
MORAGA-CASTRO VALLEY | 230 | ETL.5250 |  | ACT | 14.92 | 7.96 | 3.16 |  | 3.8
MORAGA-CLAREMONT #1 | 115 | ETL.2700 |  | ACT | 5.28 | 5.09 | 0.2 |  | -0.01
MORAGA-CLAREMONT #2 | 115 | ETL.2710 |  | ACT | 5.3 | 5.11 | 0.2 |  | -0.01
MORAGA-LAKEWOOD | 115 | ETL.3741 |  | ACT | 15.02 | 1.2 | 5.44 |  | 8.38
MORAGA-OAKLAND #1 | 115 | ETL.2720 |  | ACT | 5.04 | 3.28 | 0.79 |  | 0.97
MORAGA-OAKLAND #2 | 115 | ETL.2730 |  | ACT | 5.04 | 3.28 | 0.79 |  | 0.97
MORAGA-OAKLAND #3 | 115 | ETL.2740 |  | ACT | 5.05 | 3.28 | 0.8 |  | 0.97
MORAGA-OAKLAND #4 | 115 | ETL.2750 |  | ACT | 5.05 | 3.28 | 0.8 |  | 0.97
MORAGA-OAKLAND J | 115 | ETL.2760 |  | ACT | 17.67 | 7.71 | 1.85 |  | 8.11
MORAGA-SAN LEANDRO #1 | 115 | ETL.2770 |  | ACT | 11.14 | 7.73 | 1.85 |  | 1.56
MORAGA-SAN LEANDRO #2 | 115 | ETL.2780 |  | ACT | 11.01 | 7.73 | 1.85 |  | 1.43
MORAGA-SAN LEANDRO #3 | 115 | ETL.2790 |  | ACT | 11 | 7.71 | 1.85 |  | 1.44
MORGAN HILL-LLAGAS | 115 | ETL.2800 |  | ACT | 10.84 |  | 4.04 |  | 6.8
MORRO BAY-CALIFORNIA FLATS SW STA | 230 | ETL.5280 |  | ACT | 46.19 | 5.45 | 9.75 |  | 30.99
MORRO BAY-CALIFORNIA FLATS SW STA | 230 | ETL.5280 |  | IDL | 0.03 |  |  |  | 0.03
MORRO BAY-DIABLO | 230 | ETL.5260 |  | ACT | 15.78 | 5.18 | 7.25 |  | 3.35
MORRO BAY-MESA | 230 | ETL.5290 |  | ACT | 35.25 | 2.47 | 26.6 |  | 6.18
MORRO BAY-SAN LUIS OBISPO #1 | 115 | ETL.2810 |  | ACT | 16.01 |  | 11.32 |  | 4.69
MORRO BAY-SAN LUIS OBISPO #2 | 115 | ETL.2820 |  | ACT | 16.02 |  | 11.33 |  | 4.69
MORRO BAY-SOLAR SW STA #1 | 230 | ETL.5300 |  | ACT | 45.55 | 11.87 | 24.37 |  | 9.31
MORRO BAY-SOLAR SW STA #2 | 230 | ETL.5310 |  | ACT | 45.56 | 11.76 | 24.47 |  | 9.33
MORRO BAY-TEMPLETON | 230 | ETL.5933 |  | ACT | 16.43 | 5.45 | 4.31 |  | 6.67
MOSS LANDING - DALLAS | 500 | ETL.1272 |  | ACT | 0.07 |  |  |  | 0.07
MOSS LANDING-COBURN | 230 | ETL.5330 |  | ACT | 64.03 |  | 35.17 |  | 28.86
MOSS LANDING-CRAZY HORSE CANYON #1 | 115 | ETL.2930 |  | ACT | 10.52 |  |  |  | 10.52
MOSS LANDING-CRAZY HORSE CANYON #2 | 115 | ETL.2983 |  | ACT | 10.59 |  |  |  | 10.59
MOSS LANDING-DEL MONTE #1 | 115 | ETL.2830 |  | ACT | 23.25 |  | 5.73 |  | 17.52
MOSS LANDING-DEL MONTE #2 | 115 | ETL.2840 |  | ACT | 23.29 |  | 5.73 |  | 17.56
MOSS LANDING-GREEN VALLEY #1 | 115 | ETL.2850 |  | ACT | 14.22 |  |  |  | 14.22
MOSS LANDING-GREEN VALLEY #2 | 115 | ETL.2860 |  | ACT | 14.22 |  |  |  | 14.22
MOSS LANDING-LAS AGUILAS SW STA | 230 | ETL.5340 |  | ACT | 51.9 |  | 28.03 |  | 23.87
MOSS LANDING-LOS BANOS | 500 | ETL.6040 |  | ACT | 51.33 |  | 11.64 |  | 39.69
MOSS LANDING-METCALF | 500 | ETL.6050 |  | ACT | 34.98 | 7.17 | 14.28 |  | 13.53
MOSS LANDING-MOSS LANDING PP #1 | 230 | ETL.1282 | NON PGE | ACT | 0.05 |  |  |  | 0.05
MOSS LANDING-MOSS LANDING PP #2 | 230 | ETL.1296 |  | ACT | 0.05 |  |  |  | 0.05
MOSS LANDING-SALINAS #1 | 115 | ETL.2880 |  | ACT | 11.99 |  |  |  | 11.99
MOSS LANDING-SALINAS #2 | 115 | ETL.2890 |  | ACT | 12.03 |  |  |  | 12.03
MTN GATE JCT-CASCADE | 60 | ETL.7640 |  | ACT | 6.58 |  | 6.58 |  | 0
MTN GATE TAP | 60 | ETL.7641 |  | ACT | 0.7 |  | 0.7 |  | 0
MTN QUARRIES TAP | 60 | ETL.6991 |  | ACT | 2.63 |  | 1.98 |  | 0.65
MTN VIEW-MONTA VISTA | 115 | ETL.2920 |  | ACT | 4.8 |  |  |  | 4.8
MULE CREEK TAP | 60 | ETL.8254 |  | ACT | 0.01 |  |  |  | 0.01
MUSTANG SW STA-CABALLO-SLATE | 230 | ETL.1172 |  | ACT | 0.07 |  |  |  | 0.07
MUSTANG SW STA-GREGG | 230 | ETL.4700 |  | ACT | 45.47 |  |  |  | 45.47
MUSTANG SW STA-MCCALL | 230 | ETL.4710 |  | ACT | 42.11 |  |  |  | 42.11
MUSTANG TAP | 70 | ETL.9091 |  | ACT | 0.71 |  | 0.71 |  | 0
NARROWS #1 TAP | 60 | ETL.6511 |  | ACT | 2.65 |  | 2.65 |  | 0
NARROWS #2 TAP | 60 | ETL.6521 |  | ACT | 3.09 |  | 3.09 |  | 0
NAVY LAB TAP | 60 | ETL.6711 |  | ACT | 0.19 |  |  |  | 0.19
NEW HOGAN TAP | 60 | ETL.8211 |  | ACT | 0.06 |  |  |  | 0.06
NEWARK E-F BUS TIE | 230 | ETL.4640 |  | ACT | 0.22 |  |  |  | 0.22
NEWARK-AMES #1 | 115 | ETL.2940 |  | ACT | 8.3 |  |  |  | 8.3
NEWARK-AMES #2 | 115 | ETL.2950 |  | ACT | 8.28 |  |  |  | 8.28
NEWARK-AMES #3 | 115 | ETL.2960 |  | ACT | 8.28 |  |  |  | 8.28
NEWARK-AMES DISTRIBUTION | 115 | ETL.4313 |  | ACT | 8.25 |  |  |  | 8.25
NEWARK-APPLIED MATERIALS | 115 | ETL.2980 |  | ACT | 11.37 |  |  |  | 11.37
NEWARK-DECOTO | 60 | ETL.7650 |  | IDL | 6.1 |  |  |  | 6.1
NEWARK-DIXON LANDING | 115 | ETL.2990 |  | ACT | 4.69 |  |  |  | 4.69
NEWARK-FREMONT #1 | 115 | ETL.3000 |  | ACT | 3.67 |  |  |  | 3.67
NEWARK-FREMONT #2 | 115 | ETL.3010 |  | ACT | 3.74 |  |  |  | 3.74
NEWARK-JARVIS #1 | 115 | ETL.3020 |  | ACT | 14.25 |  |  |  | 14.25
NEWARK-JARVIS #2 | 115 | ETL.3030 |  | ACT | 14.48 |  |  |  | 14.48
NEWARK-KIFER | 115 | ETL.3040 |  | ACT | 10.61 |  |  |  | 10.61
NEWARK-LAWRENCE | 115 | ETL.3050 |  | ACT | 10.25 |  |  |  | 10.25
NEWARK-LIVERMORE | 60 | ETL.7660 |  | ACT | 19.05 |  | 3.93 |  | 15.12
NEWARK-LOS ESTEROS | 230 | ETL.2970 |  | ACT | 5.65 |  |  |  | 5.65
NEWARK-MILPITAS #1 | 115 | ETL.3070 |  | ACT | 8.48 |  |  |  | 8.48
NEWARK-MILPITAS #2 | 115 | ETL.3080 |  | ACT | 10.3 |  |  |  | 10.3
NEWARK-NORTHERN RECEIVING STATION #1 | 115 | ETL.3100 |  | ACT | 8.76 |  |  |  | 8.76
NEWARK-NORTHERN RECEIVING STATION #2 | 115 | ETL.3110 |  | ACT | 8.67 |  |  |  | 8.67
NEWARK-NUMMI | 115 | ETL.3090 |  | ACT | 4.94 |  |  |  | 4.94
NEWARK-RAVENSWOOD | 230 | ETL.5936 |  | ACT | 8.91 |  |  |  | 8.91
NEWARK-TRIMBLE | 115 | ETL.3120 |  | ACT | 12.36 |  |  |  | 12.36
NEWARK-VALLECITOS | 60 | ETL.7670 |  | ACT | 12.37 |  | 2.23 |  | 10.14
NICOLAUS-CATLETT JCT | 60 | ETL.7680 |  | ACT | 20.15 |  |  |  | 20.15
NICOLAUS-CATLETT JCT | 60 | ETL.7680 |  | IDL | 4.45 |  |  |  | 4.45
NICOLAUS-CATLETT JCT (12KV) | 60 | ETL.7680 |  | IDL | 14.18 |  |  |  | 14.18
NICOLAUS-MARYSVILLE | 60 | ETL.7690 |  | ACT | 18.73 |  |  |  | 18.73
NICOLAUS-PLAINFIELD | 60 | ETL.7700 |  | ACT | 30.63 |  |  |  | 30.63
NICOLAUS-WILKINS SLOUGH | 60 | ETL.7710 |  | ACT | 42.74 |  |  |  | 42.74
NORTECH-NORTHERN RECEIVING STATION | 115 | ETL.1551 |  | ACT | 2.21 |  |  |  | 2.21
NORTH DUBLIN-CAYETANO | 230 | ETL.4500 |  | ACT | 3.02 |  | 3.02 |  | 0
NORTH DUBLIN-VINEYARD | 230 | ETL.4501 |  | ACT | 12.46 |  | 4.9 |  | 7.56
NORTH TOWER-MARTINEZ JCT #1 (21KV) | 115 | ETL.3130 |  | IDL | 2.61 |  | 1.75 |  | 0.86
NORTHERN RECEIVING STATION-SCOTT #1 | 115 | ETL.3101 |  | ACT | 2.08 |  |  |  | 2.08
NORTHERN RECEIVING STATION-SCOTT #2 | 115 | ETL.3111 |  | ACT | 1.98 |  |  |  | 1.98
NOTRE DAME-BUTTE | 115 | ETL.4312 |  | ACT | 2.02 |  |  |  | 2.02
OAK PARK TAP | 60 | ETL.8142 |  | ACT | 0.87 |  |  |  | 0.87
OAKHURST TAP | 115 | ETL.1252 |  | ACT | 18.16 | 0.89 | 16.58 |  | 0.69
OAKLAND C-MARITIME | 115 | ETL.3135 |  | ACT | 2.36 |  |  |  | 2.36
OAKLAND C-TURBINES | 115 | ETL.3137 |  | ACT | 0.19 |  |  |  | 0.19
OAKLAND J-GRANT | 115 | ETL.3140 |  | ACT | 14.83 |  |  |  | 14.83
OCEANO-CALLENDER SW STA | 115 | ETL.2394 |  | ACT | 4.22 |  | 3 |  | 1.22
OIL CITY TAP | 70 | ETL.8574 |  | ACT | 0.05 |  |  |  | 0.05
OILFIELDS-SALINAS RIVER | 60 | ETL.7728 |  | ACT | 1.46 |  |  |  | 1.46
OILFIELDS-SARGENT CANYON | 60 | ETL.7725 |  | ACT | 2.02 |  |  |  | 2.02
OLEUM-G #1 | 115 | ETL.3150 |  | ACT | 11.29 | 2.06 | 6.95 |  | 2.28
OLEUM-G #2 | 115 | ETL.3160 |  | ACT | 11.3 | 2.06 | 6.95 |  | 2.29
OLEUM-MARTINEZ | 115 | ETL.3170 |  | ACT | 10.5 |  | 7.03 |  | 3.47
OLEUM-NORTH TOWER-CHRISTIE | 115 | ETL.3180 |  | ACT | 8.33 |  | 6.55 |  | 1.78
OLEUM-UNOCAL #1 | 115 | ETL.4260 |  | ACT | 0.01 |  |  |  | 0.01
OLEUM-UNOCAL #2 | 115 | ETL.4270 |  | ACT | 0.05 |  |  |  | 0.05
OLIVE SW STA-SMYRNA | 115 | ETL.1923 |  | ACT | 11.07 |  |  |  | 11.07
ORO FINO TAP | 60 | ETL.6721 |  | ACT | 1.3 | 1.3 |  |  | 0
ORO LOMA-CANAL #1 | 70 | ETL.9020 |  | ACT | 24.55 |  |  |  | 24.55
ORO LOMA-MENDOTA | 70 | ETL.9030 |  | ACT | 29.41 |  |  |  | 29.41
OROVILLE-TABLE MTN #2 (CDWR) | 230 | ETL.6623 | NON PGE | ACT | 10.09 |  | 3.67 |  | 6.42 | Non-PGE
OROVILLE-THERMALITO-TABLE MTN #1 (CDWR) | 230 | ETL.6621 | NON PGE | ACT | 12.44 |  | 5.06 |  | 7.38 | Non-PGE
OROVILLE-THERMALITO-TABLE MTN #3 (CDWR) | 230 | ETL.6622 | NON PGE | ACT | 12.4 |  | 3.6 |  | 8.8 | Non-PGE
OWENS ILLINOIS TAP | 115 | ETL.3971 |  | ACT | 0.68 |  |  |  | 0.68
OXBOW TAP | 60 | ETL.7561 |  | ACT | 0.15 | 0.15 |  |  | 0
OXFORD TAP | 115 | ETL.3241 |  | ACT | 3.87 |  |  |  | 3.87
P-X #2 | 115 | ETL.3125 |  | ACT | 0.28 |  |  |  | 0.28
PACIFIC ETHANOL TAP | 60 | ETL.8325 |  | ACT | 0.68 |  |  |  | 0.68
PACIFIC LUMBER (SCOTIA) TAP | 60 | ETL.7852 |  | ACT | 0.52 |  |  |  | 0.52
PACIFIC OROVILLE POWER TAP | 60 | ETL.7731 |  | IDL | 0.78 |  |  |  | 0.78
PADRE FLAT SW STA-PANOCHE | 230 | ETL.5030 |  | ACT | 33.58 |  |  |  | 33.58
PAIGE SOLAR TAP | 70 | ETL.1262 | PGE | ACT | 1.04 |  |  |  | 1.04
PALERMO-BOGUE | 115 | ETL.3200 |  | ACT | 35.73 |  | 1.24 |  | 34.49
PALERMO-COLGATE | 230 | ETL.5360 |  | ACT | 29.61 |  | 16.87 |  | 12.74
PALERMO-NICOLAUS | 115 | ETL.3210 |  | ACT | 41.18 |  | 1.19 |  | 39.99
PALERMO-OROVILLE #1 | 60 | ETL.7730 |  | ACT | 6.94 |  | 1.18 |  | 5.76
PALERMO-OROVILLE #2 | 60 | ETL.7740 |  | ACT | 10.13 |  | 2.86 |  | 7.27
PALERMO-PEASE | 115 | ETL.3220 |  | ACT | 26.53 |  | 1.08 |  | 25.45
PALERMO-WYANDOTTE | 115 | ETL.4315 |  | ACT | 3.44 |  | 1.26 |  | 2.18
PANOCHE-CAL PEAK-STARWOOD | 115 | ETL.1051 |  | ACT | 0.09 |  |  |  | 0.09
PANOCHE-EXCELSIOR SW STA #1 | 115 | ETL.3250 |  | ACT | 28.5 |  |  |  | 28.5
PANOCHE-EXCELSIOR SW STA #2 | 115 | ETL.3260 |  | ACT | 28.5 |  |  |  | 28.5
PANOCHE-MENDOTA | 115 | ETL.3230 |  | ACT | 10.08 |  |  |  | 10.08
PANOCHE-ORO LOMA | 115 | ETL.3240 |  | ACT | 18.93 |  |  |  | 18.93
PANOCHE-PANOCHE ENERGY CENTER | 230 | ETL.2293 |  | ACT | 0.09 |  |  |  | 0.09
PANOCHE-TRANQUILLITY SW STA #1 | 230 | ETL.5000 |  | ACT | 12.14 |  |  |  | 12.14
PANOCHE-TRANQUILLITY SW STA #2 | 230 | ETL.5481 |  | ACT | 12.14 |  |  |  | 12.14
PARADISE-BUTTE | 115 | ETL.4396 |  | ACT | 13.58 | 0.62 | 7.59 |  | 5.37
PARADISE-TABLE MTN | 115 | ETL.4316 |  | ACT | 35.6 | 6.69 | 19.93 |  | 8.98
PARAMOUNT FARMS TAP | 115 | ETL.1744 |  | ACT | 0.57 |  |  |  | 0.57
PARDEE #1 TAP | 60 | ETL.8231 |  | ACT | 4.33 |  | 4.33 |  | 0
PARDEE #2 TAP | 60 | ETL.8251 |  | ACT | 0.11 |  | 0.1 |  | 0.01
PARKWAY-MORAGA | 230 | ETL.5930 |  | ACT | 23.64 | 4.31 | 12.24 |  | 7.09
PASO ROBLES-TEMPLETON | 70 | ETL.9400 |  | ACT | 4.9 |  |  |  | 4.9
PEABODY-BIRDS LANDING SW STA | 230 | ETL.6171 |  | ACT | 19.85 |  |  |  | 19.85
PEACHTON-PEASE | 60 | ETL.8426 |  | ACT | 16.35 |  |  |  | 16.35
PEASE-HARTER | 60 | ETL.7760 |  | ACT | 15.91 |  |  |  | 15.91
PEASE-MARYSVILLE-HARTER | 60 | ETL.7770 |  | ACT | 10.35 |  |  |  | 10.35
PEASE-RIO OSO | 115 | ETL.3270 |  | ACT | 27.61 |  |  |  | 27.61
PENN ZIER TAP | 70 | ETL.8575 |  | ACT | 4.78 |  |  |  | 4.78
PENN ZIER TAP | 70 | ETL.8575 |  | IDL | 0.21 |  |  |  | 0.21
PENNGROVE SUB TAP | 115 | ETL.2061 |  | ACT | 0.81 |  |  |  | 0.81
PENTLAND TAP | 70 | ETL.8973 |  | ACT | 0.55 |  |  |  | 0.55
PEORIA TAP | 115 | ETL.2391 |  | ACT | 0.85 |  | 0.85 |  | 0
PERMANENTE #1 TAP | 60 | ETL.7621 |  | ACT | 0.31 |  | 0.13 |  | 0.18
PERMANENTE #2 TAP | 60 | ETL.7622 |  | ACT | 0.51 |  | 0.34 |  | 0.17
PHILO JCT-ELK | 60 | ETL.7780 |  | ACT | 37.24 |  | 32.94 |  | 4.3
PIERCY-METCALF | 115 | ETL.4318 |  | ACT | 4.72 |  |  |  | 4.72
PINE GROVE TAP | 60 | ETL.8351 |  | ACT | 2.67 | 0.48 | 2.19 |  | 0
PIT #1-COTTONWOOD | 230 | ETL.5390 |  | ACT | 59.75 | 7.62 | 42.04 |  | 10.09
PIT #1-HAT CREEK #2-BURNEY | 60 | ETL.7040 |  | ACT | 12.92 |  | 10.58 |  | 2.34
PIT #1-HAT CREEK #2-BURNEY | 60 | ETL.7040 |  | IDL | 0.05 |  | 0.05 |  | 0
PIT #1-MCARTHUR | 60 | ETL.7790 |  | ACT | 7.3 |  | 3.08 |  | 4.22
PIT #3-CARBERRY SW STA | 230 | ETL.5450 |  | ACT | 10.91 |  | 9.18 |  | 1.73
PIT #3-PIT #1 | 230 | ETL.5400 |  | ACT | 22.69 |  | 19.32 |  | 3.37
PIT #4 TAP | 230 | ETL.5432 | POWERGEN | ACT | 7.03 |  | 7.03 |  | 0
PIT #5-ROUND MTN #1 | 230 | ETL.5420 |  | ACT | 13.12 |  | 13.12 |  | 0
PIT #5-ROUND MTN #2 | 230 | ETL.5430 |  | ACT | 13.11 |  | 13.11 |  | 0
PIT #6 JCT-ROUND MTN | 230 | ETL.5440 |  | ACT | 8.15 |  | 8.15 |  | 0
PIT #6 TAP | 230 | ETL.5441 | POWERGEN | ACT | 3.43 |  | 3.43 |  | 0
PIT #7 TAP | 230 | ETL.5442 | POWERGEN | ACT | 3.59 |  | 3.59 |  | 0
PITTSBURG #1 TAP (NO FLY) | 60 | ETL.6551 |  | IDL | 1.17 |  |  |  | 1.17
PITTSBURG-BLACK DIAMOND ENERGY STORAGE | 230 | ETL.1192 |  | ACT | 0.06 |  |  |  | 0.06
PITTSBURG-CLAYTON #1 | 115 | ETL.3280 |  | ACT | 16.82 |  | 6.01 |  | 10.81
PITTSBURG-CLAYTON #3 | 115 | ETL.3290 |  | ACT | 8.41 |  | 2.91 |  | 5.5
PITTSBURG-CLAYTON #4 | 115 | ETL.3291 |  | ACT | 8.32 |  | 2.91 |  | 5.41
PITTSBURG-COLUMBIA STEEL | 115 | ETL.3300 |  | ACT | 9.23 |  | 1.21 |  | 8.02
PITTSBURG-DELTA ENERGY CENTER #1 | 230 | ETL.1254 | NON PGE | ACT | 0.01 |  |  |  | 0.01
PITTSBURG-DELTA ENERGY CENTER #2 | 230 | ETL.3315 | NON PGE | ACT | 0.01 |  |  |  | 0.01
PITTSBURG-EASTSHORE | 230 | ETL.5462 |  | ACT | 34.93 | 11.9 | 7.78 |  | 15.25
PITTSBURG-KIRKER-COLUMBIA STEEL | 115 | ETL.3310 |  | ACT | 9.26 |  | 1.13 |  | 8.13
PITTSBURG-LOS MEDANOS #1 | 115 | ETL.3304 |  | ACT | 0.5 |  |  |  | 0.5
PITTSBURG-LOS MEDANOS #2 | 115 | ETL.3305 |  | ACT | 0.5 |  |  |  | 0.5
PITTSBURG-MARTINEZ #1 | 115 | ETL.3320 |  | ACT | 17.23 |  | 0.34 |  | 16.89
PITTSBURG-MARTINEZ #2 | 115 | ETL.3330 |  | ACT | 15.83 |  | 0.38 |  | 15.45
PITTSBURG-SAN MATEO | 230 | ETL.5463 |  | ACT | 47.4 | 11.89 | 7.78 |  | 27.73
PITTSBURG-SAN RAMON | 230 | ETL.5490 |  | ACT | 21.66 | 6.1 | 7.7 |  | 7.86
PITTSBURG-TASSAJARA | 230 | ETL.5470 |  | ACT | 17.36 | 6.11 | 6.65 |  | 4.6
PITTSBURG-TESLA #1 | 230 | ETL.5510 |  | ACT | 31.35 |  | 18 |  | 13.35
PITTSBURG-TESLA #2 | 230 | ETL.5520 |  | ACT | 31.32 |  | 18.03 |  | 13.29
PITTSBURG-TESORO | 230 | ETL.5500 |  | ACT | 11.27 |  |  |  | 11.27
PITTSBURG-TIDEWATER | 230 | ETL.5530 |  | ACT | 11.27 |  |  |  | 11.27
PLACER-DEL MAR | 60 | ETL.7800 |  | ACT | 10.8 |  | 4.52 |  | 6.28
PLACER-GOLD HILL #1 | 115 | ETL.3340 |  | ACT | 20.67 |  | 9.92 |  | 10.75
PLACER-GOLD HILL #2 | 115 | ETL.4290 |  | ACT | 20.67 |  | 9.92 |  | 10.75
PLUMAS-SIERRA TAP | 60 | ETL.6291 |  | ACT | 0.75 | 0.01 | 0.06 |  | 0.68
POE-RIO OSO | 230 | ETL.5540 |  | ACT | 56.09 | 4.41 | 14.01 |  | 37.67
POINT PINOLE TAP | 115 | ETL.3792 |  | ACT | 1.29 |  |  |  | 1.29
POINT PINOLE TAP | 115 | ETL.3792 |  | IDL | 0.01 |  |  |  | 0.01
PORT COSTA BRICK TAP | 60 | ETL.6371 |  | IDL | 1.89 |  | 1.88 |  | 0.01
POST OFFICE TAP | 115 | ETL.4122 |  | ACT | 0.75 |  |  |  | 0.75
POTTER VALLEY-MENDOCINO | 60 | ETL.7810 |  | ACT | 10.94 |  | 8.38 |  | 2.56
POTTER VALLEY-WILLITS | 60 | ETL.7820 |  | ACT | 13.16 | 5.51 | 6.35 |  | 1.3
PSE MCKITTRICK TAP | 115 | ETL.2632 |  | ACT | 5.21 |  |  |  | 5.21
QUEBEC TAP | 115 | ETL.1311 |  | ACT | 4.35 |  |  |  | 4.35
QUINTO SW STA-WESTLEY | 230 | ETL.5070 |  | ACT | 57.55 |  | 6.81 |  | 50.74
RACETRACK TAP | 115 | ETL.2393 |  | ACT | 3.54 |  | 3.54 |  | 0
RADUM-LIVERMORE | 60 | ETL.7830 |  | ACT | 4.66 |  |  |  | 4.66
RADUM-VALLECITOS | 60 | ETL.8280 |  | ACT | 10.6 |  |  |  | 10.6
RAINBOW TAP | 115 | ETL.2031 |  | ACT | 2.59 |  |  |  | 2.59
RALPH TAP | 230 | ETL.4931 |  | ACT | 0.06 |  |  |  | 0.06
RANCHERS COTTON TAP | 115 | ETL.2311 |  | ACT | 2.1 |  |  |  | 2.1
RANCHO SECO-BELLOTA #1 | 230 | ETL.5550 |  | ACT | 27.39 |  |  |  | 27.39
RANCHO SECO-BELLOTA #2 | 230 | ETL.5560 |  | ACT | 27.36 |  |  |  | 27.36
RAVENSWOOD-AMES #1 | 115 | ETL.3360 |  | ACT | 7.07 |  |  |  | 7.07
RAVENSWOOD-AMES #2 | 115 | ETL.3370 |  | ACT | 7.09 |  |  |  | 7.09
RAVENSWOOD-BAIR #1 | 115 | ETL.3380 |  | ACT | 7.43 |  |  |  | 7.43
RAVENSWOOD-BAIR #2 | 115 | ETL.3385 |  | ACT | 11.29 |  |  |  | 11.29
RAVENSWOOD-COOLEY LANDING #1 | 115 | ETL.3390 |  | ACT | 1.62 |  |  |  | 1.62
RAVENSWOOD-COOLEY LANDING #2 | 115 | ETL.3400 |  | ACT | 1.62 |  |  |  | 1.62
RAVENSWOOD-PALO ALTO #1 | 115 | ETL.3410 |  | ACT | 4.27 |  |  |  | 4.27
RAVENSWOOD-PALO ALTO #2 | 115 | ETL.3420 |  | ACT | 4.26 |  |  |  | 4.26
RAVENSWOOD-SAN MATEO | 115 | ETL.3430 |  | ACT | 12.04 |  |  |  | 12.04
RAVENSWOOD-SAN MATEO #1 | 230 | ETL.5580 |  | ACT | 11.89 |  |  |  | 11.89
RAVENSWOOD-SAN MATEO #2 | 230 | ETL.5351 |  | ACT | 11.88 |  |  |  | 11.88
RED BANK TAP | 60 | ETL.6631 |  | ACT | 0.68 |  |  |  | 0.68
REEDLEY-DINUBA #1 | 70 | ETL.9050 |  | ACT | 7.7 |  |  |  | 7.7
REEDLEY-OROSI | 70 | ETL.9060 |  | ACT | 10.89 |  |  |  | 10.89
RESERVE OIL TAP | 70 | ETL.8721 |  | ACT | 0.58 |  |  |  | 0.58
RINCON #1 TAP | 115 | ETL.1601 |  | ACT | 0.57 | 0.08 | 0.49 |  | 0
RINCON #2 TAP | 115 | ETL.1611 |  | ACT | 0.55 | 0.07 | 0.48 |  | 0
RIO BRAVO (FRESNO) TAP | 115 | ETL.2312 |  | ACT | 0.32 |  |  |  | 0.32
RIO BRAVO (ROCKLIN) TAP | 115 | ETL.7974 |  | ACT | 0.4 |  |  |  | 0.4
RIO BRAVO HYDRO | 70 | ETL.9070 |  | ACT | 0.24 |  |  |  | 0.24
RIO BRAVO TOMATO TAP | 115 | ETL.8328 |  | ACT | 0.43 |  |  |  | 0.43
RIO BRAVO-KERN OIL | 115 | ETL.1922 |  | IDL | 7.28 |  |  |  | 7.28
RIO DELL JCT-BRIDGEVILLE | 60 | ETL.7850 |  | ACT | 21.23 |  | 15.05 |  | 6.18
RIO DELL TAP | 60 | ETL.7851 |  | ACT | 5.35 |  | 0.79 |  | 4.56
RIO OSO-ATLANTIC | 230 | ETL.5590 |  | ACT | 17.68 |  |  |  | 17.68
RIO OSO-BRIGHTON | 230 | ETL.5600 |  | ACT | 27.17 |  |  |  | 27.17
RIO OSO-GOLD HILL | 230 | ETL.5610 |  | ACT | 28.63 |  |  |  | 28.63
RIO OSO-LINCOLN | 115 | ETL.1320 |  | ACT | 11.04 |  |  |  | 11.04
RIO OSO-LOCKEFORD | 230 | ETL.5620 |  | ACT | 65.13 |  |  |  | 65.13
RIO OSO-NICOLAUS | 115 | ETL.3440 |  | ACT | 5.39 |  |  |  | 5.39
RIO OSO-WEST SACRAMENTO | 115 | ETL.3450 |  | ACT | 43.55 |  |  |  | 43.55
RIO OSO-WOODLAND #1 | 115 | ETL.3460 |  | ACT | 45.25 |  |  |  | 45.25
RIO OSO-WOODLAND #2 | 115 | ETL.3470 |  | ACT | 53.37 |  |  |  | 53.37
RIPON-MANTECA | 115 | ETL.1062 |  | ACT | 9.14 |  |  |  | 9.14
RIVER ROCK TAP | 70 | ETL.8503 |  | ACT | 1.22 |  |  |  | 1.22
RIVERBANK JCT SW STA-RIPON | 115 | ETL.3841 |  | ACT | 18 |  |  |  | 18
ROBERTSON TAP | 60 | ETL.8322 |  | ACT | 0.82 |  |  |  | 0.82
ROCK CREEK-POE | 230 | ETL.5630 |  | ACT | 26.98 | 6.85 | 20.13 |  | 0
ROLLINS TAP | 60 | ETL.6762 |  | ACT | 0.73 | 0.34 | 0.39 |  | 0
ROSE TAP | 70 | ETL.9251 |  | ACT | 0.31 |  |  |  | 0.31
ROSSMOOR #1 TAP | 230 | ETL.5451 |  | ACT | 0.69 | 0.48 |  |  | 0.21
ROSSMOOR #2 TAP | 230 | ETL.5461 |  | ACT | 0.66 | 0.46 |  |  | 0.2
ROUGH & READY TAP | 60 | ETL.8324 |  | ACT | 0.95 |  |  |  | 0.95
ROUND MTN-COTTONWOOD #2 | 230 | ETL.5640 |  | ACT | 33.67 | 3.73 | 22.05 |  | 7.89
ROUND MTN-COTTONWOOD #3 | 230 | ETL.5650 |  | ACT | 33.36 | 7.17 | 19.17 |  | 7.02
ROUND MTN-TABLE MTN #1 | 500 | ETL.6060 |  | ACT | 89.03 | 11.74 | 64.63 |  | 12.66
ROUND MTN-TABLE MTN #2 | 500 | ETL.6070 |  | ACT | 89.02 | 11.77 | 67.19 |  | 10.06
RUSSELL CITY ENERGY CENTER-EASTSHORE #1 | 230 | ETL.6155 |  | ACT | 1.19 |  |  |  | 1.19
RUSSELL CITY ENERGY CENTER-EASTSHORE #2 | 230 | ETL.6157 |  | ACT | 1.2 |  |  |  | 1.2
SAFEWAY TAP | 115 | ETL.3984 |  | ACT | 0.68 |  |  |  | 0.68
SALADO-CROW CREEK SW STA | 60 | ETL.7858 |  | ACT | 3.77 |  |  |  | 3.77
SALADO-NEWMAN #2 | 60 | ETL.7870 |  | ACT | 21.58 |  |  |  | 21.58
SALINAS-FIRESTONE #1 | 60 | ETL.7900 |  | ACT | 6.15 |  |  |  | 6.15
SALINAS-FORT ORD #1 | 60 | ETL.7890 |  | ACT | 10.22 |  | 3.02 |  | 7.2
SALINAS-FORT ORD #2 | 60 | ETL.8423 |  | ACT | 10.15 |  | 3 |  | 7.15
SALINAS-LAGUNITAS | 60 | ETL.7920 |  | ACT | 5.84 |  |  |  | 5.84
SALINAS-LAURELES | 60 | ETL.7930 |  | ACT | 27.44 |  | 18.24 |  | 9.2
SALINAS-SPENCE | 60 | ETL.7910 |  | ACT | 11.61 |  |  |  | 11.61
SALMON CREEK TAP | 60 | ETL.6981 |  | ACT | 10.51 | 1.04 | 5.4 |  | 4.07
SALT SPRINGS-TIGER CREEK | 115 | ETL.3500 |  | ACT | 16.48 | 1.66 | 14.82 |  | 0
SAN ANDREAS (CCSF) TAP | 60 | ETL.7571 |  | ACT | 0.39 |  |  |  | 0.39
SAN ARDO TAP | 60 | ETL.6421 |  | ACT | 0.34 |  |  |  | 0.34
SAN BENITO-HOLLISTER | 115 | ETL.2901 |  | ACT | 8.29 |  |  |  | 8.29
SAN BERNARD-TEJON | 70 | ETL.9080 |  | ACT | 6.96 |  |  |  | 6.96
SAN BRUNO TAP | 60 | ETL.7572 |  | ACT | 1.12 |  | 0.52 |  | 0.6
SAN FRANCISCO #2 | 115 | ETL.3279 |  | IDL | 3.15 |  |  |  | 3.15
SAN JOSE A-SAN JOSE B | 115 | ETL.3510 |  | ACT | 1.15 |  |  |  | 1.15
SAN JOSE B-STONE-EVERGREEN | 115 | ETL.1550 |  | ACT | 8.56 |  |  |  | 8.56
SAN LEANDRO-OAKLND J #1 | 115 | ETL.3520 |  | ACT | 6.7 |  |  |  | 6.7
SAN LUIS #3 TAP | 115 | ETL.3244 |  | ACT | 16.11 |  |  |  | 16.11
SAN LUIS #5 TAP | 115 | ETL.3243 |  | ACT | 1.88 |  |  |  | 1.88
SAN LUIS OBISPO-CAYUCOS | 70 | ETL.9090 |  | ACT | 23.39 |  | 13.39 |  | 10
SAN LUIS OBISPO-OCEANO | 115 | ETL.3530 |  | ACT | 19.9 | 2.15 | 9.72 |  | 8.03
SAN LUIS OBISPO-SANTA MARIA | 115 | ETL.3540 |  | ACT | 25.96 | 2.16 | 11.12 |  | 12.68
SAN MATEO-BAIR | 60 | ETL.7940 |  | ACT | 13.97 |  |  |  | 13.97
SAN MATEO-BAY MEADOWS #1 | 115 | ETL.3550 |  | ACT | 4.3 |  |  |  | 4.3
SAN MATEO-BAY MEADOWS #2 | 115 | ETL.3560 |  | ACT | 4.26 |  |  |  | 4.26
SAN MATEO-BELMONT | 115 | ETL.3570 |  | ACT | 7.2 |  |  |  | 7.2
SAN MATEO-HILLSDALE JCT | 60 | ETL.7950 |  | ACT | 6.85 |  | 1.15 |  | 5.7
SAN MATEO-MARTIN #3 | 115 | ETL.3580 |  | ACT | 11.55 |  |  |  | 11.55
SAN MATEO-MARTIN #4 | 115 | ETL.7500 |  | ACT | 11.62 |  |  |  | 11.62
SAN MATEO-MARTIN #6 | 115 | ETL.3590 |  | ACT | 11.69 |  |  |  | 11.69
SAN MIGUEL-PASO ROBLES | 70 | ETL.9390 |  | ACT | 9.92 |  |  |  | 9.92
SAN PABLO #1 TAP | 115 | ETL.3801 |  | ACT | 0.44 |  |  |  | 0.44
SAN PABLO #2 TAP | 115 | ETL.3791 |  | ACT | 0.45 |  |  |  | 0.45
SAN RAMON RESEARCH CENTER TAP | 230 | ETL.5921 |  | ACT | 3.27 |  |  |  | 3.27
SAN RAMON-MORAGA | 230 | ETL.5660 |  | ACT | 22.24 | 13.67 | 3.24 |  | 5.33
SAN RAMON-RADUM | 60 | ETL.7960 |  | ACT | 7.06 |  |  |  | 7.06
SANDBAR TAP | 115 | ETL.1403 |  | ACT | 0.1 | 0.1 |  |  | 0
SANGER COGEN TAP | 115 | ETL.9141 |  | ACT | 0.83 |  |  |  | 0.83
SANGER-CALIFORNIA AVE | 115 | ETL.9130 |  | ACT | 9.15 |  |  |  | 9.15
SANGER-CALIFORNIA AVE #1 | 70 | ETL.9120 |  | IDL | 2.25 |  |  |  | 2.25
SANGER-MALAGA | 115 | ETL.3600 |  | ACT | 8.69 |  |  |  | 8.69
SANGER-REEDLEY | 115 | ETL.9140 |  | ACT | 20.61 |  |  |  | 20.61
SANTA FE GEOTHERMAL TAP | 230 | ETL.4782 |  | ACT | 1.04 | 1.04 |  |  | 0
SANTA MARIA-SISQUOC | 115 | ETL.3610 |  | ACT | 10.57 |  |  |  | 10.57
SANTA PAULA-MILLBRAE | 115 | ETL.7580 |  | ACT | 0.09 |  |  |  | 0.09
SANTA ROSA-CORONA | 115 | ETL.4309 |  | ACT | 14.34 |  | 1.09 |  | 13.25
SANTA TERESA-EDENVALE | 115 | ETL.1132 |  | ACT | 0.68 |  |  |  | 0.68
SANTA YNEZ TAP | 115 | ETL.3701 |  | ACT | 4.06 |  | 3.49 |  | 0.57
SARATOGA-VASONA | 230 | ETL.5931 |  | ACT | 3.41 |  |  |  | 3.41
SCHINDLER-COALINGA #2 | 70 | ETL.9150 |  | ACT | 17.19 |  |  |  | 17.19
SCHINDLER-FIVE POINTS SW STA | 70 | ETL.9161 |  | ACT | 1.7 |  |  |  | 1.7
SCHULTE SW STA-KASSON-MANTECA | 115 | ETL.7472 |  | ACT | 16.58 |  |  |  | 16.58
SCHULTE SW STA-LAMMERS | 115 | ETL.3993 |  | ACT | 0.69 |  |  |  | 0.69
SEBASTIANI TAP | 60 | ETL.8072 |  | ACT | 0.01 |  |  |  | 0.01
SEMITROPIC-CHARCA | 115 | ETL.3620 |  | ACT | 6.91 |  |  |  | 6.91
SEMITROPIC-MIDWAY #1 | 115 | ETL.3630 |  | ACT | 14.1 |  |  |  | 14.1
SEMITROPIC-MIDWAY #2 | 115 | ETL.3640 |  | ACT | 10.53 |  |  |  | 10.53
SEMITROPIC-MIDWAY #2 | 115 | ETL.3640 |  | IDL | 9.58 |  |  |  | 9.58
SEMITROPIC-WASCO | 70 | ETL.9170 |  | ACT | 6.32 |  |  |  | 6.32
SERRAMONTE TAP | 115 | ETL.2211 |  | ACT | 2.55 |  |  |  | 2.55
SF AIRPORT-SAN MATEO | 115 | ETL.3650 |  | ACT | 6.09 |  |  |  | 6.09
SHAFTER-RIO BRAVO | 115 | ETL.3660 |  | ACT | 8.31 |  |  |  | 8.31
SHARON PRISON TAP | 115 | ETL.1251 |  | ACT | 2.57 |  |  |  | 2.57
SHILOH II-BIRDS LANDING SW STA | 230 | ETL.4240 |  | ACT | 3.56 |  |  |  | 3.56
SHREDDER TAP | 115 | ETL.3381 |  | ACT | 1.38 |  |  |  | 1.38
SIERRA #1 | 115 | ETL.3670 |  | IDL | 5.47 |  |  |  | 5.47
SIERRA #2 | 115 | ETL.3680 |  | IDL | 4.86 |  |  |  | 4.86
SIERRA (PSE) TAP | 115 | ETL.1933 |  | ACT | 1.81 |  |  |  | 1.81
SIERRA PAC IND (QUINCY) TAP | 60 | ETL.6292 |  | ACT | 0.02 |  |  |  | 0.02
SIERRA PACIFIC IND TAP | 115 | ETL.7401 |  | ACT | 0.06 |  |  |  | 0.06
SILVERADO-FULTON JCT | 115 | ETL.1610 |  | ACT | 26.16 | 5.02 | 16.85 |  | 4.29
SIMPSON-KORBEL TAP | 60 | ETL.6804 |  | ACT | 0.39 |  |  |  | 0.39
SISQUOC-GAREY | 115 | ETL.3690 |  | ACT | 5.02 | 0.23 | 0.13 |  | 4.66
SISQUOC-SANTA YNEZ SW STA | 115 | ETL.3700 |  | ACT | 22.11 |  | 16.1 |  | 6.01
SKAGGS ISLAND #1 TAP | 115 | ETL.1832 |  | ACT | 0.59 |  |  |  | 0.59
SKAGGS ISLAND #2 TAP | 115 | ETL.1842 |  | ACT | 0.6 |  |  |  | 0.6
SLAC TAP | 60 | ETL.7221 |  | ACT | 1.41 |  |  |  | 1.41
SLY CREEK TAP | 115 | ETL.4221 |  | ACT | 5.34 | 5.34 |  |  | 0
SMARTVILLE TAP | 60 | ETL.6522 |  | ACT | 0.09 |  | 0.09 |  | 0
SMARTVILLE-CAMP FAR WEST | 60 | ETL.7970 |  | ACT | 17.81 |  | 9.28 |  | 8.53
SMARTVILLE-CAMP FAR WEST (12KV) | 60 | ETL.7970 |  | IDL | 7.18 |  |  |  | 7.18
SMARTVILLE-MARYSVILLE | 60 | ETL.7980 |  | ACT | 20.14 |  | 4.86 |  | 15.28
SMARTVILLE-NICOLAUS #1 | 60 | ETL.7990 |  | ACT | 29.6 |  | 4.75 |  | 24.85
SMARTVILLE-NICOLAUS #2 | 60 | ETL.8000 |  | ACT | 30.16 |  | 4.83 |  | 25.33
SMUD TAP | 230 | ETL.1184 |  | ACT | 0.12 | 0.12 |  |  | 0
SMYRNA-SEMITROPIC-MIDWAY | 115 | ETL.3710 |  | ACT | 22.39 |  |  |  | 22.39
SNEATH LANE-HALF MOON BAY | 60 | ETL.7212 |  | ACT | 15.41 | 11.17 | 2.36 |  | 1.88
SNEATH LANE-PACIFICA | 60 | ETL.7575 |  | ACT | 3.26 | 1.36 | 1.32 |  | 0.58
SOBRANTE-G #1 | 115 | ETL.3720 |  | ACT | 5.34 | 3.86 | 1.35 |  | 0.13
SOBRANTE-G #2 | 115 | ETL.3730 |  | ACT | 5.39 | 3.86 | 1.44 |  | 0.09
SOBRANTE-GRIZZLY-CLAREMONT #1 | 115 | ETL.3740 |  | ACT | 19.57 | 12.29 | 5.05 |  | 2.23
SOBRANTE-GRIZZLY-CLAREMONT #2 | 115 | ETL.3750 |  | ACT | 19.3 | 12.15 | 4.62 |  | 2.53
SOBRANTE-MORAGA | 115 | ETL.3742 |  | ACT | 10.36 | 0.21 | 5.38 |  | 4.77
SOBRANTE-R #1 | 115 | ETL.3770 |  | ACT | 5.54 | 3.86 | 1.4 |  | 0.28
SOBRANTE-R #2 | 115 | ETL.3780 |  | ACT | 5.53 | 3.86 | 1.4 |  | 0.27
SOBRANTE-STANDARD OIL SW STA #1 | 115 | ETL.3800 |  | ACT | 18.89 |  | 8.56 |  | 10.33
SOBRANTE-STANDARD OIL SW STA #2 | 115 | ETL.3790 |  | ACT | 18.89 |  | 8.54 |  | 10.35
SOLAR SW STA-CALIENTE SW STA #1 | 230 | ETL.5215 |  | ACT | 8.22 |  |  |  | 8.22
SOLAR SW STA-CALIENTE SW STA #2 | 230 | ETL.5225 |  | ACT | 8.22 |  |  |  | 8.22
SOLAR TANNEHILL TAP | 70 | ETL.9231 |  | ACT | 2.65 |  |  |  | 2.65
SOLEDAD #1 | 60 | ETL.8010 |  | ACT | 19.37 |  |  |  | 19.37
SOLEDAD #2 | 60 | ETL.8020 |  | ACT | 18.86 |  |  |  | 18.86
SOLEDAD #3 | 60 | ETL.8030 |  | ACT | 1.6 |  |  |  | 1.6
SOLEDAD #4 | 60 | ETL.8040 |  | ACT | 6.1 |  |  |  | 6.1
SONOMA-PUEBLO | 115 | ETL.3810 |  | ACT | 18.48 |  | 2.59 | 0.05 | 15.84
SPAULDING #3-SPAULDING #1 | 60 | ETL.8050 | POWERGEN | ACT | 1.08 |  | 0.95 |  | 0.13
SPAULDING-SUMMIT | 60 | ETL.8060 |  | ACT | 19.66 |  | 14.72 | 0.08 | 4.86
SPENCE-FIRESTONE | 60 | ETL.1152 |  | ACT | 1.66 |  |  |  | 1.66
SPI (BURNEY) TAP | 230 | ETL.5392 |  | ACT | 0.04 |  | 0.04 |  | 0
SPRING GAP TAP | 115 | ETL.1402 |  | ACT | 1.64 | 1.64 |  |  | 0
STAGG-COUNTRY CLUB #1 | 60 | ETL.8080 |  | ACT | 2.43 |  |  |  | 2.43
STAGG-COUNTRY CLUB #2 | 60 | ETL.8090 |  | ACT | 2.46 |  |  |  | 2.46
STAGG-HAMMER | 60 | ETL.8100 |  | ACT | 4.25 |  |  |  | 4.25
STAGG-TESLA | 230 | ETL.5680 |  | ACT | 23.64 |  |  |  | 23.64
STANDARD #1 & #2 (12KV) | 60 | ETL.9490 |  | IDL | 4.2 |  |  |  | 4.2
STANISLAUS RECOVERY TAP | 60 | ETL.7861 |  | ACT | 0.11 |  |  |  | 0.11
STANISLAUS-MANTECA #2 | 115 | ETL.3820 |  | ACT | 53.95 |  | 24.97 |  | 28.98
STANISLAUS-MELONES SW STA-MANTECA #1 | 115 | ETL.3830 |  | ACT | 61.15 |  | 32.13 |  | 29.02
STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | 115 | ETL.3840 |  | ACT | 43.8 |  | 32.09 |  | 11.71
STANISLAUS-NEWARK #1 (12KV) | 115 | ETL.3850 |  | IDL | 0.01 |  |  |  | 0.01
STAUFFER TAP | 60 | ETL.6372 |  | ACT | 0.58 |  |  |  | 0.58
STELLING-MONTA VISTA | 115 | ETL.1000 |  | ACT | 1.61 |  |  |  | 1.61
STELLING-WOLFE | 115 | ETL.2680 |  | ACT | 1.46 |  |  |  | 1.46
STOCKTON A #1 | 60 | ETL.8110 |  | ACT | 5.58 |  |  |  | 5.58
STOCKTON A-LOCKEFORD-BELLOTA #1 | 115 | ETL.3880 |  | ACT | 43.43 |  |  |  | 43.43
STOCKTON A-LOCKEFORD-BELLOTA #2 | 115 | ETL.3890 |  | ACT | 34.49 |  |  |  | 34.49
STOCKTON A-WEBER #1 | 60 | ETL.8120 |  | ACT | 13.2 |  |  |  | 13.2
STOCKTON A-WEBER #2 | 60 | ETL.8130 |  | ACT | 9.86 |  |  |  | 9.86
STOCKTON A-WEBER #3 | 60 | ETL.8140 |  | ACT | 9.82 |  |  |  | 9.82
STOCKTON-NEWARK (12KV) | 60 | ETL.8150 |  | IDL | 14.59 |  |  |  | 14.59
STONE CORRAL TAP | 70 | ETL.8611 |  | ACT | 7.56 |  |  |  | 7.56
STONE-EVERGREEN-METCALF | 115 | ETL.2530 |  | ACT | 12.86 |  |  |  | 12.86
STONY POINT TAP | 115 | ETL.2062 |  | ACT | 3.08 |  |  |  | 3.08
SUMIDEN WIRE PRODUCTS TAP | 60 | ETL.8141 |  | ACT | 0.19 |  |  |  | 0.19
SUNOL TAP | 60 | ETL.7671 |  | ACT | 0.08 |  |  |  | 0.08
SURF TAP | 115 | ETL.1381 |  | ACT | 11.37 |  | 2.08 |  | 9.29
SUTTER HOME SW STA-LOCKEFORD-LODI | 60 | ETL.8068 |  | ACT | 29.76 |  |  |  | 29.76
SUTTER HOME SW STA-STAGG | 60 | ETL.8070 |  | ACT | 17.13 |  |  |  | 17.13
SUTTER HOME-SUTTER HOME SW STA | 60 | ETL.8069 |  | ACT | 0.03 |  |  |  | 0.03
SWIFT-METCALF | 115 | ETL.3900 |  | ACT | 8.93 |  |  |  | 8.93
SYCAMORE CREEK-NOTRE DAME-TABLE MTN | 115 | ETL.4314 |  | ACT | 20.34 |  |  |  | 20.34
SYCAMORE TAP | 70 | ETL.9281 |  | ACT | 2.04 |  |  |  | 2.04
TABLE MTN-BUTTE #1 | 115 | ETL.3910 |  | ACT | 19.54 |  |  |  | 19.54
TABLE MTN-BUTTE #2 | 115 | ETL.3920 |  | ACT | 15.82 |  |  |  | 15.82
TABLE MTN-PALERMO | 230 | ETL.5690 |  | ACT | 14.57 |  | 7.85 |  | 6.72
TABLE MTN-PEACHTON | 60 | ETL.8425 |  | ACT | 14.84 |  |  |  | 14.84
TABLE MTN-RIO OSO | 230 | ETL.5700 |  | ACT | 50.18 |  | 12.38 |  | 37.8
TABLE MTN-TESLA | 500 | ETL.6080 |  | ACT | 135 |  |  |  | 135
TABLE MTN-VACA | 500 | ETL.6090 |  | ACT | 83.3 |  |  |  | 83.3
TAFT-CHALK CLIFF | 115 | ETL.3940 |  | ACT | 7.18 |  |  |  | 7.18
TAFT-CUYAMA #1 | 70 | ETL.9200 |  | ACT | 19.25 |  |  |  | 19.25
TAFT-CUYAMA #2 | 70 | ETL.9210 |  | ACT | 18.75 |  |  |  | 18.75
TAFT-ELK HILLS | 70 | ETL.9220 |  | ACT | 12.39 |  |  |  | 12.39
TAFT-MARICOPA | 70 | ETL.9230 |  | ACT | 5.98 |  |  |  | 5.98
TASSAJARA-NEWARK | 230 | ETL.5920 |  | ACT | 31.8 | 11.36 | 7 |  | 13.44
TECUYA TAP | 70 | ETL.9311 |  | ACT | 1.91 |  |  |  | 1.91
TEICHERT TAP | 115 | ETL.1266 |  | ACT | 2.11 |  |  |  | 2.11
TEJON-LEBEC | 70 | ETL.9250 |  | ACT | 12.95 |  | 5.8 |  | 7.15
TEMBLOR-KERNRIDGE | 115 | ETL.3950 |  | ACT | 4.78 |  |  |  | 4.78
TEMBLOR-SAN LUIS OBISPO | 115 | ETL.3960 |  | ACT | 57.78 | 11.43 | 19.59 |  | 26.76
TEMPLETON-ATASCADERO | 70 | ETL.9410 |  | ACT | 8.82 |  | 5.1 |  | 3.72
TEMPLETON-GATES | 230 | ETL.5934 |  | ACT | 52.18 |  | 6.97 |  | 45.21
TERMINOUS TAP | 60 | ETL.8071 |  | ACT | 3.01 |  |  |  | 3.01
TES TAP | 230 | ETL.4531 |  | ACT | 3.28 |  |  |  | 3.28
TESLA-LAWRENCE LAB | 115 | ETL.4250 |  | ACT | 9 |  |  |  | 9
TESLA-LOS BANOS #1 | 500 | ETL.6100 |  | ACT | 57.14 |  | 3.68 |  | 53.46
TESLA-METCALF | 500 | ETL.6110 |  | ACT | 35.31 |  | 27.79 |  | 7.52
TESLA-NEWARK #1 | 230 | ETL.5720 |  | ACT | 28.19 |  | 4.78 |  | 23.41
TESLA-NEWARK #2 | 230 | ETL.5354 |  | ACT | 40.82 |  | 8.14 |  | 32.68
TESLA-RAVENSWOOD | 230 | ETL.5730 |  | ACT | 37.14 |  | 4.93 |  | 32.21
TESLA-SALADO #1 | 115 | ETL.3990 |  | ACT | 32.08 |  | 3.46 |  | 28.62
TESLA-SALADO-MANTECA | 115 | ETL.4000 |  | ACT | 53.97 |  | 3.97 |  | 50
TESLA-SCHULTE SW STA #1 | 115 | ETL.3980 |  | ACT | 7.37 |  |  |  | 7.37
TESLA-SCHULTE SW STA #2 | 115 | ETL.3970 |  | ACT | 7.34 |  |  |  | 7.34
TESLA-STOCKTON COGEN JCT | 115 | ETL.4010 |  | ACT | 25.08 |  |  |  | 25.08
TESLA-TRACY #1 | 230 | ETL.5740 |  | ACT | 5.68 |  |  |  | 5.68
TESLA-TRACY #2 | 230 | ETL.5750 |  | ACT | 5.68 |  |  |  | 5.68
TESLA-TRACY(115KV) | 115 | ETL.4020 |  | ACT | 27.85 |  |  |  | 27.85
TESLA-TRACY(500KV) | 500 | ETL.6120 |  | ACT | 1.13 |  |  |  | 1.13
TESLA-WESTLEY | 230 | ETL.5760 |  | ACT | 45.06 |  |  |  | 45.06
TESORO-SOBRANTE | 230 | ETL.5670 |  | ACT | 12.32 | 0.56 | 5.8 |  | 5.96
TEVIS #1 TAP | 115 | ETL.1144 |  | ACT | 3.25 |  |  |  | 3.25
TEVIS #2 TAP | 115 | ETL.1143 |  | ACT | 3.29 |  |  |  | 3.29
TEXACO BASIC SCHOOL TAP | 70 | ETL.8972 |  | ACT | 0.75 |  |  |  | 0.75
TEXACO TAP | 60 | ETL.6411 |  | ACT | 0.72 |  |  |  | 0.72
THERMAL ENERGY TAP | 115 | ETL.4011 |  | IDL | 0.71 |  |  |  | 0.71
TIDEWATER-SOBRANTE | 230 | ETL.5770 |  | ACT | 12.32 | 0.56 | 5.78 |  | 5.98
TIGER CREEK-ELECTRA | 230 | ETL.5780 |  | ACT | 13.68 | 8.58 | 5.1 |  | 0
TIGER CREEK-VALLEY SPRINGS | 230 | ETL.5790 |  | ACT | 24.22 | 8.72 | 12.21 |  | 3.29
TIVY VALLEY-REEDLEY | 70 | ETL.9260 |  | ACT | 12.3 |  |  |  | 12.3
TOCALOMA TAP | 60 | ETL.7721 |  | ACT | 1.03 |  | 1.03 |  | 0
TORNADO TAP | 70 | ETL.8572 |  | ACT | 0.06 |  |  |  | 0.06
TRACY-LOS BANOS | 500 | ETL.6130 |  | ACT | 56.23 |  | 3.57 |  | 52.66
TRANQUILLITY SW STA-HELM | 230 | ETL.5370 |  | ACT | 12.68 |  |  |  | 12.68
TRANQUILLITY SW STA-KEARNEY | 230 | ETL.5380 |  | ACT | 36.9 |  |  |  | 36.9
TRAVIS TAP | 60 | ETL.6731 |  | ACT | 2.88 |  |  |  | 2.88
TRIMBLE-SAN JOSE B | 115 | ETL.4030 |  | ACT | 2.54 |  |  |  | 2.54
TRINIDAD TAP | 60 | ETL.6811 |  | ACT | 1.34 |  |  |  | 1.34
TRINITY-COTTONWOOD | 115 | ETL.4040 |  | ACT | 45.97 | 10.89 | 31.92 |  | 3.16
TRINITY-MAPLE CREEK | 60 | ETL.8170 |  | ACT | 55.48 |  | 54.97 |  | 0.51
TULLOCH TAP | 115 | ETL.1071 |  | ACT | 0.31 |  | 0.28 |  | 0.03
TULUCAY-NAPA #1 | 60 | ETL.8180 |  | ACT | 9.72 |  | 4.99 |  | 4.73
TULUCAY-NAPA #2 | 60 | ETL.8190 |  | ACT | 3.93 |  |  |  | 3.93
TULUCAY-VACA | 230 | ETL.5800 |  | ACT | 23.63 |  | 16.68 |  | 6.95
TUPMAN-NORCO TAP | 115 | ETL.2592 |  | ACT | 6.67 |  |  |  | 6.67
UC DAVIS #1 TAP | 115 | ETL.6670 |  | ACT | 1.59 |  |  |  | 1.59
UC DAVIS #2 TAP | 115 | ETL.6680 |  | ACT | 1.61 |  |  |  | 1.61
UKIAH-HOPLAND-CLOVERDALE | 115 | ETL.4050 |  | ACT | 31.19 | 7.15 | 17.12 |  | 6.92
ULTRA POWER TAP | 60 | ETL.6803 |  | ACT | 1.17 |  |  |  | 1.17
ULTRAPOWER (OGLE) TAP | 115 | ETL.2121 |  | ACT | 2.45 |  |  |  | 2.45
UNION CHEMICAL TAP | 60 | ETL.6351 |  | ACT | 1.04 |  | 0.57 |  | 0.47
UNION OIL TAP | 115 | ETL.4280 |  | ACT | 0.5 |  |  |  | 0.5
UNITED COGEN INC TAP | 115 | ETL.2241 |  | ACT | 0.09 |  |  |  | 0.09
UNITED COGEN INC TAP | 115 | ETL.2241 |  | IDL | 0.59 |  |  |  | 0.59
UNIVERSITY COGEN TAP | 115 | ETL.3941 |  | ACT | 0.22 |  |  |  | 0.22
URICH TAP | 60 | ETL.6373 |  | ACT | 0.21 |  |  |  | 0.21
US WINDPOWER #3 TAP | 230 | ETL.4521 |  | ACT | 0.06 | 0.06 |  |  | 0
US WINDPOWER TAP | 60 | ETL.8261 |  | ACT | 1.52 |  |  |  | 1.52
VACA DIXON-MORAGA #1 | 230 | ETL.5935 |  | IDL | 3.08 |  |  |  | 3.08
VACA-BAHIA | 230 | ETL.5810 |  | ACT | 33.9 |  | 13.53 |  | 20.37
VACA-LAKEVILLE #1 | 230 | ETL.5840 |  | ACT | 40.93 |  | 18.48 |  | 22.45
VACA-LAMBIE SW STA | 230 | ETL.5845 |  | ACT | 13.95 |  |  |  | 13.95
VACA-PARKWAY | 230 | ETL.5850 |  | ACT | 27.76 |  | 13.55 |  | 14.21
VACA-PEABODY | 230 | ETL.5821 |  | ACT | 9.69 |  |  |  | 9.69
VACA-PLAINFIELD | 60 | ETL.8200 |  | ACT | 29.83 |  |  |  | 29.83
VACA-SUISUN | 115 | ETL.4070 |  | ACT | 22.92 |  | 8.05 |  | 14.87
VACA-SUISUN | 115 | ETL.4070 |  | IDL | 0.14 |  |  |  | 0.14
VACA-SUISUN-JAMESON | 115 | ETL.4080 |  | ACT | 25.46 |  | 8.05 |  | 17.41
VACA-TESLA | 500 | ETL.6140 |  | ACT | 57 |  |  |  | 57
VACA-VACAVILLE-CORDELIA | 115 | ETL.4090 |  | ACT | 22.04 |  | 8.06 |  | 13.98
VACA-VACAVILLE-JAMESON-NORTH TOWER | 115 | ETL.4100 |  | ACT | 36.2 |  | 8.05 |  | 28.15
VALLEY CHILDRENS HOSPITAL TAP | 115 | ETL.2142 |  | ACT | 0.03 |  |  |  | 0.03
VALLEY SPRINGS #1 | 60 | ETL.8210 |  | ACT | 27.27 |  | 10.37 |  | 16.9
VALLEY SPRINGS #2 | 60 | ETL.9460 |  | ACT | 25.65 |  | 9.31 |  | 16.34
VALLEY SPRINGS-BELLOTA | 230 | ETL.5860 |  | ACT | 20.67 |  | 5.41 |  | 15.26
VALLEY SPRINGS-CALAVERAS CEMENT | 60 | ETL.8220 |  | ACT | 7.91 |  | 7.6 |  | 0.31
VALLEY SPRINGS-CLAY | 60 | ETL.8264 |  | ACT | 17.31 |  | 10.9 |  | 6.41
VALLEY SPRINGS-MARTELL #1 | 60 | ETL.8240 |  | ACT | 12.75 |  | 7.33 |  | 5.42
VALLEY VIEW #1 TAP | 115 | ETL.3151 |  | ACT | 0.96 |  | 0.01 |  | 0.95
VALLEY VIEW #2 TAP | 115 | ETL.3161 |  | ACT | 0.97 |  | 0.01 |  | 0.96
VASCO-HERDLYN | 60 | ETL.8260 |  | ACT | 10.91 |  |  |  | 10.91
VASONA-METCALF | 230 | ETL.5932 |  | ACT | 13.29 |  | 3.38 |  | 9.91
VEDDER TAP | 115 | ETL.2141 |  | ACT | 11.09 |  | 4.84 |  | 6.25
VICTOR TAP | 60 | ETL.7442 |  | ACT | 0.04 |  |  |  | 0.04
VIEJO-MONTEREY | 60 | ETL.8270 |  | ACT | 2.28 |  | 0.63 |  | 1.65
VIERRA-TRACY-KASSON | 115 | ETL.4310 |  | ACT | 10.49 |  |  |  | 10.49
VINEYARD-NEWARK | 230 | ETL.4536 |  | ACT | 14.36 |  | 2.79 |  | 11.57
VOLTA-DESCHUTES | 60 | ETL.8290 |  | ACT | 20.85 | 7.58 | 12.52 |  | 0.75
VOLTA-SOUTH | 60 | ETL.8300 |  | ACT | 4.86 | 0.98 | 3.88 |  | 0
WADHAM TAP | 60 | ETL.6601 |  | ACT | 1.68 |  |  |  | 1.68
WARNERVILLE-WILSON | 230 | ETL.5870 |  | ACT | 38.41 |  |  |  | 38.41
WASCO PRISON TAP | 115 | ETL.3641 |  | ACT | 0.54 |  |  |  | 0.54
WASCO-FAMOSO | 70 | ETL.9241 |  | ACT | 7.13 |  |  |  | 7.13
WASHOE TAP | 60 | ETL.6911 |  | ACT | 1.04 |  | 1.04 |  | 0
WATERSHED TAP | 60 | ETL.7191 |  | ACT | 0.28 |  |  |  | 0.28
WATSONVILLE-SALINAS | 60 | ETL.8310 |  | ACT | 28.39 |  | 8.23 |  | 20.16
WAUKENA SW STA-CORCORAN | 115 | ETL.8773 |  | ACT | 2.37 |  |  |  | 2.37
WEBER-CASCADE ENERGY STORAGE | 60 | ETL.1363 |  | ACT | 0.04 |  |  |  | 0.04
WEBER-FRENCH CAMP #1 | 60 | ETL.8320 |  | ACT | 6.05 |  |  |  | 6.05
WEBER-FRENCH CAMP #2 | 60 | ETL.8321 |  | ACT | 10.89 |  |  |  | 10.89
WEBER-MORMON JCT | 60 | ETL.8330 |  | ACT | 17.63 |  |  |  | 17.63
WEBER-TESLA | 230 | ETL.5880 |  | ACT | 23.71 |  |  |  | 23.71
WEEDPATCH-SAN BERNARD | 70 | ETL.9270 |  | ACT | 9.26 |  |  |  | 9.26
WEEDPATCH-WELLFIELD | 70 | ETL.9280 |  | ACT | 5.88 |  |  |  | 5.88
WEIMAR #1 | 60 | ETL.7560 |  | ACT | 13.99 | 9.89 | 4.09 |  | 0.01
WEIMAR-HALSEY | 60 | ETL.8340 |  | ACT | 6.28 |  | 6.28 |  | 0
WESIX TAP | 70 | ETL.8984 |  | ACT | 2.49 |  |  |  | 2.49
WEST FRESNO-CALIFORNIA AVE | 115 | ETL.2361 |  | ACT | 4.89 |  |  |  | 4.89
WEST POINT-VALLEY SPRINGS | 60 | ETL.8350 |  | ACT | 21.66 | 5.44 | 12.12 |  | 4.1
WEST SAC COM TOWERS | 60 | ETL.5570 |  | ACT | 0.02 |  |  |  | 0.02
WEST SACRAMENTO-BRIGHTON | 115 | ETL.4110 |  | ACT | 13.97 |  |  |  | 13.97
WEST SACRAMENTO-DAVIS | 115 | ETL.4120 |  | ACT | 12.14 |  |  |  | 12.14
WESTINGHOUSE TAP | 60 | ETL.6561 |  | ACT | 8.01 |  |  |  | 8.01
WESTINGHOUSE TAP | 60 | ETL.6561 |  | IDL | 0.07 |  |  |  | 0.07
WESTLANDS #1 RA PUMPING PLANT TAP | 115 | ETL.3242 |  | ACT | 1.05 |  |  |  | 1.05
WESTLANDS #18 RA TAP | 115 | ETL.3252 |  | ACT | 3.52 |  |  |  | 3.52
WESTLANDS TAP | 70 | ETL.8983 |  | ACT | 1.07 |  |  |  | 1.07
WESTPARK-COLUMBUS | 115 | ETL.4130 |  | ACT | 8.58 |  |  |  | 8.58
WHEELER RIDGE PUMPING PLANT #1 TAP | 230 | ETL.5192 |  | ACT | 0.25 |  |  |  | 0.25
WHEELER RIDGE PUMPING PLANT #2 TAP | 230 | ETL.5202 |  | ACT | 0.23 |  |  |  | 0.23
WHEELER RIDGE-ADOBE SW STA | 115 | ETL.1982 |  | ACT | 1.34 |  |  |  | 1.34
WHEELER RIDGE-LAKEVIEW | 70 | ETL.9290 |  | ACT | 7.51 |  |  |  | 7.51
WHEELER RIDGE-SAN BERNARD | 70 | ETL.9300 |  | ACT | 5.88 |  |  |  | 5.88
WHEELER RIDGE-TEJON | 70 | ETL.9310 |  | ACT | 5.01 |  |  |  | 5.01
WHEELER RIDGE-WEEDPATCH | 70 | ETL.9320 |  | ACT | 22.44 |  |  |  | 22.44
WHISMAN-MONTA VISTA | 115 | ETL.1010 |  | ACT | 5.97 |  |  |  | 5.97
WILLOW PASS-CONTRA COSTA | 60 | ETL.8370 |  | ACT | 10.82 |  |  |  | 10.82
WILSON-ATWATER #2 | 115 | ETL.4160 |  | ACT | 15.41 |  |  |  | 15.41
WILSON-BORDEN #1 | 230 | ETL.5890 |  | ACT | 35.31 |  |  |  | 35.31
WILSON-BORDEN #2 | 230 | ETL.9001 |  | ACT | 35.37 |  |  |  | 35.37
WILSON-DAIRYLAND (12KV) | 115 | ETL.1284 |  | IDL | 11.37 |  |  |  | 11.37
WILSON-LE GRAND | 115 | ETL.4170 |  | ACT | 14.11 |  |  |  | 14.11
WILSON-MERCED #1 | 115 | ETL.4180 |  | ACT | 5.58 |  |  |  | 5.58
WILSON-MERCED #2 | 115 | ETL.4190 |  | ACT | 6.2 |  |  |  | 6.2
WILSON-ORO LOMA | 115 | ETL.4200 |  | ACT | 40.73 |  |  |  | 40.73
WIND FARMS | 60 | ETL.8380 |  | ACT | 3.77 |  |  |  | 3.77
WIND GAP PUMPING PLANT #1 TAP | 230 | ETL.5193 |  | ACT | 1.64 |  |  |  | 1.64
WIND GAP PUMPING PLANT #2 TAP | 230 | ETL.5203 |  | ACT | 1.63 |  |  |  | 1.63
WINDMASTER TAP | 230 | ETL.4491 |  | ACT | 0.11 |  |  |  | 0.11
WINDSOR-FITCH MOUNTAIN | 60 | ETL.6900 |  | ACT | 21.37 | 0.8 | 2.57 |  | 18
WINTU TAP | 60 | ETL.6311 |  | ACT | 1.85 |  | 0.45 |  | 1.4
WISHON-COPPERMINE | 70 | ETL.9330 |  | ACT | 19.99 | 0.11 | 14 |  | 5.88
WISHON-SAN JOAQUIN #3 | 70 | ETL.9340 |  | ACT | 7.65 | 4.87 | 2.78 |  | 0
WITCO (REFINERY) TAP | 115 | ETL.1972 |  | ACT | 0.03 |  |  |  | 0.03
WOHLER TAP | 60 | ETL.7631 |  | ACT | 1.44 |  |  |  | 1.44
WOODBRIDGE TAP | 60 | ETL.7443 |  | ACT | 0.53 |  |  |  | 0.53
WOODLAND BIOMASS TAP | 115 | ETL.4211 |  | ACT | 0.87 |  |  |  | 0.87
WOODLAND-DAVIS | 115 | ETL.4210 |  | ACT | 11.75 |  |  |  | 11.75
WOODLEAF-PALERMO | 115 | ETL.4220 |  | ACT | 19.62 | 6.53 | 11.1 |  | 1.99
WOODWARD-SHEPHERD | 115 | ETL.1895 |  | ACT | 4.84 |  |  |  | 4.84
WRIGHT TAP | 70 | ETL.8931 |  | ACT | 1.18 |  |  |  | 1.18
WYANDOTTE 1105 (12KV) | 0 | 0 |  | IDL | 10.77 |  | 8.69 |  | 2.08 | Non-ETL/Distribution
YUBA CITY COGEN TAP | 60 | ETL.7729 |  | ACT | 0.8 |  |  |  | 0.8
ZAMORA TAP | 115 | ETL.3471 |  | ACT | 1.92 |  |  |  | 1.92
ZANKER #1 TAP | 115 | ETL.3121 |  | ACT | 0.59 |  |  |  | 0.59
ZANKER #2 TAP | 115 | ETL.3041 |  | ACT | 0.73 |  |  |  | 0.73
ZOND WIND TAP | 60 | ETL.8381 |  | ACT | 1.19 |  |  |  | 1.19