## All Outage Details
HFTD WIRE-DOWN OUTAGE DETAILS (2013 - June 2025) |  |  |  | Source: Extracted from Outage Database on 7/7/2025.
Division | Tier | Feeder Name | Feeder # | Device | Oper # | Date | FNL | OIS # | Duration | Outage Level | Basic Cause | Supplemental Cause | CESO | C Min | Weather | Failed/Involved Equipment | Equipment Condition | ILIS # | Const Type | Sus/Mom | PM # | Year | Month | Wire Down | Outage Fault Type | MEDay | Conductor Energized
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | FUSE |  | 41372 | 652 | 769007 | 450 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 4050 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0022423 | OH | Sus | 0 | 2013 | APR | Yes |  | Yes
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 41372 | 1652 | 770780 | 1356 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4068 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 13-0022766 | OH | Sus | 0 | 2013 | APR | Yes | Line to Line | Yes
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 41372 | 1641 | 770758 | 47 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 3885 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 13-0022729 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | 83500401 | 83500401 | OTHER |  | 41372 | 1951 | 771132 | 1089 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 7255 | Clear;32 - 90 F | Pole-Wood | Broken- wire on ground | 13-0022825 | OH | Sus | 0 | 2013 | APR | Yes | Open Circuit | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | OTHER |  | 41372 | 1628 | 771123 | 1135 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 4136 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0022792 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 41372 | 344 | 768597 | 1006 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 14084 | Clear;32 - 90 F | Pole-Wood | Broken- wire on ground | 13-0022445 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | OTHER |  | 41372 | 850 | 769390 | 860 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 860 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0022672 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 41372 | 156 | 768329 | 941 | Distribution Circuit | Vegetation | Tree - branch fell on line | 798 | 371844 | Clear;32 - 90 F | Pole-Wood | Broken- wire on ground | 13-0022130 | OH | Sus | 41877861 | 2013 | APR | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 41372 | 441 | 768950 | 1265 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 38703 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0022550 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 41372 | 302 | 768524 | 651 | Distribution Circuit | Equipment Failure/Involved | Other | 450 | 0 | Strong winds;32 - 90 F | Connector or Splice (OH) | Broken- wire on ground | 13-0022141 | OH | Sus | 41877870 | 2013 | APR | Yes |  | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 41372 | 134 | 768275 | 926 | Distribution Circuit | Equipment Failure/Involved | Other | 5 | 4630 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 13-0022528 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 41372 | 503 | 769114 | 1137 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 53911 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0022293 | OH | Sus | 30988000 | 2013 | APR | Yes |  | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 41372 | 428 | 769770 | 1122 | Distribution Circuit | Equipment Failure/Involved | Other | 36 | 40392 | Clear;32 - 90 F | Conductor- Overhead | On Ground | 13-0022442 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 41372 | 620 | 768938 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 17010 | Clear;32 - 90 F | Conductor- Overhead | On Ground | 13-0022451 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 41372 | 218 | 768978 | 698 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 9772 | Clear;32 - 90 F | Conductor- Overhead | On Ground | 13-0022232 | OH | Sus | 41877941 | 2013 | APR | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER |  | 41372 | 1421 | 770356 | 596 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 596 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 13-0022721 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH |  | 41372 | 1555 | 770621 | 167 | Distribution Circuit | Equipment Failure/Involved | Other | 170 | 28390 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 13-0022728 | OH | Sus | 0 | 2013 | APR | Yes | None | Yes
FRESNO | Tier 2 | AUBERRY-1101 | 254151101 | FUSE |  | 41372 | 741 | 769174 | 464 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 5104 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0022304 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 41372 | 1158 | 770205 | 752 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 752 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0022575 | OH | Sus | 0 | 2013 | APR | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 41372 | 948 | 769568 | 528 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 651 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0022485 | OH | Sus | 0 | 2013 | APR | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER |  | 41372 | 1138 | 769912 | 527 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 14670 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0022531 | OH | Sus | 0 | 2013 | APR | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 41372 | 112 | 768222 | 918 | Distribution Circuit | Vegetation | Tree - branch fell on line | 68 | 41827 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0022150 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 41372 | 648 | 768993 | 602 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 3817 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0022464 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 41372 | 859 | 769414 | 646 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3876 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0022646 | OH | Sus | 0 | 2013 | APR | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 41372 | 550 | 768874 | 425 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 6375 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0022231 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER |  | 41372 | 318 | 768751 | 574 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 66584 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0022207 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 41372 | 607 | 769799 | 578 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1156 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0022453 | OH | Sus | 0 | 2013 | APR | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 41372 | 1645 | 770959 | 1181 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 44878 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0022757 | OH | Sus | 0 | 2013 | APR | Yes | Three Phase Fault | Yes
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | FUSE |  | 41372 | 834 | 769769 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4347 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0022562 | OH | Sus | 0 | 2013 | APR | Yes | Line to Line | Yes
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | OCB |  | 41372 | 2246 | 771246 | 874 | Distribution Circuit | 3rd Party | Vehicle | 3591 | 204109 | Clear;32 - 90 F | Pole-Wood | Broken- wire on ground | 13-0022826 | OH | Sus | 30988253 | 2013 | APR | Yes | Line to Ground | Yes
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | FUSE |  | 41372 | 750 | 769920 | 690 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 31274 | Clear;32 - 90 F | Conductor- Overhead | On Ground | 13-0022604 | OH | Sus | 30988242 | 2013 | APR | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER |  | 41372 | 1034 | 769861 | 1693 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 283234 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0022592 | OH | Sus | 30988243 | 2013 | APR | Yes | Line to Line | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 41372 | 416 | 768700 | 1336 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8016 | Clear;32 - 90 F | Conductor- Overhead | On Ground | 13-0022831 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 41372 | 530 | 768882 | 780 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 69630 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0022762 | OH | Sus | 0 | 2013 | APR | Yes | Line to Ground | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 41372 | 651 | 769004 | 1209 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 37479 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0022777 | OH | Sus | 0 | 2013 | APR | Yes | None | Yes
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | RECLOSER |  | 41372 | 1324 | 770213 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 481 | 92952 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0022600 | OH | Sus | 30988246 | 2013 | APR | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | SWITCH |  | 41372 | 2218 | 771228 | 282 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 17484 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on object | 13-0022819 | OH | Sus | 0 | 2013 | APR | Yes | None | Yes
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE |  | 41372 | 136 | 768287 | 619 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 40854 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0022175 | OH | Sus | 0 | 2013 | APR | Yes |  | Yes
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | OTHER |  | 41372 | 1611 | 770677 | 399 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 399 | Clear;32 - 90 F | Conductor- Overhead | On Ground | 13-0022686 | OH | Sus | 0 | 2013 | APR | Yes | None | Yes
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 41372 | 453 | 768788 | 2509 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 110396 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0022201 | OH | Sus | 0 | 2013 | APR | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 41448 | 1650 | 815162 | 653 | Distribution Circuit | Equipment Failure/Involved | Other | 112 | 15520 | Overcast;32 - 90 F | Pole-Wood | Broken- wire on ground | 13-0041878 | OH | Sus | 31004714 | 2013 | JUN | Yes | Line to Line | Yes
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | OTHER |  | 41600 | 1857 | 912995 | 254 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1200 | 53781 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078764 | OH | Sus | 0 | 2013 | NOV | Yes | None | Yes
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | RECLOSER |  | 41599 | 1857 | 908099 | 1697 | Distribution Circuit | Vegetation | Tree - fell into line | 422 | 225292 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078070 | OH | Sus | 31038174 | 2013 | NOV | Yes | None | Yes
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | FUSE |  | 41600 | 641 | 911048 | 1611 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 105823 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078446 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE |  | 41599 | 2032 | 909208 | 804 | Distribution Circuit | Vegetation | Tree - bark fell into line | 44 | 35376 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078341 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
EAST BAY | Tier 2 | OAKLAND K-1103 | 12101103 | FUSE |  | 41600 | 311 | 910794 | 1809 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 136069 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078427 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
EAST BAY | Tier 3 | OAKLAND K-1102 | 12101102 | FUSE |  | 41599 | 1849 | 908059 | 843 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 21918 | Clear;32 - 90 F | Conductor- Overhead | On Ground | 13-0078278 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
EAST BAY | Tier 2 | OAKLAND K-1103 | 12101103 | RECLOSER |  | 41599 | 1907 | 910192 | 465 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3570 | 1522290 | Clear;32 - 90 F | Conductor- Overhead | On Ground | 13-0078228 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
EAST BAY | Tier 3 | BERKELEY F-1103 | 12061103 | FUSE |  | 41599 | 1949 | 908830 | 2608 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 28688 | Clear;32 - 90 F | Conductor- Overhead | On Ground | 13-0078749 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
HUMBOLDT | Tier 2 | HOPLAND-1101 | 42251101 | FUSE |  | 41600 | 133 | 910379 | 1013 | Distribution Circuit | Equipment Failure/Involved | Other | 9 | 9117 | Drizzle;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078282 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | REDBUD-1101 | 43191101 | RECLOSER |  | 41600 | 1204 | 912235 | 1659 | Distribution Circuit | Vegetation | Tree - fell into line | 673 | 560037 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078777 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | LUCERNE-1106 | 43351106 | FUSE |  | 41600 | 1820 | 912867 | 1773 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5319 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0079011 | OH | Sus | 0 | 2013 | NOV | Yes | None | Yes
HUMBOLDT | Tier 2 | LUCERNE-1103 | 43351103 | OCB |  | 41599 | 1904 | 908530 | 2720 | Distribution Circuit | Vegetation | Tree - fell into line | 2885 | 1301516 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on object | 13-0078065 | OH | Sus | 0 | 2013 | NOV | Yes | Three Phase Fault | Yes
HUMBOLDT | Tier 2 | LUCERNE-1103 | 43351103 | FUSE |  | 41600 | 9 | 913272 | 3821 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 106492 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078827 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE |  | 41599 | 2129 | 911058 | 2881 | Distribution Circuit | Equipment Failure/Involved | Other | 27 | 77787 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 13-0078985 | OH | Sus | 0 | 2013 | NOV | Yes | None | Yes
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE |  | 41600 | 2354 | 913310 | 2461 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 22058 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on object | 13-0078913 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER |  | 41599 | 1921 | 908604 | 1703 | Distribution Circuit | Vegetation | Tree - branch fell on line | 347 | 590941 | Clear;32 - 90 F | Conductor- Overhead | On Ground | 13-0078100 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1102 | 42281102 | RECLOSER |  | 41600 | 446 | 910836 | 794 | Distribution Circuit | Equipment Failure/Involved | Other | 140 | 111160 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078486 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER |  | 41599 | 2006 | 908967 | 2659 | Distribution Circuit | Vegetation | Tree - branch fell on line | 135 | 358965 | Clear;32 - 90 F | Conductor- Overhead | On Ground | 13-0078220 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER |  | 41600 | 1357 | 912370 | 811 | Distribution Circuit | Vegetation | Tree - branch fell on line | 860 | 576690 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078846 | OH | Sus | 0 | 2013 | NOV | Yes | Open Circuit | Yes
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 41599 | 1907 | 908325 | 686 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 18585 | Clear;32 - 90 F | Pole-Wood | Broken- wire on ground | 13-0078139 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 41599 | 1626 | 908219 | 1574 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6296 | Strong winds;32 - 90 F | Crossarm- Wood | Broken- wire on ground | 13-0078055 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER |  | 41600 | 919 | 911595 | 388 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 19853 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078480 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | FUSE |  | 41600 | 1545 | 912607 | 1525 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 28975 | Clear;32 - 90 F | Pole-Wood | Broken- wire on ground | 13-0078968 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 41600 | 218 | 910590 | 1043 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 46101 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078295 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE |  | 41600 | 721 | 911109 | 984 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3936 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078697 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 41600 | 210 | 910505 | 795 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 795 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 13-0078272 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
NORTH BAY | Tier 2 | SILVERADO-2104 | 43432104 | SECTIONALIZER |  | 41600 | 29 | 910249 | 946 | Distribution Circuit | Vegetation | Tree - fell into line | 225 | 198570 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 13-0078276 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | BANGOR-1101 | 103191101 | RECLOSER |  | 41600 | 1333 | 912326 | 641 | Distribution Circuit | Equipment Failure/Involved | Other | 457 | 263412 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078626 | OH | Sus | 0 | 2013 | NOV | Yes | Multi-Fault | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER |  | 41599 | 1813 | 907875 | 1481 | Distribution Circuit | Vegetation | Tree - fell into line | 166 | 182166 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078087 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | WYANDOTTE-1105 | 102911105 | FUSE |  | 41600 | 557 | 910878 | 1920 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 5547 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 13-0078378 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE |  | 41600 | 402 | 910689 | 437 | Distribution Circuit | Vegetation | Tree - fell into line | 167 | 87508 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078347 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER |  | 41600 | 543 | 910892 | 2127 | Distribution Circuit | Vegetation | Tree - branch fell on line | 267 | 175075 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078367 | OH | Sus | 0 | 2013 | NOV | Yes | Three Phase Fault | Yes
NORTH VALLEY | Tier 3 | BUCKS CREEK-1103 | 102211103 | FUSE |  | 41600 | 1307 | 912310 | 188 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 2444 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 13-0078619 | OH | Sus | 0 | 2013 | NOV | Yes | None | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE |  | 41599 | 1301 | 907169 | 421 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2105 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 13-0077871 | OH | Sus | 41991455 | 2013 | NOV | Yes |  | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE |  | 41600 | 135 | 912292 | 2555 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 12775 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 13-0078612 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE |  | 41600 | 45 | 910277 | 2455 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 120295 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 13-0078298 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | BUCKS CREEK-1103 | 102211103 | RECLOSER |  | 41600 | 2146 | 913255 | 1497 | Distribution Circuit | Equipment Failure/Involved | Other | 321 | 477233 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 13-0078839 | OH | Sus | 31037615 | 2013 | NOV | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | ORO FINO-1102 | 103031102 | FUSE |  | 41599 | 2121 | 909633 | 3996 | Distribution Circuit | Vegetation | Tree - fell into line | 307 | 639553 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078134 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
NORTH VALLEY | Tier 2 | RED BLUFF-1104 | 103541104 | RECLOSER |  | 41599 | 634 | 906606 | 451 | Distribution Circuit | Vegetation | Tree - fell into line | 350 | 22255 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0077612 | OH | Sus | 31037645 | 2013 | NOV | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | FUSE |  | 41600 | 1010 | 911733 | 285 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 855 | Clear;32 - 90 F | Conductor- Overhead | On Ground | 13-0078597 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | FUSE |  | 41600 | 1004 | 911871 | 221 | Distribution Circuit | Equipment Failure/Involved | Other | 46 | 6308 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 13-0078543 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | FUSE |  | 41599 | 1546 | 907438 | 1224 | Distribution Circuit | Vegetation | Tree - bark fell into line | 4 | 4896 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0077991 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | RECLOSER |  | 41599 | 1933 | 908743 | 507 | Distribution Circuit | Vegetation | Tree - fell into line | 1440 | 301083 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078093 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | FUSE |  | 41599 | 356 | 906536 | 374 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 56848 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0077607 | OH | Sus | 31037575 | 2013 | NOV | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | FUSE |  | 41600 | 733 | 911134 | 222 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1332 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078514 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | FUSE |  | 41599 | 1056 | 907038 | 733 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 6142 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0077798 | OH | Sus | 31038092 | 2013 | NOV | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE |  | 41599 | 845 | 906786 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 6902 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0077677 | OH | Sus | 31037684 | 2013 | NOV | Yes |  | Yes
NORTH VALLEY | Tier 2 | WHITMORE-1101 | 103601101 | RECLOSER |  | 41600 | 20 | 910238 | 991 | Distribution Circuit | Vegetation | Tree - fell into line | 542 | 253021 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078271 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER |  | 41599 | 2105 | 909907 | 453 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 11325 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078168 | OH | Sus | 41991611 | 2013 | NOV | Yes | Open Circuit | Yes
SACRAMENTO | Tier 2 | VACA DIXON-1105 | 63591105 | FUSE |  | 41600 | 1225 | 912077 | 545 | Distribution Circuit | Equipment Failure/Involved | Other | 95 | 18781 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on object | 13-0078622 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | OTHER |  | 41599 | 2154 | 909799 | 2511 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 5022 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078998 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | OCB |  | 41599 | 2047 | 909364 | 21 | Distribution Circuit | Equipment Failure/Involved | Other | 5436 | 114156 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 13-0078113 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 41599 | 1915 | 908474 | 1555 | Distribution Circuit | Equipment Failure/Involved | Other | 84 | 105254 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 13-0078237 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 2 | EL DORADO PH-2101 | 152762101 | FUSE |  | 41600 | 43 | 911857 | 3837 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 249405 | Strong winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 13-0078541 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 2 | EL DORADO PH-2101 | 152762101 | RECLOSER |  | 41600 | 43 | 910278 | 1049 | Distribution Circuit | Equipment Failure/Involved | Other | 189 | 109436 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078241 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 41600 | 1114 | 911910 | 735 | Distribution Circuit | Vegetation | Tree - fell into line | 1012 | 126224 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078552 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 41600 | 1141 | 911991 | 2290 | Distribution Circuit | Vegetation | Tree - fell into line | 1107 | 425449 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078568 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 41600 | 1900 | 913036 | 1385 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6925 | Clear;32 - 90 F | Conductor- Overhead | On Ground | 13-0078771 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 41599 | 1609 | 907493 | 1269 | Distribution Circuit | Vegetation | Tree - fell into line | 967 | 565491 | Clear;32 - 90 F | Pole-Wood | Broken- wire on ground | 13-0077956 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 41600 | 2046 | 913186 | 1092 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 58968 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078837 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 41600 | 1531 | 912620 | 1515 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 81810 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078726 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER |  | 41600 | 1237 | 912181 | 1632 | Distribution Circuit | Vegetation | Tree - fell into line | 1038 | 630848 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078615 | OH | Sus | 0 | 2013 | NOV | Yes | Three Phase Fault | Yes
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 41600 | 1259 | 912551 | 1847 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 59320 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078675 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 3 | DRUM-1101 | 152321101 | RECLOSER |  | 41599 | 2127 | 909663 | 1323 | Distribution Circuit | Vegetation | Tree - fell into line | 320 | 225275 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on object | 13-0078249 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 3 | DRUM-1101 | 152321101 | FUSE |  | 41600 | 734 | 911141 | 2241 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 40338 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 13-0078583 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE |  | 41600 | 933 | 911606 | 2562 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 77256 | Strong winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 13-0078544 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE |  | 41600 | 1253 | 912242 | 2167 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 31816 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 13-0078891 | OH | Sus | 0 | 2013 | NOV | Yes | Three Phase Fault | Yes
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE |  | 41600 | 2131 | 913244 | 1317 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 36519 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 13-0078862 | OH | Sus | 0 | 2013 | NOV | Yes | None | Yes
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE |  | 41600 | 1540 | 912375 | 1697 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 17253 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078691 | OH | Sus | 0 | 2013 | NOV | Yes | Open Circuit | Yes
SIERRA | Tier 3 | ALLEGHANY-1102 | 152101102 | FUSE |  | 41599 | 2129 | 911665 | 2681 | Distribution Circuit | Equipment Failure/Involved | Other | 4 | 10724 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078484 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SIERRA | Tier 2 | ALLEGHANY-1101 | 152101101 | FUSE |  | 41600 | 1508 | 912541 | 2872 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 31592 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078701 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SONOMA | Tier 2 | PENNGROVE-1101 | 43471101 | FUSE |  | 41600 | 1947 | 913093 | 583 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 5247 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078815 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | OTHER |  | 41600 | 812 | 911278 | 543 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 543 | Clear;32 - 90 F | Other | Broken- wire on object | 13-0078403 | OH | Sus | 0 | 2013 | NOV | Yes | None | Yes
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE |  | 41599 | 1816 | 909415 | 2519 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 103279 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078339 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE |  | 41600 | 1659 | 912782 | 1278 | Distribution Circuit | Vegetation | Tree - branch fell on line | 134 | 169952 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078767 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 41599 | 1624 | 907529 | 424 | Distribution Circuit | Equipment Failure/Involved | Other | 90 | 38160 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078018 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
SONOMA | Tier 2 | GEYSERVILLE-1102 | 42891102 | SWITCH |  | 41599 | 2045 | 909300 | 420 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 2520 | Clear;32 - 90 F | Connector or Splice (OH) | Broken- wire on ground | 13-0078169 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
SONOMA | Tier 2 | CLOVERDALE-1101 | 42821101 | FUSE |  | 41600 | 943 | 911852 | 1518 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 36432 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078555 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
SONOMA | Tier 3 | GEYSERVILLE-1102 | 42891102 | FUSE |  | 41599 | 1940 | 907687 | 3995 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 35955 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078591 | OH | Sus | 0 | 2013 | NOV | Yes | None | Yes
STOCKTON | Tier 2 | ELECTRA-1102 | 162161102 | FUSE |  | 41600 | 1600 | 912641 | 260 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 4940 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078729 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 41600 | 2007 | 913131 | 1168 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 47888 | Clear;32 - 90 F | Pole-Wood | Broken- wire on ground | 13-0078812 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Line | Yes
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 41600 | 742 | 911167 | 1113 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 6678 | Clear;32 - 90 F | Pole-Wood | Broken- wire on ground | 13-0078547 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 41599 | 1831 | 908725 | 1024 | Distribution Circuit | Vegetation | Tree - bark fell into line | 216 | 221184 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078128 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
STOCKTON | Tier 2 | SALT SPRINGS-2102 | 163692102 | RECLOSER |  | 41600 | 225 | 910516 | 1254 | Distribution Circuit | Vegetation | Tree - fell into line | 1998 | 1244943 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078275 | OH | Sus | 31038457 | 2013 | NOV | Yes | Line to Line | Yes
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | OCB |  | 41599 | 2252 | 908797 | 386 | Distribution Circuit | Equipment Failure/Involved | Other | 2148 | 135968 | Strong winds;32 - 90 F | Crossarm- Wood | Broken- wire on object | 13-0078189 | OH | Sus | 0 | 2013 | NOV | Yes | None | Yes
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER |  | 41599 | 1828 | 908019 | 1004 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1299 | 294380 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078046 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | SWITCH |  | 41600 | 1222 | 912000 | 233 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 12815 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on object | 13-0078046 | OH | Sus | 0 | 2013 | NOV | Yes |  | Yes
STOCKTON | Tier 2 | SALT SPRINGS-2101 | 163692101 | FUSE |  | 41600 | 943 | 911634 | 997 | Distribution Circuit | Equipment Failure/Involved | Other | 23 | 15001 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078682 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 41599 | 2006 | 909124 | 654 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 23544 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078137 | OH | Sus | 0 | 2013 | NOV | Yes | Line to Ground | Yes
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 41599 | 1922 | 908563 | 386 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 25274 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 13-0078110 | OH | Sus | 41991609 | 2013 | NOV | Yes |  | Yes
NORTH BAY | Tier 2 | PUEBLO-2103 | 43292103 | FUSE |  | 41875 | 329 | 1071789 | 1156 | Distribution Circuit | Environmental/External | Earthquake | 9 | 10404 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0052765 | OH | Sus | 0 | 2014 | AUG | Yes | Line to Ground | Yes
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 41875 | 1928 | 1072340 | 283 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 19736 | Clear;32 - 90 F | Conductor- Overhead | On Ground | 14-0052913 | OH | Sus | 31096822 | 2014 | AUG | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | FUSE |  | 41984 | 838 | 1131698 | 2363 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 7089 | Drizzle;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075424 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
CENTRAL COAST | Tier 3 | LAURELES-1111 | 182371111 | FUSE |  | 41984 | 721 | 1130936 | 3484 | Distribution Circuit | Equipment Failure/Involved | Other | 8 | 27872 | Overcast;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076240 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE |  | 41984 | 917 | 1132240 | 1717 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 112429 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075812 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 41984 | 916 | 1135461 | 2354 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 21114 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075926 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 41984 | 1316 | 1133871 | 2332 | Distribution Circuit | Equipment Failure/Involved | Other | 7 | 16324 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075642 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE |  | 41985 | 1643 | 1138907 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1956 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076571 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE |  | 41984 | 837 | 1131693 | 1873 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9365 | Overcast;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076380 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | RECLOSER |  | 41984 | 730 | 1130893 | 3418 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 32886 | Drizzle;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075054 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | RECLOSER |  | 41976 | 514 | 1121721 | 796 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 17469 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073151 | OH | Sus | 31117940 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 41984 | 1242 | 1133648 | 3196 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 43320 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075820 | OH | Sus | 31120494 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 41984 | 1219 | 1133503 | 2860 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 42900 | Rain;32 - 90 F | Conductor- Overhead | On Ground | 14-0076664 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | RECLOSER |  | 41984 | 1005 | 1132798 | 2934 | Distribution Circuit | Vegetation | Tree - fell into line | 866 | 342914 | Overcast;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0075329 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 41984 | 836 | 1131681 | 334 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 5344 | Overcast;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075286 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 41976 | 1058 | 1122509 | 392 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 17248 | Overcast;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073390 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 41985 | 140 | 1138068 | 1310 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 39760 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076314 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER |  | 41984 | 751 | 1131212 | 2272 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 320352 | Drizzle;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0075194 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER |  | 41984 | 1004 | 1132789 | 3193 | Distribution Circuit | Vegetation | Tree - fell into line | 223 | 225105 | Drizzle;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0075309 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | PACIFIC GROVE-0422 | 182440422 | FUSE |  | 41984 | 811 | 1131962 | 1310 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 36586 | Partly cloudy;32 - 90 F | Conductor- Overhead | On Ground | 14-0075208 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | PACIFIC GROVE-0422 | 182440422 | SWITCH |  | 41976 | 1428 | 1123261 | 682 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 402 | 10854 | Drizzle;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0073476 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER |  | 41984 | 900 | 1131664 | 1083 | Distribution Circuit | Vegetation | Tree - fell into line | 617 | 188759 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075217 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 2 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 41985 | 1326 | 1138416 | 1329 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2658 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076392 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 41984 | 2031 | 1135947 | 1100 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 31900 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075916 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 41984 | 1407 | 1134196 | 1423 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5692 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075650 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 41984 | 1255 | 1133738 | 883 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 10864 | Heavy rain;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0075594 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 42003 | 2057 | 1155593 | 1895 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 11370 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0002021 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | RECLOSER |  | 41985 | 951 | 1137851 | 293 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2378 | 424771 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076271 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | RECLOSER |  | 41984 | 2328 | 1136631 | 905 | Distribution Circuit | Vegetation | Tree - fell into line | 452 | 409060 | Rain;32 - 90 F | Conductor- Overhead | On Ground | 14-0076002 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 42003 | 1214 | 1151785 | 1786 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 13234 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079212 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 41984 | 903 | 1131963 | 2085 | Distribution Circuit | Equipment Failure/Involved | Other | 54 | 112590 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075683 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 41984 | 1115 | 1139312 | 2730 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5460 | Overcast;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076600 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 41976 | 630 | 1121772 | 761 | Distribution Circuit | Vegetation | Tree - branch fell on line | 74 | 56314 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073228 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 42003 | 1916 | 1155163 | 875 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 64750 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079593 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 41976 | 708 | 1121833 | 1102 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8816 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073393 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 41985 | 648 | 1137234 | 647 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 7764 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076347 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 41976 | 1353 | 1123315 | 913 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 19173 | Heavy rain;32 - 90 F | Conductor- Overhead | On Ground | 14-0073618 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 42003 | 2036 | 1157188 | 1714 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 63418 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079726 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 42003 | 1544 | 1153547 | 1546 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 37227 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079385 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 42003 | 1831 | 1155994 | 795 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 13515 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079565 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 42003 | 2019 | 1155441 | 596 | Distribution Circuit | Vegetation | Tree - fell into line | 230 | 104984 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079465 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42003 | 2206 | 1155751 | 1430 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 12870 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079779 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 41984 | 1412 | 1135808 | 1068 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4272 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075834 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 41984 | 852 | 1135792 | 849 | Distribution Circuit | Equipment Failure/Involved | Other | 21 | 17829 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0075829 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 41984 | 2044 | 1135994 | 151 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 2265 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075973 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | RECLOSER |  | 41984 | 940 | 1132406 | 935 | Distribution Circuit | Vegetation | Tree - branch fell on line | 347 | 235865 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075256 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 42003 | 1926 | 1155809 | 2123 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 197757 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079516 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 41984 | 817 | 1131784 | 735 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 89661 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075833 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
CENTRAL COAST | Tier 3 | PAUL SWEET-2104 | 83252104 | OTHER |  | 41976 | 1906 | 1123961 | 634 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5072 | Fog;32 - 90 F | Conductor- Overhead | On Ground | 14-0073642 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 41976 | 2353 | 1124060 | 362 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 724 | Fog;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073661 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 2 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 41984 | 816 | 1131504 | 737 | Distribution Circuit | Vegetation | Tree - fell into line | 442 | 192760 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075138 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 41984 | 1227 | 1133578 | 1106 | Distribution Circuit | Vegetation | Tree - fell into line | 103 | 92438 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075772 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 41985 | 816 | 1137521 | 2002 | Distribution Circuit | Equipment Failure/Involved | Other | 7 | 14014 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076649 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 41984 | 702 | 1134590 | 1628 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 8140 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075619 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 41976 | 1229 | 1123053 | 931 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 4655 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0073601 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 41976 | 1055 | 1122594 | 996 | Distribution Circuit | Vegetation | Tree - branch fell on line | 122 | 121512 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073570 | OH | Sus | 42283952 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 41976 | 700 | 1121807 | 907 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2721 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073258 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 41984 | 907 | 1133339 | 2020 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 20200 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075401 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 41984 | 1814 | 1135597 | 1088 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 76160 | Heavy rain;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0076138 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 41976 | 841 | 1123613 | 849 | Distribution Circuit | Vegetation | Tree - branch fell on line | 70 | 39732 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073514 | OH | Sus | 0 | 2014 | DEC | Yes | Open Circuit | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | OTHER |  | 41984 | 853 | 1133361 | 1749 | Distribution Circuit | Vegetation | Tree - fell into line | 514 | 188980 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075409 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | CAMP EVERS-2105 | 83622105 | FUSE |  | 41976 | 1155 | 1122911 | 680 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 27880 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073441 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42003 | 2011 | 1155388 | 2197 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 39546 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079598 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 42003 | 1342 | 1152371 | 1984 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 15936 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079403 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42003 | 1856 | 1157284 | 1804 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 41168 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079736 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 41984 | 1734 | 1135169 | 1845 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 25830 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076559 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 41976 | 728 | 1122195 | 752 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 11280 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073517 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 41984 | 642 | 1129620 | 1063 | Distribution Circuit | Vegetation | Tree - branch fell on line | 883 | 322996 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0074992 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 41976 | 141 | 1121592 | 679 | Distribution Circuit | Vegetation | Tree - branch fell on line | 141 | 57808 | Rain;32 - 90 F | Conductor- Overhead | On Ground | 14-0073131 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42003 | 2001 | 1154731 | 1820 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 101920 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079607 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 41984 | 954 | 1132524 | 2003 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 34336 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076307 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 41985 | 1038 | 1138006 | 782 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 782 | Fog;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076389 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 41984 | 659 | 1130272 | 2059 | Distribution Circuit | Equipment Failure/Involved | Other | 30 | 54203 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075060 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER |  | 41984 | 921 | 1132222 | 1016 | Distribution Circuit | Vegetation | Tree - fell into line | 138 | 140208 | Heavy rain;32 - 90 F | Crossarm- Wood | Broken- wire on ground | 14-0075254 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42003 | 1832 | 1154816 | 1933 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 71521 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079560 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 41976 | 852 | 1122321 | 1973 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 45815 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073639 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 41985 | 448 | 1137063 | 552 | Distribution Circuit | Equipment Failure/Involved | Other | 25 | 13800 | Fog;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076227 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 41976 | 728 | 1121846 | 1361 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 97551 | Heavy rain;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0073187 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 41976 | 1156 | 1122918 | 939 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4695 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073593 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 41976 | 2322 | 1124051 | 536 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 536 | Fog;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073680 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | OTHER |  | 41976 | 758 | 1123048 | 1173 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 78210 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073443 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 41984 | 948 | 1132445 | 2592 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 67392 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076289 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 41984 | 923 | 1132204 | 2997 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 17982 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076333 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 41984 | 2132 | 1136251 | 1636 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 81800 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076015 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 42003 | 2045 | 1156256 | 1245 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 52290 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079660 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 41985 | 631 | 1137634 | 599 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 25158 | Strong winds;32 - 90 F | Crossarm- Wood | Broken- wire on ground | 14-0076474 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 41985 | 43 | 1136771 | 1262 | Distribution Circuit | Vegetation | Tree - fell into line | 1183 | 307760 | Overcast;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076035 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | LOMPICO-0401 | 88880401 | RECLOSER |  | 41984 | 802 | 1131296 | 1100 | Distribution Circuit | Equipment Failure/Involved | Other | 106 | 113123 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0075102 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
CENTRAL COAST | Tier 3 | LOMPICO-0401 | 88880401 | FUSE |  | 41984 | 802 | 1136351 | 2016 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2016 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075102 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 41976 | 808 | 1121957 | 696 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 15224 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073235 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 41976 | 1352 | 1123312 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 228 | 33987 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073506 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 41976 | 939 | 1122157 | 1141 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 35371 | Heavy rain;32 - 90 F | Conductor- Overhead | On Ground | 14-0073650 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | LOMPICO-0401 | 88880401 | FUSE |  | 41984 | 959 | 1132325 | 1925 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 38500 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076115 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 41976 | 2144 | 1123979 | 626 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 2504 | Fog;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073666 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 42003 | 2118 | 1155651 | 1327 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 9289 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on object | 14-0079775 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 41984 | 1035 | 1133007 | 2453 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 209809 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075698 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 41976 | 1115 | 1122605 | 945 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 31185 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073622 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 41984 | 1352 | 1134064 | 743 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 24519 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076034 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 41976 | 1047 | 1122408 | 1050 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 34650 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073586 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 41976 | 1031 | 1122359 | 793 | Distribution Circuit | Vegetation | Tree - fell into line | 629 | 360852 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073302 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 41976 | 1024 | 1122372 | 991 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 54505 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073596 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 41984 | 1259 | 1133756 | 1271 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 69905 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0076059 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 41976 | 1706 | 1123757 | 1040 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 4478 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073610 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 42003 | 2013 | 1155425 | 1588 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 192492 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079594 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER |  | 41984 | 1417 | 1136990 | 1761 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7044 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076118 | OH | Sus | 0 | 2014 | DEC | Yes | Open Circuit | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 42003 | 2011 | 1155514 | 1594 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 138379 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079669 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER |  | 42003 | 2216 | 1155999 | 1404 | Distribution Circuit | Vegetation | Tree - branch fell on line | 279 | 81266 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079613 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 42003 | 2216 | 1157480 | 1454 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8724 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079773 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER |  | 41976 | 1202 | 1122943 | 1258 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1258 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073692 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 41984 | 540 | 1129530 | 740 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 11840 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075065 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 41976 | 204 | 1121602 | 1240 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 7440 | Heavy rain;32 - 90 F | Conductor- Overhead | On Ground | 14-0073169 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 41984 | 654 | 1130234 | 813 | Distribution Circuit | Equipment Failure/Involved | Other | 108 | 78098 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0075017 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER |  | 41976 | 1029 | 1122328 | 735 | Distribution Circuit | Vegetation | Tree - branch fell on line | 94 | 64075 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073551 | OH | Sus | 0 | 2014 | DEC | Yes | Open Circuit | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 41976 | 134 | 1121585 | 436 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 6540 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073126 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER |  | 41984 | 1427 | 1134340 | 678 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 20400 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075669 | OH | Sus | 31120396 | 2014 | DEC | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 41976 | 344 | 1121676 | 766 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 24512 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073146 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 41976 | 1225 | 1123091 | 1055 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 9245 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073409 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER |  | 41976 | 245 | 1121657 | 1157 | Distribution Circuit | Vegetation | Tree - fell into line | 291 | 274737 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073128 | OH | Sus | 42284329 | 2014 | DEC | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH |  | 42003 | 2034 | 1155873 | 2945 | Distribution Circuit | Vegetation | Tree - fell into line | 491 | 291402 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079551 | OH | Sus | 31124019 | 2014 | DEC | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42003 | 1605 | 1153765 | 1695 | Distribution Circuit | Equipment Failure/Involved | Other | 12 | 20340 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079406 | OH | Sus | 42304600 | 2014 | DEC | Yes | Line to Line | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 41984 | 927 | 1132231 | 812 | Distribution Circuit | Equipment Failure/Involved | Other | 476 | 105949 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075306 | OH | Sus | 42293239 | 2014 | DEC | Yes | Line to Line | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER |  | 41984 | 859 | 1131925 | 596 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1574 | 548748 | Strong winds;32 - 90 F | Other | Broken- wire on ground | 14-0075200 | OH | Sus | 42293239 | 2014 | DEC | Yes |  | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH |  | 41976 | 1707 | 1123765 | 1242 | Distribution Circuit | Vegetation | Tree - fell into line | 167 | 51262 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073571 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 41984 | 1122 | 1133222 | 618 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 4326 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075384 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
DE ANZA | Tier 2 | SARATOGA-1106 | 83371106 | FUSE |  | 41976 | 1129 | 1122897 | 1068 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 54353 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073545 | OH | Sus | 3118510 | 2014 | DEC | Yes | Three Phase Fault | Yes
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE |  | 41984 | 852 | 1133449 | 899 | Distribution Circuit | Equipment Failure/Involved | Other | 99 | 35300 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075428 | OH | Sus | 42293239 | 2014 | DEC | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE |  | 41984 | 1536 | 1134656 | 69 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 621 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075630 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
DE ANZA | Tier 2 | SARATOGA-1106 | 83371106 | OTHER |  | 41976 | 1528 | 1123621 | 1153 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1153 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073519 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE |  | 42003 | 2000 | 1156062 | 1808 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 33308 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079668 | OH | Sus | 31124019 | 2014 | DEC | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | STELLING-1110 | 83481110 | RECLOSER |  | 41984 | 917 | 1131873 | 853 | Distribution Circuit | Vegetation | Tree - fell into line | 270 | 47238 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075295 | OH | Sus | 31120421 | 2014 | DEC | Yes |  | Yes
DIABLO | Tier 3 | TASSAJARA-2112 | 14662112 | RECLOSER |  | 41984 | 638 | 1133429 | 2136 | Distribution Circuit | Equipment Failure/Involved | Other | 32 | 55978 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076234 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
DIABLO | Tier 2 | MORAGA-1104 | 13801104 | OTHER |  | 41984 | 724 | 1131079 | 184 | Distribution Circuit | Equipment Failure/Involved | Other | 50 | 9200 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on object | 14-0075193 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
DIABLO | Tier 2 | ROSSMOOR-1101 | 14161101 | FUSE |  | 41984 | 1729 | 1135141 | 1308 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 3924 | Heavy rain;32 - 90 F | Conductor- Overhead | On Ground | 14-0075788 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
EAST BAY | Tier 2 | SAN LEANDRO-1109 | 13111109 | FUSE |  | 42003 | 1739 | 1154510 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 24480 | Drizzle;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079485 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
EAST BAY | Tier 2 | EDES-1112 | 13681112 | RECLOSER |  | 42003 | 1355 | 1152491 | 409 | Distribution Circuit | Vegetation | Tree - fell into line | 1022 | 78068 | Drizzle;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079107 | OH | Sus | 31123832 | 2014 | DEC | Yes | Line to Ground | Yes
EAST BAY | Tier 2 | OAKLAND X-1106 | 12541106 | FUSE |  | 41976 | 1407 | 1123348 | 674 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 674 | Clear;32 - 90 F | Conductor- Overhead | On Ground | 14-0073553 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
EAST BAY | Tier 2 | OAK-0401 | 12600401 | OCB |  | 41984 | 342 | 1128964 | 998 | Distribution Circuit | Equipment Failure/Involved | Other | 1011 | 150431 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0074841 | OH | Sus | 31120520 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 41984 | 346 | 1128973 | 556 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1112 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075092 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 41984 | 1841 | 1135402 | 919 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 18052 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075914 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 41984 | 1841 | 1136409 | 1229 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 43015 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075943 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 41984 | 1420 | 1134356 | 22 | Distribution Circuit | Vegetation | Tree - branch fell on line | 106 | 2332 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075570 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 41984 | 357 | 1128996 | 614 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 65084 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0074955 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 41984 | 1028 | 1132876 | 1792 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3584 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075644 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | FUSE |  | 41984 | 702 | 1130255 | 458 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 10076 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075320 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | FUSE |  | 41984 | 402 | 1129049 | 458 | Distribution Circuit | Vegetation | Tree - fell into line | 286 | 130988 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0074888 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 41984 | 743 | 1131034 | 475 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 5225 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075244 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | UKIAH-1114 | 42771114 | FUSE |  | 41984 | 1430 | 1134793 | 1250 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 7500 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075651 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER |  | 41984 | 58 | 1128908 | 852 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 80652 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0074837 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 41984 | 548 | 1129593 | 837 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 17718 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075495 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 41984 | 1023 | 1132834 | 1981 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 13867 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075986 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 41984 | 720 | 1131282 | 378 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 25471 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075457 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | OTHER |  | 41984 | 420 | 1129440 | 1016 | Distribution Circuit | Vegetation | Tree - branch fell on line | 62 | 60768 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075128 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 41984 | 258 | 1128914 | 1687 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 38801 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075929 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 41984 | 231 | 1131630 | 2374 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 78174 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076256 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | SWITCH |  | 41985 | 1000 | 1137967 | 1595 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 17545 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076378 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 41984 | 1448 | 1135353 | 1797 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 14376 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075750 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 41984 | 1452 | 1134484 | 626 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5634 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075762 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 41984 | 1452 | 1134455 | 935 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 12155 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075768 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER |  | 41984 | 58 | 1128814 | 892 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 101712 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0074826 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 41984 | 850 | 1131843 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 7840 | Clear;32 - 90 F | Conductor- Overhead | On Ground | 14-0075198 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 41984 | 520 | 1131093 | 1045 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 7315 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075069 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 41984 | 1439 | 1132161 | 731 | Distribution Circuit | Vegetation | Tree - branch fell on line | 62 | 16937 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075648 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 41984 | 756 | 1131143 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 5550 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075265 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 41984 | 1651 | 1135010 | 130 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 1950 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075694 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 41985 | 1045 | 1138029 | 366 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 1830 | Fog;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076302 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 41984 | 312 | 1128977 | 1700 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 91800 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0074868 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 41984 | 747 | 1131092 | 953 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3812 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075843 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 41984 | 2041 | 1135977 | 797 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 10361 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076054 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 41984 | 1811 | 1135291 | 1162 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 66234 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076237 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 41984 | 653 | 1133065 | 868 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 10416 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075351 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | OTHER |  | 41984 | 653 | 1133407 | 475 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 5225 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075418 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | OTHER |  | 41984 | 653 | 1133090 | 643 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 643 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0075356 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 41984 | 656 | 1130203 | 1111 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 14443 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075899 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 41984 | 309 | 1129115 | 931 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 31288 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0074900 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 41984 | 653 | 1130303 | 1072 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 37692 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075253 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER |  | 41984 | 426 | 1129098 | 497 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 59908 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075156 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 41984 | 514 | 1129329 | 841 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 9251 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075281 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 41984 | 425 | 1129072 | 670 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 38639 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075271 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 41984 | 637 | 1129998 | 752 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 9024 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075311 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 41984 | 433 | 1129100 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 7168 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075020 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 41984 | 440 | 1129126 | 2055 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 28770 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075975 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | RECLOSER |  | 41984 | 428 | 1129538 | 842 | Distribution Circuit | Vegetation | Tree - fell into line | 371 | 312382 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075001 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 41984 | 2143 | 1136223 | 786 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11004 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075970 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 41976 | 2138 | 1123974 | 962 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1924 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073664 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 41984 | 1917 | 1135604 | 1324 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 9326 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076152 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 41984 | 708 | 1130322 | 398 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 8756 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075191 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 41985 | 612 | 1137161 | 986 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 28594 | Fog;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0076297 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 41985 | 816 | 1138674 | 981 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4905 | Fog;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076558 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER |  | 41984 | 152 | 1135483 | 2184 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4368 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075778 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER |  | 41984 | 152 | 1129431 | 2184 | Distribution Circuit | Vegetation | Tree - fell into line | 244 | 432315 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0074918 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 41984 | 1247 | 1133677 | 1511 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 4533 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075925 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER |  | 41984 | 305 | 1128850 | 2538 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 298569 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0074827 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER |  | 41985 | 2150 | 1139284 | 29 | Distribution Circuit | Equipment Failure/Involved | Other | 102 | 2958 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0074827 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER |  | 41984 | 510 | 1129409 | 2410 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 52229 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0074908 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER |  | 41985 | 2123 | 1139299 | 118 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 118 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0074827 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 42003 | 846 | 1150568 | 339 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 339 | Fog;32 - 90 F | Cutout- fuse holder | Broken- wire on ground | 14-0078927 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER |  | 41984 | 441 | 1129160 | 1389 | Distribution Circuit | Vegetation | Tree - fell into line | 593 | 704376 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0074878 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 41984 | 535 | 1132583 | 1360 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1360 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075272 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER |  | 41984 | 217 | 1128884 | 3701 | Distribution Circuit | Equipment Failure/Involved | Other | 25 | 86504 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0074812 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | EEL RIVER 1101 | 192381101 | RECLOSER |  | 41984 | 322 | 1128944 | 3546 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 276588 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on object | 14-0074833 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
KERN | Tier 2 | POSO MOUNTAIN-2101 | 253642101 | RECLOSER |  | 41984 | 2342 | 1136682 | 2368 | Distribution Circuit | Equipment Failure/Involved | Other | 27 | 63936 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0076008 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
LOS PADRES | Tier 2 | BUELLTON-1101 | 183041101 | FUSE |  | 41985 | 634 | 1137198 | 1781 | Distribution Circuit | Equipment Failure/Involved | Other | 33 | 65822 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076296 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
LOS PADRES | Tier 2 | SANTA YNEZ-1102 | 182721102 | FUSE |  | 41985 | 621 | 1138040 | 2410 | Distribution Circuit | Equipment Failure/Involved | Other | 21 | 50610 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076453 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
LOS PADRES | Tier 2 | SANTA YNEZ-1104 | 182721104 | FUSE |  | 41984 | 2047 | 1136032 | 3398 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 190288 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0076098 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
LOS PADRES | Tier 2 | PURISIMA-1101 | 182971101 | OTHER |  | 41984 | 1139 | 1133323 | 518 | Distribution Circuit | Equipment Failure/Involved | Other | 14 | 7186 | Drizzle;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075587 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
LOS PADRES | Tier 3 | SANTA MARIA-1108 | 182671108 | RECLOSER |  | 41984 | 2110 | 1136342 | 2755 | Distribution Circuit | 3rd Party | Vehicle | 319 | 561161 | Drizzle;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0075934 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
LOS PADRES | Tier 3 | SANTA MARIA-1108 | 182671108 | FUSE |  | 41984 | 1920 | 1139430 | 3600 | Distribution Circuit | Equipment Failure/Involved | Other | 58 | 208800 | Rain;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0076665 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
LOS PADRES | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | FUSE |  | 41984 | 2157 | 1136947 | 1484 | Distribution Circuit | Vegetation | Tree - branch fell on line | 77 | 135674 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076103 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
LOS PADRES | Tier 2 | FOOTHILL-1101 | 182951101 | FUSE |  | 41984 | 1928 | 1139274 | 2084 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 18756 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076586 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
LOS PADRES | Tier 3 | TEMPLETON-2113 | 183052113 | FUSE |  | 41984 | 1838 | 1135375 | 1688 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 28696 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0076201 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
LOS PADRES | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE |  | 41984 | 1558 | 1134769 | 592 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 20802 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075708 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | RECLOSER |  | 41984 | 1901 | 1135524 | 547 | Distribution Circuit | Vegetation | Tree - fell into line | 522 | 160563 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075784 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
LOS PADRES | Tier 2 | CAMBRIA-1102 | 182771102 | RECLOSER |  | 41984 | 1919 | 1135720 | 769 | Distribution Circuit | Vegetation | Tree - fell into line | 611 | 79832 | Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 14-0075837 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
LOS PADRES | Tier 2 | CAMBRIA-1102 | 182771102 | FUSE |  | 41984 | 1732 | 1135157 | 1822 | Distribution Circuit | Equipment Failure/Involved | Other | 80 | 120108 | Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 14-0075760 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
MISSION | Tier 2 | VINEYARD-2107 | 14502107 | FUSE |  | 42003 | 1419 | 1152687 | 1259 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 42125 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079180 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
MISSION | Tier 3 | CASTRO VALLEY-1108 | 14091108 | RECLOSER |  | 42003 | 1330 | 1152313 | 435 | Distribution Circuit | Vegetation | Tree - fell into line | 394 | 71393 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0079088 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
MISSION | Tier 2 | CAYETANO-2111 | 14422111 | FUSE |  | 42003 | 1820 | 1154724 | 365 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 8255 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079393 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
NORTH BAY | Tier 2 | ALTO-1125 | 42031125 | FUSE |  | 41984 | 727 | 1130628 | 1498 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 55426 | Heavy rain;32 - 90 F | Conductor- Overhead | On Ground | 14-0075690 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH BAY | Tier 2 | ALTO-1125 | 42031125 | FUSE |  | 41984 | 601 | 1129696 | 1986 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 25053 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0075862 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | FUSE |  | 42003 | 1432 | 1152819 | 501 | Distribution Circuit | Equipment Failure/Involved | Other | 63 | 31563 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0079431 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH BAY | Tier 2 | BOLINAS-1101 | 42261101 | RECLOSER |  | 41984 | 51 | 1128816 | 2253 | Distribution Circuit | Vegetation | Tree - fell into line | 820 | 179748 | Heavy rain;32 - 90 F | Conductor- Overhead | On Ground | 14-0074792 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
NORTH BAY | Tier 2 | BOLINAS-1101 | 42261101 | RECLOSER |  | 41984 | 1734 | 1135428 | 773 | Distribution Circuit | Equipment Failure/Involved | Other | 415 | 320761 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075789 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE |  | 41984 | 727 | 1130627 | 423 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 10152 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075400 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH BAY | Tier 3 | GREENBRAE-1102 | 43091102 | FUSE |  | 41984 | 1005 | 1132651 | 1773 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 69147 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076269 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | RECLOSER |  | 41984 | 527 | 1129451 | 1133 | Distribution Circuit | Equipment Failure/Involved | Other | 19 | 19709 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0074913 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE |  | 41976 | 842 | 1122049 | 423 | Distribution Circuit | Vegetation | Tree - branch fell on line | 124 | 14652 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073264 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE |  | 41984 | 1736 | 1135264 | 1475 | Distribution Circuit | Vegetation | Tree - branch fell on line | 70 | 103250 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0075853 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 41984 | 433 | 1132169 | 772 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5404 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075224 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 41984 | 433 | 1129103 | 772 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 14668 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075216 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 41984 | 800 | 1131786 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 21800 | Strong winds;Below 32 F | Conductor- Overhead | On Ground | 14-0075312 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 41976 | 243 | 1121645 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3252 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073189 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | OTHER |  | 42003 | 1651 | 1154541 | 1274 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 1274 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0079480 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH BAY | Tier 2 | PUEBLO-1104 | 43291104 | FUSE |  | 41976 | 1448 | 1123622 | 677 | Distribution Circuit | Vegetation | Tree - bark fell into line | 16 | 10832 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073572 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
NORTH BAY | Tier 3 | SILVERADO-2105 | 43432105 | FUSE |  | 42003 | 1654 | 1154549 | 1271 | Distribution Circuit | Equipment Failure/Involved | Other | 36 | 26696 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0079407 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 41985 | 1053 | 1138059 | 382 | Distribution Circuit | Equipment Failure/Involved | Other | 32 | 12224 | Fog;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076370 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 41984 | 847 | 1131567 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 3712 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075242 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE |  | 41984 | 946 | 1132435 | 344 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1376 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075425 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH BAY | Tier 2 | CALISTOGA-1101 | 42711101 | FUSE |  | 42003 | 1534 | 1153473 | 807 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 8877 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0079308 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | WYANDOTTE-1107 | 102911107 | FUSE |  | 41985 | 714 | 1137603 | 473 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 946 | Fog;32 - 90 F | Conductor- Overhead | On Ground | 14-0076251 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 42003 | 1050 | 1151296 | 406 | Distribution Circuit | Equipment Failure/Involved | Other | 50 | 20300 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0078998 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 41976 | 1301 | 1123165 | 323 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 969 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0073477 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | WYANDOTTE-1102 | 102911102 | OTHER |  | 41985 | 1137 | 1138174 | 302 | Distribution Circuit | Equipment Failure/Involved | Other | 37 | 8306 | Overcast;32 - 90 F | Connector or Splice (OH) | Broken- wire on ground | 14-0076425 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | OCB |  | 42003 | 1021 | 1151159 | 909 | Distribution Circuit | Vegetation | Tree - fell into line | 726 | 157627 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0078943 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE |  | 41984 | 1123 | 1133225 | 1685 | Distribution Circuit | Equipment Failure/Involved | Other | 8 | 13480 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0075550 | OH | Sus | 0 | 2014 | DEC | Yes | Open Circuit | Yes
NORTH VALLEY | Tier 2 | ELK CREEK-1101 | 102781101 | RECLOSER |  | 41984 | 819 | 1131506 | 299 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 45670 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075288 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE |  | 42003 | 855 | 1150606 | 242 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 4840 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0078907 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE |  | 42003 | 705 | 1150386 | 288 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 5760 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0078885 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | PARADISE-1104 | 102831104 | FUSE |  | 42003 | 1029 | 1151947 | 1186 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 87709 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0079284 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | PARADISE-1104 | 102831104 | RECLOSER |  | 42003 | 849 | 1150608 | 587 | Distribution Circuit | Vegetation | Tree - fell into line | 1768 | 507031 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0078902 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
NORTH VALLEY | Tier 3 | PARADISE-1104 | 102831104 | FUSE |  | 42003 | 916 | 1150736 | 1772 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 31832 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0078916 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | WYANDOTTE-1105 | 102911105 | FUSE |  | 41984 | 818 | 1131476 | 1166 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 37022 | Heavy rain;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0075554 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | PARADISE-1101 | 102831101 | FUSE |  | 41984 | 826 | 1131592 | 738 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 50922 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075364 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | PARADISE-1101 | 102831101 | FUSE |  | 42003 | 1431 | 1152920 | 1012 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 27995 | Strong winds;32 - 90 F | Anchor or Guy | Broken- wire on object | 14-0079237 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | WYANDOTTE-1105 | 102911105 | FUSE |  | 42003 | 800 | 1156019 | 1458 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 36702 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079584 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | PARADISE-1101 | 102831101 | FUSE |  | 42003 | 929 | 1150781 | 2031 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 34527 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0078941 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | PARADISE-1106 | 102831106 | FUSE |  | 42003 | 828 | 1150497 | 1380 | Distribution Circuit | Vegetation | Tree - fell into line | 291 | 156005 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0079211 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE |  | 42003 | 1205 | 1151741 | 790 | Distribution Circuit | Vegetation | Tree - branch fell on line | 89 | 70310 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079339 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | FUSE |  | 42003 | 948 | 1150861 | 1200 | Distribution Circuit | Vegetation | Tree - fell into line | 204 | 244800 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079100 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | FUSE |  | 42003 | 928 | 1150821 | 1377 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 22032 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079487 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | BUCKS CREEK-1103 | 102211103 | FUSE |  | 41984 | 957 | 1132571 | 4646 | Distribution Circuit | Vegetation | Tree - fell into line | 313 | 1013602 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0075380 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER |  | 41984 | 822 | 1131600 | 229 | Distribution Circuit | Equipment Failure/Involved | Other | 1070 | 125303 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075147 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE |  | 41984 | 605 | 1129739 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3080 | Heavy rain;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0075081 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | FUSE |  | 41984 | 816 | 1132500 | 634 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 17118 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075484 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | FUSE |  | 41984 | 755 | 1131175 | 500 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 10500 | Heavy rain;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0075186 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | FUSE |  | 41985 | 701 | 1138660 | 934 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4670 | Fog;32 - 90 F | Connector or Splice (OH) | Broken- wire on ground | 14-0076473 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | GRAYS FLAT-0401 | 102530401 | FUSE |  | 41985 | 1636 | 1138902 | 1054 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 12648 | Overcast;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076492 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
NORTH VALLEY | Tier 2 | GRAYS FLAT-0401 | 102530401 | FUSE |  | 41985 | 939 | 1137798 | 1923 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 72085 | Fog;32 - 90 F | Connector or Splice (OH) | Broken- wire on ground | 14-0076376 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | FUSE |  | 42003 | 803 | 1150437 | 267 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 20559 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0078922 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | FUSE |  | 41984 | 436 | 1129110 | 1311 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 11358 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0075300 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | VOLTA-1102 | 102541102 | FUSE |  | 41984 | 1342 | 1134016 | 648 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 6462 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075672 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | RECLOSER |  | 41984 | 933 | 1132382 | 474 | Distribution Circuit | Equipment Failure/Involved | Other | 352 | 82248 | Strong winds;32 - 90 F | Connector or Splice (OH) | Broken- wire on ground | 14-0075354 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | FUSE |  | 41984 | 508 | 1129265 | 1213 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 8563 | Heavy rain;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0075499 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
NORTH VALLEY | Tier 3 | GIRVAN-1101 | 103401101 | RECLOSER |  | 41984 | 654 | 1130432 | 436 | Distribution Circuit | Vegetation | Tree - fell into line | 416 | 59392 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0075121 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | WHITMORE-1101 | 103601101 | FUSE |  | 41984 | 538 | 1129600 | 1535 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 53023 | Heavy rain;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0075066 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | WHITMORE-1101 | 103601101 | RECLOSER |  | 42003 | 750 | 1150422 | 832 | Distribution Circuit | Vegetation | Tree - fell into line | 174 | 94299 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0078898 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | RECLOSER |  | 41984 | 954 | 1132765 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 233 | 54873 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0075451 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | RECLOSER |  | 41984 | 925 | 1132232 | 94 | Distribution Circuit | Vegetation | Tree - fell into line | 250 | 23500 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0075234 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | OTHER |  | 41984 | 925 | 1133115 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1725 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0075234 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | FUSE |  | 42003 | 824 | 1150498 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 45333 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0078914 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | RISING RIVER-1101 | 103551101 | RECLOSER |  | 41984 | 535 | 1129851 | 1421 | Distribution Circuit | Vegetation | Tree - fell into line | 534 | 718580 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075028 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | PIT NO 3-2101 | 103732101 | RECLOSER |  | 41984 | 1203 | 1133458 | 166 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 2625 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0075430 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 41984 | 529 | 1138004 | 2596 | Distribution Circuit | Equipment Failure/Involved | Other | 20 | 51920 | Rain;32 - 90 F | Conductor- Overhead | On Ground | 14-0076299 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 41984 | 936 | 1132317 | 3529 | Distribution Circuit | Equipment Failure/Involved | Other | 5 | 14960 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076301 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 41984 | 823 | 1131545 | 887 | Distribution Circuit | Equipment Failure/Involved | Other | 13 | 11531 | Rain;32 - 90 F | Conductor- Overhead | On Ground | 14-0075467 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER |  | 41984 | 835 | 1134718 | 1210 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 20570 | Rain;32 - 90 F | Conductor- Overhead | On Ground | 14-0075639 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 41984 | 752 | 1133548 | 758 | Distribution Circuit | Equipment Failure/Involved | Other | 34 | 25772 | Rain;32 - 90 F | Conductor- Overhead | On Ground | 14-0075627 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE |  | 41984 | 1922 | 1135637 | 1748 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 24472 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076457 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | OTHER |  | 42003 | 1557 | 1153668 | 1386 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 75738 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079363 | OH | Sus | 0 | 2014 | DEC | Yes | Open Circuit | Yes
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | RECLOSER |  | 41984 | 1323 | 1133890 | 197 | Distribution Circuit | Equipment Failure/Involved | Other | 143 | 27170 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075502 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER |  | 41984 | 1320 | 1133906 | 532 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 12768 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075510 | OH | Sus | 31120659 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 41984 | 653 | 1131371 | 380 | Distribution Circuit | Vegetation | Tree - branch fell on line | 93 | 27093 | Rain;32 - 90 F | Anchor or Guy | Broken- wire on object | 14-0075453 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 41984 | 1818 | 1135345 | 1047 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 6282 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075765 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 41984 | 1537 | ODB-9919 | 3078 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 6156 | Clear;32 - 90 F | Conductor- Overhead | On Ground | 14-0076355 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 42003 | 1432 | 1153418 | 1488 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 40176 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079243 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 41976 | 1132 | 1123022 | 676 | Distribution Circuit | Vegetation | Tree - bark fell into line | 60 | 39445 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073444 | OH | Sus | 31118268 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 41976 | 1100 | 1122489 | 1029 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 44247 | Heavy rain;32 - 90 F | Conductor- Overhead | On Ground | 14-0073538 | OH | Sus | 42283848 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 41985 | 2215 | 1139311 | 807 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 10491 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076629 | OH | Sus | 31120659 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER |  | 41984 | 848 | 1131818 | 95 | Distribution Circuit | Equipment Failure/Involved | Other | 68 | 6460 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0075181 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 41984 | 1138 | 1135029 | 1686 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 23604 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075739 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 3 | HALF MOON BAY-1101 | 24101101 | FUSE |  | 41984 | 812 | 1131405 | 2198 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 17584 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075835 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | BERESFORD-0403 | 24040403 | OTHER |  | 42003 | 1950 | 1155308 | 1412 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1412 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079526 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SACRAMENTO | Tier 2 | BROWNS VALLEY-1101 | 152921101 | FUSE |  | 42003 | 1630 | 1153984 | 300 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2400 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0079333 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | RECLOSER |  | 42003 | 840 | 1150530 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 520 | 79320 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0078910 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SAN JOSE | Tier 2 | LLAGAS-2103 | 83182103 | FUSE |  | 41984 | 2140 | 1136215 | 620 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 1240 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075959 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SAN JOSE | Tier 2 | SWIFT-2110 | 83392110 | FUSE |  | 42003 | 1843 | 1156068 | 1342 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 22396 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079602 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SAN JOSE | Tier 2 | MILPITAS-1109 | 82831109 | OTHER |  | 41985 | 1115 | 1138128 | 150 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 300 | Drizzle;32 - 90 F | Conductor- Overhead | On Ground | 14-0076326 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 41976 | 958 | 1122204 | 817 | Distribution Circuit | Equipment Failure/Involved | Other | 14 | 11438 | Rain;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0073345 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 41984 | 833 | 1131657 | 1597 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 11179 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on object | 14-0075600 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
SIERRA | Tier 3 | CLARKSVILLE-2103 | 153612103 | FUSE |  | 41984 | 620 | 1129852 | 275 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 19377 | Drizzle;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075022 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 41984 | 949 | 1132513 | 511 | Distribution Circuit | Vegetation | Tree - fell into line | 192 | 70642 | Rain;32 - 90 F | Conductor- Overhead | On Ground | 14-0075426 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE |  | 41984 | 1026 | 1132860 | 1089 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 50094 | Rain;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0075446 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 3 | SHINGLE SPRINGS-2108 | 153652108 | RECLOSER |  | 41984 | 554 | 1129635 | 1951 | Distribution Circuit | Vegetation | Tree - fell into line | 1667 | 212744 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0074971 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | OTHER |  | 42003 | 1049 | 1154477 | 1251 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 136278 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079318 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 42003 | 1022 | 1151136 | 846 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4230 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079527 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 42003 | 1040 | 1151257 | 1150 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 9200 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079441 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 2 | DIAMOND SPRINGS-1107 | 152261107 | FUSE |  | 42003 | 1040 | 1151251 | 1212 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 13980 | Strong winds;32 - 90 F | Transformer | Broken- wire on object | 14-0079203 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 41985 | 1125 | 1138145 | 335 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 1910 | Drizzle;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076356 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
SIERRA | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | FUSE |  | 41976 | 609 | 1121757 | 421 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 31996 | Fog;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073194 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 42003 | 1215 | 1151794 | 615 | Distribution Circuit | Equipment Failure/Involved | Other | 20 | 4300 | Strong winds;32 - 90 F | Connector or Splice (OH) | Broken- wire on ground | 14-0079078 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 41984 | 921 | 1132264 | 307 | Distribution Circuit | Equipment Failure/Involved | Other | 2039 | 49545 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075377 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 42003 | 1630 | 1154043 | 1140 | Distribution Circuit | Equipment Failure/Involved | Other | 22 | 25080 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on object | 14-0079272 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 42003 | 1830 | 1155026 | 580 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1160 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079386 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 41976 | 511 | 1121716 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 7636 | Fog;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073166 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 42003 | 957 | 1153521 | 978 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 38694 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079209 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 42003 | 957 | 1154411 | 1388 | Distribution Circuit | Equipment Failure/Involved | Other | 87 | 115198 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079311 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 42003 | 1455 | 1153156 | 1405 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 8054 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079464 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 42003 | 1209 | 1151755 | 916 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 14607 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079011 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 42003 | 1123 | 1151556 | 1460 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 17520 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079563 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 42003 | 1037 | 1151241 | 1948 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 21324 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079550 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 42003 | 1246 | 1153941 | 964 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 16388 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079438 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 42003 | 1048 | 1151193 | 1137 | Distribution Circuit | Vegetation | Tree - fell into line | 1375 | 353622 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0078955 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE |  | 42003 | 1019 | 1154418 | 915 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 59485 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079469 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | SWITCH |  | 42003 | 1029 | 1152978 | 1217 | Distribution Circuit | Vegetation | Tree - fell into line | 127 | 154559 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079146 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 42003 | 1029 | 1152210 | 1217 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2434 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079071 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER |  | 42003 | 902 | 1150699 | 928 | Distribution Circuit | Vegetation | Tree - fell into line | 306 | 270317 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0078904 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | RECLOSER |  | 41976 | 306 | 1121664 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 875 | 150128 | Rain;32 - 90 F | Crossarm- Wood | Broken- wire on ground | 14-0073135 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | FUSE |  | 41984 | 717 | 1130439 | 538 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 10576 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075221 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE |  | 41976 | 1149 | 1122888 | 259 | Distribution Circuit | Vegetation | Tree - fell into line | 173 | 43781 | Drizzle;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073415 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | HIGGINS-1109 | 152691109 | FUSE |  | 42003 | 1147 | 1151659 | 1639 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 4298 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079241 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | FUSE |  | 42003 | 1000 | 1150948 | 307 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 18113 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0078949 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | RECLOSER |  | 42003 | 1035 | 1151235 | 1751 | Distribution Circuit | Vegetation | Tree - fell into line | 216 | 210631 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079200 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE |  | 42003 | 2121 | 1155662 | 1077 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 2154 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 14-0079488 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 42003 | 1601 | 1153724 | 1438 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 18694 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079477 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | FUSE |  | 42003 | 1116 | 1151512 | 1723 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 37906 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079281 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 42003 | 842 | 1153922 | 1751 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 105060 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079252 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER |  | 42003 | 842 | 1150810 | 1278 | Distribution Circuit | Vegetation | Tree - fell into line | 993 | 560377 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079003 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | OTHER |  | 42003 | 1657 | 1154574 | 1231 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4924 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079518 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 42003 | 922 | 1150847 | 550 | Distribution Circuit | Equipment Failure/Involved | Other | 110 | 60500 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079102 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 41984 | 1030 | 1132899 | 765 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 25180 | Strong winds;32 - 90 F | Cutout- Fused- Distribution | Broken- wire on ground | 14-0075553 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | FUSE |  | 42003 | 952 | 1150873 | 797 | Distribution Circuit | Vegetation | Tree - fell into line | 113 | 69303 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0078959 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | NARROWS-2102 | 153132102 | OTHER |  | 41984 | 125 | 1128899 | 305 | Distribution Circuit | Equipment Failure/Involved | Other | 85 | 25925 | Partly cloudy;32 - 90 F | Connector or Splice (OH) | Broken- wire on ground | 14-0074819 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
SIERRA | Tier 2 | NARROWS-2102 | 153132102 | FUSE |  | 42003 | 1013 | 1151157 | 1074 | Distribution Circuit | Vegetation | Tree - fell into line | 240 | 257760 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079082 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE |  | 41976 | 1428 | 1123470 | 691 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 33713 | Fog;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073530 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
SIERRA | Tier 3 | DRUM-1101 | 152321101 | RECLOSER |  | 41985 | 454 | 1137073 | 2361 | Distribution Circuit | Equipment Failure/Involved | Other | 103 | 86102 | Snow;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076149 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 41984 | 729 | 1130716 | 339 | Distribution Circuit | Equipment Failure/Involved | Other | 53 | 17967 | Drizzle;32 - 90 F | Connector or Splice (OH) | Broken- wire on ground | 14-0075130 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 2 | SUMMIT-1101 | 152591101 | OCB |  | 41985 | 250 | 1136968 | 1130 | Distribution Circuit | Vegetation | Tree - fell into line | 1046 | 411830 | Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 14-0076114 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE |  | 41985 | 907 | 1137709 | 1733 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 10398 | Overcast;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076718 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE |  | 41984 | 955 | 1132485 | 290 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 4060 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075342 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE |  | 42003 | 1003 | 1150967 | 2926 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 27680 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079256 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | RECLOSER |  | 41984 | 638 | 1130009 | 628 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 45216 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075279 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE |  | 42003 | 1602 | 1153754 | 1508 | Distribution Circuit | Equipment Failure/Involved | Other | 52 | 78416 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079528 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE |  | 42003 | 1007 | 1151658 | 3237 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 61503 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0079558 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | ALLEGHANY-1102 | 152101102 | OCB |  | 41984 | 556 | 1129858 | 2284 | Distribution Circuit | Vegetation | Tree - fell into line | 153 | 49907 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075037 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE |  | 41984 | 1048 | 1132493 | 700 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 15400 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075552 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SIERRA | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER |  | 41985 | 719 | 1137348 | 109 | Distribution Circuit | Equipment Failure/Involved | Other | 81 | 8829 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076193 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
SIERRA | Tier 2 | ALLEGHANY-1101 | 152101101 | RECLOSER |  | 41985 | 1519 | 1138694 | 2844 | Distribution Circuit | Equipment Failure/Involved | Other | 198 | 142613 | Overcast;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076542 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER |  | 41985 | 1235 | 1138438 | 1549 | Distribution Circuit | Equipment Failure/Involved | Other | 36 | 10649 | Drizzle;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076454 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER |  | 41984 | 445 | 1129291 | 319 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 34066 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075014 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | SWITCH |  | 42003 | 1201 | 1152477 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 48667 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079106 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER |  | 41984 | 1219 | 1133696 | 1846 | Distribution Circuit | Equipment Failure/Involved | Other | 80 | 36527 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0075806 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 41976 | 1208 | 1122972 | 252 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 9828 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073417 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
SONOMA | Tier 2 | COTATI-1105 | 42271105 | OTHER |  | 41984 | 534 | 1132514 | 926 | Distribution Circuit | Equipment Failure/Involved | Other | 489 | 384387 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075304 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
SONOMA | Tier 2 | COTATI-1105 | 42271105 | SECTIONALIZER |  | 41984 | 46 | 1128815 | 276 | Distribution Circuit | Equipment Failure/Involved | Other | 360 | 89341 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0074824 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE |  | 41984 | 707 | 1139324 | 3084 | Distribution Circuit | Vegetation | Tree - bark fell into line | 13 | 40092 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076607 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | FUSE |  | 42003 | 1530 | 1153449 | 780 | Distribution Circuit | Equipment Failure/Involved | Other | 4 | 3120 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0079501 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 3 | DUNBAR-1103 | 43071103 | FUSE |  | 41976 | 1050 | 1122427 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 6496 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073428 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 2 | DUNBAR-1101 | 43071101 | FUSE |  | 42003 | 1601 | 1153721 | 854 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11956 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079356 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 2 | DUNBAR-1101 | 43071101 | FUSE |  | 41985 | 430 | 1137036 | 608 | Distribution Circuit | Vegetation | Tree - fell into line | 151 | 91808 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076165 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 41984 | 1602 | 1134777 | 2540 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5080 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075664 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | FUSE |  | 41984 | 308 | 1131740 | 1338 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 49506 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075729 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 41985 | 1150 | 1138263 | 555 | Distribution Circuit | Vegetation | Tree - branch fell on line | 92 | 19006 | Fog;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076369 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER |  | 41984 | 604 | 1129964 | 1465 | Distribution Circuit | Equipment Failure/Involved | Other | 227 | 332555 | Heavy rain;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0075998 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 41984 | 52 | 1129030 | 930 | Distribution Circuit | Equipment Failure/Involved | Other | 1317 | 445904 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0074858 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 41985 | 753 | 1137435 | 962 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 38480 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0076248 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | FUSE |  | 41985 | 827 | 1137572 | 1684 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 35364 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076360 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 41984 | 546 | 1133068 | 1483 | Distribution Circuit | Equipment Failure/Involved | Other | 105 | 155715 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0075353 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | FUSE |  | 41985 | 838 | 1137618 | 2032 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 25648 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076336 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 42003 | 1434 | 1152843 | 690 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4830 | Strong winds;32 - 90 F | Crossarm- Wood | Broken- wire on ground | 14-0079275 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | OCB |  | 41984 | 405 | 1129219 | 655 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1151 | 583570 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0074894 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE |  | 41984 | 632 | 1131265 | 1423 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 65458 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075419 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 2 | MIRABEL-1101 | 42091101 | FUSE |  | 41984 | 47 | 1128802 | 2373 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 152658 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0074821 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | OTHER |  | 41976 | 1009 | 1122245 | 324 | Distribution Circuit | Vegetation | Tree - branch fell on line | 687 | 109791 | Heavy rain;32 - 90 F | Conductor- Overhead | On Ground | 14-0073321 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 41984 | 6 | 1128755 | 2699 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 53980 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076101 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 41984 | 951 | 1132494 | 842 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 47994 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075605 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 41985 | 1022 | 1137969 | 1398 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1398 | Drizzle;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076400 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER |  | 42003 | 1149 | 1151733 | 499 | Distribution Circuit | Vegetation | Tree - branch fell on line | 113 | 51971 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 14-0079069 | OH | Sus | 0 | 2014 | DEC | Yes | Multi-Fault | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER |  | 41984 | 608 | 1130871 | 593 | Distribution Circuit | Vegetation | Tree - fell into line | 288 | 170784 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075114 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE |  | 41976 | 1503 | 1123301 | 587 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 39329 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073573 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 41984 | 334 | 1128950 | 580 | Distribution Circuit | Equipment Failure/Involved | Other | 17 | 9860 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0074877 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER |  | 41984 | 341 | 1129058 | 852 | Distribution Circuit | Vegetation | Tree - branch fell on line | 468 | 218171 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0074859 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE |  | 41984 | 108 | 1128864 | 430 | Distribution Circuit | Vegetation | Tree - branch fell on line | 132 | 56760 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0074817 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 2 | MIRABEL-1102 | 42091102 | FUSE |  | 41984 | 503 | 1132545 | 1657 | Distribution Circuit | Equipment Failure/Involved | Other | 9 | 14913 | Heavy rain;32 - 90 F | Conductor- Overhead | On Ground | 14-0075269 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 42003 | 1305 | 1152111 | 258 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 6450 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079131 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 41984 | 519 | 1130725 | 779 | Distribution Circuit | Vegetation | Tree - branch fell on line | 90 | 70110 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075375 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | SWITCH |  | 41984 | 1115 | 1133331 | 502 | Distribution Circuit | Vegetation | Tree - branch fell on line | 210 | 105420 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075540 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE |  | 41984 | 2051 | 1136039 | 1299 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5196 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075869 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE |  | 41985 | 1742 | 1139001 | 448 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 7168 | Drizzle;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076514 | OH | Sus | 0 | 2014 | DEC | Yes | Three Phase Fault | Yes
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | OCB |  | 41984 | 303 | 1128916 | 1115 | Distribution Circuit | Vegetation | Tree - fell into line | 462 | 461704 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0074867 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 41984 | 1008 | 1134366 | 1827 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 60291 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075623 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER |  | 41984 | 28 | 1128777 | 2252 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 18310 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0074797 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
SONOMA | Tier 2 | GEYSERVILLE-1101 | 42891101 | OTHER |  | 41984 | 840 | 1131721 | 1595 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 1595 | Clear;32 - 90 F | Conductor- Overhead | On Ground | 14-0075482 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
STOCKTON | Tier 2 | CORRAL-1101 | 162991101 | FUSE |  | 41984 | 1036 | 1132954 | 310 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 3594 | Strong winds;32 - 90 F | Connector or Splice (OH) | Broken- wire on ground | 14-0075411 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE |  | 41984 | 1150 | 1134042 | 666 | Distribution Circuit | Vegetation | Tree - branch fell on line | 509 | 59610 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075526 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | OCB |  | 42003 | 1309 | 1155815 | 641 | Distribution Circuit | Equipment Failure/Involved | Other | 1895 | 207213 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079072 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
STOCKTON | Tier 3 | ELECTRA-1102 | 162161102 | FUSE |  | 41985 | 223 | 1136934 | 172 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 344 | Heavy rain;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0076095 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
STOCKTON | Tier 2 | CLAY-1101 | 163341101 | FUSE |  | 41984 | 951 | 1132634 | 1173 | Distribution Circuit | Vegetation | Tree - bark fell into line | 119 | 26835 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075476 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE |  | 42003 | 1215 | 1152803 | 797 | Distribution Circuit | Vegetation | Tree - fell into line | 241 | 69294 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079128 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE |  | 41984 | 944 | 1132405 | 1052 | Distribution Circuit | Equipment Failure/Involved | Other | 241 | 104024 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0075405 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 41984 | 929 | 1132248 | 1182 | Distribution Circuit | Equipment Failure/Involved | Other | 81 | 20205 | Rain;32 - 90 F | Pole-Wood | Broken- wire on ground | 14-0075441 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 41984 | 935 | 1132581 | 740 | Distribution Circuit | Equipment Failure/Involved | Other | 29 | 21460 | Combination wind/rain/lightning;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075361 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER |  | 42003 | 900 | 1150684 | 1793 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2021 | 1144821 | Combination wind/rain/lightning;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0078900 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | OTHER |  | 41984 | 1202 | 1135324 | 1023 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 6138 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076084 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 42003 | 1039 | 1151246 | 894 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 19318 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079260 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 41984 | 1154 | 1133389 | 1464 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 8784 | Combination wind/rain/lightning;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076197 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 42003 | 1340 | 1152368 | 1070 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 48560 | Combination wind/rain/lightning;32 - 90 F | Connector or Splice (OH) | Broken- wire on ground | 14-0079517 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 42003 | 836 | 1150510 | 601 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 15025 | Combination wind/rain/lightning;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0078917 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 41984 | 1024 | 1132842 | 1347 | Distribution Circuit | Equipment Failure/Involved | Other | 25 | 33675 | Combination wind/rain/lightning;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0076108 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 41984 | 1003 | 1132767 | 1598 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 51124 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075628 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER |  | 41984 | 955 | 1132589 | 1141 | Distribution Circuit | Vegetation | Tree - fell into line | 304 | 346864 | Combination wind/rain/lightning;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075436 | OH | Sus | 0 | 2014 | DEC | Yes |  | Yes
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | OTHER |  | 42003 | 1127 | 1152406 | 832 | Distribution Circuit | Equipment Failure/Involved | Other | 150 | 115320 | Combination wind/rain/lightning;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079096 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
YOSEMITE | Tier 2 | COARSEGOLD-2102 | 254432102 | OCB |  | 42003 | 1707 | 1155014 | 2766 | Distribution Circuit | Vegetation | Tree - fell into line | 1271 | 764428 | Combination wind/rain/lightning;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079484 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER |  | 42003 | 1811 | 1154678 | 1254 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 62419 | Combination wind/rain/lightning;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079412 | OH | Sus | 31123825 | 2014 | DEC | Yes | Line to Ground | Yes
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE |  | 41984 | 1941 | 1135767 | 325 | Distribution Circuit | Equipment Failure/Involved | Other | 109 | 10387 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075858 | OH | Sus | 0 | 2014 | DEC | Yes | None | Yes
YOSEMITE | Tier 3 | OAKHURST-1102 | 254421102 | OCB |  | 42003 | 1740 | 1154727 | 583 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1116 | 323217 | Combination wind/rain/lightning;32 - 90 F | Transformer | Broken- wire on ground | 14-0079361 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE |  | 42003 | 1621 | 1155989 | 891 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 12849 | Combination wind/rain/lightning;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079562 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER |  | 42003 | 1646 | 1154124 | 859 | Distribution Circuit | Vegetation | Tree - fell into line | 460 | 267251 | Combination wind/rain/lightning;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079321 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Ground | Yes
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 42003 | 2024 | 1155444 | 1242 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 28566 | Combination wind/rain/lightning;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0079597 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER |  | 41984 | 924 | 1132229 | 643 | Distribution Circuit | Vegetation | Tree - fell into line | 652 | 195121 | Overcast;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075233 | OH | Sus | 42295242 | 2014 | DEC | Yes | Line to Ground | Yes
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 41976 | 757 | 1121939 | 287 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 12054 | Combination wind/rain/lightning;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0073206 | OH | Sus | 31118857 | 2014 | DEC | Yes | Line to Ground | Yes
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 41984 | 1204 | 1133731 | 532 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 21812 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 14-0075604 | OH | Sus | 0 | 2014 | DEC | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER |  | 42100 | 2232 | 1214427 | 790 | Distribution Circuit | Vegetation | Tree - fell into line | 311 | 180026 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0024650 | OH | Sus | 0 | 2015 | APR | Yes | Multi-Fault | Yes
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 42351 | 1032 | 1361363 | 969 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4845 | Partly Cloudy-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084858 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 42351 | 1044 | 1361445 | 1635 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 39921 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084936 | OH | Sus | 0 | 2015 | DEC | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 42351 | 957 | 1361120 | 758 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 21142 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084859 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 42351 | 1011 | 1361207 | 483 | Distribution Circuit | Equipment Failure/Involved | Overhead | 98 | 20928 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084823 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42351 | 944 | 1361640 | 101 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 4343 | Clear;32-90 F | Conductor- Overhead | On Ground | 15-0084752 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | JUMPER |  | 42351 | 1010 | 1362302 | 673 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2019 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084876 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 42351 | 1005 | 1361152 | 578 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 10982 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084839 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 42351 | 1005 | 1361151 | 405 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 13770 | Strong Winds-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084792 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 42351 | 1731 | 1362822 | 334 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 6012 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0085039 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | OTHER |  | 42351 | 1023 | 1361691 | 911 | Distribution Circuit | Vegetation | Tree - fell into line | 500 | 125830 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084768 | OH | Sus | 42588469 | 2015 | DEC | Yes | Force Out | Yes | Yes
EAST BAY | Tier 3 | OAKLAND X 1104 | 12541104 | OTHER |  | 42351 | 923 | 1360762 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 676 | 67870 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084701 | OH | Sus | 31205544 | 2015 | DEC | Yes | Open Circuit | Yes | No
EAST BAY | Tier 2 | FLORENCE 0401 | 12690401 | OCB |  | 42351 | 743 | 1360231 | 280 | Distribution Circuit | Vegetation | Tree - fell into line | 479 | 35020 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 15-0084558 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 42351 | 1904 | 1362915 | 473 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1892 | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 15-0085050 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 42351 | 542 | 1359974 | 1085 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 9765 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084681 | OH | Sus | 0 | 2015 | DEC | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | FUSE |  | 42351 | 1035 | 1361376 | 265 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 4505 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084774 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 42351 | 1039 | 1361403 | 387 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 774 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084857 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42362 | 1850 | 1371354 | 229 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 458 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0087176 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | REDBUD-1101 | 43191101 | RECLOSER |  | 42362 | 1211 | 1371041 | 541 | Distribution Circuit | Vegetation | Tree - fell into line | 533 | 125745 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0087115 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER |  | 42351 | 1017 | 1361284 | 638 | Distribution Circuit | Vegetation | Tree - fell into line | 424 | 74987 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084853 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42351 | 1322 | 1362218 | 763 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 52647 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0085197 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42351 | 1021 | 1361267 | 1146 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 29796 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0085210 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42362 | 839 | 1370809 | 313 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 11369 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0087079 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42351 | 1331 | 1362244 | 776 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 119504 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0085196 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | JUMPER |  | 42351 | 1332 | 1362297 | 793 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 6533 | Clear;32-90 F | Conductor- Overhead | On Ground | 15-0085026 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42351 | 716 | 1362680 | 1036 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 67340 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084977 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42351 | 1353 | 1362477 | 1467 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 8652 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0085022 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER |  | 42351 | 1312 | 1362196 | 254 | Distribution Circuit | Vegetation | Tree - fell into line | 366 | 76479 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084969 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | JUMPER |  | 42351 | 714 | 1361225 | 293 | Distribution Circuit | Equipment Failure/Involved | Overhead | 670 | 168198 | Overcast-Heavy Rain;32-90 F | PGs- Kearneys | Broken- wire on ground | 15-0084696 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42362 | 1306 | 1371037 | 109 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 3270 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0087120 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER |  | 42351 | 1304 | 1362179 | 416 | Distribution Circuit | Vegetation | Tree - branch fell on line | 439 | 172554 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084934 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42351 | 713 | 1359994 | 467 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4203 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084543 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A 1104 | 42761104 | FUSE |  | 42351 | 603 | 1361545 | 858 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 64835 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084740 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 42351 | 435 | 1359783 | 306 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2448 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084488 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | SWITCH |  | 42351 | 600 | 1359981 | 413 | Distribution Circuit | Vegetation | Tree - branch fell on line | 176 | 72688 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084591 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER |  | 42351 | 532 | 1362412 | 1348 | Distribution Circuit | Vegetation | Tree - fell into line | 332 | 229513 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084908 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER |  | 42351 | 640 | 1360038 | 579 | Distribution Circuit | Vegetation | Tree - fell into line | 220 | 123430 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084515 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER |  | 42351 | 450 | 1359909 | 676 | Distribution Circuit | Vegetation | Tree - fell into line | 332 | 160358 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084503 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE |  | 42362 | 1619 | 1371732 | 4025 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 44275 | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 15-0087414 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 42351 | 1001 | 1361112 | 746 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 6246 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084912 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | OCB |  | 42351 | 523 | 1359885 | 2202 | Distribution Circuit | Equipment Failure/Involved | Overhead | 682 | 361679 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084489 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | JUMPER |  | 42362 | 445 | 1371067 | 3628 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 112690 | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 15-0087118 | OH | Sus | 0 | 2015 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 42351 | 450 | 1362029 | 970 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 33950 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084816 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | SWITCH |  | 42351 | 523 | 1363666 | 2279 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 22790 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0085352 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND 1141 | 192311141 | FUSE |  | 42351 | 917 | 1362083 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 7189 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084910 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER |  | 42362 | 656 | 1370702 | 3497 | Distribution Circuit | Vegetation | Tree - fell into line | 379 | 1236891 | Overcast-Fog;32-90 F | Crossarm- Wood | Broken- wire on ground | 15-0087061 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | FUSE |  | 42351 | 1759 | 1362856 | 361 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 5415 | Clear-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0085044 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER |  | 42362 | 1253 | 1370999 | 4432 | Distribution Circuit | Environmental/External | Ice or snow | 326 | 1281395 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 15-0087111 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | RECLOSER |  | 42362 | 1135 | 1370806 | 3104 | Distribution Circuit | Environmental/External | Ice or snow | 38 | 42349 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0087101 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE 1102 | 192461102 | FUSE |  | 42351 | 753 | 1360262 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 32376 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084833 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER 1101 | 192381101 | FUSE |  | 42351 | 514 | 1359857 | 536 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 12864 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084576 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | HARRIS 1109 | 192431109 | FUSE |  | 42351 | 734 | 1360205 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4728 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084616 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 42362 | 2130 | 1371813 | 2630 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 31560 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 15-0087306 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER |  | 42362 | 2223 | 1371460 | 3301 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 151846 | Overcast-Fog;Below 32 F | Pole-Wood | Broken- wire on ground | 15-0087230 | OH | Sus | 0 | 2015 | DEC | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER |  | 42351 | 514 | 1359863 | 847 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 38962 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084479 | OH | Sus | 0 | 2015 | DEC | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | RECLOSER |  | 42362 | 2202 | 1371438 | 1713 | Distribution Circuit | Vegetation | Tree - branch fell on line | 151 | 230322 | Snow-Sleet or Ice-Rain-Hail-Combination-Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 15-0087227 | OH | Sus | 0 | 2015 | DEC | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1102 | 192171102 | OCB |  | 42362 | 2309 | s1177329 | 3101 | Distribution Circuit | Vegetation | Tree - fell into line | 146 | 92054 | Snow-Sleet or Ice-Rain-Combination-Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 15-0087248 | OH | Sus | 0 | 2015 | DEC | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 42362 | 1943 | 1371413 | 4001 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 106920 | Snow-Sleet or Ice-Rain-Hail-Combination-Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 15-0087223 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 42351 | 1617 | 1362253 | 453 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2265 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0085003 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 42362 | 950 | 1370858 | 684 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 684 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0087119 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE |  | 42351 | 1505 | 1362526 | 66 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 132 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084945 | OH | Sus | 0 | 2015 | DEC | Yes | None | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE |  | 42351 | 849 | 1360540 | 471 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5652 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | On Ground | 15-0084782 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | BOLINAS-1101 | 42261101 | RECLOSER |  | 42351 | 843 | 1360524 | 853 | Distribution Circuit | Vegetation | Tree - fell into line | 820 | 208420 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 15-0084593 | OH | Sus | 42589004 | 2015 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | MONTICELLO-1101 | 43051101 | RECLOSER |  | 42351 | 829 | 1360465 | 866 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 22516 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 15-0084650 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | CALISTOGA 1102 | 42711102 | OTHER |  | 42351 | 928 | s1174426 | 367 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 20027 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084758 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
NORTH COAST | Tier 2 | REDBUD 1101 | 43191101 | JUMPER |  | 42362 | 1233 | 1370995 | 274 | Distribution Circuit | Vegetation | Tree - fell into line | 1593 | 146925 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0087108 | OH | Sus | 0 | 2015 | DEC | Yes | Open Circuit | Yes | No
NORTH COAST | Tier 2 | BIG RIVER 1101 | 43081101 | RECLOSER |  | 42351 | 716 | 1360154 | 492 | Distribution Circuit | Vegetation | Tree - branch fell on line | 582 | 131494 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084657 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
NORTH COAST | Tier 2 | WILLITS 1103 | 42661103 | FUSE |  | 42351 | 719 | 1360144 | 541 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1082 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084887 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | PARADISE 1104 | 102831104 | FUSE |  | 42351 | 858 | 1360574 | 249 | Distribution Circuit | Vegetation | Tree - fell into line | 165 | 41085 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084753 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO 1101 | 103031101 | OCB |  | 42351 | 856 | 1360571 | 175 | Distribution Circuit | Vegetation | Tree - fell into line | 2493 | 190854 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084609 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | CORNING 1102 | 103331102 | FUSE |  | 42362 | 2028 | 1371398 | 694 | Distribution Circuit | 3rd Party | Gun Shot | 61 | 39836 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0087229 | OH | Sus | 31208880 | 2015 | DEC | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1102 | 24131102 | FUSE |  | 42351 | 919 | 1360775 | 504 | Distribution Circuit | Vegetation | Tree - fell into line | 333 | 167832 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084641 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 42351 | 1100 | 1361605 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2300 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084881 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | BELMONT-1103 | 24031103 | FUSE |  | 42362 | 1958 | 1371392 | 945 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 45285 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0087178 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | BERESFORD 0403 | 24040403 | OTHER |  | 42351 | 1014 | 1361230 | 276 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 3334 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084772 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | PLACERVILLE-1110 | 153081110 | FUSE |  | 42351 | 1111 | 1361650 | 296 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 9472 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084894 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 42351 | 1123 | 1361721 | 642 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 43014 | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 15-0084850 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PENRYN-1107 | 152561107 | FUSE |  | 42362 | 1150 | 1370952 | 167 | Distribution Circuit | 3rd Party | Vehicle | 97 | 11766 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0087106 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | OTHER |  | 42351 | 750 | 1360617 | 520 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 14215 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084615 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 42351 | 824 | 1360443 | 546 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2730 | Strong Winds-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084773 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | OCB |  | 42351 | 803 | 1360333 | 984 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1122 | 251687 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084555 | OH | Sus | 42588659 | 2015 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 42351 | 813 | 1360357 | 749 | Distribution Circuit | Equipment Failure/Involved | Overhead | 116 | 72844 | Strong Winds-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084775 | OH | Sus | 0 | 2015 | DEC | Yes | Force Out | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | RECLOSER |  | 42362 | 1543 | 1371213 | 515 | Distribution Circuit | Equipment Failure/Involved | Overhead | 92 | 16100 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0087141 | OH | Sus | 31208799 | 2015 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE |  | 42351 | 822 | 1360429 | 329 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 21714 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084637 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER |  | 42351 | 715 | 1360165 | 1045 | Distribution Circuit | Vegetation | Tree - fell into line | 229 | 147116 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084603 | OH | Sus | 42588659 | 2015 | DEC | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 42351 | 932 | 1360868 | 763 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1910 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084968 | OH | Sus | 0 | 2015 | DEC | Yes | Force Out | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 42351 | 757 | 1362231 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2985 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084863 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | OLETA 1101 | 163541101 | RECLOSER |  | 42351 | 1056 | 1361641 | 251 | Distribution Circuit | Vegetation | Tree - branch fell on line | 478 | 93486 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0084811 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD 2104 | 254432104 | FUSE |  | 42362 | 1603 | 1371220 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 220 | 24840 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0087145 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | FUSE |  | 42362 | 334 | 1370699 | 573 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 5730 | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 15-0087054 | OH | Sus | 0 | 2015 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | FUSE |  | 42041 | 218 | 1173086 | 672 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 10080 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009879 | OH | Sus | 42329112 | 2015 | FEB | Yes | Line to Line | Yes
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | RECLOSER |  | 42041 | 1510 | 1176124 | 694 | Distribution Circuit | Vegetation | Tree - fell into line | 368 | 79208 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0010398 | OH | Sus | 31132865 | 2015 | FEB | Yes | Line to Line | Yes
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 42041 | 1621 | 1176829 | 548 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 14621 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010646 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 42042 | 652 | 1180206 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2160 | Drizzle;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011130 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 42043 | 1227 | 1182688 | 548 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 7672 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011638 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 42042 | 653 | 1180209 | 387 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 2283 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011056 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | PAUL SWEET-2102 | 83252102 | FUSE |  | 42043 | 1125 | 1182507 | 1040 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6240 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011669 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | OTHER |  | 42043 | 1056 | 1182430 | 851 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 851 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011654 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 42041 | 2123 | 1178684 | 1275 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 67575 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010872 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 42042 | 1549 | 1181473 | 569 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7397 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011297 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 42041 | 753 | 1173502 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 3019 | 259134 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009860 | OH | Sus | 31132982 | 2015 | FEB | Yes | Line to Line | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42043 | 1506 | 1183040 | 431 | Distribution Circuit | Equipment Failure/Involved | Other | 16 | 6896 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011651 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | LOMPICO-0401 | 88880401 | FUSE |  | 42041 | 1730 | 1176990 | 1610 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 25760 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011372 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | LOMPICO-0401 | 88880401 | FUSE |  | 42043 | 1829 | 1183478 | 760 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 60040 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011726 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | LOMPICO-0401 | 88880401 | FUSE |  | 42043 | 1738 | 1183996 | 848 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 16960 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011768 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 42043 | 1741 | 1183927 | 679 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 41006 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011779 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 2 | BIG BASIN-1102 | 82841102 | FUSE |  | 42043 | 1751 | 1185409 | 1918 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 13963 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011919 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42041 | 2056 | 1178468 | 1324 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 9584 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010831 | OH | Sus | 42328658 | 2015 | FEB | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 42042 | 2130 | 1181937 | 2086 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 16688 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011415 | OH | Sus | 31132912 | 2015 | FEB | Yes | Line to Line | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER |  | 42041 | 2113 | 1178840 | 3338 | Distribution Circuit | Equipment Failure/Involved | Other | 204 | 52093 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010837 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 42043 | 1419 | 1182959 | 2351 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 6851 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011611 | OH | Sus | 31132912 | 2015 | FEB | Yes | Line to Line | Yes
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE |  | 42042 | 634 | 1180520 | 1236 | Distribution Circuit | Vegetation | Tree - fell into line | 496 | 47618 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011044 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE |  | 42043 | 1219 | 1182674 | 963 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 18784 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011548 | OH | Sus | 31132916 | 2015 | FEB | Yes | Line to Ground | Yes
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE |  | 42041 | 1535 | 1176037 | 520 | Distribution Circuit | Equipment Failure/Involved | Other | 5 | 2600 | Clear;32 - 90 F | Connector or Splice (OH) | Broken- wire on ground | 15-0010384 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
DE ANZA | Tier 2 | SARATOGA-1105 | 83371105 | SWITCH |  | 42042 | 331 | 1179973 | 30 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 0 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010269 | OH | Sus | 31132912 | 2015 | FEB | Yes |  | Yes
DE ANZA | Tier 2 | STELLING-1110 | 83481110 | FUSE |  | 42041 | 1408 | 1175762 | 122 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 652 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010269 | OH | Sus | 31132912 | 2015 | FEB | Yes | Line to Ground | Yes
EAST BAY | Tier 2 | SAN LEANDRO-1109 | 13111109 | FUSE |  | 42041 | 1021 | 1174507 | 376 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 14664 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010057 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE |  | 42041 | 1428 | 1175827 | 543 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 13032 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010355 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 42042 | 1629 | 1181535 | 2026 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12156 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011311 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER |  | 42043 | 1954 | 1183953 | 1256 | Distribution Circuit | Vegetation | Tree - fell into line | 261 | 322458 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011784 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER |  | 42041 | 806 | 1173546 | 1644 | Distribution Circuit | Vegetation | Tree - fell into line | 261 | 425914 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0010247 | OH | Sus | 0 | 2015 | FEB | Yes | Three Phase Fault | Yes
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 42041 | 335 | 1173712 | 850 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11900 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009900 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 42043 | 2042 | 1185254 | 2568 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 43059 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0012201 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 42041 | 654 | 1173411 | 1593 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 128380 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010399 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 42041 | 837 | 1181135 | 4703 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 27681 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011195 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 42041 | 522 | 1173199 | 3233 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 85190 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009837 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 42041 | 613 | 1173310 | 2204 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 37468 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010933 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 42041 | 3 | 1173196 | 2367 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 54441 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009808 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 42041 | 702 | 1173418 | 3391 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 9437 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011027 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | HIGHLANDS-1103 | 43361103 | FUSE |  | 42043 | 2151 | 1185637 | 3929 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 43219 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 15-0012272 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 42041 | 1900 | 1178783 | 2580 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 15480 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010860 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | RECLOSER |  | 42042 | 901 | 1187254 | 4900 | Distribution Circuit | Vegetation | Tree - fell into line | 146 | 715400 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0012327 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | OTHER |  | 42041 | 803 | 1173629 | 547 | Distribution Circuit | Vegetation | Tree - fell into line | 216 | 112716 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009878 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 42041 | 1819 | 1178748 | 1536 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 87552 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011364 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | OTHER |  | 42043 | 2124 | 1184578 | 1867 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1867 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011973 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | FUSE |  | 42042 | 907 | 1180682 | 4798 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 43182 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011167 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 42041 | 648 | 1173398 | 1861 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 14888 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010193 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 42043 | 1831 | 1184062 | 1269 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 39339 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011819 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | LUCERNE-1106 | 43351106 | RECLOSER |  | 42041 | 808 | 1173540 | 312 | Distribution Circuit | Vegetation | Tree - fell into line | 257 | 24814 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009903 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | HARTLEY-1101 | 43211101 | FUSE |  | 42041 | 2206 | 1179022 | 4129 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12792 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010829 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | UKIAH-1114 | 42771114 | FUSE |  | 42042 | 2056 | 1180643 | 2399 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 9596 | Overcast;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011699 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | FUSE |  | 42043 | 2129 | 1185839 | 1744 | Distribution Circuit | Vegetation | Tree - branch fell on line | 52 | 90688 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0012139 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER |  | 42041 | 1921 | 1179285 | 1539 | Distribution Circuit | Vegetation | Tree - fell into line | 501 | 642067 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010596 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | RECLOSER |  | 42042 | 158 | 1179796 | 3591 | Distribution Circuit | Vegetation | Tree - fell into line | 292 | 444437 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011100 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42041 | 924 | 1173906 | 1896 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 54984 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010536 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42041 | 1921 | 1179792 | 1614 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 111366 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010883 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42041 | 1921 | 1181383 | 2859 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 71475 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011272 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42041 | 1921 | 1181210 | 5571 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 16713 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0011215 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42041 | 1141 | 1174550 | 1666 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 36652 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010380 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42041 | 1921 | 1181087 | 2430 | Distribution Circuit | Equipment Failure/Involved | Other | 5 | 12150 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011181 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42041 | 1921 | 1180961 | 2464 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 101024 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011147 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42041 | 830 | 1173680 | 3243 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3243 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009896 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42041 | 952 | 1173969 | 1640 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 23272 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010434 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42041 | 1719 | 1178233 | 2506 | Distribution Circuit | Equipment Failure/Involved | Other | 65 | 162890 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011350 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER |  | 42043 | 1927 | 1183900 | 2094 | Distribution Circuit | Vegetation | Tree - fell into line | 365 | 764310 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011805 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42041 | 2050 | 1180637 | 1000 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3000 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0011064 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42041 | 1353 | 1176004 | 1412 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 30158 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010339 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42043 | 1552 | 1183171 | 155 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 6975 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011715 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42041 | 937 | 1180028 | 2260 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 33900 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010956 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42041 | 937 | 1176443 | 1941 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 67935 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010416 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | FUSE |  | 42041 | 511 | 1173191 | 596 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 17284 | Strong winds;32 - 90 F | Crossarm- Wood | Broken- wire on ground | 15-0009819 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | FUSE |  | 42043 | 2144 | 1185613 | 716 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 57082 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011981 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42041 | 937 | 1176460 | 1698 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 91692 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010417 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42041 | 1241 | 1181873 | 2025 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 115425 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011375 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42043 | 807 | 1182144 | 498 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 19966 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011508 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42041 | 1656 | 1176920 | 1289 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 79918 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010526 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42041 | 1241 | 1177383 | 1633 | Distribution Circuit | Vegetation | Tree - fell into line | 469 | 758707 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010612 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER |  | 42041 | 935 | 1173905 | 279 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 15419 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010016 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER |  | 42041 | 604 | 1173268 | 2403 | Distribution Circuit | Vegetation | Tree - branch fell on line | 131 | 171322 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009853 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42043 | 809 | 1182153 | 294 | Distribution Circuit | Vegetation | Tree - fell into line | 172 | 50568 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011466 | OH | Sus | 0 | 2015 | FEB | Yes | Three Phase Fault | Yes
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE |  | 42041 | 2217 | 1179196 | 1033 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 114663 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010821 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 42043 | 739 | 1182795 | 646 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2584 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011649 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 42041 | 1838 | 1177568 | 2449 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 17143 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010605 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 42041 | 2332 | 1180166 | 868 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 51212 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010995 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 42043 | 2153 | 1185281 | 1330 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 120152 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011870 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 42043 | 2132 | 1184681 | 536 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 22512 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011957 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER |  | 42041 | 623 | 1173389 | 436 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 34148 | Strong winds;32 - 90 F | Crossarm- Wood | Broken- wire on ground | 15-0009869 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 42043 | 8 | 1184756 | 4159 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 324438 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011879 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 42041 | 910 | 1173752 | 560 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 10640 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010215 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 42042 | 731 | 1180319 | 721 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 7210 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 15-0011231 | OH | Sus | 0 | 2015 | FEB | Yes | Multi-Fault | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 42043 | 811 | 1182137 | 484 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 9196 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011533 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 42043 | 2216 | 1187271 | 1709 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 8545 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0012336 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 42042 | 1030 | 1180918 | 1530 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 21420 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011491 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 42042 | 1451 | 1181372 | 1629 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 3258 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011263 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 42043 | 2153 | 1184870 | 2644 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 15864 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0012582 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 42041 | 2303 | 1179382 | 1437 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 27303 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011282 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 42042 | 1126 | 1181031 | 1724 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 13792 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011512 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 42043 | 706 | 1185678 | 2089 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 87734 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011997 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 42041 | 2327 | 1179466 | 1277 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 58742 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010876 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | RECLOSER |  | 42043 | 2223 | 1185631 | 3117 | Distribution Circuit | Equipment Failure/Involved | Other | 684 | 688758 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011985 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 42041 | 2240 | 1181233 | 2809 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 53371 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 15-0011224 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER |  | 42041 | 2240 | 1179355 | 760 | Distribution Circuit | Vegetation | Tree - fell into line | 389 | 295877 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010792 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 42042 | 1501 | 1181648 | 3089 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 27801 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0011333 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | SWITCH |  | 42042 | 1512 | 1181387 | 3375 | Distribution Circuit | Equipment Failure/Involved | Other | 16 | 54000 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010794 | OH | Sus | 0 | 2015 | FEB | Yes | Open Circuit | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | SWITCH |  | 42043 | 2356 | 1185303 | 1254 | Distribution Circuit | Vegetation | Tree - branch fell on line | 63 | 0 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011878 | OH | Sus | 0 | 2015 | FEB | Yes |  | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 42042 | 1539 | 1181508 | 1873 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 14984 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0011336 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER |  | 42041 | 2252 | 1179359 | 952 | Distribution Circuit | Vegetation | Tree - fell into line | 117 | 111384 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0010794 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 42042 | 721 | 1180710 | 3224 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 58032 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011153 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER |  | 42041 | 1211 | 1174721 | 4996 | Distribution Circuit | Equipment Failure/Involved | Other | 181 | 0 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010098 | OH | Sus | 0 | 2015 | FEB | Yes |  | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 42041 | 2302 | 1180532 | 3858 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 46730 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 15-0011045 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 42043 | 912 | 1182208 | 1938 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 19380 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 15-0011579 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER |  | 42043 | 839 | 1182183 | 3295 | Distribution Circuit | Equipment Failure/Involved | Other | 87 | 259017 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011463 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FORT SEWARD-1122 | 192321122 | FUSE |  | 42043 | 1433 | 1185122 | 2867 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 17202 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0012266 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | OCB |  | 42041 | 1006 | 1174140 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 370 | 158397 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010206 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | OTHER |  | 42042 | 123 | 1180149 | 874 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 149914 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011041 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 42041 | 127 | 1181957 | 5359 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 182206 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011404 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | FUSE |  | 42042 | 221 | 1180697 | 3764 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 11292 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011075 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER |  | 42041 | 938 | 1173932 | 4799 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 119975 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009940 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | OCB |  | 42042 | 200 | 1180393 | 1122 | Distribution Circuit | Vegetation | Tree - fell into line | 739 | 679197 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011102 | OH | Sus | 0 | 2015 | FEB | Yes | Three Phase Fault | Yes
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | OTHER |  | 42042 | 1838 | 1181885 | 2809 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 7691 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011390 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 42041 | 1540 | 1176256 | 4235 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8470 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010597 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | FUSE |  | 42043 | 1452 | 1182767 | 91 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 637 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0011615 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 42042 | 1356 | 1181284 | 2764 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 96740 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011377 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
HUMBOLDT | Tier 2 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 42042 | 343 | 1179969 | 662 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 25818 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010931 | OH | Sus | 0 | 2015 | FEB | Yes | Three Phase Fault | Yes
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 42043 | 910 | 1181995 | 3248 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 3248 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011469 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
LOS PADRES | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | FUSE |  | 42042 | 1429 | 1181338 | 281 | Distribution Circuit | Vegetation | Tree - fell into line | 179 | 11149 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011274 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
LOS PADRES | Tier 3 | TEMPLETON-2113 | 183052113 | RECLOSER |  | 42041 | 1932 | 1177984 | 773 | Distribution Circuit | Vegetation | Tree - fell into line | 406 | 54085 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 15-0010615 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE |  | 42041 | 1315 | 1175327 | 1440 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 113760 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010514 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH BAY | Tier 2 | ALTO-1125 | 42031125 | FUSE |  | 42042 | 1839 | 1181788 | 201 | Distribution Circuit | Equipment Failure/Involved | Other | 357 | 67711 | Strong winds;32 - 90 F | Connector or Splice (OH) | Broken- wire on ground | 15-0011368 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE |  | 42041 | 2210 | 1179101 | 2104 | Distribution Circuit | Equipment Failure/Involved | Other | 9 | 18936 | Strong winds;32 - 90 F | Connector or Splice (OH) | Broken- wire on ground | 15-0010738 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | FUSE |  | 42041 | 2201 | 1178926 | 1716 | Distribution Circuit | Equipment Failure/Involved | Other | 90 | 154440 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0011343 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE |  | 42041 | 1924 | 1177915 | 1839 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 33102 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0011247 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE |  | 42041 | 1919 | 1177855 | 1306 | Distribution Circuit | Vegetation | Tree - branch fell on line | 85 | 65650 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010897 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE |  | 42041 | 1332 | 1175419 | 298 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 5662 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010265 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE |  | 42043 | 1803 | 1183583 | 364 | Distribution Circuit | Vegetation | Tree - fell into line | 205 | 74620 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011721 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
NORTH BAY | Tier 2 | SAN RAFAEL-1109 | 42011109 | OTHER |  | 42042 | 855 | 1180841 | 400 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 1925 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011143 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
NORTH BAY | Tier 2 | SAN RAFAEL-1109 | 42011109 | FUSE |  | 42042 | 54 | 1179707 | 1396 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 36296 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011001 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE |  | 42041 | 1737 | 1176969 | 1318 | Distribution Circuit | Vegetation | Tree - branch fell on line | 64 | 84352 | Strong winds;32 - 90 F | Cutout- Fused- Distribution | Broken- wire on ground | 15-0011262 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | OTHER |  | 42041 | 527 | 1173403 | 613 | Distribution Circuit | Vegetation | Tree - branch fell on line | 233 | 125603 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on object | 15-0009841 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE |  | 42041 | 1358 | 1175657 | 779 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 39128 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010282 | OH | Sus | 0 | 2015 | FEB | Yes | Three Phase Fault | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 42042 | 5 | 1179608 | 2376 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 3429 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on object | 15-0010826 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER |  | 42041 | 417 | 1173145 | 801 | Distribution Circuit | Vegetation | Tree - fell into line | 155 | 124155 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009790 | OH | Sus | 31133058 | 2015 | FEB | Yes | Line to Line | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 42042 | 1519 | 1180503 | 2862 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 44011 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011361 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH BAY | Tier 2 | PUEBLO-2103 | 43292103 | FUSE |  | 42041 | 1514 | 1176092 | 644 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3098 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010393 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE |  | 42043 | 2359 | 1185454 | 2623 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 10492 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0011936 | OH | Sus | 0 | 2015 | FEB | Yes | Three Phase Fault | Yes
NORTH BAY | Tier 2 | SILVERADO-2104 | 43432104 | FUSE |  | 42042 | 338 | 1179963 | 942 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 8478 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010991 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 42041 | 1225 | 1174804 | 1491 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5964 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010512 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER |  | 42041 | 1206 | 1174714 | 645 | Distribution Circuit | Vegetation | Tree - fell into line | 198 | 89506 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010127 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | OCB |  | 42042 | 131 | 1179787 | 687 | Distribution Circuit | Equipment Failure/Involved | Other | 889 | 256542 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010880 | OH | Sus | 0 | 2015 | FEB | Yes | Multi-Fault | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | FUSE |  | 42041 | 1209 | 1174689 | 824 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 6592 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010385 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE |  | 42041 | 1210 | 1175980 | 1762 | Distribution Circuit | Equipment Failure/Involved | Other | 25 | 44050 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0010742 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER |  | 42042 | 1330 | 1181235 | 1875 | Distribution Circuit | Equipment Failure/Involved | Other | 167 | 300525 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011564 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | WYANDOTTE-1105 | 102911105 | FUSE |  | 42042 | 26 | 1180221 | 2119 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 55094 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011326 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | PARADISE-1101 | 102831101 | TRANSFORMER |  | 42043 | 2333 | 1185248 | 867 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 6290 | Strong winds;32 - 90 F | Transformer | Broken- wire on ground | 15-0011917 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | PARADISE-1101 | 102831101 | FUSE |  | 42042 | 445 | 1180042 | 644 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1932 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 15-0010964 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER |  | 42041 | 425 | 1173164 | 593 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1077 | 365976 | Overcast;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009795 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | BUCKS CREEK-1103 | 102211103 | RECLOSER |  | 42042 | 132 | 1181709 | 2165 | Distribution Circuit | Vegetation | Tree - fell into line | 314 | 618504 | Strong winds;32 - 90 F | Crossarm- Wood | Broken- wire on ground | 15-0011349 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 3 | BUCKS CREEK-1103 | 102211103 | FUSE |  | 42042 | 2115 | 1181923 | 3021 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3021 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011398 | OH | Sus | 0 | 2015 | FEB | Yes | Three Phase Fault | Yes
NORTH VALLEY | Tier 3 | BUCKS CREEK-1102 | 102211102 | RECLOSER |  | 42042 | 257 | 1180224 | 5083 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 265640 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011094 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | FUSE |  | 42041 | 920 | 1175443 | 1821 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 16389 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010205 | OH | Sus | 0 | 2015 | FEB | Yes | Open Circuit | Yes
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | SWITCH |  | 42042 | 1820 | 1181726 | 1719 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 39537 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011355 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | GRAYS FLAT-0401 | 102530401 | FUSE |  | 42041 | 555 | 1173556 | 2246 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 87594 | Overcast;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009866 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | FUSE |  | 42042 | 1548 | ODB-9918 | 2607 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 49533 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009920 | OH | Sus | 0 | 2015 | FEB | Yes |  | Yes
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER |  | 42041 | 531 | 1173218 | 6233 | Distribution Circuit | Equipment Failure/Involved | Other | 3 | 18699 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009807 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | PANORAMA-1102 | 103461102 | FUSE |  | 42043 | 1150 | 1182637 | 705 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 1410 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 15-0011538 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | RECLOSER |  | 42042 | 821 | 1180550 | 524 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 143733 | Strong winds;32 - 90 F | Connector or Splice (OH) | Broken- wire on ground | 15-0011193 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER |  | 42042 | 39 | 1179687 | 949 | Distribution Circuit | Equipment Failure/Involved | Other | 391 | 296599 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 15-0010854 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | FUSE |  | 42042 | 39 | 1181929 | 2186 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 48092 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010854 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER |  | 42041 | 455 | 1173195 | 3722 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 482901 | Overcast;32 - 90 F | Conductor- Overhead | On Ground | 15-0009799 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER |  | 42041 | 355 | 1173144 | 541 | Distribution Circuit | Vegetation | Tree - fell into line | 240 | 63900 | Overcast;32 - 90 F | Conductor- Overhead | On Ground | 15-0009791 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | OTHER |  | 42041 | 355 | 1175407 | 4780 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4780 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009791 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | VOLTA-1102 | 102541102 | FUSE |  | 42042 | 342 | 1179968 | 2628 | Distribution Circuit | Equipment Failure/Involved | Other | 29 | 14052 | Strong winds;32 - 90 F | Connector or Splice (OH) | Broken- wire on ground | 15-0011126 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | VOLTA-1102 | 102541102 | RECLOSER |  | 42041 | 201 | 1173093 | 2279 | Distribution Circuit | Vegetation | Tree - fell into line | 1441 | 1622357 | Overcast;32 - 90 F | Crossarm- Wood | Broken- wire on ground | 15-0009778 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE |  | 42041 | 2116 | 1178599 | 2534 | Distribution Circuit | Equipment Failure/Involved | Other | 64 | 122386 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 15-0011122 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | DESCHUTES-1101 | 103351101 | FUSE |  | 42042 | 739 | 1179627 | 652 | Distribution Circuit | Equipment Failure/Involved | Other | 3 | 1956 | Fog;32 - 90 F | Pole-Wood | Broken- wire on ground | 15-0011020 | OH | Sus | 0 | 2015 | FEB | Yes | Three Phase Fault | Yes
NORTH VALLEY | Tier 2 | WHITMORE-1101 | 103601101 | OTHER |  | 42042 | 200 | 1182385 | 2370 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2370 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011496 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | RECLOSER |  | 42041 | 2157 | 1178915 | 2434 | Distribution Circuit | Vegetation | Tree - fell into line | 242 | 239578 | Strong winds;32 - 90 F | Connector or Splice (OH) | Broken- wire on ground | 15-0010732 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 3 | WHITMORE-1101 | 103601101 | FUSE |  | 42042 | 935 | 1180768 | 1660 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6704 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0011091 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | RISING RIVER-1101 | 103551101 | RECLOSER |  | 42041 | 114 | 1173064 | 6814 | Distribution Circuit | Vegetation | Tree - fell into line | 192 | 1173616 | Overcast;32 - 90 F | Pole-Wood | Broken- wire on ground | 15-0009784 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | BURNEY-1101 | 103311101 | RECLOSER |  | 42041 | 235 | 1173101 | 5557 | Distribution Circuit | Vegetation | Tree - fell into line | 398 | 191233 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009806 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | BURNEY-1101 | 103311101 | RECLOSER |  | 42041 | 1006 | ODB-9918 | 532 | Distribution Circuit | Equipment Failure/Involved | Other | 257 | 77704 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009806 | OH | Sus | 0 | 2015 | FEB | Yes |  | Yes
NORTH VALLEY | Tier 2 | BURNEY-1101 | 103311101 | OTHER |  | 42041 | 500 | 1173184 | 5220 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 32472 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010479 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | BURNEY-1101 | 103311101 | FUSE |  | 42041 | 157 | 1173072 | 2383 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 285960 | Overcast;32 - 90 F | Pole-Wood | Broken- wire on ground | 15-0009796 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | BURNEY-1101 | 103311101 | FUSE |  | 42041 | 1029 | 1174173 | 2916 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 137052 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010034 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | BURNEY-1101 | 103311101 | FUSE |  | 42041 | 209 | 1173714 | 2260 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 58760 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0009901 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | RISING RIVER-1101 | 103551101 | OCB |  | 42041 | 229 | ODB-9918 | 1052 | Distribution Circuit | Vegetation | Tree - fell into line | 201 | 91514 | Overcast;32 - 90 F | Pole-Wood | Broken- wire on ground | 15-0009784 | OH | Sus | 0 | 2015 | FEB | Yes |  | Yes
NORTH VALLEY | Tier 2 | BURNEY-1101 | 103311101 | FUSE |  | 42041 | 209 | 1173106 | 3696 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 88704 | Overcast;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009789 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | PIT NO 3-2101 | 103732101 | OCB |  | 42041 | 744 | 1173484 | 6438 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 465599 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 15-0009924 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
NORTH VALLEY | Tier 2 | PIT NO 3-2101 | 103732101 | FUSE |  | 42041 | 744 | 1180625 | 3343 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 90261 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 15-0011060 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | PIT NO 3-2101 | 103732101 | OTHER |  | 42041 | 744 | 1181299 | 4756 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4756 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 15-0011241 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | PIT NO 3-2101 | 103732101 | FUSE |  | 42041 | 744 | 1180610 | 6186 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 43302 | Strong winds;32 - 90 F | Crossarm- Wood | Broken- wire on ground | 15-0011058 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
NORTH VALLEY | Tier 2 | MC ARTHUR-1101 | 103491101 | FUSE |  | 42042 | 735 | 1180334 | 2112 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 35792 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011207 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER |  | 42041 | 1407 | 1177361 | 3068 | Distribution Circuit | Equipment Failure/Involved | Other | 376 | 161503 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010578 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | SWITCH |  | 42042 | 939 | 1180953 | 431 | Distribution Circuit | Equipment Failure/Involved | Other | 66 | 28446 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0011148 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 42042 | 941 | 1180796 | 139 | Distribution Circuit | Equipment Failure/Involved | Other | 93 | 12927 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0011160 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 42043 | 1544 | 1183225 | 1546 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 50146 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0011695 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
PENINSULA | Tier 3 | WOODSIDE-1104 | 24251104 | FUSE |  | 42041 | 1858 | 1177970 | 972 | Distribution Circuit | Equipment Failure/Involved | Other | 27 | 26244 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010652 | OH | Sus | 31132845 | 2015 | FEB | Yes | Line to Line | Yes
PENINSULA | Tier 2 | EMERALD LAKE-0401 | 24080401 | TRANSFORMER |  | 42043 | 1744 | 1185526 | 1387 | Distribution Circuit | Equipment Failure/Involved | Other | 37 | 33687 | Overcast;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011941 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | BERESFORD-0403 | 24040403 | OTHER |  | 42043 | 1814 | 1183727 | 716 | Distribution Circuit | Vegetation | Tree - fell into line | 625 | 46772 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0011719 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | CAROLANDS-0404 | 24060404 | FUSE |  | 42043 | 2200 | 1185226 | 869 | Distribution Circuit | Equipment Failure/Involved | Other | 64 | 55616 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011987 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
PENINSULA | Tier 2 | PACIFICA-1103 | 22811103 | RECLOSER |  | 42041 | 1229 | 1174920 | 917 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 13755 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010125 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 2 | CLARKSVILLE-2103 | 153612103 | OTHER |  | 42041 | 602 | 1173302 | 796 | Distribution Circuit | Vegetation | Tree - fell into line | 2001 | 244527 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009826 | OH | Sus | 31132929 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 42041 | 605 | 1173272 | 1825 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 31025 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010100 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 42041 | 1412 | 1176109 | 1528 | Distribution Circuit | Equipment Failure/Involved | Other | 58 | 88376 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on object | 15-0010458 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 42042 | 2050 | 1181895 | 910 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3640 | Rain;32 - 90 F | Conductor- Overhead | On Ground | 15-0011412 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | SWITCH |  | 42041 | 1542 | 1176263 | 3175 | Distribution Circuit | Vegetation | Tree - fell into line | 275 | 29718 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010649 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 42041 | 1222 | 1175368 | 1678 | Distribution Circuit | Vegetation | Tree - fell into line | 450 | 129316 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010365 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 42041 | 1631 | 1176562 | 1669 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5333 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010510 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 42041 | 637 | 1173384 | 324 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2916 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009919 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER |  | 42041 | 605 | 1173314 | 272 | Distribution Circuit | Equipment Failure/Involved | Other | 624 | 118178 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009821 | OH | Sus | 0 | 2015 | FEB | Yes |  | Yes
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 42041 | 1958 | 1178209 | 1352 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 202456 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011119 | OH | Sus | 0 | 2015 | FEB | Yes | Three Phase Fault | Yes
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 42042 | 213 | 1180346 | 846 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 32890 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011019 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE |  | 42041 | 747 | 1173489 | 486 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 486 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009898 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 42041 | 653 | 1173408 | 1033 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2066 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010083 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 42041 | 639 | 1173390 | 364 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 12375 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0009882 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | RECLOSER |  | 42041 | 1202 | 1174623 | 1121 | Distribution Circuit | Vegetation | Tree - fell into line | 880 | 375194 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0010334 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | RECLOSER |  | 42041 | 1250 | 1175132 | 1761 | Distribution Circuit | Vegetation | Tree - fell into line | 1219 | 635170 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010285 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | FUSE |  | 42042 | 1732 | 1181675 | 1243 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 1477 | Drizzle;32 - 90 F | Pole-Wood | Broken- wire on ground | 15-0011345 | OH | Sus | 0 | 2015 | FEB | Yes | Open Circuit | Yes
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 42041 | 1237 | 1175199 | 1463 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 24871 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010731 | OH | Sus | 42328531 | 2015 | FEB | Yes | Line to Line | Yes
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER |  | 42041 | 1230 | 1174902 | 1597 | Distribution Circuit | Vegetation | Tree - fell into line | 1202 | 532333 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 15-0010341 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE |  | 42041 | 1243 | 1175015 | 1861 | Distribution Circuit | Equipment Failure/Involved | Other | 14 | 26054 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011312 | OH | Sus | 0 | 2015 | FEB | Yes | Open Circuit | Yes
SIERRA | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE |  | 42041 | 1321 | 1175365 | 1529 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 131494 | Heavy rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010684 | OH | Sus | 0 | 2015 | FEB | Yes | Three Phase Fault | Yes
SIERRA | Tier 3 | DRUM-1101 | 152321101 | OCB |  | 42041 | 1353 | 1175581 | 1615 | Distribution Circuit | Vegetation | Tree - branch fell on line | 193 | 22175 | Clear;32 - 90 F | Crossarm- Wood | Broken- wire on object | 15-0010248 | OH | Sus | 0 | 2015 | FEB | Yes |  | Yes
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE |  | 42041 | 1227 | 1175745 | 2749 | Distribution Circuit | Vegetation | Tree - fell into line | 157 | 431593 | Strong winds;32 - 90 F | Crossarm- Wood | Broken- wire on ground | 15-0010527 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE |  | 42041 | 422 | 1173180 | 503 | Distribution Circuit | Vegetation | Tree - branch fell on line | 43 | 8509 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0009836 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | SWITCH |  | 42042 | 1614 | 1181653 | 1426 | Distribution Circuit | Equipment Failure/Involved | Other | 167 | 238142 | Overcast;32 - 90 F | Crossarm- Wood | Broken- wire on ground | 15-0011338 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE |  | 42041 | 1238 | 1179246 | 4381 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 198813 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011142 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 2 | SUMMIT-1101 | 152591101 | OCB |  | 42042 | 319 | 1180207 | 529 | Distribution Circuit | Vegetation | Tree - fell into line | 1036 | 502076 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011037 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 2 | COLUMBIA HILL-1101 | 152471101 | FUSE |  | 42041 | 1914 | 1177774 | 1327 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 49099 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011115 | OH | Sus | 31132899 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE |  | 42043 | 2007 | 1183975 | 938 | Distribution Circuit | Equipment Failure/Involved | Other | 3 | 2814 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011797 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | OTHER |  | 42041 | 952 | 1173968 | 3068 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 9420 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010035 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE |  | 42042 | 1232 | 1181149 | 1553 | Distribution Circuit | Equipment Failure/Involved | Other | 52 | 12620 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011227 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | OTHER |  | 42041 | 1231 | 1175866 | 2870 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 14350 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 15-0010297 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE |  | 42042 | 1351 | 1181589 | 1704 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5752 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 15-0011318 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE |  | 42041 | 1231 | 1176836 | 3219 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3219 | Strong winds;32 - 90 F | Pole-Wood | Broken- wire on ground | 15-0010485 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SIERRA | Tier 2 | ALLEGHANY-1101 | 152101101 | FUSE |  | 42042 | 709 | 1183003 | 2286 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 2286 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011604 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 42041 | 1227 | 1174830 | 368 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 2944 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010115 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE |  | 42041 | 1245 | 1175033 | 1030 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 18221 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010414 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | SWITCH |  | 42043 | 2127 | 1184674 | 875 | Distribution Circuit | Vegetation | Tree - branch fell on line | 78 | 36996 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011887 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE |  | 42041 | 1544 | 1176277 | 1452 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 15972 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010464 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | OTHER |  | 42041 | 1632 | 1176571 | 48 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 48 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on object | 15-0010439 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 2 | COTATI-1105 | 42271105 | FUSE |  | 42041 | 1601 | 1176374 | 485 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5820 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010559 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | SALMON CREEK-1101 | 43161101 | FUSE |  | 42041 | 1321 | 1175364 | 399 | Distribution Circuit | Equipment Failure/Involved | Other | 16 | 3121 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on object | 15-0010264 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE |  | 42041 | 1259 | 1175978 | 1988 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 25844 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010472 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | DUNBAR-1102 | 43071102 | FUSE |  | 42042 | 124 | 1179757 | 2093 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 23023 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0011266 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | FUSE |  | 42043 | 2115 | 1184510 | 1224 | Distribution Circuit | Vegetation | Tree - fell into line | 166 | 176994 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0011921 | OH | Sus | 0 | 2015 | FEB | Yes | Three Phase Fault | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 42041 | 1539 | 1176244 | 2886 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 37518 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010694 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 42041 | 2244 | 1181667 | 2358 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 14148 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011359 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 42041 | 2350 | 1178988 | 1007 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 55385 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on object | 15-0010802 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE |  | 42043 | 2059 | 1184157 | 893 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 14288 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011835 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE |  | 42043 | 2206 | 1184985 | 1106 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 12166 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0012083 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE |  | 42042 | 1600 | 1181494 | 1452 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 15972 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011300 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 42042 | 2202 | 1181943 | 143 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 1859 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on object | 15-0011400 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | FUSE |  | 42041 | 2131 | 1178755 | 1457 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 28193 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0010818 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 42042 | 415 | 1180005 | 748 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 10472 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0010948 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE |  | 42043 | 1656 | 1183291 | 279 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 279 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011744 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE |  | 42041 | 2107 | 1178547 | 1742 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 20904 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0010966 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 42041 | 1659 | 1176717 | 761 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 15220 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010655 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 42043 | 2054 | 1184128 | 1056 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 21120 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011867 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 42043 | 2128 | 1185394 | 802 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 17395 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011971 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 42041 | 1704 | 1176749 | 2685 | Distribution Circuit | Equipment Failure/Involved | Other | 11 | 29535 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010757 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 42041 | 2214 | 1179148 | 587 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 42851 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010852 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 42041 | 1600 | 1176515 | 2280 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 54720 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010647 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE |  | 42041 | 1700 | 1176792 | 514 | Distribution Circuit | Equipment Failure/Involved | Other | 133 | 41682 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010595 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE |  | 42041 | 1607 | 1176448 | 675 | Distribution Circuit | Vegetation | Tree - branch fell on line | 132 | 89100 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0010550 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | OTHER |  | 42041 | 1250 | 1175208 | 377 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 1885 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010163 | OH | Sus | 0 | 2015 | FEB | Yes | None | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 42043 | 2348 | 1185265 | 737 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 22847 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011976 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 42041 | 1440 | 1175912 | 2920 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 90520 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010448 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 42043 | 2354 | 1185274 | 1221 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 30525 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011952 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER |  | 42041 | 1214 | 1176051 | 1615 | Distribution Circuit | Vegetation | Tree - branch fell on line | 314 | 411978 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010357 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 42041 | 1844 | 1177691 | 766 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 91920 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010779 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 42041 | 2154 | 1179103 | 933 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 83970 | Strong winds;32 - 90 F | Conductor- Overhead | On Ground | 15-0010970 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE |  | 42041 | 1601 | 1176715 | 1684 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 69900 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010736 | OH | Sus | 0 | 2015 | FEB | Yes | Multi-Fault | Yes
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE |  | 42042 | 1038 | 1180965 | 1782 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 28512 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011245 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 42041 | 1725 | 1176885 | 99 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 297 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010497 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | FULTON-1107 | 42561107 | FUSE |  | 42041 | 1618 | 1176570 | 2903 | Distribution Circuit | Equipment Failure/Involved | Other | 33 | 16869 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010611 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 42042 | 1403 | 1181312 | 1663 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3326 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011246 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 42042 | 1859 | 1181810 | 1081 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 33511 | Drizzle;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011393 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 42042 | 1056 | 1181025 | 1804 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 30668 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011265 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 42043 | 2059 | 1184159 | 1096 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 31784 | Rain;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011938 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
SONOMA | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE |  | 42041 | 1742 | 1177023 | 2609 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 82103 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010861 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
SONOMA | Tier 2 | CLOVERDALE-1102 | 42821102 | FUSE |  | 42043 | 2124 | 1186201 | 802 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 17981 | Strong winds;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0012112 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
STOCKTON | Tier 2 | OLETA-1101 | 163541101 | FUSE |  | 42041 | 2214 | 1179141 | 1006 | Distribution Circuit | Equipment Failure/Involved | Other | 4 | 1540 | Partly cloudy;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0010828 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Line | Yes
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | OTHER |  | 42043 | 1425 | 1183027 | 1414 | Distribution Circuit | Vegetation | Tree - branch fell on line | 663 | 102749 | Lightning;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0011639 | OH | Sus | 0 | 2015 | FEB | Yes | Line to Ground | Yes
HUMBOLDT | Tier 2 | COVELO-1101 | 43061101 | FUSE |  | 42203 | 1859 | 1270312 | 411 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2466 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0048410 | OH | Sus | 0 | 2015 | JUL | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | OCEANO-1108 | 182601108 | FUSE |  | 42204 | 1354 | 1272537 | 946 | Distribution Circuit | Environmental/External | Lightning | 32 | 30272 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0048930 | OH | Sus | 0 | 2015 | JUL | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | PERRY 1101 | 183071101 | OTHER |  | 42204 | 735 | 1272189 | 1535 | Distribution Circuit | Environmental/External | Lightning | 96 | 97605 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0048751 | OH | Sus | 0 | 2015 | JUL | Yes | Open Circuit | Yes | No
NORTH COAST | Tier 2 | GUALALA 1112 | 42841112 | JUMPER |  | 42203 | 1700 | 1270334 | 894 | Distribution Circuit | Vegetation | Tree - fell into line | 250 | 51806 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0048394 | OH | Sus | 0 | 2015 | JUL | Yes | Three Phase Fault | Yes | No
NORTH COAST | Tier 2 | PHILO 1101 | 42601101 | FUSE |  | 42203 | 634 | 1269890 | 630 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3150 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0048331 | OH | Sus | 31170011 | 2015 | JUL | Yes | Line to Line | Yes | No
NORTH COAST | Tier 2 | KONOCTI 1102 | 43311102 | FUSE |  | 42203 | 139 | 1269867 | 531 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 23364 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 15-0048315 | OH | Sus | 31170009 | 2015 | JUL | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BANGOR 1101 | 103191101 | FUSE |  | 42203 | 1643 | 1270179 | 485 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 6305 | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 15-0048403 | OH | Sus | 31170289 | 2015 | JUL | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | UKIAH-1115 | 42771115 | FUSE |  | 42163 | 1123 | 1245614 | 196 | Distribution Circuit | 3rd Party | Vehicle | 128 | 17408 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0039293 | OH | Sus | 42401929 | 2015 | JUN | Yes | Line to Line | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 42163 | 2050 | 1246905 | 990 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 5347 | Clear;32 - 90 F | Pole-Wood | Broken- wire on ground | 15-0039553 | OH | Sus | 0 | 2015 | JUN | Yes | Line to Ground | Yes
NORTH BAY | Tier 2 | PUEBLO-1105 | 43291105 | FUSE |  | 42163 | 1000 | 1245524 | 229 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 794 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0039246 | OH | Sus | 42401796 | 2015 | JUN | Yes | Line to Ground | Yes
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 42163 | 2017 | 1246807 | 895 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 40275 | Clear;32 - 90 F | Conductor- Overhead | Broken- wire on ground | 15-0039527 | OH | Sus | 0 | 2015 | JUN | Yes | Line to Ground | Yes
STOCKTON | Tier 2 | CORRAL-1101 | 162991101 | RECLOSER |  | 42163 | 1418 | 1245781 | 337 | Distribution Circuit | 3rd Party | Vehicle | 314 | 65168 | Clear;Above 90 F | Pole-Wood | Broken- wire on ground | 15-0039368 | OH | Sus | 31159870 | 2015 | JUN | Yes | Line to Ground | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND 0401 | 83040401 | JUMPER |  | 42295 | 49 | 1324491 | 508 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 3048 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 15-0071472 | OH | Sus | 0 | 2015 | OCT | Yes | None | Yes | No
LOS PADRES | Tier 2 | OCEANO 1104 | 182601104 | RECLOSER |  | 42295 | 2159 | 1325661 | 291 | Distribution Circuit | Equipment Failure/Involved | Overhead | 819 | 155970 | Overcast;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 15-0071600 | OH | Sus | 42521324 | 2015 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | JUMPER |  | 42417 | 1427 | 1405459 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1635 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013271 | OH | Sus | 0 | 2016 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 42417 | 1638 | 1405933 | 737 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1474 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013302 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | JUMPER |  | 42417 | 1942 | 1407599 | 828 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 828 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013489 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE |  | 42417 | 1950 | 1406650 | 1327 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 9289 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013773 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER |  | 42417 | 2129 | 1407539 | 1006 | Distribution Circuit | Vegetation | Tree - branch fell on line | 129 | 111744 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013647 | OH | Sus | 42632627 | 2016 | FEB | Yes | Open Circuit | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 42417 | 1612 | 1405976 | 633 | Distribution Circuit | Vegetation | Tree - fell into line | 337 | 135477 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013277 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 42417 | 2137 | 1407390 | 1838 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1838 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013459 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE |  | 42417 | 1909 | 1406369 | 1157 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2314 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 16-0013596 | OH | Sus | 42632627 | 2016 | FEB | Yes | None | Yes | No
DE ANZA | Tier 2 | SARATOGA 1104 | 83371104 | FUSE |  | 42417 | 1552 | 1405667 | 652 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 4564 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013316 | OH | Sus | 42632627 | 2016 | FEB | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | JUMPER |  | 42417 | 1757 | 1406157 | 663 | Distribution Circuit | Vegetation | Tree - bark fell into line | 117 | 32864 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013324 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | Yes
EAST BAY | Tier 3 | OAKLAND K-1102 | 12101102 | FUSE |  | 42417 | 2151 | 1407396 | 634 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 19107 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013482 | OH | Sus | 31219888 | 2016 | FEB | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | MENDOCINO-1101 | 42951101 | FUSE |  | 42417 | 841 | 1404619 | 155 | Distribution Circuit | Animal | Bird found | 134 | 20770 | Strong Winds-Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0012987 | OH | Sus | 42632252 | 2016 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | GOLDTREE 1107 | 182581107 | OCB |  | 42417 | 2242 | 1407584 | 364 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 9169 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013484 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER |  | 42417 | 2054 | 1407205 | 557 | Distribution Circuit | Vegetation | Tree - fell into line | 355 | 197735 | Snow-Overcast;Below 32 F | Conductor- Overhead | Broken- wire on ground | 16-0013446 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 42417 | 2015 | 1407847 | 1378 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2756 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013615 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS 2110 | 153652110 | FUSE |  | 42417 | 1957 | 1406788 | 1201 | Distribution Circuit | Vegetation | Tree - fell into line | 258 | 119826 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013524 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 42417 | 2015 | 1407534 | 1284 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 32100 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013396 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 42417 | 1955 | 1407634 | 1508 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 24128 | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013521 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 42417 | 1949 | 1406645 | 1336 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 131360 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013669 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS 1107 | 152261107 | FUSE |  | 42417 | 2027 | 1407069 | 1753 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 20485 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 16-0013566 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1111 | 153081111 | JUMPER |  | 42417 | 1910 | 1406951 | 921 | Distribution Circuit | Equipment Failure/Involved | Overhead | 80 | 17295 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013392 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE |  | 42417 | 1952 | 1408518 | 2741 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 16446 | Partly Cloudy-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013867 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 42417 | 2041 | 1407581 | 1385 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 34625 | Overcast-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 16-0013786 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | RECLOSER |  | 42417 | 1959 | 1406901 | 1322 | Distribution Circuit | Vegetation | Tree - fell into line | 3294 | 1569268 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 16-0013390 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH 2102 | 152762102 | FUSE |  | 42417 | 731 | 1404530 | 663 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 29835 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013111 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 42417 | 2111 | 1407292 | 1507 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 19378 | Partly Cloudy-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013605 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 42417 | 738 | 1404550 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 5140 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013097 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 42417 | 1944 | 1406632 | 525 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 67725 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013561 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 42417 | 731 | 1404541 | 618 | Distribution Circuit | Vegetation | Tree - fell into line | 1015 | 161119 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0012964 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 42417 | 1956 | 1406733 | 876 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 55382 | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013499 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | AUBURN 1102 | 152161102 | FUSE |  | 42417 | 2059 | 1407233 | 255 | Distribution Circuit | Vegetation | Tree - fell into line | 185 | 47175 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013475 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 42417 | 2006 | 1407048 | 1058 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 165496 | Partly Cloudy-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 16-0013479 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE |  | 42417 | 725 | 1404730 | 414 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3726 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0012962 | OH | Sus | 0 | 2016 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE |  | 42417 | 725 | 1404729 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5382 | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 16-0012962 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 42417 | 944 | 1404585 | 269 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 13450 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013009 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | JUMPER |  | 42417 | 1301 | 1405446 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 2540 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013188 | OH | Sus | 31219754 | 2016 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER |  | 42417 | 749 | 1404658 | 443 | Distribution Circuit | Vegetation | Tree - fell into line | 203 | 36514 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0012990 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | ELECTRA-1102 | 162161102 | RECLOSER |  | 42417 | 1950 | 1406653 | 1189 | Distribution Circuit | Vegetation | Tree - fell into line | 204 | 120837 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013480 | OH | Sus | 0 | 2016 | FEB | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | ELECTRA-1102 | 162161102 | RECLOSER |  | 42417 | 1813 | 1406173 | 717 | Distribution Circuit | Vegetation | Tree - fell into line | 209 | 46864 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013358 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | FUSE |  | 42417 | 1949 | 1406647 | 950 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 50350 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013512 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | JUMPER |  | 42417 | 1906 | 1407515 | 504 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 10236 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013472 | OH | Sus | 0 | 2016 | FEB | Yes | Open Circuit | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE |  | 42417 | 1510 | 1405530 | 384 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 7716 | Strong Winds-Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 16-0013219 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 42417 | 952 | 1404747 | 372 | Distribution Circuit | Vegetation | Tree - branch fell on line | 123 | 6386 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013041 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER |  | 42417 | 2009 | 1406999 | 1529 | Distribution Circuit | Vegetation | Tree - fell into line | 157 | 143966 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 16-0013527 | OH | Sus | 0 | 2016 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 42417 | 2032 | 1407085 | 501 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 15777 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013478 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | Yes
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE |  | 42417 | 1940 | 1406627 | 402 | Distribution Circuit | Vegetation | Tree - branch fell on line | 251 | 100902 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013458 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | FUSE |  | 42417 | 1941 | 1406828 | 880 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 8800 | Overcast-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 16-0013585 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | CURTIS 1704 | 163351704 | FUSE |  | 42417 | 1710 | 1405975 | 794 | Distribution Circuit | Vegetation | Tree - fell into line | 145 | 104216 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 16-0013320 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | RACETRACK 1703 | 163761703 | FUSE |  | 42417 | 1905 | 1406346 | 425 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 9160 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0013398 | OH | Sus | 0 | 2016 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE |  | 42434 | 1753 | 1420877 | 1174 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 18886 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | On Ground | 16-0018103 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 42434 | 2157 | 1419887 | 973 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 8757 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018197 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 42434 | 1646 | 1417459 | 1329 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 19935 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 16-0017667 | OH | Sus | 0 | 2016 | MAR | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE |  | 42434 | 2142 | 1417491 | 548 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 21920 | Overcast-Rain;32-90 F | Conductor- Overhead | On Ground | 16-0018040 | OH | Sus | 0 | 2016 | MAR | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | OCB |  | 42434 | 2102 | 1419375 | 1071 | Distribution Circuit | Vegetation | Tree - fell into line | 6887 | 631240 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017873 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE |  | 42434 | 1628 | 1417245 | 552 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 21176 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017602 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER |  | 42434 | 1616 | 1417182 | 805 | Distribution Circuit | Vegetation | Tree - fell into line | 429 | 71579 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017557 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 42434 | 2058 | 1420902 | 1900 | Distribution Circuit | Vegetation | Tree - fell into line | 265 | 370817 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018136 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 42434 | 2045 | 1419193 | 1521 | Distribution Circuit | Vegetation | Tree - fell into line | 136 | 173554 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017828 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 42434 | 2049 | s1189817 | 246 | Distribution Circuit | Equipment Failure/Involved | Overhead | 808 | 138399 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 16-0017955 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42434 | 731 | 1416317 | 714 | Distribution Circuit | Equipment Failure/Involved | Overhead | 317 | 42327 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 16-0017396 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42434 | 1313 | 1416660 | 426 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2130 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017496 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 42434 | 1544 | 1416983 | 666 | Distribution Circuit | Vegetation | Tree - fell into line | 3432 | 251938 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017537 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 42434 | 2049 | 1419389 | 1468 | Distribution Circuit | Vegetation | Tree - branch fell on line | 184 | 172095 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | On Ground | 16-0017987 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE |  | 42434 | 2106 | 1423823 | 2609 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 5218 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018853 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER |  | 42434 | 1721 | 1421565 | 1374 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5496 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018345 | OH | Sus | 0 | 2016 | MAR | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42434 | 1157 | 1416594 | 339 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 5424 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017465 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42434 | 1830 | 1418135 | 436 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3052 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | On Ground | 16-0018037 | OH | Sus | 0 | 2016 | MAR | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42434 | 1632 | 1418034 | 705 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 60572 | Clear;32-90 F | Conductor- Overhead | On Ground | 16-0017695 | OH | Sus | 0 | 2016 | MAR | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42434 | 1740 | 1421282 | 2843 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 56860 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018413 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 42434 | 1930 | 1418526 | 250 | Distribution Circuit | Vegetation | Tree - branch fell on line | 90 | 22500 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017965 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 42434 | 1556 | 1417015 | 322 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 15080 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017628 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 42434 | 1933 | 1418557 | 1172 | Distribution Circuit | Vegetation | Tree - fell into line | 174 | 188631 | Overcast-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 16-0018051 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 42434 | 1641 | 1417392 | 903 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 18060 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018033 | OH | Sus | 0 | 2016 | MAR | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 42434 | 2246 | 1421125 | 1055 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 14770 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018246 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 42434 | 1644 | 1417445 | 850 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 20206 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017976 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 42434 | 1727 | 1419060 | 1390 | Distribution Circuit | Equipment Failure/Involved | Overhead | 716 | 339716 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017809 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 42434 | 1347 | 1416718 | 1151 | Distribution Circuit | Vegetation | Tree - fell into line | 789 | 117853 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 16-0017487 | OH | Sus | 31222889 | 2016 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 42434 | 1810 | 1418995 | 759 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 5184 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017815 | OH | Sus | 42646371 | 2016 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 42434 | 1124 | 1416563 | 656 | Distribution Circuit | Vegetation | Tree - fell into line | 612 | 34496 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017451 | OH | Sus | 0 | 2016 | MAR | Yes | Multi-Fault | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 42434 | 1624 | 1417274 | 2291 | Distribution Circuit | Vegetation | Tree - fell into line | 328 | 185751 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017573 | OH | Sus | 31222889 | 2016 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | STELLING-1110 | 83481110 | JUMPER |  | 42434 | 2229 | 1420792 | 2916 | Distribution Circuit | Equipment Failure/Involved | Overhead | 171 | 227228 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018071 | OH | Sus | 42646371 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 2 | STELLING-1110 | 83481110 | FUSE |  | 42434 | 1839 | 1418253 | 1211 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 70238 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017840 | OH | Sus | 42646371 | 2016 | MAR | Yes | Line to Ground | Yes | No
DIABLO | Tier 3 | MORAGA-1101 | 13801101 | FUSE |  | 42434 | 1631 | 1417302 | 653 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 43206 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017600 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
DIABLO | Tier 2 | MORAGA-1104 | 13801104 | TRANSFORMER |  | 42434 | 1435 | 1416785 | 476 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1428 | Overcast-Drizzle;32-90 F | Transformer | Broken- wire on ground | 16-0017569 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
DIABLO | Tier 3 | MORAGA-1101 | 13801101 | JUMPER |  | 42434 | 1931 | 1418518 | 745 | Distribution Circuit | Vegetation | Tree - fell into line | 220 | 144349 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018145 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
DIABLO | Tier 2 | SOBRANTE-1102 | 14671102 | FUSE |  | 42434 | 2059 | 1419310 | 442 | Distribution Circuit | Vegetation | Tree - branch fell on line | 77 | 34034 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018036 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | SAN LEANDRO U 1109 | 13111109 | RECLOSER |  | 42434 | 2100 | 1419339 | 840 | Distribution Circuit | Vegetation | Tree - fell into line | 419 | 83790 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017860 | OH | Sus | 31222882 | 2016 | MAR | Yes | Multi-Fault | Yes | No
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | FUSE |  | 42434 | 2259 | 1420616 | 818 | Distribution Circuit | Vegetation | Tree - fell into line | 233 | 51016 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018093 | OH | Sus | 31222882 | 2016 | MAR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | JUMPER |  | 42434 | 2058 | 1419340 | 474 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 29762 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018006 | OH | Sus | 31222882 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
FRESNO | Tier 2 | AUBERRY-1101 | 254151101 | FUSE |  | 42434 | 2022 | 1418915 | 459 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2295 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017870 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | SWITCH |  | 42434 | 1831 | 1418141 | 864 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 40608 | Partly Cloudy-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017977 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42434 | 1636 | 1417367 | 418 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 28842 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017657 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | CALPELLA-1101 | 43411101 | FUSE |  | 42434 | 1708 | 1417544 | 640 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6400 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 16-0017610 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42434 | 1748 | 1417769 | 852 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 20956 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017769 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42434 | 1752 | 1417862 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 19175 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017717 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42434 | 1550 | 1417010 | 250 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 7500 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017626 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | OTHER |  | 42434 | 1811 | 1417980 | 581 | Distribution Circuit | Vegetation | Tree - branch fell on line | 131 | 56128 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017818 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER |  | 42434 | 638 | 1416467 | 1140 | Distribution Circuit | Vegetation | Tree - fell into line | 439 | 187153 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017426 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | JUMPER |  | 42434 | 1528 | 1416920 | 690 | Distribution Circuit | Vegetation | Tree - fell into line | 372 | 177661 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017558 | OH | Sus | 0 | 2016 | MAR | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | OTHER |  | 42434 | 1625 | 1417218 | 487 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2642 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017702 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 42434 | 1612 | 1417127 | 467 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 934 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017678 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | Yes
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | FUSE |  | 42434 | 1410 | 1421227 | 1577 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 11039 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018474 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER |  | 42434 | 1942 | 1418672 | 1200 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1934 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017757 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER |  | 42434 | 1410 | 1416493 | 922 | Distribution Circuit | Vegetation | Tree - fell into line | 327 | 286241 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 16-0017549 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | JUMPER |  | 42434 | 1811 | 1418018 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 23408 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017789 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER 1101 | 192381101 | FUSE |  | 42434 | 1559 | 1417041 | 317 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 4353 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017648 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
LOS PADRES | Tier 2 | TEMPLETON-2111 | 183052111 | RECLOSER |  | 42434 | 2310 | 1420581 | 800 | Distribution Circuit | Vegetation | Tree - fell into line | 959 | 131092 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018035 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | CAYUCOS 1101 | 182551101 | FUSE |  | 42434 | 2337 | 1420675 | 425 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 10200 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 16-0018118 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE |  | 42434 | 2008 | 1418779 | 1387 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 66576 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on object | 16-0018041 | OH | Sus | 0 | 2016 | MAR | Yes | Three Phase Fault | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | JUMPER |  | 42434 | 1736 | 1417941 | 635 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1297 | 195739 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 16-0017642 | OH | Sus | 0 | 2016 | MAR | Yes | Open Circuit | Yes | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE |  | 42434 | 2012 | 1418810 | 935 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 15895 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017902 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | WOODACRE-1102 | 43021102 | JUMPER |  | 42434 | 2038 | 1419315 | 1217 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 17038 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 16-0018236 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | OCB |  | 42434 | 2051 | 1419222 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 1211 | 71100 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017833 | OH | Sus | 0 | 2016 | MAR | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 42434 | 1045 | 1416501 | 648 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 16601 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017457 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | OTHER |  | 42434 | 2304 | 1420950 | 1793 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 16418 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018142 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 42434 | 1729 | 1417663 | 481 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2886 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017956 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 42434 | 1449 | 1416818 | 821 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 9031 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 16-0017530 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 42434 | 2205 | 1420745 | 1136 | Distribution Circuit | Vegetation | Tree - fell into line | 191 | 112494 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018138 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | PUEBLO 1105 | 43291105 | FUSE |  | 42434 | 1453 | 1417281 | 322 | Distribution Circuit | Vegetation | Tree - fell into line | 161 | 46642 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017566 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 42434 | 1831 | 1418159 | 1441 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 138380 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 16-0018152 | OH | Sus | 0 | 2016 | MAR | Yes | Three Phase Fault | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | OTHER |  | 42434 | 2125 | 1421101 | 1039 | Distribution Circuit | Equipment Failure/Involved | Overhead | 528 | 471460 | Overcast-Fog-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018237 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | BANGOR-1101 | 103191101 | RECLOSER |  | 42434 | 2219 | 1420171 | 2464 | Distribution Circuit | Vegetation | Tree - fell into line | 426 | 131385 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018147 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1109 | 102911109 | SWITCH |  | 42434 | 2119 | 1420604 | 376 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 32712 | Partly Cloudy-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018025 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER |  | 42434 | 1923 | 1418475 | 354 | Distribution Circuit | Vegetation | Tree - fell into line | 198 | 54878 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017808 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1107 | 102911107 | FUSE |  | 42434 | 2037 | 1419076 | 285 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 9405 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017865 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | JUMPER |  | 42434 | 2211 | 1422568 | 1389 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 9723 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018537 | OH | Sus | 0 | 2016 | MAR | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1104 | 102831104 | FUSE |  | 42434 | 2156 | 1419848 | 579 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 6948 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018169 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1104 | 102831104 | FUSE |  | 42434 | 1812 | 1417976 | 498 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 10458 | Strong Winds-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017771 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1105 | 102831105 | JUMPER |  | 42434 | 2146 | 1420623 | 324 | Distribution Circuit | Vegetation | Tree - fell into line | 1291 | 93786 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 16-0018010 | OH | Sus | 0 | 2016 | MAR | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 3 | ORO FINO 1102 | 103031102 | RECLOSER |  | 42434 | 1741 | 1417726 | 166 | Distribution Circuit | Vegetation | Tree - fell into line | 997 | 147826 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017617 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE |  | 42434 | 1727 | 1417653 | 1052 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 28846 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 16-0017656 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | BUCKS CREEK 1101 | 102211101 | RECLOSER |  | 42434 | 2343 | 1420831 | 2625 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 60741 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018442 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER |  | 42434 | 2132 | 1419627 | 138 | Distribution Circuit | Vegetation | Tree - fell into line | 316 | 43608 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017617 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | RED BLUFF-1103 | 103541103 | RECLOSER |  | 42434 | 2101 | 1419432 | 191 | Distribution Circuit | Equipment Failure/Involved | Overhead | 221 | 42211 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017941 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | RED BLUFF 1101 | 103541101 | FUSE |  | 42434 | 1820 | 1418086 | 196 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 12788 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017720 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | JUMPER |  | 42434 | 1807 | 1417935 | 1926 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 15408 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017805 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER |  | 42434 | 2021 | 1418987 | 1401 | Distribution Circuit | Vegetation | Tree - fell into line | 240 | 84830 | Overcast-Fog-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 16-0017879 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1101 | 103381101 | FUSE |  | 42434 | 1755 | 1417821 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 13625 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017773 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | FUSE |  | 42434 | 1746 | 1417752 | 1319 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 14509 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017920 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER |  | 42434 | 1614 | 1417174 | 1256 | Distribution Circuit | Vegetation | Tree - branch fell on line | 153 | 189248 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 16-0018045 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER |  | 42434 | 2101 | 1419333 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 9225 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018008 | OH | Sus | 0 | 2016 | MAR | Yes | Open Circuit | Yes | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 42434 | 1610 | 1417315 | 717 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 25095 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017669 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 42434 | 1627 | 1417226 | 1240 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1240 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017753 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1104 | 24251104 | FUSE |  | 42434 | 1627 | 1417227 | 381 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 6096 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017826 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 42434 | 1751 | 1417798 | 424 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 12904 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017983 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER |  | 42434 | 2042 | 1419150 | 207 | Distribution Circuit | Vegetation | Tree - fell into line | 602 | 45367 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017820 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | FUSE |  | 42434 | 1719 | 1417619 | 316 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 6952 | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017621 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE |  | 42434 | 2102 | 1419429 | 809 | Distribution Circuit | Vegetation | Tree - branch fell on line | 298 | 224099 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017988 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 42434 | 2150 | 1419747 | 1005 | Distribution Circuit | Vegetation | Tree - fell into line | 262 | 263310 | Strong Winds-Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018360 | OH | Sus | 0 | 2016 | MAR | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE |  | 42434 | 2119 | 1421530 | 2296 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 34188 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018433 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1105 | 152481105 | FUSE |  | 42434 | 2014 | 1418826 | 1157 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 34710 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017839 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE |  | 42434 | 2245 | 1421177 | 1198 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 23960 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018340 | OH | Sus | 31223007 | 2016 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL 1101 | 152471101 | FUSE |  | 42434 | 2237 | 1421366 | 2538 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 51774 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018400 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | JUMPER |  | 42434 | 2237 | 1422204 | 2543 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2543 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018459 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | RECLOSER |  | 42434 | 2157 | 1421605 | 2481 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 154286 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 16-0018350 | OH | Sus | 31223007 | 2016 | MAR | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | FUSE |  | 42434 | 1841 | 1418200 | 291 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 4901 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017842 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 42434 | 1909 | 1418337 | 1393 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 11144 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017810 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 42434 | 1704 | 1417545 | 525 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 18900 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017743 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 42434 | 1759 | 1417948 | 632 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 69520 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017746 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER |  | 42434 | 1823 | 1418145 | 314 | Distribution Circuit | Vegetation | Tree - branch fell on line | 515 | 100456 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017683 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE |  | 42434 | 1557 | 1417038 | 1419 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 82053 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017578 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER |  | 42434 | 1618 | 1417447 | 621 | Distribution Circuit | Equipment Failure/Involved | Overhead | 229 | 135141 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017625 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | CLOVERDALE-1102 | 42821102 | RECLOSER |  | 42434 | 2214 | 1420157 | 447 | Distribution Circuit | Vegetation | Tree - fell into line | 590 | 83569 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017975 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | RECLOSER |  | 42434 | 2209 | 1420144 | 832 | Distribution Circuit | Vegetation | Tree - fell into line | 620 | 222586 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017953 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | FUSE |  | 42434 | 2222 | 1421239 | 1101 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 14313 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018279 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CLAY-1101 | 163341101 | FUSE |  | 42434 | 2034 | 1419051 | 1275 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 20100 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 16-0018160 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE 1101 | 163751101 | RECLOSER |  | 42434 | 2157 | 1419908 | 550 | Distribution Circuit | Vegetation | Tree - fell into line | 683 | 147306 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0018028 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | OLETA-1101 | 163541101 | FUSE |  | 42434 | 2052 | 1419210 | 483 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 13971 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0017895 | OH | Sus | 0 | 2016 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 42657 | 1515 | 1559890 | 195 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 975 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0072262 | OH | Sus | 0 | 2016 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 42657 | 1805 | 1560193 | 680 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 15640 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0072307 | OH | Sus | 0 | 2016 | OCT | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER |  | 42657 | 335 | 1558105 | 751 | Distribution Circuit | Vegetation | Tree - fell into line | 442 | 35593 | Clear;32-90 F | Conductor- Overhead | On Ground | 16-0071846 | OH | Sus | 0 | 2016 | OCT | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 42657 | 828 | 1558710 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6220 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0072089 | OH | Sus | 0 | 2016 | OCT | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE |  | 42657 | 2312 | 1560488 | 868 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 15932 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0072393 | OH | Sus | 42815227 | 2016 | OCT | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE |  | 42657 | 1113 | 1559350 | 400 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2800 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0072159 | OH | Sus | 0 | 2016 | OCT | Yes | Three Phase Fault | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE |  | 42657 | 1102 | 1559009 | 299 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 7375 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0072063 | OH | Sus | 0 | 2016 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | SILVERADO-2102 | 43432102 | SWITCH |  | 42657 | 1024 | 1559279 | 775 | Distribution Circuit | Equipment Failure/Involved | Overhead | 354 | 258709 | Overcast-Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 16-0072113 | OH | Sus | 0 | 2016 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | CALISTOGA-1102 | 42711102 | OCB |  | 42657 | 2357 | 1560534 | 297 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2112 | 151605 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0072389 | OH | Sus | 0 | 2016 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | RECLOSER |  | 42657 | 132 | 1558011 | 826 | Distribution Circuit | Vegetation | Tree - fell into line | 540 | 213622 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 16-0071832 | OH | Sus | 0 | 2016 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1102 | 102541102 | FUSE |  | 42657 | 432 | 1558437 | 779 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 38950 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 16-0071897 | OH | Sus | 0 | 2016 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 42657 | 705 | 1558419 | 580 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6960 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 16-0071922 | OH | Sus | 0 | 2016 | OCT | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 42832 | 49 | 1749516 | 838 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 34358 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 17-0037604 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE |  | 42832 | 223 | 1747995 | 677 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 12186 | Overcast-Fog-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037521 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | OTHER |  | 42832 | 628 | 1750338 | 546 | Distribution Circuit | Vegetation | Tree - branch fell on line | 198 | 59160 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037796 | OH | Sus | 42984159 | 2017 | APR | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 42832 | 303 | 1749043 | 711 | Distribution Circuit | Vegetation | Tree - branch fell on line | 326 | 79963 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037547 | OH | Sus | 42984110 | 2017 | APR | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42832 | 1604 | 1751262 | 1636 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 93252 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0038119 | OH | Sus | 42984110 | 2017 | APR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42832 | 1538 | 1751184 | 1425 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 28500 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 17-0038071 | OH | Sus | 31316813 | 2017 | APR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 42832 | 447 | 1749433 | 1980 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 50340 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037586 | OH | Sus | 42984110 | 2017 | APR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 42831 | 2018 | 1751187 | 4365 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 21825 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0038433 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | CLAYTON-2212 | 12022212 | FUSE |  | 42831 | 2043 | 1747043 | 2780 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 11120 | Overcast-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0037948 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | SAN LEANDRO-1109 | 13111109 | RECLOSER |  | 42832 | 114 | 1749128 | 1064 | Distribution Circuit | Equipment Failure/Involved | Overhead | 420 | 300305 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037629 | OH | Sus | 0 | 2017 | APR | Yes | Three Phase Fault | Yes | No
EAST BAY | Tier 2 | OAKLAND X-1106 | 12541106 | SWITCH |  | 42832 | 623 | 1749549 | 796 | Distribution Circuit | Equipment Failure/Involved | Overhead | 204 | 29614 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037609 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | OTHER |  | 42831 | 2025 | 1747442 | 505 | Distribution Circuit | Vegetation | Tree - branch fell on line | 154 | 67942 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037583 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | FUSE |  | 42831 | 2327 | 1748783 | 1873 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 91176 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0038059 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAKLAND K-1104 | 12101104 | RECLOSER |  | 42831 | 2131 | 1747837 | 1084 | Distribution Circuit | Equipment Failure/Involved | Overhead | 417 | 97411 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037451 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | BERKELEY F-1103 | 12061103 | FUSE |  | 42831 | 2052 | 1746827 | 1725 | Distribution Circuit | Vegetation | Tree - fell into line | 1931 | 22619 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037714 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 2 | FRANKLIN-1104 | 13921104 | OTHER |  | 42831 | 2113 | 1749290 | 837 | Distribution Circuit | Equipment Failure/Involved | Overhead | 82 | 67233 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037545 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | Yes
FRESNO | Tier 3 | AUBERRY-1101 | 254151101 | JUMPER |  | 42832 | 542 | 1749536 | 453 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1812 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037721 | OH | Sus | 0 | 2017 | APR | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | OTHER |  | 42832 | 1423 | 1751068 | 2802 | Distribution Circuit | Vegetation | Tree - fell into line | 2452 | 132368 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037967 | OH | Sus | 0 | 2017 | APR | Yes | Open Circuit | Yes | Yes
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | OTHER |  | 42831 | 2013 | 1748482 | 1090 | Distribution Circuit | Vegetation | Tree - fell into line | 1039 | 975240 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037421 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 42831 | 2043 | 1747039 | 2393 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 38288 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037463 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | RECLOSER |  | 42831 | 1725 | 1745838 | 2964 | Distribution Circuit | Vegetation | Tree - fell into line | 624 | 166036 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037246 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE |  | 42831 | 1244 | 1745500 | 257 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 771 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037181 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | TRIP-SAVER |  | 42831 | 2101 | 1747398 | 851 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 82547 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037415 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | FUSE |  | 42831 | 2204 | 1748190 | 1006 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 39234 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037481 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42831 | 1924 | 1746221 | 2544 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 15264 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037728 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 42871101 | RECLOSER |  | 42832 | 1903 | 1751575 | 888 | Distribution Circuit | Vegetation | Tree - fell into line | 291 | 127434 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0038106 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42831 | 2029 | 1746809 | 1055 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 31650 | Partly Cloudy-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037495 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42831 | 1833 | 1745940 | 2472 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 12360 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037472 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42831 | 1910 | 1746107 | 1310 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 15720 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037475 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42831 | 1931 | 1751113 | 1364 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 13640 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037983 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | OTHER |  | 42831 | 1934 | 1747547 | 1197 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 129435 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037311 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42832 | 1407 | 1750166 | 208 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 2704 | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0037941 | OH | Sus | 0 | 2017 | APR | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42831 | 1847 | 1746093 | 1437 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 30177 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037320 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | JUMPER |  | 42831 | 1914 | 1749127 | 1476 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1476 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037500 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 42831 | 2109 | 1747443 | 1131 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 19227 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037441 | OH | Sus | 0 | 2017 | APR | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER |  | 42831 | 2056 | 1747345 | 1333 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 57121 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037342 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 42831 | 1543 | 1745780 | 555 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 32745 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0037203 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE |  | 42831 | 1829 | 1745935 | 1444 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 8287 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037272 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 42831 | 2132 | 1747803 | 1279 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2543 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037531 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 42831 | 2306 | 1748639 | 2524 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 25240 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037511 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 42831 | 25 | 1745025 | 278 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 556 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0036882 | OH | Sus | 42984508 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 42831 | 1902 | 1746177 | 2734 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 78664 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037309 | OH | Sus | 0 | 2017 | APR | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE |  | 42832 | 743 | 1749889 | 1832 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7328 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0038023 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 42846 | 1424 | 1764233 | 759 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3795 | Clear;32-90 F | Conductor- Overhead | On Ground | 17-0042022 | OH | Sus | 42999178 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER |  | 42831 | 137 | 1745074 | 516 | Distribution Circuit | Vegetation | Tree - fell into line | 223 | 114508 | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0036890 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER |  | 42831 | 256 | 1745167 | 2511 | Distribution Circuit | Vegetation | Tree - fell into line | 304 | 104424 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0036905 | OH | Sus | 0 | 2017 | APR | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE |  | 42831 | 540 | 1745261 | 1760 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 12320 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037112 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE |  | 42832 | 17 | 1748995 | 938 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 22512 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037706 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | MAPLE CREEK-1101 | 192101101 | FUSE |  | 42831 | 924 | 1745327 | 656 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 656 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037077 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | RECLOSER |  | 42831 | 147 | 1745114 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 8806 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0036900 | OH | Sus | 0 | 2017 | APR | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | HARRIS-1109 | 192431109 | FUSE |  | 42831 | 231 | 1745200 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 7710 | Strong Winds-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0036920 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 42831 | 1334 | 1745565 | 356 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 60520 | Strong Winds-Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037151 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 42832 | 717 | 1749779 | 1847 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4145 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037815 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE |  | 42832 | 1729 | 1751417 | 1229 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 13519 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 17-0038104 | OH | Sus | 31318406 | 2017 | APR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | BOLINAS-1101 | 42261101 | OTHER |  | 42831 | 1923 | 1746312 | 1682 | Distribution Circuit | Equipment Failure/Involved | Overhead | 477 | 799044 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037454 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | SAN RAFAEL-1107 | 42011107 | FUSE |  | 42832 | 1036 | 1750502 | 665 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 26600 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0037800 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | RECLOSER |  | 42831 | 1058 | 1745410 | 844 | Distribution Circuit | Vegetation | Tree - fell into line | 544 | 166949 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037052 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | MONTICELLO-1101 | 43051101 | OTHER |  | 42832 | 723 | 1751153 | 3107 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 8804 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037995 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | PUEBLO-1105 | 43291105 | OTHER |  | 42831 | 1940 | 1750156 | 1345 | Distribution Circuit | Equipment Failure/Involved | Overhead | 211 | 219306 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037692 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 42831 | 2229 | 1748349 | 1361 | Distribution Circuit | Equipment Failure/Involved | Overhead | 266 | 50506 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037447 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 42832 | 2334 | 1752201 | 1053 | Distribution Circuit | Equipment Failure/Involved | Overhead | 266 | 57355 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0038178 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 42832 | 207 | 1749185 | 1963 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 111644 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037727 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE |  | 42832 | 1754 | 1751460 | 2762 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 24858 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0038061 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER |  | 42831 | 2304 | 1748789 | 1365 | Distribution Circuit | Vegetation | Tree - fell into line | 425 | 330489 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0037632 | OH | Sus | 0 | 2017 | APR | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | FUSE |  | 42832 | 1900 | 1751570 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3360 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0038086 | OH | Sus | 0 | 2017 | APR | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE |  | 42832 | 857 | 1750170 | 523 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 12029 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037693 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE |  | 42832 | 19 | 1749374 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4112 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037572 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1103 | 102831103 | RECLOSER |  | 42832 | 1220 | 1750770 | 506 | Distribution Circuit | Vegetation | Tree - fell into line | 769 | 79028 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037908 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1103 | 102831103 | FUSE |  | 42832 | 11 | 1748900 | 514 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1542 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037522 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | PARADISE-1103 | 102831103 | FUSE |  | 42831 | 2224 | 1748319 | 699 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 19799 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037563 | OH | Sus | 0 | 2017 | APR | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1103 | 102831103 | FUSE |  | 42832 | 148 | 1749167 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 19312 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037584 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CENTERVILLE-1101 | 102021101 | TRIP-SAVER |  | 42831 | 2224 | 1748364 | 679 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 25918 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037564 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1101 | 102931101 | FUSE |  | 42832 | 201 | 1749183 | 494 | Distribution Circuit | Vegetation | Tree - branch fell on line | 85 | 9928 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037544 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1102 | 103441102 | RECLOSER |  | 42831 | 2303 | 1748675 | 345 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1408 | 150746 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037446 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | RECLOSER |  | 42831 | 1939 | 1748111 | 1358 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 74690 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037356 | OH | Sus | 0 | 2017 | APR | Yes | Force Out | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER |  | 42831 | 2028 | 1746810 | 1412 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 96016 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0037279 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | TRIP-SAVER |  | 42831 | 2039 | 1746939 | 1366 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 57372 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0037971 | OH | Sus | 31316082 | 2017 | APR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | RECLOSER |  | 42831 | 2233 | 1748398 | 842 | Distribution Circuit | Vegetation | Tree - fell into line | 753 | 422384 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037397 | OH | Sus | 31318176 | 2017 | APR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2110 | 153652110 | FUSE |  | 42832 | 2052 | 1751947 | 934 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 15878 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0038159 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 42831 | 2009 | 1746543 | 840 | Distribution Circuit | Vegetation | Tree - branch fell on line | 308 | 258720 | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037315 | OH | Sus | 42985909 | 2017 | APR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1110 | 152691110 | JUMPER |  | 42832 | 809 | 1750085 | 227 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 2985 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037675 | OH | Sus | 0 | 2017 | APR | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE |  | 42832 | 51 | 1749080 | 974 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 22138 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0037549 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1101 | 152031101 | FUSE |  | 42831 | 2115 | 1747621 | 1054 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5620 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0037317 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1104 | 152481104 | RECLOSER |  | 42831 | 2102 | 1747359 | 1033 | Distribution Circuit | Vegetation | Tree - fell into line | 505 | 277904 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037304 | OH | Sus | 42985912 | 2017 | APR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | NARROWS-2102 | 153132102 | FUSE |  | 42831 | 2347 | 1750120 | 1643 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 23002 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037945 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE |  | 42831 | 2222 | 1748343 | 1299 | Distribution Circuit | Vegetation | Tree - fell into line | 155 | 201345 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0037746 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | RECLOSER |  | 42831 | 1907 | 1746115 | 883 | Distribution Circuit | Vegetation | Tree - fell into line | 1017 | 145509 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037238 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | COTATI-1102 | 42271102 | FUSE |  | 42832 | 1553 | 1751214 | 188 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 10155 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0038029 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | BELLEVUE-2103 | 43182103 | FUSE |  | 42831 | 2154 | 1748032 | 2290 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 84730 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037479 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | OTHER |  | 42832 | 241 | 1749224 | 608 | Distribution Circuit | Vegetation | Tree - fell into line | 388 | 8532 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037613 | OH | Sus | 0 | 2017 | APR | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE |  | 42831 | 2125 | 1747741 | 1363 | Distribution Circuit | Equipment Failure/Involved | Overhead | 126 | 135174 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037460 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | OTHER |  | 42832 | 220 | 1749220 | 800 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 87211 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037575 | OH | Sus | 0 | 2017 | APR | Yes | Open Circuit | Yes | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 42831 | 1810 | 1745918 | 412 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 11536 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037250 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | OCB |  | 42831 | 2009 | 1746631 | 2878 | Distribution Circuit | Vegetation | Tree - fell into line | 523 | 818800 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0037273 | OH | Sus | 0 | 2017 | APR | Yes | Multi-Fault | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 42831 | 2009 | 1750403 | 2878 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 20146 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037737 | OH | Sus | 0 | 2017 | APR | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER |  | 42831 | 2002 | 1750400 | 2893 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 89683 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037736 | OH | Sus | 0 | 2017 | APR | Yes | Multi-Fault | Yes | No
SONOMA | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE |  | 42832 | 1640 | 1751350 | 155 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 775 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0038046 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 42831 | 1604 | 1745743 | 397 | Distribution Circuit | Vegetation | Tree - fell into line | 189 | 56748 | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0037200 | OH | Sus | 42985900 | 2017 | APR | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER |  | 42831 | 2359 | 1748927 | 592 | Distribution Circuit | Vegetation | Tree - fell into line | 215 | 127280 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037539 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 42832 | 1039 | 1750513 | 351 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 10179 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037849 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 254432104 | JUMPER |  | 42832 | 1225 | 1750653 | 180 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 180 | Overcast-Rain;32-90 F | Insulator | Broken- wire on ground | 17-0037885 | OH | Sus | 0 | 2017 | APR | Yes | Open Circuit | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE |  | 42832 | 805 | 1749567 | 782 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4485 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0037651 | OH | Sus | 0 | 2017 | APR | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 42832 | 338 | 1749338 | 827 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 51895 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037588 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | JUMPER |  | 42832 | 557 | 1750837 | 1011 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 13630 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037882 | OH | Sus | 0 | 2017 | APR | Yes | Open Circuit | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 42831 | 2019 | 1746872 | 734 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2202 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 17-0037385 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER |  | 42831 | 2250 | 1746649 | 1019 | Distribution Circuit | Vegetation | Tree - fell into line | 657 | 337855 | Overcast-Drizzle-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0037414 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | JUMPER |  | 42832 | 528 | 1749492 | 471 | Distribution Circuit | Vegetation | Tree - fell into line | 207 | 11226 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037649 | OH | Sus | 0 | 2017 | APR | Yes | Open Circuit | Yes | Yes
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE |  | 42831 | 2018 | 1746627 | 1152 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 46554 | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0037621 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE |  | 42831 | 2012 | 1746573 | 883 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 43910 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 17-0037524 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1705 | 163781705 | RECLOSER |  | 42831 | 2131 | 1747854 | 1400 | Distribution Circuit | Vegetation | Tree - fell into line | 1453 | 585827 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037401 | OH | Sus | 0 | 2017 | APR | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | RECLOSER |  | 42832 | 2158 | 1752019 | 173 | Distribution Circuit | Vegetation | Tree - fell into line | 421 | 72833 | Overcast-Rain;32-90 F | Conductor- Overhead | On Ground | 17-0038164 | OH | Sus | 0 | 2017 | APR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 42831 | 2254 | 1748568 | 873 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 65460 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0037600 | OH | Sus | 0 | 2017 | APR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 43073 | 1444 | 1935590 | 664 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2656 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0099755 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 43073 | 1927 | 1936047 | 463 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 28243 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 17-0099837 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 43085 | 931 | 1944249 | 570 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 6946 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0102065 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 43085 | 935 | 1944224 | 1352 | Distribution Circuit | Vegetation | Tree - fell into line | 527 | 38602 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0101957 | OH | Sus | 31370082 | 2017 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 43085 | 919 | 1944344 | 683 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 14343 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0102009 | OH | Sus | 1370082 | 2017 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 43073 | 1352 | 1935401 | 494 | Distribution Circuit | Vegetation | Tree - fell into line | 2200 | 442980 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0099694 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 43085 | 1225 | 1944818 | 1396 | Distribution Circuit | Vegetation | Tree - fell into line | 295 | 28283 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0102088 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 43073 | 1359 | 1935552 | 1604 | Distribution Circuit | Vegetation | Tree - fell into line | 750 | 355891 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0099716 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER |  | 43085 | 646 | 1944042 | 3186 | Distribution Circuit | Vegetation | Tree - fell into line | 908 | 1847418 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0101910 | OH | Sus | 31370181 | 2017 | DEC | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 43073 | 2006 | 1936048 | 2249 | Distribution Circuit | Vegetation | Tree - fell into line | 685 | 35805 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0099811 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 43073 | 1826 | 1935939 | 753 | Distribution Circuit | Vegetation | Tree - branch fell on line | 36 | 27108 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0099810 | OH | Sus | 43227153 | 2017 | DEC | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 43085 | 924 | 1944237 | 3342 | Distribution Circuit | Vegetation | Tree - fell into line | 2232 | 3670529 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0101950 | OH | Sus | 31370183 | 2017 | DEC | Yes | Multi-Fault | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 43073 | 2152 | 1936115 | 1058 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 17876 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0099865 | OH | Sus | 31368279 | 2017 | DEC | Yes | Line to Line | Yes | No
DIABLO | Tier 3 | MORAGA-1105 | 13801105 | FUSE |  | 43073 | 1633 | 1936022 | 607 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1894 | 115928 | Clear;32-90 F | Crossarm- Wood | Broken- wire on object | 17-0099807 | OH | Sus | 31368105 | 2017 | DEC | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 2 | FLORENCE-0401 | 12690401 | OCB |  | 43085 | 1622 | 1945670 | 414 | Distribution Circuit | Equipment Failure/Involved | Overhead | 492 | 63550 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0102194 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | JUMPER |  | 43085 | 1151 | 1945058 | 353 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 26120 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0102101 | OH | Sus | 0 | 2017 | DEC | Yes | Three Phase Fault | Yes | No
LOS PADRES | Tier 2 | SANTA MARIA-1108 | 182671108 | FUSE |  | 43073 | 930 | 1934673 | 813 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2439 | Strong Winds-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0099678 | OH | Sus | 43227091 | 2017 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | SAUSALITO-1102 | 42491102 | FUSE |  | 43085 | 1033 | 1944459 | 481 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 3896 | Clear-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 17-0102014 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | Yes
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | FUSE |  | 43085 | 908 | 1944195 | 394 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 21670 | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0101966 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | FUSE |  | 43085 | 939 | 1944273 | 477 | Distribution Circuit | Vegetation | Tree - fell into line | 1792 | 21402 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0101995 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE |  | 43073 | 1736 | 1935873 | 319 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 957 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0099800 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 43085 | 924 | 1944474 | 1112 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 23408 | Clear;32-90 F | Conductor- Overhead | On Ground | 17-0102074 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 43085 | 845 | 1944152 | 285 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1425 | Strong Winds-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0101947 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 43073 | 813 | 1934532 | 954 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 11448 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0099647 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE |  | 43073 | 911 | 1934633 | 454 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 20884 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0099617 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE |  | 43073 | 921 | 1934647 | 620 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2480 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0099600 | OH | Sus | 0 | 2017 | DEC | Yes | Three Phase Fault | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE |  | 43073 | 1121 | 1934978 | 834 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3336 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0099624 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | BUCKS CREEK-1103 | 102211103 | RECLOSER |  | 43085 | 924 | 1944580 | 3250 | Distribution Circuit | Vegetation | Tree - fell into line | 314 | 875514 | Clear;Below 32 F | Pole-Wood | Broken- wire on ground | 17-0102019 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | ORO FINO-1102 | 103031102 | FUSE |  | 43073 | 1130 | 1935634 | 628 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 46472 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0099731 | OH | Sus | 31368299 | 2017 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | OTHER |  | 43085 | 1206 | 1944712 | 221 | Distribution Circuit | Vegetation | Tree - fell into line | 1076 | 155662 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0102098 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | SWITCH |  | 43085 | 1527 | 1945909 | 525 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 8218 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0102222 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE |  | 43073 | 1650 | 1935846 | 604 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 13838 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0099791 | OH | Sus | 43227146 | 2017 | DEC | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | BELL-1108 | 152701108 | FUSE |  | 43085 | 1611 | 1945541 | 163 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 2659 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0102185 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 43073 | 1032 | 1934860 | 1328 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 30299 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0099679 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE |  | 43085 | 2221 | 1946009 | 1138 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 30601 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0102266 | OH | Sus | 35024126 | 2017 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SUMMIT-1101 | 152591101 | FUSE |  | 43085 | 940 | 1944327 | 393 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 6288 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0102011 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1102 | 152101102 | RECLOSER |  | 43085 | 1122 | 1944589 | 3283 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 58853 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0102021 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | FUSE |  | 43073 | 1131 | 1934989 | 424 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4240 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0099652 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER |  | 43073 | 1452 | 1935616 | 853 | Distribution Circuit | Vegetation | Tree - fell into line | 769 | 167781 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0099725 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE |  | 43073 | 1715 | 1935886 | 741 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 58016 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0099836 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE |  | 43073 | 1756 | 1935884 | 1213 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 41242 | Clear-Strong Winds;Below 32 F | Conductor- Overhead | On Ground | 17-0099815 | OH | Sus | 0 | 2017 | DEC | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE |  | 43073 | 1731 | 1935962 | 1239 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 18585 | Clear-Strong Winds;Below 32 F | Conductor- Overhead | On Ground | 17-0099809 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE |  | 43073 | 1720 | 1935841 | 1158 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 56508 | Clear-Strong Winds;Below 32 F | Pole-Wood | Broken- wire on ground | 17-0099850 | OH | Sus | 0 | 2017 | DEC | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE |  | 43073 | 1820 | 1935925 | 1200 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 30056 | Clear-Strong Winds;Below 32 F | Pole-Wood | Broken- wire on ground | 17-0099866 | OH | Sus | 31368344 | 2017 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | ELECTRA-1102 | 162161102 | FUSE |  | 43073 | 1341 | 1935278 | 725 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3625 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0099721 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | OTHER |  | 43073 | 1327 | 1935513 | 601 | Distribution Circuit | Vegetation | Tree - fell into line | 348 | 29088 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0099706 | OH | Sus | 0 | 2017 | DEC | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | OTHER |  | 43073 | 1421 | 1935747 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 1311 | 97276 | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0099754 | OH | Sus | 0 | 2017 | DEC | Yes | Open Circuit | Yes | Yes
STOCKTON | Tier 2 | SALT SPRINGS-2101 | 163692101 | JUMPER |  | 43085 | 2107 | 1945975 | 982 | Distribution Circuit | Vegetation | Tree - fell into line | 908 | 42056 | Strong Winds-Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0102264 | OH | Sus | 0 | 2017 | DEC | Yes | Open Circuit | Yes | No
STOCKTON | Tier 2 | SALT SPRINGS-2101 | 163692101 | RECLOSER |  | 43073 | 1909 | 1936934 | 1510 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 75500 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0100140 | OH | Sus | 0 | 2017 | DEC | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER |  | 43073 | 2239 | 1936143 | 501 | Distribution Circuit | Vegetation | Tree - fell into line | 1025 | 303452 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0099860 | OH | Sus | 31368360 | 2017 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | RECLOSER |  | 42784 | 1716 | s1263100 | 8370 | Distribution Circuit | Environmental/External | Flood/Erosion | 52 | 435240 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0026389 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | RECLOSER |  | 42783 | 649 | 1691384 | 2004 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 248406 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0021827 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | FUSE |  | 42784 | 1644 | 1701282 | 1492 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 20792 | Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023391 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | RECLOSER |  | 42786 | 728 | 1703510 | 4938 | Distribution Circuit | Vegetation | Tree - fell into line | 423 | 2085732 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023848 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | SWITCH |  | 42783 | 716 | 1691491 | 1924 | Distribution Circuit | Vegetation | Tree - fell into line | 364 | 684593 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0021997 | OH | Sus | 31306180 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | OCB |  | 42786 | 1237 | 1703213 | 6129 | Distribution Circuit | Equipment Failure/Involved | Overhead | 191 | 375767 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023801 | OH | Sus | 0 | 2017 | FEB | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | JUMPER |  | 42773 | 849 | 1680627 | 1811 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1811 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018675 | OH | Sus | 31304264 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | JUMPER |  | 42773 | 1205 | 1680125 | 1662 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3324 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018633 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | FUSE |  | 42786 | 1953 | 1705762 | 5447 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 141622 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0025671 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | FUSE |  | 42783 | 1548 | 1698474 | 2836 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 62392 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022705 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | TRIP-SAVER |  | 42787 | 1657 | 1709110 | 1077 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 32310 | Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025248 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | RECLOSER |  | 42786 | 1900 | 1705434 | 1843 | Distribution Circuit | Vegetation | Tree - bark fell into line | 638 | 780630 | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0024074 | OH | Sus | 31306180 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | FUSE |  | 42783 | 631 | 1699372 | 4802 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 196882 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0023154 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | FUSE |  | 42787 | 1652 | 1709104 | 1464 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 19032 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025243 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1112 | 182371112 | FUSE |  | 42786 | 1740 | 1705093 | 1334 | Distribution Circuit | Equipment Failure/Involved | Overhead | 133 | 177422 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024044 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1112 | 182371112 | FUSE |  | 42786 | 1524 | 1703915 | 1259 | Distribution Circuit | Vegetation | Tree - branch fell on line | 170 | 214030 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023933 | OH | Sus | 42949491 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1112 | 182371112 | FUSE |  | 42784 | 1421 | 1700097 | 1248 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 12587 | Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023212 | OH | Sus | 42949491 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE |  | 42783 | 823 | 1696697 | 4788 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 309033 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0022386 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 42786 | 1116 | 1703538 | 2012 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 74444 | Partly Cloudy-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0023852 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 42783 | 804 | 1701693 | 3647 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 51902 | Heavy Rain-Strong Winds-Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 17-0023467 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 42786 | 1115 | 1703542 | 2013 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 38247 | Partly Cloudy-Heavy Rain;32-90 F | Conductor- Overhead | On Ground | 17-0023853 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 42783 | 1836 | 1699433 | 1171 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 57379 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023064 | OH | Sus | 31306180 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1112 | 182371112 | FUSE |  | 42783 | 552 | 1691210 | 1653 | Distribution Circuit | Vegetation | Tree - fell into line | 104 | 171912 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022220 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1112 | 182371112 | FUSE |  | 42783 | 527 | 1692398 | 4754 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 57048 | Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022660 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1112 | 182371112 | FUSE |  | 42783 | 529 | 1691021 | 6099 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 36594 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023841 | OH | Sus | 42949491 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | OCB |  | 42786 | 1748 | 1705142 | 1620 | Distribution Circuit | Vegetation | Tree - fell into line | 2752 | 2776086 | Overcast-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0024003 | OH | Sus | 31306180 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE |  | 42786 | 2023 | 1708955 | 3127 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 34165 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 17-0025453 | OH | Sus | 31306180 | 2017 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 42786 | 1545 | 1703785 | 3021 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12084 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025754 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE |  | 42787 | 245 | 1704578 | 2293 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2293 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024835 | OH | Sus | 31306180 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | JUMPER |  | 42787 | 1121 | 1708345 | 1818 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5454 | Partly Cloudy;32-90 F | Conductor- Overhead | On Ground | 17-0025061 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2104 | 182222104 | RECLOSER |  | 42783 | 500 | 1690890 | 9340 | Distribution Circuit | Vegetation | Tree - fell into line | 3187 | 5555655 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0021790 | OH | Sus | 31306180 | 2017 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | RECLOSER |  | 42786 | 1429 | 1703515 | 2925 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 65946 | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0023850 | OH | Sus | 31306180 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE |  | 42786 | 1808 | 1705198 | 2947 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 29470 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024024 | OH | Sus | 31306180 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2104 | 182222104 | OTHER |  | 42786 | 1725 | 1704787 | 2901 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 54295 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024683 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 42784 | 341 | 1698824 | 4932 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 83040 | Heavy Rain-Strong Winds-Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023082 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | OTHER |  | 42786 | 1607 | 1710298 | 2978 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3942 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025481 | OH | Sus | 42949491 | 2017 | FEB | Yes | Line to Line | Yes | Yes
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | JUMPER |  | 42786 | 1607 | 1710290 | 3106 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3106 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 17-0025477 | OH | Sus | 42949491 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE |  | 42784 | 620 | 1698967 | 720 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 13808 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022988 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | OCB |  | 42786 | 1905 | 1705431 | 492 | Distribution Circuit | Vegetation | Tree - fell into line | 2283 | 1090928 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024037 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | RESERVATION ROAD-1101 | 182731101 | RECLOSER |  | 42783 | 505 | 1690928 | 9195 | Distribution Circuit | Vegetation | Tree - fell into line | 706 | 2064974 | Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0021789 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | SECTIONALIZER |  | 42786 | 1719 | 1704739 | 2973 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 115808 | Overcast-Drizzle-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0023965 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE |  | 42786 | 1615 | 1703988 | 2895 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 168930 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024025 | OH | Sus | 31306180 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE |  | 42786 | 1915 | 1706204 | 2561 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 120367 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024868 | OH | Sus | 31306180 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE |  | 42786 | 1949 | 1705735 | 3160 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 37920 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025423 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HOLLISTER-2106 | 182492106 | JUMPER |  | 42784 | 1853 | 1699622 | 2715 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 46155 | Heavy Rain-Strong Winds-Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023210 | OH | Sus | 0 | 2017 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 2 | SAN JUSTO-1101 | 183181101 | SWITCH |  | 42787 | 1628 | 1708878 | 1478 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 32516 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025238 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN JUSTO-1101 | 183181101 | JUMPER |  | 42786 | 836 | 1703223 | 1677 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 57018 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023796 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN JUSTO-1101 | 183181101 | FUSE |  | 42783 | 606 | 1701681 | 4834 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 19336 | Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023463 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE |  | 42783 | 1837 | 1698283 | 2659 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 231333 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023299 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE |  | 42786 | 506 | 1702455 | 679 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 7215 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023664 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE |  | 42786 | 713 | 1702729 | 776 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 8301 | Strong Winds-Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023693 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN JUSTO-1101 | 183181101 | FUSE |  | 42783 | 938 | 1693433 | 4621 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 90909 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022126 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | RECLOSER |  | 42786 | 2045 | 1705987 | 1412 | Distribution Circuit | Environmental/External | Flood/Erosion | 1237 | 428435 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 17-0024104 | OH | Sus | 42949498 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 42783 | 843 | 1692466 | 5929 | Distribution Circuit | Vegetation | Tree - bark fell into line | 70 | 25157 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022014 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 42783 | 825 | 1698735 | 4665 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 139950 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022903 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 42784 | 536 | 1698931 | 6401 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 25604 | Strong Winds-Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025083 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 42773 | 901 | 1679387 | 1849 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 83205 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | On Ground | 17-0018528 | OH | Sus | 42939797 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2105 | 83692105 | FUSE |  | 42783 | 824 | 1692151 | 3174 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 136482 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0023363 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 42786 | 1928 | 1705546 | 1308 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 24852 | Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024949 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | PAUL SWEET-2109 | 83252109 | FUSE |  | 42783 | 750 | 1691606 | 3621 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 155703 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0021973 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2105 | 83692105 | RECLOSER |  | 42775 | 1751 | 1684021 | 41 | Distribution Circuit | Vegetation | Tree - fell into line | 582 | 20334 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019491 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER |  | 42775 | 2345 | 1684103 | 1067 | Distribution Circuit | Vegetation | Tree - fell into line | 393 | 133534 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019718 | OH | Sus | 42939797 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER |  | 42775 | 1957 | 1684137 | 1361 | Distribution Circuit | Vegetation | Tree - fell into line | 262 | 356582 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019632 | OH | Sus | 31304215 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER |  | 42786 | 1243 | 1703277 | 2350 | Distribution Circuit | Vegetation | Tree - fell into line | 269 | 631989 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0023808 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 42786 | 1800 | 1705140 | 4280 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 9698 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025305 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 42783 | 828 | 1694719 | 3043 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 331687 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023367 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 42786 | 2019 | 1708286 | 4106 | Distribution Circuit | Environmental/External | Flood/Erosion | 1 | 4106 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0025405 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | RECLOSER |  | 42783 | 2147 | 1698528 | 1347 | Distribution Circuit | Vegetation | Tree - fell into line | 430 | 392418 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022724 | OH | Sus | 31306188 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 42787 | 29 | 1706890 | 3602 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 61234 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025137 | OH | Sus | 31306188 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 42786 | 1844 | 1705338 | 2589 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 28479 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025079 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2102 | 83252102 | FUSE |  | 42786 | 2320 | 1706735 | 1251 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 40032 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0024820 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 42788 | 1543 | 1711006 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 332 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025710 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 42788 | 1801 | 1711260 | 1388 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 12492 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025769 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 42775 | 2345 | 1684396 | 655 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1965 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019731 | OH | Sus | 31304215 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | PAUL SWEET-2106 | 83252106 | FUSE |  | 42773 | 135 | 1677342 | 757 | Distribution Circuit | Environmental/External | Flood/Erosion | 102 | 52137 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0018054 | OH | Sus | 42939835 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | OTHER |  | 42773 | 2134 | 1681093 | 1162 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 16565 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018823 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 42786 | 1319 | 1703355 | 115 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 2875 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023864 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 42775 | 1243 | 1683403 | 1457 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 6410 | Clear;32-90 F | Conductor- Overhead | On Ground | 17-0019497 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2104 | 83252104 | SWITCH |  | 42787 | 1617 | 1708985 | 1406 | Distribution Circuit | Vegetation | Tree - branch fell on line | 142 | 199652 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025218 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2102 | 83252102 | FUSE |  | 42783 | 1306 | 1695836 | 5844 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 35064 | Overcast-Rain;32-90 F | Conductor- Overhead | On Ground | 17-0023155 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | SECTIONALIZER |  | 42783 | 955 | 1694253 | 815 | Distribution Circuit | Vegetation | Tree - fell into line | 1368 | 1114746 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022411 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 42787 | 744 | 1704296 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 27720 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024911 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 42787 | 1140 | 1707685 | 1907 | Distribution Circuit | Environmental/External | Flood/Erosion | 109 | 207863 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025073 | OH | Sus | 0 | 2017 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 42787 | 1936 | 1709418 | 1193 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 25053 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025313 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 42773 | 345 | 1682634 | 3613 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 18065 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019368 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 42786 | 1826 | 1705272 | 1613 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 9678 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025065 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 42773 | 1428 | 1680508 | 3073 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 64533 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 17-0018743 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 42783 | 901 | 1703506 | 5084 | Distribution Circuit | Environmental/External | Flood/Erosion | 8 | 40672 | Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023847 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 42775 | 1953 | 1684134 | 4087 | Distribution Circuit | Environmental/External | Flood/Erosion | 21 | 60427 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019710 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 42773 | 107 | 1677325 | 778 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 57572 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018045 | OH | Sus | 31304293 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 42783 | 1108 | 1694745 | 3135 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 97185 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023434 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 42783 | 901 | 1706770 | 5914 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 76882 | Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024741 | OH | Sus | 0 | 2017 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 42786 | 602 | 1702505 | 603 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 7236 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023669 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 42786 | 1620 | 1704033 | 4109 | Distribution Circuit | Vegetation | Tree - fell into line | 296 | 444914 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024598 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 42786 | 1658 | 1704416 | 3004 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 75100 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0025235 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 42786 | 1622 | 1704031 | 2808 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 16848 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024753 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | OTHER |  | 42783 | 1319 | 1698177 | 5865 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 17251 | Heavy Rain-Strong Winds-Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022601 | OH | Sus | 0 | 2017 | FEB | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 42786 | 1621 | 1704077 | 3174 | Distribution Circuit | Vegetation | Tree - fell into line | 486 | 783560 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0023922 | OH | Sus | 42949498 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 42783 | 717 | 1691347 | 6542 | Distribution Circuit | Vegetation | Tree - fell into line | 745 | 156896 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0021846 | OH | Sus | 42949498 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | OTHER |  | 42775 | 1433 | 1683708 | 1580 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 12640 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019521 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | OTHER |  | 42783 | 501 | 1691237 | 1896 | Distribution Circuit | Vegetation | Tree - fell into line | 296 | 149623 |  | Conductor- Overhead | On Ground | 17-0021809 | OH | Sus | 31306188 | 2017 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 42773 | 104 | 1678178 | 2380 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 140420 | Overcast-Rain;32-90 F | Conductor- Overhead | On Ground | 17-0018273 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 42773 | 1735 | 1680782 | 2450 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 24500 | Overcast-Drizzle;32-90 F | Conductor- Overhead | On Ground | 17-0018915 | OH | Sus | 42939797 | 2017 | FEB | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | RECLOSER |  | 42786 | 1637 | 1704223 | 2476 | Distribution Circuit | Vegetation | Tree - fell into line | 340 | 318650 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023930 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | SECTIONALIZER |  | 42786 | 1651 | 1704367 | 1414 | Distribution Circuit | Equipment Failure/Involved | Overhead | 368 | 293972 | Overcast-Heavy Rain-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 17-0024404 | OH | Sus | 42949498 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42783 | 1711 | 1697612 | 7089 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 19017 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022966 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | JUMPER |  | 42786 | 1320 | 1703353 | 118 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 118 | Strong Winds-Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023819 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42775 | 1351 | 1684110 | 1539 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3078 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | On Ground | 17-0019626 | OH | Sus | 31304215 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42784 | 1613 | 1694376 | 1653 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 8265 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023150 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42786 | 1526 | 1704440 | 1599 | Distribution Circuit | Vegetation | Tree - fell into line | 193 | 118579 | Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024020 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42786 | 1716 | 1704611 | 2739 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 65736 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0024935 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE |  | 42773 | 1043 | 1680242 | 1497 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 13473 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018699 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 42783 | 1633 | 1697398 | 102 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 510 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022567 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE |  | 42773 | 452 | 1677830 | 2748 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 10992 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018120 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE |  | 42787 | 930 | 1711917 | 3345 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10035 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025965 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 42783 | 1231 | 1695769 | 3506 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 49084 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0022263 | OH | Sus | 31306188 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 42775 | 824 | 1682868 | 1869 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 13083 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0019333 | OH | Sus | 31304215 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42786 | 1603 | 1703886 | 2725 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 155325 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0023971 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 42786 | 1523 | 1703714 | 3180 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 248040 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023886 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 42786 | 1458 | 1703624 | 4146 | Distribution Circuit | Environmental/External | Flood/Erosion | 525 | 514596 | Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023913 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42775 | 2316 | 1684351 | 1116 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8928 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019736 | OH | Sus | 42939797 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 42787 | 1256 | 1708585 | 1837 | Distribution Circuit | Vegetation | Tree - fell into line | 546 | 156387 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025114 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 42788 | 1148 | 1710593 | 581 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7553 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025575 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE |  | 42773 | 1001 | 1679617 | 3185 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 22295 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018795 | OH | Sus | 31304215 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 42783 | 1330 | 1696022 | 4272 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 136704 | Strong Winds-Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022361 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | JUMPER |  | 42788 | 1638 | 1711090 | 1377 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 13770 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025936 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42786 | 2020 | 1707804 | 2489 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 199120 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025282 | OH | Sus | 0 | 2017 | FEB | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42786 | 1450 | 1703589 | 1665 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 123210 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023885 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER |  | 42786 | 1706 | 1704473 | 2784 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 343328 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023956 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42786 | 2044 | 1706188 | 2716 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 13312 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025224 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42787 | 323 | 1709254 | 2257 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 41975 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025274 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 42773 | 747 | 1678755 | 1646 | Distribution Circuit | Vegetation | Tree - fell into line | 522 | 194099 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018264 | OH | Sus | 31304215 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 42786 | 1607 | 1703838 | 2903 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 84526 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023910 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42784 | 1009 | 1699415 | 5988 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 50478 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023008 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42786 | 1515 | 1707556 | 3986 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 25557 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024894 | OH | Sus | 42949498 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42788 | 1536 | 1710998 | 204 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 816 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025704 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 42773 | 1123 | 1679930 | 4520 | Distribution Circuit | Environmental/External | Flood/Erosion | 289 | 192265 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0018500 | OH | Sus | 31304215 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42773 | 130 | 1677332 | 1569 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 26673 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018325 | OH | Sus | 42939797 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42787 | 319 | 1709351 | 3731 | Distribution Circuit | Vegetation | Tree - fell into line | 412 | 1345108 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025283 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 42787 | 325 | 1709172 | 2387 | Distribution Circuit | Vegetation | Tree - branch fell on line | 115 | 75425 | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0025257 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42788 | 2308 | 1711488 | 1002 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 98196 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025876 | OH | Sus | 42949498 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42773 | 1128 | 1680927 | 1657 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 128686 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018812 | OH | Sus | 31304215 | 2017 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42786 | 1515 | 1707553 | 3113 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 305074 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024891 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42786 | 1550 | 1703807 | 3310 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 18440 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024011 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER |  | 42787 | 319 | 1710608 | 3336 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 32764 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025570 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 42783 | 848 | 1692567 | 4449 | Distribution Circuit | Vegetation | Tree - branch fell on line | 169 | 220685 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022832 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 42775 | 2123 | 1684190 | 2263 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 77561 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019711 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42773 | 756 | 1679056 | 6047 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 57290 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0018388 | OH | Sus | 31304215 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | TRANSFORMER |  | 42783 | 1656 | 1697533 | 8145 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 8145 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022713 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42786 | 1831 | 1705173 | 2709 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 56889 | Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024059 | OH | Sus | 42949498 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42786 | 1631 | 1705165 | 2837 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 139013 | Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024073 | OH | Sus | 31306188 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42786 | 1804 | 1705171 | 2951 | Distribution Circuit | Environmental/External | Flood/Erosion | 6 | 17706 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025037 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42773 | 1639 | 1680684 | 1410 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8460 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018693 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42788 | 828 | 1710127 | 598 | Distribution Circuit | Environmental/External | Flood/Erosion | 6 | 3588 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025446 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER |  | 42787 | 737 | 1709006 | 3473 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 14867 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025221 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 42783 | 959 | 1693717 | 3159 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 22113 | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022158 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42773 | 730 | 1679363 | 2071 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 41420 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 17-0018748 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 42786 | 1730 | 1704907 | 1581 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 52173 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 17-0025020 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 42787 | 28 | 1707470 | 765 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 42840 | Heavy Rain-Strong Winds;32-90 F | Insulator | Broken- wire on object | 17-0025105 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | SECTIONALIZER |  | 42786 | 1738 | 1704199 | 2788 | Distribution Circuit | Vegetation | Tree - fell into line | 178 | 262858 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023976 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 42773 | 830 | 1678971 | 1827 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 92872 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018659 | OH | Sus | 42939797 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 42786 | 1732 | 1704944 | 2812 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 41414 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024742 | OH | Sus | 42949498 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 42775 | 1557 | 1683829 | 1343 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 26860 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | On Ground | 17-0019614 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 42786 | 930 | 1703085 | 3162 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 91698 | Overcast-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0023764 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 42787 | 1240 | 1704677 | 3053 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4141 | Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025377 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER |  | 42783 | 1556 | 1697014 | 1540 | Distribution Circuit | Equipment Failure/Involved | Overhead | 270 | 38337 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022552 | OH | Sus | 31306421 | 2017 | FEB | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 42786 | 1721 | 1704700 | 4164 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 33312 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 17-0025275 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | TRIP-SAVER |  | 42786 | 1636 | 1704194 | 4137 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 91014 | Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025057 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 42786 | 1651 | 1705811 | 3915 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 58725 | Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024995 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 42773 | 639 | 1680008 | 2298 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 11490 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018532 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | TRIP-SAVER |  | 42773 | 848 | 1679132 | 381 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 29718 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018469 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 42786 | 1737 | 1704989 | 4245 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 12735 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0024806 | OH | Sus | 31306426 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 42786 | 1707 | 1704480 | 4216 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 139104 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025761 | OH | Sus | 31306421 | 2017 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 42786 | 1619 | 1704013 | 3142 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 78385 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025464 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 42788 | 1652 | 1711126 | 308 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 9856 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025855 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 42786 | 1634 | 1704184 | 1676 | Distribution Circuit | Vegetation | Tree - fell into line | 207 | 346932 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024730 | OH | Sus | 31306426 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 42773 | 629 | 1678191 | 1906 | Distribution Circuit | Vegetation | Tree - fell into line | 338 | 175889 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018174 | OH | Sus | 31304239 | 2017 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 42786 | 1550 | 1703743 | 7049 | Distribution Circuit | Vegetation | Tree - fell into line | 338 | 1772057 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023898 | OH | Sus | 31306421 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER |  | 42775 | 1918 | 1684101 | 1853 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 17557 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019734 | OH | Sus | 31304342 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 42786 | 1503 | 1703629 | 5850 | Distribution Circuit | Vegetation | Tree - fell into line | 718 | 3670876 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023867 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH |  | 42786 | 1620 | 1704048 | 4331 | Distribution Circuit | Vegetation | Tree - fell into line | 160 | 694083 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023924 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 42786 | 1552 | 1703842 | 1649 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 222615 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023899 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER |  | 42788 | 640 | 1711513 | 992 | Distribution Circuit | Environmental/External | Flood/Erosion | 8 | 7936 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025874 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 42786 | 2111 | 1704263 | 3968 | Distribution Circuit | Vegetation | Tree - fell into line | 309 | 1136634 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024200 | OH | Sus | 31306421 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH |  | 42786 | 1859 | 1705660 | 5715 | Distribution Circuit | Environmental/External | Flood/Erosion | 9 | 51435 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024916 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 42773 | 833 | 1679023 | 178 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 16554 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0018321 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 42786 | 1748 | 1704704 | 7629 | Distribution Circuit | Equipment Failure/Involved | Overhead | 508 | 2696073 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023990 | OH | Sus | 31306421 | 2017 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | STELLING-1110 | 83481110 | FUSE |  | 42786 | 1543 | 1704777 | 9909 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 56984 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0026749 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | LOS GATOS-1101 | 82021101 | FUSE |  | 42786 | 1642 | 1705251 | 2916 | Distribution Circuit | Environmental/External | Flood/Erosion | 84 | 244944 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025632 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE |  | 42783 | 923 | 1695077 | 2239 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 17912 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022859 | OH | Sus | 31306421 | 2017 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | HICKS-1116 | 83431116 | OTHER |  | 42786 | 1706 | 1704476 | 4028 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 108756 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025621 | OH | Sus | 42950074 | 2017 | FEB | Yes | None | Yes | Yes
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE |  | 42786 | 1747 | 1705726 | 5799 | Distribution Circuit | Environmental/External | Flood/Erosion | 35 | 124357 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024892 | OH | Sus | 31306421 | 2017 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE |  | 42783 | 1540 | 1693227 | 1771 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 8855 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023041 | OH | Sus | 31306421 | 2017 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 2 | SARATOGA 1105 | 83371105 | SWITCH |  | 42773 | 1512 | 1680535 | 2008 | Distribution Circuit | Vegetation | Tree - branch fell on line | 310 | 35608 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018656 | OH | Sus | 31304239 | 2017 | FEB | Yes | Force Out | Yes | No
DE ANZA | Tier 2 | STELLING-1110 | 83481110 | TRIP-SAVER |  | 42773 | 512 | 1678870 | 1929 | Distribution Circuit | Equipment Failure/Involved | Overhead | 461 | 309020 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018379 | OH | Sus | 42939926 | 2017 | FEB | Yes | Line to Line | Yes | No
DIABLO | Tier 2 | TASSAJARA-2112 | 14662112 | RECLOSER |  | 42773 | 2250 | 1681188 | 1273 | Distribution Circuit | Vegetation | Tree - fell into line | 1257 | 133984 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018811 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
DIABLO | Tier 2 | SOBRANTE-1102 | 14671102 | FUSE |  | 42773 | 111 | 1677318 | 427 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 32452 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018033 | OH | Sus | 31304292 | 2017 | FEB | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAKLAND J-1102 | 12091102 | FUSE |  | 42773 | 304 | 1677526 | 610 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 17962 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018118 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
EAST BAY | Tier 2 | OAKLAND X-1106 | 12541106 | FUSE |  | 42784 | 619 | 1698965 | 1686 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 40464 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022917 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAKLAND X-1106 | 12541106 | SWITCH |  | 42788 | 1705 | 1711077 | 609 | Distribution Circuit | Vegetation | Tree - fell into line | 1658 | 36593 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025740 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | RECLOSER |  | 42773 | 604 | 1678074 | 506 | Distribution Circuit | Vegetation | Tree - branch fell on line | 221 | 27636 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018169 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1102 | 12101102 | OTHER |  | 42787 | 33 | 1706964 | 1029 | Distribution Circuit | Vegetation | Tree - fell into line | 1323 | 345024 | Overcast-Fog-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024836 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 42775 | 1159 | 1683246 | 1745 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 12215 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019580 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER |  | 42786 | 322 | 1702367 | 841 | Distribution Circuit | Equipment Failure/Involved | Overhead | 314 | 264074 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023655 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE |  | 42786 | 2348 | 1706765 | 2384 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 50064 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0024838 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE |  | 42773 | 825 | 1678936 | 330 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1490 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018425 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE |  | 42786 | 2119 | 1706142 | 1459 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 8754 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0024905 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 42786 | 2050 | 1708048 | 1079 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4814 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024976 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 42775 | 818 | 1682859 | 407 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2035 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019388 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE |  | 42787 | 534 | 1707450 | 481 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1924 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024934 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | OTHER |  | 42786 | 940 | 1702931 | 320 | Distribution Circuit | Environmental/External | Flood/Erosion | 1 | 320 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023732 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | RECLOSER |  | 42783 | 1157 | 1695296 | 773 | Distribution Circuit | Vegetation | Tree - fell into line | 544 | 118435 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0022229 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | TRIP-SAVER |  | 42786 | 2034 | 1705947 | 1508 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 48324 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0024320 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 42783 | 1101 | 1694634 | 319 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 26158 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022153 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 42784 | 805 | 1699127 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1755 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022953 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER |  | 42786 | 1856 | 1705418 | 90 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 25380 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024064 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | RECLOSER |  | 42786 | 2125 | 1706809 | 863 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 44345 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024560 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | KONOCTI-1108 | 43311108 | FUSE |  | 42788 | 1501 | 1710847 | 238 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 5957 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025699 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE |  | 42775 | 31 | 1682652 | 747 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 24051 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019209 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER |  | 42773 | 401 | 1677894 | 488 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 37336 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018160 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | UKIAH-1115 | 42771115 | FUSE |  | 42786 | 829 | 1702742 | 716 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 27302 | Partly Cloudy-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023733 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | RECLOSER |  | 42773 | 226 | 1677401 | 872 | Distribution Circuit | Vegetation | Tree - fell into line | 292 | 206364 | Overcast-Fog-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0018119 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42784 | 424 | 1699084 | 570 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2850 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022905 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42775 | 915 | 1682966 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2025 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019380 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42783 | 1202 | 1695273 | 474 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2448 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022268 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42786 | 1641 | 1704236 | 1254 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 40192 | Clear;32-90 F | Conductor- Overhead | On Ground | 17-0023957 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER |  | 42788 | 1450 | 1710908 | 590 | Distribution Circuit | Vegetation | Tree - fell into line | 357 | 62400 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025703 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42773 | 35 | 1677632 | 925 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 15725 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018313 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42775 | 1608 | 1683856 | 2817 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 43631 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019589 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE |  | 42773 | 546 | 1677989 | 888 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 19536 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018490 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42784 | 408 | 1698868 | 442 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3536 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022959 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 42775 | 728 | 1682804 | 431 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 20257 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019288 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42784 | 649 | 1699000 | 641 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3846 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022935 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | RECLOSER |  | 42786 | 1440 | 1703577 | 1390 | Distribution Circuit | Vegetation | Tree - fell into line | 938 | 271604 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023880 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42773 | 717 | 1679122 | 707 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2828 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018704 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42773 | 1152 | 1680018 | 163 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 163 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018615 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE |  | 42786 | 1439 | 1706083 | 1645 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 13160 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024132 | OH | Sus | 0 | 2017 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | RECLOSER |  | 42773 | 359 | 1677687 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 298 | 68528 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018179 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE |  | 42775 | 1018 | 1683066 | 438 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 13578 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019395 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER |  | 42784 | 1019 | 1699420 | 822 | Distribution Circuit | Vegetation | Tree - branch fell on line | 89 | 35363 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023003 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 42773 | 410 | 1677713 | 874 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 3496 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018345 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | RECLOSER |  | 42775 | 823 | s1256917 | 455 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 50050 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019290 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 42773 | 1025 | 1679718 | 1565 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3130 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018588 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 42773 | 843 | 1678957 | 346 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 8996 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018452 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 42775 | 909 | 1683016 | 321 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 12519 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019338 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 42773 | 316 | 1679710 | 2024 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 41580 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018464 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 42773 | 326 | 1677594 | 879 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 18459 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018352 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 42775 | 1428 | 1683640 | 465 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4185 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019577 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER |  | 42773 | 2130 | 1679549 | 806 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 7254 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018744 | OH | Sus | 0 | 2017 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1103 | 192221103 | RECLOSER |  | 42775 | 1303 | 1683446 | 1859 | Distribution Circuit | Vegetation | Tree - fell into line | 2653 | 1247182 | Overcast-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0019450 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER |  | 42773 | 231 | 1677429 | 606 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 53694 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018052 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | SWITCH |  | 42786 | 1953 | 1705782 | 1028 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 35879 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024078 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER |  | 42775 | 1009 | 1683053 | 234 | Distribution Circuit | Vegetation | Tree - branch fell on line | 551 | 40158 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019336 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE 1103 | 192221103 | FUSE |  | 42775 | 439 | 1682851 | 2216 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 77560 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019322 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | CARLOTTA-1121 | 192291121 | OTHER |  | 42784 | 351 | 1698869 | 414 | Distribution Circuit | Vegetation | Tree - fell into line | 230 | 27697 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022876 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | EEL RIVER-1103 | 192381103 | FUSE |  | 42775 | 744 | 1682821 | 279 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1674 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019302 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | HUMBOLDT BAY-1102 | 192341102 | FUSE |  | 42787 | 1231 | 1708531 | 266 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1064 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025205 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | MAPLE CREEK-1101 | 192101101 | FUSE |  | 42783 | 1127 | 1694961 | 178 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 534 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022109 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER |  | 42773 | 431 | 1678835 | 1698 | Distribution Circuit | Vegetation | Tree - fell into line | 290 | 475244 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018311 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER |  | 42786 | 1741 | 1705017 | 1467 | Distribution Circuit | Vegetation | Tree - branch fell on line | 133 | 156970 | Partly Cloudy-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023979 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | SWITCH |  | 42786 | 1741 | 1708350 | 1745 | Distribution Circuit | Vegetation | Tree - fell into line | 465 | 811425 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025064 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | CABRILLO-1103 | 183101103 | FUSE |  | 42784 | 744 | 1699093 | 289 | Distribution Circuit | Equipment Failure/Involved | Overhead | 163 | 7093 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023007 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | OCEANO-1108 | 182601108 | FUSE |  | 42783 | 1029 | 1696511 | 3010 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6020 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022333 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | OCEANO-1108 | 182601108 | SWITCH |  | 42783 | 1750 | 1696038 | 10 | Distribution Circuit | Vegetation | Tree - fell into line | 890 | 8900 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0022557 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | OCEANO-1108 | 182601108 | FUSE |  | 42783 | 957 | 1694172 | 4458 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 4458 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022227 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | OCEANO-1108 | 182601108 | FUSE |  | 42783 | 1015 | 1694221 | 2918 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 145900 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022828 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | OCEANO-1104 | 182601104 | FUSE |  | 42784 | 2344 | 1700964 | 1225 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 18375 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023308 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER |  | 42786 | 534 | 1702489 | 450 | Distribution Circuit | Vegetation | Tree - fell into line | 183 | 46692 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0023646 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | OCEANO-1104 | 182601104 | FUSE |  | 42783 | 925 | 1698372 | 6020 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 355180 | Partly Cloudy-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0022640 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | OCEANO-1104 | 182601104 | FUSE |  | 42783 | 930 | 1701241 | 3896 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 27272 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023378 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | OCEANO-1104 | 182601104 | FUSE |  | 42783 | 930 | 1701361 | 4380 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 13140 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023411 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | FUSE |  | 42786 | 1120 | 1703107 | 766 | Distribution Circuit | Vegetation | Tree - fell into line | 1179 | 166918 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023599 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | OCEANO-1105 | 182601105 | OCB |  | 42783 | 959 | 1693522 | 3576 | Distribution Circuit | Vegetation | Tree - fell into line | 9178 | 3700800 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022024 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 3 | ATASCADERO-1103 | 182541103 | RECLOSER |  | 42787 | 746 | 1707754 | 1054 | Distribution Circuit | Equipment Failure/Involved | Overhead | 131 | 21824 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024923 | OH | Sus | 31306099 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | ATASCADERO-1103 | 182541103 | RECLOSER |  | 42783 | 1806 | 1697994 | 1478 | Distribution Circuit | Vegetation | Tree - fell into line | 1613 | 415250 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022620 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2113 | 183052113 | FUSE |  | 42783 | 1101 | 1694781 | 2092 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 18828 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023187 | OH | Sus | 42949651 | 2017 | FEB | Yes | Multi-Fault | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2113 | 183052113 | FUSE |  | 42784 | 1118 | 1699608 | 1447 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1447 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023038 | OH | Sus | 31306099 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE |  | 42787 | 833 | 1708645 | 412 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2060 | Heavy Rain-Strong Winds-Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025134 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE |  | 42784 | 1345 | 1699960 | 1214 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 9712 | Strong Winds-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023115 | OH | Sus | 42949651 | 2017 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE |  | 42784 | 953 | 1699402 | 1834 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 18340 | Overcast-Strong Winds-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022979 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE |  | 42786 | 1553 | 1703819 | 512 | Distribution Circuit | Equipment Failure/Involved | Overhead | 107 | 54784 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023909 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE |  | 42784 | 1321 | 1699925 | 3013 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 123533 | Strong Winds-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0023111 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE |  | 42787 | 1134 | 1708392 | 412 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 8906 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025179 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | CAMBRIA-1101 | 182771101 | OTHER |  | 42773 | 1651 | 1680705 | 1344 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 37965 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018731 | OH | Sus | 0 | 2017 | FEB | Yes | Open Circuit | Yes | Yes
MISSION | Tier 2 | CAYETANO-2109 | 14422109 | FUSE |  | 42783 | 1946 | 1698321 | 449 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 21103 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022796 | OH | Sus | 0 | 2017 | FEB | Yes | None | Yes | No
NORTH BAY | Tier 2 | ALTO-1120 | 42031120 | FUSE |  | 42773 | 1305 | 1680203 | 448 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1792 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018590 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | ALTO-1120 | 42031120 | FUSE |  | 42783 | 733 | 1691532 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1576 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0021922 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE |  | 42773 | 423 | 1677751 | 849 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 40814 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018116 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE |  | 42786 | 2200 | 1706294 | 1332 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 121656 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024649 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE |  | 42773 | 513 | 1677921 | 3687 | Distribution Circuit | Environmental/External | Flood/Erosion | 1840 | 294046 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0018157 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE |  | 42787 | 732 | 1707705 | 448 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 21952 | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025139 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | SAN RAFAEL-1105 | 42011105 | FUSE |  | 42773 | 555 | 1678003 | 357 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 4641 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018180 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE |  | 42787 | 1044 | 1708265 | 651 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1302 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025168 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE |  | 42786 | 2115 | 1706127 | 850 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 6800 | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024745 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE |  | 42786 | 2052 | 1706016 | 1052 | Distribution Circuit | Equipment Failure/Involved | Overhead | 228 | 77342 | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024264 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE |  | 42773 | 126 | 1677340 | 853 | Distribution Circuit | Vegetation | Tree - fell into line | 228 | 100460 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018072 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | Yes
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | RECLOSER |  | 42773 | 616 | 1678087 | 1189 | Distribution Circuit | Vegetation | Tree - fell into line | 831 | 300856 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0018209 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE |  | 42784 | 709 | 1699027 | 1354 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4062 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022923 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE |  | 42773 | 322 | 1677630 | 803 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2409 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018092 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE |  | 42775 | 1333 | 1683536 | 792 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 18216 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019512 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 42786 | 1610 | 1703959 | 1191 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 9528 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024023 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 42775 | 858 | 1682925 | 1169 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 14028 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019421 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 42784 | 1351 | 1699976 | 673 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 17498 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023166 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 42775 | 1337 | 1683477 | 1207 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 31382 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019470 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER |  | 42786 | 154 | 1702308 | 763 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 113687 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023603 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | PUEBLO-1104 | 43291104 | RECLOSER |  | 42783 | 1114 | 1694844 | 3406 | Distribution Circuit | Equipment Failure/Involved | Overhead | 156 | 266906 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022594 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 42788 | 2317 | 1711480 | 2468 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 128336 | Clear-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025873 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 42786 | 1709 | 1704507 | 974 | Distribution Circuit | Vegetation | Tree - fell into line | 153 | 62117 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023993 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 2 | SILVERADO-2102 | 43432102 | FUSE |  | 42786 | 1615 | 1704065 | 735 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 8550 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023987 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE |  | 42773 | 503 | 1677878 | 1232 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 23408 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0018453 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 42788 | 1406 | 1710827 | 572 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 18943 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025669 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1102 | 42711102 | JUMPER |  | 42786 | 2309 | 1707410 | 1086 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2172 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025059 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 42786 | 2230 | 1706528 | 974 | Distribution Circuit | Equipment Failure/Involved | Overhead | 87 | 32258 | Overcast-Fog-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024727 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE |  | 42773 | 501 | 1678224 | 4186 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 189914 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018290 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
NORTH BAY | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE |  | 42783 | 908 | 1692915 | 2859 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 40026 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022009 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE |  | 42787 | 210 | 1707259 | 2330 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 22708 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024936 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1107 | 102911107 | FUSE |  | 42773 | 231 | 1677406 | 451 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 21054 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018097 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE |  | 42773 | 419 | 1677732 | 960 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 5172 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018423 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE |  | 42787 | 119 | 1707121 | 2131 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 17048 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024980 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE |  | 42773 | 1816 | 1680856 | 996 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1278 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018747 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | OTHER |  | 42787 | 1117 | 1708329 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 358 | 221997 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0025092 | OH | Sus | 0 | 2017 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | RECLOSER |  | 42773 | 418 | 1677739 | 744 | Distribution Circuit | 3rd Party | Vehicle | 3403 | 883011 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0018125 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | BUCKS CREEK-1103 | 102211103 | RECLOSER |  | 42787 | 28 | 1710770 | 3709 | Distribution Circuit | Equipment Failure/Involved | Overhead | 314 | 1164626 | Overcast;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0025633 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | FUSE |  | 42787 | 1250 | 1708599 | 1633 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 11431 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025118 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | GRAYS FLAT 0401 | 102530401 | FUSE |  | 42787 | 938 | 1708126 | 2027 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 24324 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025080 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | GRAYS FLAT-0401 | 102530401 | FUSE |  | 42787 | 702 | 1708248 | 666 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 26640 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0025128 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | SPANISH CREEK-4401 | 103104401 | FUSE |  | 42787 | 1752 | 1709219 | 2630 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2630 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025267 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | SPANISH CREEK-4401 | 103104401 | OTHER |  | 42787 | 547 | 1707859 | 753 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 19179 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025199 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | FUSE |  | 42787 | 521 | 1707440 | 3181 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 206504 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024889 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | FUSE |  | 42786 | 2139 | 1706186 | 1201 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 25221 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024762 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER |  | 42773 | 1400 | 1680318 | 136 | Distribution Circuit | Equipment Failure/Involved | Overhead | 975 | 132600 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018641 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER |  | 42786 | 1857 | 1708664 | 2655 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 222027 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025138 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1101 | 102931101 | FUSE |  | 42786 | 1614 | 1703746 | 1216 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2789 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023920 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER |  | 42786 | 2042 | 1705973 | 3975 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 615828 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0024102 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | FUSE |  | 42787 | 230 | 1707228 | 612 | Distribution Circuit | Vegetation | Tree - fell into line | 1167 | 163416 | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 17-0024840 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | Yes
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE |  | 42773 | 425 | 1677761 | 769 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 9228 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0018327 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE |  | 42775 | 106 | s1256834 | 304 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 6992 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019215 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | OTHER |  | 42775 | 1014 | 1683059 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 957 | 26340 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019391 | OH | Sus | 0 | 2017 | FEB | Yes | Open Circuit | Yes | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 42775 | 1900 | 1684093 | 1252 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 47576 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019634 | OH | Sus | 31304022 | 2017 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 42773 | 906 | -1680268 | 1048 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 39824 |  | Conductor- Overhead | Broken- wire on ground | 17-0018614 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | JUMPER |  | 42786 | 1040 | 1702873 | 903 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 34314 | Clear;32-90 F | Conductor- Overhead | On Ground | 17-0023767 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | TRIP-SAVER |  | 42786 | 1635 | 1704608 | 1443 | Distribution Circuit | Equipment Failure/Involved | Overhead | 106 | 152958 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0024680 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 42773 | 601 | 1678185 | 1010 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 34340 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018292 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 42775 | 2302 | 1684331 | 1058 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 15215 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019761 | OH | Sus | 42939220 | 2017 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | RECLOSER |  | 42783 | 951 | 1693622 | 204 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 24271 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0021980 | OH | Sus | 42950847 | 2017 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE |  | 42783 | 938 | 1693429 | 844 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3354 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022113 | OH | Sus | 31306686 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 42786 | 1804 | 1705161 | 2743 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 21944 | Overcast-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0024165 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | JUMPER |  | 42784 | 614 | 1699086 | 468 | Distribution Circuit | Vegetation | Tree - fell into line | 160 | 36457 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022911 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE |  | 42786 | 2044 | 1706007 | 2447 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 122350 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024802 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER |  | 42787 | 829 | 1707906 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 927 | 156962 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024948 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 42773 | 639 | 1678242 | 837 | Distribution Circuit | Equipment Failure/Involved | Overhead | 314 | 69594 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0018195 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER |  | 42786 | 639 | 1702537 | 527 | Distribution Circuit | Vegetation | Tree - fell into line | 314 | 44742 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023662 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | SWITCH |  | 42773 | 941 | 1680647 | 1818 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 54540 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018677 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER |  | 42775 | 1345 | 1683562 | 524 | Distribution Circuit | Environmental/External | Flood/Erosion | 341 | 29789 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019480 | OH | Sus | 42939220 | 2017 | FEB | Yes | Force Out | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER |  | 42786 | 1647 | 1704369 | 782 | Distribution Circuit | Vegetation | Tree - fell into line | 341 | 58195 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023943 | OH | Sus | 0 | 2017 | FEB | Yes | None | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 42773 | 942 | 1679537 | 708 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 14160 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 17-0018462 | OH | Sus | 31304022 | 2017 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 42786 | 2029 | 1705908 | 1421 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 28420 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025078 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE |  | 42787 | 1341 | 1708768 | 349 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 5933 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025169 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
PENINSULA | Tier 2 | BERESFORD-0403 | 24040403 | JUMPER |  | 42786 | 2026 | 1705900 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4291 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024267 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | PUTAH CREEK-1102 | 63681102 | RECLOSER |  | 42788 | 2134 | 1711452 | 956 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 30897 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025868 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SAN JOSE | Tier 2 | LLAGAS-2101 | 83182101 | FUSE |  | 42773 | 736 | 1678652 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 6146 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018354 | OH | Sus | 0 | 2017 | FEB | Yes | None | Yes | No
SAN JOSE | Tier 2 | MORGAN HILL-2105 | 83242105 | OTHER |  | 42773 | 1126 | 1679934 | 664 | Distribution Circuit | Equipment Failure/Involved | Overhead | 98 | 17648 | Strong Winds-Rain-Heavy Rain-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018660 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
SAN JOSE | Tier 3 | MORGAN HILL-2111 | 83242111 | TRIP-SAVER |  | 42773 | 1723 | 1680858 | 4728 | Distribution Circuit | Environmental/External | Flood/Erosion | 63 | 297864 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018740 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | Yes
SAN JOSE | Tier 2 | MC KEE-1111 | 83531111 | FUSE |  | 42783 | 827 | 1693487 | 1969 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 11814 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023138 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 42788 | 1236 | 1710649 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1542 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025604 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-1104 | 153651104 | FUSE |  | 42773 | 735 | 1678787 | 340 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 9520 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0018358 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE |  | 42787 | 1011 | 1708200 | 912 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 7296 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025175 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | CLARKSVILLE-2104 | 153612104 | FUSE |  | 42786 | 1947 | 1705719 | 1257 | Distribution Circuit | Vegetation | Tree - fell into line | 205 | 184993 | Overcast-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0024364 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 42775 | 2320 | 1684439 | 1101 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 105696 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019741 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1111 | 153081111 | FUSE |  | 42786 | 2341 | 1706752 | 844 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 10256 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024815 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | RECLOSER |  | 42786 | 2327 | 1706706 | 1081 | Distribution Circuit | Equipment Failure/Involved | Overhead | 759 | 111751 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024784 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 42786 | 2301 | 1706611 | 1061 | Distribution Circuit | Vegetation | Tree - fell into line | 224 | 237664 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024798 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 42773 | 1229 | 1680149 | 335 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 3685 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018623 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 42786 | 2153 | 1706251 | 1777 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 56864 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024857 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 42787 | 1217 | 1708496 | 1493 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 19409 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025147 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 42786 | 1943 | 1705704 | 996 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 72708 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0024080 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 42787 | 351 | 1707321 | 2042 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 55134 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024990 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | ECHO SUMMIT-1101 | 158031101 | OTHER |  | 42788 | 1129 | 1710507 | 238 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 11186 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025542 | OH | Sus | 0 | 2017 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | ECHO SUMMIT-1101 | 158031101 | RECLOSER |  | 42775 | 2159 | 1684259 | 1239 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 59472 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019708 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | ECHO SUMMIT-1101 | 158031101 | RECLOSER |  | 42786 | 2312 | 1706647 | 3899 | Distribution Circuit | Equipment Failure/Involved | Overhead | 293 | 450134 | Overcast-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0024714 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | ECHO SUMMIT-1101 | 158031101 | FUSE |  | 42787 | 1452 | 1711171 | 4195 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 20975 | Partly Cloudy;Below 32 F | Crossarm- Wood | Broken- wire on ground | 17-0025739 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 42787 | 620 | 1707480 | 1858 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 42734 | Overcast-Fog-Rain-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025166 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | LINCOLN-1101 | 153701101 | FUSE |  | 42787 | 153 | 1707165 | 2347 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4694 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024864 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 42786 | 1924 | 1705555 | 1481 | Distribution Circuit | Equipment Failure/Involved | Overhead | 645 | 573918 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024047 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 42773 | 48 | 1677300 | 997 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 24411 | Partly Cloudy-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018042 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | FUSE |  | 42786 | 2113 | 1706118 | 1336 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 13360 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024721 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | RECLOSER |  | 42786 | 2019 | 1705858 | 1505 | Distribution Circuit | Vegetation | Tree - fell into line | 613 | 649253 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024082 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 42773 | 559 | 1678016 | 1997 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 15827 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018308 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | FUSE |  | 42787 | 142 | 1707147 | 993 | Distribution Circuit | Vegetation | Tree - fell into line | 221 | 165903 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0024841 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 42787 | 26 | 1706854 | 2503 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 120144 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025208 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 42787 | 224 | 1708238 | 1981 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8798 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025185 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1109 | 152691109 | FUSE |  | 42786 | 2205 | 1706301 | 883 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 42384 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024793 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | FUSE |  | 42773 | 613 | 1678069 | 637 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 66885 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018258 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 42787 | 1145 | 1708413 | 1648 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 19776 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025160 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 42773 | 431 | 1677779 | 2016 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 26208 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018900 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 42773 | 1548 | 1680568 | 1403 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 75762 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018698 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 42787 | 223 | 1707223 | 687 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 20307 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024881 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 42786 | 2036 | 1708834 | 2590 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 118828 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025187 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | FUSE |  | 42773 | 708 | 1678445 | 1770 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4770 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018596 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 42787 | 204 | 1707324 | 723 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 58563 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024960 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | FUSE |  | 42787 | 737 | 1707723 | 1798 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 26970 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0024972 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE |  | 42786 | 2258 | 1707124 | 1091 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 50186 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024796 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER |  | 42773 | 633 | 1678716 | 938 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 66747 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018350 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER |  | 42786 | 2310 | 1707254 | 2622 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 149454 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025005 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER |  | 42775 | 1244 | 1683408 | 229 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 229 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019423 | OH | Sus | 0 | 2017 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1104 | 152481104 | FUSE |  | 42773 | 801 | 1678913 | 1837 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 99198 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018437 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SUMMIT-1102 | 152591102 | FUSE |  | 42786 | 909 | 1702805 | 4973 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 14919 | Overcast-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0023949 | OH | Sus | 0 | 2017 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 2 | SUMMIT-1102 | 152591102 | RECLOSER |  | 42786 | 2303 | 1706446 | 2397 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 89981 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024702 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SUMMIT-1102 | 152591102 | FUSE |  | 42787 | 2308 | 1709592 | 2580 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 10320 | Overcast-Snow;Below 32 F | Conductor- Overhead | On Ground | 17-0026002 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 42787 | 150 | 1707161 | 1042 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 55226 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0025071 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | SUMMIT-1101 | 152591101 | SECTIONALIZER |  | 42786 | 2040 | 1706415 | 3965 | Distribution Circuit | Vegetation | Tree - fell into line | 238 | 505460 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024705 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SIERRA CITY DIESEL-1101 | 158011101 | RECLOSER |  | 42786 | 2006 | 1707364 | 14116 | Distribution Circuit | Vegetation | Tree - fell into line | 554 | 1789554 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025679 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER |  | 42773 | 224 | 1677412 | 721 | Distribution Circuit | Vegetation | Tree - fell into line | 182 | 81498 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018057 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 42786 | 857 | 1702782 | 483 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1449 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023734 | OH | Sus | 0 | 2017 | FEB | Yes | Force Out | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE |  | 42786 | 2247 | 1706489 | 833 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 35819 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024829 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1104 | 42271104 | FUSE |  | 42773 | 804 | 1678601 | 506 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4048 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018514 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | OTHER |  | 42773 | 1507 | 1680503 | 1453 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 4359 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018737 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | FUSE |  | 42787 | 1410 | 1708756 | 411 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 8030 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025246 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER |  | 42775 | 1216 | 1683342 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 26003 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019471 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | FUSE |  | 42773 | 303 | 1677772 | 861 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 18942 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018291 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 42786 | 2154 | 1706261 | 1004 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 16406 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024771 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE |  | 42773 | 456 | 1677976 | 1982 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3964 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018374 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 42773 | 1218 | 1680588 | 2395 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 84538 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018720 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | JUMPER |  | 42773 | 1025 | 1681962 | 1925 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 38500 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019031 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 42783 | 2125 | 1698484 | 710 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 9230 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022769 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | JUMPER |  | 42786 | 1441 | 1703543 | 371 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 9897 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023876 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 42773 | 629 | 1680184 | 950 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 16150 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018582 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 42773 | 822 | 1680191 | 733 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 25655 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018586 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE |  | 42786 | 2049 | 1705997 | 978 | Distribution Circuit | Vegetation | Tree - branch fell on line | 53 | 51834 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0024348 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE |  | 42773 | 907 | 1679369 | 4863 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 27917 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018519 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE |  | 42787 | 1724 | 1709163 | 1251 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2502 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025268 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER |  | 42784 | 135 | 1698749 | 687 | Distribution Circuit | Environmental/External | Flood/Erosion | 689 | 258198 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0022844 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | RINCON-1103 | 43321103 | OCB |  | 42775 | 1423 | 1683627 | 1100 | Distribution Circuit | Vegetation | Tree - fell into line | 458 | 419106 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0019503 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | JUMPER |  | 42773 | 817 | 1678885 | 708 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 4248 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018630 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 42786 | 2102 | 1706068 | 950 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 34200 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024718 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 42786 | 2230 | 1706267 | 731 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 73100 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024996 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER |  | 42775 | 1243 | 1683406 | 497 | Distribution Circuit | Vegetation | Tree - fell into line | 312 | 125756 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019448 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | OTHER |  | 42773 | 904 | 1679352 | 1619 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 17809 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018556 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | OTHER |  | 42787 | 116 | 1707172 | 1090 | Distribution Circuit | Vegetation | Tree - fell into line | 171 | 137031 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024937 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 42773 | 112 | 1677190 | 803 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11242 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018190 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 42773 | 309 | 1679273 | 2485 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 19172 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0018332 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 42787 | 140 | 1707245 | 729 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 19683 | Overcast-Drizzle;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 17-0024846 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 42773 | 902 | 1679630 | 786 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5502 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018420 | OH | Sus | 0 | 2017 | FEB | Yes | Force Out | Yes | No
SONOMA | Tier 3 | FULTON-1107 | 42561107 | OTHER |  | 42773 | 1417 | 1680804 | 1310 | Distribution Circuit | Vegetation | Tree - branch fell on line | 149 | 114666 | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0018723 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER |  | 42775 | 643 | 1682791 | 715 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 22165 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0019307 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 42773 | 315 | 1678975 | 2156 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 118580 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018642 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 42773 | 445 | 1679879 | 2090 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 280060 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0018486 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE |  | 42786 | 2047 | 1705953 | 2393 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 39159 | Clear;32-90 F | Conductor- Overhead | On Ground | 17-0024531 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE |  | 42786 | 732 | 1702616 | 403 | Distribution Circuit | Equipment Failure/Involved | Overhead | 236 | 95108 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0023681 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CORRAL-1101 | 162991101 | OTHER |  | 42784 | 500 | 1699005 | 1027 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 26665 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022892 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 2 | CORRAL-1103 | 162991103 | FUSE |  | 42773 | 1310 | 1680120 | 182 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 1670 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018600 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE |  | 42783 | 1916 | 1698213 | 595 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 33726 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 17-0022632 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE |  | 42786 | 2019 | 1705859 | 431 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 8118 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0024110 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE |  | 42783 | 1447 | 1696592 | 833 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 19738 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 17-0022518 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER |  | 42787 | 51 | 1707060 | 1197 | Distribution Circuit | Vegetation | Tree - fell into line | 339 | 118521 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024818 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | KERCKHOFF-1101 | 252561101 | FUSE |  | 42783 | 1742 | 1697863 | 1675 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 14793 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0022730 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2102 | 254432102 | JUMPER |  | 42786 | 1010 | 1702901 | 201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 201 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0023724 | OH | Sus | 0 | 2017 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE |  | 42773 | 1111 | 1679892 | 1618 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 17334 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018653 | OH | Sus | 31304498 | 2017 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE |  | 42773 | 404 | 1677711 | 531 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 8282 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018129 | OH | Sus | 42939896 | 2017 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2102 | 254452102 | JUMPER |  | 42783 | 1230 | 1696483 | 1753 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1753 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022326 | OH | Sus | 0 | 2017 | FEB | Yes | Open Circuit | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 42783 | 1341 | 1696056 | 1530 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 44370 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0022417 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2101 | 252192101 | RECLOSER |  | 42775 | 1728 | 1683971 | 594 | Distribution Circuit | Vegetation | Tree - fell into line | 196 | 53959 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0019623 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2101 | 252192101 | RECLOSER |  | 42783 | 927 | 1693299 | 322 | Distribution Circuit | Vegetation | Tree - fell into line | 196 | 41981 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022157 | OH | Sus | 0 | 2017 | FEB | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER |  | 42783 | 1709 | 1697621 | 1461 | Distribution Circuit | Vegetation | Tree - fell into line | 900 | 590508 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0022662 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER |  | 42786 | 1501 | 1703616 | 826 | Distribution Circuit | Vegetation | Tree - fell into line | 657 | 245117 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0023866 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MERCED FALLS-1102 | 252811102 | OCB |  | 42783 | 1648 | 1697539 | 1998 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2315 | 2188163 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0022546 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE |  | 42787 | 311 | 1707281 | 934 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 37360 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024994 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER |  | 42787 | 43 | 1706981 | 433 | Distribution Circuit | Vegetation | Tree - fell into line | 995 | 136819 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024773 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE |  | 42786 | 1418 | 1703495 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 10487 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0023882 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE |  | 42788 | 1645 | 1711109 | 1013 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5065 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025762 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | JUMPER |  | 42786 | 1828 | 1706344 | 557 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 5551 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024595 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 42783 | 1540 | 1698618 | 1526 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 13734 | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0022767 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | JUMPER |  | 42788 | 1429 | 1710873 | 246 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 492 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025713 | OH | Sus | 0 | 2017 | FEB | Yes | Open Circuit | Yes | No
YOSEMITE | Tier 2 | MIWUK-1702 | 163661702 | JUMPER |  | 42787 | 934 | 1708246 | 393 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 60858 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0025032 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 42783 | 1218 | 1695543 | 800 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 1904 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0022335 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | FUSE |  | 42786 | 1829 | 1705151 | 345 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 17250 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024077 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 42773 | 1211 | 1680090 | 681 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 18663 | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0018605 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | OTHER |  | 42786 | 1812 | 1705891 | 793 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 10309 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0024084 | OH | Sus | 0 | 2017 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | FUSE |  | 42783 | 1311 | 1695876 | 733 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 19791 | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0022408 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | FUSE |  | 42773 | 103 | 1677320 | 706 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 14874 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0018069 | OH | Sus | 31304303 | 2017 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 42783 | 1747 | 1697933 | 1293 | Distribution Circuit | Vegetation | Tree - fell into line | 290 | 319070 | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0022963 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER |  | 42786 | 1729 | 1704921 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 847 | 360667 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0024006 | OH | Sus | 0 | 2017 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 42783 | 1935 | 1698261 | 1565 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 87640 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0022774 | OH | Sus | 0 | 2017 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | JUMPER |  | 42754 | 1830 | 1651782 | 8395 | Distribution Circuit | Environmental/External | Flood/Erosion | 52 | 16696 | Clear;32-90 F | Conductor- Overhead | On Ground | 17-0011077 | OH | Sus | 31297011 | 2017 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 2 | LOS OSITOS-2103 | 182082103 | FUSE |  | 42758 | 751 | 1663095 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 8050 | Clear;32-90 F | Conductor- Overhead | On Ground | 17-0013627 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | OTHER |  | 42757 | 1305 | 1660483 | 1673 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 6692 | Overcast-Drizzle;32-90 F | Connector or Splice (OH) | Broken- wire on object | 17-0013162 | OH | Sus | 31297011 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | FUSE |  | 42757 | 717 | 1660839 | 1807 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 7228 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013103 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | RECLOSER |  | 42744 | 901 | 1630615 | 1406 | Distribution Circuit | Environmental/External | Flood/Erosion | 416 | 579980 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005966 | OH | Sus | 31293495 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | TRIP-SAVER |  | 42757 | 248 | 1660992 | 2099 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 15055 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013144 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | OTHER |  | 42738 | 1536 | 1615941 | 764 | Distribution Circuit | Equipment Failure/Involved | Overhead | 579 | 235871 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 17-0003151 | OH | Sus | 42909923 | 2017 | JAN | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | FUSE |  | 42743 | 1213 | 1626055 | 610 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 13420 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005484 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE |  | 42757 | 220 | 1660916 | 2155 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 175985 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013124 | OH | Sus | 31297011 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE |  | 42743 | 1248 | 1626423 | 212 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 636 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005379 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE |  | 42743 | 1427 | 1628029 | 884 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 16796 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005511 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | RECLOSER |  | 42757 | 346 | s1251532 | 747 | Distribution Circuit | Vegetation | Tree - branch fell on line | 292 | 41531 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012709 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 42743 | 748 | 1623241 | 372 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 1488 | Overcast-Fog-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005039 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 42745 | 1428 | 1633754 | 982 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 16798 | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0006711 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | RECLOSER |  | 42757 | 150 | 1658095 | 2376 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 195633 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012600 | OH | Sus | 31297011 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | FUSE |  | 42755 | 1407 | 1654407 | 1553 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 3106 | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011712 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | FUSE |  | 42755 | 1319 | 1653046 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 13156 | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011575 | OH | Sus | 31297011 | 2017 | JAN | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 42757 | 554 | 1659143 | 429 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4719 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012824 | OH | Sus | 42928578 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE |  | 42757 | 343 | 1660358 | 978 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 10758 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013021 | OH | Sus | 42928578 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE |  | 42758 | 302 | 1662909 | 583 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3010 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013596 | OH | Sus | 42928578 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 42757 | 325 | 1658396 | 1805 | Distribution Circuit | Vegetation | Tree - branch fell on line | 180 | 148122 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0013085 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 42743 | 1523 | 1628439 | 1481 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 62202 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005644 | OH | Sus | 31293495 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE |  | 42753 | 2047 | 1648956 | 1089 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 21780 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010570 | OH | Sus | 31297011 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | OCB |  | 42756 | 900 | 1656047 | 278 | Distribution Circuit | 3rd Party | Vehicle | 6011 | 190342 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011934 | OH | Sus | 31297517 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 42757 | 657 | 1659369 | 256 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 4864 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | On Ground | 17-0013005 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 42755 | 528 | 1652469 | 725 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 36250 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011593 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE |  | 42753 | 1959 | 1648748 | 899 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 32442 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010494 | OH | Sus | 42928578 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 42757 | 654 | 1659355 | 1711 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 32509 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0013721 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 42755 | 544 | 1652565 | 1830 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 18300 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011627 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE |  | 42753 | 2047 | 1648948 | 244 | Distribution Circuit | Vegetation | Tree - branch fell on line | 47 | 11468 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010572 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE |  | 42755 | 1219 | 1654154 | 1545 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 21630 | Overcast-Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 17-0012016 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE |  | 42743 | 1508 | 1627637 | 1707 | Distribution Circuit | Equipment Failure/Involved | Overhead | 163 | 54934 | Overcast-Rain;32-90 F | Conductor- Overhead | On Ground | 17-0005642 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE |  | 42746 | 333 | 1638560 | 625 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 54375 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007431 | OH | Sus | 42912765 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE |  | 42755 | 1521 | 1654559 | 1849 | Distribution Circuit | Vegetation | Tree - fell into line | 103 | 35761 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011721 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN JUSTO-1101 | 183181101 | FUSE |  | 42745 | 1628 | 1634348 | 1077 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 4535 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006910 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | OTHER |  | 42757 | 626 | 1659254 | 2069 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 41425 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012952 | OH | Sus | 31297427 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | GREEN VALLEY-2101 | 83192101 | JUMPER |  | 42755 | 1053 | 1653789 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3386 | Partly Cloudy-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011510 | OH | Sus | 31297127 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER |  | 42755 | 1507 | 1654535 | 853 | Distribution Circuit | Vegetation | Tree - fell into line | 431 | 75682 | Overcast-Drizzle;32-90 F | Conductor- Overhead | On Ground | 17-0011658 | OH | Sus | 31297127 | 2017 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 42743 | 942 | 1624468 | 4458 | Distribution Circuit | Vegetation | Tree - fell into line | 262 | 726569 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0005192 | OH | Sus | 31294181 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 42757 | 1935 | 1662215 | 1865 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 26655 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013543 | OH | Sus | 31297127 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 42746 | 254 | 1638817 | 2081 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12486 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007507 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | RECLOSER |  | 42745 | 1442 | 1633797 | 1708 | Distribution Circuit | Vegetation | Tree - fell into line | 430 | 223903 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006697 | OH | Sus | 31294181 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | PAUL SWEET-2109 | 83252109 | RECLOSER |  | 42757 | 1957 | 1662249 | 853 | Distribution Circuit | Vegetation | Tree - fell into line | 212 | 172388 | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on object | 17-0013395 | OH | Sus | 31297127 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | OTHER |  | 42743 | 635 | 1622784 | 524 | Distribution Circuit | Vegetation | Tree - fell into line | 292 | 78433 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0004936 | OH | Sus | 42912765 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | PAUL SWEET-2106 | 83252106 | FUSE |  | 42756 | 640 | 1655700 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 38296 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011921 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 42743 | 1850 | 1628154 | 1782 | Distribution Circuit | Vegetation | Tree - fell into line | 144 | 255358 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005768 | OH | Sus | 31294181 | 2017 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 42753 | 2030 | 1648889 | 1284 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 33384 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010554 | OH | Sus | 31297127 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 42743 | 940 | 1624286 | 361 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 5054 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005163 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 42744 | 332 | 1630264 | 2518 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 148562 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005898 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 42745 | 1731 | 1634710 | 2944 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 11776 | Overcast-Heavy Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 17-0006906 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 42757 | 511 | 1658973 | 790 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 56090 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013194 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 42757 | 533 | 1659036 | 708 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 21471 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013280 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 42758 | 1109 | 1663741 | 3156 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 80508 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013798 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 42738 | 2303 | 1617210 | 2395 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 15274 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003363 | OH | Sus | 31292865 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 42755 | 1855 | 1655040 | 2745 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 19215 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013129 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 42756 | 912 | 1656099 | 3274 | Distribution Circuit | Vegetation | Tree - fell into line | 266 | 105470 | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 17-0011931 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 42746 | 1627 | 1640341 | 1394 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 16728 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007938 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 42745 | 1956 | 1638665 | 1174 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 24654 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007411 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 42744 | 1240 | 1631241 | 460 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 460 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006258 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | OTHER |  | 42743 | 1919 | 1628824 | 2888 | Distribution Circuit | Vegetation | Tree - fell into line | 335 | 98368 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005628 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 42746 | 2357 | 1640886 | 2305 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 15995 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0008264 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 42743 | 2027 | 1629067 | 2493 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 32409 | Clear;32-90 F | Conductor- Overhead | On Ground | 17-0005774 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 42745 | 1822 | 1635359 | 1278 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 21726 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007363 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 42757 | 1222 | 1660882 | 1392 | Distribution Circuit | Vegetation | Tree - fell into line | 145 | 76914 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013142 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | JUMPER |  | 42755 | 724 | 1652973 | 3450 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7912 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011405 | OH | Sus | 31297127 | 2017 | JAN | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 42743 | 1100 | 1626288 | 1648 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 6592 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005269 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 42757 | 732 | 1660089 | 1693 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 93087 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013074 | OH | Sus | 42928924 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 42753 | 1922 | 1648649 | 1103 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 58322 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010455 | OH | Sus | 31297127 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE |  | 42745 | 1926 | 1636215 | 1194 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 108654 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007302 | OH | Sus | 42912765 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE |  | 42755 | 1315 | 1654294 | 1455 | Distribution Circuit | Equipment Failure/Involved | Overhead | 91 | 15651 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011629 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE |  | 42738 | 2141 | 1616979 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 9310 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003318 | OH | Sus | 42909935 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42745 | 2105 | 1637179 | 1155 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 60500 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0007266 | OH | Sus | 31294181 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | TRIP-SAVER |  | 42745 | 1442 | 1633788 | 1300 | Distribution Circuit | Vegetation | Tree - branch fell on line | 98 | 119344 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007445 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 42743 | 902 | 1623885 | 2465 | Distribution Circuit | Vegetation | Tree - fell into line | 1634 | 308579 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005068 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | OTHER |  | 42743 | 941 | 1624296 | 1887 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 18523 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005428 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | JUMPER |  | 42757 | 204 | 1658252 | 609 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 10353 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012721 | OH | Sus | 31297127 | 2017 | JAN | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42757 | 546 | 1659121 | 1904 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3808 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | On Ground | 17-0013656 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 42757 | 511 | 1658985 | 2074 | Distribution Circuit | Vegetation | Tree - fell into line | 178 | 42876 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0012789 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE |  | 42757 | 557 | 1659272 | 1748 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 7052 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013271 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42743 | 1504 | 1627581 | 2485 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 57155 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005600 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE |  | 42744 | 1833 | 1632070 | 1122 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3366 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006272 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 42753 | 1814 | 1649117 | 1202 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 8414 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010460 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 42743 | 1635 | 1628065 | 1828 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 10968 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005569 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 42743 | 709 | 1622950 | 444 | Distribution Circuit | Equipment Failure/Involved | Overhead | 617 | 57692 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0004994 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42738 | 1012 | 1615612 | 96 | Distribution Circuit | Vegetation | Tree - fell into line | 2034 | 147983 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0002955 | OH | Sus | 42908763 | 2017 | JAN | Yes | Three Phase Fault | Yes | Yes
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 42738 | 2247 | 1617172 | 1153 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 61170 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003317 | OH | Sus | 31292865 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | RECLOSER |  | 42743 | 1205 | 1626008 | 148 | Distribution Circuit | Vegetation | Tree - fell into line | 534 | 78536 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0004989 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42745 | 2355 | 1638151 | 2160 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 17280 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007701 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42743 | 1732 | 1628395 | 1588 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 25556 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005622 | OH | Sus | 31294181 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42743 | 1851 | 1629523 | 1228 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 23332 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005736 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE |  | 42758 | 930 | 1663437 | 1720 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 3440 | Clear;32-90 F | Footings- Tower or Pole | Broken- wire on object | 17-0013857 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42743 | 200 | 1622468 | 870 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 14370 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0004900 | OH | Sus | 31294181 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42745 | 1909 | 1635973 | 2555 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 7665 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007737 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42757 | 538 | 1659120 | 1942 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5826 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013302 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 42743 | 834 | 1623735 | 1721 | Distribution Circuit | Vegetation | Tree - fell into line | 136 | 168352 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005021 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE |  | 42753 | 1951 | 1648711 | 989 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 6923 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010486 | OH | Sus | 31297127 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE |  | 42755 | 553 | 1652605 | 1984 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 13888 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011558 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42746 | 2059 | s1247764 | 1295 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1295 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0008346 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 42755 | 1531 | 1654594 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 6062 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011668 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER |  | 42743 | 1625 | 1629940 | 3075 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12300 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005828 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | SECTIONALIZER |  | 42744 | 524 | 1630158 | 1935 | Distribution Circuit | Vegetation | Tree - fell into line | 1896 | 163482 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005875 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 42745 | 2325 | 1638064 | 2315 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 57579 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007254 | OH | Sus | 31294181 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42757 | 1100 | 1660485 | 3015 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12060 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013343 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | RECLOSER |  | 42743 | 2249 | 1629739 | 2528 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 86560 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005772 | OH | Sus | 31294181 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42755 | 1115 | 1653882 | 1405 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1405 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 17-0011563 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER |  | 42755 | 1124 | 1653992 | 476 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2380 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011711 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER |  | 42745 | 837 | 1632698 | 578 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 578 | Strong Winds-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006659 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 42756 | 1644 | 1656979 | 1189 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 14482 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012166 | OH | Sus | 31297127 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 42743 | 1003 | 1624565 | 7247 | Distribution Circuit | Environmental/External | Flood/Erosion | 64 | 474176 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0005274 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 42756 | 2020 | 1657228 | 1061 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 12732 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012315 | OH | Sus | 31297127 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | JUMPER |  | 42743 | 10 | 1622372 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 7308 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0004890 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 42757 | 317 | 1658375 | 4998 | Distribution Circuit | Environmental/External | Flood/Erosion | 522 | 970726 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | On Ground | 17-0012713 | OH | Sus | 42928924 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42745 | 1939 | 1638919 | 1301 | Distribution Circuit | Vegetation | Tree - fell into line | 382 | 164745 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007433 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER |  | 42743 | 1600 | 1630333 | 2925 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 90675 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005943 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 42758 | 2215 | 1665069 | 1019 | Distribution Circuit | Environmental/External | Flood/Erosion | 1009 | 151850 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0014213 | OH | Sus | 31297127 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 42757 | 546 | 1659127 | 1765 | Distribution Circuit | Vegetation | Tree - fell into line | 1079 | 87210 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012819 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE |  | 42743 | 1807 | 1628522 | 2033 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 14231 | Overcast-Rain;32-90 F | Conductor- Overhead | On Ground | 17-0006347 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER |  | 42758 | 1011 | 1663596 | 1866 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 77148 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013809 | OH | Sus | 31297127 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER |  | 42745 | 1933 | 1640082 | 2731 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 140889 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007742 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42755 | 941 | 1653546 | 1715 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 10290 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011650 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER |  | 42746 | 656 | 1639979 | 2086 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 6258 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007828 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 42745 | 1646 | 1634493 | 1485 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7425 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007608 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 42755 | 1035 | 1653756 | 1747 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 15723 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011631 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER |  | 42744 | 1211 | 1631729 | 4651 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 13953 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006226 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 42758 | 1108 | 1663734 | 202 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 1616 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0013748 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | JUMPER |  | 42743 | 935 | 1627443 | 1530 | Distribution Circuit | Vegetation | Tree - branch fell on line | 137 | 47202 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005411 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 42745 | 2046 | 1637013 | 985 | Distribution Circuit | Vegetation | Tree - fell into line | 636 | 565128 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0007048 | OH | Sus | 31294181 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 42744 | 1609 | 1631724 | 1294 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 37526 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006517 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER |  | 42743 | 1603 | 1630335 | 2962 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 167071 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0005912 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN SUB | 8284 | OCB |  | 42743 | 650 | 1622844 | 3315 | Distribution Circuit | Vegetation | Tree - fell into line | 2942 | 3680039 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0004942 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 42744 | 1852 | 1632090 | 923 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 30459 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006443 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 42755 | 805 | 1653163 | 1688 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 13504 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011441 | OH | Sus | 31297127 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 42756 | 1959 | 1657227 | 4016 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 156718 | Strong Winds-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012506 | OH | Sus | 42928924 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 42743 | 741 | s1245139 | 2129 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 117095 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005350 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 42757 | 1057 | 1660473 | 193 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 965 | Overcast-Drizzle;32-90 F | Conductor- Overhead | On Ground | 17-0013047 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 42743 | 956 | 1624575 | 1730 | Distribution Circuit | Vegetation | Tree - fell into line | 240 | 195317 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005095 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 42743 | 650 | 1625134 | 4839 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4839 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0005147 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 42755 | 1513 | 1654540 | 1287 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 64350 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0011739 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER |  | 42743 | 811 | 1629928 | 4768 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 16784 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005852 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER |  | 42756 | 1035 | 1656282 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 1640 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012093 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 42745 | 2047 | 1636280 | 1242 | Distribution Circuit | Vegetation | Tree - fell into line | 687 | 261630 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007046 | OH | Sus | 31294181 | 2017 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 42746 | 1933 | 1640692 | 1182 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 14736 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007937 | OH | Sus | 31294181 | 2017 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 42746 | 233 | 1638504 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1024 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007359 | OH | Sus | 31294181 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 42744 | 915 | 1630649 | 1845 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5535 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005975 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 42758 | 408 | 1662752 | 937 | Distribution Circuit | Vegetation | Tree - branch fell on line | 71 | 61407 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013603 | OH | Sus | 31297030 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 42745 | 1328 | 1633397 | 3142 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 95536 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006882 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | JUMPER |  | 42746 | 856 | 1639138 | 3289 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 16445 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007514 | OH | Sus | 31294278 | 2017 | JAN | Yes | Force Out | Yes | Yes
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER |  | 42745 | 1028 | 1632615 | 2661 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 7626 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0006519 | OH | Sus | 31294361 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 42743 | 1318 | 1627251 | 1197 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 34713 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005385 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 42745 | 27 | 1632419 | 852 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 8470 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006382 | OH | Sus | 31294278 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH |  | 42745 | 1954 | 1636576 | 4017 | Distribution Circuit | Vegetation | Tree - fell into line | 469 | 208453 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007001 | OH | Sus | 31294278 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 42745 | 1040 | 1632952 | 412 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1236 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006576 | OH | Sus | 42913015 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 42738 | 1547 | 1615982 | 660 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 26457 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003164 | OH | Sus | 42909755 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 42757 | 1127 | 1660580 | 3234 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 19404 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013294 | OH | Sus | 31297030 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 42744 | 1529 | 1631634 | 4281 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 10369 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006375 | OH | Sus | 31294361 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER |  | 42743 | 1842 | 1627933 | 1149 | Distribution Circuit | Vegetation | Tree - fell into line | 843 | 919162 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005604 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 42745 | 2046 | 1637006 | 4293 | Distribution Circuit | Environmental/External | Flood/Erosion | 104 | 446472 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007211 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | STELLING-1110 | 83481110 | FUSE |  | 42755 | 1210 | 1654124 | 3401 | Distribution Circuit | Environmental/External | Flood/Erosion | 31 | 25753 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011564 | OH | Sus | 31297028 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 42757 | 2317 | 1662576 | 890 | Distribution Circuit | Environmental/External | Flood/Erosion | 20 | 17800 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013552 | OH | Sus | 42928670 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE |  | 42738 | 40 | 1615236 | 787 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 30724 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0002877 | OH | Sus | 31292530 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | SARATOGA-1106 | 83371106 | FUSE |  | 42745 | 1545 | 1634134 | 1509 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 60903 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006848 | OH | Sus | 31294278 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
DE ANZA | Tier 2 | SARATOGA-1106 | 83371106 | FUSE |  | 42746 | 913 | 1639242 | 1664 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 99102 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007560 | OH | Sus | 42913015 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE |  | 42745 | 1448 | 1634151 | 1717 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 25755 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006782 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | JUMPER |  | 42738 | 2130 | 1616948 | 1280 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1280 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003333 | OH | Sus | 42909755 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | OTHER |  | 42743 | 1018 | 1624830 | 1922 | Distribution Circuit | Vegetation | Tree - fell into line | 494 | 174739 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005263 | OH | Sus | 31294278 | 2017 | JAN | Yes | Force Out | Yes | Yes
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE |  | 42757 | 716 | 1659461 | 2384 | Distribution Circuit | Environmental/External | Flood/Erosion | 9 | 21456 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012915 | OH | Sus | 31297028 | 2017 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE |  | 42744 | 2002 | 1632193 | 4058 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 36522 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006326 | OH | Sus | 31294278 | 2017 | JAN | Yes | Line to Line | Yes | No
DE ANZA | Tier 2 | STELLING-1110 | 83481110 | OTHER |  | 42743 | 42 | 1622449 | 643 | Distribution Circuit | Vegetation | Tree - branch fell on line | 63 | 6018 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0004885 | OH | Sus | 42913015 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
DIABLO | Tier 3 | MORAGA-1105 | 13801105 | FUSE |  | 42743 | 654 | 1622872 | 1809 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 4905 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005423 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
DIABLO | Tier 2 | MORAGA-1104 | 13801104 | OCB |  | 42743 | 1145 | 1625793 | 908 | Distribution Circuit | Vegetation | Tree - fell into line | 1708 | 706554 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0005237 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
DIABLO | Tier 3 | CLAYTON-2212 | 12022212 | FUSE |  | 42743 | 649 | 1625435 | 674 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 10110 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005186 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
DIABLO | Tier 3 | CLAYTON-2212 | 12022212 | FUSE |  | 42745 | 1831 | 1639207 | 1835 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 27525 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0008230 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | LAS AROMAS-0401 | 13600401 | RECLOSER |  | 42745 | 1215 | 1633185 | 866 | Distribution Circuit | Vegetation | Tree - fell into line | 174 | 61530 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006571 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
DIABLO | Tier 2 | ROSSMOOR-1101 | 14161101 | SECTIONALIZER |  | 42738 | 2149 | 1617025 | 549 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1079 | 68015 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003314 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | ALHAMBRA-1105 | 14101105 | FUSE |  | 42757 | 1037 | 1659787 | 550 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 3275 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0013028 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | Yes
EAST BAY | Tier 2 | SAN LEANDRO-1109 | 13111109 | FUSE |  | 42743 | 957 | 1624525 | 353 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 6707 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005230 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 2 | OAKLAND J-1102 | 12091102 | FUSE |  | 42745 | 1317 | 1633358 | 919 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 42274 | Heavy Rain-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006655 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAKLAND X-1106 | 12541106 | FUSE |  | 42746 | 19 | 1638166 | 1195 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 10755 | Overcast-Fog-Rain-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007370 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAKLAND X-1106 | 12541106 | FUSE |  | 42758 | 433 | 1662783 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 10875 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013605 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | FUSE |  | 42745 | 1228 | 1633278 | 1006 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 14084 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0006634 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE |  | 42745 | 1623 | 1634295 | 1138 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 39830 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006860 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAKLAND K-1103 | 12101103 | FUSE |  | 42745 | 1334 | 1633406 | 366 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 8784 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006685 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1102 | 12101102 | FUSE |  | 42743 | 1041 | 1625023 | 1579 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 93062 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005216 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | EL CERRITO G-1105 | 12501105 | RECLOSER |  | 42743 | 1544 | 1627794 | 1481 | Distribution Circuit | Vegetation | Tree - fell into line | 2152 | 143997 | Overcast-Rain;32-90 F | Conductor- Overhead | On Ground | 17-0005469 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
FRESNO | Tier 2 | SAND CREEK-1103 | 254601103 | FUSE |  | 42756 | 101 | 1655384 | 481 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 40885 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0011886 | OH | Sus | 42930433 | 2017 | JAN | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | SWITCH |  | 42757 | 1453 | 1661368 | 123 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 7995 | Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0012500 | OH | Sus | 42930533 | 2017 | JAN | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | FUSE |  | 42758 | 1620 | 1664590 | 1232 | Distribution Circuit | Environmental/External | Ice or snow | 61 | 75152 | Overcast;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0013043 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER |  | 42746 | 20 | 1638345 | 854 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 240828 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007485 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
FRESNO | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER |  | 42757 | 1048 | 1660448 | 1494 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 413458 | Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0013043 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
FRESNO | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER |  | 42755 | 1825 | 1653783 | 1523 | Distribution Circuit | Vegetation | Tree - branch fell on line | 282 | 426086 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0011753 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
FRESNO | Tier 2 | AUBERRY-1101 | 254151101 | RECLOSER |  | 42757 | 1140 | 1660681 | 204 | Distribution Circuit | Vegetation | Tree - fell into line | 421 | 43624 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013127 | OH | Sus | 42930604 | 2017 | JAN | Yes | Line to Ground | Yes | No
FRESNO | Tier 3 | AUBERRY-1101 | 254151101 | FUSE |  | 42757 | 427 | 1658745 | 1938 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 6971 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013060 | OH | Sus | 31297701 | 2017 | JAN | Yes | Line to Ground | Yes | No
FRESNO | Tier 3 | AUBERRY-1101 | 254151101 | FUSE |  | 42758 | 1715 | 1664724 | 155 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 310 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0013985 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | JUMPER |  | 42753 | 1643 | 1647122 | 1570 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7805 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010184 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | RECLOSER |  | 42745 | 1730 | 1634723 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 171 | 191436 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007513 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER |  | 42756 | 2151 | 1657406 | 1192 | Distribution Circuit | Vegetation | Tree - branch fell on line | 317 | 286999 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0012530 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | OTHER |  | 42743 | 1022 | 1625185 | 1708 | Distribution Circuit | Vegetation | Tree - fell into line | 408 | 657236 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005226 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 42757 | 736 | 1659534 | 654 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2616 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013117 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | JUMPER |  | 42743 | 1427 | 1627324 | 4293 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4293 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005452 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 42743 | 921 | 1624138 | 4839 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5289 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005127 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 42746 | 1520 | 1640218 | 28 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 112 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007780 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 42756 | 2316 | 1657750 | 947 | Distribution Circuit | Vegetation | Tree - branch fell on line | 54 | 36615 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012978 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 42757 | 744 | 1659576 | 374 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 6358 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013134 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | Yes
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 42743 | 1037 | 1624980 | 3171 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 19026 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005299 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 42753 | 1154 | 1646083 | 326 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 652 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0009905 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | OTHER |  | 42743 | 1708 | 1628373 | 1104 | Distribution Circuit | Vegetation | Tree - fell into line | 304 | 328917 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005602 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER |  | 42743 | 754 | 1623559 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 302 | 32722 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005055 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER |  | 42738 | 2232 | 1617141 | 916 | Distribution Circuit | Vegetation | Tree - fell into line | 302 | 52372 | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0003334 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | JUMPER |  | 42754 | 956 | 1650538 | 404 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 13453 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010867 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | RECLOSER |  | 42743 | 452 | 1622539 | 844 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 21100 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005038 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | RECLOSER |  | 42753 | 1254 | 1646194 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 24864 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010007 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 42757 | 1154 | 1660722 | 1492 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8952 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0013189 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | OTHER |  | 42743 | 1034 | 1625492 | 1934 | Distribution Circuit | Vegetation | Tree - fell into line | 762 | 169590 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005356 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | Yes
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | JUMPER |  | 42743 | 920 | 1624135 | 2981 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 8943 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005416 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE |  | 42744 | 1556 | 1631690 | 2837 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 28370 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006219 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 42753 | 1047 | 1646050 | 1473 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2946 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0009930 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | RECLOSER |  | 42757 | 205 | 1658149 | 546 | Distribution Circuit | Equipment Failure/Involved | Overhead | 217 | 118482 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0012794 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 42743 | 949 | 1624384 | 5826 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 5826 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0008416 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 42743 | 524 | 1622556 | 2018 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 10090 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005092 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 42757 | 1041 | 1660436 | 1540 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 12320 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013057 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LUCERNE-1106 | 43351106 | RECLOSER |  | 42745 | 1224 | 1633199 | 666 | Distribution Circuit | Vegetation | Tree - fell into line | 259 | 17964 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006612 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | RECLOSER |  | 42746 | 1520 | 1640169 | 1515 | Distribution Circuit | Vegetation | Tree - branch fell on line | 243 | 18939 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 17-0007819 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LUCERNE-1106 | 43351106 | FUSE |  | 42746 | 105 | 1638293 | 1090 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 57882 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007389 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LUCERNE-1106 | 43351106 | FUSE |  | 42744 | 813 | 1630342 | 1593 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4779 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005930 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE |  | 42753 | 1541 | 1646802 | 1170 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 15210 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010236 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE |  | 42745 | 800 | 1632630 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7566 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006516 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE |  | 42743 | 923 | 1624170 | 2081 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 45782 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005156 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | SWITCH |  | 42744 | 959 | 1630771 | 1831 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9155 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006116 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | FUSE |  | 42744 | 1209 | 1631170 | 1481 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5924 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006166 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | FUSE |  | 42743 | 1011 | 1625129 | 1863 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 44712 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0006107 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | SWITCH |  | 42743 | 1645 | 1627779 | 2655 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 76995 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005547 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LUCERNE-1103 | 43351103 | TRIP-SAVER |  | 42753 | 1327 | s1249172 | 193 | Distribution Circuit | Equipment Failure/Involved | Overhead | 85 | 16405 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010039 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER |  | 42743 | 1043 | 1625132 | 3060 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 278301 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005459 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER |  | 42745 | 1839 | 1635588 | 1511 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 111625 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006956 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42743 | 1426 | 1627318 | 2877 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5754 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005393 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE |  | 42757 | 1204 | 1660776 | 196 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 1960 | Overcast;Below 32 F | Conductor- Overhead | Broken- wire on object | 17-0013094 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | OTHER |  | 42744 | 3 | 1631738 | 3902 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10813 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006228 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42746 | 805 | 1638984 | 624 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5616 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007543 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | JUMPER |  | 42743 | 1211 | 1631719 | 4683 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4683 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006223 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42743 | 804 | 1628114 | 4741 | Distribution Circuit | Equipment Failure/Involved | Overhead | 194 | 373423 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0005521 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42753 | 1501 | 1646586 | 1256 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6280 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010227 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42744 | 1412 | 1631461 | 1487 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 60967 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0006162 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 42746 | 29 | 1638185 | 1111 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 45551 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007483 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42744 | 1638 | 1632115 | 1649 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3298 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006281 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42743 | 910 | 1626791 | 2093 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 102557 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005320 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42744 | 2029 | 1635771 | 2559 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 115155 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006922 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42743 | 758 | 1629882 | 3616 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 47008 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005813 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER |  | 42744 | 1633 | 1631858 | 1111 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 135542 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006290 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42745 | 449 | 1632488 | 845 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 14365 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006581 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42743 | 633 | 1624724 | 4502 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 81036 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005099 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER |  | 42743 | 633 | 1622773 | 2228 | Distribution Circuit | Vegetation | Tree - fell into line | 328 | 751702 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0004982 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42743 | 630 | 1623848 | 4666 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 32662 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005035 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42744 | 2031 | 1632509 | 1146 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 69906 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006466 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | JUMPER |  | 42743 | 633 | 1632081 | 4850 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 14550 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006277 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42744 | 1656 | 1632051 | 3060 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 52020 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006269 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42754 | 253 | 1649783 | 682 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 11594 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010660 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 42745 | 805 | 1632657 | 2185 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 34960 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0006521 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 42753 | 1217 | 1646119 | 1755 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 27209 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0009995 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42743 | 543 | 1622949 | 3482 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 141424 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0004949 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42743 | 752 | 1629170 | 2963 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 174817 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005679 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42738 | 1959 | 1616676 | 460 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 27140 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | On Ground | 17-0003288 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42743 | 810 | 1633163 | 3311 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 16555 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0004949 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42743 | 850 | 1633166 | 3315 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 13260 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0004949 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | JUMPER |  | 42757 | 914 | 1660366 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2272 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013022 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42743 | 850 | 1633168 | 3400 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 23800 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0004949 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42743 | 754 | 1623345 | 2376 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 21384 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005676 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42743 | 959 | 1624699 | 1691 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 40584 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006089 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42743 | 850 | 1633172 | 3430 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10290 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0004949 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42757 | 712 | 1659444 | 421 | Distribution Circuit | Vegetation | Tree - fell into line | 145 | 21229 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012951 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42743 | 850 | 1633178 | 4511 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 9022 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0004949 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42743 | 904 | 1627222 | 2082 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 52050 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005378 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42744 | 1014 | 1630823 | 2294 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4588 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006183 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | JUMPER |  | 42745 | 948 | 1632845 | 1874 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 7496 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006493 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 42755 | 724 | 1653014 | 312 | Distribution Circuit | Vegetation | Tree - fell into line | 251 | 78312 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011322 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42743 | 959 | 1624538 | 4660 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 27960 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007706 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42743 | 733 | 1630767 | 4977 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 19908 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006009 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | JUMPER |  | 42745 | 2114 | 1637989 | 1266 | Distribution Circuit | Vegetation | Tree - fell into line | 128 | 5173 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0007238 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | SWITCH |  | 42746 | 2319 | 1640874 | 789 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 39450 | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0008241 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | SWITCH |  | 42743 | 752 | 1628133 | 2174 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 104352 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005525 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER |  | 42756 | 2320 | 1657760 | 2170 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 121680 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012563 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42745 | 1702 | 1634566 | 85 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 850 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006836 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42743 | 752 | 1629027 | 3293 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 125134 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005731 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | JUMPER |  | 42743 | 2029 | 1630364 | 2671 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2671 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005906 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42743 | 2029 | 1630596 | 1505 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 18060 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005953 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42743 | 752 | 1625350 | 740 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 17760 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005181 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 42744 | 913 | 1630647 | 2155 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 53710 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005974 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 42745 | 1051 | 1633702 | 1786 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 28576 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006726 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 42743 | 1110 | 1627166 | 3565 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 14260 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005366 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 42743 | 1038 | 1627181 | 3509 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10527 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005370 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE |  | 42757 | 151 | 1658097 | 705 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 3525 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012601 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 42743 | 833 | 1623560 | 4487 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 21980 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005184 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 42758 | 845 | 1663288 | 423 | Distribution Circuit | Vegetation | Tree - branch fell on line | 93 | 32239 | Clear;32-90 F | Insulator | Broken- wire on ground | 17-0013701 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 42738 | 23 | 1615253 | 979 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 98096 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0002897 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 42746 | 1701 | 1640399 | 89 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 178 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007840 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 42745 | 1725 | 1634687 | 1733 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2714 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007231 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | JUMPER |  | 42758 | 845 | 1664091 | 555 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 555 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013827 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 42743 | 835 | 1628402 | 2294 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 22940 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005554 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER |  | 42745 | 1348 | 1633520 | 1900 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 122926 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0006682 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 42745 | 1515 | 1633970 | 1251 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 18765 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0006810 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 42744 | 1330 | 1639668 | 3101 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6202 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007604 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | JUMPER |  | 42753 | 1425 | s1249472 | 388 | Distribution Circuit | Vegetation | Tree - fell into line | 177 | 68466 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010088 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 42745 | 1512 | 1633956 | 1784 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3568 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006994 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 42743 | 1223 | 1626168 | 1627 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 42302 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005310 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 42743 | 931 | 1624355 | 1895 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 75800 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005173 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 42743 | 930 | 1624230 | 672 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 47712 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005260 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 42746 | 1319 | 1639605 | 1608 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 10800 | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0007725 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 42746 | 1233 | 1639774 | 1668 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 11676 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0008438 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 42746 | 849 | 1639110 | 1658 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1658 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007778 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 42743 | 922 | 1634625 | 4883 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 24415 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006842 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 42757 | 133 | 1658053 | 1967 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 57043 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012937 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 42746 | 1005 | 1639395 | 1551 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 9306 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007652 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 42746 | 1120 | 1639677 | 340 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1360 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007609 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 42743 | 716 | 1627314 | 2116 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 12696 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005392 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 42753 | 1419 | 1648814 | 1646 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 8230 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010411 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER |  | 42743 | 716 | 1623071 | 3397 | Distribution Circuit | Vegetation | Tree - fell into line | 248 | 532194 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0004963 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER |  | 42753 | 1428 | 1646451 | 1851 | Distribution Circuit | Vegetation | Tree - fell into line | 117 | 132061 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010015 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | JUMPER |  | 42743 | 717 | s1246410 | 4743 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 18309 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006824 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 42743 | 717 | 1626362 | 2238 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 11190 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0005277 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER |  | 42743 | 1107 | 1625380 | 5854 | Distribution Circuit | Vegetation | Tree - fell into line | 321 | 296992 | Overcast-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0005395 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 42743 | 746 | 1628478 | 1900 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 74100 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005572 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 42743 | 746 | 1628465 | 4899 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4899 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005565 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER |  | 42758 | 750 | 1663109 | 507 | Distribution Circuit | Vegetation | Tree - branch fell on line | 117 | 64904 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013631 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE |  | 42738 | 1106 | 1615658 | 3194 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12776 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003620 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE |  | 42756 | 1200 | 1656548 | 1776 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1776 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012042 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE |  | 42755 | 808 | 1653293 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 24477 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011511 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 42743 | 905 | 1634644 | 4647 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 88293 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006845 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 42738 | 719 | 1615363 | 1181 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 11810 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0002980 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 42743 | 716 | 1627478 | 6253 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 68783 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005420 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 42745 | 1136 | 1633088 | 1868 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 13076 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006555 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 42743 | 905 | 1626914 | 4760 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 9520 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005334 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | FUSE |  | 42756 | 730 | 1655765 | 645 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 14 | 9030 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012120 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 42756 | 54 | 1655381 | 603 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 9045 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011880 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 42743 | 942 | 1630783 | 4427 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 203642 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006014 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 42755 | 749 | 1652023 | 362 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 724 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011329 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER |  | 42743 | 905 | 1624053 | 4792 | Distribution Circuit | Vegetation | Tree - branch fell on line | 579 | 758109 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005153 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER |  | 42753 | 1458 | 1646619 | 1532 | Distribution Circuit | Vegetation | Tree - branch fell on line | 565 | 62542 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010049 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 42743 | 1247 | 1626410 | 4393 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 52716 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007672 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER |  | 42743 | 851 | 1623842 | 1497 | Distribution Circuit | Equipment Failure/Involved | Overhead | 66 | 98802 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005236 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER |  | 42757 | 646 | 1659328 | 2133 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 123714 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012851 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER |  | 42756 | 333 | 1655460 | 827 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 41570 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 17-0011878 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | OTHER |  | 42744 | 1002 | 1630946 | 3704 | Distribution Circuit | Vegetation | Tree - fell into line | 221 | 222140 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006207 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | FUSE |  | 42743 | 924 | 1627686 | 4592 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4592 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005446 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | FUSE |  | 42744 | 1926 | 1632134 | 2422 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2422 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006506 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER |  | 42743 | 919 | 1626741 | 4835 | Distribution Circuit | Environmental/External | Water | 324 | 1130611 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0005307 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | BRIDGEVILLE-1102 | 192461102 | FUSE |  | 42758 | 1204 | 1663955 | 649 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 649 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0013845 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | BRIDGEVILLE-1102 | 192461102 | FUSE |  | 42753 | 1140 | 1646052 | 265 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 530 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010058 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER |  | 42744 | 2215 | 1632328 | 2570 | Distribution Circuit | Vegetation | Tree - fell into line | 416 | 626894 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006339 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | FUSE |  | 42756 | 928 | 1656470 | 246 | Distribution Circuit | Environmental/External | Ice or snow | 72 | 17712 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012000 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | RECLOSER |  | 42743 | 1006 | 1625400 | 3324 | Distribution Circuit | Vegetation | Tree - fell into line | 399 | 164480 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0005481 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | FUSE |  | 42745 | 2310 | 1635202 | 879 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3516 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007252 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE |  | 42743 | 852 | 1623812 | 3054 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 33594 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006463 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE |  | 42753 | 1908 | 1648406 | 901 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 21624 | Partly Cloudy-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010541 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | NEWBURG-1133 | 192151133 | FUSE |  | 42757 | 2223 | 1662544 | 692 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3460 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013525 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | HARRIS-1109 | 192431109 | FUSE |  | 42757 | 1343 | 1661587 | 168 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 2856 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013256 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | SWITCH |  | 42753 | 415 | 1645681 | 986 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 69074 | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0009722 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1121 | 192021121 | FUSE |  | 42744 | 125 | 1630127 | 510 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 33150 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005890 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 42738 | 1650 | 1618816 | 4136 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 62040 | Clear-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0003770 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER |  | 42738 | 1956 | 1616675 | 2126 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 99922 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003223 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 42738 | 1417 | 1618586 | 4463 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 17852 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0003705 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 42738 | 2001 | 1618353 | 2686 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 75208 | Clear-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0003607 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | JUMPER |  | 42738 | 1853 | 1618674 | 2924 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 55556 | Clear-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0003735 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 42738 | 1914 | 1618290 | 2790 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 181350 | Clear-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0003576 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1101 | 192171101 | JUMPER |  | 42738 | 1918 | 1618098 | 2353 | Distribution Circuit | Vegetation | Tree - fell into line | 424 | 997672 | Clear-Strong Winds;Below 32 F | Pole-Wood | Broken- wire on ground | 17-0003212 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 42738 | 1918 | 1618737 | 2786 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 153230 | Clear-Strong Winds;Below 32 F | Pole-Wood | Broken- wire on ground | 17-0003760 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | RECLOSER |  | 42738 | 1918 | 1616446 | 2353 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 108238 | Overcast-Fog-Strong Winds;Below 32 F | Pole-Wood | Broken- wire on ground | 17-0003212 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | RECLOSER |  | 42743 | 2139 | 1629613 | 1158 | Distribution Circuit | Vegetation | Tree - fell into line | 590 | 683220 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005759 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1102 | 192171102 | OCB |  | 42738 | 1957 | 1616369 | 1705 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 223355 | Overcast-Fog-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0003227 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | HOOPA-1101 | 192401101 | JUMPER |  | 42738 | 1854 | 1618495 | 4213 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 45209 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003662 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 42743 | 1008 | 1624651 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4125 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005089 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 42743 | 1106 | 1625243 | 317 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2536 | Overcast-Fog-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0005164 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | OTHER |  | 42738 | 1627 | 1618624 | 4370 | Distribution Circuit | Vegetation | Tree - fell into line | 164 | 716680 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003723 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 42738 | 1627 | 1618621 | 4370 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 30590 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003722 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 42744 | 759 | 1630434 | 731 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5117 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005923 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 42738 | 629 | 1615340 | 9461 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 37844 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0002947 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 42738 | 1254 | 1619903 | 8871 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 62097 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0004142 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 42744 | 1135 | 1631069 | 287 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 861 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006079 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 42744 | 706 | 1630298 | 1952 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 9760 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005896 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
LOS PADRES | Tier 2 | CABRILLO-1104 | 183101104 | FUSE |  | 42758 | 813 | 1663170 | 1799 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1799 | Overcast-Drizzle;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 17-0013854 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | SANTA YNEZ-1101 | 182721101 | RECLOSER |  | 42757 | 2045 | 1662536 | 1585 | Distribution Circuit | Equipment Failure/Involved | Overhead | 190 | 259226 | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013523 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | SANTA MARIA-1108 | 182671108 | OTHER |  | 42753 | 1248 | 1646173 | 950 | Distribution Circuit | Equipment Failure/Involved | Overhead | 439 | 105340 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0009934 | OH | Sus | 42929077 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
LOS PADRES | Tier 2 | MESA-1101 | 182821101 | FUSE |  | 42757 | 820 | 1660464 | 2124 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 36108 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0013341 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | OCEANO-1104 | 182601104 | JUMPER |  | 42757 | 703 | 1660466 | 3312 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1449 | 260666 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013045 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | OCEANO-1104 | 182601104 | FUSE |  | 42757 | 734 | 1659529 | 346 | Distribution Circuit | Vegetation | Tree - branch fell on line | 32 | 11072 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013038 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | FOOTHILL-1101 | 182951101 | JUMPER |  | 42757 | 831 | 1659776 | 3109 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6218 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013259 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | FOOTHILL-1101 | 182951101 | FUSE |  | 42753 | 1453 | 1646560 | 186 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 2046 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010071 | OH | Sus | 42929062 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | FOOTHILL-1101 | 182951101 | FUSE |  | 42757 | 626 | 1659255 | 896 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 9856 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013034 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 3 | TEMPLETON-2113 | 183052113 | FUSE |  | 42758 | 123 | 1662645 | 822 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 13974 | Rain-Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013600 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 3 | TEMPLETON-2113 | 183052113 | SWITCH |  | 42757 | 1456 | 1661588 | 2377 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 52294 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0013257 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | ATASCADERO-1103 | 182541103 | FUSE |  | 42743 | 1004 | 1624576 | 369 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 2302 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005110 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | ATASCADERO-1103 | 182541103 | FUSE |  | 42757 | 435 | 1658770 | 1047 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 26938 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0013079 | OH | Sus | 31297289 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | ATASCADERO-1101 | 182541101 | FUSE |  | 42746 | 14 | 1638172 | 306 | Distribution Circuit | Vegetation | Tree - branch fell on line | 62 | 14072 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007344 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | ATASCADERO-1101 | 182541101 | RECLOSER |  | 42757 | 339 | 1658478 | 770 | Distribution Circuit | Vegetation | Tree - fell into line | 487 | 40648 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012685 | OH | Sus | 42929174 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 3 | ATASCADERO-1101 | 182541101 | SWITCH |  | 42757 | 831 | 1659777 | 300 | Distribution Circuit | Vegetation | Tree - fell into line | 175 | 37389 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012925 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE |  | 42743 | 1859 | 1628888 | 206 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 13999 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005667 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
LOS PADRES | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE |  | 42758 | 649 | 1662990 | 1801 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 30547 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013804 | OH | Sus | 31297289 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE |  | 42757 | 647 | 1659311 | 267 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2136 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012852 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | OTHER |  | 42746 | 957 | 1639368 | 790 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2370 | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 17-0007581 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE |  | 42757 | 748 | 1659595 | 466 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 8388 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012934 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE |  | 42755 | 540 | 1652521 | 443 | Distribution Circuit | Vegetation | Tree - fell into line | 303 | 48013 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011234 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE |  | 42757 | 638 | 1659420 | 552 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 44712 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012998 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE |  | 42755 | 728 | 1653008 | 663 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 26520 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011615 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2110 | 183052110 | FUSE |  | 42744 | 210 | 1629943 | 610 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 4310 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005865 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
MISSION | Tier 3 | SUNOL-1101 | 14241101 | OTHER |  | 42756 | 1715 | 1657026 | 941 | Distribution Circuit | Vegetation | Tree - fell into line | 205 | 99799 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012145 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
MISSION | Tier 3 | CASTRO VALLEY-1108 | 14091108 | FUSE |  | 42745 | 1412 | 1633645 | 721 | Distribution Circuit | Vegetation | Tree - fell into line | 121 | 87241 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006767 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
MISSION | Tier 3 | CASTRO VALLEY-1108 | 14091108 | RECLOSER |  | 42755 | 1523 | 1654572 | 1198 | Distribution Circuit | Vegetation | Tree - fell into line | 385 | 84293 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011676 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
MISSION | Tier 3 | SAN RAMON 2108 | 14232108 | FUSE |  | 42744 | 417 | 1630063 | 612 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3060 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005889 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
MISSION | Tier 3 | SAN RAMON-2108 | 14232108 | FUSE |  | 42745 | 31 | 1632426 | 1049 | Distribution Circuit | Vegetation | Tree - branch fell on line | 99 | 34726 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006380 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | ALTO-1125 | 42031125 | FUSE |  | 42746 | 2245 | 1640827 | 380 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 6460 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0008222 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | RECLOSER |  | 42738 | 1852 | 1616469 | 2148 | Distribution Circuit | Equipment Failure/Involved | Overhead | 202 | 396358 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0003201 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE |  | 42738 | 1917 | 1616573 | 827 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 8270 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003346 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | OTHER |  | 42744 | 435 | 1630371 | 975 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 37810 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005937 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE |  | 42743 | 1251 | 1626580 | 1965 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 180780 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005562 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | Yes
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE |  | 42745 | 1913 | 1636046 | 699 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 8388 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007204 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | ALTO-1122 | 42031122 | FUSE |  | 42738 | 2301 | 1617421 | 625 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 18323 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003388 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | ALTO-1122 | 42031122 | FUSE |  | 42743 | 915 | 1623260 | 757 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 102195 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005514 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1122 | 42031122 | FUSE |  | 42743 | 725 | 1623105 | 1631 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 45668 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005176 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | OTHER |  | 42743 | 107 | 1622436 | 412 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1648 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0004893 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | BOLINAS-1101 | 42261101 | RECLOSER |  | 42755 | 217 | 1652054 | 171 | Distribution Circuit | Environmental/External | Flood/Erosion | 345 | 58995 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011176 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE |  | 42746 | 622 | 1638730 | 438 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 22776 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007427 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | RECLOSER |  | 42745 | 1921 | 1638850 | 2312 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 43928 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007429 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | OTHER |  | 42738 | 2215 | 1617093 | 559 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 10360 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0003348 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | OTHER |  | 42745 | 1835 | 1635382 | 393 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 13473 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006947 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE |  | 42738 | 1746 | 1616324 | 638 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 12760 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003331 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | RECLOSER |  | 42743 | 1015 | 1624812 | 1337 | Distribution Circuit | Vegetation | Tree - fell into line | 3074 | 752850 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 17-0005119 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE |  | 42744 | 1702 | 1631874 | 486 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 6804 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006273 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE |  | 42743 | 713 | 1622984 | 1127 | Distribution Circuit | Vegetation | Tree - fell into line | 408 | 60186 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005004 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE |  | 42743 | 703 | 1623118 | 2241 | Distribution Circuit | Vegetation | Tree - fell into line | 203 | 454923 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0004985 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | Yes
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE |  | 42755 | 1828 | 1655055 | 2800 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5600 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011762 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE |  | 42753 | 1834 | 1648173 | 550 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 44000 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010389 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | OCB |  | 42743 | 1219 | 1623506 | 798 | Distribution Circuit | Vegetation | Tree - fell into line | 2689 | 563462 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005332 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE |  | 42745 | 1535 | 1634078 | 1825 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 33458 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006778 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | LAS GALLINAS A-1105 | 42991105 | FUSE |  | 42745 | 1824 | 1635375 | 1566 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 7830 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007214 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 42743 | 1056 | 1629785 | 5800 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 61300 | Strong Winds-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005782 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER |  | 42753 | 1820 | 1648052 | 1216 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 229787 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010296 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 42755 | 431 | 1652308 | 566 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 38488 | Overcast-Heavy Rain-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011252 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 42745 | 1537 | 1634107 | 585 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 39780 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006843 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 42743 | 840 | 1623734 | 957 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 33495 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | On Ground | 17-0005059 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 42743 | 834 | 1623684 | 846 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2428 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005182 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | Yes
NORTH BAY | Tier 2 | STAFFORD-1102 | 43201102 | OTHER |  | 42745 | 1034 | 1632937 | 476 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 1936 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006551 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 42757 | 310 | 1658395 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 14170 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012750 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER |  | 42745 | 8 | 1632412 | 1034 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 138556 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006360 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 42743 | 909 | 1624182 | 1866 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 40413 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0005063 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | STAFFORD 1101 | 43201101 | RECLOSER |  | 42743 | 1331 | 1626941 | 1004 | Distribution Circuit | Vegetation | Tree - fell into line | 2023 | 332436 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005360 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 42743 | 1632 | 1628054 | 2930 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 43950 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005873 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | PUEBLO-2103 | 43292103 | FUSE |  | 42743 | 1116 | 1628573 | 899 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2697 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005589 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 42743 | 726 | 1623182 | 2694 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 33654 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005183 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 42743 | 1526 | 1627922 | 1307 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 32028 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005512 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 42743 | 1222 | 1626146 | 3133 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 164801 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005592 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE |  | 42746 | 532 | 1638656 | 1211 | Distribution Circuit | Vegetation | Tree - fell into line | 175 | 70469 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007473 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2102 | 43432102 | FUSE |  | 42744 | 723 | 1631788 | 3382 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 37202 | Overcast-Fog-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006287 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2105 | 43432105 | FUSE |  | 42743 | 1107 | 1625288 | 1679 | Distribution Circuit | Vegetation | Tree - branch fell on line | 143 | 293696 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005447 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 42745 | 1805 | 1635219 | 2117 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 86797 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0008244 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | OTHER |  | 42745 | 1822 | 1636689 | 1041 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1457 | 283939 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007284 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE |  | 42746 | 1728 | 1640464 | 27019 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 79402 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0008208 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE |  | 42745 | 1455 | 1634935 | 2762 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 16572 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0008265 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE |  | 42746 | 1802 | 1640528 | 3148 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 18888 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0008261 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE |  | 42746 | 1351 | 1640898 | 1724 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 6896 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0008240 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE |  | 42745 | 2255 | 1638828 | 2640 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 179520 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007648 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE |  | 42746 | 722 | 1639211 | 1110 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 22200 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007902 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE |  | 42743 | 1200 | 1625954 | 770 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 34650 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0005267 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE |  | 42746 | 1748 | 1640498 | 2727 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 18887 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0008211 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 42745 | 622 | 1632520 | 686 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 10290 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006405 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 42738 | 1901 | 1616550 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 48680 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003221 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE |  | 42745 | 1451 | 1635050 | 2190 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 37136 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0007563 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 42757 | 313 | 1658356 | 1068 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8544 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0012834 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | SWITCH |  | 42745 | 1439 | 1633752 | 1756 | Distribution Circuit | Vegetation | Tree - fell into line | 182 | 93355 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006748 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE |  | 42746 | 633 | 1638794 | 803 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4015 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007601 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE |  | 42746 | 800 | 1639386 | 2090 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12540 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007915 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 42745 | 1812 | 1638666 | 1372 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 18964 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007412 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE |  | 42743 | 1845 | 1628653 | 1860 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1860 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005607 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE |  | 42743 | 1139 | 1630079 | 2276 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 31864 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005870 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | BANGOR-1101 | 103191101 | RECLOSER |  | 42753 | 1350 | 1646317 | 1332 | Distribution Circuit | Vegetation | Tree - fell into line | 433 | 138251 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0009979 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 42757 | 2355 | 1662593 | 847 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 35574 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013567 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 42745 | 534 | 1632530 | 689 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 28938 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0006490 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | JUMPER |  | 42744 | 1547 | 1631669 | 128 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 512 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006215 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 42743 | 1318 | 1626785 | 1917 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 29216 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005584 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER |  | 42753 | 1300 | 1646223 | 463 | Distribution Circuit | Vegetation | Tree - branch fell on line | 457 | 209843 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0009937 | OH | Sus | 42928979 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1107 | 102911107 | RECLOSER |  | 42757 | 300 | 1658314 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 444 | 179089 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012653 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1107 | 102911107 | RECLOSER |  | 42744 | 2323 | 1632387 | 1042 | Distribution Circuit | Vegetation | Tree - fell into line | 661 | 381461 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006353 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER |  | 42745 | 1848 | 1636626 | 225 | Distribution Circuit | Vegetation | Tree - fell into line | 896 | 70817 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0007034 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | OTHER |  | 42757 | 2224 | 1662615 | 971 | Distribution Circuit | Vegetation | Tree - fell into line | 458 | 64158 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013557 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | KANAKA-1101 | 103221101 | OTHER |  | 42755 | 1445 | 1654952 | 1033 | Distribution Circuit | Equipment Failure/Involved | Overhead | 179 | 21676 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011750 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | WYANDOTTE-1103 | 102911103 | FUSE |  | 42743 | 1224 | 1626167 | 1786 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 25004 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005410 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE |  | 42743 | 1808 | 1628523 | 2522 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 20176 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006505 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE |  | 42743 | 1430 | 1627346 | 1768 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 18803 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006051 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER |  | 42754 | 1001 | 1650579 | 8944 | Distribution Circuit | Vegetation | Tree - fell into line | 458 | 2592877 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010776 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | CLARK ROAD-1102 | 103091102 | FUSE |  | 42743 | 1516 | 1627654 | 1588 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 28584 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005653 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER |  | 42745 | 1628 | 1634391 | 4379 | Distribution Circuit | Vegetation | Tree - fell into line | 167 | 558905 | Overcast-Fog-Snow-Strong Winds;Below 32 F | Crossarm- Wood | Broken- wire on ground | 17-0007278 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1104 | 102831104 | FUSE |  | 42743 | 814 | 1623578 | 515 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3090 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005084 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1103 | 102831103 | RECLOSER |  | 42743 | 1139 | 1625697 | 1370 | Distribution Circuit | Vegetation | Tree - fell into line | 564 | 584314 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0005345 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1105 | 102831105 | FUSE |  | 42743 | 1336 | 1629184 | 2502 | Distribution Circuit | Vegetation | Tree - bark fell into line | 31 | 77562 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0005685 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1101 | 102831101 | TRANSFORMER |  | 42743 | 1123 | 1631133 | 3177 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 9531 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006093 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BIG BEND-1101 | 103751101 | FUSE |  | 42745 | 1507 | 1633938 | 187 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 12155 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006772 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | NOTRE DAME-1104 | 102041104 | TRIP-SAVER |  | 42743 | 1426 | 1626728 | 1946 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 85624 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0005492 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER |  | 42755 | 412 | 1652273 | 702 | Distribution Circuit | Vegetation | Tree - fell into line | 561 | 327080 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011171 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO LOMA-1102 | 255371102 | RECLOSER |  | 42758 | 517 | 1662842 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 561 | 154169 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013588 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE |  | 42738 | 2302 | 1617383 | 564 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 64860 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003359 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | BUCKS CREEK-1103 | 102211103 | RECLOSER |  | 42753 | 1859 | 1648330 | 6012 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 704056 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0010942 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | BUCKS CREEK 1102 | 102211102 | OCB |  | 42743 | 1941 | 1630293 | 6944 | Distribution Circuit | Environmental/External | Flood/Erosion | 131 | 909664 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0006104 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | FUSE |  | 42757 | 1912 | 1662164 | 1098 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 18666 | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 17-0013702 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | ORO FINO-1102 | 103031102 | OTHER |  | 42755 | 1618 | 1655046 | 1188 | Distribution Circuit | Vegetation | Tree - branch fell on line | 316 | 368832 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011760 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER |  | 42744 | 2236 | 1632352 | 4787 | Distribution Circuit | Vegetation | Tree - fell into line | 2747 | 1407309 | Overcast-Fog-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0006341 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | JUMPER |  | 42745 | 1413 | 1634235 | 601 | Distribution Circuit | Equipment Failure/Involved | Overhead | 199 | 89910 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0006828 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | Yes
NORTH VALLEY | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | JUMPER |  | 42745 | 1922 | 1638026 | 1507 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 10549 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007245 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | CHESTER-1102 | 103181102 | FUSE |  | 42754 | 943 | 1650512 | 237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1970 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0010850 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | RECLOSER |  | 42755 | 812 | 1653526 | 464 | Distribution Circuit | Vegetation | Tree - fell into line | 287 | 128458 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011380 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER |  | 42743 | 1316 | 1626779 | 2917 | Distribution Circuit | Vegetation | Tree - fell into line | 548 | 1435667 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005624 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER |  | 42755 | 1543 | 1654632 | 3102 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 800762 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011675 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD 1102 | 102931102 | FUSE |  | 42745 | 1247 | 1633298 | 67 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 67 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0006595 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | WILDWOOD 1101 | 103611101 | RECLOSER |  | 42753 | 1859 | 1649034 | 1152 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 117426 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0010452 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | WILDWOOD-1101 | 103611101 | TRANSFORMER |  | 42754 | 1845 | 1651932 | 1155 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4575 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011106 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | WILDWOOD-1101 | 103611101 | OTHER |  | 42753 | 2157 | 1649972 | 1248 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 19544 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010844 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1101 | 103401101 | FUSE |  | 42756 | 2025 | 1657241 | 337 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 16176 | Partly Cloudy-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012368 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | OTHER |  | 42755 | 1854 | 1655074 | 160 | Distribution Circuit | Vegetation | Tree - fell into line | 983 | 24544 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011771 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 3 | KESWICK-1101 | 103451101 | OCB |  | 42753 | 1558 | 1646895 | 971 | Distribution Circuit | Vegetation | Tree - fell into line | 789 | 207405 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0010121 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | RECLOSER |  | 42755 | 310 | 1652103 | 518 | Distribution Circuit | Vegetation | Tree - fell into line | 626 | 146318 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0011156 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | JUMPER |  | 42755 | 405 | 1653087 | 592 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4144 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011293 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | FUSE |  | 42758 | 632 | 1662910 | 333 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 8991 | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0013629 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CEDAR CREEK-1101 | 103321101 | FUSE |  | 42754 | 1923 | 1653273 | 2709 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 21672 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011583 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | CEDAR CREEK 1101 | 103321101 | FUSE |  | 42738 | 2111 | 1616945 | 753 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 24942 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003454 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE |  | 42754 | 1145 | 1651052 | 1705 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 157640 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010851 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BURNEY-1101 | 103311101 | FUSE |  | 42755 | 1003 | 1653620 | 196 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 392 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on object | 17-0011415 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE |  | 42755 | 1711 | 1655174 | 5360 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 187737 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0011812 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | PIT NO 5-1101 | 101321101 | RECLOSER |  | 42755 | 1848 | 1655023 | 7210 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7210 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011755 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | PIT NO 5-1101 | 101321101 | JUMPER |  | 42755 | 1958 | 1657663 | 5593 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 33558 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012538 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | PIT NO 5-1101 | 101321101 | RECLOSER |  | 42755 | 1958 | 1655969 | 2953 | Distribution Circuit | Vegetation | Tree - bark fell into line | 12 | 35206 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011986 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | PIT NO 5-1101 | 101321101 | RECLOSER |  | 42757 | 1846 | s1253524 | 4162 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 4162 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0014956 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | PIT NO 3-2101 | 103732101 | OCB |  | 42738 | 2025 | 1616744 | 1497 | Distribution Circuit | Vegetation | Tree - branch fell on line | 154 | 157796 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003238 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | PIT NO 3-2101 | 103732101 | RECLOSER |  | 42755 | 810 | 1653191 | 9058 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 85733 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0011326 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | PIT NO 5-1101 | 101321101 | RECLOSER |  | 42755 | 1311 | 1654321 | 8844 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 344374 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011653 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | PIT NO 3-2101 | 103732101 | RECLOSER |  | 42758 | 903 | 1663345 | 721 | Distribution Circuit | Environmental/External | Ice or snow | 64 | 45652 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0013829 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 42757 | 914 | 1660216 | 811 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 10543 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013217 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 42745 | 1724 | 1634683 | 2670 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5340 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006851 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 42755 | 736 | 1653033 | 508 | Distribution Circuit | Vegetation | Tree - branch fell on line | 67 | 34036 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011429 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 42743 | 1450 | 1627471 | 3146 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 102792 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005965 | OH | Sus | 31294580 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 42743 | 1530 | 1630921 | 1167 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 7002 | Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0006049 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 42744 | 1145 | 1631090 | 20 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 60 | Strong Winds-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0006088 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER |  | 42743 | 1126 | 1627946 | 1754 | Distribution Circuit | Equipment Failure/Involved | Overhead | 142 | 63454 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005515 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
PENINSULA | Tier 2 | MENLO-0401 | 24130401 | OTHER |  | 42743 | 113 | 1623835 | 1091 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 58679 | Strong Winds-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005033 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 42757 | 315 | 1658576 | 772 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2316 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0012704 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | SWITCH |  | 42746 | 1107 | 1639568 | 8 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 472 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0007567 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | SWITCH |  | 42746 | 1130 | 1639630 | 674 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 54594 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0007567 | OH | Sus | 42913270 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 42757 | 1603 | 1661628 | 4484 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 98648 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013347 | OH | Sus | 42928223 | 2017 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | JUMPER |  | 42757 | 1200 | 1660898 | 705 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2820 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013115 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE |  | 42738 | 2009 | 1616723 | 913 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 14608 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003329 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 2 | MENLO-0401 | 24130401 | SWITCH |  | 42744 | 952 | 1630373 | 748 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2244 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0006008 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE |  | 42755 | 1359 | 1654381 | 1056 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 15840 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011669 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 42743 | 859 | 1623846 | 3381 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10143 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005971 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER |  | 42743 | 1009 | 1625271 | 1556 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 39020 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005168 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER |  | 42757 | 426 | 1658740 | 507 | Distribution Circuit | Vegetation | Tree - branch fell on line | 579 | 9755 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012809 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE |  | 42757 | 447 | 1658815 | 528 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 26400 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012863 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 42743 | 1236 | 1626875 | 1409 | Distribution Circuit | Vegetation | Tree - branch fell on line | 53 | 57153 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005329 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1102 | 24131102 | FUSE |  | 42753 | 1533 | 1646768 | 1490 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 58110 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | On Ground | 17-0010229 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 42743 | 944 | 1624335 | 1522 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 18264 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 17-0005339 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 42743 | 1012 | 1624697 | 4798 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 201521 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005275 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER |  | 42743 | 833 | 1623805 | 899 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 82091 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005177 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 42746 | 1148 | 1639760 | 381 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 15621 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007876 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 42743 | 2217 | 1629643 | 3020 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 33220 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005927 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 42744 | 1930 | 1632155 | 1758 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 25516 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006295 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 42746 | 2041 | 1641184 | 2104 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 10520 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0008382 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER |  | 42745 | 1937 | 1636276 | 2999 | Distribution Circuit | Vegetation | Tree - fell into line | 246 | 25597 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006973 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER |  | 42745 | 1742 | 1637400 | 1688 | Distribution Circuit | Vegetation | Tree - fell into line | 1692 | 805011 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007175 | OH | Sus | 31294580 | 2017 | JAN | Yes | Force Out | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER |  | 42757 | 949 | 1660198 | 790 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 19915 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013075 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER |  | 42753 | 1923 | 1648539 | 618 | Distribution Circuit | Vegetation | Tree - branch fell on line | 226 | 148279 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010356 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | HALF MOON BAY-1101 | 24101101 | RECLOSER |  | 42743 | 1251 | 1626502 | 1650 | Distribution Circuit | Vegetation | Tree - branch fell on line | 68 | 92895 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 17-0005286 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1104 | 24251104 | FUSE |  | 42745 | 1414 | 1633654 | 868 | Distribution Circuit | Vegetation | Tree - branch fell on line | 74 | 64232 | Overcast-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on object | 17-0006723 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 42743 | 320 | 1622495 | 716 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 10024 | Overcast-Fog-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0004910 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER |  | 42743 | 1817 | 1628988 | 1351 | Distribution Circuit | Vegetation | Tree - fell into line | 193 | 26371 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005665 | OH | Sus | 31294580 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 42738 | 2041 | 1616773 | 1111 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 17776 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003321 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 3 | HALF MOON BAY-1101 | 24101101 | FUSE |  | 42746 | 1649 | 1640373 | 1423 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 11384 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007870 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | EMERALD LAKE-0401 | 24080401 | FUSE |  | 42745 | 1745 | 1637906 | 1681 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1681 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007206 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | PACIFICA-1103 | 22811103 | JUMPER |  | 42743 | 1531 | 1628055 | 1389 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 16821 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005507 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | VACAVILLE-1108 | 63601108 | FUSE |  | 42745 | 1917 | 1636080 | 930 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5580 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | On Ground | 17-0007253 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | NARROWS-2101 | 153132101 | FUSE |  | 42743 | 1239 | 1626357 | 453 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 12606 | Partly Cloudy-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005482 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | JUMPER |  | 42753 | 1527 | 1646735 | 229 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 458 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0010068 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 42743 | 1227 | 1626017 | 257 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 7710 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005344 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SAN FRANCISCO | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER |  | 42753 | 1759 | s1249610 | 694 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 9920 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010247 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
SAN JOSE | Tier 2 | MORGAN HILL-2105 | 83242105 | FUSE |  | 42745 | 2051 | 1637040 | 2529 | Distribution Circuit | Vegetation | Tree - branch fell on line | 86 | 15704 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007155 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SAN JOSE | Tier 2 | MORGAN HILL-2111 | 83242111 | FUSE |  | 42745 | 2002 | 1636629 | 2428 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 246744 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007249 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SAN JOSE | Tier 2 | SWIFT-2110 | 83392110 | RECLOSER |  | 42754 | 1010 | 1650603 | 1664 | Distribution Circuit | Environmental/External | Lightning | 194 | 189436 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010809 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 42758 | 406 | 1664354 | 2129 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 6387 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013887 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 42758 | 723 | 1663566 | 1808 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 19888 | Drizzle-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013698 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER |  | 42758 | 710 | 1662972 | 1786 | Distribution Circuit | Vegetation | Tree - fell into line | 696 | 396322 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013612 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE |  | 42744 | 925 | 1630275 | 1770 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4857 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005978 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE |  | 42745 | 659 | 1632548 | 1900 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 34079 | Heavy Rain-Strong Winds-Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0006476 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 42758 | 403 | 1663102 | 765 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 52020 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0013628 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER |  | 42743 | 2115 | 1629283 | 1352 | Distribution Circuit | Vegetation | Tree - fell into line | 1226 | 309908 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0005727 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | JUMPER |  | 42745 | 1155 | 1633126 | 1653 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1653 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006729 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE |  | 42753 | 2342 | 1649578 | 816 | Distribution Circuit | Vegetation | Tree - fell into line | 258 | 151576 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010698 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS 2108 | 153652108 | FUSE |  | 42743 | 1729 | 1628414 | 2684 | Distribution Circuit | Vegetation | Tree - fell into line | 150 | 214164 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005683 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2110 | 153652110 | FUSE |  | 42743 | 1757 | 1627977 | 1054 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 12814 | Overcast-Fog-Rain;32-90 F | Anchor or Guy | Broken- wire on ground | 17-0005586 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 42745 | 2119 | 1637575 | 2394 | Distribution Circuit | Equipment Failure/Involved | Overhead | 118 | 282492 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007580 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 42743 | 1205 | 1625997 | 543 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 14706 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005377 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | JUMPER |  | 42757 | 1854 | 1662147 | 383 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1174 | 304136 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013373 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 42745 | 1533 | 1634068 | 2950 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 29950 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006795 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 42758 | 319 | 1662930 | 5194 | Distribution Circuit | Vegetation | Tree - fell into line | 254 | 986037 | Partly Cloudy-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 17-0013630 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | FUSE |  | 42745 | 2043 | 1636978 | 2823 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 26585 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0007848 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 42745 | 2038 | 1636915 | 879 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 35160 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007314 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 42745 | 1844 | 1635609 | 2793 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 34080 | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007783 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 42743 | 722 | 1623078 | 283 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 2830 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005057 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 42758 | 1429 | 1664345 | 1444 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 11552 | Partly Cloudy-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013975 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 42757 | 1403 | 1661177 | 1737 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3474 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013239 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 42758 | 319 | 1664337 | 3713 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 33417 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 17-0013876 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER |  | 42758 | 416 | 1662767 | 983 | Distribution Circuit | Vegetation | Tree - fell into line | 1142 | 383946 | Partly Cloudy-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0013576 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 42756 | 13 | 1655343 | 1045 | Distribution Circuit | Vegetation | Tree - fell into line | 450 | 300438 | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 17-0011867 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | FUSE |  | 42745 | 1747 | 1634447 | 1588 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 15117 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006912 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1111 | 153081111 | OTHER |  | 42745 | 1855 | 1635762 | 493 | Distribution Circuit | Vegetation | Tree - fell into line | 616 | 150379 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007113 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | FUSE |  | 42745 | 2102 | 1637108 | 2773 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5546 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0008527 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | SWITCH |  | 42743 | 2129 | 1628985 | 1153 | Distribution Circuit | Vegetation | Tree - fell into line | 197 | 24281 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005730 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 42758 | 721 | 1663029 | 2162 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 13164 | Snow-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013710 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 42744 | 239 | s1245747 | 2097 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 8284 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005991 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 42745 | 2124 | 1637618 | 2476 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 14856 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0008227 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | RECLOSER |  | 42743 | 2019 | 1629044 | 1118 | Distribution Circuit | Vegetation | Tree - fell into line | 760 | 315709 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005783 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | RECLOSER |  | 42757 | 651 | 1659939 | 969 | Distribution Circuit | Vegetation | Tree - fell into line | 760 | 303638 | Partly Cloudy-Fog-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012943 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 42746 | 111 | 1638319 | 1372 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 79576 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007372 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | JUMPER |  | 42743 | 815 | 1624970 | 268 | Distribution Circuit | Environmental/External | Lightning | 572 | 98692 | Overcast-Fog-Rain-Lightning-Strong Winds;32-90 F | Jumper | Broken- wire on object | 17-0005126 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 42756 | 557 | 1655615 | 518 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 8409 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011929 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 42743 | 1017 | 1624755 | 557 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 11140 | Partly Cloudy-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005243 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 42746 | 1040 | 1639501 | 485 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 4063 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007639 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 42758 | 349 | 1662723 | 3253 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 24010 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0014356 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | ECHO SUMMIT-1101 | 158031101 | FUSE |  | 42744 | 657 | 1633309 | 6208 | Distribution Circuit | Environmental/External | Flood/Erosion | 6 | 37248 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006597 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | EL DORADO PH-2101 | 152762101 | SWITCH |  | 42756 | 1154 | 1655261 | 7312 | Distribution Circuit | Vegetation | Tree - branch fell on line | 443 | 598639 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010893 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 42743 | 2202 | 1629607 | 1390 | Distribution Circuit | Vegetation | Tree - fell into line | 1019 | 1011862 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005757 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | ECHO SUMMIT-1101 | 158031101 | RECLOSER |  | 42758 | 1829 | 1664813 | 1351 | Distribution Circuit | Equipment Failure/Involved | Overhead | 640 | 830590 | Overcast;Below 32 F | Crossarm- Wood | Broken- wire on ground | 17-0014026 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | ECHO SUMMIT-1101 | 158031101 | RECLOSER |  | 42755 | 203 | 1652044 | 2589 | Distribution Circuit | Equipment Failure/Involved | Overhead | 246 | 327105 | Overcast-Snow;Below 32 F | Connector or Splice (OH) | Broken- wire on ground | 17-0011145 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PENRYN-1103 | 152561103 | FUSE |  | 42745 | 1822 | 1635361 | 1336 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 73480 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007276 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | PENRYN-1103 | 152561103 | FUSE |  | 42753 | 1507 | 1646633 | 279 | Distribution Circuit | Vegetation | Tree - fell into line | 633 | 27919 | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010100 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 42743 | 1904 | 1628748 | 2730 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 20778 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0005732 | OH | Sus | 31294707 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | FUSE |  | 42753 | 1558 | 1646766 | 625 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 33750 | Partly Cloudy-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 17-0010218 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 42744 | 607 | 1630221 | 2344 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 9376 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006249 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 42745 | 1207 | 1633157 | 3127 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 10600 | Partly Cloudy-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006646 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | FUSE |  | 42743 | 1218 | 1626097 | 222 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 4392 | Partly Cloudy-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0005295 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER |  | 42746 | 104 | 1638322 | 1321 | Distribution Circuit | Vegetation | Tree - fell into line | 604 | 171496 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007320 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PENRYN-1105 | 152561105 | FUSE |  | 42745 | 1620 | 1634282 | 1122 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 33666 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006867 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 42758 | 153 | 1662476 | 2115 | Distribution Circuit | Vegetation | Tree - fell into line | 896 | 491372 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | On Ground | 17-0013563 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 42756 | 1117 | 1656404 | 623 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 48594 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0012150 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BELL-1107 | 152701107 | FUSE |  | 42755 | 1030 | 1653713 | 1594 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 7300 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 17-0011549 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 42743 | 2209 | 1629610 | 2398 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 38368 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006004 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | RECLOSER |  | 42753 | 2042 | 1648942 | 2527 | Distribution Circuit | Equipment Failure/Involved | Overhead | 266 | 196977 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010437 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | RECLOSER |  | 42757 | 450 | 1658832 | 435 | Distribution Circuit | Vegetation | Tree - fell into line | 267 | 53545 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012764 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | RECLOSER |  | 42743 | 1502 | 1627596 | 683 | Distribution Circuit | Vegetation | Tree - grew into line | 267 | 63858 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005433 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | FUSE |  | 42753 | 1546 | 1646832 | 3130 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 62600 | Rain-Strong Winds-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 17-0010326 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | OTHER |  | 42757 | 2101 | 1662269 | 1407 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 116781 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013537 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | LINCOLN-1104 | 153701104 | FUSE |  | 42754 | 1023 | 1650642 | 1500 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4500 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010786 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | JUMPER |  | 42744 | 2021 | 1632219 | 1224 | Distribution Circuit | Vegetation | Tree - fell into line | 166 | 9051 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005598 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | RECLOSER |  | 42745 | 2119 | 1637588 | 248 | Distribution Circuit | Vegetation | Tree - fell into line | 382 | 45873 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007233 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 42745 | 2005 | 1636661 | 2783 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 33396 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0007794 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE |  | 42745 | 2046 | 1636999 | 1249 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 14454 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007264 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 42746 | 929 | 1639330 | 589 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 9424 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007746 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | WEIMAR 1102 | 152491102 | FUSE |  | 42746 | 24 | 1638181 | 957 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 22968 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007650 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE |  | 42745 | 1738 | 1634764 | 1602 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6408 | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0007027 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | SECTIONALIZER |  | 42758 | 830 | 1663209 | 330 | Distribution Circuit | Vegetation | Tree - fell into line | 591 | 121954 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0013678 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE |  | 42746 | 126 | 1638376 | 1304 | Distribution Circuit | Vegetation | Tree - fell into line | 288 | 256170 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007365 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE |  | 42745 | 1913 | 1636038 | 1224 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 35496 | Partly Cloudy-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007107 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1109 | 152691109 | FUSE |  | 42753 | 1539 | 1646985 | 635 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 34335 | Partly Cloudy-Rain;32-90 F | Pole-Wood | Broken- wire on object | 17-0010132 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | FUSE |  | 42753 | 1731 | 1646477 | 380 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 22420 | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010264 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1107 | 152691107 | FUSE |  | 42744 | 357 | 1630021 | 827 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 10751 | Strong Winds-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005942 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 42753 | 1554 | 1646615 | 1066 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 58630 | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010188 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 42744 | 311 | 1629982 | 1248 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 19968 | Strong Winds-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0005932 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | HIGGINS-1109 | 152691109 | FUSE |  | 42744 | 558 | 1630218 | 1670 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 27672 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0005979 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1109 | 152691109 | FUSE |  | 42745 | 1907 | 1637690 | 1273 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 61104 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007172 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 42744 | 38 | 1629879 | 2349 | Distribution Circuit | Equipment Failure/Involved | Overhead | 752 | 37353 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005829 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 42746 | 817 | 1639018 | 543 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 11138 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007524 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 42743 | 1453 | 1627510 | 1197 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 56259 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005737 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 42746 | 929 | 1639249 | 1658 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 16580 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007765 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | RECLOSER |  | 42756 | 115 | 1655395 | 614 | Distribution Circuit | Vegetation | Tree - fell into line | 1309 | 160761 | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on object | 17-0011873 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | GRASS VALLEY 1101 | 152031101 | FUSE |  | 42743 | 1351 | 1627090 | 1486 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 29720 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0005704 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 42744 | 1524 | 1631582 | 1279 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 5025 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006205 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 42743 | 1024 | 1624846 | 344 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 15136 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005157 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | TRIP-SAVER |  | 42745 | 1840 | 1635621 | 982 | Distribution Circuit | Vegetation | Tree - fell into line | 226 | 221932 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007000 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 42757 | 1951 | 1662238 | 882 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 35280 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013485 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER |  | 42758 | 800 | 1663148 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 1007 | 209089 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013655 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | JUMPER |  | 42757 | 1920 | 1662532 | 1244 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 15011 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013519 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER |  | 42743 | 1216 | 1627010 | 1464 | Distribution Circuit | Vegetation | Tree - fell into line | 2032 | 789644 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0005426 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE |  | 42754 | 133 | 1649725 | 2176 | Distribution Circuit | Vegetation | Tree - fell into line | 121 | 245124 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010744 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | FUSE |  | 42746 | 1343 | 1639923 | 395 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 5730 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007809 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK 1101 | 152301101 | OCB |  | 42738 | 548 | 1615292 | 404 | Distribution Circuit | Vegetation | Tree - fell into line | 513 | 90044 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0002880 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | FUSE |  | 42745 | 1727 | 1634697 | 1533 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 14641 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006879 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 42744 | 135 | 1629925 | 2133 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 12137 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005861 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | DRUM-1101 | 152321101 | JUMPER |  | 42745 | 1514 | 1634159 | 1589 | Distribution Circuit | Vegetation | Tree - fell into line | 151 | 86286 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006803 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | DRUM-1101 | 152321101 | RECLOSER |  | 42758 | 121 | 1662642 | 2429 | Distribution Circuit | Equipment Failure/Involved | Overhead | 105 | 203778 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0013558 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 3 | DRUM-1101 | 152321101 | FUSE |  | 42756 | 420 | 1655484 | 755 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3775 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 17-0011882 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2102 | 153132102 | FUSE |  | 42753 | 2058 | 1648991 | 934 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 79390 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010489 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | DRUM-1101 | 152321101 | FUSE |  | 42757 | 330 | 1659270 | 2107 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 185416 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013185 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER |  | 42738 | 1056 | 1615646 | 1999 | Distribution Circuit | Vegetation | Tree - branch fell on line | 652 | 471639 | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0002967 | OH | Sus | 42908603 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE |  | 42754 | 12 | 1649609 | 1110 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 31080 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010628 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | NARROWS-2102 | 153132102 | FUSE |  | 42744 | 626 | 1630242 | 711 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 25477 | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 17-0006005 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER |  | 42743 | 657 | 1622900 | 252 | Distribution Circuit | Vegetation | Tree - branch fell on line | 114 | 19722 | Strong Winds-Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0004980 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | DRUM-1101 | 152321101 | FUSE |  | 42745 | 942 | 1632834 | 5248 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 94464 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0007913 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | DRUM-1101 | 152321101 | RECLOSER |  | 42758 | 110 | 1662624 | 2563 | Distribution Circuit | Equipment Failure/Involved | Overhead | 87 | 222981 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0013556 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 42756 | 1831 | 1659879 | 1350 | Distribution Circuit | Equipment Failure/Involved | Overhead | 123 | 166050 | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0012930 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 42755 | 718 | 1652948 | 787 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 5509 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011592 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE |  | 42746 | 1736 | 1640476 | 1921 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 95086 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0008220 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SUMMIT 1102 | 152591102 | FUSE |  | 42743 | 1020 | 1625922 | 7734 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 30936 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0005234 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE |  | 42746 | 743 | 1638902 | 2593 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 72604 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0008417 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER |  | 42755 | 827 | 1653712 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2020 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011445 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE |  | 42754 | 1227 | 1651144 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 69734 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on object | 17-0010918 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE |  | 42754 | 1555 | 1651558 | 1271 | Distribution Circuit | Equipment Failure/Involved | Overhead | 54 | 68634 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0011142 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE |  | 42745 | 2141 | 1643785 | 5573 | Distribution Circuit | Vegetation | Tree - grew into line | 54 | 300942 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0008785 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER |  | 42756 | 648 | 1655705 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 68015 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0011949 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 42758 | 1759 | 1664762 | 931 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2793 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0013995 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | SWITCH |  | 42756 | 1713 | 1659965 | 1469 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 45077 | Strong Winds-Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012948 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | COLUMBIA HILL-1101 | 152471101 | FUSE |  | 42743 | 1219 | 1626111 | 1510 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 55870 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005422 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | OCB |  | 42745 | 1936 | 1636324 | 2670 | Distribution Circuit | Vegetation | Tree - fell into line | 1130 | 1246286 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007467 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | COLUMBIA HILL-1101 | 152471101 | FUSE |  | 42745 | 1500 | 1633879 | 2914 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 17484 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0008336 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | RECLOSER |  | 42738 | 2309 | 1617255 | 1248 | Distribution Circuit | Vegetation | Tree - fell into line | 237 | 187104 | Overcast-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0003403 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE |  | 42753 | 2116 | 1649065 | 1339 | Distribution Circuit | Vegetation | Tree - branch fell on line | 36 | 48204 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010566 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | RECLOSER |  | 42738 | 1927 | 1616634 | 4448 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 133251 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003215 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1101 | 152101101 | JUMPER |  | 42756 | 428 | 1661218 | 5041 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 15123 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0013190 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE |  | 42738 | 536 | 1615461 | 831 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 9141 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0002908 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE |  | 42755 | 1203 | 1653404 | 230 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 2300 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0011535 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | Yes
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 42743 | 522 | 1630212 | 5333 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 10666 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005878 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 42744 | 1325 | 1631365 | 1278 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5112 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006208 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1105 | 42271105 | FUSE |  | 42745 | 1244 | 1633282 | 2851 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 4255 | Partly Cloudy-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0006689 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | SONOMA-1103 | 42721103 | FUSE |  | 42746 | 540 | 1639122 | 2145 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 155705 | Partly Cloudy-Fog-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0007472 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1105 | 42271105 | RECLOSER |  | 42743 | 1321 | 1626893 | 454 | Distribution Circuit | Vegetation | Tree - branch fell on line | 662 | 219114 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005343 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1105 | 42271105 | RECLOSER |  | 42745 | 1739 | 1635033 | 1285 | Distribution Circuit | Equipment Failure/Involved | Overhead | 660 | 556009 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006875 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | LAKEVILLE-1102 | 43371102 | JUMPER |  | 42745 | 2228 | 1638128 | 1272 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1272 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007408 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | JUMPER |  | 42744 | 1511 | 1631695 | 4204 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 12612 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006220 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1105 | 42271105 | FUSE |  | 42745 | 1442 | 1633837 | 1324 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 65442 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007038 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE |  | 42744 | 941 | 1631664 | 4451 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8902 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006212 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | SALMON CREEK-1101 | 43161101 | OTHER |  | 42754 | 1933 | 1651846 | 382 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 764 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011112 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
SONOMA | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE |  | 42755 | 852 | 1653353 | 174 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 348 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011361 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | FUSE |  | 42745 | 1754 | 1635461 | 4071 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 77349 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007663 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | FUSE |  | 42743 | 1338 | 1626975 | 1775 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 60350 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006196 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | FUSE |  | 42757 | 940 | 1660164 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1992 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012984 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1101 | 42571101 | OTHER |  | 42743 | 1115 | 1625342 | 4515 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 61454 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005594 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | DUNBAR-1103 | 43071103 | OTHER |  | 42757 | 528 | 1659020 | 588 | Distribution Circuit | Vegetation | Tree - branch fell on line | 118 | 14224 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012991 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | RECLOSER |  | 42738 | 1657 | 1616109 | 659 | Distribution Circuit | Vegetation | Tree - fell into line | 376 | 31670 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003174 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 42743 | 738 | 1625138 | 1614 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 124278 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005148 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | FUSE |  | 42745 | 1337 | 1634698 | 1843 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 18430 | Clear;32-90 F | Conductor- Overhead | On Ground | 17-0006855 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | DUNBAR-1103 | 43071103 | OTHER |  | 42743 | 1745 | 1628450 | 1013 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 89606 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005754 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 42738 | 1626 | 1616007 | 358 | Distribution Circuit | Vegetation | Tree - branch fell on line | 81 | 21198 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003158 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | DUNBAR-1101 | 43071101 | FUSE |  | 42743 | 1854 | 1628711 | 3901 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 15604 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007499 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | JUMPER |  | 42745 | 1834 | 1636505 | 2906 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5812 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006988 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 42743 | 1704 | 1629175 | 4325 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 56225 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005725 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | JUMPER |  | 42738 | 1638 | 1616642 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 9090 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003218 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 42743 | 1117 | 1625928 | 3360 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 54271 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005527 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER |  | 42743 | 738 | 1623186 | 845 | Distribution Circuit | Vegetation | Tree - fell into line | 1242 | 1038565 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0004977 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | FUSE |  | 42743 | 1243 | 1626420 | 1518 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 54648 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005528 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 42754 | 457 | 1649900 | 428 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3573 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010685 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 42743 | 547 | 1622733 | 2049 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 114744 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0004973 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | JUMPER |  | 42744 | 1815 | 1632044 | 2940 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2940 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006337 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | FUSE |  | 42755 | 319 | 1652107 | 958 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 20118 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011215 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 42743 | 738 | 1628823 | 1756 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 159870 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005627 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | RECLOSER |  | 42757 | 449 | 1659021 | 755 | Distribution Circuit | Vegetation | Tree - fell into line | 386 | 291430 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0012820 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE |  | 42743 | 945 | 1624342 | 3122 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6244 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006173 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | FUSE |  | 42745 | 1752 | 1634972 | 1617 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 21221 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007321 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | SANTA ROSA A 1107 | 42151107 | OTHER |  | 42745 | 1752 | 1635207 | 2431 | Distribution Circuit | Vegetation | Tree - fell into line | 203 | 21678 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007304 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 42753 | 2257 | 1649303 | 774 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 27090 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010587 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE |  | 42745 | 918 | 1632783 | 1778 | Distribution Circuit | Environmental/External | Water | 15 | 26670 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0006503 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER |  | 42745 | 1515 | 1634000 | 1609 | Distribution Circuit | Vegetation | Tree - fell into line | 620 | 670768 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006897 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE |  | 42745 | 251 | 1632464 | 3605 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 18025 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006383 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE |  | 42745 | 1323 | 1633371 | 2647 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 23823 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006661 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | RINCON-1103 | 43321103 | OCB |  | 42745 | 1414 | 1633660 | 579 | Distribution Circuit | Vegetation | Tree - fell into line | 2228 | 285114 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006680 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 42743 | 626 | 1622748 | 371 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 42294 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0004983 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | JUMPER |  | 42745 | 836 | 1632922 | 1980 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 63888 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006513 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 42743 | 651 | 1622833 | 304 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 3952 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0004990 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 42743 | 734 | 1623134 | 4948 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 178128 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0005105 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | OTHER |  | 42743 | 849 | 1625486 | 2025 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 161839 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005190 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 42754 | 242 | 1649766 | 469 | Distribution Circuit | Vegetation | Tree - branch fell on line | 110 | 51590 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010643 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 42743 | 816 | 1623555 | 1785 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 168231 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005113 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 42743 | 1050 | 1625102 | 2998 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 110926 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005648 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER |  | 42745 | 1238 | 1633280 | 3062 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 455556 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0006657 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 2 | MIRABEL-1102 | 42091102 | FUSE |  | 42755 | 338 | 1652166 | 464 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4176 | Partly Cloudy-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011202 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE |  | 42743 | 636 | 1625477 | 2083 | Distribution Circuit | Vegetation | Tree - fell into line | 143 | 209900 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0005472 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE |  | 42743 | 1132 | 1625565 | 1364 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 17732 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006024 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 42745 | 1600 | 1634189 | 2851 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 45616 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0006993 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MIRABEL-1102 | 42091102 | FUSE |  | 42756 | 1028 | 1656267 | 1577 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5303 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012037 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 42743 | 1048 | 1625076 | 421 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 10104 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005257 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 42745 | 1342 | 1640661 | 3260 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 22820 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0008420 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 42743 | 1951 | 1631579 | 1524 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 27432 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006214 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | FULTON-1107 | 42561107 | OTHER |  | 42743 | 1216 | 1626173 | 1646 | Distribution Circuit | Vegetation | Tree - fell into line | 222 | 77180 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005412 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | Yes
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | JUMPER |  | 42743 | 1448 | 1627674 | 1497 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 20958 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005443 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER |  | 42756 | 1829 | 1657113 | 1519 | Distribution Circuit | Vegetation | Tree - fell into line | 232 | 289669 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0012165 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER |  | 42753 | 1315 | 1646247 | 1591 | Distribution Circuit | Vegetation | Tree - fell into line | 640 | 197059 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010035 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER |  | 42744 | 1213 | 1632095 | 3104 | Distribution Circuit | Vegetation | Tree - fell into line | 171 | 433710 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006309 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 42746 | 1643 | 1640336 | 4042 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 74140 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007880 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 42738 | 2055 | 1616778 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 7530 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0003336 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | GEYSERVILLE-1101 | 42891101 | JUMPER |  | 42743 | 1528 | 1627707 | 2646 | Distribution Circuit | Vegetation | Tree - branch fell on line | 72 | 21360 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005449 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE |  | 42743 | 1504 | 1627577 | 2951 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 17706 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005608 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE |  | 42743 | 1753 | 1628472 | 1132 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 64240 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005677 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CORRAL-1101 | 162991101 | RECLOSER |  | 42757 | 322 | 1658391 | 508 | Distribution Circuit | Equipment Failure/Involved | Overhead | 413 | 98459 | Overcast-Drizzle-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0012688 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 42753 | 1542 | 1646817 | 658 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 5214 | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0010154 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | STANISLAUS-1701 | 162821701 | RECLOSER |  | 42756 | 917 | 1656126 | 4541 | Distribution Circuit | Vegetation | Tree - fell into line | 816 | 741085 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011933 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS 1701 | 162821701 | FUSE |  | 42756 | 247 | 1655445 | 1150 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 86250 | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 17-0011887 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | JUMPER |  | 42743 | 2026 | 1629108 | 501 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2263 | 401870 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005734 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER |  | 42756 | 552 | 1655236 | 724 | Distribution Circuit | Vegetation | Tree - fell into line | 1373 | 994052 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0011894 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 42756 | 448 | 1656981 | 5077 | Distribution Circuit | Vegetation | Tree - branch fell on line | 43 | 218311 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0012113 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 42756 | 1822 | 1664016 | 4016 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 52208 | Clear;32-90 F | Conductor- Overhead | On Ground | 17-0013796 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 42756 | 903 | 1656379 | 694 | Distribution Circuit | Vegetation | Tree - fell into line | 189 | 80646 | Overcast-Fog;Below 32 F | Pole-Wood | Broken- wire on ground | 17-0012019 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 42758 | 1010 | 1663742 | 1741 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 13928 | Overcast;32-90 F | Conductor- Overhead | On Ground | 17-0013751 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | JUMPER |  | 42757 | 1318 | 1661997 | 2882 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 20482 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013338 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 42756 | 1738 | 1657057 | 1555 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 29545 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0012950 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER |  | 42756 | 1014 | 1655642 | 1987 | Distribution Circuit | Vegetation | Tree - fell into line | 287 | 289340 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0012029 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 42756 | 1819 | 1657097 | 1213 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 52159 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012542 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 42756 | 1307 | 1661429 | 3377 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 50655 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013243 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | SWITCH |  | 42756 | 557 | 1657018 | 3607 | Distribution Circuit | Vegetation | Tree - fell into line | 153 | 551871 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0012126 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 42755 | 2232 | 1661417 | 3899 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 280728 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0013242 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 42756 | 2232 | 1660173 | 780 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 7020 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | On Ground | 17-0012987 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | JUMPER |  | 42755 | 2223 | 1666221 | 6637 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 19911 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0014509 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 42756 | 114 | 1664476 | 5202 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 150858 | Clear;Below 32 F | Pole-Wood | Broken- wire on ground | 17-0013917 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER |  | 42756 | 114 | s1251084 | 5189 | Distribution Circuit | Vegetation | Tree - fell into line | 1137 | 1708981 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011863 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER |  | 42756 | 1715 | 1657023 | 20 | Distribution Circuit | Vegetation | Tree - fell into line | 399 | 7980 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012128 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 42756 | 1717 | 1657042 | 41 | Distribution Circuit | Vegetation | Tree - branch fell on line | 61 | 2501 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012133 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 42756 | 532 | 1656960 | 2017 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 86212 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0012105 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 42757 | 206 | 1658134 | 3591 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 75411 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0014330 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 42757 | 1956 | 1662248 | 4250 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 30215 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013394 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 42755 | 2018 | 1655127 | 5123 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 630129 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0011856 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 42755 | 1401 | 1655154 | 5510 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 380190 | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 17-0011855 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | OTHER |  | 42756 | 400 | 1655629 | 4661 | Distribution Circuit | Equipment Failure/Involved | Overhead | 114 | 520574 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0011896 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE |  | 42745 | 748 | 1632710 | 483 | Distribution Circuit | Vegetation | Tree - fell into line | 332 | 65496 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006485 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 42758 | 2037 | 1664970 | 2699 | Distribution Circuit | Environmental/External | Ice or snow | 154 | 415646 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0014334 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER |  | 42755 | 1401 | 1654386 | 348 | Distribution Circuit | Vegetation | Tree - fell into line | 991 | 196316 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011646 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER |  | 42756 | 623 | 1655779 | 3647 | Distribution Circuit | Vegetation | Tree - fell into line | 628 | 2260797 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0011908 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 42758 | 2037 | 1665800 | 2713 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 111233 | Overcast-Fog;Below 32 F | Conductor- Overhead | On Ground | 17-0014384 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | JUMPER |  | 42758 | 2037 | 1665877 | 2699 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 72873 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0014426 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE |  | 42756 | 812 | 1666897 | 6319 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 233803 | Clear;Below 32 F | Conductor- Overhead | On Ground | 17-0014731 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 42756 | 40 | 1661647 | 6797 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 747670 | Clear;Below 32 F | Pole-Wood | Broken- wire on ground | 17-0013267 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CLAY-1103 | 163341103 | FUSE |  | 42746 | 614 | 1638735 | 1942 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 56982 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007682 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 42756 | 534 | 1661350 | 6418 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 299962 | Clear;Below 32 F | Pole-Wood | Broken- wire on ground | 17-0013222 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | CLAY-1103 | 163341103 | RECLOSER |  | 42738 | 707 | 1615352 | 393 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 2002 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0002884 | OH | Sus | 31292586 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CLAY-1101 | 163341101 | OCB |  | 42745 | 2110 | 1637469 | 885 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1711 | 118689 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007140 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | ELECTRA-1102 | 162161102 | FUSE |  | 42746 | 145 | 1638461 | 2350 | Distribution Circuit | Vegetation | Tree - fell into line | 338 | 423252 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007667 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | MARTELL-1103 | 163011103 | RECLOSER |  | 42743 | 950 | 1624448 | 873 | Distribution Circuit | Environmental/External | Flood/Erosion | 139 | 121347 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0005193 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE |  | 42757 | 706 | 1659419 | 2042 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 10210 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 17-0012977 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE |  | 42757 | 537 | 1659046 | 715 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 20060 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012972 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 42745 | 730 | 1632588 | 711 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 6399 | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0006468 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE |  | 42757 | 550 | 1659134 | 707 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 11312 | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0013200 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER |  | 42744 | 526 | 1630069 | 2154 | Distribution Circuit | Environmental/External | Flood/Erosion | 1910 | 403369 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0005879 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER |  | 42745 | 2036 | 1636930 | 1332 | Distribution Circuit | Vegetation | Tree - fell into line | 1181 | 315066 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007222 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER |  | 42758 | 906 | 1663699 | 1804 | Distribution Circuit | Vegetation | Tree - branch fell on line | 98 | 39137 | Overcast-Snow;32-90 F | Conductor- Overhead | On Ground | 17-0013878 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE |  | 42746 | 132 | 1638401 | 1869 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 21930 | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0007774 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | TRANSFORMER |  | 42758 | 1440 | 1663376 | 139 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 834 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013756 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER |  | 42743 | 16 | 1622373 | 907 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 63698 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0004886 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 42755 | 2332 | 1655312 | 3928 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 23568 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012134 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | MARTELL-1101 | 163011101 | FUSE |  | 42743 | 920 | 1624332 | 335 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 15999 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005162 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE |  | 42745 | 1939 | 1635597 | 1312 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 26240 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006977 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 42743 | 2342 | 1629790 | 983 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2949 | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0005854 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | OCB |  | 42746 | 123 | 1638362 | 685 | Distribution Circuit | Vegetation | Tree - fell into line | 4383 | 622884 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0007328 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | RECLOSER |  | 42745 | 1044 | 1632967 | 434 | Distribution Circuit | Vegetation | Tree - fell into line | 686 | 49270 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006529 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | SALT SPRINGS-2102 | 163692102 | RECLOSER |  | 42755 | 2059 | 1655172 | 8204 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 405005 | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 17-0011814 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | SALT SPRINGS-2102 | 163692102 | RECLOSER |  | 42745 | 2337 | 1638099 | 3993 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2000 | 127889 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0007269 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 42756 | 446 | 1655550 | 1896 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 26544 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | On Ground | 17-0012015 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | MARTELL-1101 | 163011101 | FUSE |  | 42745 | 1009 | 1632890 | 461 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1844 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006599 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER |  | 42756 | 811 | 1655890 | 587 | Distribution Circuit | Equipment Failure/Involved | Overhead | 973 | 494544 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0011926 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | MARTELL-1101 | 163011101 | FUSE |  | 42744 | 703 | 1630345 | 791 | Distribution Circuit | Equipment Failure/Involved | Overhead | 77 | 47611 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006006 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER |  | 42756 | 1209 | 1655655 | 1433 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1153 | 390401 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0012006 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | Yes
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 42758 | 731 | 1663558 | 895 | Distribution Circuit | Equipment Failure/Involved | Overhead | 154 | 109984 | Overcast-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 17-0013697 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 42756 | 434 | 1655869 | 1869 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 168210 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | On Ground | 17-0012011 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | JUMPER |  | 42745 | 2140 | 1638375 | 1412 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4236 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007333 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | JUMPER |  | 42756 | 1050 | 1656565 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 616 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012032 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 42756 | 520 | 1656196 | 1893 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 84069 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0011951 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 42745 | 52 | 1632443 | 998 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3992 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006384 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER |  | 42757 | 1311 | 1661303 | 457 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1070 | 203063 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013212 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | Yes
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 42756 | 428 | 1655504 | 888 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 13320 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012051 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 42756 | 4 | 1655328 | 2406 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 76992 | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 17-0011969 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 42758 | 842 | 1663256 | 725 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 23200 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013767 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 42758 | 419 | 1662774 | 738 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 50184 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0013704 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | OTHER |  | 42746 | 559 | 1638729 | 2029 | Distribution Circuit | Vegetation | Tree - branch fell on line | 150 | 14098 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007823 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | Yes
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 42756 | 429 | 1655532 | 2342 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 32788 | Strong Winds-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 17-0011966 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | JUMPER |  | 42744 | 950 | 1630756 | 1599 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4797 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0006122 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 42756 | 7 | 1657194 | 2706 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 224598 | Strong Winds-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 17-0012161 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE |  | 42745 | 2259 | 1638008 | 267 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 17955 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007281 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE |  | 42754 | 449 | 1649895 | 541 | Distribution Circuit | Vegetation | Tree - fell into line | 204 | 21764 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0010667 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2103 | 254432103 | FUSE |  | 42755 | 1917 | 1655070 | 1182 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 35460 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 17-0011778 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1103 | 252531103 | FUSE |  | 42756 | 1410 | 1656676 | 266 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 2926 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012085 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | RECLOSER |  | 42758 | 1030 | s1252562 | 253 | Distribution Circuit | Equipment Failure/Involved | Overhead | 458 | 115874 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 17-0013785 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE |  | 42758 | 906 | 1663374 | 659 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 22439 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 17-0013774 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | TRIP-SAVER |  | 42758 | 908 | 1663394 | 588 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 26460 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013784 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE |  | 42758 | 217 | 1663088 | 537 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 51015 | Overcast-Snow;32-90 F | Conductor- Overhead | On Ground | 17-0013644 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | FUSE |  | 42758 | 145 | 1662662 | 2076 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 45672 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013580 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER |  | 42757 | 1929 | 1662203 | 1360 | Distribution Circuit | Vegetation | Tree - fell into line | 455 | 183281 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013406 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | FUSE |  | 42758 | 1120 | 1663805 | 550 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 6801 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013934 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 42758 | 1122 | 1663782 | 1474 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 47168 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0014033 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER |  | 42757 | 808 | 1659678 | 739 | Distribution Circuit | Vegetation | Tree - fell into line | 676 | 467067 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0013033 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1101 | 254421101 | FUSE |  | 42758 | 823 | 1664670 | 2042 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4084 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013968 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | OTHER |  | 42743 | 1202 | 1625979 | 950 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 14250 | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0005278 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 42745 | 2039 | 1636923 | 565 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 14690 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007153 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER |  | 42755 | 1006 | 1653644 | 805 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 57890 | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0011538 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER |  | 42745 | 2200 | 1637832 | 3708 | Distribution Circuit | Vegetation | Tree - fell into line | 602 | 332739 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007385 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | FUSE |  | 42745 | 1902 | 1635853 | 992 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5952 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007396 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE |  | 42744 | 523 | 1630215 | 301 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 13271 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0005904 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1704 | 163761704 | OCB |  | 42745 | 2337 | 1638092 | 219 | Distribution Circuit | Vegetation | Tree - fell into line | 677 | 112231 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007267 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 42743 | 1311 | 1626709 | 409 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3272 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0005473 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
YOSEMITE | Tier 3 | CURTIS-1705 | 163351705 | FUSE |  | 42756 | 132 | 1655410 | 3348 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 63152 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012155 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | RECLOSER |  | 42757 | 4 | 1658371 | 3815 | Distribution Circuit | Equipment Failure/Involved | Overhead | 130 | 147843 | Overcast-Fog-Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 17-0013276 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | FUSE |  | 42743 | 1428 | 1627326 | 302 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3322 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 17-0005489 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 42756 | 652 | 1655708 | 4804 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 110492 | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 17-0012136 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | FUSE |  | 42756 | 734 | 1655773 | 2111 | Distribution Circuit | Vegetation | Tree - grew into line | 32 | 23872 | Overcast-Fog;Below 32 F | Pole-Wood | Broken- wire on ground | 17-0012139 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 42756 | 537 | 1655724 | 1938 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 25194 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | On Ground | 17-0011915 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 42756 | 535 | 1655723 | 657 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 17082 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0011932 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | FUSE |  | 42753 | 1723 | 1647381 | 338 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 5070 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0010357 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | CURTIS-1704 | 163351704 | FUSE |  | 42745 | 1533 | 1634069 | 668 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 63460 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0006800 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 42756 | 359 | 1655805 | 1062 | Distribution Circuit | Vegetation | Tree - fell into line | 354 | 343329 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0012073 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 42758 | 1726 | 1664713 | 1243 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 12979 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0014027 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | FUSE |  | 42756 | 645 | 1655701 | 1935 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 30960 | Overcast-Fog;Below 32 F | Insulator | Broken- wire on object | 17-0012069 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | OTHER |  | 42758 | 1000 | 1663553 | 1730 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 65870 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013981 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | Yes
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 42756 | 803 | 1655833 | 3678 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 117696 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0011991 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER |  | 42756 | 1843 | 1659135 | 1558 | Distribution Circuit | Vegetation | Tree - fell into line | 872 | 957431 | Overcast-Fog;Below 32 F | Pole-Wood | Broken- wire on ground | 17-0012821 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 42755 | 2107 | 1656225 | 5553 | Distribution Circuit | Vegetation | Tree - bark fell into line | 404 | 1861104 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0011965 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 42756 | 504 | 1656221 | 4786 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 378094 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 17-0012114 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 42757 | 1341 | 1661133 | 2846 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 35642 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013168 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 42756 | 701 | 1655730 | 4570 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 49023 | Overcast-Fog;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0012014 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 42756 | 1024 | 1656248 | 3537 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 53055 | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0012081 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 42758 | 1257 | 1664078 | 504 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 49392 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0013824 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 42757 | 724 | 1664771 | 3269 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 134029 | Clear;Below 32 F | Crossarm- Wood | Broken- wire on ground | 17-0013996 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | Yes
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | OTHER |  | 42755 | 2341 | 1655320 | 1243 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 23708 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0011858 | OH | Sus | 0 | 2017 | JAN | Yes | Open Circuit | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 42756 | 1000 | 1656374 | 3277 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 51073 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0012061 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER |  | 42756 | 720 | 1656246 | 3730 | Distribution Circuit | Vegetation | Tree - fell into line | 304 | 791514 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0011998 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 42756 | 2056 | 1657288 | 3778 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 196456 | Overcast;Below 32 F | Conductor- Overhead | On Ground | 17-0013218 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER |  | 42745 | 1904 | 1635913 | 550 | Distribution Circuit | Vegetation | Tree - branch fell on line | 918 | 245988 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0006975 | OH | Sus | 0 | 2017 | JAN | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 42756 | 944 | 1656171 | 4626 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 60138 | Overcast-Fog;Below 32 F | Conductor- Overhead | On Ground | 17-0013433 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 42756 | 744 | 1655680 | 3410 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 264966 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0013385 | OH | Sus | 0 | 2017 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 42758 | 1659 | 1664595 | 1355 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 7439 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0014015 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1701 | 162831701 | FUSE |  | 42757 | 914 | 1664628 | 3581 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 204117 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013958 | OH | Sus | 0 | 2017 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1701 | 162831701 | JUMPER |  | 42756 | 1553 | 1666433 | 5873 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 58730 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0014523 | OH | Sus | 0 | 2017 | JAN | Yes | None | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1701 | 162831701 | FUSE |  | 42756 | 1305 | 1664382 | 6026 | Distribution Circuit | Vegetation | Tree - branch fell on line | 106 | 638756 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0013897 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | PINECREST 0401 | 163160401 | FUSE |  | 42756 | 1935 | 1657181 | 2586 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 77580 | Clear;Below 32 F | Conductor- Overhead | On Ground | 17-0013264 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1701 | 162831701 | FUSE |  | 42758 | 1304 | 1664106 | 3120 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 45808 | Partly Cloudy-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0014034 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1701 | 162831701 | FUSE |  | 42745 | 1737 | 1634756 | 1039 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 14546 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 17-0006933 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1701 | 162831701 | FUSE |  | 42758 | 1257 | 1664076 | 3139 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 65919 | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 17-0014381 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1701 | 162831701 | RECLOSER |  | 42755 | 2321 | 1655300 | 2459 | Distribution Circuit | Vegetation | Tree - fell into line | 153 | 376227 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 17-0011870 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1701 | 162831701 | FUSE |  | 42745 | 1927 | 1636153 | 1003 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 45135 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0007288 | OH | Sus | 0 | 2017 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | FELTON-0401 | 83140401 | OTHER |  | 42904 | 1315 | 1807762 | 685 | Distribution Circuit | Vegetation | Tree - fell into line | 1915 | 180924 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0056107 | OH | Sus | 0 | 2017 | JUN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE |  | 42904 | 1056 | 1807649 | 198 | Distribution Circuit | 3rd Party | Vehicle | 6 | 1188 | Clear-Heat Wave;32-90 F | Pole-Wood | Broken- wire on ground | 17-0056092 | OH | Sus | 0 | 2017 | JUN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | RECLOSER |  | 43028 | 440 | 1905242 | 339 | Distribution Circuit | 3rd Party | Vehicle | 135 | 37765 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 17-0088903 | OH | Sus | 31361694 | 2017 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | TRIP-SAVER |  | 43016 | 2151 | 1893977 | 559 | Distribution Circuit | Equipment Failure/Involved | Overhead | 48 | 26832 | Clear;32-90 F | Insulator | Broken- wire on object | 17-0085312 | OH | Sus | 43169679 | 2017 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | FELTON-0401 | 83140401 | JUMPER |  | 43028 | 313 | 1905181 | 408 | Distribution Circuit | Vegetation | Tree - fell into line | 1912 | 52596 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0088877 | OH | Sus | 43198596 | 2017 | OCT | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 43017 | 131 | 1894906 | 984 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 50249 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085482 | OH | Sus | 31355742 | 2017 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER |  | 43028 | 715 | 1905815 | 433 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 9010 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0089038 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 43028 | 412 | 1906576 | 2175 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 43500 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0089318 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 43016 | 2221 | 1894126 | 928 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 24464 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085291 | OH | Sus | 31355577 | 2017 | OCT | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | TASSAJARA 2109 | 14662109 | OTHER |  | 43028 | 801 | 1905576 | 597 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 23826 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0089040 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | OTHER |  | 43017 | 142 | 1894986 | 2690 | Distribution Circuit | Vegetation | Tree - branch fell on line | 336 | 218099 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085344 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | Yes
HUMBOLDT | Tier 2 | HIGHLANDS-1103 | 43361103 | FUSE |  | 43016 | 2018 | 1893966 | 1293 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 67236 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085214 | OH | Sus | 31355575 | 2017 | OCT | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE |  | 43016 | 2254 | 1894140 | 2451 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 186751 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085739 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | REDBUD-1101 | 43191101 | JUMPER |  | 43017 | 29 | 1894896 | 630 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 13314 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085335 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LUCERNE-1106 | 43351106 | OCB |  | 43017 | 51 | 1894798 | 2036 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2972 | 1633084 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085361 | OH | Sus | 0 | 2017 | OCT | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | CALPELLA-1101 | 43411101 | FUSE |  | 43017 | 620 | 1895763 | 10105 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 111 | 1048890 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0085418 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | MENDOCINO-1101 | 42951101 | FUSE |  | 43017 | 52 | 1898710 | 8143 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 7 | 57001 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085395 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | CABRILLO-1103 | 183101103 | FUSE |  | 43028 | 1610 | 1906380 | 173 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 173 | Partly Cloudy;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0089249 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
MISSION | Tier 2 | SAN LEANDRO-1114 | 13111114 | RECLOSER |  | 43017 | 102 | 1894797 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 4769 | 376540 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085325 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 43016 | 2225 | 1894077 | 21285 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 617265 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0086273 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | PUEBLO-1105 | 43291105 | FUSE |  | 43017 | 154 | 1902561 | 16497 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 41 | 676377 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0087984 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | PUEBLO-1105 | 43291105 | FUSE |  | 43016 | 2220 | 1899635 | 17025 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 34050 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0086893 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | PUEBLO-1104 | 43291104 | SWITCH |  | 43016 | 2259 | 1901273 | 19761 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 513786 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0087501 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | MONTICELLO-1101 | 43051101 | RECLOSER |  | 43017 | 138 | 1900638 | 10906 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 535 | 5266351 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0087310 | OH | Sus | 0 | 2017 | OCT | Yes | Three Phase Fault | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2105 | 43432105 | JUMPER |  | 43022 | 2018 | 1901035 | 972 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2916 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0087429 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER |  | 43016 | 2149 | 1893975 | 2774 | Distribution Circuit | Vegetation | Tree - branch fell on line | 526 | 1416648 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085216 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE |  | 43017 | 11 | 1895660 | 5298 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 84768 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085393 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | CALISTOGA-1101 | 42711101 | JUMPER |  | 43016 | 2120 | 1898920 | 24194 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 3 | 66878 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0086476 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE |  | 43016 | 2324 | 1908131 | 21147 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 63441 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0089778 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | CALISTOGA-1101 | 42711101 | RECLOSER |  | 43016 | 2202 | 1893951 | 19823 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 149 | 1855187 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085239 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | CALISTOGA-1101 | 42711101 | FUSE |  | 43016 | 2202 | 1903598 | 19950 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 39900 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0088407 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | CALISTOGA-1101 | 42711101 | FUSE |  | 43016 | 1841 | 1893704 | 20024 | Distribution Circuit | Equipment Failure/Involved | Overhead | 62 | 1241488 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085175 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | SWITCH |  | 43016 | 2202 | 1903474 | 21238 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 42476 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 17-0088360 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 43016 | 2129 | 1893943 | 2675 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 22535 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085359 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER |  | 43016 | 2039 | 1893816 | 2591 | Distribution Circuit | Vegetation | Tree - branch fell on line | 200 | 100195 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085263 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER |  | 43028 | 54 | 1904944 | 594 | Distribution Circuit | Vegetation | Tree - fell into line | 214 | 78976 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0088893 | OH | Sus | 43198926 | 2017 | OCT | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | CLARK ROAD-1102 | 103091102 | FUSE |  | 43016 | 2255 | 1894161 | 2535 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 160479 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085276 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | RECLOSER |  | 43016 | 2039 | 1893810 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 616 | 181992 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085196 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1103 | 102831103 | JUMPER |  | 43016 | 2219 | 1896055 | 2125 | Distribution Circuit | Vegetation | Tree - fell into line | 772 | 42839 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085504 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 3 | PARADISE-1104 | 102831104 | FUSE |  | 43028 | 658 | 1905445 | 597 | Distribution Circuit | Vegetation | Tree - grew into line | 16 | 9552 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0088953 | OH | Sus | 43198933 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1104 | 102831104 | FUSE |  | 43016 | 1839 | 1894153 | 761 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 6849 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085265 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1103 | 102831103 | FUSE |  | 43016 | 1917 | 1893731 | 1738 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 50577 | Clear;32-90 F | Pole-Wood | Broken- wire on object | 17-0085314 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | Yes
NORTH VALLEY | Tier 3 | PARADISE-1101 | 102831101 | FUSE |  | 43028 | 335 | 1905198 | 777 | Distribution Circuit | Vegetation | Tree - bark fell into line | 59 | 45843 | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0088896 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BIG BEND-1101 | 103751101 | FUSE |  | 43016 | 2012 | 1893777 | 943 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 60352 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085339 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CENTERVILLE-1101 | 102021101 | RECLOSER |  | 43016 | 2015 | 1893833 | 372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 409 | 134500 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085303 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | JUMPER |  | 43017 | 834 | 1896296 | 305 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 7625 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085524 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | DESCHUTES-1101 | 103351101 | FUSE |  | 43016 | 639 | 1892952 | 581 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 22340 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0085039 | OH | Sus | 31355701 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 43016 | 2322 | 1899487 | 6858 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 20574 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086819 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 43016 | 2322 | 1899490 | 6991 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 13982 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086820 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 43016 | 2322 | 1899491 | 7601 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 7601 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086821 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 43016 | 2322 | 1899493 | 8123 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 8123 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086822 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 43016 | 2322 | 1899495 | 7863 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 29 | 228027 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086823 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 43016 | 2322 | 1899496 | 6703 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 13406 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086825 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 43016 | 2322 | 1899498 | 6839 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 151 | 897785 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086826 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | JUMPER |  | 43016 | 2308 | 1899500 | 6882 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 6882 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086827 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 43016 | 2308 | 1899501 | 6502 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 4 | 26008 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086828 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 43016 | 2322 | 1896866 | 6701 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 69 | 462369 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0085755 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 43016 | 2316 | 1899504 | 6894 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 6894 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086829 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 43016 | 2308 | 1899536 | 6767 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 13534 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086849 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 43016 | 2316 | 1899506 | 6874 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 6874 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086830 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 43016 | 2322 | 1899533 | 6758 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 20274 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086847 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 43016 | 2322 | 1899532 | 6768 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 6768 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086846 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 43016 | 2316 | 1899530 | 6779 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 13558 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086845 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 43016 | 2322 | 1899529 | 6893 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 13786 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086842 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 43016 | 2316 | 1899516 | 6884 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 6884 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086833 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 43016 | 2322 | 1899526 | 6662 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 19986 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086841 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | JUMPER |  | 43016 | 2308 | 1899517 | 6939 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 6939 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086835 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 43016 | 2322 | 1899525 | 6669 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 20007 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086840 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 43016 | 2322 | 1899520 | 6886 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 6886 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086837 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 43016 | 2322 | 1894286 | 8085 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 30 | 242550 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086839 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 43016 | 2322 | 1899523 | 6890 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 11 | 75790 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086838 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 43016 | 2322 | 1899357 | 8197 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 4 | 32788 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086750 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 3 | DOBBINS-1101 | 153741101 | FUSE |  | 43028 | 59 | 1905604 | 771 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1542 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0089070 | OH | Sus | 43199090 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | DOBBINS-1101 | 153741101 | RECLOSER |  | 43016 | 2205 | 1894014 | 3750 | Distribution Circuit | Vegetation | Tree - fell into line | 169 | 426606 | Strong Winds-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085274 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | DOBBINS-1101 | 153741101 | FUSE |  | 43016 | 2145 | 1893968 | 4099 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4099 | Strong Winds-Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086135 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 43017 | 920 | 1896202 | 408 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 2438 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085492 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43016 | 2108 | 1893857 | 1312 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 10496 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085600 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE |  | 43017 | 1945 | 1897030 | 174 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 174 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085795 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 43028 | 108 | 1904968 | 2488 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 47369 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 17-0089061 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE |  | 43016 | 2347 | 1894921 | 4128 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 41 | 169248 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0086029 | OH | Sus | 0 | 2017 | OCT | Yes | None | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | OCB |  | 43017 | 124 | 1894576 | 4031 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1424 | 2445169 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085336 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | FUSE |  | 43016 | 2352 | 1897935 | 5230 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 125520 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0086158 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2102 | 153132102 | JUMPER |  | 43016 | 2327 | 1897902 | 5463 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 29043 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0086150 | OH | Sus | 31360786 | 2017 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | JUMPER |  | 43017 | 104 | 1897872 | 5033 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 56 | 281848 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0086141 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | RECLOSER |  | 43016 | 2325 | 1894346 | 1044 | Distribution Circuit | Vegetation | Tree - fell into line | 1759 | 252040 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085282 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | JUMPER |  | 43016 | 2343 | 1897875 | 3677 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 5 | 18385 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0086143 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | SWITCH |  | 43017 | 104 | 1899353 | 5488 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 5488 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0086747 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE |  | 43016 | 2303 | 1894177 | 2350 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 30550 | Clear;32-90 F | Pole-Wood | Broken- wire on object | 17-0085778 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | OTHER |  | 43028 | 119 | 1905467 | 706 | Distribution Circuit | Equipment Failure/Involved | Overhead | 155 | 102410 | Overcast-Fog-Heavy Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 17-0088957 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 43016 | 2209 | 1894021 | 2127 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2229 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085266 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SUMMIT-1101 | 152591101 | TRIP-SAVER |  | 43017 | 427 | 1895640 | 507 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 23322 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085436 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | SWITCH |  | 43016 | 2258 | 1894156 | 978 | Distribution Circuit | Vegetation | Tree - fell into line | 223 | 198802 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0085355 | OH | Sus | 31355729 | 2017 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE |  | 43016 | 1931 | 1893744 | 2723 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 46291 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085204 | OH | Sus | 43169673 | 2017 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE |  | 43016 | 2153 | 1896299 | 1357 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 17773 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085527 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | JUMPER |  | 43016 | 2110 | 1894011 | 1098 | Distribution Circuit | Vegetation | Tree - fell into line | 258 | 255784 | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0085261 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | SONOMA-1105 | 42721105 | SWITCH |  | 43017 | 147 | 1902150 | 19500 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 132 | 2574000 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0087806 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | SONOMA-1102 | 42721102 | FUSE |  | 43016 | 2330 | 1894367 | 9843 | Distribution Circuit | Vegetation | Tree - bark fell into line | 15 | 50106 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085345 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | PENNGROVE-1101 | 43471101 | FUSE |  | 43017 | 36 | 1894682 | 2251 | Distribution Circuit | Vegetation | Tree - branch fell on line | 49 | 66143 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085419 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | JUMPER |  | 43017 | 417 | 1900182 | 19584 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 275 | 3394903 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0087154 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | DUNBAR-1102 | 43071102 | FUSE |  | 43017 | 136 | 1899587 | 16703 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 9 | 150327 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086872 | OH | Sus | 0 | 2017 | OCT | Yes | None | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | JUMPER |  | 43017 | 412 | 1902088 | 17673 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 17673 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0087779 | OH | Sus | 0 | 2017 | OCT | Yes | Multi-Fault | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | FUSE |  | 43016 | 2350 | 1898756 | 12720 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 5 | 51364 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086444 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | FUSE |  | 43017 | 417 | 1900920 | 12347 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 14 | 172858 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0087154 | OH | Sus | 0 | 2017 | OCT | Yes | None | Yes | No
SONOMA | Tier 2 | DUNBAR-1103 | 43071103 | JUMPER |  | 43016 | 2350 | 1899662 | 15147 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 4 | 60588 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086901 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | TRIP-SAVER |  | 43016 | 2333 | 1894391 | 2437 | Distribution Circuit | Equipment Failure/Involved | Overhead | 77 | 187649 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085384 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | BELLEVUE-2103 | 43182103 | FUSE |  | 43017 | 313 | 1898790 | 13693 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 581551 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0086452 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | BELLEVUE-2103 | 43182103 | FUSE |  | 43017 | 313 | 1898660 | 13587 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 17 | 230979 | Clear;32-90 F | Pole-Wood | Broken- wire on object | 17-0086414 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | DUNBAR-1101 | 43071101 | JUMPER |  | 43028 | 1740 | 1906463 | 2767 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 5534 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on object | 17-0089267 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 3 | DUNBAR-1101 | 43071101 | FUSE |  | 43016 | 2335 | 1903260 | 16495 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 19 | 313405 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0088276 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | DUNBAR-1101 | 43071101 | JUMPER |  | 43016 | 2335 | 1900094 | 16805 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 33 | 539330 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0087122 | OH | Sus | 0 | 2017 | OCT | Yes | None | Yes | No
SONOMA | Tier 3 | DUNBAR-1101 | 43071101 | JUMPER |  | 43016 | 2358 | s1308557 | 19690 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 6 | 81458 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0087580 | OH | Sus | 0 | 2017 | OCT | Yes | None | Yes | No
SONOMA | Tier 2 | DUNBAR-1101 | 43071101 | JUMPER |  | 43016 | 2358 | 1900347 | 15332 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 33 | 468604 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0087205 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | DUNBAR-1101 | 43071101 | JUMPER |  | 43016 | 2154 | 1901286 | 14034 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 7 | 98238 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0087504 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | DUNBAR-1101 | 43071101 | FUSE |  | 43016 | 2336 | 1901716 | 16517 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 198204 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0087678 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | DUNBAR-1101 | 43071101 | JUMPER |  | 43016 | 2154 | 1900167 | 19746 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 19746 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0087147 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | RINCON 1101 | 43321101 | JUMPER |  | 43016 | 2326 | 1896967 | 6704 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 60336 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085772 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE |  | 43017 | 1605 | 1896824 | 2706 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 10824 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0085746 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | RINCON 1102 | 43321102 | FUSE |  | 43017 | 138 | 1896669 | 10977 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 19 | 208131 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0086666 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE |  | 43016 | 2331 | 1901328 | 12595 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 25190 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0087522 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE |  | 43016 | 2331 | 1901331 | 18409 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 46 | 846454 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0087524 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | SANTA ROSA A-1104 | 42151104 | FUSE |  | 43017 | 211 | 1901336 | 12122 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 5 | 60610 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0087528 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE |  | 43016 | 2331 | 1901847 | 12669 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 19 | 240711 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0087723 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE |  | 43016 | 2240 | 1902794 | 15602 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 5 | 78010 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0088077 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 2 | SANTA ROSA A-1104 | 42151104 | FUSE |  | 43017 | 211 | 1901338 | 20796 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 9 | 187164 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0087529 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE |  | 43017 | 211 | 1901335 | 13934 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 41802 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0087527 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE |  | 43016 | 2240 | 1901320 | 18032 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 11 | 198352 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0087517 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | SANTA ROSA A-1104 | 42151104 | FUSE |  | 43016 | 2240 | 1901380 | 12560 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 37680 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0087553 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE |  | 43016 | 2240 | 1903137 | 13945 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 27890 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0088207 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | JUMPER |  | 43016 | 2240 | 1900838 | 11229 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 11229 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0087384 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE |  | 43016 | 2240 | 1902478 | 19435 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 57 | 1106870 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0087940 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE |  | 43017 | 141 | 1901218 | 17881 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 18 | 321858 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0087473 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | SWITCH |  | 43017 | 141 | 1903332 | 25429 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 49 | 974037 | Clear;32-90 F | Other | Broken- wire on ground | 17-0088299 | OH | Sus | 0 | 2017 | OCT | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | JUMPER |  | 43016 | 2240 | 1907299 | 19803 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 5 | 99015 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0089504 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 43016 | 2317 | 1901016 | 9687 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 90 | 871830 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0087420 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 43016 | 2317 | 1900887 | 19569 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 19569 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0087394 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 43017 | 17 | 1900803 | 19704 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 43 | 847272 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0087372 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | RECLOSER |  | 43016 | 2317 | 1901028 | 21108 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 53 | 136988 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0087422 | OH | Sus | 0 | 2017 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 43017 | 17 | 1900801 | 19756 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 59268 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0087371 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | FULTON-1102 | 42561102 | FUSE |  | 43016 | 2150 | 1897466 | 2410 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 87406 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 17-0085970 | OH | Sus | 0 | 2017 | OCT | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | CLOVERDALE-1102 | 42821102 | FUSE |  | 43016 | 2324 | 1906698 | 19846 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 27 | 535842 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0089338 | OH | Sus | 0 | 2017 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | CLOVERDALE-1102 | 42821102 | FUSE |  | 43017 | 30 | 1900344 | 7846 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 31384 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0087204 | OH | Sus | 0 | 2017 | OCT | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | RECLOSER |  | 43017 | 446 | 1895664 | 843 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2466 | 312981 | Strong Winds-Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 17-0085394 | OH | Sus | 31356040 | 2017 | OCT | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 2 | GABILAN-1101 | 182331101 | JUMPER |  | 42989 | 1751 | 1875982 | 436 | Distribution Circuit | Environmental/External | Lightning | 36 | 13596 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0077860 | OH | Sus | 0 | 2017 | SEP | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 42981 | 2113 | 1869254 | 1098 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 3294 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0075732 | OH | Sus | 31348848 | 2017 | SEP | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 42981 | 735 | 1867841 | 1091 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 24002 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0075541 | OH | Sus | 0 | 2017 | SEP | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | OTHER |  | 42989 | 626 | 1875124 | 404 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 19830 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0077544 | OH | Sus | 0 | 2017 | SEP | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE |  | 42989 | 314 | 1875033 | 805 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 15295 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0077592 | OH | Sus | 0 | 2017 | SEP | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 2 | SARATOGA 1103 | 83371103 | JUMPER |  | 42989 | 327 | 1874784 | 713 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 7184 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0077619 | OH | Sus | 0 | 2017 | SEP | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | GREENBRAE 1103 | 43091103 | FUSE |  | 42989 | 420 | 1874799 | 548 | Distribution Circuit | Vegetation | Tree - branch fell on line | 80 | 13896 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0077470 | OH | Sus | 31350105 | 2017 | SEP | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | MENLO-1102 | 24131102 | JUMPER |  | 42981 | 1626 | 1869183 | 1341 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4023 | Clear-Heat Wave;Above 90 | Conductor- Overhead | Broken- wire on ground | 17-0075627 | OH | Sus | 0 | 2017 | SEP | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 2 | MENLO-1102 | 24131102 | JUMPER |  | 42981 | 828 | 1867889 | 1231 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2750 | Clear-Heat Wave;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0075505 | OH | Sus | 0 | 2017 | SEP | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | SNEATH LANE-1106 | 22721106 | OTHER |  | 42989 | 1904 | 1876236 | 488 | Distribution Circuit | Environmental/External | Lightning | 4032 | 116781 | Partly Cloudy-Drizzle-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0077883 | OH | Sus | 0 | 2017 | SEP | Yes | Line to Ground | Yes | Yes
SACRAMENTO | Tier 2 | BROWNS VALLEY-1101 | 152921101 | JUMPER |  | 42981 | 1855 | 1869070 | 115 | Distribution Circuit | Equipment Failure/Involved | Overhead | 582 | 55325 | Partly Cloudy-Heat Wave;Above 90 | Conductor- Overhead | Broken- wire on ground | 17-0075611 | OH | Sus | 0 | 2017 | SEP | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | PLACER-1103 | 152461103 | JUMPER |  | 42981 | 717 | 1867829 | 218 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 218 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0075507 | OH | Sus | 31349005 | 2017 | SEP | Yes | Open Circuit | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 42989 | 1246 | s1301537 | 404 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 33 | 11107 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 17-0077730 | OH | Sus | 31350305 | 2017 | SEP | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | FUSE |  | 43309 | 108 | 142200 | 688 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 19264 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 18-0064531 | OH | Sus | 43422806 | 2018 | JUL | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | OTHER |  | 43309 | 838 | 142285 | 394 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2321 | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 18-0064573 | OH | Sus | 43422814 | 2018 | JUL | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | WYANDOTTE-1107 | 102911107 | FUSE |  | 43309 | 1808 | 142676 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 6264 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 18-0064616 | OH | Sus | 0 | 2018 | JUL | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1101 | 103401101 | FUSE |  | 43309 | 449 | 148785 | 13955 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 18 | 72 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 18-0066705 | OH | Sus | 0 | 2018 | JUL | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1101 | 103401101 | FUSE |  | 43309 | 449 | 146126 | 14779 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 10 | 80 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 18-0065462 | OH | Sus | 0 | 2018 | JUL | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1101 | 103401101 | FUSE |  | 43309 | 449 | 146134 | 14874 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 30 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 18-0065468 | OH | Sus | 0 | 2018 | JUL | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1101 | 103401101 | FUSE |  | 43309 | 449 | 146141 | 14885 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 31 | 775 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 18-0065470 | OH | Sus | 0 | 2018 | JUL | Yes | Force Out | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43309 | 633 | 142227 | 417 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 15429 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 18-0064545 | OH | Sus | 0 | 2018 | JUL | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 43175 | 205 | 45189 | 678 | Distribution Circuit | Vegetation | Tree - branch fell on line | 263 | 73608 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023231 | OH | Sus | 43301937 | 2018 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 43175 | 629 | 45299 | 249 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 3924 | Partly Cloudy-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023295 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 43175 | 1202 | 45737 | 334 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 8196 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023410 | OH | Sus | 43302840 | 2018 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | CALPELLA-1101 | 43411101 | FUSE |  | 43175 | 453 | 45212 | 447 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 447 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023246 | OH | Sus | 43302651 | 2018 | MAR | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | MESA-1103 | 182821103 | SWITCH |  | 43175 | 1653 | 46189 | 11 | Distribution Circuit | Company Initiated | Return Circuit Normal | 1 | 11 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 18-0023230 | OH | Sus | 31384355 | 2018 | MAR | Yes | None | Yes | No
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | FUSE |  | 43175 | 108 | 45156 | 620 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 19220 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023225 | OH | Sus | 43301932 | 2018 | MAR | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | RISING RIVER-1101 | 103551101 | RECLOSER |  | 43175 | 1013 | 45549 | 429 | Distribution Circuit | Vegetation | Tree - branch fell on line | 536 | 123960 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023409 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BURNEY-1101 | 103311101 | RECLOSER |  | 43175 | 644 | 45248 | 188 | Distribution Circuit | Environmental/External | Ice or snow | 66 | 8092 | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 18-0023263 | OH | Sus | 31384484 | 2018 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | PIT NO 3-2101 | 103732101 | OCB |  | 43175 | 954 | 45480 | 466 | Distribution Circuit | Vegetation | Tree - branch fell on line | 155 | 57958 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023329 | OH | Sus | 43302933 | 2018 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43175 | 859 | 45398 | 1192 | Distribution Circuit | Vegetation | Tree - fell into line | 126 | 198450 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023498 | OH | Sus | 0 | 2018 | MAR | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43175 | 1523 | 46098 | 1541 | Distribution Circuit | Vegetation | Tree - fell into line | 247 | 65694 | Overcast-Fog-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 18-0023752 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 43175 | 1333 | 45927 | 1532 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 12256 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023501 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43175 | 842 | 46170 | 3015 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 93465 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023563 | OH | Sus | 0 | 2018 | MAR | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | JUMPER |  | 43175 | 1141 | 46981 | 2936 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 23488 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 18-0023800 | OH | Sus | 0 | 2018 | MAR | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 43175 | 1141 | 45734 | 1913 | Distribution Circuit | Environmental/External | Ice or snow | 95 | 181735 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 18-0023586 | OH | Sus | 0 | 2018 | MAR | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 43175 | 1533 | 46268 | 2749 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 131952 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023723 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 43175 | 1003 | 45615 | 3470 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 262819 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023411 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43175 | 1140 | 46114 | 1979 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 120719 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 18-0023539 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43175 | 950 | 46111 | 3337 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 90099 | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 18-0023538 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | RECLOSER |  | 43175 | 820 | 45315 | 3571 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1257 | 2290224 | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on object | 18-0023279 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43175 | 834 | 47271 | 3461 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 10383 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023873 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 43175 | 1145 | 45676 | 3268 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 13072 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023750 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | ECHO SUMMIT-1101 | 158031101 | FUSE |  | 43175 | 738 | 45625 | 4673 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 322437 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 18-0023361 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | OCB |  | 43175 | 1225 | 45766 | 1706 | Distribution Circuit | Vegetation | Tree - fell into line | 2184 | 777200 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023399 | OH | Sus | 0 | 2018 | MAR | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | OCB |  | 43175 | 2036 | 46283 | 1476 | Distribution Circuit | Vegetation | Tree - fell into line | 3242 | 622369 | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 18-0023620 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43175 | 918 | 45439 | 975 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 10725 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 18-0023446 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 43175 | 804 | 45335 | 2068 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 102268 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023318 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER |  | 43175 | 516 | 45306 | 848 | Distribution Circuit | Vegetation | Tree - fell into line | 603 | 157730 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023258 | OH | Sus | 0 | 2018 | MAR | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | STANISLAUS-1701 | 162821701 | RECLOSER |  | 43175 | 1058 | 45419 | 2936 | Distribution Circuit | Vegetation | Tree - fell into line | 912 | 271973 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023352 | OH | Sus | 0 | 2018 | MAR | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1701 | 162821701 | FUSE |  | 43175 | 1751 | 46238 | 2463 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 38310 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023711 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 43175 | 559 | 45235 | 662 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 19198 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 18-0023260 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 43175 | 715 | 45282 | 418 | Distribution Circuit | Vegetation | Tree - branch fell on line | 281 | 117458 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023317 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 43175 | 1201 | 46634 | 2838 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 28380 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 18-0023735 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 43175 | 741 | 45310 | 507 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 11154 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 18-0023313 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 43175 | 1341 | 45949 | 501 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 16032 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023526 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 43175 | 1839 | 46308 | 2597 | Distribution Circuit | Vegetation | Tree - branch fell on line | 171 | 266265 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 18-0023618 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER |  | 43175 | 1255 | 45876 | 1523 | Distribution Circuit | Vegetation | Tree - fell into line | 418 | 636614 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023419 | OH | Sus | 0 | 2018 | MAR | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 43175 | 1913 | 46305 | 1212 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 25452 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | On Ground | 18-0023755 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 43175 | 1054 | 47310 | 4496 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 26976 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 18-0023880 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER |  | 43175 | 1321 | 45911 | 3168 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 278099 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023619 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER |  | 43175 | 1154 | 45697 | 2002 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 155249 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023488 | OH | Sus | 0 | 2018 | MAR | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 43175 | 812 | 45340 | 3360 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 168000 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 18-0023303 | OH | Sus | 31384483 | 2018 | MAR | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER |  | 43175 | 1042 | 45719 | 3347 | Distribution Circuit | Vegetation | Tree - fell into line | 1472 | 1227672 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 18-0023417 | OH | Sus | 0 | 2018 | MAR | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | TIGER CREEK 0201 | 161380201 | FUSE |  | 43175 | 1447 | 46059 | 4380 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 13140 | Overcast-Drizzle;32-90 F | Insulator | Broken- wire on object | 18-0023507 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 43175 | 1636 | 46176 | 3054 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 76350 | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 18-0023578 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 43175 | 1050 | 45729 | 3331 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 63250 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023736 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 43175 | 1606 | 46157 | 2919 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 117621 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0023561 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 43175 | 1705 | 46261 | 4132 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 49584 | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 18-0023751 | OH | Sus | 0 | 2018 | MAR | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 43175 | 939 | 46303 | 2141 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 36397 | Overcast-Fog;Below 32 F | Pole-Wood | Broken- wire on ground | 18-0023597 | OH | Sus | 0 | 2018 | MAR | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | FUSE |  | 43175 | 1231 | 45965 | 654 | Distribution Circuit | Vegetation | Tree - branch fell on line | 100 | 17304 | Overcast-Fog;Below 32 F | Pole-Wood | Broken- wire on ground | 18-0023455 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER |  | 43175 | 1421 | 46035 | 1776 | Distribution Circuit | Vegetation | Tree - fell into line | 614 | 856508 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 18-0023546 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 43175 | 1153 | 45960 | 404 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3636 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 18-0023545 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Ground | Yes | Yes
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 43175 | 1421 | 46156 | 1645 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 27965 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 18-0023559 | OH | Sus | 0 | 2018 | MAR | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 43175 | 1111 | 45874 | 1835 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 135790 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 18-0023543 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 43175 | 1423 | 46334 | 1643 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 221805 | Overcast-Fog;Below 32 F | Crossarm- Wood | Broken- wire on ground | 18-0023616 | OH | Sus | 0 | 2018 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | RECLOSER |  | 43433 | 48 | 227377 | 1118 | Distribution Circuit | Vegetation | Tree - fell into line | 417 | 462449 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0104665 | OH | Sus | 31416754 | 2018 | NOV | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | FUSE |  | 43412 | 1239 | 211702 | 89 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 848 | 51106 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 18-0098270 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | JUMPER |  | 43433 | 1213 | 228898 | 1555 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1555 | Partly Cloudy-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0105438 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2105 | 83252105 | FUSE |  | 43433 | 854 | 228337 | 2268 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 49896 | Overcast-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 18-0105146 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 43433 | 210 | 227530 | 2695 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 63343 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0105138 | OH | Sus | 31416754 | 2018 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE |  | 43425 | 1541 | 220657 | 570 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 5700 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0102192 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 43425 | 1505 | 220593 | 4167 | Distribution Circuit | Equipment Failure/Involved | Overhead | 123 | 216927 | Overcast-Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 18-0101966 | OH | Sus | 31416550 | 2018 | NOV | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | FELTON-0401 | 83140401 | FUSE |  | 43433 | 819 | 228367 | 1711 | Distribution Circuit | Equipment Failure/Involved | Overhead | 60 | 102660 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0105156 | OH | Sus | 43586641 | 2018 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | RECLOSER |  | 43433 | 740 | 227969 | 1778 | Distribution Circuit | Vegetation | Tree - fell into line | 267 | 117726 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0104810 | OH | Sus | 31416754 | 2018 | NOV | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | FELTON-0401 | 83140401 | FUSE |  | 43433 | 1512 | 229261 | 1268 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 20288 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0105440 | OH | Sus | 43586641 | 2018 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | TRIP-SAVER |  | 43433 | 1026 | 228660 | 1759 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 84432 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0105091 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 43412 | 1202 | 211662 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 10810 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0098292 | OH | Sus | 43534781 | 2018 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 43433 | 1031 | 228670 | 429 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3432 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0105107 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 43425 | 1051 | 219955 | 634 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 16484 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0101851 | OH | Sus | 43584947 | 2018 | NOV | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 43433 | 959 | 228569 | 1815 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 21780 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0105322 | OH | Sus | 43586641 | 2018 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 43433 | 659 | 227935 | 1626 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 85596 | Strong Winds-Heavy Rain-Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0104884 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 43433 | 753 | 228017 | 2045 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 22495 | Overcast-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 18-0104854 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 43433 | 754 | 228179 | 1646 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 106771 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0105021 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 43433 | 837 | 228279 | 562 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 21356 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0104981 | OH | Sus | 43586552 | 2018 | NOV | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 43412 | 931 | 211438 | 902 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 8118 | Strong Winds-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0098245 | OH | Sus | 0 | 2018 | NOV | Yes | Force Out | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER |  | 43433 | 818 | 228121 | 1752 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1752 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0105018 | OH | Sus | 31416745 | 2018 | NOV | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 43433 | 822 | 228166 | 509 | Distribution Circuit | Vegetation | Tree - branch fell on line | 143 | 53737 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0104832 | OH | Sus | 31416747 | 2018 | NOV | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE |  | 43412 | 945 | 211460 | 423 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2538 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0098214 | OH | Sus | 43533911 | 2018 | NOV | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER |  | 43433 | 36 | 227355 | 748 | Distribution Circuit | Vegetation | Tree - fell into line | 350 | 79638 | Clear;32-90 F | Conductor- Overhead | On Ground | 18-0104657 | OH | Sus | 31417162 | 2018 | NOV | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE |  | 43425 | 216 | 219464 | 579 | Distribution Circuit | 3rd Party | Gun Shot | 78 | 4834 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0101683 | OH | Sus | 43584639 | 2018 | NOV | Yes | Open Circuit | Yes | Yes
LOS PADRES | Tier 2 | OCEANO-1104 | 182601104 | FUSE |  | 43433 | 222 | 227529 | 855 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 12825 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0104799 | OH | Sus | 43587912 | 2018 | NOV | Yes | Line to Ground | Yes | No
MISSION | Tier 3 | CASTRO VALLEY-1108 | 14091108 | TRIP-SAVER |  | 43433 | 2218 | 229734 | 1062 | Distribution Circuit | 3rd Party | Vehicle | 67 | 57285 | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 18-0105428 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE |  | 43433 | 727 | 227916 | 554 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 23822 | Overcast-Heavy Rain-Lightning-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0104908 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2103 | 43432103 | FUSE |  | 43433 | 945 | 228416 | 5925 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 22241 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0104940 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | JUMPER |  | 43412 | 1220 | 211569 | 265 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 265 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0098264 | OH | Sus | 0 | 2018 | NOV | Yes | None | Yes | No
NORTH VALLEY | Tier 2 | CLARK ROAD-1102 | 103091102 | JUMPER |  | 43412 | 1050 | 214521 | 8866 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 17732 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 18-0099388 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | CLARK ROAD-1102 | 103091102 | FUSE |  | 43412 | 1050 | 214503 | 10465 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 18 | 188370 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 18-0099384 | OH | Sus | 0 | 2018 | NOV | Yes | None | Yes | No
NORTH VALLEY | Tier 2 | CLARK ROAD-1102 | 103091102 | RECLOSER |  | 43412 | 1044 | 211509 | 20092 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 148 | 2672214 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0098208 | OH | Sus | 0 | 2018 | NOV | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | BIG BEND-1101 | 103751101 | SWITCH |  | 43412 | 746 | 212778 | 42326 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 206 | 8647832 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 18-0098064 | OH | Sus | 0 | 2018 | NOV | Yes | None | Yes | No
NORTH VALLEY | Tier 2 | NOTRE DAME-1104 | 102041104 | TRIP-SAVER |  | 43412 | 1907 | 211953 | 22615 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 44 | 995060 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0098438 | OH | Sus | 0 | 2018 | NOV | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | RECLOSER |  | 43433 | 114 | 227403 | 171 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1053 | 180063 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | On Ground | 18-0104677 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 43433 | 737 | 227952 | 633 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 32283 | Overcast-Heavy Rain-Lightning-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0104871 | OH | Sus | 43587430 | 2018 | NOV | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | HALF MOON BAY-1101 | 24101101 | FUSE |  | 43412 | 1644 | 211874 | 148 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 1184 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0098441 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | FUSE |  | 43433 | 1032 | 228677 | 656 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 11152 | Partly Cloudy-Fog-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 18-0105035 | OH | Sus | 0 | 2018 | NOV | Yes | Force Out | Yes | Yes
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 43433 | 1000 | 228573 | 483 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 6762 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 18-0104944 | OH | Sus | 31416672 | 2018 | NOV | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SUMMIT-1102 | 152591102 | OCB |  | 43433 | 1133 | 228831 | 1448 | Distribution Circuit | Equipment Failure/Involved | Overhead | 292 | 64558 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0105014 | OH | Sus | 0 | 2018 | NOV | Yes | Multi-Fault | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | TRIP-SAVER |  | 43433 | 1301 | 229048 | 720 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 40142 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0105199 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | RINCON-1104 | 43321104 | FUSE |  | 43433 | 1611 | 229419 | 1329 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 31896 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0105283 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | TRIP-SAVER |  | 43425 | 521 | 219567 | 787 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 42298 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0101716 | OH | Sus | 43584951 | 2018 | NOV | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1702 | 163451702 | OCB |  | 43433 | 1527 | 229315 | 1389 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4024 | 523222 | Overcast-Drizzle-Lightning;32-90 F | Conductor- Overhead | Broken- wire on object | 18-0105202 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | FUSE |  | 43433 | 752 | 228013 | 336 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 336 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0104893 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 43433 | 8 | 227311 | 483 | Distribution Circuit | Vegetation | Tree - fell into line | 403 | 194649 | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 18-0104659 | OH | Sus | 0 | 2018 | NOV | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 43433 | 413 | 227701 | 987 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 29079 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 18-0104767 | OH | Sus | 0 | 2018 | NOV | Yes | Line to Line | Yes | No
MISSION | Tier 3 | SAN RAMON-2108 | 14232108 | RECLOSER |  | 43387 | 2305 | 195161 | 686 | Distribution Circuit | Vegetation | Tree - branch fell on line | 90 | 54411 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0090336 | OH | Sus | 43506702 | 2018 | OCT | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1101 | 102931101 | FUSE |  | 43387 | 1123 | 194784 | 397 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 945 | Clear-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 18-0090193 | OH | Sus | 0 | 2018 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | FUSE |  | 43387 | 1815 | 194986 | 1048 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 8688 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 18-0090287 | OH | Sus | 43506621 | 2018 | OCT | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER |  | 43387 | 1956 | 195020 | 2893 | Distribution Circuit | Vegetation | Tree - fell into line | 609 | 1694964 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 18-0090290 | OH | Sus | 0 | 2018 | OCT | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER |  | 43387 | 1936 | 195004 | 2635 | Distribution Circuit | Vegetation | Tree - fell into line | 623 | 1641605 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 18-0090288 | OH | Sus | 0 | 2018 | OCT | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE |  | 43692 | 1444 | 513553 | 72 | Distribution Circuit | Equipment Failure/Involved | Overhead | 88 | 6336 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0088407 | OH | Sus | 0 | 2019 | AUG | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | RECLOSER |  | 43498 | 322 | 286174 | 4108 | Distribution Circuit | Equipment Failure/Involved | Overhead | 441 | 1790658 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0016877 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | FUSE |  | 43498 | 2 | 285892 | 1050 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 75600 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0016851 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | FUSE |  | 43498 | 834 | 286973 | 3086 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 15430 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017171 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | HATTON-1101 | 182291101 | FUSE |  | 43498 | 1306 | 287423 | 2931 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 287238 | Heavy Rain-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017244 | OH | Sus | 43665416 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | FUSE |  | 43513 | 620 | 315261 | 820 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 50840 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025123 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | FUSE |  | 43511 | 913 | 311642 | 1927 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3854 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024123 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | OTHER |  | 43509 | 1427 | 305024 | 4666 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 37826 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 19-0022470 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 2 | LAURELES-1112 | 182371112 | FUSE |  | 43509 | 838 | 304618 | 2003 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 324263 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022271 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE |  | 43498 | 103 | 285962 | 2331 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 77094 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0016970 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE |  | 43509 | 532 | 307974 | 4890 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 180930 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022988 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE |  | 43509 | 532 | 310107 | 3680 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 353280 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023478 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE |  | 43498 | 243 | 286316 | 1149 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 70861 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0016999 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE |  | 43509 | 532 | 311922 | 5076 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 96444 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0023971 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 43498 | 258 | 286135 | 2199 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 52824 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017224 | OH | Sus | 43665408 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 43509 | 734 | 312465 | 6099 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 6099 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024150 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 43509 | 734 | 311893 | 3494 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 139760 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023961 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | RECLOSER |  | 43498 | 357 | 287686 | 2807 | Distribution Circuit | Vegetation | Tree - fell into line | 104 | 160135 | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017217 | OH | Sus | 31424211 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 43509 | 734 | 308658 | 6298 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 37788 | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0023140 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE |  | 43498 | 55 | 286920 | 3747 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 71193 | Overcast-Heavy Rain-Strong Winds;32-90 F | Insulator | Broken- wire on ground | 19-0017100 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | TRANSFORMER |  | 43498 | 1315 | 287507 | 1900 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 9525 | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0017178 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE |  | 43509 | 1327 | 304621 | 2899 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 201986 | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023655 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | FUSE |  | 43509 | 1058 | 305177 | 2051 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 28714 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022432 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | FUSE |  | 43498 | 338 | 286281 | 1847 | Distribution Circuit | Vegetation | Tree - fell into line | 383 | 707401 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0016919 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | OCB |  | 43509 | 1052 | 303879 | 2058 | Distribution Circuit | Vegetation | Tree - fell into line | 1959 | 957728 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022134 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | RECLOSER |  | 43498 | 1702 | 287895 | 1602 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 26675 | Partly Cloudy-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017292 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 43509 | 739 | 309175 | 5058 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 60696 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023248 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 43498 | 1416 | 287589 | 1794 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 20673 | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017327 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | JUMPER |  | 43509 | 1926 | 312811 | 2995 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 8175 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024243 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 43498 | 242 | 286104 | 844 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 29540 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0016957 | OH | Sus | 31424211 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 43509 | 729 | 308941 | 4969 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 64597 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023191 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 43509 | 729 | 314849 | 6124 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 42868 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024691 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 43509 | 1918 | 305568 | 2918 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 32098 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023378 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 43512 | 556 | 313437 | 238 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2142 | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024443 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE |  | 43509 | 1816 | 305595 | 2790 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 21423 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023084 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE |  | 43509 | 710 | 310527 | 4978 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 104538 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023595 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 43509 | 729 | 305820 | 4969 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 109318 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022677 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER |  | 43509 | 807 | 303128 | 7714 | Distribution Circuit | Vegetation | Tree - fell into line | 327 | 1074917 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021875 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 43498 | 724 | 287587 | 2126 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 174332 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017265 | OH | Sus | 43665408 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 43509 | 729 | 305708 | 3582 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 75222 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022583 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 43509 | 739 | 314852 | 6184 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 179336 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024692 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | RECLOSER |  | 43498 | 118 | 286139 | 2515 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3301 | 3896741 | Overcast-Heavy Rain-Strong Winds;32-90 F | Switch (OH) | Broken- wire on ground | 19-0016874 | OH | Sus | 31424211 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | OCB |  | 43509 | 817 | 303177 | 4793 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 221714 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021880 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | OCB |  | 43510 | 507 | 306671 | 4892 | Distribution Circuit | Vegetation | Tree - fell into line | 4847 | 1473842 | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022824 | OH | Sus | 31425388 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | OCB |  | 43498 | 330 | 286230 | 3602 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5926 | 1943971 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0016884 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | OCB |  | 43523 | 43 | 325967 | 455 | Distribution Circuit | Vegetation | Tree - fell into line | 849 | 165487 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028656 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 43509 | 1308 | 304574 | 3103 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 118965 | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023266 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE |  | 43509 | 1731 | 308454 | 5450 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 87200 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023117 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | JUMPER |  | 43510 | 658 | 307269 | 3482 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 24374 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023087 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE |  | 43509 | 1131 | 304147 | 2073 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 43896 | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0023065 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE |  | 43509 | 511 | 310350 | 4940 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 192660 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023555 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE |  | 43510 | 552 | s1417125 | 1900 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 199500 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024014 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE |  | 43498 | 354 | 286363 | 2295 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 139500 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017123 | OH | Sus | 31424211 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE |  | 43510 | 601 | 307620 | 2069 | Distribution Circuit | Equipment Failure/Involved | Overhead | 156 | 271244 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023034 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE |  | 43509 | 1009 | 303622 | 6204 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 55836 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022936 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE |  | 43509 | 828 | 312287 | 6415 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 301505 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024100 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | TRIP-SAVER |  | 43509 | 828 | 303242 | 3206 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 327012 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023894 | OH | Sus | 43677321 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2105 | 182222105 | FUSE |  | 43498 | 437 | 286379 | 3581 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 89931 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017264 | OH | Sus | 31424211 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 43510 | 950 | 308325 | 1900 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 11400 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0023331 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | 83500401 | 83500401 | FUSE |  | 43506 | 1343 | 298992 | 484 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 9196 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020758 | OH | Sus | 43676142 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | OTHER |  | 43511 | 1737 | 312721 | 1408 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 11881 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024269 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 43500 | 636 | 289615 | 324 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 19116 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017769 | OH | Sus | 31424216 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | 83500401 | 83500401 | JUMPER |  | 43498 | 1714 | 287911 | 1103 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 7721 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017333 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2102 | 83252102 | FUSE |  | 43510 | 1803 | 310520 | 2587 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 12935 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024520 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 43510 | 1235 | 309634 | 2300 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 248400 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023424 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 43511 | 1359 | 312294 | 1681 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 33620 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024654 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | FELTON-0401 | 83140401 | TRANSFORMER |  | 43510 | 1635 | 310209 | 4229 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 4229 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024114 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | RECLOSER |  | 43498 | 425 | 286360 | 415 | Distribution Circuit | Vegetation | Tree - branch fell on line | 267 | 110805 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0016908 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | FELTON-0401 | 83140401 | FUSE |  | 43510 | 1243 | 309139 | 1547 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 23205 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023240 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 43510 | 216 | 306571 | 3514 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 35140 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024449 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 43509 | 848 | 303431 | 1922 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 21322 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0021965 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 43498 | 1434 | 287731 | 1176 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 50568 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017233 | OH | Sus | 43665416 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 43510 | 227 | 306382 | 2088 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7464 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023080 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE |  | 43498 | 1804 | 288221 | 1189 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 10701 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017371 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 43509 | 649 | 302920 | 752 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 12032 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0021958 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE |  | 43511 | 1650 | 312641 | 1208 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 9664 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024197 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | TRIP-SAVER |  | 43498 | 1411 | 287808 | 1207 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 13657 | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017259 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | TRIP-SAVER |  | 43500 | 730 | 289633 | 471 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 32499 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017871 | OH | Sus | 31424216 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 43509 | 650 | 302922 | 670 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3445 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022151 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 43509 | 2248 | 305833 | 5541 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 437093 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022690 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 43510 | 213 | 306350 | 3865 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 12540 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023587 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE |  | 43523 | 518 | 326347 | 2097 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5079 | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0028797 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 43511 | 1032 | 311864 | 356 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1068 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 19-0023950 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 43510 | 414 | 306780 | 2092 | Distribution Circuit | Vegetation | Tree - fell into line | 666 | 531645 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023038 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 43500 | 1208 | 290216 | 1416 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2832 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018112 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 43510 | 337 | 306960 | 1941 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 83440 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023290 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 43510 | 1419 | 310290 | 2096 | Distribution Circuit | Vegetation | Tree - branch fell on line | 61 | 32428 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023672 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER |  | 43510 | 1229 | 308769 | 1857 | Distribution Circuit | Vegetation | Tree - fell into line | 146 | 234460 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023219 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 43509 | 1544 | 305134 | 276 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1380 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022520 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 43510 | 419 | 306746 | 2028 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 24336 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024032 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 43510 | 415 | 306745 | 2392 | Distribution Circuit | Vegetation | Tree - fell into line | 430 | 670999 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0022802 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 43500 | 601 | 289532 | 637 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1274 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017748 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 43512 | 1721 | 314835 | 1226 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 12260 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024742 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 43500 | 1100 | 290040 | 1668 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 16680 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018007 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 43506 | 642 | 298482 | 951 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 22824 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0020625 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 43498 | 748 | 286838 | 517 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3102 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017058 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | OTHER |  | 43509 | 1713 | 305362 | 1743 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 50714 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022562 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 43522 | 2132 | 325323 | 946 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 8514 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028597 | OH | Sus | 43685094 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 43510 | 558 | 308250 | 3342 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 30078 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023421 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 43498 | 2327 | 288286 | 1123 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 14599 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | On Ground | 19-0017469 | OH | Sus | 31424211 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 43505 | 2250 | 297547 | 980 | Distribution Circuit | Vegetation | Tree - fell into line | 985 | 191758 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020495 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 43510 | 629 | 307462 | 467 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 25685 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022890 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | JUMPER |  | 43510 | 606 | 308087 | 1808 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 23868 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023017 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 43523 | 1332 | 327115 | 1321 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 48747 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0029083 | OH | Sus | 43687242 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 43510 | 508 | 306959 | 3502 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 21012 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024523 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | TRIP-SAVER |  | 43523 | 221 | 326153 | 631 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 20772 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028703 | OH | Sus | 43685094 | 2019 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 43510 | 739 | 307463 | 884 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 36244 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023166 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 43509 | 2122 | 305747 | 4208 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 260896 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022695 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 43498 | 543 | 286625 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 15017 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017082 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 43509 | 2359 | 311558 | 4051 | Distribution Circuit | Environmental/External | Flood/Erosion | 44 | 178244 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0023855 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 43513 | 1302 | 315896 | 215 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 430 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025152 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 43501 | 1258 | 292704 | 497 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1491 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018645 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | TRIP-SAVER |  | 43509 | 2359 | 311487 | 3990 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 87780 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023839 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 43509 | 2359 | 311485 | 4193 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 142562 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023837 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 43509 | 2359 | 311495 | 4134 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 53742 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023843 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 43509 | 2359 | 309562 | 3912 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 11736 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023339 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER |  | 43510 | 6 | 306012 | 2619 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 50318 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0022717 | OH | Sus | 31425395 | 2019 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 43510 | 605 | 307160 | 1345 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 69940 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023198 | OH | Sus | 43677333 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | RECLOSER |  | 43510 | 143 | 306368 | 2432 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 77824 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022748 | OH | Sus | 31425395 | 2019 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE |  | 43509 | 802 | 303116 | 358 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 14678 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021961 | OH | Sus | 31425395 | 2019 | FEB | Yes | Open Circuit | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE |  | 43523 | 541 | 326371 | 664 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3984 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028735 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
DIABLO | Tier 3 | CLAYTON-2212 | 12022212 | FUSE |  | 43513 | 753 | 315343 | 302 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 4530 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025051 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
DIABLO | Tier 2 | SOBRANTE-1102 | 14671102 | FUSE |  | 43523 | 40 | 325950 | 693 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 28413 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028748 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
DIABLO | Tier 2 | ROSSMOOR-1101 | 14161101 | FUSE |  | 43511 | 3 | 311057 | 661 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 27762 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023808 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | ORINDA-0401 | 12350401 | OTHER |  | 43510 | 2212 | 311050 | 240 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 5406 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on object | 19-0023752 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 2 | OAKLAND K SUB | 1210 | OCB |  | 43510 | 1113 | 308726 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 10992 | 808191 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023258 | OH | Sus | 31425494 | 2019 | FEB | Yes | Line to Line | Yes | No
EAST BAY | Tier 2 | RIDGE 0401 | 12840401 | FUSE |  | 43498 | 602 | 286601 | 891 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 53460 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0016981 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | FUSE |  | 43500 | 1359 | 296545 | 8250 | Distribution Circuit | Environmental/External | Ice or snow | 4 | 40636 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018005 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER |  | 43500 | 256 | 289407 | 10624 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 150788 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017740 | OH | Sus | 43669499 | 2019 | FEB | Yes | Line to Line | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | FUSE |  | 43500 | 506 | 289478 | 3701 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 111030 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018401 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | RECLOSER |  | 43500 | 1359 | 290490 | 7414 | Distribution Circuit | Equipment Failure/Involved | Overhead | 303 | 1040880 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0018005 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
FRESNO | Tier 2 | DUNLAP-1103 | 254061103 | FUSE |  | 43505 | 955 | 296826 | 375 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 375 | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0020277 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
FRESNO | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER |  | 43500 | 256 | 292038 | 3518 | Distribution Circuit | Environmental/External | Ice or snow | 354 | 969928 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017740 | OH | Sus | 43669499 | 2019 | FEB | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | AUBERRY-1102 | 254151102 | FUSE |  | 43513 | 2247 | 317102 | 693 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 24255 | Partly Cloudy-Fog;Below 32 F | Connector or Splice (OH) | Broken- wire on ground | 19-0025522 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
FRESNO | Tier 3 | AUBERRY-1101 | 254151101 | FUSE |  | 43510 | 1357 | 309515 | 1625 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 63402 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0023635 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 43523 | 1037 | 326844 | 1590 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 25471 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0029138 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER |  | 43512 | 1154 | 314111 | 347 | Distribution Circuit | Vegetation | Tree - fell into line | 316 | 100494 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024570 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 43510 | 726 | 307384 | 3144 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12576 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023207 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 43505 | 1304 | 297028 | 386 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 758 | Overcast-Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 19-0020356 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 43522 | 745 | 324064 | 5825 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 34950 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028126 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 43523 | 321 | 326234 | 2327 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 16289 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0029004 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER |  | 43508 | 2128 | 301150 | 1031 | Distribution Circuit | Vegetation | Tree - fell into line | 611 | 68487 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021644 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 43498 | 240 | 286092 | 662 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 7282 | Partly Cloudy-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0016978 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 43509 | 1259 | 304548 | 2793 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 30723 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022525 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 43508 | 2128 | 304443 | 2200 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 37400 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022211 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 43509 | 1008 | 303457 | 1889 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 26446 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022315 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 43498 | 724 | 286748 | 312 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 312 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017015 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | KONOCTI-1102 | 43311102 | FUSE |  | 43509 | 1903 | 305550 | 1032 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 51239 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022577 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | KONOCTI-1102 | 43311102 | FUSE |  | 43522 | 817 | 324061 | 605 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2420 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028161 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE |  | 43522 | 731 | 323924 | 295 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 7375 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028170 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | UKIAH-1114 | 42771114 | FUSE |  | 43509 | 138 | 301798 | 5337 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 112077 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021840 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | RECLOSER |  | 43508 | 2010 | 301078 | 4348 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 120301 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021577 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 43509 | 1054 | 303948 | 4614 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 240124 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022122 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | FUSE |  | 43523 | 906 | 326674 | 452 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4068 | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0028929 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 43510 | 805 | 307595 | 3286 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 19716 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023437 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | JUMPER |  | 43522 | 2255 | 325726 | 937 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 50542 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028688 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER |  | 43510 | 1843 | 310646 | 1290 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 64164 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023621 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE |  | 43522 | 627 | 323875 | 414 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 1342 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028100 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 43522 | 2316 | 325565 | 969 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 21107 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028724 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | SWITCH |  | 43510 | 645 | 309266 | 1725 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 36225 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023262 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 43522 | 2332 | 325724 | 1157 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 26611 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0029001 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 43523 | 4 | 325930 | 2135 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 32399 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028962 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 43508 | 2131 | 301312 | 2712 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 8136 | Clear;32-90 F | Conductor- Overhead | On Ground | 19-0021652 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | JUMPER |  | 43522 | 709 | 324052 | 435 | Distribution Circuit | Vegetation | Tree - fell into line | 225 | 97875 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028121 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | OTHER |  | 43508 | 2218 | 301347 | 2582 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 168090 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021694 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 43522 | 2213 | 325435 | 1159 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8906 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0029110 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 43508 | 2156 | 301237 | 2744 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 24696 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022095 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 43508 | 2152 | 301209 | 953 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 19060 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022224 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 43522 | 2333 | 326174 | 1167 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 24507 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028957 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 43510 | 1414 | 309608 | 1479 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7395 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023579 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 43523 | 224 | 326677 | 1074 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4296 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0029014 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 43511 | 1911 | 312909 | 1150 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 16100 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024370 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 43508 | 1906 | 301003 | 4154 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 58156 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021585 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | FUSE |  | 43508 | 1829 | 300962 | 1633 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 74161 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0021579 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 43508 | 2156 | 302591 | 3667 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 88008 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021761 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MENDOCINO-1101 | 42951101 | FUSE |  | 43508 | 1714 | 300901 | 4355 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 23593 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 19-0021565 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 43508 | 1651 | 301790 | 4311 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 303710 | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 19-0021717 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | JUMPER |  | 43508 | 1914 | 310247 | 4225 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8450 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023527 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | JUMPER |  | 43509 | 620 | 302883 | 3260 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3260 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022379 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 43508 | 2111 | 302651 | 2582 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 152338 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 19-0021777 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 43508 | 1651 | 301765 | 4311 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 99153 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021712 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 43508 | 1651 | 301404 | 3926 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 340423 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021648 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 43509 | 1834 | 305522 | 1238 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 37140 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023044 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 43509 | 457 | 302680 | 1030 | Distribution Circuit | Vegetation | Tree - fell into line | 140 | 123432 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021790 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER |  | 43522 | 1739 | 324987 | 329 | Distribution Circuit | Vegetation | Tree - fell into line | 537 | 82593 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028507 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 43508 | 1914 | 301069 | 3724 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 160132 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021651 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | FUSE |  | 43508 | 1843 | 300977 | 1527 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 38175 | Strong Winds-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0021580 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER |  | 43508 | 2213 | 301152 | 1221 | Distribution Circuit | Vegetation | Tree - branch fell on line | 389 | 441731 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021642 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 43509 | 2315 | 305877 | 1160 | Distribution Circuit | Vegetation | Tree - fell into line | 160 | 101050 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022736 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 43509 | 1023 | 303686 | 1877 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5631 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022128 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 43508 | 2209 | 301307 | 2666 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 45322 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0021882 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER |  | 43506 | 1621 | 299174 | 232 | Distribution Circuit | Vegetation | Tree - branch fell on line | 868 | 96096 | Clear;32-90 F | Conductor- Overhead | On Ground | 19-0020798 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 43522 | 1723 | 324950 | 955 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 11460 | Clear;32-90 F | Conductor- Overhead | On Ground | 19-0028509 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | RECLOSER |  | 43506 | 1306 | 298957 | 1358 | Distribution Circuit | Vegetation | Tree - fell into line | 571 | 70142 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020714 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 43522 | 2114 | 325303 | 2428 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 38848 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0028598 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 43508 | 1935 | 305318 | 2819 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 11276 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022482 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 43509 | 407 | 302618 | 3437 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6874 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0021812 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 43522 | 1423 | 324816 | 217 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 18879 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028461 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER |  | 43506 | 938 | 298539 | 521 | Distribution Circuit | Equipment Failure/Involved | Overhead | 88 | 12521 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 19-0020639 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 43509 | 228 | 304741 | 2223 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 17784 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022325 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 43509 | 2222 | 305807 | 1113 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 10017 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023535 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 43510 | 730 | 307400 | 1605 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 57780 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022944 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 43509 | 407 | 304736 | 2058 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 20580 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022322 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 43509 | 228 | 305557 | 3742 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 7484 | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0022550 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 43522 | 2227 | 325313 | 7982 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 17474 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0029288 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 43506 | 1142 | 298823 | 368 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1104 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020691 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 43508 | 1852 | 312377 | 5228 | Distribution Circuit | Vegetation | Tree - grew into line | 39 | 185620 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024119 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 43522 | 2229 | 325488 | 2181 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 111231 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028935 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 43506 | 1056 | 298795 | 309 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 14523 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020682 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER |  | 43506 | 447 | 298139 | 2050 | Distribution Circuit | Vegetation | Tree - fell into line | 323 | 517807 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020571 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 43506 | 638 | 299983 | 2136 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12816 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021112 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 43508 | 1311 | 300706 | 234 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 468 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021502 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 43510 | 846 | 307912 | 494 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 494 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0022972 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 43522 | 1447 | 324701 | 1528 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7640 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028503 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER |  | 43506 | 510 | 297988 | 5074 | Distribution Circuit | Vegetation | Tree - fell into line | 1360 | 1786477 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 19-0020550 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | OCB |  | 43506 | 710 | 298102 | 6230 | Distribution Circuit | Vegetation | Tree - fell into line | 985 | 1158702 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020576 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER |  | 43506 | 502 | 297966 | 2134 | Distribution Circuit | Vegetation | Tree - fell into line | 446 | 747992 | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0020546 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE |  | 43506 | 1121 | 298832 | 2873 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 54587 | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021156 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER |  | 43513 | 1116 | 315683 | 1594 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 47908 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025107 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER |  | 43506 | 654 | 298132 | 2118 | Distribution Circuit | Vegetation | Tree - branch fell on line | 224 | 393741 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020569 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | OCB |  | 43506 | 928 | 298309 | 1963 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 330690 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020635 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 43506 | 827 | 298480 | 1943 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 184585 | Clear-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020811 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER |  | 43511 | 1917 | 312684 | 1234 | Distribution Circuit | Vegetation | Tree - fell into line | 144 | 177696 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024262 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | FUSE |  | 43513 | 801 | 315353 | 2024 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12144 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025268 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER |  | 43506 | 1337 | 298987 | 1890 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 49140 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020718 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER |  | 43508 | 2234 | 301375 | 3935 | Distribution Circuit | Equipment Failure/Involved | Overhead | 417 | 1303157 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021645 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER |  | 43506 | 904 | 298476 | 5951 | Distribution Circuit | Vegetation | Tree - fell into line | 302 | 563459 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020621 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | RECLOSER |  | 43505 | 1724 | 297227 | 5824 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 124272 | Overcast;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020385 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | FUSE |  | 43511 | 1024 | 311845 | 1651 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4953 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024050 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1102 | 192461102 | FUSE |  | 43506 | 1009 | 298639 | 1656 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 39744 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020741 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | FUSE |  | 43511 | 2225 | 313201 | 848 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 848 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024369 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1102 | 192461102 | FUSE |  | 43513 | 1152 | 315780 | 238 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 2618 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025194 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1102 | 192461102 | FUSE |  | 43506 | 629 | 298087 | 1791 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 19701 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020837 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | RECLOSER |  | 43506 | 316 | 297827 | 5268 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 320960 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020528 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | RECLOSER |  | 43512 | 1124 | 314020 | 1761 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 66199 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024517 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | FUSE |  | 43506 | 316 | 300203 | 6632 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 53056 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021196 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | CARLOTTA-1121 | 192291121 | RECLOSER |  | 43506 | 554 | 298064 | 3629 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 49966 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020567 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE |  | 43510 | 513 | 307177 | 392 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 4312 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022956 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | NEWBURG-1131 | 192151131 | FUSE |  | 43506 | 231 | 297796 | 2288 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 19346 | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 19-0020596 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | FUSE |  | 43506 | 16 | 300888 | 3969 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 15876 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021549 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | FUSE |  | 43506 | 17 | 299274 | 3938 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 15752 | Clear-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020808 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | MAPLE CREEK-1101 | 192101101 | FUSE |  | 43506 | 59 | 299287 | 5311 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 74354 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020815 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | MAPLE CREEK-1101 | 192101101 | OCB |  | 43506 | 59 | 297704 | 5176 | Distribution Circuit | Vegetation | Tree - fell into line | 130 | 371859 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020494 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1102 | 192171102 | FUSE |  | 43513 | 1531 | 316405 | 1415 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 39620 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025278 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | JUMPER |  | 43506 | 17 | 300885 | 4018 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8036 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0021548 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 43513 | 1745 | 316582 | 1281 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 10248 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025294 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | FUSE |  | 43506 | 17 | 300892 | 3960 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 23760 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021550 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 43506 | 109 | 308264 | 11297 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 214643 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0023086 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1121 | 192021121 | OTHER |  | 43500 | 1210 | 290365 | 385 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5390 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018024 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
HUMBOLDT | Tier 2 | ARCATA-1121 | 192021121 | FUSE |  | 43505 | 925 | 296874 | 382 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5348 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020326 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 43506 | 109 | 305605 | 12027 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 216486 | Clear;Below 32 F | Crossarm- Wood | Broken- wire on ground | 19-0022557 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 43506 | 109 | 305581 | 10949 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 10949 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0022555 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 43511 | 2133 | 314800 | 2221 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 33315 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024674 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | JUMPER |  | 43506 | 109 | 307307 | 10944 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 32832 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0022872 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1102 | 192171102 | FUSE |  | 43506 | 109 | 299601 | 4136 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 49632 | Overcast-Fog;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0020924 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | JUMPER |  | 43511 | 2133 | 314703 | 1214 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4856 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024651 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1102 | 192171102 | RECLOSER |  | 43522 | 1931 | 325167 | 1424 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 68352 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028550 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER |  | 43506 | 109 | 300865 | 8423 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 404304 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0021540 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1102 | 192171102 | FUSE |  | 43506 | 109 | 300749 | 6706 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 114002 | Clear;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0021476 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 43522 | 1121 | 324322 | 149 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 298 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0028252 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 43505 | 1326 | 299771 | 8969 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 8969 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020999 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | OTHER |  | 43505 | 1323 | 297041 | 8994 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 570842 | Overcast;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0020330 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1102 | 192171102 | JUMPER |  | 43506 | 109 | 299101 | 2283 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 15981 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020772 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1101 | 192171101 | SWITCH |  | 43506 | 109 | 298999 | 3925 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 15700 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020724 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1101 | 192171101 | SWITCH |  | 43509 | 326 | 302813 | 484 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1936 | Clear-Strong Winds;Below 32 F | Conductor- Overhead | On Ground | 19-0021803 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | OTHER |  | 43506 | 109 | 298903 | 6299 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 317669 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020693 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 43506 | 109 | 299589 | 5121 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 92178 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020920 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 43500 | 1431 | 290570 | 1448 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 26064 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018075 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 43523 | 226 | 326167 | 701 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 22238 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028726 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | JUMPER |  | 43506 | 121 | 299421 | 3829 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 38290 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020857 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 43506 | 121 | 300150 | 5049 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5049 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0021186 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER |  | 43505 | 2350 | 297595 | 8364 | Distribution Circuit | Vegetation | Tree - fell into line | 510 | 2240269 | Overcast-Fog;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0020485 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 43505 | 2350 | 300809 | 8282 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 82820 | Clear;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0021513 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 43505 | 2350 | 299370 | 8364 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 184008 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020836 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 43500 | 1834 | 291084 | 1166 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5830 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018155 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 3 | BUELLTON-1102 | 183041102 | FUSE |  | 43500 | 1326 | 290380 | 1433 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 7165 | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 19-0017961 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | BUELLTON-1102 | 183041102 | FUSE |  | 43498 | 428 | 287123 | 2218 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 17744 | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0017067 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
LOS PADRES | Tier 2 | CABRILLO-1104 | 183101104 | FUSE |  | 43498 | 830 | 286967 | 2061 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 20610 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017199 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | SANTA YNEZ-1104 | 182721104 | FUSE |  | 43498 | 1413 | 288255 | 2828 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 121604 | Strong Winds-Rain-Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 19-0017374 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
LOS PADRES | Tier 2 | ZACA-1102 | 182681102 | OCB |  | 43498 | 327 | 286215 | 1176 | Distribution Circuit | Vegetation | Tree - fell into line | 1427 | 751030 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0016880 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | PALMER-1101 | 183031101 | RECLOSER |  | 43498 | 236 | 286085 | 622 | Distribution Circuit | Vegetation | Tree - branch fell on line | 787 | 74114 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0016863 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | FOOTHILL-1101 | 182951101 | FUSE |  | 43498 | 559 | 286585 | 3592 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 8978 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017515 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | MORRO BAY-1102 | 183011102 | FUSE |  | 43509 | 709 | 302969 | 436 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 3052 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021876 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
LOS PADRES | Tier 3 | TEMPLETON-2113 | 183052113 | RECLOSER |  | 43498 | 611 | 286610 | 1670 | Distribution Circuit | Vegetation | Tree - fell into line | 130 | 106171 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0016944 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | ATASCADERO-1101 | 182541101 | JUMPER |  | 43498 | 1230 | 287402 | 1511 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1511 | Strong Winds-Heavy Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 19-0017307 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
LOS PADRES | Tier 2 | ATASCADERO-1101 | 182541101 | FUSE |  | 43498 | 331 | 286221 | 704 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3803 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0016901 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE |  | 43498 | 533 | 286526 | 975 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 13650 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017042 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE |  | 43498 | 151 | 286027 | 1164 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3492 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0016882 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | RECLOSER |  | 43498 | 2039 | 288120 | 1208 | Distribution Circuit | Vegetation | Tree - fell into line | 382 | 212654 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0017348 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE |  | 43498 | 901 | 287046 | 1664 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 13312 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017271 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE |  | 43523 | 1606 | 327387 | 1373 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 11864 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 19-0029173 | OH | Sus | 31426870 | 2019 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | CAMBRIA-1101 | 182771101 | FUSE |  | 43509 | 1044 | 303783 | 836 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 7539 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022150 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | ALTO-1120 | 42031120 | FUSE |  | 43510 | 1719 | 310362 | 1544 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6176 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023559 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE |  | 43510 | 322 | 307396 | 831 | Distribution Circuit | Vegetation | Tree - fell into line | 171 | 119045 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023243 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | Yes
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE |  | 43509 | 2116 | 305746 | 1244 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 18165 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022711 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | BOLINAS-1101 | 42261101 | OTHER |  | 43509 | 1052 | 303957 | 3231 | Distribution Circuit | Vegetation | Tree - fell into line | 831 | 2532753 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022172 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | TRIP-SAVER |  | 43512 | 1743 | 314867 | 1285 | Distribution Circuit | Vegetation | Tree - fell into line | 195 | 54393 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024717 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | BOLINAS-1101 | 42261101 | OCB |  | 43510 | 822 | 307670 | 3227 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1160 | 122660 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022934 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | GREENBRAE-1102 | 43091102 | FUSE |  | 43510 | 1859 | 310675 | 2801 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 33612 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023821 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE |  | 43510 | 1205 | 308867 | 728 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 18928 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023178 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | BOLINAS-1101 | 42261101 | OTHER |  | 43510 | 948 | s1422019 | 4632 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 23160 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0023654 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE |  | 43522 | 1607 | 324846 | 1542 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 21171 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028528 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | WOODACRE-1102 | 43021102 | RECLOSER |  | 43510 | 156 | 306278 | 3606 | Distribution Circuit | Equipment Failure/Involved | Overhead | 729 | 525588 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023143 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE |  | 43522 | 1746 | 324998 | 1424 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7120 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028517 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE |  | 43510 | 233 | 306422 | 2444 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3064 | 402449 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023501 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | WOODACRE-1101 | 43021101 | RECLOSER |  | 43522 | 2203 | 325405 | 694 | Distribution Circuit | Equipment Failure/Involved | Overhead | 274 | 82726 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028591 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE |  | 43522 | 1931 | 325159 | 1344 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 6720 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028561 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | LAS GALLINAS A-1105 | 42991105 | RECLOSER |  | 43510 | 401 | 306699 | 3782 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 224052 | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0022798 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 43522 | 2210 | 325428 | 1211 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6055 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028662 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 43509 | 1924 | 305582 | 1032 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 36120 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022565 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 43522 | 2338 | 325753 | 876 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 30660 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028660 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 43510 | 250 | 308096 | 2386 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 57264 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023067 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 43522 | 2107 | 325299 | 253 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1771 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028590 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 43510 | 804 | 307586 | 3266 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 39192 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023235 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | IGNACIO 1105 | 42481105 | FUSE |  | 43523 | 206 | 326120 | 956 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 42888 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028691 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 43522 | 2041 | 325274 | 3310 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 49650 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0028584 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 43510 | 456 | 306898 | 2240 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 20160 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023130 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 43510 | 358 | 306689 | 1012 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 21565 | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022842 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | MONTICELLO-1101 | 43051101 | RECLOSER |  | 43510 | 500 | 306973 | 3643 | Distribution Circuit | Vegetation | Tree - fell into line | 220 | 717520 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022832 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER |  | 43510 | 1042 | 308405 | 1359 | Distribution Circuit | Vegetation | Tree - fell into line | 752 | 618261 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023276 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER |  | 43522 | 1914 | 325146 | 1225 | Distribution Circuit | Vegetation | Tree - fell into line | 351 | 417965 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028529 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER |  | 43522 | 900 | 324120 | 370 | Distribution Circuit | Equipment Failure/Involved | Overhead | 415 | 65005 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028156 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER |  | 43505 | 1911 | 297357 | 1125 | Distribution Circuit | Vegetation | Tree - fell into line | 202 | 78956 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020401 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER |  | 43522 | 1849 | 325116 | 1271 | Distribution Circuit | Vegetation | Tree - fell into line | 202 | 197116 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028520 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1103 | 102911103 | RECLOSER |  | 43510 | 442 | 306861 | 523 | Distribution Circuit | Vegetation | Tree - fell into line | 1191 | 732699 | Partly Cloudy-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022815 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER |  | 43510 | 429 | 306999 | 896 | Distribution Circuit | Vegetation | Tree - fell into line | 214 | 98132 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022876 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER |  | 43523 | 129 | 326308 | 1145 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 68258 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0028766 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1110 | 102911110 | TRANSFORMER |  | 43522 | 1016 | 324240 | 390 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 724 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028263 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER |  | 43510 | 758 | 307625 | 372 | Distribution Circuit | Vegetation | Tree - fell into line | 249 | 42714 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022912 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | FUSE |  | 43511 | 1145 | 312250 | 1560 | Distribution Circuit | Environmental/External | Ice or snow | 3 | 4680 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0024102 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | ELK CREEK-1101 | 102781101 | FUSE |  | 43511 | 1917 | 312894 | 2799 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 41985 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024410 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE |  | 43500 | 1157 | 290383 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 28600 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017998 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | JUMPER |  | 43510 | 1840 | 310717 | 865 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 73441 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023641 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
NORTH VALLEY | Tier 3 | BIG BEND-1102 | 103751102 | OTHER |  | 43509 | 344 | 303383 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 41238 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021983 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE |  | 43509 | 634 | 302898 | 971 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 13323 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022452 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | OCB |  | 43509 | 441 | 302659 | 926 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4318 | 1174921 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021783 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER |  | 43509 | 837 | 303256 | 895 | Distribution Circuit | Vegetation | Tree - fell into line | 181 | 160987 | Overcast-Fog-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0022507 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER |  | 43500 | 457 | 289465 | 343 | Distribution Circuit | Vegetation | Tree - fell into line | 181 | 61453 | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0017711 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | CORNING-1102 | 103331102 | FUSE |  | 43510 | 1658 | 310308 | 1494 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 7470 | Overcast-Fog-Snow;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 19-0023542 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | FUSE |  | 43523 | 1257 | 326778 | 413 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 9912 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0029026 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | EAST QUINCY-1101 | 102551101 | FUSE |  | 43522 | 1005 | 324219 | 360 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 360 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028273 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | FUSE |  | 43522 | 149 | 324636 | 3783 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 98358 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | On Ground | 19-0028383 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | CORNING-1101 | 103331101 | FUSE |  | 43523 | 340 | 326503 | 659 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 6905 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on object | 19-0028762 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BUCKS CREEK-1102 | 102211102 | OTHER |  | 43522 | 946 | 324441 | 1577 | Distribution Circuit | Equipment Failure/Involved | Overhead | 130 | 52991 | Overcast-Fog-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on object | 19-0028322 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 2 | BUCKS CREEK-1102 | 102211102 | FUSE |  | 43522 | 1217 | 324110 | 4239 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 4239 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0028296 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | JUMPER |  | 43522 | 58 | 324565 | 3762 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3762 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028356 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | FUSE |  | 43522 | 103 | 323772 | 957 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4785 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028347 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER |  | 43500 | 2107 | 291101 | 1025 | Distribution Circuit | Vegetation | Tree - fell into line | 1372 | 645067 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018159 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | OTHER |  | 43523 | 551 | 326416 | 390 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1359 | 94474 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on object | 19-0028746 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER |  | 43522 | 137 | 323788 | 2531 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 7575 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028060 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | RECLOSER |  | 43522 | 259 | 323824 | 1024 | Distribution Circuit | Vegetation | Tree - fell into line | 203 | 207872 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028069 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1101 | 102931101 | SWITCH |  | 43508 | 2309 | 314821 | 9426 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 480726 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0024682 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | JUMPER |  | 43508 | 2329 | 305838 | 5440 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 54400 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022697 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | JUMPER |  | 43508 | 2329 | 314843 | 6841 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6841 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0024689 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE |  | 43508 | 2329 | 312536 | 5438 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 304528 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0024173 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | RED BLUFF-1104 | 103541104 | FUSE |  | 43509 | 652 | 302933 | 655 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 66155 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0021969 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1101 | 102931101 | FUSE |  | 43513 | 928 | 315481 | 4823 | Distribution Circuit | Environmental/External | Ice or snow | 6 | 28938 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0026365 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE |  | 43513 | 821 | 316557 | 2073 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 122307 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025593 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE |  | 43513 | 828 | 316555 | 3172 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 15966 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025684 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE |  | 43508 | 2349 | 311492 | 5526 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 77364 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023842 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | RECLOSER |  | 43508 | 2342 | 301568 | 9452 | Distribution Circuit | Vegetation | Tree - fell into line | 290 | 2662630 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021680 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1101 | 102931101 | FUSE |  | 43511 | 1922 | 312900 | 1252 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 15024 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024612 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1101 | 102931101 | JUMPER |  | 43509 | 202 | 312882 | 5187 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 41484 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0024258 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE |  | 43508 | 2329 | 312121 | 5232 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 181660 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 19-0024037 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER |  | 43522 | 2344 | 325782 | 2472 | Distribution Circuit | Environmental/External | Ice or snow | 784 | 1384234 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028635 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | RECLOSER |  | 43508 | 2329 | 301522 | 5402 | Distribution Circuit | Vegetation | Tree - fell into line | 468 | 2035242 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0021669 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | FUSE |  | 43509 | 229 | 305552 | 3677 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 22062 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022549 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1101 | 102931101 | FUSE |  | 43509 | 202 | 311533 | 3498 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 111936 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023849 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1102 | 102931102 | FUSE |  | 43508 | 2242 | 315506 | 6569 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 72259 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0025073 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1101 | 102931101 | FUSE |  | 43509 | 202 | 304403 | 3733 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 317305 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0022201 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1102 | 102931102 | FUSE |  | 43508 | 2242 | 314937 | 8167 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 253177 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024712 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1102 | 102931102 | FUSE |  | 43508 | 2242 | 314930 | 6600 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 59400 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024710 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1102 | 102931102 | FUSE |  | 43510 | 1511 | 309869 | 3049 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12196 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024567 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1102 | 102931102 | FUSE |  | 43509 | 216 | 308961 | 8104 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 853888 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023195 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1102 | 102931102 | FUSE |  | 43511 | 531 | 311356 | 659 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1318 | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 19-0023868 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER |  | 43500 | 225 | 289396 | 621 | Distribution Circuit | Equipment Failure/Involved | Overhead | 784 | 486659 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017688 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER |  | 43509 | 229 | 311926 | 3679 | Distribution Circuit | Environmental/External | Ice or snow | 149 | 547544 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023867 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | PANORAMA-1102 | 103461102 | RECLOSER |  | 43513 | 729 | 315319 | 3536 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 35360 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025697 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | FUSE |  | 43509 | 229 | 305354 | 3391 | Distribution Circuit | Environmental/External | Ice or snow | 13 | 44083 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022489 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER |  | 43509 | 221 | 301942 | 6704 | Distribution Circuit | Environmental/External | Ice or snow | 218 | 749622 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0021731 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER |  | 43522 | 739 | 323939 | 1902 | Distribution Circuit | Vegetation | Tree - fell into line | 242 | 61868 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028109 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1102 | 103441102 | FUSE |  | 43509 | 103 | 313719 | 10027 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 157922 | Overcast-Fog-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0024433 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1102 | 103441102 | JUMPER |  | 43509 | 29 | 311493 | 8626 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 17252 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0023841 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANDERSON-1101 | 103261101 | JUMPER |  | 43509 | 238 | 304559 | 9091 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 63637 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022248 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1102 | 103441102 | RECLOSER |  | 43509 | 103 | 301726 | 9407 | Distribution Circuit | Vegetation | Tree - fell into line | 860 | 5167335 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021709 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | PANORAMA-1102 | 103461102 | OTHER |  | 43522 | 1451 | 324969 | 1139 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 92651 | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028501 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1102 | 103441102 | JUMPER |  | 43509 | 103 | 317655 | 12471 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 67032 | Overcast-Fog-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0025629 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1101 | 103401101 | FUSE |  | 43508 | 2305 | 318964 | 12277 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 184155 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0026127 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | VOLTA-1101 | 102541101 | JUMPER |  | 43510 | 1600 | 310172 | 6881 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 68810 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023508 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1102 | 103441102 | FUSE |  | 43513 | 1917 | 317812 | 2511 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 10044 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0025667 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1102 | 103441102 | FUSE |  | 43508 | 2303 | 314542 | 8372 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 125580 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0024592 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1102 | 103441102 | FUSE |  | 43513 | 1917 | 316792 | 1398 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 27960 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025603 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | JUMPER |  | 43508 | 2312 | 317766 | 10868 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 76076 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025656 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1103 | 103441103 | JUMPER |  | 43508 | 2358 | 311617 | 3604 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 72080 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023874 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1102 | 103441102 | SWITCH |  | 43508 | 2303 | 316487 | 8427 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 935397 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0025250 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANDERSON-1103 | 103261103 | JUMPER |  | 43509 | 115 | 316716 | 7952 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 24261 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025306 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | JUMPER |  | 43508 | 2312 | 317688 | 11230 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 33690 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0025638 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | ANDERSON-1103 | 103261103 | JUMPER |  | 43509 | 114 | 307279 | 6754 | Distribution Circuit | Environmental/External | Ice or snow | 41 | 231212 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022862 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | RECLOSER |  | 43508 | 2312 | 301476 | 10995 | Distribution Circuit | Vegetation | Tree - fell into line | 325 | 2925182 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021665 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | JUMPER |  | 43508 | 2251 | 303350 | 8382 | Distribution Circuit | Environmental/External | Ice or snow | 103 | 863346 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021931 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | FUSE |  | 43508 | 2342 | 316780 | 9693 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 67851 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025315 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1101 | 103401101 | FUSE |  | 43508 | 2305 | 319266 | 12004 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 12004 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0026238 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1103 | 103441103 | FUSE |  | 43509 | 5 | 308059 | 11158 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 44632 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023010 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | FUSE |  | 43508 | 2312 | 318005 | 10983 | Distribution Circuit | Environmental/External | Ice or snow | 9 | 98847 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025699 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1103 | 103441103 | FUSE |  | 43509 | 5 | 307864 | 11005 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 22010 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022960 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | FUSE |  | 43509 | 49 | 319132 | 11039 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 430521 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0026200 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | FUSE |  | 43508 | 2343 | 314876 | 6886 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 68860 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024700 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | JUMPER |  | 43508 | 2343 | 314909 | 9591 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 143865 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024706 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | JUMPER |  | 43508 | 2343 | 312125 | 8253 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 8253 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024039 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | JUMPER |  | 43508 | 2356 | 319213 | 10789 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 10789 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0026231 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | TRIP-SAVER |  | 43508 | 2343 | 313880 | 9767 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 848127 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0024483 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | RECLOSER |  | 43509 | 725 | 303015 | 6468 | Distribution Circuit | Vegetation | Tree - fell into line | 1169 | 6266140 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021846 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1101 | 103401101 | RECLOSER |  | 43501 | 624 | 291738 | 325 | Distribution Circuit | 3rd Party | Gun Shot | 163 | 47900 | Partly Cloudy;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018269 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1101 | 103401101 | JUMPER |  | 43513 | 1623 | 316486 | 4397 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 26382 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025909 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1101 | 103401101 | FUSE |  | 43508 | 2305 | 317717 | 9611 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 326774 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025641 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1101 | 103401101 | FUSE |  | 43508 | 2305 | 317714 | 11180 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 111800 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025640 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1101 | 103401101 | JUMPER |  | 43509 | 204 | 307993 | 9031 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 18062 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0022996 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1101 | 103401101 | FUSE |  | 43509 | 145 | 305742 | 9600 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 153600 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 19-0022606 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1101 | 103401101 | JUMPER |  | 43513 | 1213 | 315816 | 317 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 317 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025130 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1101 | 103401101 | FUSE |  | 43508 | 2305 | 317713 | 9754 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 224342 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025639 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1101 | 103401101 | RECLOSER |  | 43508 | 2305 | 301456 | 9607 | Distribution Circuit | Vegetation | Tree - fell into line | 200 | 1654387 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0021661 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1101 | 103401101 | JUMPER |  | 43508 | 2357 | 312203 | 11203 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 22406 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 19-0024070 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1102 | 103401102 | FUSE |  | 43508 | 2356 | 310768 | 5526 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 176832 | Snow-Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023659 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | DESCHUTES-1101 | 103351101 | SWITCH |  | 43508 | 2321 | 305197 | 9680 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 234492 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 19-0022438 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1102 | 103401102 | FUSE |  | 43509 | 153 | 312638 | 11168 | Distribution Circuit | Vegetation | Tree - branch fell on line | 36 | 402048 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024194 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1102 | 103401102 | FUSE |  | 43509 | 108 | 311741 | 9490 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 104390 | Snow-Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0023902 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | DESCHUTES-1104 | 103351104 | JUMPER |  | 43509 | 2142 | 307194 | 4071 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 38642 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023002 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE |  | 43509 | 209 | 308677 | 4011 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 260715 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023141 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE |  | 43509 | 51 | 312782 | 8290 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 24870 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0024239 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1102 | 103401102 | JUMPER |  | 43509 | 153 | 311867 | 12387 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 734691 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023952 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE |  | 43509 | 204 | 312778 | 8196 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 73764 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024235 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE |  | 43513 | 1800 | 316966 | 4122 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8244 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025327 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1101 | 103401101 | FUSE |  | 43511 | 1423 | 312323 | 7069 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 98966 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 19-0024610 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1102 | 103401102 | FUSE |  | 43508 | 132 | 312460 | 5255 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 47295 | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0024143 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1102 | 103401102 | FUSE |  | 43509 | 119 | 312588 | 11000 | Distribution Circuit | Vegetation | Tree - bark fell into line | 25 | 275000 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024179 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | DESCHUTES-1101 | 103351101 | JUMPER |  | 43508 | 2321 | 319098 | 12320 | Distribution Circuit | Vegetation | Tree - fell into line | 319 | 85814 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0026190 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE |  | 43509 | 209 | 312776 | 7841 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 39205 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024234 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1102 | 103401102 | FUSE |  | 43509 | 153 | 312605 | 12177 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 395417 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 19-0024182 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | DESCHUTES-1101 | 103351101 | RECLOSER |  | 43508 | 2321 | 301501 | 5446 | Distribution Circuit | Vegetation | Tree - fell into line | 1082 | 2124073 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021843 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE |  | 43509 | 209 | 312611 | 9135 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 63945 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024184 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | DESCHUTES-1101 | 103351101 | JUMPER |  | 43509 | 221 | 308505 | 4857 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 63141 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023129 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | DESCHUTES-1104 | 103351104 | FUSE |  | 43510 | 1713 | 308200 | 4362 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 200652 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023665 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1102 | 103401102 | RECLOSER |  | 43509 | 154 | 301532 | 3793 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 508262 | Snow-Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | On Ground | 19-0021724 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1102 | 103401102 | FUSE |  | 43508 | 2316 | 302895 | 9687 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 116244 | Snow-Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021821 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE |  | 43509 | 116 | 305203 | 8284 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 124260 | Overcast-Fog-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0022445 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE |  | 43509 | 209 | 310127 | 10659 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 42636 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023489 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | WHITMORE-1101 | 103601101 | FUSE |  | 43509 | 822 | 318982 | 11888 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 47552 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0026140 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | WHITMORE-1101 | 103601101 | FUSE |  | 43509 | 822 | 318677 | 10748 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 150472 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025997 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | KESWICK-1101 | 103451101 | JUMPER |  | 43509 | 44 | 316485 | 11964 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 622128 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0025248 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | DESCHUTES-1104 | 103351104 | FUSE |  | 43509 | 121 | 305190 | 2419 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 26609 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022435 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | JUMPER |  | 43509 | 209 | 310855 | 10933 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 54665 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023686 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | KESWICK-1101 | 103451101 | FUSE |  | 43513 | 804 | 320347 | 6326 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 69586 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0026780 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | DESCHUTES-1104 | 103351104 | JUMPER |  | 43509 | 121 | 304780 | 10631 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 10631 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022339 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KESWICK-1101 | 103451101 | JUMPER |  | 43509 | 47 | 315717 | 10978 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 21956 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025112 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KESWICK-1101 | 103451101 | FUSE |  | 43509 | 23 | 315878 | 8207 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 49242 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025142 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | KESWICK-1101 | 103451101 | JUMPER |  | 43509 | 47 | 315866 | 9583 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 153328 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025139 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | KESWICK-1101 | 103451101 | FUSE |  | 43509 | 47 | 315869 | 8083 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 193992 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025141 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE |  | 43508 | 2340 | 318179 | 9419 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 103609 | Overcast-Fog-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0025745 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KESWICK-1101 | 103451101 | FUSE |  | 43513 | 835 | 315359 | 5860 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 69790 | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 19-0025043 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 3 | KESWICK-1101 | 103451101 | RECLOSER |  | 43509 | 47 | 301717 | 6881 | Distribution Circuit | Vegetation | Tree - fell into line | 274 | 1755928 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | On Ground | 19-0021700 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE |  | 43508 | 2340 | 318190 | 9575 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 306400 | Overcast-Fog-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0025748 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | OCB |  | 43509 | 209 | 301902 | 7681 | Distribution Circuit | Vegetation | Tree - fell into line | 687 | 3078183 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021850 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | Yes
NORTH VALLEY | Tier 2 | WHITMORE-1101 | 103601101 | RECLOSER |  | 43509 | 823 | 303217 | 7467 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 1253635 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025089 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | SWITCH |  | 43509 | 40 | 314657 | 8279 | Distribution Circuit | Vegetation | Tree - fell into line | 234 | 1937286 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024635 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE |  | 43508 | 2340 | 314636 | 9271 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 9271 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024628 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE |  | 43508 | 2340 | 314634 | 9415 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 122395 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024625 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE |  | 43508 | 2340 | 314631 | 8243 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 140131 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024624 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE |  | 43509 | 345 | 309799 | 7999 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 459117 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023411 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | JUMPER |  | 43509 | 227 | 312522 | 9484 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 294004 | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0024169 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | SWITCH |  | 43508 | 2340 | 305193 | 6717 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 664983 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022436 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE |  | 43523 | 1442 | 327241 | 1099 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 13086 | Partly Cloudy-Rain;32-90 F | Woodpin | Broken- wire on object | 19-0029136 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE |  | 43509 | 345 | 310314 | 6568 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 85384 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0023545 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | OTHER |  | 43513 | 1619 | 316488 | 1286 | Distribution Circuit | Equipment Failure/Involved | Overhead | 393 | 120656 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025253 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE |  | 43508 | 2340 | 314444 | 9644 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 125372 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024564 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE |  | 43510 | 2031 | 310841 | 5429 | Distribution Circuit | Vegetation | Tree - branch fell on line | 64 | 47913 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023762 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | JUMPER |  | 43509 | 345 | 310024 | 6345 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6345 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023459 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE |  | 43509 | 236 | 302490 | 10813 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 227073 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025208 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE |  | 43512 | 1206 | 314128 | 4346 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 22300 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025320 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE |  | 43509 | 41 | 314872 | 9709 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 29127 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024697 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | JUMPER |  | 43509 | 202 | 310324 | 9216 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 46080 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023548 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | RECLOSER |  | 43523 | 1057 | 326877 | 404 | Distribution Circuit | Vegetation | Tree - branch fell on line | 244 | 48120 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028938 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | RECLOSER |  | 43509 | 314 | 302537 | 9308 | Distribution Circuit | Vegetation | Tree - fell into line | 243 | 1131261 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021795 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE |  | 43509 | 227 | 317513 | 11058 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 77406 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0025595 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | RECLOSER |  | 43509 | 227 | 303048 | 11057 | Distribution Circuit | Vegetation | Tree - fell into line | 414 | 2406517 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023890 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | RECLOSER |  | 43523 | 209 | 326128 | 1885 | Distribution Circuit | Vegetation | Tree - fell into line | 536 | 293776 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0028696 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE |  | 43498 | 3 | 285901 | 631 | Distribution Circuit | Vegetation | Tree - fell into line | 243 | 7815 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0016836 | OH | Sus | 31424435 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KESWICK-1101 | 103451101 | FUSE |  | 43513 | 1519 | 318449 | 3041 | Distribution Circuit | Environmental/External | Ice or snow | 2 | 6082 | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 19-0025889 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1102 | 103381102 | OTHER |  | 43513 | 932 | 315566 | 4674 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 135500 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025086 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | DESCHUTES-1101 | 103351101 | FUSE |  | 43509 | 221 | 308515 | 9354 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 9354 | Overcast-Fog-Heavy Rain;32-90 F | Anchor or Guy | Broken- wire on object | 19-0023136 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE |  | 43509 | 227 | 315979 | 11058 | Distribution Circuit | Environmental/External | Ice or snow | 51 | 563958 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025167 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | JUMPER |  | 43509 | 227 | 320065 | 12098 | Distribution Circuit | Environmental/External | Ice or snow | 22 | 266156 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0026616 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE |  | 43510 | 1737 | 310457 | 8687 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 78183 | Overcast-Drizzle;32-90 F | Pole - Tower- steel | Broken- wire on ground | 19-0024190 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE |  | 43509 | 13 | 317477 | 12232 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 61160 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0025587 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | SWITCH |  | 43511 | 1020 | 310511 | 483 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 16905 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024207 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | JUMPER |  | 43509 | 249 | 312440 | 10751 | Distribution Circuit | Environmental/External | Ice or snow | 53 | 569803 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 19-0024145 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | JUMPER |  | 43510 | 1800 | 312797 | 2860 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 11440 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024240 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | FUSE |  | 43509 | 249 | 312708 | 10860 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 32580 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024215 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1101 | 103381101 | OCB |  | 43509 | 415 | 302628 | 12008 | Distribution Circuit | Environmental/External | Ice or snow | 187 | 1180095 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0021769 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | FUSE |  | 43509 | 249 | 312516 | 6666 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 253318 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024166 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | FUSE |  | 43511 | 2205 | 313086 | 3975 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 166950 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024356 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | WHITMORE-1101 | 103601101 | JUMPER |  | 43509 | 823 | 316518 | 7756 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 31024 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0025273 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | JUMPER |  | 43509 | 33 | 314532 | 6925 | Distribution Circuit | Equipment Failure/Involved | Overhead | 70 | 484702 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0024584 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | JUMPER |  | 43509 | 33 | 316803 | 9517 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 9517 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0025323 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | RECLOSER |  | 43509 | 33 | 301697 | 8289 | Distribution Circuit | Vegetation | Tree - fell into line | 436 | 1564961 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021695 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | FUSE |  | 43509 | 33 | 312380 | 11227 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 233622 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0024118 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE |  | 43510 | 1800 | 314931 | 8568 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 34272 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 19-0024711 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1101 | 103381101 | RECLOSER |  | 43513 | 1306 | 315894 | 3164 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12656 | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 19-0025150 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | FUSE |  | 43509 | 33 | 316532 | 6859 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 569297 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025284 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | FUSE |  | 43509 | 33 | 316534 | 7981 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 183563 | Overcast-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0025286 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | FUSE |  | 43509 | 33 | 317560 | 10835 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 32505 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025614 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | SWITCH |  | 43509 | 220 | 315012 | 8108 | Distribution Circuit | Vegetation | Tree - branch fell on line | 52 | 374638 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 19-0024741 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | JUMPER |  | 43509 | 33 | 318115 | 9729 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 107019 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025726 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | JUMPER |  | 43509 | 33 | 318113 | 9508 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 19016 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025725 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | FUSE |  | 43509 | 33 | 317570 | 8189 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 253859 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025616 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | FUSE |  | 43509 | 33 | 317567 | 9361 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 102971 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025615 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1101 | 103381101 | JUMPER |  | 43508 | 2122 | 319138 | 11251 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 281535 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0026201 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | FUSE |  | 43509 | 220 | 315391 | 8104 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 56728 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0025041 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | FUSE |  | 43509 | 33 | 308218 | 13671 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 451143 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0023063 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CEDAR CREEK-1101 | 103321101 | JUMPER |  | 43511 | 1739 | 312728 | 1131 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 29403 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024236 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | FUSE |  | 43509 | 220 | 317994 | 9379 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 703425 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0025695 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1101 | 103381101 | JUMPER |  | 43508 | 2315 | 320010 | 13965 | Distribution Circuit | Environmental/External | Ice or snow | 50 | 666330 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0026603 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | CEDAR CREEK-1101 | 103321101 | OTHER |  | 43509 | 1 | 301740 | 5425 | Distribution Circuit | Equipment Failure/Involved | Overhead | 789 | 2031981 | Overcast-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 19-0021704 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | FUSE |  | 43508 | 2337 | 317926 | 12212 | Distribution Circuit | Environmental/External | Ice or snow | 99 | 1208988 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025677 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | RECLOSER |  | 43508 | 2335 | 301544 | 12306 | Distribution Circuit | Vegetation | Tree - branch fell on line | 67 | 771489 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021674 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | ANTLER-1101 | 103271101 | FUSE |  | 43509 | 57 | 317955 | 11122 | Distribution Circuit | Environmental/External | Ice or snow | 10 | 111220 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0025686 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | ANTLER-1101 | 103271101 | JUMPER |  | 43509 | 57 | 317956 | 13363 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 80178 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0025688 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | RISING RIVER-1101 | 103551101 | RECLOSER |  | 43500 | 1014 | 289947 | 1795 | Distribution Circuit | Vegetation | Tree - fell into line | 536 | 712220 | Overcast;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0017942 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | FUSE |  | 43509 | 57 | 318032 | 11067 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 154938 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0025706 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE |  | 43511 | 1443 | 312463 | 1419 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 18447 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0024211 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | RECLOSER |  | 43513 | 1653 | 316517 | 1142 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 93644 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025285 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | RECLOSER |  | 43508 | 2317 | 314747 | 6793 | Distribution Circuit | Vegetation | Tree - branch fell on line | 83 | 563819 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0021707 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | JUMPER |  | 43508 | 2317 | 315656 | 9853 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 137942 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025104 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | JUMPER |  | 43513 | 1653 | 317554 | 4352 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4352 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025611 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | FUSE |  | 43508 | 2317 | 316031 | 11235 | Distribution Circuit | Environmental/External | Ice or snow | 32 | 359520 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025181 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 43513 | 1151 | 318142 | 3079 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6158 | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 19-0025737 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 43509 | 1029 | 304425 | 3643 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 32787 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023318 | OH | Sus | 43677704 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE |  | 43509 | 2319 | 308290 | 2340 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 71108 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023372 | OH | Sus | 43677704 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 43501 | 559 | 291671 | 661 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 3966 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018303 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 43508 | 2315 | 301628 | 917 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5502 | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0021721 | OH | Sus | 31425520 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE |  | 43509 | 616 | 302878 | 601 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 7212 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021938 | OH | Sus | 31425418 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 43510 | 145 | 307798 | 3506 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 3506 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 19-0022945 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER |  | 43501 | 1956 | 293676 | 464 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 11634 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0018773 | OH | Sus | 31424639 | 2019 | FEB | Yes | Open Circuit | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | JUMPER |  | 43498 | 1832 | 288022 | 537 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 15573 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on object | 19-0017359 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 43509 | 1315 | 304592 | 605 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 5315 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022410 | OH | Sus | 31425418 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 43513 | 1014 | 315558 | 1790 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5540 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025121 | OH | Sus | 31425418 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 43509 | 1550 | 305146 | 4240 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 12720 | Overcast-Drizzle;32-90 F | Conductor- Overhead | On Ground | 19-0022524 | OH | Sus | 31425418 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER |  | 43510 | 1221 | 310866 | 4637 | Distribution Circuit | Vegetation | Tree - fell into line | 953 | 691981 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023737 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER |  | 43510 | 37 | 306275 | 844 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3230 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022743 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER |  | 43506 | 2028 | 299395 | 2993 | Distribution Circuit | Vegetation | Tree - fell into line | 343 | 153185 | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 19-0020853 | OH | Sus | 31425315 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 3 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 43510 | 718 | 310489 | 2017 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 34333 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023599 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER |  | 43498 | 405 | 286993 | 474 | Distribution Circuit | Vegetation | Tree - branch fell on line | 68 | 12927 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017036 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER |  | 43510 | 30 | 306070 | 1162 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 80178 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022723 | OH | Sus | 43677704 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | WOODSIDE-1104 | 24251104 | TRIP-SAVER |  | 43523 | 41 | 325954 | 710 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 54746 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028725 | OH | Sus | 43684677 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | RALSTON-1101 | 24141101 | FUSE |  | 43510 | 12 | 306027 | 3991 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 63856 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023500 | OH | Sus | 31425418 | 2019 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE |  | 43509 | 746 | 303068 | 674 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1348 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022190 | OH | Sus | 43677704 | 2019 | FEB | Yes | Line to Line | Yes | No
SAN JOSE | Tier 3 | LLAGAS-2107 | 83182107 | FUSE |  | 43509 | 1319 | 304628 | 546 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 8736 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022427 | OH | Sus | 31425399 | 2019 | FEB | Yes | Line to Ground | Yes | No
SAN JOSE | Tier 2 | HICKS-2101 | 83432101 | FUSE |  | 43512 | 1743 | 314870 | 448 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 23744 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024737 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SAN JOSE | Tier 2 | MILPITAS-1109 | 82831109 | FUSE |  | 43498 | 1352 | 287562 | 4368 | Distribution Circuit | Vegetation | Tree - bark fell into line | 4 | 17472 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018584 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43509 | 304 | 302351 | 989 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 3956 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022505 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43510 | 2000 | 310790 | 1162 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4648 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0023669 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | CLARKSVILLE-2103 | 153612103 | FUSE |  | 43509 | 848 | 303310 | 1727 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6908 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022175 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43500 | 2005 | 294961 | 5382 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 113022 | Clear;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0019444 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | OTHER |  | 43508 | 2154 | 301255 | 952 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1711 | 148676 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021637 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER |  | 43510 | 810 | 307642 | 494 | Distribution Circuit | Vegetation | Tree - fell into line | 712 | 136054 | Overcast-Drizzle;32-90 F | Capacitor | Broken- wire on ground | 19-0022910 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | OTHER |  | 43509 | 1526 | 305256 | 140 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 3982 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021637 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | RECLOSER |  | 43512 | 509 | 313269 | 5084 | Distribution Circuit | Vegetation | Tree - fell into line | 686 | 424731 | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 19-0024386 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43500 | 2005 | 294948 | 4911 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 39288 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0019438 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | JUMPER |  | 43500 | 2005 | 294691 | 5365 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 10730 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0019340 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43500 | 2005 | 294665 | 5579 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 89264 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0019331 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | JUMPER |  | 43500 | 2005 | 294337 | 6798 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 115566 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 19-0019177 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43513 | 1024 | 315786 | 198 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 5544 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025120 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43513 | 1027 | 315576 | 103 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 10094 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025117 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43506 | 1152 | 298880 | 3245 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 113575 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0021026 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43513 | 328 | 315218 | 504 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 6552 | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 19-0025044 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43500 | 2005 | 294365 | 5363 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 316417 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0019193 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43506 | 1446 | 299068 | 1461 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 100809 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020887 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER |  | 43506 | 657 | 298148 | 615 | Distribution Circuit | Vegetation | Tree - fell into line | 1215 | 81335 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020572 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43513 | 1038 | 315614 | 1597 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 88903 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0025178 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43510 | 819 | 307726 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 194 | 38182 | Overcast-Fog-Heavy Rain-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023109 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 43500 | 835 | 289722 | 650 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 21450 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017832 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 43501 | 119 | 294496 | 5082 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 167706 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019265 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 43501 | 632 | 293117 | 3605 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 439810 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018726 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43500 | 2005 | 295030 | 7080 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 182939 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0019538 | OH | Sus | 31424310 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43500 | 2005 | 293649 | 4002 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 100050 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018747 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 43501 | 119 | 294139 | 5082 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 696234 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019070 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43500 | 2005 | 294332 | 6834 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 20502 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0019176 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 43501 | 2259 | 293786 | 1006 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8048 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018799 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 43500 | 2313 | 294151 | 2557 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 25570 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019079 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43500 | 2005 | 293740 | 4016 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 124496 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018781 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43508 | 2239 | 301383 | 1071 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 100674 | Overcast-Drizzle-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0021874 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | OTHER |  | 43500 | 2205 | 291576 | 4030 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 247513 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018240 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43500 | 2337 | 291206 | 3352 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 97208 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0019229 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 43500 | 1225 | 290256 | 1340 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 21081 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018008 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | DIAMOND SPRINGS-1104 | 152261104 | FUSE |  | 43510 | 749 | 307494 | 1811 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 14488 | Overcast-Drizzle-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0023294 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 43500 | 457 | 289476 | 533 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 36777 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017722 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | RECLOSER |  | 43501 | 632 | 291764 | 1868 | Distribution Circuit | Environmental/External | Ice or snow | 633 | 801734 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018273 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43500 | 2005 | 300051 | 10365 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 93285 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0021148 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43500 | 2005 | 291125 | 4244 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 72148 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018188 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43510 | 846 | 307913 | 734 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 17765 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0023077 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43500 | 2005 | 294010 | 3966 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 106890 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019027 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE |  | 43501 | 1348 | 292795 | 1602 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 86508 | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on object | 19-0019209 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | JUMPER |  | 43501 | 600 | 292502 | 2040 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4080 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018446 | OH | Sus | 31424310 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43513 | 935 | 315499 | 658 | Distribution Circuit | Vegetation | Tree - fell into line | 562 | 351561 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025087 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 43501 | 1358 | 292986 | 2976 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 32736 | Overcast;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0018886 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43500 | 2005 | 295530 | 9917 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 29751 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019731 | OH | Sus | 31424310 | 2019 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43500 | 2005 | 294581 | 8451 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 267929 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019309 | OH | Sus | 31424310 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-1103 | 153661103 | OTHER |  | 43501 | 15 | 291233 | 806 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2418 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018225 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE |  | 43500 | 2314 | 291191 | 6336 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 272706 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018389 | OH | Sus | 31424310 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43500 | 2005 | 295068 | 9972 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 129636 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019500 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43500 | 1608 | 291138 | 2943 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 258984 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018681 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1103 | 153661103 | FUSE |  | 43501 | 1359 | 295750 | 4321 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 25926 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0019791 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-1103 | 153661103 | FUSE |  | 43501 | 1415 | 294177 | 3233 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 64660 | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 19-0019096 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43500 | 1805 | 291035 | 10056 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 181008 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019448 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1103 | 153661103 | FUSE |  | 43501 | 328 | 291689 | 3699 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 77679 | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 19-0019102 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43513 | 939 | 316434 | 768 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 15360 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025227 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1107 | 152261107 | FUSE |  | 43505 | 2308 | 297566 | 966 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 42504 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020560 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43506 | 213 | 299062 | 2059 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12354 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020745 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43513 | 939 | 315988 | 1504 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 91744 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025171 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | APPLE HILL-1103 | 153661103 | FUSE |  | 43501 | 1347 | 292792 | 2938 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5876 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 19-0018585 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1111 | 153081111 | SWITCH |  | 43501 | 611 | 292222 | 899 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 45849 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018387 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1103 | 153661103 | OTHER |  | 43506 | 16 | 297828 | 2274 | Distribution Circuit | Vegetation | Tree - fell into line | 233 | 395822 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020529 | OH | Sus | 43666953 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | SWITCH |  | 43512 | 1527 | 315874 | 3148 | Distribution Circuit | Vegetation | Tree - fell into line | 307 | 608094 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025143 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | FUSE |  | 43501 | 523 | 291644 | 2182 | Distribution Circuit | Vegetation | Tree - bark fell into line | 11 | 24002 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018699 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE |  | 43501 | 1237 | 292672 | 399 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 26 | 10374 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018656 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | FUSE |  | 43505 | 2224 | 297491 | 1258 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 11322 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0020544 | OH | Sus | 43666953 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43510 | 313 | 306513 | 967 | Distribution Circuit | Vegetation | Tree - fell into line | 211 | 137201 | Overcast-Drizzle-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0023200 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE |  | 43501 | 1400 | 292936 | 1485 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5430 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018706 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE |  | 43501 | 1348 | 293048 | 4467 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 56457 | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 19-0018707 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE |  | 43501 | 1351 | 293066 | 2769 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 11076 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018750 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | RECLOSER |  | 43506 | 804 | 297872 | 2154 | Distribution Circuit | Vegetation | Tree - fell into line | 640 | 326964 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020600 | OH | Sus | 31424310 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | OCB |  | 43505 | 1826 | 297302 | 2624 | Distribution Circuit | Vegetation | Tree - fell into line | 1824 | 194084 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020394 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | OCB |  | 43500 | 2005 | 290949 | 5496 | Distribution Circuit | Vegetation | Tree - fell into line | 3456 | 14931003 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018147 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 43500 | 2120 | 291112 | 2701 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 216439 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018728 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43506 | 1626 | 299177 | 2548 | Distribution Circuit | Vegetation | Tree - branch fell on line | 103 | 128114 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0021011 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | OTHER |  | 43513 | 1630 | 316643 | 1227 | Distribution Circuit | Vegetation | Tree - fell into line | 2378 | 76952 | Partly Cloudy-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025299 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43510 | 246 | 306426 | 1086 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 17376 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023618 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 43508 | 2325 | 301511 | 4050 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 48600 | Overcast-Drizzle-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0021897 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 43506 | 352 | 298337 | 3548 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 24836 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020831 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | RECLOSER |  | 43501 | 808 | 291613 | 5953 | Distribution Circuit | Vegetation | Tree - fell into line | 423 | 1188276 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018316 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER |  | 43506 | 114 | 297664 | 3680 | Distribution Circuit | Vegetation | Tree - fell into line | 655 | 99252 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020501 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER |  | 43501 | 507 | 291626 | 6324 | Distribution Circuit | Environmental/External | Ice or snow | 655 | 3029661 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018257 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 43506 | 117 | 297773 | 3478 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 76516 | Overcast-Fog;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0020799 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 43506 | 352 | 299366 | 3525 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 52875 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020834 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 43512 | 652 | 313518 | 4835 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 135380 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0024509 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 43506 | 352 | 299195 | 3563 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 99764 | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 19-0021142 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 43505 | 2148 | 299064 | 2740 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 87680 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020748 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 43505 | 2144 | 297460 | 2327 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 41886 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020476 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 43501 | 142 | 292643 | 2622 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 65550 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018506 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 43512 | 839 | 313702 | 341 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 5797 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0024444 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | RECLOSER |  | 43511 | 2231 | 313131 | 917 | Distribution Circuit | Vegetation | Tree - fell into line | 504 | 80245 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0024355 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43505 | 1522 | 305017 | 7228 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 36140 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0022378 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER |  | 43513 | 1334 | 315960 | 1651 | Distribution Circuit | Vegetation | Tree - fell into line | 1166 | 602490 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025163 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER |  | 43501 | 916 | 291952 | 2773 | Distribution Circuit | Vegetation | Tree - fell into line | 1442 | 1454949 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018370 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43506 | 125 | 298784 | 6625 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 72875 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020667 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43513 | 1303 | 317233 | 3319 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 36509 | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 19-0025534 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER |  | 43513 | 1303 | 315909 | 3319 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 564230 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025200 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43506 | 333 | 298342 | 2233 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 44660 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020598 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43505 | 1522 | 305286 | 7344 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 22032 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0022473 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 43505 | 2115 | 299860 | 4235 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 160930 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021032 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 43512 | 405 | 314041 | 3586 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 54053 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0024518 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 43505 | 2115 | 299702 | 4235 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 38115 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020958 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | APPLE HILL-1103 | 153661103 | OTHER |  | 43501 | 1412 | 294330 | 2965 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 125536 | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 19-0019175 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43513 | 1259 | 315892 | 467 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 34091 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025157 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43505 | 2339 | 297587 | 2326 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 27912 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020669 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43506 | 333 | 298897 | 922 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 7376 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020690 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1110 | 153081110 | FUSE |  | 43513 | 956 | 315526 | 377 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 6786 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025168 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43513 | 1216 | 315826 | 2872 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 48824 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025261 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43512 | 1033 | 313872 | 226 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 4520 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024545 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | OCB |  | 43505 | 2249 | 297461 | 4141 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1097 | 3128800 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020499 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | OCB |  | 43501 | 731 | 291874 | 681 | Distribution Circuit | Vegetation | Tree - fell into line | 1649 | 512931 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018302 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43501 | 620 | 291730 | 1932 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 197064 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018646 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 43522 | 2334 | 326648 | 726 | Distribution Circuit | Vegetation | Tree - fell into line | 130 | 94380 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028825 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 43509 | 1713 | 305363 | 1050 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5250 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022544 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | JUMPER |  | 43513 | 1440 | 317409 | 1653 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 21286 | Partly Cloudy-Fog;Below 32 F | Connector or Splice (OH) | Broken- wire on ground | 19-0025572 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43510 | 721 | 307366 | 681 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 13626 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023516 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | OTHER |  | 43501 | 855 | 292101 | 340 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2360 | 89237 | Overcast-Fog-Snow;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 19-0018473 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43509 | 337 | 302511 | 648 | Distribution Circuit | Vegetation | Tree - fell into line | 928 | 68664 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021817 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER |  | 43523 | 1923 | 327564 | 92 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 3470 | Strong Winds-Rain-Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028627 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER |  | 43513 | 900 | 315453 | 560 | Distribution Circuit | Vegetation | Tree - fell into line | 235 | 73936 | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0025057 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 43513 | 941 | 315504 | 303 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 9999 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025085 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PENRYN-1105 | 152561105 | FUSE |  | 43508 | 2258 | 301454 | 1023 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 11882 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022266 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | FUSE |  | 43510 | 304 | 306487 | 450 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 13500 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022782 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 43523 | 955 | 326830 | 611 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 611 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0028907 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 43510 | 633 | 307197 | 817 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 7353 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023580 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 43512 | 731 | 313538 | 2048 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4096 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0024475 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43511 | 125 | 311100 | 743 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 31949 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023780 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 43506 | 107 | 297594 | 2487 | Distribution Circuit | Vegetation | Tree - fell into line | 658 | 491996 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020496 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 43506 | 428 | 297836 | 2276 | Distribution Circuit | Vegetation | Tree - fell into line | 479 | 389929 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020496 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 43512 | 1154 | 314164 | 3428 | Distribution Circuit | Vegetation | Tree - fell into line | 475 | 656583 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 19-0024541 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER |  | 43522 | 2312 | 325667 | 201 | Distribution Circuit | Vegetation | Tree - fell into line | 3664 | 483938 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028627 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43512 | 937 | 315158 | 3565 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 28520 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0024963 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | FUSE |  | 43500 | 755 | 289665 | 312 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 2216 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017836 | OH | Sus | 31424320 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | JUMPER |  | 43512 | 422 | 318138 | 5096 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 20384 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025734 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | RECLOSER |  | 43523 | 324 | 326235 | 850 | Distribution Circuit | Vegetation | Tree - fell into line | 892 | 503360 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028697 | OH | Sus | 31426710 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | TRIP-SAVER |  | 43505 | 2040 | 297407 | 1050 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 97650 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020450 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | RECLOSER |  | 43511 | 138 | 311107 | 838 | Distribution Circuit | Vegetation | Tree - fell into line | 621 | 241224 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023772 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE |  | 43522 | 2231 | 325497 | 696 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6960 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028630 | OH | Sus | 31426710 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | JUMPER |  | 43522 | 2237 | 325506 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2240 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028978 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | HIGGINS-1110 | 152691110 | FUSE |  | 43523 | 141 | 326086 | 765 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 14535 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028877 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1109 | 152691109 | OTHER |  | 43523 | 701 | 326563 | 584 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 2684 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028781 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | OTHER |  | 43512 | 359 | 313468 | 684 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 24884 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0024393 | OH | Sus | 31424320 | 2019 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | OTHER |  | 43512 | 130 | 313722 | 1473 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 115880 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0024463 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | FUSE |  | 43510 | 329 | 306570 | 3541 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 21246 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0023576 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | RECLOSER |  | 43508 | 2248 | 301407 | 735 | Distribution Circuit | Vegetation | Tree - fell into line | 1517 | 170849 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021653 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | RECLOSER |  | 43510 | 122 | 306138 | 1045 | Distribution Circuit | Vegetation | Tree - fell into line | 1660 | 501037 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022733 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 43510 | 1918 | 310859 | 1253 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 12530 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023744 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE |  | 43523 | 343 | 326257 | 1866 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3732 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028926 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | OTHER |  | 43511 | 1859 | 313126 | 1011 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 35000 | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 19-0024353 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 43510 | 322 | 306770 | 2353 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 91767 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0022976 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER |  | 43505 | 2110 | 297435 | 959 | Distribution Circuit | Vegetation | Tree - fell into line | 1059 | 394653 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020434 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 43510 | 216 | 306358 | 2331 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 27972 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022843 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE |  | 43512 | 1822 | 314938 | 2679 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 16074 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0024752 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE |  | 43505 | 2057 | 297424 | 1285 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 147775 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020473 | OH | Sus | 31424320 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | SWITCH |  | 43506 | 1238 | 298919 | 194 | Distribution Circuit | Environmental/External | Ice or snow | 127 | 24638 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020703 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 43506 | 1855 | 299288 | 1275 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4979 | Partly Cloudy;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020821 | OH | Sus | 31424320 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 43512 | 2312 | 315155 | 1239 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6195 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025018 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 43508 | 2147 | 301343 | 922 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 117015 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021859 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE |  | 43513 | 810 | 316026 | 3305 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 128895 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025180 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 43508 | 758 | 300407 | 518 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 23752 | Partly Cloudy;Below 32 F | Crossarm- Wood | Broken- wire on ground | 19-0021345 | OH | Sus | 31424320 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE |  | 43513 | 810 | 316019 | 1750 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 21000 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025179 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | OTHER |  | 43506 | 343 | 297900 | 526 | Distribution Circuit | Vegetation | Tree - fell into line | 139 | 72376 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020643 | OH | Sus | 31424320 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | RECLOSER |  | 43506 | 224 | 297571 | 946 | Distribution Circuit | Equipment Failure/Involved | Overhead | 399 | 273390 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0020521 | OH | Sus | 31424320 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 43505 | 2057 | 297419 | 2787 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 256404 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0020420 | OH | Sus | 31424320 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 43513 | 1031 | 316476 | 2060 | Distribution Circuit | Vegetation | Tree - grew into line | 7 | 14420 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025239 | OH | Sus | 31424320 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 43505 | 1830 | 299268 | 2657 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5314 | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on object | 19-0020807 | OH | Sus | 31424320 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 43510 | 820 | 307717 | 2161 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 30254 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023299 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 43523 | 220 | 326150 | 2081 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 13536 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028802 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | SPAULDING-1101 | 152251101 | SWITCH |  | 43522 | 1610 | 325163 | 8792 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 26376 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028532 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 43510 | 1630 | 310190 | 1630 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 22260 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | On Ground | 19-0023817 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | OTHER |  | 43500 | 801 | 289699 | 464 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4440 | Overcast-Fog-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0017821 | OH | Sus | 31424257 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | OTHER |  | 43513 | 1115 | 315675 | 3169 | Distribution Circuit | Vegetation | Tree - fell into line | 201 | 123681 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0025165 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER |  | 43510 | 811 | 307702 | 2065 | Distribution Circuit | Vegetation | Tree - fell into line | 988 | 493014 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022925 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2102 | 153132102 | FUSE |  | 43522 | 702 | 323901 | 703 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6596 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028294 | OH | Sus | 31426712 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SPAULDING-1101 | 152251101 | RECLOSER |  | 43522 | 2029 | 325256 | 8434 | Distribution Circuit | Vegetation | Tree - fell into line | 319 | 753746 | Overcast-Fog-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028556 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SPAULDING-1101 | 152251101 | FUSE |  | 43522 | 1145 | 324380 | 1319 | Distribution Circuit | Vegetation | Tree - fell into line | 325 | 20759 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028268 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE |  | 43523 | 21 | 326443 | 2355 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 15741 | Partly Cloudy-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0029117 | OH | Sus | 31426712 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE |  | 43523 | 716 | 327317 | 1829 | Distribution Circuit | Vegetation | Tree - branch fell on line | 64 | 104929 | Strong Winds-Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0029148 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | COLUMBIA HILL-1101 | 152471101 | FUSE |  | 43523 | 307 | 326222 | 996 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 36852 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028884 | OH | Sus | 31426712 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER |  | 43522 | 13 | 323739 | 10688 | Distribution Circuit | Vegetation | Tree - fell into line | 1075 | 3063636 | Overcast-Fog-Snow-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0028071 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1102 | 152101102 | RECLOSER |  | 43505 | 1928 | 297365 | 5097 | Distribution Circuit | Vegetation | Tree - fell into line | 164 | 283891 | Overcast-Fog-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020403 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PIKE CITY-1102 | 152201102 | OTHER |  | 43508 | 1213 | 300654 | 1712 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 46224 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021425 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER |  | 43509 | 854 | 303404 | 2913 | Distribution Circuit | Vegetation | Tree - fell into line | 387 | 414101 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021943 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PIKE CITY-1102 | 152201102 | FUSE |  | 43512 | 325 | 315723 | 2300 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 62097 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025115 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 43510 | 1335 | 309444 | 1705 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 3410 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023305 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | PETALUMA C-1109 | 42631109 | FUSE |  | 43510 | 235 | 306411 | 743 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 11145 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022920 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 43522 | 2256 | 327079 | 2382 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 2382 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0029041 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | PETALUMA C-1109 | 42631109 | JUMPER |  | 43523 | 748 | 326533 | 244 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 788 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028857 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | OTHER |  | 43510 | 156 | 306893 | 916 | Distribution Circuit | Vegetation | Tree - fell into line | 138 | 86236 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022833 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE |  | 43510 | 711 | 307157 | 769 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2307 | Overcast-Fog-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022889 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE |  | 43510 | 21 | 306046 | 921 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 49734 | Overcast-Fog-Lightning-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022857 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE |  | 43510 | 1630 | 310194 | 1465 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1465 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023589 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE |  | 43522 | 2135 | 325329 | 2243 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 47603 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 19-0028795 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER |  | 43510 | 245 | 306425 | 847 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 36769 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022753 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | RECLOSER |  | 43505 | 1628 | 297191 | 1225 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1019 | 544883 | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 19-0020377 | OH | Sus | 43672759 | 2019 | FEB | Yes | Force Out | Yes | Yes
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 43510 | 714 | 307326 | 1836 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 12852 | Overcast-Fog-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023075 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1102 | 42271102 | TRANSFORMER |  | 43510 | 1138 | 307125 | 545 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1090 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023156 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1105 | 42271105 | RECLOSER |  | 43510 | 102 | 306093 | 1212 | Distribution Circuit | Vegetation | Tree - fell into line | 375 | 146016 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022725 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | FUSE |  | 43510 | 809 | 307621 | 1800 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7200 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023155 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | SALMON CREEK-1101 | 43161101 | RECLOSER |  | 43510 | 1934 | 310741 | 1296 | Distribution Circuit | Equipment Failure/Involved | Overhead | 182 | 171819 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023646 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 43522 | 1310 | 324525 | 3230 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 25840 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0029113 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 43523 | 100 | 326056 | 2204 | Distribution Circuit | Vegetation | Tree - fell into line | 253 | 23104 | Clear;32-90 F | Cutout- fuse holder | Broken- wire on ground | 19-0028695 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | FUSE |  | 43510 | 221 | 306375 | 519 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 19722 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022797 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 43508 | 2254 | 301430 | 676 | Distribution Circuit | Vegetation | Tree - fell into line | 247 | 166972 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021683 | OH | Sus | 43678389 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 43523 | 1336 | 327124 | 1377 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4081 | Clear;32-90 F | Conductor- Overhead | On Ground | 19-0029052 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | DUNBAR-1101 | 43071101 | FUSE |  | 43500 | 1329 | 290547 | 365 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 730 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018037 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 43508 | 1520 | 300805 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 247 | 18338 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021522 | OH | Sus | 43678033 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 43522 | 1949 | 325181 | 2726 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 57246 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0028952 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 43522 | 1717 | 324909 | 1513 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 58874 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028903 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | MIRABEL-1101 | 42091101 | FUSE |  | 43510 | 822 | 307730 | 1878 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9390 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023097 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | RECLOSER |  | 43522 | 1536 | 324785 | 5870 | Distribution Circuit | Environmental/External | Flood/Erosion | 492 | 300853 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0028450 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 43510 | 1211 | 308918 | 1815 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5445 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023186 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER |  | 43522 | 2248 | 325487 | 4178 | Distribution Circuit | Environmental/External | Flood/Erosion | 1431 | 4432998 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0028605 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER |  | 43510 | 2215 | 310977 | 3917 | Distribution Circuit | Vegetation | Tree - fell into line | 3897 | 403375 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0023738 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE |  | 43509 | 1748 | 305424 | 1705 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 15345 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022552 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER |  | 43523 | 54 | 325997 | 3944 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 244528 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0029555 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 43509 | 1700 | 305331 | 1570 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 58090 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022539 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | MIRABEL-1102 | 42091102 | FUSE |  | 43523 | 1051 | 326672 | 4654 | Distribution Circuit | Environmental/External | Flood/Erosion | 35 | 23082 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0029828 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 43522 | 2236 | 325505 | 5126 | Distribution Circuit | Environmental/External | Flood/Erosion | 10 | 51260 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0029858 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 43510 | 201 | 307665 | 3328 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 49920 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023123 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE |  | 43510 | 243 | 307636 | 1896 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9480 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022908 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 43522 | 2229 | 327860 | 4131 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 152847 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0029297 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | MIRABEL-1102 | 42091102 | FUSE |  | 43522 | 1854 | 325128 | 4191 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 37719 | Partly Cloudy-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028600 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE |  | 43522 | 1635 | 324876 | 4209 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 138897 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028499 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE |  | 43522 | 2115 | 325305 | 4064 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 52832 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | On Ground | 19-0029680 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 43522 | 2029 | 325251 | 4268 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 46948 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0029299 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 43522 | 605 | 323868 | 5260 | Distribution Circuit | Vegetation | Tree - fell into line | 144 | 160137 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028092 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER |  | 43523 | 543 | 326383 | 3763 | Distribution Circuit | Environmental/External | Flood/Erosion | 117 | 245153 | Clear;32-90 F | Conductor- Overhead | On Ground | 19-0028728 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | RECLOSER |  | 43522 | 217 | 323781 | 1056 | Distribution Circuit | Vegetation | Tree - fell into line | 156 | 30950 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0028067 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE |  | 43522 | 1930 | 325158 | 5563 | Distribution Circuit | Environmental/External | Flood/Erosion | 16 | 89008 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0029861 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 43522 | 339 | 323831 | 511 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 511 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028074 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 43522 | 1932 | 325162 | 2764 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 38696 | Clear;32-90 F | Conductor- Overhead | On Ground | 19-0029351 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | TRIP-SAVER |  | 43522 | 1556 | 324897 | 4590 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 362610 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | On Ground | 19-0029429 | OH | Sus | 0 | 2019 | FEB | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 43523 | 40 | 326022 | 1092 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 48048 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028678 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER |  | 43508 | 1810 | 300950 | 1434 | Distribution Circuit | Vegetation | Tree - branch fell on line | 229 | 248170 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021884 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER |  | 43509 | 2208 | 305797 | 609 | Distribution Circuit | Vegetation | Tree - branch fell on line | 187 | 113883 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022647 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 43510 | 1700 | 310380 | 2546 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 7637 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023561 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 43506 | 912 | 297225 | 206 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 412 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020629 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE |  | 43522 | 2220 | 325471 | 1214 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 43850 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | On Ground | 19-0028881 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | CLOVERDALE-1101 | 42821101 | FUSE |  | 43522 | 2230 | 325553 | 705 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 61694 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028671 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE |  | 43498 | 751 | 286893 | 503 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 7079 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017029 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE |  | 43506 | 829 | 298386 | 578 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 3468 | Overcast-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0020719 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1701 | 163451701 | JUMPER |  | 43501 | 1541 | 293545 | 1502 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 78423 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018737 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1701 | 163451701 | FUSE |  | 43501 | 550 | 291667 | 625 | Distribution Circuit | Equipment Failure/Involved | Overhead | 101 | 37682 | Overcast-Fog;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018332 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | STANISLAUS-1701 | 162821701 | FUSE |  | 43508 | 2344 | 301573 | 1061 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 11671 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021926 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | STANISLAUS-1701 | 162821701 | FUSE |  | 43509 | 537 | 302980 | 240 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1395 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021927 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | STANISLAUS-1701 | 162821701 | RECLOSER |  | 43501 | 1226 | 292648 | 1502 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 50889 | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 19-0018519 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1701 | 162821701 | FUSE |  | 43498 | 1030 | 287195 | 550 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 36850 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017131 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER |  | 43506 | 622 | 298092 | 708 | Distribution Circuit | Vegetation | Tree - fell into line | 806 | 505850 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020604 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER |  | 43508 | 2158 | 301268 | 1006 | Distribution Circuit | Equipment Failure/Involved | Overhead | 320 | 296876 | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 19-0021682 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 43508 | 2158 | 301646 | 899 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 899 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021688 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER |  | 43510 | 834 | 307824 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 279 | 89151 | Overcast-Fog-Heavy Rain-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022953 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 43511 | 1304 | 312173 | 1392 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 7455 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024085 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | FROGTOWN-1701 | 163451701 | OTHER |  | 43501 | 1149 | 294504 | 2828 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 8484 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0019268 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER |  | 43510 | 45 | 306057 | 1032 | Distribution Circuit | Vegetation | Tree - fell into line | 499 | 207326 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 19-0022721 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER |  | 43506 | 502 | 298003 | 2398 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1157 | 229279 | Overcast-Fog;32-90 F | Insulator | Broken- wire on ground | 19-0020552 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER |  | 43510 | 725 | 307292 | 1878 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 42123 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022883 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 43510 | 933 | 310174 | 1773 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 21276 | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0023585 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | JUMPER |  | 43511 | 1156 | 312361 | 421 | Distribution Circuit | Vegetation | Tree - fell into line | 670 | 22318 | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 19-0024011 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER |  | 43522 | 1955 | 325192 | 608 | Distribution Circuit | Vegetation | Tree - fell into line | 1464 | 166100 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028537 | OH | Sus | 31426840 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER |  | 43498 | 802 | 286877 | 1854 | Distribution Circuit | Vegetation | Tree - fell into line | 947 | 411236 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0017012 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 43501 | 754 | 291945 | 1920 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 29200 | Clear;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018437 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | ELECTRA-1102 | 162161102 | FUSE |  | 43510 | 1430 | 309676 | 1630 | Distribution Circuit | Environmental/External | Water | 1 | 1630 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0023377 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 43511 | 442 | 311324 | 873 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 31767 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023840 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | CALAVERAS CEMENT-1101 | 162211101 | JUMPER |  | 43501 | 105 | 294675 | 5149 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 30894 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019333 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 43508 | 2158 | 303503 | 1213 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4852 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021994 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | JUMPER |  | 43513 | 2132 | 317122 | 875 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5894 | Partly Cloudy;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025518 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | JUMPER |  | 43508 | 2158 | 305441 | 5313 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5313 | Overcast;32-90 F | Conductor- Overhead | On Ground | 19-0022521 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
STOCKTON | Tier 3 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 43501 | 1139 | 292553 | 2984 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 10720 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018566 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | JUMPER |  | 43510 | 703 | 310391 | 1947 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9735 | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0022883 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 43510 | 27 | 308001 | 1080 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2160 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022998 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | SWITCH |  | 43508 | 2158 | 305355 | 2399 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 338259 | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 19-0021682 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
STOCKTON | Tier 3 | CALAVERAS CEMENT-1101 | 162211101 | SWITCH |  | 43501 | 239 | 292459 | 3035 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 397585 | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 19-0018236 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | JUMPER |  | 43501 | 239 | 294962 | 3388 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3388 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019447 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 43511 | 1805 | 312802 | 2583 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 51432 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024267 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 43501 | 20 | 292308 | 2875 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 48875 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018397 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
STOCKTON | Tier 2 | ELECTRA-1102 | 162161102 | RECLOSER |  | 43508 | 2147 | 301202 | 2600 | Distribution Circuit | Equipment Failure/Involved | Overhead | 309 | 283608 | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 19-0021705 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | ELECTRA-1102 | 162161102 | RECLOSER |  | 43506 | 742 | 298370 | 629 | Distribution Circuit | Vegetation | Tree - fell into line | 309 | 147456 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020696 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | WEST POINT-1101 | 163201101 | TRIP-SAVER |  | 43510 | 1140 | 308760 | 1340 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 115240 | Overcast-Fog-Heavy Rain-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023158 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | WEST POINT-1101 | 163201101 | FUSE |  | 43505 | 1022 | 296844 | 1819 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 10911 | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0020382 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 43508 | 2208 | 301311 | 3753 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 86319 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023879 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | RECLOSER |  | 43506 | 551 | 298046 | 625 | Distribution Circuit | Vegetation | Tree - fell into line | 360 | 191610 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020563 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | SWITCH |  | 43501 | 20 | 291610 | 5322 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 505590 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018209 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE |  | 43510 | 557 | 307096 | 276 | Distribution Circuit | Vegetation | Tree - fell into line | 138 | 20703 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022868 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | Yes
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER |  | 43501 | 20 | 293663 | 4020 | Distribution Circuit | Vegetation | Tree - fell into line | 175 | 703500 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018749 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 43501 | 20 | 293696 | 4020 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 24120 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on object | 19-0018760 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER |  | 43510 | 825 | 307719 | 554 | Distribution Circuit | Vegetation | Tree - fell into line | 1065 | 267879 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022935 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER |  | 43501 | 20 | 291260 | 5333 | Distribution Circuit | Vegetation | Tree - fell into line | 739 | 2006234 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018209 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | WEST POINT-1101 | 163201101 | FUSE |  | 43501 | 20 | 293110 | 3518 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 56288 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018725 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | JUMPER |  | 43501 | 44 | 293004 | 2275 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2275 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018685 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | TRIP-SAVER |  | 43509 | 419 | 302626 | 863 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 84574 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0021834 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | TRIP-SAVER |  | 43501 | 44 | 291750 | 2275 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 220675 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018435 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | OTHER |  | 43501 | 900 | 292454 | 490 | Distribution Circuit | Vegetation | Tree - fell into line | 535 | 27685 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018429 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | OTHER |  | 43506 | 434 | 298489 | 893 | Distribution Circuit | Vegetation | Tree - fell into line | 330 | 161234 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020740 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER |  | 43500 | 508 | 289485 | 408 | Distribution Circuit | Vegetation | Tree - fell into line | 450 | 75420 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | On Ground | 19-0017698 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | OTHER |  | 43501 | 1504 | 292931 | 845 | Distribution Circuit | Vegetation | Tree - fell into line | 624 | 107164 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018715 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 43501 | 44 | 294411 | 3944 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 59160 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0019217 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | JUMPER |  | 43501 | 44 | 292901 | 3944 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 15776 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018624 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | TRIP-SAVER |  | 43501 | 8 | 291225 | 3977 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 441447 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018256 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE |  | 43500 | 458 | 289473 | 900 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 18900 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0017827 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 43501 | 900 | 292943 | 1843 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 125324 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018360 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER |  | 43500 | 2348 | 291212 | 3968 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4362 | 5966430 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018203 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 43501 | 900 | 294555 | 2088 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 29232 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | On Ground | 19-0019344 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | TRIP-SAVER |  | 43501 | 1518 | 292941 | 1587 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 25958 | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0018683 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER |  | 43501 | 718 | 291856 | 2375 | Distribution Circuit | Vegetation | Tree - fell into line | 198 | 467194 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018333 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 43505 | 927 | 296794 | 4848 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 24240 | Overcast-Fog;32-90 F | Conductor- Overhead | On Ground | 19-0020300 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 43500 | 1651 | s1413559 | 6591 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 32955 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0019771 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 43501 | 733 | 292405 | 2155 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 2155 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | On Ground | 19-0018413 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 43510 | 818 | 307704 | 1611 | Distribution Circuit | Vegetation | Tree - bark fell into line | 123 | 81827 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023309 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 43501 | 1918 | 293668 | 2707 | Distribution Circuit | Vegetation | Tree - fell into line | 975 | 227161 | Partly Cloudy-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019045 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER |  | 43500 | 2348 | 295544 | 5519 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5519 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019749 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER |  | 43508 | 2309 | 304538 | 1129 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 10810 | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0022237 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 43501 | 900 | 294714 | 3337 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 83425 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019346 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER |  | 43500 | 2348 | 294845 | 4940 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 415230 | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 19-0019376 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | MARTELL-1101 | 163011101 | OTHER |  | 43506 | 629 | 298159 | 775 | Distribution Circuit | Equipment Failure/Involved | Overhead | 84 | 27748 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020636 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 43500 | 2348 | 294150 | 3933 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 66861 | Partly Cloudy-Fog;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0019078 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER |  | 43508 | 2201 | 301211 | 665 | Distribution Circuit | Vegetation | Tree - branch fell on line | 970 | 397339 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021636 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER |  | 43500 | 2207 | 291131 | 955 | Distribution Circuit | Vegetation | Tree - fell into line | 955 | 111619 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018191 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER |  | 43513 | 1455 | 316342 | 1724 | Distribution Circuit | Vegetation | Tree - fell into line | 946 | 337775 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025203 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 43501 | 102 | s1412617 | 3685 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 29480 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0018419 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 43513 | 1612 | 316477 | 2825 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 42375 | Overcast-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 19-0025721 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 43500 | 2207 | 295231 | 5302 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 79530 | Clear;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0019560 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER |  | 43506 | 751 | 298123 | 167 | Distribution Circuit | 3rd Party | Vehicle | 100 | 16700 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on object | 19-0020591 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 43501 | 900 | 295243 | 4773 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 38184 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019561 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 43501 | 900 | 292843 | 2163 | Distribution Circuit | Environmental/External | Ice or snow | 32 | 69216 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018608 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 43500 | 727 | 289520 | 442 | Distribution Circuit | Vegetation | Tree - fell into line | 237 | 16842 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0017737 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | OTHER |  | 43506 | 535 | 298021 | 660 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 42108 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020689 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 43501 | 544 | 292108 | 2463 | Distribution Circuit | Vegetation | Tree - fell into line | 150 | 369450 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018353 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 43513 | 1216 | 315830 | 1732 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 90064 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025153 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | OTHER |  | 43508 | 2206 | 301439 | 896 | Distribution Circuit | Vegetation | Tree - fell into line | 312 | 38519 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021737 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | OTHER |  | 43513 | 638 | 315356 | 2010 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 21210 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025037 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER |  | 43506 | 534 | 298529 | 768 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 5376 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020633 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | OLETA-1102 | 163541102 | FUSE |  | 43506 | 556 | 298050 | 870 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 46980 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020764 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | SALT SPRINGS-2101 | 163692101 | FUSE |  | 43501 | 1645 | 293028 | 10075 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 473525 | Partly Cloudy-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020162 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE |  | 43501 | 727 | 291864 | 1644 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 16440 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018802 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | SWITCH |  | 43501 | 630 | 291604 | 3270 | Distribution Circuit | Equipment Failure/Involved | Overhead | 179 | 6474 | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 19-0018272 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE |  | 43500 | 1559 | 290667 | 308 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 37576 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0018110 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE |  | 43501 | 516 | 291635 | 888 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 88800 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018443 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1103 | 252531103 | OTHER |  | 43501 | 715 | 291830 | 699 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 959 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018528 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | FUSE |  | 43501 | 1815 | 294471 | 2460 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 19680 | Partly Cloudy;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019298 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER |  | 43501 | 842 | 292065 | 1620 | Distribution Circuit | Vegetation | Tree - fell into line | 889 | 546452 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018600 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2104 | 254432104 | FUSE |  | 43510 | 1035 | 308712 | 203 | Distribution Circuit | Vegetation | Tree - bark fell into line | 123 | 24969 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023104 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER |  | 43500 | 1913 | 290889 | 1020 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 80823 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018141 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER |  | 43512 | 1003 | 313840 | 481 | Distribution Circuit | Equipment Failure/Involved | Overhead | 109 | 11398 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024467 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER |  | 43506 | 1315 | 298972 | 295 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 13580 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020721 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | RECLOSER |  | 43510 | 1308 | 309344 | 4357 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 71879 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0023285 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE |  | 43501 | 835 | 292039 | 3543 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 47139 | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018767 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | FUSE |  | 43506 | 1011 | 298642 | 479 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 14849 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020702 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE |  | 43501 | 325 | 292939 | 2275 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 86187 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018651 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 43501 | 1141 | 292923 | 4360 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 34580 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018772 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 43500 | 1911 | 292665 | 4110 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 83195 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018959 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER |  | 43500 | 2124 | 291114 | 1256 | Distribution Circuit | Vegetation | Tree - fell into line | 466 | 201670 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018163 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | JUMPER |  | 43500 | 356 | 289483 | 791 | Distribution Circuit | Vegetation | Tree - fell into line | 3921 | 44912 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017701 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 43501 | 807 | 291898 | 571 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 48535 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018410 | OH | Sus | 31424289 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 43500 | 1935 | 290897 | 2694 | Distribution Circuit | Environmental/External | Ice or snow | 33 | 88902 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018502 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 43500 | 1641 | 290715 | 4003 | Distribution Circuit | Vegetation | Tree - fell into line | 140 | 439643 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018207 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1101 | 254421101 | FUSE |  | 43513 | 940 | 315503 | 1594 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 3188 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025209 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE |  | 43511 | 1610 | 312565 | 206 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 19570 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024204 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 43505 | 2124 | 298732 | 2382 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2382 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020653 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 43501 | 1820 | 293145 | 2664 | Distribution Circuit | Vegetation | Tree - branch fell on line | 226 | 102889 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019368 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 43505 | 1451 | 297222 | 1464 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 43920 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020388 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | JUMPER |  | 43508 | 2351 | 302499 | 890 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 26700 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021752 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | RECLOSER |  | 43509 | 205 | 301872 | 48 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 48 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 19-0021739 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER |  | 43500 | 1458 | 290572 | 4393 | Distribution Circuit | Vegetation | Tree - fell into line | 405 | 1778127 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0018046 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER |  | 43511 | 2042 | 312996 | 2338 | Distribution Circuit | Vegetation | Tree - fell into line | 669 | 1235032 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0024287 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 43509 | 720 | 302991 | 2065 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8478 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0022218 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 43506 | 720 | 298268 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 156 | 88452 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020587 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 43506 | 629 | 298472 | 657 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 7884 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0020626 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER |  | 43501 | 917 | 292153 | 376 | Distribution Circuit | Vegetation | Tree - fell into line | 416 | 155480 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018372 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER |  | 43510 | 1231 | 309804 | 1663 | Distribution Circuit | Vegetation | Tree - fell into line | 520 | 172967 | Overcast-Heavy Rain-Lightning-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023274 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER |  | 43509 | 246 | 302244 | 979 | Distribution Circuit | Vegetation | Tree - fell into line | 662 | 308990 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 19-0021738 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 43510 | 1541 | 310011 | 1694 | Distribution Circuit | Vegetation | Tree - bark fell into line | 8 | 13552 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023624 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 43510 | 1109 | 308494 | 1785 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 230265 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0023251 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 43510 | 1109 | 312712 | 1918 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5754 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023307 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 43510 | 655 | 307259 | 6355 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7441 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0022980 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 43501 | 29 | 293666 | 2511 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 198369 | Partly Cloudy;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018744 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 43498 | 534 | 286531 | 828 | Distribution Circuit | Animal | Other | 33 | 20102 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0016964 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 43501 | 29 | 292453 | 2511 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 22599 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018428 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 43510 | 1109 | 309451 | 3288 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 29592 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0023307 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 43506 | 532 | 298014 | 1898 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 49382 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020666 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 43510 | 1723 | 312097 | 4252 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 29764 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024031 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | CURTIS-1703 | 163351703 | FUSE |  | 43501 | 12 | 295701 | 4173 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 95979 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019778 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | FUSE |  | 43498 | 532 | 286525 | 485 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5820 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | On Ground | 19-0017053 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER |  | 43500 | 1057 | 290037 | 4853 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 227913 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0017879 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER |  | 43510 | 1205 | 308894 | 532 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 36708 | Overcast-Heavy Rain-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023182 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER |  | 43506 | 645 | 298026 | 1126 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 150544 | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0020568 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | SWITCH |  | 43511 | 1735 | 313231 | 1085 | Distribution Circuit | Vegetation | Tree - bark fell into line | 156 | 169260 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 19-0024219 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE |  | 43511 | 1737 | 314639 | 2611 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 20888 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 19-0024630 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | SWITCH |  | 43510 | 1205 | 310867 | 3294 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 209390 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023182 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | JUMPER |  | 43511 | 1737 | 315885 | 5663 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 11469 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025145 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | JUMPER |  | 43511 | 1737 | 315882 | 2903 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 14515 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025144 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE |  | 43498 | 1207 | 287373 | 401 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1840 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0017193 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | CURTIS-1703 | 163351703 | RECLOSER |  | 43511 | 1735 | 312723 | 1098 | Distribution Circuit | Vegetation | Tree - fell into line | 371 | 287294 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 19-0024219 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | CURTIS-1703 | 163351703 | RECLOSER |  | 43501 | 129 | 291313 | 2431 | Distribution Circuit | Vegetation | Tree - fell into line | 276 | 101536 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018224 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | CURTIS-1703 | 163351703 | RECLOSER |  | 43510 | 628 | 307191 | 645 | Distribution Circuit | Vegetation | Tree - fell into line | 2474 | 654340 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0022848 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE |  | 43510 | 1302 | 309596 | 1763 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 172774 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0023349 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER |  | 43501 | 712 | 291840 | 1986 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 333648 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018287 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER |  | 43501 | 635 | 291777 | 3281 | Distribution Circuit | Vegetation | Tree - fell into line | 645 | 452257 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018294 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1705 | 163781705 | FUSE |  | 43510 | 641 | 307244 | 912 | Distribution Circuit | Vegetation | Tree - branch fell on line | 101 | 68652 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023359 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 43501 | 602 | 293674 | 3188 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 47820 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018754 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | JUMPER |  | 43501 | 755 | 293014 | 3030 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 27270 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018690 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | RECLOSER |  | 43506 | 943 | 298591 | 337 | Distribution Circuit | Vegetation | Tree - fell into line | 521 | 69186 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020660 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE |  | 43501 | 759 | 292784 | 528 | Distribution Circuit | Environmental/External | Ice or snow | 162 | 58285 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018581 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1705 | 163781705 | FUSE |  | 43510 | 1110 | 308497 | 588 | Distribution Circuit | Vegetation | Tree - bark fell into line | 22 | 12936 | Overcast-Heavy Rain-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0023399 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1705 | 163781705 | FUSE |  | 43522 | 1336 | 324566 | 667 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 4831 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0028420 | OH | Sus | 31426754 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE |  | 43501 | 455 | 292759 | 4595 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 18380 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018565 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | JUMPER |  | 43501 | 629 | 293099 | 2061 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 39159 | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0018723 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1704 | 163761704 | FUSE |  | 43506 | 702 | 298156 | 192 | Distribution Circuit | Equipment Failure/Involved | Overhead | 555 | 34605 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020582 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | Yes
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | FUSE |  | 43506 | 542 | 298029 | 663 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 19160 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020620 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 43501 | 602 | 293063 | 3460 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 20760 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | On Ground | 19-0018713 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE |  | 43501 | 759 | 292598 | 4456 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 13368 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018489 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | SWITCH |  | 43501 | 759 | 293920 | 1978 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 219631 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 19-0018309 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | OTHER |  | 43501 | 812 | 291982 | 1918 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7672 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019232 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 43501 | 329 | 292224 | 2075 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 10375 | Overcast-Fog;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018388 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE |  | 43501 | 143 | 291320 | 2285 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 25135 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018463 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 43501 | 429 | 291709 | 3653 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 51142 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018632 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | FUSE |  | 43506 | 900 | 298461 | 710 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 8520 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0020720 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | OTHER |  | 43506 | 544 | 298288 | 650 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3508 | 366649 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0020606 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | Yes
YOSEMITE | Tier 2 | TAR FLAT-0401 | 163240401 | FUSE |  | 43506 | 723 | 298200 | 339 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 8166 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0020641 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | CURTIS-1705 | 163351705 | FUSE |  | 43501 | 226 | 294198 | 2385 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 109710 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019111 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | FUSE |  | 43501 | 1341 | 292776 | 4424 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4424 | Overcast-Drizzle;32-90 F | Conductor- Overhead | On Ground | 19-0019273 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | JUMPER |  | 43501 | 846 | 294448 | 3209 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6418 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019240 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 43501 | 602 | 293723 | 3288 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 23016 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018770 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE |  | 43501 | 226 | 294234 | 3485 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 45305 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0019132 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | CURTIS-1705 | 163351705 | FUSE |  | 43501 | 226 | 294231 | 3485 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 209100 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019131 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MIWUK-1702 | 163661702 | RECLOSER |  | 43501 | 120 | 291213 | 2457 | Distribution Circuit | Vegetation | Tree - fell into line | 183 | 414415 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018222 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | RECLOSER |  | 43501 | 1007 | 292342-2 | 1755 | Distribution Circuit | Vegetation | Tree - fell into line | 791 | 838169 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0018399 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | RECLOSER |  | 43501 | 710 | 291831 | 4570 | Distribution Circuit | Vegetation | Tree - branch fell on line | 132 | 113685 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018284 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | RECLOSER |  | 43501 | 335 | 291292 | 3774 | Distribution Circuit | Vegetation | Tree - fell into line | 246 | 876060 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018245 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | TRIP-SAVER |  | 43501 | 602 | 294031 | 2300 | Distribution Circuit | Vegetation | Tree - fell into line | 266 | 525355 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019034 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | JUMPER |  | 43509 | 740 | 304757 | 465 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 930 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022332 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 43501 | 49 | 292339 | 4338 | Distribution Circuit | Vegetation | Tree - fell into line | 204 | 884952 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on object | 19-0018398 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | RECLOSER |  | 43501 | 116 | 291286 | 3940 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 520747 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018218 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 43501 | 116 | 295365 | 4001 | Distribution Circuit | Vegetation | Tree - fell into line | 160 | 640160 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019632 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | JUMPER |  | 43509 | 806 | 303130 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 469 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0022034 | OH | Sus | 0 | 2019 | FEB | Yes | Open Circuit | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | SWITCH |  | 43501 | 49 | 292372 | 4367 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 235818 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on object | 19-0018407 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | FUSE |  | 43501 | 116 | 295287 | 3940 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 31520 | Clear;Below 32 F | Conductor- Overhead | On Ground | 19-0019594 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 43512 | 1657 | 315774 | 4117 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 32138 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025234 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | FUSE |  | 43501 | 116 | 292733 | 3940 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 149720 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018550 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | JUMPER |  | 43501 | 1007 | 294032 | 2962 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5924 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0019036 | OH | Sus | 0 | 2019 | FEB | Yes | None | Yes | No
YOSEMITE | Tier 3 | RACETRACK-1703 | 163761703 | SWITCH |  | 43501 | 1007 | 294131 | 2945 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 58900 | Overcast-Snow;Below 32 F | Conductor- Overhead | On Ground | 19-0019064 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 43501 | 602 | 293975 | 4853 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 57423 | Overcast-Fog;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018263 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER |  | 43512 | 1742 | 314873 | 3067 | Distribution Circuit | Vegetation | Tree - fell into line | 208 | 124801 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0024698 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER |  | 43513 | 1505 | 317521 | 2493 | Distribution Circuit | Vegetation | Tree - fell into line | 185 | 442429 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025206 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 43512 | 1749 | 314878 | 140 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 7280 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0024703 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 43513 | 453 | 315233 | 949 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 49348 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025065 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | JUMPER |  | 43501 | 335 | 295829 | 6178 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6178 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0019811 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | CURTIS-1704 | 163351704 | JUMPER |  | 43506 | 802 | 298856 | 714 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 714 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0020594 | OH | Sus | 0 | 2019 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 43512 | 1807 | 314908 | 2847 | Distribution Circuit | Vegetation | Tree - fell into line | 355 | 805589 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025095 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | CURTIS-1704 | 163351704 | JUMPER |  | 43501 | 1930 | 293662 | 1038 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 20016 | Partly Cloudy;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018977 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | Yes
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | TRIP-SAVER |  | 43512 | 2119 | 315193 | 2609 | Distribution Circuit | Vegetation | Tree - fell into line | 194 | 152040 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025060 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER |  | 43509 | 632 | 302899 | 736 | Distribution Circuit | Vegetation | Tree - fell into line | 139 | 66400 | Overcast-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0021822 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 43513 | 1329 | 315995 | 2788 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 55760 | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0025202 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER |  | 43512 | 1353 | 314559 | 1664 | Distribution Circuit | Environmental/External | Ice or snow | 611 | 220748 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024598 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | OCB |  | 43513 | 1142 | 315741 | 391 | Distribution Circuit | Vegetation | Tree - fell into line | 3739 | 345369 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025122 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | OCB |  | 43501 | 330 | 291297 | 2522 | Distribution Circuit | Vegetation | Tree - fell into line | 3248 | 2051686 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018244 | OH | Sus | 0 | 2019 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | JUMPER |  | 43501 | 1905 | 293856 | 2915 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5830 | Partly Cloudy;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018962 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | TRANSFORMER |  | 43505 | 2220 | 297487 | 2189 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2189 | Rain-Overcast;32-90 F | Transformer | Broken- wire on ground | 19-0020474 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 43512 | 1749 | 315045 | 2916 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2916 | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 19-0024755 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 43513 | 1916 | 316743 | 1546 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 20098 | Partly Cloudy;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0025367 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 43501 | 446 | 291615 | 2333 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 30329 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0018659 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 43512 | 1424 | 314599 | 1685 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 21905 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0024690 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 43513 | 1809 | 316637 | 1521 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 89104 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0025313 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | FUSE |  | 43501 | 1905 | 293635 | 697 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 19516 | Partly Cloudy;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0018961 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER |  | 43509 | 433 | 302650 | 558 | Distribution Circuit | Vegetation | Tree - fell into line | 360 | 147520 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0021776 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER |  | 43512 | 1055 | 313959 | 4412 | Distribution Circuit | Vegetation | Tree - fell into line | 687 | 201858 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0024502 | OH | Sus | 0 | 2019 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | RECLOSER |  | 43481 | 1922 | 269755 | 2778 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 256680 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010102 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | OTHER |  | 43481 | 2147 | 271259 | 2308 | Distribution Circuit | Equipment Failure/Involved | Overhead | 442 | 215330 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010513 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | HATTON-1101 | 182291101 | FUSE |  | 43471 | 2124 | 258155 | 1208 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 118384 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005554 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE |  | 43481 | 1553 | 267639 | 1703 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 133721 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009950 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 43482 | 712 | 272776 | 677 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 32496 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011238 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE |  | 43481 | 2300 | 271781 | 1301 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 171732 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011094 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | JUMPER |  | 43482 | 2112 | 275005 | 2237 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 6711 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011498 | OH | Sus | 0 | 2019 | JAN | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | OCB |  | 43481 | 1608 | 267368 | 1702 | Distribution Circuit | Vegetation | Tree - fell into line | 2026 | 1063227 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0009860 | OH | Sus | 0 | 2019 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 43481 | 2142 | 275017 | 2725 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 84475 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011468 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE |  | 43481 | 2123 | 275097 | 2666 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 39990 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011497 | OH | Sus | 0 | 2019 | JAN | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE |  | 43481 | 1559 | 275086 | 4111 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 45221 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0011489 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 43481 | 2142 | 275690 | 3843 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 23058 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011728 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 43481 | 2142 | 274260 | 2732 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 19124 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011129 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE |  | 43471 | 1657 | 255730 | 2988 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 42633 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0005401 | OH | Sus | 31420586 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | JUMPER |  | 43471 | 1658 | 255732 | 1448 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1448 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005269 | OH | Sus | 0 | 2019 | JAN | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | OCB |  | 43481 | 2123 | 270492 | 2667 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5206 | 4928972 | Overcast-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0010273 | OH | Sus | 0 | 2019 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | OCB |  | 43482 | 59 | 272227 | 463 | Distribution Circuit | Vegetation | Tree - fell into line | 209 | 86031 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010474 | OH | Sus | 43634200 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | SECTIONALIZER |  | 43471 | 1814 | 256397 | 1422 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 55681 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005268 | OH | Sus | 0 | 2019 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 43481 | 2036 | 270730 | 984 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 35424 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010516 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | RECLOSER |  | 43481 | 1616 | 267767 | 1243 | Distribution Circuit | Equipment Failure/Involved | Overhead | 600 | 198534 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009896 | OH | Sus | 43634200 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER |  | 43481 | 1947 | 270139 | 1468 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1193 | 406884 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010136 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER |  | 43481 | 1439 | 267213 | 1794 | Distribution Circuit | Vegetation | Tree - fell into line | 380 | 79995 | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 19-0009754 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE |  | 43481 | 1907 | 269626 | 2702 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 62354 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011063 | OH | Sus | 31422108 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE |  | 43471 | 2038 | 258732 | 1422 | Distribution Circuit | Vegetation | Tree - fell into line | 163 | 72469 | Overcast;32-90 F | Conductor- Overhead | On Ground | 19-0005661 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER |  | 43471 | 1944 | 257358 | 1633 | Distribution Circuit | Equipment Failure/Involved | Overhead | 269 | 262292 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0005363 | OH | Sus | 31420586 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 43482 | 1500 | 275004 | 1282 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1282 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011432 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2104 | 83252104 | OTHER |  | 43471 | 1713 | 255929 | 425 | Distribution Circuit | Vegetation | Tree - fell into line | 295 | 58445 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005263 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 43471 | 1726 | 255878 | 1457 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 85963 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005797 | OH | Sus | 0 | 2019 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2105 | 83252105 | FUSE |  | 43471 | 1743 | 256015 | 1202 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4808 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005466 | OH | Sus | 0 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | SECTIONALIZER |  | 43471 | 1818 | 256412 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 2129 | 376381 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005332 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | SWITCH |  | 43482 | 829 | 273472 | 541 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 52477 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010915 | OH | Sus | 0 | 2019 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | RECLOSER |  | 43482 | 723 | 272664 | 2214 | Distribution Circuit | Vegetation | Tree - fell into line | 277 | 268878 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 19-0010628 | OH | Sus | 0 | 2019 | JAN | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 2 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 43481 | 2302 | 271783 | 1047 | Distribution Circuit | Vegetation | Tree - fell into line | 517 | 294924 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0010224 | OH | Sus | 31422113 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 43481 | 2301 | 273141 | 1215 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 21870 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010731 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | TRIP-SAVER |  | 43471 | 1736 | 255948 | 2696 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 133985 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005454 | OH | Sus | 31420894 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | TRIP-SAVER |  | 43471 | 1808 | 256225 | 1181 | Distribution Circuit | Equipment Failure/Involved | Overhead | 97 | 101519 | Overcast-Heavy Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 19-0005652 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | FELTON-0401 | 83140401 | OCB |  | 43471 | 1917 | 258251 | 1003 | Distribution Circuit | Vegetation | Tree - branch fell on line | 912 | 632115 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005486 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | FELTON-0401 | 83140401 | OCB |  | 43481 | 2308 | 271960 | 2049 | Distribution Circuit | Vegetation | Tree - fell into line | 912 | 639550 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010481 | OH | Sus | 31422113 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 43471 | 1735 | 255942 | 1123 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 23583 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005357 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 43471 | 1830 | 256499 | 2370 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2370 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005932 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 43481 | 1313 | 266969 | 1283 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 29509 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009760 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 43482 | 1139 | 274879 | 3071 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 6142 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011375 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | OTHER |  | 43482 | 1513 | 274401 | 659 | Distribution Circuit | Vegetation | Tree - branch fell on line | 116 | 8044 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011306 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 43481 | 1925 | 272969 | 1414 | Distribution Circuit | Vegetation | Tree - branch fell on line | 184 | 260176 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010673 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 43471 | 1336 | 255338 | 1181 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 35430 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005120 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 43481 | 1408 | 267109 | 1452 | Distribution Circuit | Vegetation | Tree - branch fell on line | 136 | 28333 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009718 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 43471 | 1906 | 256877 | 1223 | Distribution Circuit | Vegetation | Tree - branch fell on line | 136 | 143283 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005378 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 43481 | 1844 | 269526 | 1334 | Distribution Circuit | Equipment Failure/Involved | Overhead | 112 | 143805 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0010150 | OH | Sus | 31422113 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 43481 | 1817 | 273676 | 2738 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 167018 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010922 | OH | Sus | 0 | 2019 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER |  | 43481 | 2104 | 270974 | 1195 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 25015 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010253 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 43481 | 2119 | 271061 | 2783 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 19481 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011278 | OH | Sus | 31422113 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 43471 | 1806 | 257734 | 1202 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3606 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0005408 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 43471 | 1418 | 255311 | 1323 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 33075 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005092 | OH | Sus | 0 | 2019 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 43481 | 1949 | 274220 | 2966 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 118074 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011118 | OH | Sus | 43634211 | 2019 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 43481 | 1830 | 274100 | 3274 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 65580 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011197 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | RECLOSER |  | 43481 | 2025 | 276631 | 4153 | Distribution Circuit | Vegetation | Tree - fell into line | 219 | 909507 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0012097 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 43481 | 1918 | 269709 | 2478 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 11190 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011144 | OH | Sus | 43634211 | 2019 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 43481 | 1945 | 270127 | 1231 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 42967 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010133 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 43471 | 1353 | 255363 | 1262 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 20192 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005150 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 43471 | 1133 | 255153 | 396 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2772 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005074 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 43481 | 1743 | 271848 | 1127 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 7889 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | On Ground | 19-0010389 | OH | Sus | 0 | 2019 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 43471 | 1507 | 255478 | 1258 | Distribution Circuit | Vegetation | Tree - fell into line | 638 | 46169 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005117 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 43482 | 1520 | 274413 | 1367 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2734 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011417 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 43481 | 49 | 266427 | 688 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 67211 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009363 | OH | Sus | 31422113 | 2019 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 43481 | 1822 | 272725 | 3034 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 127428 | Overcast-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0010606 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 43482 | 634 | 274135 | 2101 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12606 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011078 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 43482 | 1520 | 274412 | 1244 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 14928 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011333 | OH | Sus | 43634211 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER |  | 43482 | 557 | 272838 | 2207 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 17656 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010638 | OH | Sus | 0 | 2019 | JAN | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 43481 | 1518 | 272507 | 2684 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 48312 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010576 | OH | Sus | 43634211 | 2019 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | TRANSFORMER |  | 43471 | 2239 | 258320 | 1077 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1077 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005780 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER |  | 43471 | 1839 | 258408 | 1241 | Distribution Circuit | Vegetation | Tree - fell into line | 473 | 200329 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005550 | OH | Sus | 31420594 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 43481 | 1410 | 267804 | 4130 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 167220 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009903 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 43481 | 1809 | 267626 | 3989 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 26518 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011376 | OH | Sus | 43634211 | 2019 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 43481 | 1609 | 267716 | 2762 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 49716 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010978 | OH | Sus | 0 | 2019 | JAN | Yes | Force Out | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | TRIP-SAVER |  | 43481 | 2100 | 275113 | 2476 | Distribution Circuit | Vegetation | Tree - fell into line | 117 | 224036 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010265 | OH | Sus | 43634154 | 2019 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 43471 | 1815 | 256332 | 2071 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 84994 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005414 | OH | Sus | 31420535 | 2019 | JAN | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 43481 | 1950 | 271687 | 1522 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 44138 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010569 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 43471 | 1632 | 255654 | 382 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 6494 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005194 | OH | Sus | 31420581 | 2019 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 43481 | 2045 | 274832 | 3055 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 113035 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0011363 | OH | Sus | 31422106 | 2019 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER |  | 43481 | 1548 | 267619 | 2838 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 263305 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009835 | OH | Sus | 43634152 | 2019 | JAN | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 43481 | 2022 | 270595 | 5229 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 392405 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010191 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER |  | 43471 | 1748 | 256034 | 426 | Distribution Circuit | Equipment Failure/Involved | Overhead | 172 | 40440 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005341 | OH | Sus | 43625028 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 43482 | 614 | 273173 | 850 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 36238 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 19-0010840 | OH | Sus | 43634152 | 2019 | JAN | Yes | Open Circuit | Yes | No
DE ANZA | Tier 2 | LOS GATOS-1106 | 82021106 | FUSE |  | 43481 | 1954 | 270207 | 4091 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 46585 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010970 | OH | Sus | 43634152 | 2019 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE |  | 43481 | 2010 | 270659 | 1369 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 127275 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010340 | OH | Sus | 31422104 | 2019 | JAN | Yes | Force Out | Yes | Yes
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | RECLOSER |  | 43481 | 1705 | 268225 | 2921 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 93472 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009938 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE |  | 43471 | 1111 | 255170 | 1893 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 11358 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005084 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
DIABLO | Tier 2 | CLAYTON-2212 | 12022212 | FUSE |  | 43482 | 240 | 274210 | 1190 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 10970 | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011114 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE |  | 43482 | 1237 | 273989 | 228 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 16188 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011128 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 3 | BERKELEY F-1103 | 12061103 | FUSE |  | 43471 | 1440 | 255424 | 714 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 9282 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005153 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAK SUB | 1260 | OCB |  | 43481 | 1713 | 268446 | 654 | Distribution Circuit | Vegetation | Tree - fell into line | 1012 | 351822 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009986 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | AUBERRY-1102 | 254151102 | FUSE |  | 43471 | 2018 | 257577 | 363 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 21054 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005476 | OH | Sus | 43626773 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 43481 | 1206 | 266852 | 1541 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 46230 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009691 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 43481 | 1211 | 267002 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 32630 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009660 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 43481 | 1400 | 267082 | 1613 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 9678 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009773 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 43471 | 2326 | 258392 | 826 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5782 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005695 | OH | Sus | 31421138 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | TRIP-SAVER |  | 43482 | 125 | 272256 | 2369 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 50222 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 19-0011149 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 43481 | 1234 | 266894 | 1601 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 40025 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009931 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE |  | 43482 | 647 | 273871 | 1922 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 34596 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011198 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER |  | 43481 | 1836 | 269390 | 1181 | Distribution Circuit | Vegetation | Tree - fell into line | 336 | 394688 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0010056 | OH | Sus | 0 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | FUSE |  | 43481 | 1906 | 269618 | 2632 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 42112 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011295 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 43481 | 1139 | 266819 | 1472 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5888 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009593 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HIGHLANDS-1103 | 43361103 | FUSE |  | 43481 | 1859 | 269559 | 2461 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 36915 | Strong Winds-Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0010287 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LUCERNE-1106 | 43351106 | RECLOSER |  | 43481 | 1849 | 269490 | 1703 | Distribution Circuit | Vegetation | Tree - fell into line | 260 | 100636 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0010069 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 43481 | 1431 | 276225 | 4207 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 25242 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011962 | OH | Sus | 0 | 2019 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER |  | 43481 | 1431 | 267175 | 3958 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 141214 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009901 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER |  | 43481 | 1353 | 267068 | 1727 | Distribution Circuit | Vegetation | Tree - fell into line | 908 | 154568 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009782 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | RECLOSER |  | 43482 | 1952 | 274924 | 2899 | Distribution Circuit | Vegetation | Tree - branch fell on line | 455 | 233033 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0011465 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | OTHER |  | 43481 | 1825 | 269163 | 2425 | Distribution Circuit | Vegetation | Tree - fell into line | 151 | 363151 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010079 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 43481 | 1745 | 268768 | 2655 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 124785 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010291 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 43482 | 1726 | 274715 | 1378 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2756 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011320 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 43481 | 1719 | 268442 | 2448 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 31824 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010128 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 43481 | 1706 | 268214 | 2548 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 10192 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010041 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 43481 | 1703 | 268196 | 2429 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 12145 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010336 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 43481 | 1951 | 269761 | 2434 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 36510 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010308 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MENDOCINO-1101 | 42951101 | FUSE |  | 43481 | 2044 | 270797 | 2691 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 39115 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011132 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 43481 | 1727 | 268518 | 1688 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 35448 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010022 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER |  | 43481 | 1816 | 269159 | 4077 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 82839 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010932 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE |  | 43481 | 1803 | 268915 | 2807 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 129612 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010175 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 43481 | 1724 | 268821 | 1291 | Distribution Circuit | Vegetation | Tree - branch fell on line | 83 | 107153 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010170 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 43481 | 1724 | 270366 | 1700 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6582 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010172 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 43481 | 2302 | 272101 | 3734 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 29872 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010431 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER |  | 43481 | 1802 | 268983 | 4161 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 145920 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010021 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 43481 | 1808 | 268951 | 2963 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 57914 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011203 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | TRIP-SAVER |  | 43481 | 1811 | 268999 | 1600 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 82069 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010545 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | RECLOSER |  | 43481 | 1805 | 268942 | 2922 | Distribution Circuit | Vegetation | Tree - fell into line | 127 | 278574 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010012 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 43482 | 508 | 273608 | 1927 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 98277 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010918 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 43481 | 1855 | 269534 | 2645 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 21160 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011360 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 43482 | 1226 | 273945 | 1672 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3344 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0011223 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER |  | 43481 | 1841 | 269539 | 2552 | Distribution Circuit | Vegetation | Tree - fell into line | 159 | 405768 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010078 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | FUSE |  | 43481 | 1802 | 273261 | 2539 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2539 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011499 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | FUSE |  | 43482 | 159 | 272304 | 984 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 15678 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010961 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER |  | 43481 | 1711 | 268396 | 2868 | Distribution Circuit | Vegetation | Tree - fell into line | 850 | 1157121 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009952 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE |  | 43471 | 1140 | 255289 | 235 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 235 | Overcast-Fog-Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 19-0005081 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE |  | 43481 | 1727 | 268538 | 1463 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 7371 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010091 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HUMBOLDT BAY-1102 | 192341102 | FUSE |  | 43481 | 1858 | 269555 | 1073 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 3315 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010238 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER |  | 43482 | 1713 | 274695 | 429 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2706 | 679889 | Partly Cloudy;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 19-0011313 | OH | Sus | 31422124 | 2019 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2113 | 183052113 | RECLOSER |  | 43481 | 2011 | 270405 | 1008 | Distribution Circuit | Equipment Failure/Involved | Overhead | 924 | 414175 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0010176 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | ALTO-1125 | 42031125 | FUSE |  | 43471 | 922 | 255021 | 280 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 33600 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005045 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE |  | 43481 | 1617 | 267772 | 4060 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 48720 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010130 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE |  | 43481 | 1714 | 268460 | 1718 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 86010 | Strong Winds-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009996 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | FUSE |  | 43481 | 1445 | 267248 | 221 | Distribution Circuit | Vegetation | Tree - branch fell on line | 45 | 9945 | Strong Winds-Heavy Rain-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009817 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | GREENBRAE-1103 | 43091103 | OTHER |  | 43471 | 1227 | 255244 | 983 | Distribution Circuit | Vegetation | Tree - fell into line | 406 | 303746 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0005083 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | GREENBRAE-1102 | 43091102 | FUSE |  | 43481 | 2031 | 270515 | 1272 | Distribution Circuit | Vegetation | Tree - branch fell on line | 104 | 132288 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010784 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE |  | 43481 | 2020 | 272420 | 1442 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 37492 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010556 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE |  | 43481 | 1633 | 267952 | 1918 | Distribution Circuit | Equipment Failure/Involved | Overhead | 158 | 228868 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010037 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | JUMPER |  | 43482 | 422 | 273917 | 1868 | Distribution Circuit | Vegetation | Tree - branch fell on line | 546 | 40233 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011021 | OH | Sus | 0 | 2019 | JAN | Yes | Force Out | Yes | Yes
NORTH BAY | Tier 2 | SAN RAFAEL-1109 | 42011109 | FUSE |  | 43481 | 2027 | 270621 | 959 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 26852 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010346 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE |  | 43481 | 1735 | 268629 | 249 | Distribution Circuit | Vegetation | Tree - branch fell on line | 124 | 30876 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009999 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | OTHER |  | 43482 | 135 | 272275 | 1645 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1222 | 60277 | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010496 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | JUMPER |  | 43482 | 2333 | 275084 | 329 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 8883 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011488 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE |  | 43481 | 1540 | 267467 | 440 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 3488 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009821 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | RECLOSER |  | 43481 | 1930 | 269720 | 1098 | Distribution Circuit | Vegetation | Tree - fell into line | 1046 | 571468 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010122 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | WOODACRE-1102 | 43021102 | JUMPER |  | 43481 | 1523 | 267446 | 550 | Distribution Circuit | Equipment Failure/Involved | Overhead | 511 | 54460 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009925 | OH | Sus | 0 | 2019 | JAN | Yes | Force Out | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE |  | 43481 | 1525 | 267552 | 503 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 24144 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009840 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE |  | 43481 | 2046 | 270625 | 1329 | Distribution Circuit | Vegetation | Tree - bark fell into line | 36 | 47844 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010751 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE |  | 43481 | 1418 | 267131 | 1824 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 9120 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009786 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 43481 | 2144 | 271248 | 2315 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 25465 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010417 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | STAFFORD-1102 | 43201102 | FUSE |  | 43481 | 1754 | 269292 | 1636 | Distribution Circuit | Vegetation | Tree - branch fell on line | 72 | 117792 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010046 | OH | Sus | 0 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 43481 | 1954 | 270323 | 1351 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 26179 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010778 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2103 | 43432103 | FUSE |  | 43482 | 651 | 272718 | 1329 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 18606 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011167 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2102 | 43432102 | SWITCH |  | 43482 | 149 | 274009 | 973 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 39893 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011023 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2105 | 43432105 | JUMPER |  | 43482 | 1035 | 273624 | 2950 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 5900 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010906 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE |  | 43482 | 524 | 272547 | 3171 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 19026 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011067 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | MONTICELLO-1101 | 43051101 | RECLOSER |  | 43481 | 1906 | 272351 | 2859 | Distribution Circuit | Equipment Failure/Involved | Overhead | 141 | 403119 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010528 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 43481 | 2017 | 270487 | 2533 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 15198 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010312 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1102 | 42711102 | RECLOSER |  | 43481 | 1542 | 267581 | 644 | Distribution Circuit | Vegetation | Tree - fell into line | 597 | 88673 | Strong Winds-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009830 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1103 | 102911103 | RECLOSER |  | 43482 | 1659 | 274653 | 641 | Distribution Circuit | 3rd Party | Vehicle | 1365 | 711942 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 19-0011300 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER |  | 43481 | 2150 | 271283 | 875 | Distribution Circuit | Vegetation | Tree - fell into line | 1146 | 704347 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010311 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER |  | 43481 | 1902 | 270864 | 1427 | Distribution Circuit | Vegetation | Tree - fell into line | 214 | 93211 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010243 | OH | Sus | 0 | 2019 | JAN | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER |  | 43471 | 1821 | 256415 | 1136 | Distribution Circuit | Vegetation | Tree - fell into line | 457 | 440995 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005266 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | CLARK ROAD-1102 | 103091102 | RECLOSER |  | 43481 | 1818 | 269193 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 403 | 92881 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | On Ground | 19-0010040 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | OTHER |  | 43471 | 2255 | 259151 | 895 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 76075 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005794 | OH | Sus | 0 | 2019 | JAN | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | CLARK ROAD-1102 | 103091102 | FUSE |  | 43481 | 2134 | 271174 | 1122 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 28602 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010867 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | PARADISE-1104 | 102831104 | FUSE |  | 43481 | 2313 | 271838 | 1137 | Distribution Circuit | Equipment Failure/Involved | Overhead | 161 | 126335 | Overcast-Heavy Rain-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 19-0010386 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | OTHER |  | 43471 | 1012 | 255066 | 158 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1086 | 148398 | Overcast-Fog-Heavy Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 19-0005051 | OH | Sus | 43626761 | 2019 | JAN | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE |  | 43471 | 2011 | 257518 | 929 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 107764 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005497 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | BUCKS CREEK-1103 | 102211103 | RECLOSER |  | 43482 | 834 | 273115 | 1796 | Distribution Circuit | Vegetation | Tree - fell into line | 315 | 517838 | Overcast-Fog-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011368 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | GRAYS FLAT-0401 | 102530401 | OTHER |  | 43481 | 1159 | 266846 | 415 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 12134 | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 19-0009948 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER |  | 43471 | 1147 | 255177 | 760 | Distribution Circuit | Vegetation | Tree - fell into line | 1372 | 622480 | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 19-0005061 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | PIT NO 5-1101 | 101321101 | RECLOSER |  | 43471 | 1936 | 257186 | 961 | Distribution Circuit | Environmental/External | Ice or snow | 126 | 93721 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005346 | OH | Sus | 0 | 2019 | JAN | Yes | Force Out | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | OTHER |  | 43471 | 1310 | 255461 | 608 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 31685 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005121 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER |  | 43471 | 1732 | 255924 | 1088 | Distribution Circuit | Vegetation | Tree - branch fell on line | 154 | 19102 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005295 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | JUMPER |  | 43482 | 812 | 276596 | 6241 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 18723 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0012088 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 43482 | 833 | 275982 | 1922 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 5766 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011907 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1102 | 24131102 | TRIP-SAVER |  | 43481 | 1728 | 268656 | 1402 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 37854 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010096 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1102 | 24131102 | OTHER |  | 43481 | 1838 | 272060 | 1807 | Distribution Circuit | Vegetation | Tree - fell into line | 1157 | 603505 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0010421 | OH | Sus | 0 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 43471 | 1727 | 255922 | 1574 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 80274 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005246 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER |  | 43481 | 2302 | 271784 | 938 | Distribution Circuit | Vegetation | Tree - fell into line | 310 | 96394 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 19-0010563 | OH | Sus | 31422194 | 2019 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 43471 | 1934 | 257428 | 1219 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 70600 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005477 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER |  | 43482 | 40 | 272190 | 890 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 22998 | Overcast-Fog;32-90 F | Conductor- Overhead | On Ground | 19-0010501 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 43481 | 1542 | 268252 | 1458 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 29160 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010086 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 43481 | 2343 | 272010 | 1503 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 21042 | Overcast-Fog-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011180 | OH | Sus | 31422194 | 2019 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | TRIP-SAVER |  | 43481 | 2105 | 270948 | 1172 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 49224 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010441 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | SAN CARLOS-1103 | 24181103 | FUSE |  | 43482 | 1744 | 274742 | 1373 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6865 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011332 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | NARROWS-2101 | 153132101 | FUSE |  | 43482 | 146 | 272280 | 714 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 8568 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011107 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SAN JOSE | Tier 3 | MORGAN HILL-2111 | 83242111 | FUSE |  | 43471 | 1954 | 257386 | 1536 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 18432 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005517 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43481 | 2325 | 274204 | 2463 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 78816 | Overcast-Fog-Snow-Strong Winds;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0011110 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | JUMPER |  | 43481 | 2325 | 273614 | 1300 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 11700 | Overcast-Fog-Heavy Rain-Lightning;32-90 F | Pole-Wood | Broken- wire on ground | 19-0010901 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43481 | 2329 | 273570 | 2456 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 50671 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010884 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | FUSE |  | 43481 | 2332 | 271920 | 2386 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 11930 | Overcast-Fog-Heavy Rain-Lightning-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011802 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43481 | 2329 | 273883 | 2504 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 12520 | Overcast-Fog-Heavy Rain-Lightning;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0010995 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43481 | 2329 | 273898 | 2381 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4762 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0010999 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43482 | 8 | 272652 | 2431 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 13340 | Overcast-Fog-Heavy Rain-Lightning;32-90 F | Pole-Wood | Broken- wire on ground | 19-0011242 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | TRIP-SAVER |  | 43482 | 1100 | 273887 | 1679 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 71964 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010996 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43481 | 2315 | 271824 | 2238 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 40284 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010711 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER |  | 43481 | 2325 | 271904 | 2462 | Distribution Circuit | Vegetation | Tree - fell into line | 1172 | 754567 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0010402 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE |  | 43482 | 432 | 272492 | 793 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 25376 | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 19-0010870 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43481 | 2345 | 272796 | 2477 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 86695 | Partly Cloudy-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 19-0011168 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43471 | 1854 | 256757 | 1013 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 8448 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005388 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43481 | 2338 | 272817 | 1357 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 16284 | Partly Cloudy-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010989 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43481 | 2336 | 271987 | 2391 | Distribution Circuit | Vegetation | Tree - fell into line | 173 | 165864 | Overcast-Fog-Heavy Rain-Lightning-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0010542 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1110 | 153081110 | JUMPER |  | 43471 | 2019 | 257563 | 1028 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6168 | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005457 | OH | Sus | 0 | 2019 | JAN | Yes | None | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER |  | 43481 | 2346 | 272052 | 3719 | Distribution Circuit | Vegetation | Tree - fell into line | 1155 | 196676 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010424 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 43482 | 1335 | 275935 | 2880 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 11520 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0011849 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 43481 | 2334 | 272263 | 979 | Distribution Circuit | Vegetation | Tree - fell into line | 117 | 37439 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010493 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | OTHER |  | 43481 | 2333 | 272041 | 2762 | Distribution Circuit | Vegetation | Tree - fell into line | 450 | 291918 | Overcast-Fog-Heavy Rain-Lightning-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0010662 | OH | Sus | 0 | 2019 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 43481 | 1747 | 268772 | 1579 | Distribution Circuit | Vegetation | Tree - fell into line | 1026 | 265796 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009985 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 43482 | 622 | 272650 | 1908 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9540 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011302 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | FUSE |  | 43482 | 50 | 272208 | 863 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 14671 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010881 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43482 | 950 | 273445 | 1504 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 16544 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010912 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BELL-1107 | 152701107 | FUSE |  | 43482 | 1124 | 273831 | 494 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 2214 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010979 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BELL-1108 | 152701108 | FUSE |  | 43471 | 1408 | 255378 | 467 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 18213 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005098 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE |  | 43482 | 205 | 272316 | 764 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 40478 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010875 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | FORESTHILL-1102 | 152181102 | RECLOSER |  | 43481 | 1956 | 270326 | 938 | Distribution Circuit | Equipment Failure/Involved | Overhead | 423 | 100008 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010162 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 43481 | 2324 | 271875 | 2301 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 62127 | Partly Cloudy-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011166 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | FUSE |  | 43482 | 651 | 272716 | 459 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2295 | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010857 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1109 | 152691109 | FUSE |  | 43481 | 2350 | 272043 | 1327 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 14764 | Partly Cloudy-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010946 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | RECLOSER |  | 43471 | 2033 | 257875 | 1091 | Distribution Circuit | Vegetation | Tree - fell into line | 408 | 107385 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005518 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1110 | 152691110 | OTHER |  | 43481 | 1922 | 269727 | 935 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 18813 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010314 | OH | Sus | 43635519 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | HIGGINS-1109 | 152691109 | TRIP-SAVER |  | 43481 | 2159 | 271401 | 2489 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 151810 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0011009 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | FUSE |  | 43481 | 2229 | 271618 | 1118 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 80496 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010488 | OH | Sus | 31422233 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | FUSE |  | 43481 | 2003 | 270324 | 1286 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 10288 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0010268 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | FUSE |  | 43482 | 350 | 273552 | 1875 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3750 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011388 | OH | Sus | 43635519 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE |  | 43482 | 2 | 272663 | 2247 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 31458 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011243 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | RECLOSER |  | 43481 | 849 | 266596 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 886 | 65200 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0009451 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 43471 | 2105 | 258055 | 1051 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 21233 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005481 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2102 | 153132102 | RECLOSER |  | 43481 | 823 | 266550 | 689 | Distribution Circuit | Vegetation | Tree - fell into line | 1173 | 78141 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0009441 | OH | Sus | 31422068 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 43481 | 2134 | 271170 | 821 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 80458 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010352 | OH | Sus | 31422233 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER |  | 43471 | 1811 | 256324 | 987 | Distribution Circuit | Equipment Failure/Involved | Overhead | 207 | 19399 | Snow-Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005255 | OH | Sus | 43626490 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE |  | 43471 | 2014 | 257526 | 963 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5778 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005419 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 43481 | 2259 | 271766 | 1371 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2742 | Lightning-Fog-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0010448 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 43482 | 747 | 272918 | 1718 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3436 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011808 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | RECLOSER |  | 43481 | 2132 | 271190 | 1388 | Distribution Circuit | Vegetation | Tree - fell into line | 256 | 337277 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010290 | OH | Sus | 43635519 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE |  | 43482 | 804 | 276146 | 2005 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 6015 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011945 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PIKE CITY-1102 | 152201102 | FUSE |  | 43471 | 1801 | 256154 | 2934 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 79218 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005852 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 43482 | 2022 | 275008 | 1004 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2008 | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 19-0011442 | OH | Sus | 0 | 2019 | JAN | Yes | Force Out | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 43481 | 1434 | 267187 | 1531 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 13431 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009930 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE |  | 43481 | 1757 | 268867 | 2634 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 52680 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010085 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | OTHER |  | 43482 | 1052 | 274703 | 1455 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5820 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011322 | OH | Sus | 0 | 2019 | JAN | Yes | Open Circuit | Yes | Yes
SONOMA | Tier 2 | COTATI-1103 | 42271103 | OTHER |  | 43481 | 1904 | 271160 | 1200 | Distribution Circuit | Vegetation | Tree - fell into line | 227 | 260078 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010286 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | SALMON CREEK-1101 | 43161101 | FUSE |  | 43482 | 2320 | 275085 | 1177 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3531 | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011487 | OH | Sus | 0 | 2019 | JAN | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | OTHER |  | 43482 | 702 | 274066 | 678 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 24066 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011085 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 43481 | 1830 | 272660 | 1125 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 45000 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010594 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | FUSE |  | 43481 | 1522 | 267478 | 1588 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 52404 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010090 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1101 | 42571101 | FUSE |  | 43481 | 1812 | 269199 | 1149 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 90771 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010428 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | TRIP-SAVER |  | 43481 | 1825 | 269411 | 2684 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 53036 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010518 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 43481 | 1453 | 267275 | 265 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 7420 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009804 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 43481 | 1829 | 272008 | 2346 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 23028 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010411 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 43481 | 1609 | 267714 | 226 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 11978 | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 19-0009960 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 43481 | 1626 | 272510 | 1658 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 46424 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010577 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE |  | 43481 | 1958 | 270264 | 2894 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 43410 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011309 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | MIRABEL-1101 | 42091101 | FUSE |  | 43481 | 2045 | 270806 | 2765 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 22120 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011618 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER |  | 43482 | 802 | 272971 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 28800 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010966 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 43482 | 823 | 273062 | 1680 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 8400 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010876 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | OTHER |  | 43481 | 1519 | 267795 | 3913 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 114879 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009869 | OH | Sus | 0 | 2019 | JAN | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 43481 | 1741 | 270792 | 2570 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 51400 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011220 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 43481 | 2025 | 270607 | 2543 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 61032 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010452 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | OTHER |  | 43481 | 1721 | 270517 | 1511 | Distribution Circuit | Vegetation | Tree - branch fell on line | 505 | 471427 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010284 | OH | Sus | 0 | 2019 | JAN | Yes | Open Circuit | Yes | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER |  | 43481 | 2010 | 270390 | 1052 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 114668 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010992 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | TRIP-SAVER |  | 43481 | 1040 | 266734 | 343 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 18548 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009575 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE |  | 43481 | 2243 | 271679 | 2612 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 96644 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0011036 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 43481 | 2112 | 270941 | 2438 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 19504 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011193 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 43481 | 1441 | 267208 | 324 | Distribution Circuit | Vegetation | Tree - branch fell on line | 98 | 31752 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009770 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 43481 | 1207 | 266854 | 264 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 7128 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009626 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE |  | 43482 | 806 | 272990 | 1923 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1923 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011668 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 43481 | 2123 | 273321 | 1356 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 33900 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011011 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE |  | 43482 | 1629 | 274567 | 2630 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 26300 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011667 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | TRIP-SAVER |  | 43482 | 459 | 272558 | 1962 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 154998 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011665 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 43471 | 1142 | 255169 | 378 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4158 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005082 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | FULTON-1107 | 42561107 | FUSE |  | 43481 | 1829 | 269281 | 2483 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 27313 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 19-0011389 | OH | Sus | 0 | 2019 | JAN | Yes | Force Out | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 43481 | 1748 | 267899 | 2502 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 20397 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009997 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | OTHER |  | 43481 | 1832 | 272312 | 1361 | Distribution Circuit | Vegetation | Tree - branch fell on line | 138 | 166097 | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0010519 | OH | Sus | 0 | 2019 | JAN | Yes | Open Circuit | Yes | Yes
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | TRIP-SAVER |  | 43481 | 1450 | 267251 | 256 | Distribution Circuit | Vegetation | Tree - branch fell on line | 134 | 15145 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009868 | OH | Sus | 0 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 43471 | 2009 | 257482 | 1021 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 9189 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005503 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 43481 | 1900 | 269566 | 2454 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 9816 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010313 | OH | Sus | 0 | 2019 | JAN | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 43481 | 2055 | 270874 | 1081 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 99452 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010566 | OH | Sus | 0 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 2 | GEYSERVILLE-1102 | 42891102 | FUSE |  | 43471 | 1230 | 255247 | 155 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 4340 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005073 | OH | Sus | 0 | 2019 | JAN | Yes | Multi-Fault | Yes | No
SONOMA | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE |  | 43481 | 1455 | 267287 | 2980 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 51425 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0009962 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1702 | 163451702 | OTHER |  | 43482 | 58 | 272179 | 1070 | Distribution Circuit | Vegetation | Tree - fell into line | 239 | 38430 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010560 | OH | Sus | 0 | 2019 | JAN | Yes | Force Out | Yes | Yes
STOCKTON | Tier 2 | CORRAL-1102 | 162991102 | FUSE |  | 43482 | 545 | 272568 | 415 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 830 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010586 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CORRAL-1103 | 162991103 | FUSE |  | 43481 | 1700 | 268230 | 200 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 4740 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010026 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE |  | 43471 | 1741 | 255991 | 1216 | Distribution Circuit | Vegetation | Tree - fell into line | 239 | 145852 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005220 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | TRIP-SAVER |  | 43482 | 1710 | 274685 | 1042 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 80234 | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0011361 | OH | Sus | 0 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | CORRAL-1101 | 162991101 | FUSE |  | 43481 | 1617 | 267328 | 651 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 10080 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 19-0009917 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 43471 | 1603 | 255579 | 535 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 5568 | Overcast-Fog-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0005159 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER |  | 43482 | 13 | 272173 | 758 | Distribution Circuit | Vegetation | Tree - fell into line | 418 | 117666 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010460 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | FUSE |  | 43471 | 1659 | 257996 | 887 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 12418 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005424 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | TRIP-SAVER |  | 43482 | 729 | 272834 | 1930 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 42636 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010959 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 43471 | 1728 | 255894 | 430 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 28380 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005297 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | TRIP-SAVER |  | 43482 | 15 | 272322 | 1518 | Distribution Circuit | 3rd Party | Vehicle | 111 | 168498 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0010514 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE |  | 43482 | 200 | 272307 | 1418 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 54478 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010782 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CLAY-1103 | 163341103 | RECLOSER |  | 43471 | 1751 | 256076 | 1609 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 110371 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005229 | OH | Sus | 0 | 2019 | JAN | Yes | Multi-Fault | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | RECLOSER |  | 43481 | 2230 | 271610 | 1021 | Distribution Circuit | Vegetation | Tree - fell into line | 711 | 625611 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010339 | OH | Sus | 0 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | RECLOSER |  | 43471 | 1813 | 256272 | 615 | Distribution Circuit | Vegetation | Tree - fell into line | 372 | 141559 | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005261 | OH | Sus | 0 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE |  | 43481 | 2333 | 271922 | 2293 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 23704 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010826 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 43482 | 1205 | 273879 | 1781 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 16029 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0010994 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CLAY-1101 | 163341101 | FUSE |  | 43471 | 1909 | 256855 | 1511 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3528 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005591 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | MARTELL-1101 | 163011101 | FUSE |  | 43481 | 2323 | 271866 | 1190 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 16660 | Overcast-Fog-Heavy Rain-Lightning-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010669 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 43482 | 0 | 272074 | 493 | Distribution Circuit | Vegetation | Tree - branch fell on line | 62 | 30566 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010499 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | TRIP-SAVER |  | 43481 | 2355 | 272062 | 835 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 67965 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010743 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | Yes
STOCKTON | Tier 2 | MARTELL-1101 | 163011101 | FUSE |  | 43481 | 2327 | 271901 | 2048 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 16384 | Overcast-Fog-Heavy Rain-Lightning-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011256 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 43481 | 2345 | 272021 | 1137 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 23877 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0010502 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | MERCED FALLS-1102 | 252811102 | FUSE |  | 43471 | 1855 | 256767 | 891 | Distribution Circuit | Equipment Failure/Involved | Overhead | 544 | 43545 | Overcast-Fog-Heavy Rain;32-90 F | Insulator | Broken- wire on ground | 19-0005406 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE |  | 43482 | 1409 | 275202 | 1809 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 8898 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0011525 | OH | Sus | 0 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER |  | 43482 | 26 | 272170 | 885 | Distribution Circuit | Vegetation | Tree - fell into line | 2643 | 1033194 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010458 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | FUSE |  | 43482 | 619 | 275675 | 2072 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12432 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0011723 | OH | Sus | 0 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | OTHER |  | 43482 | 1309 | 274086 | 1201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1269 | 82537 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011065 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | Yes
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE |  | 43482 | 635 | 272681 | 1727 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 13816 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010833 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE |  | 43471 | 1838 | 256566 | 1322 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 7682 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005556 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 43482 | 212 | 272325 | 932 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 20504 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0010572 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 43471 | 1737 | 255964 | 1337 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 29414 | Overcast-Fog-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0005274 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | JUMPER |  | 43482 | 715 | 272786 | 2065 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 2515 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011654 | OH | Sus | 0 | 2019 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER |  | 43481 | 1936 | 269994 | 1396 | Distribution Circuit | Vegetation | Tree - fell into line | 280 | 122341 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0010113 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | FUSE |  | 43482 | 2 | 272081 | 2163 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 21945 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0010831 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | OCB |  | 43482 | 13 | 272123 | 1254 | Distribution Circuit | Vegetation | Tree - fell into line | 2841 | 1041827 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0010443 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 43482 | 1209 | 273894 | 386 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 71796 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0011074 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 43481 | 2335 | 273854 | 1292 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 19380 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on object | 19-0010983 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 43471 | 1739 | 255977 | 1446 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 40226 | Overcast-Fog-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0005331 | OH | Sus | 0 | 2019 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 43481 | 2137 | 271839 | 1320 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 141240 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on object | 19-0010410 | OH | Sus | 0 | 2019 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE |  | 43626 | 436 | 403105 | 708 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 8889 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0065104 | OH | Sus | 0 | 2019 | JUN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2107 | 83252107 | OTHER |  | 43624 | 1043 | 401447 | 29267 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 65606 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0064604 | OH | Sus | 0 | 2019 | JUN | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 43624 | 519 | 401182 | 941 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 21392 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0064523 | OH | Sus | 43832032 | 2019 | JUN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | SAN LEANDRO-1109 | 13111109 | FUSE |  | 43624 | 2045 | 401833 | 1094 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 20786 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0064773 | OH | Sus | 31452134 | 2019 | JUN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 43626 | 1120 | 403592 | 200 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 9400 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0065314 | OH | Sus | 43837205 | 2019 | JUN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 43626 | 1912 | 404560 | 1503 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3006 | Partly Cloudy-Heat Wave;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0065525 | OH | Sus | 0 | 2019 | JUN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE |  | 43624 | 308 | 401169 | 736 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 62560 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0064515 | OH | Sus | 31451974 | 2019 | JUN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 43626 | 1854 | 404516 | 1013 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 16 | 16208 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0065574 | OH | Sus | 43837871 | 2019 | JUN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43626 | 1627 | 404148 | 768 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 14169 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0065481 | OH | Sus | 31452985 | 2019 | JUN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 43624 | 1017 | 401355 | 241 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 21690 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0064576 | OH | Sus | 0 | 2019 | JUN | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | TRIP-SAVER |  | 43624 | 1848 | 401789 | 1065 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 44664 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0064689 | OH | Sus | 0 | 2019 | JUN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | RIO DEL MAR-0401 | 83260401 | RECLOSER |  | 43795 | 1957 | 718231 | 538 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1047 | 143343 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129530 | OH | Sus | 44107269 | 2019 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2102 | 83252102 | FUSE |  | 43795 | 1936 | 719209 | 1116 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 46138 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129725 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2107 | 83252107 | JUMPER |  | 43795 | 2007 | 722205 | 4063 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 74785 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0130658 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | SWITCH |  | 43796 | 222 | 719777 | 2348 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 44612 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129870 | OH | Sus | 0 | 2019 | NOV | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 43795 | 2022 | 718447 | 2410 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 74710 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129827 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 43795 | 1913 | 717781 | 1433 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 149659 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0129462 | OH | Sus | 31479279 | 2019 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 43795 | 2014 | 718349 | 1365 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 79170 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129864 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 43795 | 1957 | 719898 | 2764 | Distribution Circuit | Vegetation | Tree - branch fell on line | 104 | 75680 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129893 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | JUMPER |  | 43789 | 117 | 710634 | 1478 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 20176 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0126615 | OH | Sus | 44102958 | 2019 | NOV | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER |  | 43796 | 826 | 720604 | 2030 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 6090 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130943 | OH | Sus | 44107269 | 2019 | NOV | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | SAND CREEK-1103 | 254601103 | RECLOSER |  | 43796 | 2230 | 722651 | 1778 | Distribution Circuit | Vegetation | Tree - fell into line | 360 | 283675 | Overcast;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0130733 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | OCB |  | 43796 | 855 | 721312 | 1845 | Distribution Circuit | Vegetation | Tree - fell into line | 706 | 202469 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0130243 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 43795 | 2020 | 718423 | 4218 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 43144 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129779 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 43795 | 1645 | 717904 | 1341 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 12069 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129481 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | FUSE |  | 43795 | 1539 | 716683 | 1517 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 31857 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129334 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER |  | 43795 | 1603 | 716269 | 1505 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 133550 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129209 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | OTHER |  | 43795 | 1553 | 716142 | 333 | Distribution Circuit | Vegetation | Tree - branch fell on line | 426 | 141378 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129217 | OH | Sus | 0 | 2019 | NOV | Yes | Open Circuit | Yes | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER |  | 43795 | 1558 | 716184 | 1423 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 89306 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129220 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 43795 | 1601 | 716166 | 1302 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 31248 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129727 | OH | Sus | 0 | 2019 | NOV | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 43795 | 1601 | 716168 | 1565 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 27358 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129754 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER |  | 43795 | 1549 | 716125 | 1036 | Distribution Circuit | Vegetation | Tree - branch fell on line | 372 | 140939 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129212 | OH | Sus | 0 | 2019 | NOV | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | OTHER |  | 43795 | 1536 | 716066 | 290 | Distribution Circuit | Vegetation | Tree - branch fell on line | 495 | 82500 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129264 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 43795 | 1541 | 716084 | 2789 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 19164 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0129218 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 43795 | 1557 | 716154 | 1648 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4944 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130555 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 43795 | 1538 | 719022 | 1408 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 53504 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129674 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 43795 | 1538 | 721718 | 2762 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5524 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130397 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 43795 | 1538 | 721712 | 1583 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 23745 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130395 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 43795 | 1538 | 719005 | 1408 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 130944 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129663 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 43795 | 1538 | 721833 | 1499 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 29980 | Partly Cloudy-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130479 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 43795 | 1538 | 718993 | 1582 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 17402 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129650 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | TRIP-SAVER |  | 43795 | 1538 | 718999 | 1478 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 134498 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129659 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 43796 | 1544 | 721988 | 1147 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 11470 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130802 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | JUMPER |  | 43796 | 1533 | 721974 | 1156 | Distribution Circuit | Vegetation | Tree - fell into line | 195 | 208236 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130578 | OH | Sus | 0 | 2019 | NOV | Yes | Force Out | Yes | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER |  | 43795 | 1810 | 719660 | 1264 | Distribution Circuit | Vegetation | Tree - fell into line | 230 | 232218 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129836 | OH | Sus | 0 | 2019 | NOV | Yes | Open Circuit | Yes | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER |  | 43795 | 1759 | 716877 | 4259 | Distribution Circuit | Vegetation | Tree - fell into line | 371 | 670970 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0129365 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER |  | 43795 | 1803 | 717121 | 4121 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 97342 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129375 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | FUSE |  | 43795 | 1417 | 715802 | 2823 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 8545 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129424 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | FUSE |  | 43795 | 2255 | 719352 | 2306 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 29978 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130275 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | FUSE |  | 43796 | 849 | 720680 | 3266 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3266 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130401 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE |  | 43789 | 130 | 710642 | 536 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 8576 | Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0126622 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1103 | 192381103 | FUSE |  | 43795 | 1738 | 717591 | 2875 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 17250 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130033 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HARRIS-1109 | 192431109 | FUSE |  | 43795 | 1252 | 715996 | 3142 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 81692 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129138 | OH | Sus | 0 | 2019 | NOV | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | FUSE |  | 43795 | 1332 | 717453 | 5664 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 22656 | Overcast-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129407 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | FUSE |  | 43795 | 1415 | 723105 | 4212 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 63180 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130908 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1121 | 192021121 | FUSE |  | 43795 | 1240 | 715324 | 4533 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 299178 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129521 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 43795 | 1344 | 722848 | 4581 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 270279 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | On Ground | 19-0130846 | OH | Sus | 0 | 2019 | NOV | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE |  | 43795 | 1807 | 717216 | 1108 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 109016 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129625 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | OTHER |  | 43795 | 1802 | 716982 | 301 | Distribution Circuit | Equipment Failure/Involved | Overhead | 391 | 33779 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129529 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | SILVERADO-2102 | 43432102 | FUSE |  | 43796 | 702 | 720360 | 1103 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3309 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129988 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 43796 | 1918 | 722256 | 1183 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 19014 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130879 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | BANGOR-1101 | 103191101 | JUMPER |  | 43796 | 1604 | 721990 | 76 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 76 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130575 | OH | Sus | 0 | 2019 | NOV | Yes | Force Out | Yes | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 43796 | 1415 | 721945 | 182 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 546 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129558 | OH | Sus | 0 | 2019 | NOV | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER |  | 43795 | 2009 | 717866 | 1080 | Distribution Circuit | Equipment Failure/Involved | Overhead | 459 | 460755 | Overcast-Fog-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0129558 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER |  | 43795 | 1928 | 717979 | 976 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 49776 | Overcast-Fog-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0129551 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | RECLOSER |  | 43795 | 1916 | 717841 | 1270 | Distribution Circuit | Vegetation | Tree - fell into line | 625 | 676969 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0129482 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | BIG BEND-1102 | 103751102 | JUMPER |  | 43795 | 1926 | 720924 | 1195 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 54185 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130119 | OH | Sus | 0 | 2019 | NOV | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | BIG BEND-1102 | 103751102 | OTHER |  | 43795 | 2219 | 720482 | 1143 | Distribution Circuit | Vegetation | Tree - fell into line | 301 | 207583 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130373 | OH | Sus | 0 | 2019 | NOV | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 3 | BIG BEND-1101 | 103751101 | FUSE |  | 43796 | 47 | 719578 | 1012 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 25300 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130351 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE |  | 43795 | 1838 | 719177 | 1133 | Distribution Circuit | Vegetation | Tree - branch fell on line | 163 | 184679 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130186 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1101 | 103401101 | FUSE |  | 43796 | 1328 | 721668 | 3041 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 91230 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130618 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1101 | 103401101 | FUSE |  | 43796 | 1115 | 721529 | 4650 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 204600 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130302 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1101 | 103401101 | RECLOSER |  | 43795 | 1642 | 716498 | 5562 | Distribution Circuit | Vegetation | Tree - fell into line | 403 | 914868 | Overcast-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0129258 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KESWICK-1101 | 103451101 | FUSE |  | 43795 | 2201 | 721773 | 2165 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 10825 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130444 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KESWICK-1101 | 103451101 | FUSE |  | 43795 | 1833 | 722717 | 4479 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 103017 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130796 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | KESWICK-1101 | 103451101 | RECLOSER |  | 43795 | 2134 | 717369 | 2526 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2526 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129667 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE |  | 43796 | 1536 | 721871 | 1186 | Distribution Circuit | Environmental/External | Ice or snow | 7 | 8302 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130770 | OH | Sus | 0 | 2019 | NOV | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | RECLOSER |  | 43795 | 2056 | 718140 | 728 | Distribution Circuit | Equipment Failure/Involved | Overhead | 479 | 347860 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129601 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE |  | 43795 | 1844 | 720638 | 1111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 64438 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130020 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1102 | 103381102 | RECLOSER |  | 43795 | 2250 | 719540 | 3720 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 93000 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129802 | OH | Sus | 0 | 2019 | NOV | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | JUMPER |  | 43796 | 1851 | 722209 | 1236 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 95804 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130694 | OH | Sus | 0 | 2019 | NOV | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | FUSE |  | 43795 | 1848 | 722789 | 2682 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 80460 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 19-0130814 | OH | Sus | 0 | 2019 | NOV | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | FUSE |  | 43795 | 1848 | 718177 | 2512 | Distribution Circuit | Vegetation | Tree - branch fell on line | 114 | 286368 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129523 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1101 | 103381101 | TRIP-SAVER |  | 43795 | 1644 | 716479 | 2749 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 111150 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0130829 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | JUMPER |  | 43795 | 2033 | 721994 | 3829 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3829 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130583 | OH | Sus | 0 | 2019 | NOV | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | JUMPER |  | 43795 | 2033 | 721989 | 3705 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 3705 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130573 | OH | Sus | 0 | 2019 | NOV | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | OTHER |  | 43795 | 1717 | 722085 | 4230 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 143820 | Overcast-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0130619 | OH | Sus | 0 | 2019 | NOV | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | FUSE |  | 43795 | 1734 | 722089 | 5986 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 191358 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130621 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1101 | 103381101 | FUSE |  | 43795 | 1644 | 723064 | 4066 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 121980 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0130898 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | FUSE |  | 43795 | 1915 | 722874 | 5245 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 23003 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130853 | OH | Sus | 0 | 2019 | NOV | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | FUSE |  | 43795 | 1915 | 722877 | 4026 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 52338 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130854 | OH | Sus | 0 | 2019 | NOV | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | FUSE |  | 43795 | 1726 | 722872 | 5449 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 553614 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130851 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ANTLER-1101 | 103271101 | JUMPER |  | 43795 | 1915 | 722886 | 4311 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 21555 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0130859 | OH | Sus | 0 | 2019 | NOV | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | ANTLER-1101 | 103271101 | FUSE |  | 43795 | 1915 | 722881 | 4171 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 291970 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0130855 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | FUSE |  | 43795 | 1718 | 722806 | 4357 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 121996 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0130820 | OH | Sus | 0 | 2019 | NOV | Yes | Force Out | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 43795 | 2006 | 718287 | 4136 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 16680 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130047 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 43795 | 2338 | 720387 | 1441 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 62565 | Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130215 | OH | Sus | 31479229 | 2019 | NOV | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER |  | 43795 | 1920 | 720647 | 1526 | Distribution Circuit | Equipment Failure/Involved | Overhead | 122 | 152142 | Heavy Rain-Strong Winds-Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130068 | OH | Sus | 0 | 2019 | NOV | Yes | Open Circuit | Yes | No
SACRAMENTO | Tier 2 | DOBBINS-1101 | 153741101 | FUSE |  | 43795 | 2105 | 717715 | 2595 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 15021 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129792 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | OTHER |  | 43795 | 1824 | 718582 | 1353 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 40807 | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0129594 | OH | Sus | 0 | 2019 | NOV | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43796 | 2355 | 722494 | 1276 | Distribution Circuit | Vegetation | Tree - fell into line | 521 | 602844 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0130790 | OH | Sus | 0 | 2019 | NOV | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | TRIP-SAVER |  | 43796 | 405 | 719839 | 687 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 84135 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130005 | OH | Sus | 0 | 2019 | NOV | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE |  | 43795 | 2056 | 718884 | 1108 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6648 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129760 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 43795 | 1940 | 718035 | 1141 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5705 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0130174 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | FUSE |  | 43795 | 1842 | 717470 | 2509 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 35126 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0130261 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | OTHER |  | 43795 | 2247 | 718547 | 2159 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 135 | 268779 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 19-0130032 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER |  | 43796 | 654 | 720344 | 642 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 51186 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129944 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE |  | 43795 | 1516 | 716004 | 1135 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 23835 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0129445 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE |  | 43796 | 1103 | 721010 | 344 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1032 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130309 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 43795 | 1741 | 717830 | 955 | Distribution Circuit | 3rd Party | Other | 2 | 1910 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129553 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | TRIP-SAVER |  | 43795 | 2059 | 718816 | 1411 | Distribution Circuit | Vegetation | Tree - branch fell on line | 78 | 110058 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0129752 | OH | Sus | 0 | 2019 | NOV | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 43795 | 2105 | 719133 | 1232 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 55440 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0129980 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | RECLOSER |  | 43795 | 2106 | 718950 | 932 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 122092 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129649 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE |  | 43789 | 1400 | 711702 | 488 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 4880 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0126948 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 43796 | 357 | 716724 | 481 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 12025 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129912 | OH | Sus | 0 | 2019 | NOV | Yes | Multi-Fault | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 43795 | 2152 | 720605 | 758 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2274 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130010 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CORRAL-1102 | 162991102 | OTHER |  | 43795 | 833 | 715107 | 343 | Distribution Circuit | Equipment Failure/Involved | Overhead | 123 | 41683 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0128739 | OH | Sus | 44107399 | 2019 | NOV | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | OCB |  | 43795 | 1833 | 717361 | 992 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3488 | 379798 | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0129490 | OH | Sus | 0 | 2019 | NOV | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | STANISLAUS-1702 | 162821702 | FUSE |  | 43796 | 650 | 720327 | 570 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 12540 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0130126 | OH | Sus | 0 | 2019 | NOV | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1701 | 162821701 | FUSE |  | 43796 | 645 | 721345 | 1971 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 19710 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0129967 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER |  | 43796 | 2350 | 722430 | 1038 | Distribution Circuit | Vegetation | Tree - fell into line | 541 | 487534 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 19-0130739 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | OCB |  | 43796 | 303 | 719762 | 2250 | Distribution Circuit | Vegetation | Tree - fell into line | 1782 | 1137844 | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0129863 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 43796 | 428 | 719875 | 3494 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 129278 | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0130633 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 43796 | 822 | 720600 | 1759 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7036 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130613 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 43796 | 525 | 720073 | 3667 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 168719 | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0130950 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 43796 | 1621 | 722510 | 2733 | Distribution Circuit | Vegetation | Tree - fell into line | 2532 | 356331 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130751 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER |  | 43796 | 1643 | 723236 | 2607 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 2607 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130864 | OH | Sus | 0 | 2019 | NOV | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 43796 | 1643 | 722900 | 1676 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 186659 | Partly Cloudy;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0130864 | OH | Sus | 0 | 2019 | NOV | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 43796 | 657 | 720348 | 173 | Distribution Circuit | Vegetation | Tree - fell into line | 153 | 25845 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129963 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER |  | 43796 | 712 | 720941 | 708 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 708 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129963 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 43796 | 414 | 720133 | 931 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 51205 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130339 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | OTHER |  | 43795 | 1857 | 718156 | 1058 | Distribution Circuit | Vegetation | Tree - branch fell on line | 150 | 13611 | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0129549 | OH | Sus | 0 | 2019 | NOV | Yes | Open Circuit | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2104 | 254432104 | FUSE |  | 43796 | 1952 | 722413 | 785 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 5345 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 19-0130725 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | RECLOSER |  | 43796 | 947 | 720969 | 399 | Distribution Circuit | Equipment Failure/Involved | Overhead | 398 | 158802 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0130133 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | TRANSFORMER |  | 43796 | 829 | 721762 | 605 | Distribution Circuit | Vegetation | Tree - bark fell into line | 1 | 605 | Snow-Overcast-Fog;32-90 F | Transformer | Broken- wire on ground | 19-0130432 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | OTHER |  | 43796 | 207 | 720359 | 927 | Distribution Circuit | Vegetation | Tree - fell into line | 515 | 94402 | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 19-0129973 | OH | Sus | 0 | 2019 | NOV | Yes | Open Circuit | Yes | Yes
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 43796 | 859 | 720816 | 684 | Distribution Circuit | Vegetation | Tree - bark fell into line | 3 | 2052 | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 19-0130160 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | RECLOSER |  | 43795 | 1859 | 717705 | 1432 | Distribution Circuit | Vegetation | Tree - fell into line | 744 | 203131 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0129455 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 43796 | 1947 | 722278 | 1222 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 36660 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 19-0130695 | OH | Sus | 0 | 2019 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 43764 | 2137 | 691726 | 4048 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 8 | 32384 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116048 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 43764 | 2042 | 690739 | 2853 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 27 | 77031 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116013 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 43764 | 2052 | 690183 | 3720 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 3 | 11160 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116189 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 43764 | 2042 | 688139 | 3800 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 66 | 250800 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116013 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 43764 | 2137 | 693656 | 4253 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 4253 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116048 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 43764 | 2137 | 692589 | 5480 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 6 | 32880 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116048 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | RECLOSER |  | 43764 | 2039 | 685630 | 2735 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 369 | 1009215 | Partly Cloudy;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0115935 | OH | Sus | 44082351 | 2019 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 43764 | 2042 | 692818 | 4436 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 8872 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0118288 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 43747 | 2246 | 653297 | 1231 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 13 | 16003 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0109132 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 43764 | 2043 | 691505 | 4115 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 17 | 69955 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0115935 | OH | Sus | 44082351 | 2019 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 43764 | 2043 | 692588 | 4115 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 40 | 164600 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0115935 | OH | Sus | 44082351 | 2019 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 43764 | 2043 | 685626 | 2802 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 125 | 350250 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0115935 | OH | Sus | 44082351 | 2019 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER |  | 43747 | 2244 | 654665 | 2853 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 11 | 31383 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0109236 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 43764 | 2043 | 692596 | 4074 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 73 | 297402 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0115935 | OH | Sus | 44082351 | 2019 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | SWITCH |  | 43764 | 2043 | 685628 | 2808 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 166 | 466128 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0115935 | OH | Sus | 44082351 | 2019 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 43764 | 2043 | 690456 | 4074 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 12 | 48888 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0115935 | OH | Sus | 44082351 | 2019 | OCT | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER |  | 43764 | 2043 | 687637 | 2808 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 2 | 5616 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0115935 | OH | Sus | 44082351 | 2019 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | SWITCH |  | 43764 | 2037 | 692647 | 3846 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 68 | 261528 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116227 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 43764 | 2116 | s1487894 | 4395 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 18 | 79110 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116042 | OH | Sus | 31476475 | 2019 | OCT | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 43764 | 2116 | 691866 | 4097 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 39 | 159783 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0116042 | OH | Sus | 31476475 | 2019 | OCT | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 43764 | 2116 | 689231 | 4097 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 142 | 581774 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116042 | OH | Sus | 31476475 | 2019 | OCT | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 43764 | 2116 | 692601 | 5795 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 6 | 34770 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0116042 | OH | Sus | 31476475 | 2019 | OCT | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 43764 | 2116 | 690446 | 4174 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 12 | 50088 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116112 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 43764 | 2116 | 694180 | 5234 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 4 | 20936 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116112 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 43764 | 2050 | 686073 | 4000 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 92 | 368000 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0116373 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
DE ANZA | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER |  | 43767 | 1945 | 694583 | 349 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 8725 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0118769 | OH | Sus | 44082355 | 2019 | OCT | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 2 | STELLING-1110 | 83481110 | JUMPER |  | 43761 | 130 | 677261 | 879 | Distribution Circuit | 3rd Party | Vehicle | 1 | 879 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0114891 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | Yes
DIABLO | Tier 2 | SOBRANTE-1102 | 14671102 | FUSE |  | 43764 | 2022 | 692603 | 4329 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 10 | 43290 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116797 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE |  | 43764 | 1753 | 696552 | 14377 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 6 | 86262 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0119496 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER |  | 43764 | 1753 | 690508 | 5947 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 348 | 2069556 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116482 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | HIGHLANDS-1102 | 43361102 | RECLOSER |  | 43764 | 1939 | 689779 | 5614 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 35 | 196490 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0116439 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
MISSION | Tier 3 | SAN RAMON-2107 | 14232107 | FUSE |  | 43764 | 2017 | 691573 | 2843 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 9 | 25587 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0117805 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE |  | 43764 | 2025 | 690781 | 3846 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 26 | 99996 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0117634 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
NORTH BAY | Tier 2 | SAN RAFAEL-1108 | 42011108 | JUMPER |  | 43764 | 2025 | 691993 | 4315 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 9 | 38835 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0117942 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | OCB |  | 43764 | 1720 | 681175 | 5620 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 3195 | 17955900 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116711 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 43764 | 1728 | 694591 | 7307 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 17 | 124219 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0118767 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2102 | 43432102 | FUSE |  | 43764 | 2040 | 687605 | 6741 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 6 | 40446 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0117290 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | JUMPER |  | 43764 | 1728 | s1486157 | 6887 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 33 | 219303 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0117503 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2105 | 43432105 | FUSE |  | 43764 | 2112 | 690484 | 6804 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 14 | 95256 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0117589 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 43764 | 1728 | 692571 | 5712 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 87 | 496944 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0118147 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 43764 | 1728 | 687104 | 2821 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 130 | 366730 | Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0117211 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE |  | 43764 | 1753 | 694496 | 8487 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 20 | 169740 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 19-0118739 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE |  | 43764 | 1753 | 687124 | 6059 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 4 | 24236 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0117217 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | CALISTOGA-1101 | 42711101 | FUSE |  | 43764 | 1753 | 689349 | 18557 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 72 | 1264228 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0117471 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | SWITCH |  | 43764 | 1753 | 696904 | 7362 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 26 | 191412 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0116729 | OH | Sus | 8191019 | 2019 | OCT | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 43764 | 1830 | 688343 | 2976 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 12 | 35712 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116380 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 43764 | 1830 | 689875 | 5651 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 50 | 282550 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0116380 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 43764 | 1830 | 690037 | 2974 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 10 | 29740 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116380 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 43761 | 1425 | 679870 | 1680 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 65 | 109200 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0114876 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | BIG BEND-1101 | 103751101 | RECLOSER |  | 43747 | 22 | s1479573 | 3853 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 94 | 362182 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0110191 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | RED BLUFF-1101 | 103541101 | FUSE |  | 43764 | 1702 | 690660 | 2795 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 175 | 489125 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0116543 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | JUMPER |  | 43764 | 1706 | 692760 | 4143 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 3 | 12429 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116336 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | FUSE |  | 43764 | 1813 | 694259 | 5607 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 14 | 78498 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 19-0116579 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1102 | 102541102 | FUSE |  | 43764 | 1813 | 696734 | 7267 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 39 | 283413 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0119578 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | JUMPER |  | 43764 | 1813 | 691770 | 7004 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 55 | 385220 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116583 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER |  | 43764 | 2002 | s1487800 | 4063 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 172 | 698836 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0115661 | OH | Sus | 0 | 2019 | OCT | Yes | None | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 43764 | 2002 | s1487798 | 3868 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 10 | 38680 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0115661 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 43764 | 2020 | 692082 | 2867 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 11 | 31537 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0115795 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 3 | DOBBINS-1101 | 153741101 | FUSE |  | 43764 | 1830 | 692095 | 5371 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 8 | 42968 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116162 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SACRAMENTO | Tier 2 | DOBBINS-1101 | 153741101 | FUSE |  | 43764 | 1830 | 694718 | 5724 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 32 | 183168 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116162 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SACRAMENTO | Tier 2 | DOBBINS-1101 | 153741101 | FUSE |  | 43764 | 1830 | 694782 | 5724 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 5 | 28620 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116162 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SACRAMENTO | Tier 2 | DOBBINS-1101 | 153741101 | FUSE |  | 43761 | 1507 | 679827 | 1782 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 51 | 90882 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0114824 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43764 | 2004 | 696342 | 6927 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 57 | 394839 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0115989 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | SWITCH |  | 43764 | 2008 | 692216 | 5625 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 203 | 1141875 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0115912 | OH | Sus | 0 | 2019 | OCT | Yes | None | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE |  | 43764 | 1829 | 692357 | 3911 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 32 | 125152 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0116642 | OH | Sus | 0 | 2019 | OCT | Yes | None | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | TRIP-SAVER |  | 43764 | 1811 | 692042 | 2920 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 75 | 219000 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0117976 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1107 | 152261107 | SWITCH |  | 43764 | 1741 | 690163 | 2818 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 330 | 929940 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116536 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | FUSE |  | 43764 | 1719 | 693609 | 5756 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 39 | 224484 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0116136 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43747 | 335 | 651143 | 3413 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 72 | 245736 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0109728 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 43764 | 1811 | 690417 | 2924 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 81872 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0117572 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 43764 | 1811 | 692201 | 2975 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 15 | 44625 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116618 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43764 | 2008 | 690299 | 5678 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 30 | 170340 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0117557 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 43764 | 1957 | 690136 | 5272 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 32 | 168704 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0117539 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | SWITCH |  | 43764 | 2008 | 695864 | 6860 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 8 | 54880 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0116140 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | JUMPER |  | 43764 | 2008 | 695854 | 6954 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 6954 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0116140 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43764 | 2008 | 696060 | 7216 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 8 | 57728 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116140 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43764 | 2008 | 696049 | 6867 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 6 | 41202 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116140 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | JUMPER |  | 43764 | 2008 | 693454 | 5678 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 2 | 11356 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116140 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | LINCOLN-1101 | 153701101 | FUSE |  | 43767 | 1513 | 694256 | 1213 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 14556 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 19-0118709 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | JUMPER |  | 43764 | 1957 | 693962 | 5277 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 11 | 58047 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0115982 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | JUMPER |  | 43764 | 1855 | 691431 | 2737 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 13685 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0115927 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 43764 | 1858 | 688974 | 2688 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 34944 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0117452 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | JUMPER |  | 43764 | 1705 | 691899 | 5312 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5312 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0115965 | OH | Sus | 0 | 2019 | OCT | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE |  | 43764 | 1901 | 691441 | 2779 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 20 | 55580 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116068 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | JUMPER |  | 43764 | 1947 | 692305 | 5621 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 5621 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0115970 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | JUMPER |  | 43764 | 1705 | 691977 | 5418 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5418 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0115965 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE |  | 43764 | 1841 | 690545 | 5410 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 29 | 156890 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116052 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1101 | 152031101 | FUSE |  | 43764 | 1841 | 691709 | 5430 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 108600 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0117871 | OH | Sus | 0 | 2019 | OCT | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 43764 | 1947 | 688008 | 2713 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 44 | 119372 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 19-0117340 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 43764 | 1947 | 692315 | 2861 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 8 | 22888 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0115970 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | JUMPER |  | 43764 | 1947 | 690116 | 5621 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 5621 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0115970 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | RECLOSER |  | 43764 | 1852 | 683601 | 3131 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 266 | 751842 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116145 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | SWITCH |  | 43764 | 1901 | 690716 | 5669 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 146 | 827674 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0117543 | OH | Sus | 0 | 2019 | OCT | Yes | None | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | JUMPER |  | 43764 | 1852 | 692507 | 5453 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 17 | 92701 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116145 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 43764 | 1943 | 692093 | 5304 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 14 | 74256 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0115956 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER |  | 43764 | 1943 | 692144 | 5326 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 11 | 58586 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0115956 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | COLUMBIA HILL-1101 | 152471101 | FUSE |  | 43764 | 1824 | 692399 | 5741 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 86115 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0118081 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE |  | 43764 | 1824 | 696761 | 7105 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 92 | 653660 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0115951 | OH | Sus | 0 | 2019 | OCT | Yes | None | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | RECLOSER |  | 43764 | 1824 | 683199 | 6951 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 32 | 222432 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0115951 | OH | Sus | 0 | 2019 | OCT | Yes | None | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1102 | 152101102 | RECLOSER |  | 43764 | 1824 | 682404 | 8517 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 165 | 1405305 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0115946 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | ALLEGHANY-1101 | 152101101 | RECLOSER |  | 43764 | 1824 | 682956 | 7061 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 466 | 1472054 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0115942 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE |  | 43747 | 1056 | 650876 | 357 | Distribution Circuit | 3rd Party | Vehicle | 11 | 1127 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0109622 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | SONOMA-1103 | 42721103 | SWITCH |  | 43764 | 1817 | 692237 | 2828 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 37 | 104636 | Partly Cloudy;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0116648 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 3 | SALMON CREEK-1101 | 43161101 | FUSE |  | 43748 | 1439 | 653377 | 473 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 3 | 1419 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0110133 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 43764 | 1950 | 690352 | 7193 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 22 | 158246 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0117562 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 3 | DUNBAR-1103 | 43071103 | FUSE |  | 43764 | 2104 | 691257 | 6958 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 98 | 681884 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116650 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 43764 | 1950 | 689876 | 8234 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 81 | 601448 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0117499 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | DUNBAR-1101 | 43071101 | SWITCH |  | 43764 | 2104 | 696662 | 6878 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 17 | 116926 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116637 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 43764 | 1950 | 691767 | 7248 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 35 | 253680 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0117895 | OH | Sus | 0 | 2019 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | RINCON-1104 | 43321104 | FUSE |  | 43764 | 1815 | 690866 | 5385 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 17 | 91545 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116661 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 3 | CLOVERDALE-1102 | 42821102 | FUSE |  | 43761 | 1511 | 680656 | 12803 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 12 | 153636 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0114789 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | CORRAL-1102 | 162991102 | JUMPER |  | 43748 | 419 | 652929 | 614 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3070 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 19-0110003 | OH | Sus | 43986879 | 2019 | OCT | Yes | Open Circuit | Yes | Yes
STOCKTON | Tier 2 | FROGTOWN-1701 | 163451701 | SWITCH |  | 43765 | 9 | 688844 | 3694 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 308 | 1137752 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116209 | OH | Sus | 8191136 | 2019 | OCT | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | CLAY-1103 | 163341103 | OCB |  | 43761 | 1221 | 677569 | 277 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1506 | 18960 | Clear;32-90 F | Pole-Wood | Broken- wire on object | 19-0115158 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | Yes
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER |  | 43764 | 1752 | 689856 | 5421 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 53 | 287313 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0116449 | OH | Sus | 8191136 | 2019 | OCT | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | SWITCH |  | 43764 | 1752 | 690177 | 6812 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 227 | 1546324 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116449 | OH | Sus | 8191136 | 2019 | OCT | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 43764 | 1752 | 690013 | 6812 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 6812 | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 19-0116449 | OH | Sus | 8191136 | 2019 | OCT | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | SALT SPRINGS-2102 | 163692102 | RECLOSER |  | 43764 | 1741 | 683399 | 7160 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 63 | 393967 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0116592 | OH | Sus | 8191136 | 2019 | OCT | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE |  | 43767 | 1333 | 694471 | 1287 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 7 | 9009 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116904 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1102 | 252531102 | OCB |  | 43765 | 1333 | 689538 | 1823 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 199 | 362777 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116906 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1102 | 252531102 | FUSE |  | 43765 | 1333 | 691791 | 4202 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 64 | 268928 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0116906 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 43765 | 1341 | 692785 | 4496 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 18 | 80928 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 19-0116902 | OH | Sus | 0 | 2019 | OCT | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 43731 | 513 | 604148 | 389 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3890 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0102283 | OH | Sus | 0 | 2019 | SEP | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 43731 | 1259 | 606674 | 257 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 771 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0102537 | OH | Sus | 43964150 | 2019 | SEP | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE |  | 43733 | 310 | 615333 | 1074 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 41 | 44034 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0103082 | OH | Sus | 31473325 | 2019 | SEP | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE |  | 43733 | 627 | 612845 | 518 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 7066 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0103372 | OH | Sus | 0 | 2019 | SEP | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | OTHER |  | 43731 | 1452 | 607255 | 642 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 14 | 8708 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0102604 | OH | Sus | 43964302 | 2019 | SEP | Yes | Open Circuit | Yes | Yes
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE |  | 43731 | 2304 | 608006 | 1208 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 24160 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 19-0102785 | OH | Sus | 31473062 | 2019 | SEP | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 44059 | 239 | 1011539 | 1015 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 109620 | Partly Cloudy;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0084611 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | PAUL SWEET-2106 | 83252106 | FUSE |  | 44059 | 254 | 1009844 | 2062 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 53960 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0084835 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2107 | 83252107 | FUSE |  | 44060 | 746 | 1014940 | 1879 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 37450 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0086728 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 44059 | 257 | 1011432 | 2238 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 58188 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0085226 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 44059 | 1146 | 1013115 | 364 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 33545 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0085160 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 44059 | 1757 | 1014194 | 1183 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1183 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0085292 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 44060 | 857 | 1015541 | 1595 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 14891 | Partly Cloudy-Heat Wave;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0086124 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 44059 | 243 | 1009747 | 3615 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 801 | 331038 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0084614 | OH | Sus | 0 | 2020 | AUG | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | JUMPER |  | 44059 | 241 | 1014395 | 1917 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 34506 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0085389 | OH | Sus | 0 | 2020 | AUG | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 44059 | 241 | 1014308 | 1957 | Distribution Circuit | Vegetation | Tree - branch fell on line | 60 | 117420 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0085354 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44059 | 241 | 1014066 | 2357 | Distribution Circuit | Vegetation | Tree - branch fell on line | 44 | 103708 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0084613 | OH | Sus | 44436413 | 2020 | AUG | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44059 | 241 | 1011479 | 1260 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 42840 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0084775 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44059 | 252 | 1010502 | 1000 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 14000 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0084706 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44059 | 244 | 1009933 | 2406 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 190074 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0085630 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | JUMPER |  | 44059 | 243 | 1012071 | 1820 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 3640 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0085392 | OH | Sus | 0 | 2020 | AUG | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44059 | 250 | 1009948 | 2117 | Distribution Circuit | Vegetation | Tree - branch fell on line | 57 | 112074 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0085297 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 44060 | 322 | 1014489 | 1061 | Distribution Circuit | Vegetation | Tree - fell into line | 181 | 141530 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0085524 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 2 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 44059 | 434 | 1010524 | 749 | Distribution Circuit | Equipment Failure/Involved | Overhead | 397 | 68445 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0084687 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44059 | 252 | 1010503 | 851 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 41699 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0085075 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 44059 | 1636 | 1013404 | 1429 | Distribution Circuit | Vegetation | Tree - branch fell on line | 102 | 126078 | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 20-0085159 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 44059 | 244 | 1013223 | 3891 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 160184 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0084616 | OH | Sus | 0 | 2020 | AUG | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | JUMPER |  | 44059 | 244 | s1555723 | 2293 | Distribution Circuit | Vegetation | Tree - branch fell on line | 58 | 132963 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0084616 | OH | Sus | 0 | 2020 | AUG | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44059 | 254 | 1009843 | 2489 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 108635 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0085865 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | JUMPER |  | 44060 | 1314 | 1017666 | 1438 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1438 | Partly Cloudy-Heat Wave;Above 90 | Conductor- Overhead | Broken- wire on ground | 20-0086178 | OH | Sus | 0 | 2020 | AUG | Yes | None | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44059 | 252 | 1012937 | 898 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 20654 | Partly Cloudy;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0085007 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44059 | 252 | 1010478 | 3455 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2165 | 562314 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0084689 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44059 | 2103 | 1014188 | 1305 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 67744 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0085566 | OH | Sus | 0 | 2020 | AUG | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | OCB |  | 44059 | 249 | 1009841 | 1258 | Distribution Circuit | Vegetation | Tree - fell into line | 1827 | 1609959 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0084626 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44060 | 1926 | 1017773 | 979 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 12727 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0086250 | OH | Sus | 44436413 | 2020 | AUG | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER |  | 44059 | 247 | 1016210 | 3549 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 319410 | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 20-0085727 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44059 | 254 | 1011258 | 1101 | Distribution Circuit | Environmental/External | Lightning | 34 | 37434 | Lightning-Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0084746 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER |  | 44059 | 300 | 1011852 | 2422 | Distribution Circuit | Environmental/External | Lightning | 93 | 85969 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0085342 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE |  | 44059 | 1457 | 1013079 | 4535 | Distribution Circuit | Vegetation | Tree - bark fell into line | 5 | 22675 | Partly Cloudy-Heat Wave;Above 90 | Conductor- Overhead | Broken- wire on ground | 20-0085071 | OH | Sus | 35193065 | 2020 | AUG | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | OTHER |  | 44059 | 104 | 1009634 | 1681 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 14416 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0084603 | OH | Sus | 44436482 | 2020 | AUG | Yes | Line to Ground | Yes | Yes
DIABLO | Tier 2 | SOBRANTE-1103 | 14671103 | OCB |  | 44059 | 347 | 1010226 | 6205 | Distribution Circuit | Vegetation | Tree - fell into line | 981 | 105177 | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 20-0084663 | OH | Sus | 0 | 2020 | AUG | Yes | Multi-Fault | Yes | No
DIABLO | Tier 2 | ALHAMBRA-1105 | 14101105 | FUSE |  | 44059 | 424 | 1010859 | 3719 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 59504 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0085265 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-0001 | 254060001 | FUSE |  | 44060 | 1452 | 1017281 | 370 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 5507 | Partly Cloudy-Heat Wave;Above 90 | Crossarm- Wood | Broken- wire on ground | 20-0086152 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LUCERNE-1106 | 43351106 | RECLOSER |  | 44059 | 552 | 1010933 | 560 | Distribution Circuit | Vegetation | Tree - fell into line | 259 | 145040 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0084718 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | HOPLAND-1101 | 42251101 | FUSE |  | 44059 | 1503 | 1013103 | 434 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 19530 | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 20-0085153 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | ATASCADERO-1101 | 182541101 | FUSE |  | 44058 | 752 | 1003856 | 653 | Distribution Circuit | Vegetation | Tree - fell into line | 187 | 92586 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0084094 | OH | Sus | 31511504 | 2020 | AUG | Yes | Line to Ground | Yes | No
MISSION | Tier 3 | SUNOL-1101 | 14241101 | FUSE |  | 44059 | 2054 | 1014171 | 1235 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 132929 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0085343 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | BOLINAS-1101 | 42261101 | OCB |  | 44060 | 1034 | 1015966 | 623 | Distribution Circuit | Environmental/External | Lightning | 1631 | 737299 | Partly Cloudy-Heat Wave;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0085674 | OH | Sus | 31511584 | 2020 | AUG | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE |  | 44060 | 1047 | 1015994 | 938 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 12342 | Partly Cloudy-Lightning-Heat Wave;32-90 F | Transformer (OH) | Broken- wire on ground | 20-0086444 | OH | Sus | 3151584 | 2020 | AUG | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | STAFFORD-1102 | 43201102 | RECLOSER |  | 44060 | 300 | 1014482 | 965 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 20290 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0085412 | OH | Sus | 44437092 | 2020 | AUG | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 44059 | 438 | 1010457 | 856 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 22256 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0084754 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | PUEBLO-1104 | 43291104 | OTHER |  | 44059 | 1041 | 1011956 | 1841 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3076 | Heat Wave | Crossarm- Wood | Broken- wire on ground | 20-0085291 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE |  | 44060 | 2216 | 1017980 | 40071 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 50 | 304 | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 20-0086524 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | SYCAMORE CREEK-1111 | 102971111 | RECLOSER |  | 44060 | 818 | 1015209 | 391 | Distribution Circuit | Environmental/External | Lightning | 537 | 209967 | Partly Cloudy-Lightning-Heat Wave;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0085570 | OH | Sus | 0 | 2020 | AUG | Yes | Three Phase Fault | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 44059 | 903 | 1011595 | 507 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 16445 | Partly Cloudy-Drizzle-Lightning-Heat Wave;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0084802 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE |  | 44059 | 527 | 1017400 | 3412 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6824 | Partly Cloudy-Drizzle-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0086003 | OH | Sus | 31511461 | 2020 | AUG | Yes | Force Out | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 44059 | 2134 | 1014238 | 1119 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1119 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0085352 | OH | Sus | 0 | 2020 | AUG | Yes | Force Out | Yes | No
SAN JOSE | Tier 3 | MORGAN HILL-2105 | 83242105 | OTHER |  | 44060 | 645 | 1015257 | 316 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 13858 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0085670 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 44059 | 1235 | 1012726 | 515 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2060 | Partly Cloudy-Heat Wave;Above 90 | Pole-Wood | Broken- wire on ground | 20-0085010 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44060 | 1755 | 1017674 | 1164 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 100104 | Clear-Heat Wave;Above 90 | Conductor- Overhead | Broken- wire on ground | 20-0086210 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | RECLOSER |  | 44058 | 316 | 1003656 | 468 | Distribution Circuit | 3rd Party | Vehicle | 849 | 297015 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0084057 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44059 | 1517 | 1013150 | 381 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 1799 | Clear-Heat Wave;Above 90 | Conductor- Overhead | Broken- wire on ground | 20-0085084 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER |  | 44059 | 425 | 1010400 | 750 | Distribution Circuit | Vegetation | Tree - branch fell on line | 434 | 325500 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0084672 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 44059 | 427 | 1010403 | 1212 | Distribution Circuit | Vegetation | Tree - branch fell on line | 152 | 184224 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0084864 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1107 | 42151107 | FUSE |  | 44059 | 436 | 1010513 | 1177 | Distribution Circuit | Vegetation | Tree - branch fell on line | 263 | 240069 | Overcast-Drizzle-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0084871 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE |  | 44059 | 448 | 1010564 | 860 | Distribution Circuit | Environmental/External | Lightning | 33 | 28380 | Overcast-Drizzle-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0084813 | OH | Sus | 0 | 2020 | AUG | Yes | Force Out | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 44059 | 455 | 1010637 | 707 | Distribution Circuit | Vegetation | Tree - branch fell on line | 179 | 126553 | Partly Cloudy-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0084737 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | CLOVERDALE-1102 | 42821102 | FUSE |  | 44059 | 500 | 1014145 | 2047 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 34362 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0085273 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | CLOVERDALE-1102 | 42821102 | FUSE |  | 44059 | 1208 | 1012330 | 1424 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 27056 | Partly Cloudy-Heat Wave;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0085086 | OH | Sus | 0 | 2020 | AUG | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | RESERVATION ROAD-1102 | 182731102 | FUSE |  | 43870 | 1223 | 783783 | 794 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 7146 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 20-0019434 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE |  | 43870 | 1409 | 784800 | 1475 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 10325 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019436 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 43870 | 1003 | 784987 | 2989 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 29890 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019361 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 43870 | 1612 | 785541 | 2901 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 49317 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0020413 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | RECLOSER |  | 43870 | 1136 | 781981 | 3552 | Distribution Circuit | Vegetation | Tree - fell into line | 441 | 645405 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019193 | OH | Sus | 0 | 2020 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER |  | 43870 | 1016 | 782145 | 1904 | Distribution Circuit | Vegetation | Tree - fell into line | 254 | 473431 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 20-0019090 | OH | Sus | 0 | 2020 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 43870 | 919 | 783984 | 3638 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 24196 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019244 | OH | Sus | 31490380 | 2020 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 43870 | 919 | 781568 | 1007 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 28110 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019177 | OH | Sus | 31490380 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 43870 | 1445 | 785030 | 1703 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 13624 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0020230 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | RECLOSER |  | 43870 | 1041 | 782442 | 4263 | Distribution Circuit | Vegetation | Tree - branch fell on line | 448 | 820210 | Clear;32-90 F | Insulator | Broken- wire on ground | 20-0019218 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 43870 | 1128 | 782984 | 3145 | Distribution Circuit | Vegetation | Tree - branch fell on line | 49 | 154105 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019813 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 43870 | 1002 | 785282 | 3058 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 45870 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019405 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 43870 | 1023 | 782197 | 1630 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 94540 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019548 | OH | Sus | 44182926 | 2020 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2105 | 83252105 | FUSE |  | 43870 | 1129 | 782993 | 2256 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 38352 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019658 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | JUMPER |  | 43870 | 1041 | 787997 | 3069 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 12276 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019218 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 43870 | 1557 | 785876 | 2815 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 154825 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019650 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 43870 | 816 | 781532 | 335 | Distribution Circuit | Vegetation | Tree - branch fell on line | 94 | 31490 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019015 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | PAUL SWEET-2106 | 83252106 | FUSE |  | 43870 | 1041 | 786787 | 1977 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 35586 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019698 | OH | Sus | 0 | 2020 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | JUMPER |  | 43870 | 1014 | 787942 | 3343 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 40116 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0020216 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 43870 | 1041 | 786545 | 1873 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 95523 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019632 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 43870 | 1014 | 787875 | 3343 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 160464 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019878 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 43870 | 41 | 787352 | 2932 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 102758 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019878 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | SWITCH |  | 43870 | 1041 | 787543 | 3290 | Distribution Circuit | Vegetation | Tree - branch fell on line | 106 | 348740 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019878 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 43870 | 1041 | 787448 | 4528 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 80788 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019878 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | RECLOSER |  | 43870 | 1041 | 787528 | 1861 | Distribution Circuit | Vegetation | Tree - branch fell on line | 115 | 214015 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019878 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 43870 | 1041 | 787350 | 1711 | Distribution Circuit | Vegetation | Tree - branch fell on line | 87 | 64947 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019878 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 43870 | 1052 | 782481 | 4243 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 178206 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0020257 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER |  | 43870 | 1052 | 788083 | 4243 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4243 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0020257 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE |  | 43870 | 1041 | 787247 | 1907 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 173537 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019817 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | FELTON SUB | 8314 | OCB |  | 43870 | 1154 | 782541 | 1350 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 35842 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019473 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 43870 | 913 | 781506 | 3031 | Distribution Circuit | Vegetation | Tree - branch fell on line | 80 | 242480 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019128 | OH | Sus | 0 | 2020 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | TRIP-SAVER |  | 43870 | 704 | 781007 | 3591 | Distribution Circuit | Vegetation | Tree - bark fell into line | 69 | 14879 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 20-0019040 | OH | Sus | 31490380 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | TRIP-SAVER |  | 43870 | 1052 | 785174 | 3363 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 209064 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019383 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 43870 | 943 | 781796 | 4570 | Distribution Circuit | Vegetation | Tree - branch fell on line | 184 | 62947 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019178 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 43870 | 710 | 783653 | 3415 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 72790 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019645 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | OTHER |  | 43870 | 639 | 780969 | 398 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 9964 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0018956 | OH | Sus | 44182952 | 2020 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 43870 | 1025 | 783288 | 623 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 17444 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019202 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 43870 | 1052 | 782494 | 3441 | Distribution Circuit | Vegetation | Tree - branch fell on line | 67 | 200355 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019123 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 43870 | 1109 | 787066 | 2935 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 49895 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019763 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 43870 | 1123 | 784138 | 2879 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 123797 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019261 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | OTHER |  | 43870 | 1357 | 784724 | 1310 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 9376 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019396 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 43870 | 1450 | 785070 | 358 | Distribution Circuit | Vegetation | Tree - branch fell on line | 71 | 21130 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019425 | OH | Sus | 0 | 2020 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 43870 | 713 | 781025 | 3412 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 208132 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 20-0018943 | OH | Sus | 31490382 | 2020 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER |  | 43870 | 1057 | 787802 | 3203 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 9609 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0020174 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | TRIP-SAVER |  | 43870 | 859 | 781381 | 3648 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 25536 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019807 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | JUMPER |  | 43870 | 1308 | 786333 | 3158 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 51189 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019577 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 43870 | 1041 | 785433 | 1935 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9675 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 20-0019429 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | JUMPER |  | 43870 | 1037 | 787577 | 3328 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6656 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0020008 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 43870 | 1118 | 785447 | 3106 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 77110 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 20-0019430 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 43870 | 1308 | 784247 | 1575 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 88200 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019569 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 43870 | 1210 | 783656 | 1536 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 52224 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019685 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 43870 | 1959 | 786318 | 2741 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 11393 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0020191 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER |  | 43870 | 933 | 783911 | 402 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2010 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019240 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 43870 | 1204 | 783566 | 3535 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 84840 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019469 | OH | Sus | 31489891 | 2020 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 43870 | 1240 | 783980 | 1584 | Distribution Circuit | Vegetation | Tree - fell into line | 176 | 44763 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019242 | OH | Sus | 31489889 | 2020 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 43870 | 852 | 781354 | 3914 | Distribution Circuit | Vegetation | Tree - fell into line | 357 | 115326 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 20-0018999 | OH | Sus | 31489889 | 2020 | FEB | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE |  | 43870 | 1214 | 785741 | 1841 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 150092 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019464 | OH | Sus | 31489889 | 2020 | FEB | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE |  | 43870 | 1327 | 785280 | 1800 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 10800 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019501 | OH | Sus | 31489889 | 2020 | FEB | Yes | Line to Line | Yes | No
DIABLO | Tier 3 | ORINDA-0402 | 12350402 | FUSE |  | 43870 | 1011 | 782109 | 1083 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 27372 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019264 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | SOBRANTE-1101 | 14671101 | OCB |  | 43870 | 910 | 782192 | 1075 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2752 | 500796 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019094 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | ROSSMOOR-1101 | 14161101 | FUSE |  | 43870 | 819 | 781294 | 240 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 3943 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019000 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | Yes
DIABLO | Tier 2 | ALHAMBRA-1105 | 14101105 | FUSE |  | 43870 | 808 | 781136 | 411 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 7398 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0018960 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 2 | OAKLAND J-1106 | 12091106 | FUSE |  | 43870 | 819 | 781217 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 72834 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0018981 | OH | Sus | 31490427 | 2020 | FEB | Yes | Three Phase Fault | Yes | No
EAST BAY | Tier 2 | OAKLAND X-1106 | 12541106 | RECLOSER |  | 43870 | 1114 | 781972 | 2159 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1309 | 497059 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019164 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | FUSE |  | 43870 | 1016 | 782138 | 1610 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 120944 | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0019581 | OH | Sus | 0 | 2020 | FEB | Yes | Three Phase Fault | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE |  | 43870 | 1157 | 783484 | 2833 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 80245 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 20-0019527 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | OTHER |  | 43870 | 1300 | 787241 | 2322 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 111012 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019812 | OH | Sus | 0 | 2020 | FEB | Yes | None | Yes | No
EAST BAY | Tier 2 | FLORENCE-0401 | 12690401 | OCB |  | 43870 | 856 | 782653 | 991 | Distribution Circuit | Vegetation | Tree - branch fell on line | 494 | 214304 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019139 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAKLAND K-1103 | 12101103 | OCB |  | 43870 | 1202 | 783635 | 1931 | Distribution Circuit | Vegetation | Tree - fell into line | 4779 | 990592 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019265 | OH | Sus | 0 | 2020 | FEB | Yes | Three Phase Fault | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | RECLOSER |  | 43870 | 1822 | 786054 | 747 | Distribution Circuit | Vegetation | Tree - fell into line | 308 | 127528 | Strong Winds-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019535 | OH | Sus | 31490411 | 2020 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | FUSE |  | 43870 | 1230 | 784209 | 592 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1776 | Clear | Pole-Wood | Broken- wire on ground | 20-0019275 | OH | Sus | 0 | 2020 | FEB | Yes | Open Circuit | Yes | No
MISSION | Tier 3 | CASTRO VALLEY-1106 | 14091106 | FUSE |  | 43870 | 1501 | 785130 | 2353 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 7059 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019379 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | FUSE |  | 43870 | 1455 | 784958 | 554 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 3324 | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on object | 20-0019382 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1122 | 42031122 | FUSE |  | 43870 | 947 | 781825 | 382 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 34442 | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0019092 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE |  | 43870 | 1530 | 785278 | 1101 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 40737 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019447 | OH | Sus | 0 | 2020 | FEB | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 2 | SAN RAFAEL-1106 | 42011106 | FUSE |  | 43870 | 1002 | 782040 | 1898 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5694 | Clear;32-90 F | Pole-Wood | Broken- wire on object | 20-0019220 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE |  | 43870 | 1130 | 783005 | 900 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 9000 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019279 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE |  | 43870 | 1141 | 783946 | 1404 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 16848 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019442 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2102 | 43292102 | FUSE |  | 43870 | 323 | 781017 | 2857 | Distribution Circuit | Vegetation | Tree - branch fell on line | 63 | 165810 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019109 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2102 | 43292102 | JUMPER |  | 43870 | 323 | 782866 | 2854 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 22832 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019168 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2102 | 43432102 | FUSE |  | 43870 | 545 | 780939 | 1313 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 22770 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019038 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2105 | 43432105 | OTHER |  | 43870 | 1440 | 786619 | 1413 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 6539 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019668 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | TRIP-SAVER |  | 43870 | 1251 | 784052 | 1717 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 8511 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019360 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE |  | 43870 | 858 | 784299 | 1770 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 36795 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019287 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 43870 | 1218 | 783724 | 262 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 786 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019320 | OH | Sus | 31490408 | 2020 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 43870 | 1233 | 783918 | 1725 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 58650 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019586 | OH | Sus | 31490119 | 2020 | FEB | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 43870 | 1604 | 785485 | 958 | Distribution Circuit | Vegetation | Tree - branch fell on line | 92 | 18908 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019481 | OH | Sus | 44181889 | 2020 | FEB | Yes | Line to Line | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 43870 | 1149 | 783363 | 1068 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 11748 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019324 | OH | Sus | 44181889 | 2020 | FEB | Yes | Line to Line | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 43870 | 1151 | 783965 | 3124 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 93720 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019624 | OH | Sus | 44190286 | 2020 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER |  | 43870 | 1128 | 784924 | 2233 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 71533 | Strong Winds | Conductor- Overhead | Broken- wire on ground | 20-0019440 | OH | Sus | 44181889 | 2020 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | WOODSIDE-1104 | 24251104 | TRIP-SAVER |  | 43870 | 1024 | 782224 | 829 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 50342 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019284 | OH | Sus | 31490119 | 2020 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE |  | 43870 | 742 | 781243 | 476 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 32844 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019082 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | SWITCH |  | 43870 | 1725 | 785891 | 260 | Distribution Circuit | Vegetation | Tree - branch fell on line | 660 | 24811 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019493 | OH | Sus | 0 | 2020 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1112 | 153081112 | RECLOSER |  | 43870 | 1100 | 782689 | 670 | Distribution Circuit | Vegetation | Tree - branch fell on line | 758 | 71411 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 20-0019161 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43870 | 714 | 781231 | 426 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 2556 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 20-0018955 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43870 | 1129 | 783029 | 305 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 26535 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019238 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | EL DORADO PH-2101 | 152762101 | RECLOSER |  | 43870 | 626 | 780966 | 738 | Distribution Circuit | Vegetation | Tree - fell into line | 771 | 167271 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0018908 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | OTHER |  | 43870 | 1007 | 782728 | 526 | Distribution Circuit | Vegetation | Tree - fell into line | 268 | 12928 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0019147 | OH | Sus | 0 | 2020 | FEB | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | NARROWS-2102 | 153132102 | FUSE |  | 43870 | 904 | 781421 | 503 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 12584 | Clear; | Pole-Wood | Broken- wire on ground | 20-0019060 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE |  | 43870 | 933 | 781707 | 374 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 20944 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 20-0019137 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER |  | 43870 | 925 | 781601 | 669 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 40140 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019030 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER |  | 43870 | 1053 | 782348 | 456 | Distribution Circuit | Vegetation | Tree - fell into line | 352 | 67040 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019132 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | FUSE |  | 43870 | 1020 | 785843 | 738 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 84132 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019479 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE |  | 43870 | 1108 | 782144 | 284 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 2840 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019175 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 43870 | 1019 | 782204 | 999 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 40959 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019180 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE |  | 43870 | 1308 | 784243 | 1556 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 12448 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019516 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 43870 | 1005 | 782014 | 1613 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 10576 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 20-0019478 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 43870 | 1956 | 786314 | 1493 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 122754 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0019804 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | OCB |  | 43870 | 747 | 781046 | 1557 | Distribution Circuit | Vegetation | Tree - fell into line | 1052 | 563756 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0018932 | OH | Sus | 0 | 2020 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | FUSE |  | 43870 | 716 | 781175 | 608 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 58368 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0018918 | OH | Sus | 44182951 | 2020 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | FUSE |  | 43870 | 656 | 780990 | 1998 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 133866 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019151 | OH | Sus | 0 | 2020 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2102 | 254432102 | RECLOSER |  | 43870 | 803 | 781130 | 534 | Distribution Circuit | Vegetation | Tree - fell into line | 1237 | 293723 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 20-0018939 | OH | Sus | 31490289 | 2020 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1103 | 252531103 | JUMPER |  | 43870 | 649 | 783457 | 2005 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2005 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019151 | OH | Sus | 0 | 2020 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER |  | 43870 | 949 | 781715 | 1681 | Distribution Circuit | Vegetation | Tree - fell into line | 541 | 593834 | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0019050 | OH | Sus | 0 | 2020 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | FUSE |  | 43870 | 820 | 781219 | 1737 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 67743 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019085 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | JUMPER |  | 43870 | 803 | 782185 | 1922 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 23064 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 20-0019089 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER |  | 43870 | 913 | 781347 | 1472 | Distribution Circuit | Vegetation | Tree - fell into line | 465 | 279940 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 20-0019017 | OH | Sus | 0 | 2020 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE |  | 43870 | 1247 | 784029 | 840 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 52080 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0019472 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | CURTIS-1705 | 163351705 | FUSE |  | 43870 | 1319 | 784291 | 1536 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 30720 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 20-0019402 | OH | Sus | 0 | 2020 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER |  | 43870 | 945 | 781821 | 1697 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 179668 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 20-0019045 | OH | Sus | 0 | 2020 | FEB | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 43846 | 1436 | 763116 | 139 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1529 | Overcast-Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 20-0010080 | OH | Sus | 0 | 2020 | JAN | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 43846 | 906 | 762422 | 494 | Distribution Circuit | Vegetation | Tree - branch fell on line | 800 | 171201 | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0009638 | OH | Sus | 44157208 | 2020 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | JUMPER |  | 43846 | 904 | 763185 | 658 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1316 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010232 | OH | Sus | 44157208 | 2020 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 43846 | 906 | 763040 | 549 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 9333 | Partly Cloudy-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0009991 | OH | Sus | 31486501 | 2020 | JAN | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 43846 | 934 | 763363 | 1811 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1811 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010328 | OH | Sus | 31486644 | 2020 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER |  | 43846 | 318 | 761942 | 347 | Distribution Circuit | Vegetation | Tree - fell into line | 630 | 62299 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0009489 | OH | Sus | 0 | 2020 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 43846 | 1153 | 763354 | 3187 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 54179 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010315 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 43846 | 620 | 762221 | 822 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 15618 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0009576 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 43846 | 658 | 763582 | 2023 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 135541 | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0010309 | OH | Sus | 0 | 2020 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | OCB |  | 43846 | 748 | 762227 | 1973 | Distribution Circuit | Vegetation | Tree - fell into line | 601 | 270017 | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken- wire on object | 20-0009587 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 43846 | 649 | 765124 | 2290 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 107630 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010932 | OH | Sus | 0 | 2020 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | JUMPER |  | 43846 | 519 | 763565 | 1744 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 22672 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010301 | OH | Sus | 0 | 2020 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 43846 | 606 | 762073 | 3579 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 60843 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0009939 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 43846 | 613 | 762038 | 3195 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 146765 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0009955 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 43846 | 545 | 762026 | 4945 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 39560 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0009710 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | RECLOSER |  | 43846 | 627 | 762105 | 4832 | Distribution Circuit | Vegetation | Tree - fell into line | 525 | 1796587 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010377 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 43846 | 413 | 765118 | 3457 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 48398 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 20-0010920 | OH | Sus | 0 | 2020 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 43846 | 413 | 763648 | 2265 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 18120 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010326 | OH | Sus | 0 | 2020 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER |  | 43846 | 413 | 761956 | 2265 | Distribution Circuit | Vegetation | Tree - fell into line | 356 | 792687 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0009495 | OH | Sus | 0 | 2020 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE |  | 43846 | 614 | 766118 | 4897 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 73455 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0011174 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE |  | 43846 | 614 | 765253 | 4630 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 18520 | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 20-0010994 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 43846 | 726 | 766142 | 4968 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 228528 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0011186 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER |  | 43846 | 610 | 762125 | 601 | Distribution Circuit | Vegetation | Tree - fell into line | 161 | 96761 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0009525 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER |  | 43846 | 217 | 761896 | 11 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 286 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 20-0009483 | OH | Sus | 0 | 2020 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER |  | 43846 | 317 | 761945 | 2412 | Distribution Circuit | Vegetation | Tree - fell into line | 303 | 275436 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0009490 | OH | Sus | 0 | 2020 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | RECLOSER |  | 43846 | 432 | 761980 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 55514 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0009497 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | MAPLE CREEK-1101 | 192101101 | OCB |  | 43846 | 125 | 761886 | 976 | Distribution Circuit | Vegetation | Tree - fell into line | 146 | 34096 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0009480 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | FUSE |  | 43846 | 146 | 761891 | 689 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 11024 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0009498 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1121 | 192021121 | FUSE |  | 43846 | 202 | 761903 | 2101 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 81939 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0009594 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | JUMPER |  | 43846 | 1921 | 764829 | 2601 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 6841 | Partly Cloudy-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010636 | OH | Sus | 0 | 2020 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 43846 | 1942 | 764754 | 2576 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 54096 | Overcast-Fog;Below 32 F | Pole-Wood | Broken- wire on ground | 20-0010579 | OH | Sus | 0 | 2020 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 43846 | 300 | 763576 | 3425 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 58225 | Clear;Below 32 F | Connector or Splice (OH) | Broken- wire on ground | 20-0010307 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | RECLOSER |  | 43846 | 134 | 761887 | 9185 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 871469 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0009481 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 43846 | 259 | 765175 | 6649 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6649 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0010959 | OH | Sus | 0 | 2020 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | SWITCH |  | 43846 | 259 | 762158 | 6436 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 51488 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0009554 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 43846 | 300 | 764770 | 3522 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 91572 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010592 | OH | Sus | 0 | 2020 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 43846 | 259 | 765494 | 5001 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 25005 | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 20-0011049 | OH | Sus | 0 | 2020 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 43846 | 259 | 763568 | 6605 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 145310 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010303 | OH | Sus | 0 | 2020 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 43846 | 259 | 766566 | 10666 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 42664 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0011341 | OH | Sus | 0 | 2020 | JAN | Yes | Open Circuit | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 43847 | 1622 | 765121 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 405 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010955 | OH | Sus | 44159086 | 2020 | JAN | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER |  | 43846 | 1545 | 763291 | 285 | Distribution Circuit | Vegetation | Tree - branch fell on line | 136 | 28120 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010211 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE |  | 43846 | 1600 | 763499 | 1570 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4710 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0010625 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | BIG BEND-1102 | 103751102 | FUSE |  | 43846 | 1502 | 763226 | 1353 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 121770 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010251 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | WHITMORE-1101 | 103601101 | JUMPER |  | 43846 | 1101 | 762714 | 337 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 31375 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0009909 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER |  | 43846 | 839 | 762280 | 535 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 36915 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0009621 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43846 | 946 | 762549 | 234 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 1404 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0009767 | OH | Sus | 31486518 | 2020 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | JUMPER |  | 43846 | 1641 | 763348 | 269 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2402 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010264 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43847 | 1825 | 765201 | 135 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 53 | 7155 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010985 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 43847 | 1007 | 764712 | 167 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 9352 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010564 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 43846 | 1625 | 763329 | 1122 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 63954 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010296 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 43847 | 654 | 764495 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1956 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010528 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 43846 | 1819 | 763551 | 1106 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 18802 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010333 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | OTHER |  | 43846 | 1815 | 763673 | 1430 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 18479 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010339 | OH | Sus | 0 | 2020 | JAN | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 43846 | 1426 | 763096 | 1258 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 42772 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010227 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 43847 | 49 | 763778 | 2022 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 55692 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010891 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | NARROWS-2102 | 153132102 | JUMPER |  | 43846 | 929 | 762623 | 258 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 21930 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0009717 | OH | Sus | 31486515 | 2020 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE |  | 43846 | 1555 | 765314 | 4105 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 111642 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010254 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER |  | 43847 | 1048 | 764762 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 539 | 89920 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010610 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 43847 | 709 | 763865 | 302 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 9966 | Partly Cloudy-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0010476 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 43847 | 24 | 763772 | 448 | Distribution Circuit | Vegetation | Tree - fell into line | 676 | 147619 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0010393 | OH | Sus | 0 | 2020 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | OCB |  | 43905 | 934 | 852139 | 86 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 5732 | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0032258 | OH | Sus | 0 | 2020 | MAR | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 43906 | 7 | 853030 | 182 | Distribution Circuit | Vegetation | Tree - bark fell into line | 181 | 32942 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032480 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 43906 | 7 | 853308 | 698 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2094 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032481 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 43905 | 100 | 851642 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 5760 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032166 | OH | Sus | 31495831 | 2020 | MAR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1102 | 12101102 | FUSE |  | 43906 | 910 | 853962 | 1220 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 55420 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032668 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | AUBERRY-1101 | 254151101 | FUSE |  | 43906 | 1846 | 855890 | 1550 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 18600 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 20-0033083 | OH | Sus | 31497435 | 2020 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE |  | 43905 | 836 | 852070 | 249 | Distribution Circuit | Vegetation | Tree - fell into line | 113 | 10545 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032249 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 43905 | 634 | 851917 | 794 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 12704 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032250 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | OTHER |  | 43905 | 623 | 851911 | 323 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 2263 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 20-0032241 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | OCB |  | 43905 | 406 | 851771 | 800 | Distribution Circuit | Environmental/External | Ice or snow | 1270 | 158601 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032183 | OH | Sus | 0 | 2020 | MAR | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | OTHER |  | 43905 | 401 | 851763 | 2111 | Distribution Circuit | Environmental/External | Ice or snow | 62 | 130882 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032189 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE |  | 43905 | 401 | 852075 | 2110 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 32258 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032247 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | Yes
LOS PADRES | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE |  | 43905 | 851 | 852090 | 507 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4563 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032262 | OH | Sus | 44258655 | 2020 | MAR | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | OTHER |  | 43905 | 615 | 851915 | 732 | Distribution Circuit | Vegetation | Tree - fell into line | 201 | 135037 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032219 | OH | Sus | 44259032 | 2020 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | OCB |  | 43905 | 518 | 851849 | 2222 | Distribution Circuit | Vegetation | Tree - fell into line | 694 | 1528565 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032199 | OH | Sus | 44259033 | 2020 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | JUMPER |  | 43905 | 424 | 851964 | 1911 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 7644 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032399 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43906 | 931 | 855126 | 1929 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 61728 | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 20-0032487 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43906 | 214 | 853405 | 2383 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 54809 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032487 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43906 | 218 | 858411 | 6304 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 359328 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033909 | OH | Sus | 0 | 2020 | MAR | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43906 | 1708 | 855653 | 5812 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 5812 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0034369 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43906 | 1118 | 854518 | 2882 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 46112 | Partly Cloudy-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033457 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43906 | 1018 | 854516 | 3042 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 36504 | Partly Cloudy-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033033 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43905 | 1044 | 852412 | 5787 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 70461 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032339 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER |  | 43906 | 313 | 853258 | 4968 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1923 | 4626262 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032487 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43906 | 1125 | 857104 | 4529 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 158515 | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0033538 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43906 | 434 | 856472 | 3655 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 69100 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033258 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 43906 | 825 | 853847 | 1962 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 62784 | Partly Cloudy-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032786 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE |  | 43906 | 136 | 853117 | 3669 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 102732 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032505 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43906 | 608 | 853778 | 5039 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 90702 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033892 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43906 | 339 | 853776 | 6701 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 50196 | Overcast-Fog-Snow;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 20-0034139 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43906 | 203 | 853408 | 2350 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 223250 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032941 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43906 | 1622 | 856516 | 7065 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 204885 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0034763 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43906 | 1210 | 855010 | 2990 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 5580 | Partly Cloudy-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033034 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43906 | 145 | 853406 | 6758 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 81096 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0034372 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43906 | 1633 | 856520 | 5970 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 52295 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 20-0034290 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 43906 | 2124 | 856066 | 2652 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 127296 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033105 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1103 | 153661103 | JUMPER |  | 43906 | 637 | 856550 | 2125 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12750 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033299 | OH | Sus | 0 | 2020 | MAR | Yes | None | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 43906 | 325 | 853410 | 5240 | Distribution Circuit | Vegetation | Tree - fell into line | 173 | 522520 | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0032487 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-1103 | 153661103 | FUSE |  | 43906 | 201 | 853532 | 4964 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 104244 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033319 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-1103 | 153661103 | JUMPER |  | 43906 | 635 | 856383 | 3352 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10056 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033203 | OH | Sus | 0 | 2020 | MAR | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | RECLOSER |  | 43906 | 638 | 853664 | 1733 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 144 | 249552 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032510 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | Yes
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 43905 | 2314 | 853246 | 5304 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 121992 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0033689 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | JUMPER |  | 43906 | 225 | s1522362 | 3535 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10605 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033237 | OH | Sus | 0 | 2020 | MAR | Yes | None | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43905 | 426 | 851930 | 3756 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 44220 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032255 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE |  | 43906 | 508 | 853663 | 4892 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 92931 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 20-0033460 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | RECLOSER |  | 43905 | 2049 | 852876 | 6982 | Distribution Circuit | Vegetation | Tree - fell into line | 1374 | 4796647 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032442 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 43906 | 1608 | 855559 | 3985 | Distribution Circuit | Vegetation | Tree - branch fell on line | 44 | 175337 | Partly Cloudy-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 20-0032989 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43905 | 640 | 859182 | 7520 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 30080 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0034377 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43905 | 1851 | 859233 | 8687 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 486472 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032421 | OH | Sus | 0 | 2020 | MAR | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | JUMPER |  | 43905 | 2058 | 856978 | 5436 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 59796 | Partly Cloudy-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033499 | OH | Sus | 0 | 2020 | MAR | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 43905 | 2058 | 853448 | 3854 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 142598 | Partly Cloudy-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 20-0032500 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43905 | 1851 | 859232 | 6956 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 69560 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032421 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 43905 | 2058 | 856974 | 4079 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 53027 | Partly Cloudy-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033496 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 43905 | 1811 | 852714 | 8270 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 16540 | Overcast-Fog-Rain;32-90 F | Insulator | Broken- wire on object | 20-0032409 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | RECLOSER |  | 43905 | 2332 | 852999 | 7926 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1150 | 4983415 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032454 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 43906 | 128 | 856985 | 2461 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 196880 | Partly Cloudy-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033507 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 43905 | 2331 | 857098 | 6610 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 19830 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 20-0033535 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43905 | 2133 | 852916 | 3890 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 38900 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032449 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43905 | 2355 | 853317 | 3988 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 235292 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032485 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43906 | 843 | 858365 | 6370 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 171990 | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0034083 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER |  | 43905 | 1851 | 852775 | 6784 | Distribution Circuit | Vegetation | Tree - fell into line | 1871 | 2447658 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032421 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43905 | 454 | 851838 | 3461 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 69220 | Snow-Snow-Snow-Overcast-Heavy Rain;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032352 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 43905 | 2355 | 855867 | 8182 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 297227 | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 20-0033051 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43905 | 2142 | 858565 | 6999 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 111984 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0033980 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 43906 | 302 | 858447 | 7708 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 23124 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0033917 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 43905 | 418 | 852509 | 2342 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 112416 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032368 | OH | Sus | 0 | 2020 | MAR | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | TRIP-SAVER |  | 43905 | 2119 | 853735 | 4254 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 182922 | Partly Cloudy-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032967 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | OCB |  | 43905 | 418 | 851598 | 865 | Distribution Circuit | Vegetation | Tree - fell into line | 773 | 409373 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032186 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | OCB |  | 43906 | 843 | 853342 | 4710 | Distribution Circuit | Vegetation | Tree - fell into line | 661 | 1193124 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032568 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER |  | 43905 | 2143 | 852888 | 5644 | Distribution Circuit | Vegetation | Tree - fell into line | 888 | 3331406 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032447 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43906 | 1643 | 855618 | 5937 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 53433 | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 20-0034613 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43906 | 1149 | 854533 | 5921 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 82894 | Partly Cloudy-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0034623 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | ECHO SUMMIT-1101 | 158031101 | RECLOSER |  | 43905 | 1627 | 852654 | 8744 | Distribution Circuit | Vegetation | Tree - fell into line | 121 | 950462 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032405 | OH | Sus | 0 | 2020 | MAR | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 43905 | 900 | 852178 | 2310 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 6930 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 20-0032379 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43906 | 739 | 855491 | 4761 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 209484 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032178 | OH | Sus | 0 | 2020 | MAR | Yes | None | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43906 | 646 | 855633 | 4814 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 28884 | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0032178 | OH | Sus | 0 | 2020 | MAR | Yes | None | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | SWITCH |  | 43906 | 207 | 853228 | 3747 | Distribution Circuit | Vegetation | Tree - fell into line | 270 | 918858 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 20-0032472 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43906 | 634 | 854436 | 4871 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 189969 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 20-0032178 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | SWITCH |  | 43906 | 207 | 857700 | 3747 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 558303 | Overcast-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0032472 | OH | Sus | 0 | 2020 | MAR | Yes | None | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | JUMPER |  | 43906 | 321 | 857681 | 5175 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 25875 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032178 | OH | Sus | 0 | 2020 | MAR | Yes | None | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43906 | 641 | 855133 | 3067 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 67474 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 20-0032178 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 43906 | 207 | 857171 | 3747 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 187350 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032472 | OH | Sus | 0 | 2020 | MAR | Yes | None | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 43906 | 124 | 858285 | 3882 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 46584 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032472 | OH | Sus | 0 | 2020 | MAR | Yes | None | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43906 | 646 | 855328 | 3425 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 68500 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032178 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 43906 | 124 | 858282 | 3874 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 34866 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032472 | OH | Sus | 0 | 2020 | MAR | Yes | None | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 43905 | 332 | 852117 | 8074 | Distribution Circuit | Vegetation | Tree - fell into line | 1075 | 2272586 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 20-0032178 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | JUMPER |  | 43905 | 8 | 860002 | 9554 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 28662 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0034821 | OH | Sus | 0 | 2020 | MAR | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43906 | 59 | 856589 | 3526 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 197456 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033335 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43906 | 59 | 857141 | 3626 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 36260 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032178 | OH | Sus | 0 | 2020 | MAR | Yes | None | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43905 | 332 | 852244 | 8005 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 8005 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032178 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 43905 | 332 | 858727 | 8107 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 105391 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 20-0032178 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | JUMPER |  | 43905 | 332 | 859896 | 9158 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 109896 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032178 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | JUMPER |  | 43905 | 332 | 859901 | 9336 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 9336 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 20-0032178 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | OTHER |  | 43906 | 238 | 856071 | 6734 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 150748 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033241 | OH | Sus | 0 | 2020 | MAR | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | SECTIONALIZER |  | 43906 | 301 | 855915 | 2472 | Distribution Circuit | Vegetation | Tree - fell into line | 347 | 857784 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032197 | OH | Sus | 0 | 2020 | MAR | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 43906 | 301 | 855967 | 4222 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 12666 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032197 | OH | Sus | 0 | 2020 | MAR | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 43906 | 300 | 855960 | 4223 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 38007 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032197 | OH | Sus | 0 | 2020 | MAR | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 43906 | 301 | 855957 | 4222 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 16888 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032197 | OH | Sus | 0 | 2020 | MAR | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 43906 | 300 | 855940 | 7860 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 365057 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 20-0032197 | OH | Sus | 0 | 2020 | MAR | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 43906 | 301 | 855939 | 4222 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8444 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032197 | OH | Sus | 0 | 2020 | MAR | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 43906 | 300 | 855925 | 4106 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 12318 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032197 | OH | Sus | 0 | 2020 | MAR | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 43906 | 359 | 854313 | 6626 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 28578 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032838 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 43905 | 117 | 851694 | 8011 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 360495 | Overcast-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 20-0032318 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | RECLOSER |  | 43905 | 1 | 851839 | 9760 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1984 | 2459609 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032197 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 43905 | 1 | 857662 | 6913 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 48391 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033683 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 43905 | 1 | 852708 | 9653 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 19306 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 20-0032197 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 43905 | 1 | 860020 | 9371 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 46855 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0034827 | OH | Sus | 0 | 2020 | MAR | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 43905 | 1 | 852561 | 8409 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 84090 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032197 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE |  | 43906 | 736 | 853688 | 4838 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 145140 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0033408 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 43906 | 532 | 856552 | 4839 | Distribution Circuit | Vegetation | Tree - branch fell on line | 127 | 614553 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0033301 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 43906 | 528 | 854039 | 4812 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 72180 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032638 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 43906 | 454 | 853911 | 5194 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 436296 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032550 | OH | Sus | 0 | 2020 | MAR | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 43906 | 213 | 856687 | 3575 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 143000 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0033368 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE |  | 43905 | 11 | 857955 | 6753 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 87789 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033776 | OH | Sus | 0 | 2020 | MAR | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE |  | 43905 | 11 | 857937 | 5331 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 127944 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033775 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | RECLOSER |  | 43905 | 11 | 851523 | 5185 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 383690 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032150 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 43905 | 2336 | 853014 | 2543 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 43231 | Partly Cloudy-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032497 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 43906 | 931 | 854043 | 3073 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 39949 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033070 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | Yes
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 43906 | 637 | 853567 | 533 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 27183 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032861 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | RECLOSER |  | 43905 | 242 | 851497 | 3793 | Distribution Circuit | Vegetation | Tree - fell into line | 182 | 679190 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032168 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER |  | 43905 | 1610 | 852650 | 6770 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 27080 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032390 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | DRUM-1101 | 152321101 | RECLOSER |  | 43906 | 3 | 853083 | 5161 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 244800 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032467 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 43905 | 410 | 852470 | 6609 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 72699 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032359 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 43905 | 410 | 852311 | 6666 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 173316 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032308 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | TRIP-SAVER |  | 43905 | 51 | 852104 | 6865 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 899315 | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0032253 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE |  | 43906 | 552 | 854505 | 1856 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7424 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0033331 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER |  | 43905 | 1603 | 852629 | 8323 | Distribution Circuit | Vegetation | Tree - fell into line | 1526 | 5618866 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032190 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER |  | 43905 | 303 | 851720 | 719 | Distribution Circuit | Vegetation | Tree - branch fell on line | 201 | 116997 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032190 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER |  | 43906 | 259 | 853310 | 933 | Distribution Circuit | Vegetation | Tree - branch fell on line | 114 | 86474 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032482 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 43905 | 303 | 852194 | 5271 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 31626 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032271 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1102 | 152101102 | FUSE |  | 43905 | 211 | 859270 | 12326 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 110934 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0034396 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1102 | 152101102 | FUSE |  | 43905 | 139 | 856794 | 12157 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 425429 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0033406 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE |  | 43905 | 723 | 851960 | 1569 | Distribution Circuit | Vegetation | Tree - branch fell on line | 92 | 172684 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032278 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | JUMPER |  | 43905 | 548 | 852112 | 1804 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1804 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032294 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | OCB |  | 43905 | 548 | 852521 | 9493 | Distribution Circuit | Vegetation | Tree - branch fell on line | 110 | 1044230 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032371 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE |  | 43905 | 548 | 855845 | 10770 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 118470 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 20-0033049 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER |  | 43905 | 335 | 851740 | 8129 | Distribution Circuit | Vegetation | Tree - branch fell on line | 83 | 673741 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032179 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | ALLEGHANY-1101 | 152101101 | FUSE |  | 43905 | 352 | 855408 | 8167 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 294012 | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 20-0032949 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE |  | 43906 | 1249 | 855135 | 2876 | Distribution Circuit | Equipment Failure/Involved | Overhead | 79 | 28279 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 20-0032948 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER |  | 43906 | 943 | 854176 | 2037 | Distribution Circuit | Vegetation | Tree - fell into line | 207 | 421659 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032659 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | OTHER |  | 43906 | 1115 | 855612 | 1696 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 119726 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 20-0033039 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | SWITCH |  | 43906 | 1254 | 855570 | 342 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 19836 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032820 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 43906 | 1304 | 855193 | 2966 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 11864 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033074 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 43905 | 1724 | 852681 | 5346 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 71772 | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0032943 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER |  | 43905 | 1629 | 852646 | 1183 | Distribution Circuit | Vegetation | Tree - fell into line | 418 | 87180 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032389 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | JUMPER |  | 43906 | 721 | 854552 | 4914 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4914 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032780 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 43906 | 942 | 855247 | 2040 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2040 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 20-0032864 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 43905 | 1216 | 858283 | 10454 | Distribution Circuit | Environmental/External | Ice or snow | 68 | 710872 | Overcast-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 20-0033878 | OH | Sus | 0 | 2020 | MAR | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | SWITCH |  | 43905 | 1216 | 852669 | 10454 | Distribution Circuit | Vegetation | Tree - fell into line | 303 | 3167562 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032397 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | JUMPER |  | 43905 | 2022 | 861151 | 9964 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 39856 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032324 | OH | Sus | 31497461 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | TRIP-SAVER |  | 43905 | 1028 | 852205 | 9209 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 136414 | Overcast-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0032314 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 43905 | 2022 | 852780 | 10052 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 1186136 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032324 | OH | Sus | 31497461 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 43905 | 2022 | 860019 | 8568 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 137088 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 20-0032324 | OH | Sus | 31497461 | 2020 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | JUMPER |  | 43905 | 2022 | 860024 | 9691 | Distribution Circuit | Vegetation | Tree - fell into line | 506 | 3619990 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 20-0032324 | OH | Sus | 31497461 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 43905 | 2022 | 860017 | 8193 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 24579 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032324 | OH | Sus | 31497461 | 2020 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 43905 | 1017 | 852659 | 9181 | Distribution Circuit | Vegetation | Tree - branch fell on line | 149 | 1367969 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 20-0032395 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | TRIP-SAVER |  | 43905 | 1017 | 861141 | 11517 | Distribution Circuit | Equipment Failure/Involved | Overhead | 111 | 1153473 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 20-0032395 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 43905 | 1015 | 856488 | 9053 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 434544 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033264 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 43905 | 1500 | 858792 | 10169 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 71183 | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0034170 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | JUMPER |  | 43905 | 2022 | 860021 | 9649 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 154384 | Overcast-Fog-Snow;Below 32 F | Transformer (OH) | Broken- wire on ground | 20-0032324 | OH | Sus | 31497461 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER |  | 43906 | 903 | s1521951 | 3363 | Distribution Circuit | Equipment Failure/Involved | Overhead | 153 | 514539 | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0032615 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | SWITCH |  | 43906 | 903 | 856996 | 3370 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 53920 | Overcast-Rain;32-90 F | Other | Broken- wire on object | 20-0033511 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | TRIP-SAVER |  | 43906 | 2006 | 856474 | 2397 | Distribution Circuit | Vegetation | Tree - branch fell on line | 296 | 609745 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | On Ground | 20-0033259 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | SWITCH |  | 43906 | 903 | 856887 | 3363 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 97527 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033446 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | OTHER |  | 43906 | 2104 | 856052 | 1345 | Distribution Circuit | Vegetation | Tree - fell into line | 422 | 16629 | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 20-0033093 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | Yes
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | OTHER |  | 43906 | 2104 | 856052 | 1345 | Distribution Circuit | Vegetation | Tree - fell into line | 422 | 16629 | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 20-0033093 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | Yes
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER |  | 43906 | 1111 | 854005 | 1365 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1671 | 1802670 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032745 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | OTHER |  | 43906 | 1138 | 855400 | 1542 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 9630 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032944 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER |  | 43906 | 924 | 854037 | 1693 | Distribution Circuit | Environmental/External | Ice or snow | 169 | 276258 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032644 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER |  | 43906 | 924 | 856512 | 3325 | Distribution Circuit | Vegetation | Tree - branch fell on line | 93 | 309225 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033279 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 43906 | 958 | 855637 | 1856 | Distribution Circuit | Environmental/External | Ice or snow | 23 | 42688 | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 20-0033012 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 43906 | 921 | 855281 | 1660 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 18260 | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0032877 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER |  | 43906 | 1020 | 854310 | 3892 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1549 | 809074 | Overcast-Fog-Drizzle;32-90 F | Insulator | Broken- wire on ground | 20-0032698 | OH | Sus | 0 | 2020 | MAR | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | SWITCH |  | 43906 | 924 | 854162 | 3337 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 286982 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032619 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 43906 | 1004 | 854276 | 2055 | Distribution Circuit | Vegetation | Tree - fell into line | 280 | 260278 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033016 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | SALT SPRINGS-2102 | 163692102 | RECLOSER |  | 43905 | 252 | 851712 | 896 | Distribution Circuit | Vegetation | Tree - fell into line | 2007 | 70311 | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 20-0032171 | OH | Sus | 0 | 2020 | MAR | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | SWITCH |  | 43906 | 1020 | 855397 | 1544 | Distribution Circuit | Vegetation | Tree - fell into line | 148 | 223706 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032698 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 43905 | 2133 | 855591 | 2590 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 318570 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032998 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 43906 | 2019 | 856797 | 2679 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 30338 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 20-0033407 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 43905 | 2133 | 856394 | 3873 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 228507 | Partly Cloudy;Below 32 F | Pole-Wood | Broken- wire on ground | 20-0033219 | OH | Sus | 0 | 2020 | MAR | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | SWITCH |  | 43905 | 2133 | 856707 | 4015 | Distribution Circuit | Vegetation | Tree - fell into line | 2388 | 2478465 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032698 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | SWITCH |  | 43905 | 2133 | 856782 | 4050 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 44550 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 20-0033405 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | SWITCH |  | 43906 | 853 | 858522 | 4931 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 187378 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 20-0032475 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | SWITCH |  | 43905 | 2133 | 853545 | 3907 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 277397 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 20-0032506 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 43906 | 132 | 854422 | 2562 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 235704 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 20-0032475 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | WEST POINT-1101 | 163201101 | RECLOSER |  | 43906 | 133 | 853127 | 3818 | Distribution Circuit | Vegetation | Tree - fell into line | 1123 | 2781300 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 20-0032475 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 43906 | 1021 | 855649 | 1420 | Distribution Circuit | Vegetation | Tree - bark fell into line | 8 | 11360 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033017 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | JUMPER |  | 43906 | 133 | 855444 | 2375 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 83125 | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0032959 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 43906 | 1945 | 855943 | 1277 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5108 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033064 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 43906 | 1020 | 855729 | 1543 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 15430 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033031 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 43906 | 546 | 855724 | 3344 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 50160 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033549 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 43906 | 132 | 856984 | 3888 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 128304 | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0033506 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | TRIP-SAVER |  | 43906 | 132 | 854556 | 3508 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 245560 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | On Ground | 20-0032781 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 43906 | 132 | 858136 | 4022 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8044 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033826 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | JUMPER |  | 43906 | 839 | 855307 | 1976 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9880 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 20-0032892 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | TRIP-SAVER |  | 43906 | 133 | 854512 | 5063 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 243024 | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0032767 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | JUMPER |  | 43906 | 828 | 855312 | 1598 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1598 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032895 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1101 | 254421101 | FUSE |  | 43906 | 1755 | 855747 | 1139 | Distribution Circuit | Environmental/External | Ice or snow | 105 | 119595 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033062 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE |  | 43906 | 2205 | 856083 | 877 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 8770 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0033116 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 43906 | 2326 | 856117 | 1174 | Distribution Circuit | Environmental/External | Ice or snow | 19 | 8698 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 20-0033114 | OH | Sus | 31497454 | 2020 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 43906 | 2316 | 856114 | 1226 | Distribution Circuit | Vegetation | Tree - fell into line | 148 | 141152 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 20-0033119 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | RECLOSER |  | 43906 | 2050 | 856033 | 2449 | Distribution Circuit | Vegetation | Tree - fell into line | 471 | 302468 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033085 | OH | Sus | 0 | 2020 | MAR | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 43906 | 2011 | 855996 | 2529 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 20232 | Overcast;Below 32 F | Pole-Wood | Broken- wire on ground | 20-0033439 | OH | Sus | 0 | 2020 | MAR | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER |  | 43906 | 1900 | 855894 | 2646 | Distribution Circuit | Equipment Failure/Involved | Overhead | 155 | 410130 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033056 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | CURTIS-1703 | 163351703 | FUSE |  | 43906 | 1632 | 855604 | 1450 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 17400 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 20-0033365 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE |  | 43906 | 1553 | 855519 | 1472 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 58880 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 20-0033035 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER |  | 43906 | 1708 | 855931 | 1369 | Distribution Circuit | Vegetation | Tree - fell into line | 600 | 302492 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 20-0033104 | OH | Sus | 31497445 | 2020 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | FUSE |  | 43906 | 1846 | 855866 | 1479 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 14790 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 20-0033080 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE |  | 43906 | 1735 | 855707 | 1120 | Distribution Circuit | Vegetation | Tree - branch fell on line | 173 | 55644 | Overcast-Drizzle;32-90 F | Transformer (OH) | Broken- wire on ground | 20-0033082 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | FUSE |  | 43906 | 1401 | 855544 | 221 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 8840 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032980 | OH | Sus | 0 | 2020 | MAR | Yes | None | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | RECLOSER |  | 43906 | 1400 | 855293 | 141 | Distribution Circuit | Vegetation | Tree - fell into line | 1290 | 171194 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032886 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | FUSE |  | 43906 | 1222 | 855076 | 411 | Distribution Circuit | Vegetation | Tree - branch fell on line | 117 | 48087 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032871 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | CURTIS-1704 | 163351704 | FUSE |  | 43906 | 1058 | 854413 | 384 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 19200 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032792 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 43906 | 2221 | 856299 | 2316 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8820 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0033154 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 43906 | 2202 | 856082 | 1110 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 62160 | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 20-0033122 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | JUMPER |  | 43906 | 759 | 855935 | 3596 | Distribution Circuit | Vegetation | Tree - fell into line | 331 | 489772 | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0032802 | OH | Sus | 0 | 2020 | MAR | Yes | None | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 43906 | 759 | 857018 | 3596 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 57536 | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0033513 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE |  | 43906 | 302 | 858445 | 5025 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 195975 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 20-0033918 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | SWITCH |  | 43906 | 528 | 858440 | 3708 | Distribution Circuit | Vegetation | Tree - branch fell on line | 96 | 355968 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0033916 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE |  | 43906 | 249 | 858438 | 4894 | Distribution Circuit | Vegetation | Tree - branch fell on line | 47 | 230018 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0033915 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | JUMPER |  | 43906 | 302 | 858448 | 5042 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 191596 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0033919 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE |  | 43905 | 2324 | 852994 | 5260 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 562820 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 20-0032488 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | SWITCH |  | 43906 | 302 | 857594 | 5042 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 35294 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0033657 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE |  | 43905 | 2332 | 854155 | 5233 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 559931 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 20-0032655 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE |  | 43906 | 302 | 858455 | 4881 | Distribution Circuit | Vegetation | Tree - branch fell on line | 45 | 219645 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0033920 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE |  | 43906 | 528 | 858471 | 4709 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 164815 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0033925 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE |  | 43906 | 528 | 858470 | 4913 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 9826 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0033924 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | SWITCH |  | 43906 | 528 | 853588 | 3683 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 268859 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032490 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE |  | 43906 | 54 | 853666 | 3389 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 193991 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0032807 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | OCB |  | 43906 | 746 | 853719 | 3220 | Distribution Circuit | Vegetation | Tree - fell into line | 461 | 808711 | Overcast-Fog-Snow;Below 32 F | Connector or Splice (OH) | Broken- wire on ground | 20-0032719 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE |  | 43906 | 746 | 855693 | 2263 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 63364 | Overcast-Fog;Below 32 F | Pole-Wood | Broken- wire on ground | 20-0033026 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER |  | 43906 | 302 | 853318 | 137 | Distribution Circuit | Environmental/External | Ice or snow | 224 | 30688 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032490 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER |  | 43905 | 1046 | 852234 | 501 | Distribution Circuit | Vegetation | Tree - fell into line | 687 | 344187 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0032283 | OH | Sus | 0 | 2020 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | PINECREST-0401 | 163160401 | FUSE |  | 43906 | 231 | 856884 | 3708 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 278100 | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 20-0033445 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE |  | 43906 | 739 | 855978 | 3184 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 235616 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 20-0033069 | OH | Sus | 0 | 2020 | MAR | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44129 | 2124 | 1129061 | 2372 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 7 | 16604 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0113194 | OH | Sus | 0 | 2020 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44129 | 2201 | 1128477 | 2309 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 18 | 41050 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 20-0112237 | OH | Sus | 0 | 2020 | OCT | Yes | Force Out | Yes | No
DE ANZA | Tier 3 | STELLING-1110 | 83481110 | SWITCH |  | 44118 | 2021 | 1118090 | 1387 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 205 | 221707 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 20-0108615 | OH | Sus | 0 | 2020 | OCT | Yes | Force Out | Yes | No
EAST BAY | Tier 2 | OAKLAND K-1104 | 12101104 | RECLOSER |  | 44129 | 2045 | 1127411 | 2627 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 421 | 1105967 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0113040 | OH | Sus | 0 | 2020 | OCT | Yes | Force Out | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1101 | 12101101 | FUSE |  | 44129 | 2029 | 1127371 | 1264 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 35 | 44240 | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 20-0113036 | OH | Sus | 8196861 | 2020 | OCT | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER |  | 44129 | 2041 | 1127408 | 956 | Distribution Circuit | Vegetation | Tree - branch fell on line | 634 | 604799 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0113188 | OH | Sus | 0 | 2020 | OCT | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | SWITCH |  | 44129 | 1626 | 1129200 | 2949 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 23592 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 20-0112668 | OH | Sus | 0 | 2020 | OCT | Yes | None | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 44126 | 1520 | 1123687 | 666 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2664 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 20-0111915 | OH | Sus | 0 | 2020 | OCT | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | SAN LUIS OBISPO-1104 | 182631104 | FUSE |  | 44126 | 1042 | 1123457 | 428 | Distribution Circuit | 3rd Party | Vehicle | 10 | 4280 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 20-0111660 | OH | Sus | 31516575 | 2020 | OCT | Yes | Three Phase Fault | Yes | No
MISSION | Tier 3 | CASTRO VALLEY-1108 | 14091108 | FUSE |  | 44129 | 2034 | 1129481 | 2669 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 2 | 5338 | Strong Winds; | Conductor- Overhead | Broken- wire on ground | 20-0112479 | OH | Sus | 0 | 2020 | OCT | Yes | Force Out | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | SWITCH |  | 44129 | 1908 | 1129915 | 2435 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 14 | 34090 | Strong Winds-Clear;32-90 F | Switch (OH) | Broken- wire on object | 20-0112802 | OH | Sus | 0 | 2020 | OCT | Yes | Force Out | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 44129 | 1600 | 1130362 | 3970 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 3970 | Strong Winds-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0112922 | OH | Sus | 0 | 2020 | OCT | Yes | Force Out | Yes | No
NORTH BAY | Tier 3 | MIDDLETOWN-1101 | 43141101 | RECLOSER |  | 44129 | 1214 | 1125266 | 4669 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 37352 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 20-0113107 | OH | Sus | 0 | 2020 | OCT | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE |  | 44129 | 1401 | 1128960 | 2932 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 35184 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 20-0112790 | OH | Sus | 0 | 2020 | OCT | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | BUCKS CREEK-1103 | 102211103 | TRIP-SAVER |  | 44129 | 1404 | 1129193 | 4173 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 88 | 367224 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 20-0112515 | OH | Sus | 0 | 2020 | OCT | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER |  | 44129 | 1404 | 1125462 | 3079 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 57 | 175503 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0112499 | OH | Sus | 0 | 2020 | OCT | Yes | Force Out | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 44129 | 2200 | 1129557 | 2395 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 34 | 81430 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0112869 | OH | Sus | 0 | 2020 | OCT | Yes | Force Out | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER |  | 44129 | 2200 | 1128948 | 2560 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 27 | 69120 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0112876 | OH | Sus | 0 | 2020 | OCT | Yes | Force Out | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 44118 | 2000 | 1119274 | 2528 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 2 | 5056 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0109619 | OH | Sus | 0 | 2020 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 44129 | 1524 | 1126421 | 3028 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1413 | 807455 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0112901 | OH | Sus | 0 | 2020 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1104 | 152481104 | FUSE |  | 44126 | 1506 | 1123685 | 645 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 34830 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 20-0111834 | OH | Sus | 31516613 | 2020 | OCT | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER |  | 44129 | 1901 | 1127114 | 3796 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1172 | 2961664 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0112950 | OH | Sus | 44505513 | 2020 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 44129 | 1901 | 1128301 | 3845 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 107 | 411415 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0112950 | OH | Sus | 44505513 | 2020 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | RECLOSER |  | 44129 | 1506 | 1126366 | 3130 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 50 | 156500 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0112699 | OH | Sus | 31516803 | 2020 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 44129 | 1506 | 1128408 | 3225 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 170574 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0112699 | OH | Sus | 31516803 | 2020 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 44129 | 1506 | 1128338 | 4266 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 46 | 196236 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0112699 | OH | Sus | 31516803 | 2020 | OCT | Yes | Open Circuit | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 44129 | 1601 | 1128716 | 1702 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 3 | 5106 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 20-0112356 | OH | Sus | 0 | 2020 | OCT | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | JUMPER |  | 44129 | 1601 | 1129353 | 2883 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 2883 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 20-0112356 | OH | Sus | 31516743 | 2020 | OCT | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE |  | 44129 | 1601 | 1129234 | 2662 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 27 | 71874 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0112152 | OH | Sus | 0 | 2020 | OCT | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER |  | 44129 | 1601 | 1126974 | 2662 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 330 | 878460 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0112152 | OH | Sus | 0 | 2020 | OCT | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 2 | RIO DEL MAR-0401 | 83260401 | FUSE |  | 44082 | 653 | 1060599 | 783 | Distribution Circuit | Vegetation | Tree - fell into line | 244 | 54525 | Clear;32-90 F | Transformer (OH) | Broken- wire on ground | 20-0094801 | OH | Sus | 0 | 2020 | SEP | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER |  | 44081 | 1830 | 1058925 | 1274 | Distribution Circuit | Vegetation | Tree - fell into line | 432 | 232395 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0094422 | OH | Sus | 31513173 | 2020 | SEP | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | JUMPER |  | 44101 | 1525 | 1095253 | 665 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 3990 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0102122 | OH | Sus | 0 | 2020 | SEP | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | ALHAMBRA-1105 | 14101105 | OTHER |  | 44101 | 1329 | 1095205 | 547 | Distribution Circuit | Vegetation | Tree - branch fell on line | 402 | 25980 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0102102 | OH | Sus | 31514676 | 2020 | SEP | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER |  | 44082 | 30 | 1060507 | 4134 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 144 | 595296 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 20-0094539 | OH | Sus | 0 | 2020 | SEP | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | CARLOTTA-1121 | 192291121 | FUSE |  | 44082 | 1232 | 1061112 | 1513 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 52955 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0095091 | OH | Sus | 0 | 2020 | SEP | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | OTHER |  | 44082 | 505 | 1060534 | 880 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 12320 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 20-0094798 | OH | Sus | 0 | 2020 | SEP | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2105 | 43432105 | FUSE |  | 44101 | 2313 | 1135835 | 55746 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 20 | 20 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 20-0109055 | OH | Sus | 0 | 2020 | SEP | Yes | Force Out | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2102 | 43432102 | FUSE |  | 44101 | 2316 | 1131008 | 45604 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 2 | Strong Winds-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0104159 | OH | Sus | 0 | 2020 | SEP | Yes | Force Out | Yes | No
NORTH BAY | Tier 2 | SILVERADO-2102 | 43432102 | FUSE |  | 44101 | 2316 | 1105797 | 44241 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 18 | 58 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0104159 | OH | Sus | 0 | 2020 | SEP | Yes | Force Out | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2102 | 43432102 | JUMPER |  | 44101 | 2316 | 1131003 | 48222 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 1 | Strong Winds-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0104159 | OH | Sus | 0 | 2020 | SEP | Yes | Force Out | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 44101 | 2302 | 1116159 | 51405 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 4 | 404 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0107853 | OH | Sus | 0 | 2020 | SEP | Yes | Force Out | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 44101 | 550 | 1119979 | 30664 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 1 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 20-0102013 | OH | Sus | 0 | 2020 | SEP | Yes | Force Out | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | SWITCH |  | 44101 | 550 | 1114904 | 19217 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 79 | 79 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0102013 | OH | Sus | 0 | 2020 | SEP | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER |  | 44101 | 435 | 1094960 | 2286 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 130 | 297180 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0101980 | OH | Sus | 0 | 2020 | SEP | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | VOLTA-1101 | 102541101 | FUSE |  | 44081 | 2224 | 1062021 | 2661 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 14 | 37254 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0094671 | OH | Sus | 0 | 2020 | SEP | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | RECLOSER |  | 44082 | 1025 | 1060925 | 673 | Distribution Circuit | Vegetation | Tree - fell into line | 256 | 172261 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0094909 | OH | Sus | 0 | 2020 | SEP | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE |  | 44082 | 3 | 1062325 | 3810 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 11 | 41910 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0094585 | OH | Sus | 0 | 2020 | SEP | Yes | None | Yes | No
SACRAMENTO | Tier 2 | PUTAH CREEK-1102 | 63681102 | FUSE |  | 44082 | 1835 | 1061525 | 1030 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4120 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 20-0095263 | OH | Sus | 0 | 2020 | SEP | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | JUMPER |  | 44082 | 110 | 1062402 | 3648 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 2 | 7296 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 20-0094533 | OH | Sus | 0 | 2020 | SEP | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER |  | 44101 | 1241 | 1095169 | 428 | Distribution Circuit | Vegetation | Tree - fell into line | 185 | 70828 | Clear;Above 90 | Conductor- Overhead | Broken- wire on ground | 20-0102103 | OH | Sus | 31514675 | 2020 | SEP | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 44412 | 755 | 1433409 | 610 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1970 | 512625 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0099476 | OH | Sus | 44932682 | 2021 | AUG | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 44420 | 924 | 1440947 | 1026 | Distribution Circuit | Vegetation | Tree - fell into line | 2224 | 800032 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0103505 | OH | Sus | 0 | 2021 | AUG | Yes | Line to Line | Yes | No
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | OTHER |  | 44412 | 1749 | 1434218 | 521 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 8749 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0100057 | OH | Sus | 44933289 | 2021 | AUG | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER |  | 44425 | 2123 | 1446130 | 1282 | Distribution Circuit | Vegetation | Tree - branch fell on line | 315 | 385400 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0106037 | OH | Sus | 0 | 2021 | AUG | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | OTHER |  | 44425 | 1741 | 1445387 | 1339 | Distribution Circuit | Vegetation | Tree - branch fell on line | 77 | 7928 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0106020 | OH | Sus | 0 | 2021 | AUG | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | MAPLE CREEK-1101 | 192101101 | OCB |  | 44412 | 55 | 1433291 | 102 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 150 | 6191 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0099421 | OH | Sus | 0 | 2021 | AUG | Yes | Three Phase Fault | Yes | No
LOS PADRES | Tier 2 | CAMBRIA-1102 | 182771102 | FUSE |  | 44420 | 1618 | 1441321 | 356 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 29548 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 21-0103873 | OH | Sus | 44945723 | 2021 | AUG | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | SAN RAFAEL-1104 | 42011104 | FUSE |  | 44409 | 2044 | 1428303 | 797 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 47023 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0098270 | OH | Sus | 44928050 | 2021 | AUG | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 44425 | 240 | 1457670 | 30921 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 47 | 94 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0106011 | OH | Sus | 0 | 2021 | AUG | Yes | Force Out | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | FUSE |  | 44420 | 1137 | 1441120 | 636 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 23532 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0103653 | OH | Sus | 0 | 2021 | AUG | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | OTHER |  | 44557 | 1311 | 1585799 | 643 | Distribution Circuit | Vegetation | Tree - branch fell on line | 139 | 80466 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161120 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | HATTON-1101 | 182291101 | FUSE |  | 44544 | 1212 | 1570827 | 1486 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 147114 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158200 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 44543 | 829 | 1566023 | 1817 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 14536 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157569 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | PACIFIC GROVE-0422 | 182440422 | FUSE |  | 44545 | 1951 | 1573791 | 206 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 19982 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158658 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 44544 | 1023 | 1571382 | 1006 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 23252 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158090 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | TRIP-SAVER |  | 44557 | 420 | 1584296 | 455 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 15925 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161023 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 44545 | 1604 | 1572971 | 1283 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3849 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158508 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 44543 | 1159 | 1567012 | 1966 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 18262 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157941 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 44543 | 1054 | 1566030 | 365 | Distribution Circuit | Vegetation | Tree - fell into line | 821 | 139418 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157122 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | JUMPER |  | 44543 | 1049 | 1567027 | 1599 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 15772 | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 21-0157221 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 44543 | 1153 | 1567103 | 1562 | Distribution Circuit | Vegetation | Tree - fell into line | 146 | 228052 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157286 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44543 | 1049 | 1566752 | 1803 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 77529 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157566 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44543 | 1119 | 1566883 | 1401 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 13483 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157314 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | OTHER |  | 44543 | 1415 | 1568069 | 1440 | Distribution Circuit | Equipment Failure/Involved | Overhead | 91 | 130905 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157449 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 44543 | 1804 | 1568369 | 1368 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 82080 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157555 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44557 | 142 | 1583811 | 944 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 7235 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161049 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | OTHER |  | 44543 | 1427 | 1568158 | 2674 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 99534 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157460 | OH | Sus | 35311163 | 2021 | DEC | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44543 | 1908 | 1568493 | 1312 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2624 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157899 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44543 | 1150 | 1566992 | 1269 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6345 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157254 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | JUMPER |  | 44543 | 1145 | 1566961 | 1554 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3108 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157467 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 44543 | 426 | 1565708 | 406 | Distribution Circuit | Vegetation | Tree - branch fell on line | 186 | 75516 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0156952 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44543 | 559 | 1565765 | 278 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 16680 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0156949 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 44543 | 447 | 1565720 | 3426 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 305082 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0157486 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER |  | 44543 | 1055 | 1566783 | 1794 | Distribution Circuit | Vegetation | Tree - fell into line | 257 | 51378 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0157409 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER |  | 44555 | 1124 | 1581319 | 304 | Distribution Circuit | Vegetation | Tree - branch fell on line | 140 | 24056 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160562 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | OCB |  | 44543 | 757 | 1565902 | 1955 | Distribution Circuit | Vegetation | Tree - branch fell on line | 658 | 124842 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157031 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 44545 | 2156 | 1573949 | 780 | Distribution Circuit | Environmental/External | Flood/Erosion | 95 | 23700 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 21-0158712 | OH | Sus | 35311077 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER |  | 44543 | 1050 | 1566736 | 1825 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 226300 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157115 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 44543 | 913 | 1566092 | 1836 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 40392 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157365 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44543 | 1113 | 1566863 | 1731 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 15579 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157354 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER |  | 44543 | 37 | 1565601 | 980 | Distribution Circuit | Vegetation | Tree - fell into line | 175 | 118292 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0156934 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44543 | 1139 | 1570210 | 1383 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 4149 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157862 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44543 | 705 | 1565815 | 625 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 30625 | Clear;32-90F | Conductor- Overhead | Broken- wire on object | 21-0157313 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER |  | 44543 | 1240 | 1567136 | 1913 | Distribution Circuit | Vegetation | Tree - fell into line | 292 | 32730 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157215 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER |  | 44543 | 1607 | 1568314 | 1296 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 7500 | Heavy Rain-Rain-Strong Winds-Combination;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157495 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44543 | 910 | 1566420 | 1964 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 16228 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0157242 | OH | Sus | 35311199 | 2021 | DEC | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER |  | 44543 | 420 | 1565705 | 818 | Distribution Circuit | Vegetation | Tree - fell into line | 1137 | 77785 | Heavy Rain-Rain-Combination;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0156928 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
DIABLO | Tier 2 | MORAGA-1104 | 13801104 | FUSE |  | 44543 | 1842 | 1568433 | 1340 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 41782 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157626 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 2 | EDES-1112 | 13681112 | FUSE |  | 44544 | 530 | 1569702 | 596 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2384 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157820 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAKLAND X-1106 | 12541106 | RECLOSER |  | 44543 | 2103 | 1568773 | 1150 | Distribution Circuit | Vegetation | Tree - fell into line | 435 | 171114 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157591 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAKLAND X-1106 | 12541106 | RECLOSER |  | 44559 | 1324 | 1588552 | 815 | Distribution Circuit | Vegetation | Tree - fell into line | 436 | 60902 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161583 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | RECLOSER |  | 44557 | 1133 | 1585637 | 1291 | Distribution Circuit | Vegetation | Tree - fell into line | 308 | 396524 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161082 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | RECLOSER |  | 44543 | 2302 | 1569566 | 1572 | Distribution Circuit | Vegetation | Tree - fell into line | 309 | 445820 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157873 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | FUSE |  | 44545 | 1419 | 1572813 | 1526 | Distribution Circuit | Vegetation | Tree - fell into line | 185 | 282310 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158646 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
FRESNO | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER |  | 44545 | 506 | 1572094 | 1271 | Distribution Circuit | Vegetation | Tree - fell into line | 280 | 506184 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158302 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | AUBERRY-1102 | 254151102 | FUSE |  | 44543 | 1217 | 1567063 | 214 | Distribution Circuit | 3rd Party | Other | 20 | 4280 | Clear;32-90F | Conductor- Overhead | On Ground | 21-0157266 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER |  | 44545 | 1346 | 1572754 | 1461 | Distribution Circuit | Vegetation | Tree - fell into line | 272 | 354000 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158460 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | RECLOSER |  | 44544 | 735 | 1570038 | 1970 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7880 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157833 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | RECLOSER |  | 44555 | 2353 | 1581956 | 540 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 22232 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160664 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | UKIAH-1114 | 42771114 | FUSE |  | 44557 | 842 | 1585209 | 1568 | Distribution Circuit | Environmental/External | Water | 5 | 7840 | Clear;32-90F | Conductor- Overhead | On Ground | 21-0161134 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | TRIP-SAVER |  | 44545 | 1422 | 1572748 | 1176 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 67032 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158521 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER |  | 44545 | 1514 | 1572899 | 1258 | Distribution Circuit | Vegetation | Tree - fell into line | 127 | 159766 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158490 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | FUSE |  | 44557 | 833 | 1585175 | 2100 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 37800 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161064 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER |  | 44559 | 1630 | 1588850 | 1151 | Distribution Circuit | Vegetation | Tree - fell into line | 252 | 19638 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161637 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1102 | 42661102 | FUSE |  | 44557 | 149 | 1583825 | 501 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 60120 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160947 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE |  | 44557 | 709 | 1584730 | 306 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 12240 | Clear;32-90F | Conductor- Overhead | On Ground | 21-0161012 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | OTHER |  | 44557 | 1228 | 1585745 | 329 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1316 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161157 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 44545 | 1517 | 1572900 | 363 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1815 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158512 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 44545 | 1046 | 1572419 | 347 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 15946 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158432 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 44557 | 928 | 1585319 | 3190 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6380 | Clear;32-90F | Conductor- Overhead | On Ground | 21-0161153 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 44556 | 1324 | 1582635 | 293 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 8204 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160782 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 44557 | 729 | 1584795 | 2101 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 39919 | Clear;32-90F | Conductor- Overhead | On Ground | 21-0161125 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 44556 | 1213 | 1582444 | 467 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1868 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160770 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 44557 | 120 | 1583733 | 3717 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 40887 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161173 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 44545 | 1515 | 1572894 | 1386 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 18018 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158540 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44557 | 747 | 1585050 | 1763 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 29971 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161042 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 44555 | 928 | 1581227 | 4577 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 9154 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160549 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44556 | 2252 | 1583132 | 6854 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 68540 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160873 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44557 | 623 | 1584580 | 2050 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 65600 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161055 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | OTHER |  | 44556 | 2355 | 1583430 | 3865 | Distribution Circuit | Environmental/External | Water | 46 | 177790 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161028 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER |  | 44543 | 319 | 1565670 | 478 | Distribution Circuit | Vegetation | Tree - fell into line | 375 | 163972 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0156920 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER |  | 44557 | 321 | 1585345 | 6338 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 259858 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161047 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE |  | 44557 | 853 | 1585105 | 4781 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 43029 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0161200 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 44555 | 158 | 1581130 | 714 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 19278 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160523 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1122 | 192321122 | FUSE |  | 44557 | 1218 | 1585717 | 5957 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 71484 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161382 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER |  | 44556 | 2354 | 1583012 | 10877 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 195596 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160887 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER |  | 44557 | 210 | 1583907 | 3799 | Distribution Circuit | Vegetation | Tree - fell into line | 368 | 916684 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160931 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | BRIDGEVILLE-1102 | 192461102 | FUSE |  | 44557 | 721 | 1585045 | 9135 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 63945 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161894 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | RECLOSER |  | 44556 | 2206 | 1583066 | 8268 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 272409 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0160861 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | JUMPER |  | 44555 | 953 | 1581225 | 1672 | Distribution Circuit | Environmental/External | Ice or snow | 8 | 10111 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160638 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | FUSE |  | 44556 | 1758 | 1582816 | 8693 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 78237 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160876 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | FUSE |  | 44557 | 246 | 1585593 | 2427 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4854 | Clear;32-90F | Conductor- Overhead | On Ground | 21-0160942 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HUMBOLDT BAY-1102 | 192341102 | FUSE |  | 44545 | 1135 | 1572633 | 425 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 16575 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158436 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HARRIS-1109 | 192431109 | FUSE |  | 44545 | 1127 | 1572477 | 344 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 9632 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158440 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44556 | 49 | 1582910 | 21918 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 432033 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160836 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44556 | 605 | 1590804 | 21602 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 475244 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0162002 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44556 | 605 | 1591918 | 21602 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 64806 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160689 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44556 | 605 | 1591907 | 21602 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 151214 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160689 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER |  | 44556 | 605 | 1582759 | 21602 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 1101702 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160733 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | SWITCH |  | 44556 | 605 | 1598569 | 21290 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 617410 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0007721 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44556 | 605 | 1590816 | 22218 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 150666 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0162007 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44556 | 605 | 1595718 | 21290 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 255480 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 22-0006408 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44556 | 605 | 1590810 | 21379 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 1090329 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0162005 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44556 | 605 | 1590815 | 21290 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 340640 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0162006 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | SWITCH |  | 44556 | 605 | 1582310 | 21382 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 915562 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0160689 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44556 | 605 | 1591926 | 21290 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 255480 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160689 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | SWITCH |  | 44556 | 906 | 1591498 | 13589 | Distribution Circuit | Environmental/External | Ice or snow | 14 | 190246 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160733 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44556 | 605 | 1594867 | 21290 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 894180 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0005982 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | JUMPER |  | 44556 | 255 | 1596874 | 21479 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 21479 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 22-0007076 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1101 | 192171101 | RECLOSER |  | 44555 | 2342 | 1589847 | 16687 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 282855 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161817 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | RECLOSER |  | 44556 | 914 | 1582761 | 13582 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 27164 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160733 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44556 | 255 | 1590910 | 19786 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 19786 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0162026 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44556 | 605 | 1596387 | 19595 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 176355 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0006686 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44556 | 255 | 1590732 | 19786 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 336362 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161990 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44556 | 605 | 1590742 | 19595 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 254735 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161992 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44556 | 605 | 1590027 | 16376 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 147384 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161872 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44556 | 605 | 1588786 | 16237 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 211081 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161621 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 44556 | 906 | 1592008 | 17709 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 35418 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160733 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER |  | 44556 | 605 | 1582071 | 6453 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 433195 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160689 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44556 | 906 | 1588569 | 10768 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 139984 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 21-0161589 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44556 | 906 | 1589499 | 14637 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 453747 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161750 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 44556 | 906 | 1582822 | 22264 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 89055 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160822 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44556 | 906 | 1588484 | 10768 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 376880 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0161565 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | JUMPER |  | 44556 | 906 | 1588473 | 10768 | Distribution Circuit | Environmental/External | Ice or snow | 31 | 266098 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160733 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 44556 | 906 | 1595832 | 19215 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 115290 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 22-0006459 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44556 | 906 | 1590031 | 10784 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 474496 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161873 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 44556 | 906 | 1591044 | 19215 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 38430 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0162059 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44556 | 906 | 1590034 | 10796 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 64776 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161876 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44556 | 906 | 1582731 | 14837 | Distribution Circuit | Environmental/External | Ice or snow | 27 | 400599 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160809 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1101 | 192171101 | JUMPER |  | 44556 | 906 | 1598217 | 20323 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 101615 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0161528 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44556 | 906 | 1585954 | 9144 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 347472 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161152 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER |  | 44556 | 906 | 1582758 | 6407 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 269094 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160733 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | JUMPER |  | 44556 | 906 | 1586154 | 8992 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 242784 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0161206 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 44556 | 906 | 1596859 | 20888 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 83552 | Clear;32-90F | Conductor- Overhead | On Ground | 22-0007069 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 44556 | 906 | 1593321 | 20888 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 41776 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0005365 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER |  | 44556 | 1918 | 1586127 | 6903 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 497997 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0160733 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 44556 | 906 | 1588298 | 18881 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 1045029 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161528 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 44556 | 113 | 1590119 | 21333 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 63999 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161897 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1101 | 192171101 | JUMPER |  | 44556 | 2033 | 1586310 | 4373 | Distribution Circuit | Vegetation | Tree - fell into line | 266 | 1163218 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160733 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 44556 | 2033 | 1588503 | 17050 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 68200 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0161574 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 44556 | 119 | 1581984 | 21328 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 383904 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160686 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 44556 | 906 | 1582324 | 16320 | Distribution Circuit | Vegetation | Tree - fell into line | 161 | 2503297 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160723 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 44556 | 119 | 1590117 | 22067 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 66201 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161895 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 44556 | 113 | 1590121 | 21333 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 42666 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161898 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1102 | 192171102 | FUSE |  | 44556 | 906 | 1590206 | 14619 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 190047 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161901 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1102 | 192171102 | JUMPER |  | 44556 | 906 | 1589715 | 14554 | Distribution Circuit | Environmental/External | Ice or snow | 41 | 549163 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160733 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1102 | 192171102 | FUSE |  | 44556 | 906 | 1582884 | 16099 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 144891 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160831 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1102 | 192171102 | FUSE |  | 44556 | 906 | 1591632 | 14861 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 59444 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0160733 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1102 | 192171102 | FUSE |  | 44556 | 906 | 1591710 | 14671 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 234736 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160733 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1101 | 192171101 | SWITCH |  | 44556 | 906 | 1587856 | 17658 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 494424 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161483 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 44556 | 906 | 1587864 | 17737 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 620795 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0161484 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1102 | 192171102 | FUSE |  | 44556 | 906 | 1591715 | 14405 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 244885 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160733 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1102 | 192171102 | FUSE |  | 44556 | 906 | 1591718 | 17708 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 318744 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160733 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1102 | 192171102 | RECLOSER |  | 44556 | 906 | 1582769 | 23440 | Distribution Circuit | Environmental/External | Ice or snow | 2 | 46880 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160733 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 44557 | 529 | 1584521 | 2126 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 173646 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161315 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 44556 | 2340 | 1589501 | 9734 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 155744 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161751 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 44557 | 625 | 1584526 | 13550 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 74402 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161348 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | JUMPER |  | 44556 | 906 | 1583044 | 14749 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 44247 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160857 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 44556 | 2340 | 1588927 | 11228 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 22456 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161657 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 44559 | 836 | 1588061 | 13510 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 108080 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161562 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER |  | 44556 | 2357 | 1587196 | 3817 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 194667 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160902 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 44556 | 906 | 1588773 | 17612 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 404345 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161619 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 44556 | 906 | 1590999 | 18930 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 738270 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0162047 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
KERN | Tier 2 | POSO MOUNTAIN-2101 | 253642101 | OTHER |  | 44556 | 2014 | 1582944 | 936 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 14040 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161040 | OH | Sus | 45102116 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
LOS PADRES | Tier 2 | FOOTHILL-1102 | 182951102 | OCB |  | 44543 | 2049 | 1568724 | 835 | Distribution Circuit | Vegetation | Tree - bark fell into line | 3482 | 490526 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157570 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE |  | 44543 | 1744 | 1568155 | 681 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 34050 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157493 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | RECLOSER |  | 44544 | 2028 | 1571835 | 1284 | Distribution Circuit | Equipment Failure/Involved | Overhead | 128 | 164352 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158236 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
MISSION | Tier 3 | TASSAJARA-2113 | 14662113 | FUSE |  | 44559 | 2239 | 1589247 | 692 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 692 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161713 | OH | Sus | 31588487 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | SAUSALITO-1102 | 42491102 | OTHER |  | 44543 | 1932 | 1568538 | 571 | Distribution Circuit | Vegetation | Tree - bark fell into line | 16 | 8366 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157610 | OH | Sus | 45092024 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | OLEMA-1101 | 42291101 | FUSE |  | 44545 | 1954 | 1573612 | 1460 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 17520 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158924 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 44545 | 1408 | 1572800 | 578 | Distribution Circuit | Vegetation | Tree - fell into line | 113 | 43607 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158500 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | LAS GALLINAS A-1105 | 42991105 | SWITCH |  | 44545 | 2030 | 1573742 | 619 | Distribution Circuit | Vegetation | Tree - fell into line | 1124 | 162020 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158652 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 44545 | 1836 | 1573324 | 321 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 21507 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158581 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | CALISTOGA-1101 | 42711101 | RECLOSER |  | 44557 | 1138 | 1585661 | 1747 | Distribution Circuit | Equipment Failure/Involved | Overhead | 128 | 17456 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161086 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1107 | 102911107 | FUSE |  | 44543 | 2206 | 1569135 | 2244 | Distribution Circuit | Environmental/External | Flood/Erosion | 48 | 31680 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0157673 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | OTHER |  | 44544 | 42 | 1569203 | 4889 | Distribution Circuit | Vegetation | Tree - fell into line | 200 | 556613 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157712 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 44559 | 1044 | 1588333 | 7460 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 96980 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161626 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 44543 | 2354 | 1571933 | 4041 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 52023 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0158242 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | JUMPER |  | 44545 | 1710 | 1573280 | 1150 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1150 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158566 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | OTHER |  | 44559 | 1221 | 1588470 | 263 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 5508 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161578 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 44559 | 1048 | 1588340 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1137 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161623 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | OCB |  | 44559 | 215 | 1587617 | 3730 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 401738 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161470 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE |  | 44543 | 1734 | 1568213 | 1396 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 10415 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157603 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1103 | 102911103 | FUSE |  | 44545 | 2250 | 1574003 | 805 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 9660 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158812 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE |  | 44559 | 415 | 1588921 | 7910 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 31640 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161654 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 44559 | 1559 | 1588818 | 3986 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 11735 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161642 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER |  | 44545 | 1816 | 1573287 | 2566 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 129568 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158609 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER |  | 44557 | 505 | 1584419 | 1856 | Distribution Circuit | Vegetation | Tree - fell into line | 370 | 212970 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160961 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER |  | 44559 | 540 | 1587784 | 6568 | Distribution Circuit | Vegetation | Tree - fell into line | 455 | 302624 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161480 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | FUSE |  | 44559 | 28 | 1588956 | 2459 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 199179 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161669 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | FUSE |  | 44559 | 429 | 1589741 | 7856 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 102128 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161470 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | JUMPER |  | 44559 | 1152 | 1588867 | 4440 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 15397 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161773 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE |  | 44559 | 321 | 1588462 | 2079 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 12474 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 21-0161560 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER |  | 44556 | 1438 | 1582627 | 10238 | Distribution Circuit | Vegetation | Tree - branch fell on line | 450 | 4330384 | Strong Winds-Snow-Sleet or Ice-Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160790 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | OTHER |  | 44543 | 1533 | 1567880 | 1754 | Distribution Circuit | Vegetation | Tree - fell into line | 393 | 683979 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157438 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 3 | BIG BEND-1102 | 103751102 | FUSE |  | 44559 | 1040 | 1588324 | 7159 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 71590 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161535 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | OTHER |  | 44543 | 1634 | 1569479 | 7033 | Distribution Circuit | Vegetation | Tree - fell into line | 405 | 764887 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157748 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | FUSE |  | 44543 | 1634 | 1576352 | 7252 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 572908 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157748 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | FUSE |  | 44543 | 1634 | 1576356 | 8332 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 33454 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157748 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER |  | 44543 | 1040 | 1566698 | 11638 | Distribution Circuit | Vegetation | Tree - fell into line | 171 | 1677448 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157106 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | OTHER |  | 44556 | 923 | 1582593 | 377 | Distribution Circuit | Environmental/External | Ice or snow | 6 | 2262 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160774 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 3 | PARADISE-1104 | 102831104 | FUSE |  | 44543 | 1345 | 1567443 | 1591 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7955 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157674 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | BUTTE-1105 | 103081105 | OTHER |  | 44543 | 1459 | 1567840 | 1518 | Distribution Circuit | Vegetation | Tree - fell into line | 198 | 65196 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157442 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 3 | PARADISE-1105 | 102831105 | RECLOSER |  | 44543 | 812 | 1565934 | 1929 | Distribution Circuit | Vegetation | Tree - fell into line | 399 | 126371 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0156977 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | FUSE |  | 44559 | 1358 | 1588874 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 960 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161638 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BIG BEND-1101 | 103751101 | TRANSFORMER |  | 44557 | 840 | 1585198 | 6007 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 18021 | Clear;32-90F | Conductor- Overhead | On Ground | 21-0161077 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | SYCAMORE CREEK-1111 | 102971111 | RECLOSER |  | 44559 | 357 | 1587736 | 458 | Distribution Circuit | Vegetation | Tree - fell into line | 535 | 213774 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0161475 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1105 | 102831105 | FUSE |  | 44545 | 1954 | 1573940 | 2285 | Distribution Circuit | Vegetation | Tree - fell into line | 296 | 659744 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0159303 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | OTHER |  | 44559 | 639 | 1587908 | 413 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4776 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161488 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | FUSE |  | 44545 | 1952 | 1574004 | 1389 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 100008 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0158627 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | FUSE |  | 44559 | 853 | 1588076 | 2058 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 128180 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161635 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | OTHER |  | 44545 | 1406 | 1575134 | 3128 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 107106 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158970 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE |  | 44559 | 218 | 1587678 | 892 | Distribution Circuit | Vegetation | Tree - fell into line | 167 | 114987 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161537 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | RECLOSER |  | 44559 | 639 | 1587910 | 1902 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1008 | 138216 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161499 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | FUSE |  | 44545 | 1406 | 1575030 | 3303 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 72666 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158955 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE |  | 44543 | 1438 | 1567626 | 312 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 5928 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157433 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE |  | 44545 | 1911 | 1574524 | 5410 | Distribution Circuit | Environmental/External | Ice or snow | 21 | 113610 | Strong Winds-Snow-Sleet or Ice-Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0158600 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | OCB |  | 44545 | 1953 | 1573644 | 4464 | Distribution Circuit | Vegetation | Tree - fell into line | 675 | 1439322 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158629 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | OCB |  | 44545 | 1952 | 1573542 | 2293 | Distribution Circuit | Vegetation | Tree - fell into line | 1580 | 2581617 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158627 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER |  | 44545 | 1911 | 1573477 | 5557 | Distribution Circuit | Vegetation | Tree - fell into line | 286 | 1562467 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0158600 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | JUMPER |  | 44545 | 1911 | 1575795 | 5410 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 64920 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0159326 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE |  | 44545 | 1929 | 1574847 | 1397 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 12573 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158629 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | SWITCH |  | 44545 | 1729 | 1574343 | 5636 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1407 | 2011974 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158629 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | FUSE |  | 44543 | 424 | 1565729 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 34086 | Clear;32-90F | Conductor- Overhead | On Ground | 21-0156941 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | JUMPER |  | 44559 | 528 | 1587846 | 2044 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 55771 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161552 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | FUSE |  | 44557 | 1523 | 1586004 | 1663 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 144681 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161201 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | FUSE |  | 44545 | 2033 | 1573782 | 3906 | Distribution Circuit | Vegetation | Tree - fell into line | 513 | 487798 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158668 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | JUMPER |  | 44545 | 1939 | 1575086 | 2743 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2743 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158962 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | FUSE |  | 44557 | 16 | 1585486 | 2176 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 13056 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161067 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | FUSE |  | 44557 | 16 | 1585683 | 2256 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 108288 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0161090 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | FUSE |  | 44545 | 2225 | 1574351 | 2090 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 98230 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158958 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | SWITCH |  | 44557 | 16 | 1585290 | 6559 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 334509 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0160898 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | FUSE |  | 44556 | 2341 | 1589973 | 8013 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 80130 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161853 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | FUSE |  | 44557 | 16 | 1589979 | 6559 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 177093 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161855 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | FUSE |  | 44556 | 2322 | 1589982 | 6634 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 185752 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161857 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | GRAYS FLAT-0401 | 102530401 | JUMPER |  | 44555 | 1642 | 1581491 | 198 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 594 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160600 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | ORO FINO-1102 | 103031102 | RECLOSER |  | 44545 | 703 | 1572142 | 540 | Distribution Circuit | Environmental/External | Ice or snow | 251 | 134589 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 21-0158312 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ORO FINO-1102 | 103031102 | RECLOSER |  | 44544 | 26 | 1569156 | 8498 | Distribution Circuit | Vegetation | Tree - fell into line | 311 | 743187 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157685 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER |  | 44545 | 1257 | 1572643 | 3080 | Distribution Circuit | Vegetation | Tree - fell into line | 1388 | 4100553 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0158526 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | OTHER |  | 44557 | 242 | 1584041 | 375 | Distribution Circuit | Equipment Failure/Involved | Overhead | 631 | 236625 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160981 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | OTHER |  | 44544 | 101 | 1569214 | 1253 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 10120 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157724 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | FUSE |  | 44544 | 657 | 1570890 | 1979 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 69265 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158105 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | FUSE |  | 44545 | 2003 | 1573978 | 2578 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 90230 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158719 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | FUSE |  | 44545 | 1910 | 1573977 | 3784 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 52976 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0158719 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | RECLOSER |  | 44544 | 222 | 1569053 | 1062 | Distribution Circuit | Vegetation | Tree - fell into line | 302 | 297104 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0157716 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | RECLOSER |  | 44544 | 459 | 1569049 | 4709 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 187742 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157775 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | FUSE |  | 44544 | 459 | 1571966 | 6368 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 292928 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0157775 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | FUSE |  | 44544 | 459 | 1572169 | 5055 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 283080 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0157775 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | FUSE |  | 44543 | 2316 | 1570599 | 5404 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 308028 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0157775 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | WILDWOOD-1101 | 103611101 | RECLOSER |  | 44545 | 2238 | 1573993 | 2247 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 96105 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158723 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER |  | 44543 | 1406 | 1567506 | 8680 | Distribution Circuit | Environmental/External | Ice or snow | 781 | 4609174 | Sleet or Ice-Strong Winds-Snow-Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157345 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER |  | 44544 | 201 | 1569263 | 734 | Distribution Circuit | Vegetation | Tree - fell into line | 239 | 175426 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157708 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | FUSE |  | 44544 | 200 | 1571390 | 2091 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2091 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157708 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | OTHER |  | 44545 | 1826 | 1574444 | 1405 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 33975 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158808 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | VOLTA-1102 | 102541102 | RECLOSER |  | 44545 | 2000 | 1574165 | 1253 | Distribution Circuit | Vegetation | Tree - fell into line | 415 | 516387 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158759 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1102 | 102541102 | FUSE |  | 44545 | 1855 | 1576096 | 4039 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 153482 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0158580 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1102 | 102541102 | OTHER |  | 44544 | 648 | 1569885 | 1364 | Distribution Circuit | Vegetation | Tree - fell into line | 189 | 261471 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157915 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | VOLTA-1102 | 102541102 | FUSE |  | 44545 | 1855 | 1575911 | 3937 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 159773 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158580 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1102 | 102541102 | FUSE |  | 44544 | 601 | 1571437 | 2123 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 99883 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157915 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | OTHER |  | 44544 | 28 | 1569157 | 2456 | Distribution Circuit | Vegetation | Tree - fell into line | 243 | 596808 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157808 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | FUSE |  | 44545 | 1929 | 1575720 | 2361 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2361 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158759 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | JUMPER |  | 44545 | 1929 | 1574603 | 2351 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 171623 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158759 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1102 | 103401102 | FUSE |  | 44543 | 826 | 1565969 | 893 | Distribution Circuit | Environmental/External | Water | 16 | 2483 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0157006 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1102 | 103381102 | RECLOSER |  | 44545 | 2038 | 1573775 | 2800 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 19600 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158669 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1101 | 103381101 | RECLOSER |  | 44545 | 1709 | 1573029 | 1356 | Distribution Circuit | Environmental/External | Ice or snow | 73 | 94668 | Snow-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158536 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | WHITMORE-1101 | 103601101 | FUSE |  | 44545 | 1616 | 1572991 | 1258 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 69190 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158604 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | CEDAR CREEK-1101 | 103321101 | OTHER |  | 44545 | 2051 | 1573820 | 1074 | Distribution Circuit | Vegetation | Tree - fell into line | 212 | 219889 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158765 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | FUSE |  | 44545 | 1803 | 1574462 | 2700 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 275400 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0158638 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE |  | 44545 | 1740 | 1573214 | 1346 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 9422 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158769 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | OTHER |  | 44545 | 1811 | 1574939 | 2443 | Distribution Circuit | Environmental/External | Ice or snow | 103 | 246841 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158929 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 2 | BURNEY-1101 | 103311101 | RECLOSER |  | 44543 | 2322 | 1569056 | 1212 | Distribution Circuit | Vegetation | Tree - fell into line | 143 | 115347 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157662 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | FUSE |  | 44545 | 1700 | 1573112 | 1404 | Distribution Circuit | Vegetation | Tree - fell into line | 165 | 184100 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0158545 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE |  | 44557 | 952 | 1585379 | 2009 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 4018 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0161143 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | JUMPER |  | 44543 | 616 | 1566456 | 1224 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 58752 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157072 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE |  | 44543 | 1634 | 1568549 | 1338 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 46206 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157683 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 44543 | 952 | 1567887 | 671 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 53246 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157413 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 44559 | 1852 | 1588999 | 1804 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5412 | Rain-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161700 | OH | Sus | 45103202 | 2021 | DEC | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | TRIP-SAVER |  | 44545 | 1857 | 1573390 | 909 | Distribution Circuit | Vegetation | Tree - branch fell on line | 43 | 39087 | Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158661 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | DOBBINS-1101 | 153741101 | RECLOSER |  | 44543 | 2102 | 1568768 | 945 | Distribution Circuit | Vegetation | Tree - fell into line | 169 | 25641 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157580 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
SACRAMENTO | Tier 3 | DOBBINS-1101 | 153741101 | FUSE |  | 44557 | 30 | 1583313 | 2521 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 88235 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161036 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SACRAMENTO | Tier 3 | DOBBINS-1101 | 153741101 | JUMPER |  | 44557 | 13 | 1587550 | 3835 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 15340 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161036 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SACRAMENTO | Tier 3 | DOBBINS-1101 | 153741101 | JUMPER |  | 44557 | 30 | 1587553 | 3687 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 7374 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161036 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SAN JOSE | Tier 2 | MORGAN HILL-2105 | 83242105 | FUSE |  | 44557 | 1446 | 1585919 | 390 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 16380 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161149 | OH | Sus | 45102203 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 44557 | 239 | 1593432 | 12355 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 284165 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0160970 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 44557 | 516 | 1588648 | 9459 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 217557 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160970 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 44557 | 239 | 1590937 | 10641 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 74487 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0162032 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | OTHER |  | 44543 | 1930 | 1569069 | 1418 | Distribution Circuit | Vegetation | Tree - fell into line | 718 | 758950 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157774 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER |  | 44543 | 1120 | 1566809 | 457 | Distribution Circuit | Equipment Failure/Involved | Overhead | 718 | 183289 | Strong Winds-Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0157144 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 44557 | 34 | 1592537 | 10880 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 272000 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0005214 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 44557 | 646 | 1587302 | 9293 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 83637 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160970 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE |  | 44543 | 1252 | 1567170 | 1549 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 17039 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157357 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 44557 | 516 | 1589854 | 5053 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 171802 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160970 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | SWITCH |  | 44557 | 639 | 1586153 | 3568 | Distribution Circuit | Vegetation | Tree - fell into line | 401 | 1430768 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160982 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 44557 | 639 | 1585363 | 4675 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 56100 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161052 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 44557 | 639 | 1586008 | 3558 | Distribution Circuit | Vegetation | Tree - fell into line | 280 | 996240 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161162 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 44557 | 639 | 1586055 | 3558 | Distribution Circuit | Vegetation | Tree - fell into line | 136 | 478184 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160982 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 44544 | 426 | 1569579 | 1834 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 23842 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157973 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | JUMPER |  | 44557 | 639 | 1586017 | 6161 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 18483 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161165 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | SWITCH |  | 44557 | 728 | 1590582 | 5937 | Distribution Circuit | Vegetation | Tree - branch fell on line | 469 | 962780 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161001 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 44544 | 542 | 1569727 | 716 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5728 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158024 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 44557 | 639 | 1585943 | 4804 | Distribution Circuit | Vegetation | Tree - bark fell into line | 70 | 336280 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161148 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER |  | 44557 | 527 | 1583522 | 9190 | Distribution Circuit | Vegetation | Tree - fell into line | 667 | 3591051 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160970 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | JUMPER |  | 44557 | 728 | 1588553 | 8232 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 16464 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161020 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 44557 | 728 | 1591643 | 7825 | Distribution Circuit | Vegetation | Tree - fell into line | 525 | 4108125 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161001 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 44557 | 728 | 1590458 | 7833 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 187992 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 22-0004987 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | DIAMOND SPRINGS-1103 | 152261103 | FUSE |  | 44557 | 1028 | 1585503 | 4895 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 195800 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161096 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE |  | 44557 | 728 | 1591487 | 8232 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 485688 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005017 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 44557 | 700 | 1590245 | 9259 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 370360 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161949 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | OTHER |  | 44557 | 701 | 1590894 | 10484 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 136292 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0162020 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1103 | 153661103 | FUSE |  | 44557 | 728 | 1588711 | 8232 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 49392 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161020 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | APPLE HILL-1103 | 153661103 | FUSE |  | 44557 | 728 | 1585354 | 8232 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 172872 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161048 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 44557 | 728 | 1587455 | 5024 | Distribution Circuit | Equipment Failure/Involved | Overhead | 146 | 733504 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160970 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 44557 | 728 | 1592487 | 12326 | Distribution Circuit | Vegetation | Tree - fell into line | 409 | 5040398 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161001 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1112 | 153081112 | FUSE |  | 44544 | 712 | 1569952 | 2072 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 4144 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158119 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | OTHER |  | 44544 | 417 | 1570166 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 8061 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157855 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1112 | 153081112 | JUMPER |  | 44557 | 1905 | 1587223 | 1501 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 15010 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161237 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 44557 | 728 | 1592107 | 12336 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 135696 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161001 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1112 | 153081112 | FUSE |  | 44557 | 1905 | 1587073 | 7223 | Distribution Circuit | Vegetation | Tree - fell into line | 174 | 1044402 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161237 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 44557 | 728 | 1592763 | 10761 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 64566 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161001 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1112 | 153081112 | FUSE |  | 44557 | 1905 | 1587220 | 10029 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 80232 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161237 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1111 | 153081111 | FUSE |  | 44557 | 2144 | 1586361 | 2374 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 97547 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161328 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE |  | 44557 | 728 | 1591588 | 8934 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 17868 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161020 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE |  | 44557 | 728 | 1590619 | 8232 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 24696 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0161020 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | JUMPER |  | 44557 | 728 | 1590790 | 7913 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 253216 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161020 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 44557 | 728 | 1590701 | 7767 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 427185 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160970 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE |  | 44557 | 728 | 1591737 | 9182 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 275460 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161020 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE |  | 44557 | 619 | 1585309 | 9433 | Distribution Circuit | Equipment Failure/Involved | Overhead | 118 | 956294 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161034 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 44543 | 2348 | 1569127 | 1296 | Distribution Circuit | Vegetation | Tree - fell into line | 1994 | 1735810 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 21-0157672 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 44557 | 443 | 1585011 | 10781 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 442021 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005082 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 44557 | 728 | 1591434 | 8973 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 367893 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005031 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | JUMPER |  | 44557 | 728 | 1588991 | 6371 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6371 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161021 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 44557 | 420 | 1585009 | 7970 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 151430 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161962 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | JUMPER |  | 44557 | 728 | 1586124 | 3509 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 7018 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160910 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | SWITCH |  | 44557 | 728 | 1586145 | 3422 | Distribution Circuit | Equipment Failure/Involved | Overhead | 208 | 711776 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160910 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 44543 | 2159 | 1568893 | 2301 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 23010 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0157671 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 44557 | 728 | 1592304 | 9324 | Distribution Circuit | Vegetation | Tree - fell into line | 167 | 1557108 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161020 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44557 | 728 | 1586128 | 4889 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 205338 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0160910 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 44557 | 630 | 1585012 | 9382 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 140730 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161021 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 44557 | 344 | 1592286 | 12414 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 335178 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005157 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 44557 | 728 | 1585850 | 13024 | Distribution Circuit | Vegetation | Tree - bark fell into line | 27 | 351648 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161124 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 44557 | 728 | 1588664 | 9324 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 307692 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161021 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 44543 | 2242 | 1568985 | 2313 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 76032 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0157965 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 44557 | 728 | 1588816 | 6438 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 515040 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161021 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 44557 | 728 | 1594073 | 13526 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 284046 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005700 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | SWITCH |  | 44556 | 2143 | 1593779 | 12209 | Distribution Circuit | Environmental/External | Ice or snow | 240 | 2930160 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161001 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 44557 | 728 | 1592779 | 10501 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 84008 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161001 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 44557 | 233 | 1590314 | 12376 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 1498095 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161928 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | Yes
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | SWITCH |  | 44557 | 728 | 1592773 | 13579 | Distribution Circuit | Vegetation | Tree - fell into line | 221 | 2713911 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161001 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1110 | 153081110 | RECLOSER |  | 44544 | 427 | 1569588 | 3530 | Distribution Circuit | Vegetation | Tree - fell into line | 223 | 320713 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0157770 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 44557 | 344 | 1588383 | 12421 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 12421 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161021 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 44557 | 716 | 1590201 | 7838 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 164598 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161021 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 44557 | 728 | 1592770 | 13157 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 223669 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161001 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1110 | 153081110 | FUSE |  | 44544 | 427 | 1571005 | 2082 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 6246 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158045 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | RECLOSER |  | 44543 | 1725 | 1568182 | 1426 | Distribution Circuit | Vegetation | Tree - fell into line | 616 | 351486 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157469 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER |  | 44557 | 412 | 1583446 | 13709 | Distribution Circuit | Equipment Failure/Involved | Overhead | 211 | 2892059 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160954 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1110 | 153081110 | FUSE |  | 44557 | 1905 | 1586249 | 2753 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 27898 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161330 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | RECLOSER |  | 44543 | 1922 | 1568653 | 1241 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 142715 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157550 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | JUMPER |  | 44557 | 716 | 1594631 | 11771 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 58855 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005832 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 44557 | 420 | 1584925 | 13313 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 119817 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005198 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | SWITCH |  | 44556 | 2253 | 1583146 | 6409 | Distribution Circuit | Vegetation | Tree - fell into line | 243 | 776164 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160874 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 44557 | 728 | 1592245 | 9214 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 635766 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005149 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 44557 | 728 | 1590825 | 10417 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 156255 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0162009 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | EL DORADO PH-2101 | 152762101 | SWITCH |  | 44544 | 220 | 1569285 | 3888 | Distribution Circuit | Environmental/External | Ice or snow | 166 | 696764 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157715 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | Yes
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 44557 | 728 | 1591750 | 11964 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 203388 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0161001 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 44557 | 728 | 1590846 | 11890 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 249690 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0162013 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44557 | 727 | 1587380 | 4689 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 14067 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160874 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 44557 | 619 | 1591817 | 12123 | Distribution Circuit | Vegetation | Tree - fell into line | 458 | 87567 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161021 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 44557 | 619 | 1588803 | 6198 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 415266 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161021 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 44557 | 522 | 1588017 | 6518 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 71698 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161021 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44557 | 659 | 1589554 | 16337 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 196044 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160910 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44544 | 1038 | 1570664 | 1773 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 12066 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0158220 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 44557 | 56 | 1583064 | 13473 | Distribution Circuit | Vegetation | Tree - fell into line | 1484 | 8291245 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160910 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | JUMPER |  | 44557 | 56 | 1590633 | 15321 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 168531 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161974 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44557 | 127 | 1583738 | 12566 | Distribution Circuit | Vegetation | Tree - branch fell on line | 470 | 685690 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160910 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | OTHER |  | 44544 | 1906 | 1571824 | 1060 | Distribution Circuit | Equipment Failure/Involved | Overhead | 555 | 187228 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157752 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44557 | 455 | 1590711 | 13735 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 13735 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160910 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44557 | 56 | 1590638 | 18104 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 36208 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161976 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | JUMPER |  | 44557 | 56 | 1590639 | 17849 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 17849 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161977 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | SWITCH |  | 44557 | 56 | 1589743 | 13651 | Distribution Circuit | Environmental/External | Ice or snow | 186 | 2119070 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160910 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44557 | 637 | 1589949 | 16275 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 480097 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160875 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44556 | 2320 | 1591696 | 8369 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 108797 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005066 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44556 | 2333 | 1593703 | 18239 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 200629 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005531 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44556 | 2320 | 1591695 | 16742 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 50226 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0005065 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44556 | 2333 | 1593277 | 18230 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 692740 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005346 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | JUMPER |  | 44556 | 2304 | 1592566 | 14007 | Distribution Circuit | Environmental/External | Ice or snow | 462 | 331580 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160910 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | JUMPER |  | 44556 | 2320 | 1591688 | 16961 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 288337 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005060 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44556 | 2324 | 1591692 | 16918 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 16918 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005061 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44556 | 2320 | 1589533 | 14047 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 168564 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160875 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44557 | 825 | 1585256 | 12063 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 36189 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0006139 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44556 | 2320 | 1590842 | 11091 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 343821 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160875 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER |  | 44556 | 2308 | 1583167 | 12594 | Distribution Circuit | Vegetation | Tree - fell into line | 542 | 2629912 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160875 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44544 | 112 | 1569218 | 2117 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 23792 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158128 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44556 | 2320 | 1593967 | 15522 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 108654 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005678 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44556 | 2320 | 1593964 | 12546 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 526932 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005677 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44557 | 56 | 1593411 | 18092 | Distribution Circuit | Environmental/External | Ice or snow | 13 | 235196 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005405 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44556 | 2147 | 1590839 | 15696 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 497932 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0162011 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44556 | 2320 | 1593969 | 15386 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 246176 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0005680 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44556 | 2320 | 1593970 | 14008 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 378216 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005681 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44556 | 2308 | 1592681 | 16696 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 525238 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 21-0160875 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44556 | 2308 | 1594010 | 18315 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 750653 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005692 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44556 | 2308 | 1583079 | 15487 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 556407 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160875 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44556 | 2308 | 1592665 | 15175 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 30350 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160875 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44556 | 2308 | 1592634 | 11163 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 636291 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160875 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44556 | 2308 | 1594009 | 15367 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 184404 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005691 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44556 | 2308 | 1595188 | 13832 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 138320 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0006194 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 44556 | 33 | 1583364 | 18376 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 506520 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160905 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44544 | 407 | 1569541 | 1870 | Distribution Circuit | Vegetation | Tree - branch fell on line | 175 | 327250 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158366 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44556 | 2120 | 1582996 | 14185 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 354625 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0005423 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44556 | 2308 | 1595186 | 12693 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 266553 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0006193 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44556 | 2305 | 1593479 | 11101 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 44404 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005435 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44557 | 33 | 1596458 | 16768 | Distribution Circuit | Vegetation | Tree - grew into line | 34 | 570112 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0006737 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44557 | 408 | 1593502 | 10752 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 258048 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005439 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44557 | 33 | 1597192 | 19666 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 471984 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007280 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44557 | 33 | 1596460 | 15370 | Distribution Circuit | Environmental/External | Ice or snow | 22 | 338140 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0006739 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44557 | 217 | 1593504 | 15346 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 1052491 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0005441 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44544 | 353 | 1569500 | 1024 | Distribution Circuit | Vegetation | Tree - branch fell on line | 87 | 78316 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158005 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | SWITCH |  | 44557 | 33 | 1597579 | 19667 | Distribution Circuit | Vegetation | Tree - fell into line | 159 | 3127053 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160905 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44557 | 835 | 1597293 | 16454 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 246810 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007327 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44557 | 33 | 1597621 | 19441 | Distribution Circuit | Environmental/External | Ice or snow | 57 | 1108137 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0007536 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44557 | 33 | 1597182 | 19666 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 117996 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007276 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44556 | 2302 | 1583173 | 20865 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 318720 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007081 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44556 | 2305 | 1593509 | 11140 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 44560 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005443 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44557 | 220 | 1593513 | 10996 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 98964 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005444 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | JUMPER |  | 44557 | 220 | 1594091 | 18078 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 144624 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005705 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44557 | 305 | 1593517 | 16710 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 334200 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0005448 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44557 | 228 | 1593522 | 18139 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 380919 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0005451 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE |  | 44543 | 2211 | 1568917 | 1249 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 87430 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0157869 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | RECLOSER |  | 44557 | 500 | 1583867 | 5085 | Distribution Circuit | Vegetation | Tree - fell into line | 464 | 1432830 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160958 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | SWITCH |  | 44557 | 242 | 1595269 | 16559 | Distribution Circuit | Environmental/External | Ice or snow | 204 | 3378036 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160943 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44557 | 149 | 1591649 | 11011 | Distribution Circuit | Vegetation | Tree - fell into line | 140 | 1541012 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160871 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | TRIP-SAVER |  | 44557 | 158 | 1585289 | 2342 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 252936 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160958 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44557 | 242 | 1592530 | 12501 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 1250100 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160943 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE |  | 44557 | 938 | 1585340 | 1858 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 206238 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161159 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44557 | 149 | 1590997 | 10617 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 31851 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0162046 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44557 | 131 | 1590992 | 15114 | Distribution Circuit | Environmental/External | Ice or snow | 2 | 30228 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0162043 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44557 | 253 | 1591707 | 12536 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 188040 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0005072 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44557 | 253 | 1591703 | 12535 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 150420 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005071 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44557 | 253 | 1591653 | 12535 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 1090545 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0005055 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44557 | 253 | 1591094 | 13651 | Distribution Circuit | Environmental/External | Ice or snow | 24 | 327624 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160943 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | FUSE |  | 44557 | 207 | 1588721 | 6661 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 532880 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160958 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44557 | 253 | 1587996 | 7973 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 239190 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160943 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44557 | 253 | 1591701 | 15243 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 499944 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005068 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44557 | 149 | 1584096 | 13865 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 360490 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0005069 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | FUSE |  | 44557 | 500 | 1588727 | 6114 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 12228 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160958 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | RECLOSER |  | 44555 | 920 | 1581205 | 445 | Distribution Circuit | Vegetation | Tree - fell into line | 629 | 48530 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160544 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1102 | 152181102 | SWITCH |  | 44557 | 425 | 1587959 | 18056 | Distribution Circuit | Vegetation | Tree - fell into line | 236 | 2301503 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160955 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | RECLOSER |  | 44557 | 253 | 1589919 | 5110 | Distribution Circuit | Environmental/External | Ice or snow | 71 | 362810 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160943 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | SECTIONALIZER |  | 44557 | 253 | 1589798 | 9694 | Distribution Circuit | Environmental/External | Ice or snow | 53 | 513782 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160943 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | FUSE |  | 44557 | 500 | 1587294 | 6337 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 152088 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160958 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE |  | 44543 | 1415 | 1567530 | 240 | Distribution Circuit | Vegetation | Tree - branch fell on line | 120 | 28800 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157378 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | FUSE |  | 44556 | 2323 | 1583210 | 18086 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 90430 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161054 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | FUSE |  | 44557 | 403 | 1591593 | 9091 | Distribution Circuit | Environmental/External | Ice or snow | 63 | 572733 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005039 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | FUSE |  | 44557 | 259 | 1588718 | 6679 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 554357 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0160958 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44557 | 253 | 1589795 | 10904 | Distribution Circuit | Environmental/External | Ice or snow | 22 | 239888 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160943 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | JUMPER |  | 44557 | 955 | 1591631 | 11467 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 34401 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0005053 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | RECLOSER |  | 44557 | 253 | 1584070 | 5106 | Distribution Circuit | Environmental/External | Ice or snow | 104 | 531024 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160943 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE |  | 44557 | 654 | 1585276 | 1851 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 234149 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161103 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE |  | 44557 | 425 | 1587985 | 15038 | Distribution Circuit | Environmental/External | Ice or snow | 20 | 300760 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160955 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE |  | 44557 | 228 | 1595230 | 16391 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 825099 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0006207 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | FORESTHILL-1102 | 152181102 | JUMPER |  | 44557 | 425 | 1595233 | 13639 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 68195 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0006208 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1102 | 152181102 | RECLOSER |  | 44557 | 425 | 1584313 | 12354 | Distribution Circuit | Environmental/External | Ice or snow | 28 | 345912 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160955 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE |  | 44557 | 220 | 1591526 | 17828 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 17828 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005024 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44557 | 519 | 1588010 | 3743 | Distribution Circuit | Environmental/External | Ice or snow | 32 | 119776 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160943 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44557 | 519 | 1588686 | 6493 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 144390 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160943 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44557 | 456 | 1591036 | 13584 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 366768 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0162056 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | JUMPER |  | 44557 | 519 | 1588681 | 6334 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6334 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160943 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | FUSE |  | 44557 | 204 | 1584253 | 11236 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 303372 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161209 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44557 | 438 | 1590854 | 13551 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 81306 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0162015 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44544 | 557 | 1569792 | 2000 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4000 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158143 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | SWITCH |  | 44557 | 955 | 1585381 | 10765 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 1288630 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161054 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44557 | 456 | 1590903 | 15101 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 60404 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0162023 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44557 | 456 | 1590860 | 18091 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 199001 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0162016 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44557 | 359 | 1590905 | 12370 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 296880 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0162024 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44557 | 16 | 1583338 | 19397 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 911659 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0162057 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | FUSE |  | 44557 | 352 | 1586168 | 12314 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 295536 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161207 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | RECLOSER |  | 44557 | 11 | 1583296 | 12343 | Distribution Circuit | Vegetation | Tree - branch fell on line | 324 | 3309256 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160895 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | JUMPER |  | 44557 | 11 | 1590674 | 14083 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 366158 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161983 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | TRIP-SAVER |  | 44557 | 209 | 1583885 | 7995 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 487695 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0162039 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | OCB |  | 44557 | 156 | 1585435 | 10907 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 263671 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160895 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | OCB |  | 44557 | 955 | 1585433 | 9069 | Distribution Circuit | Vegetation | Tree - fell into line | 145 | 1159210 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161054 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44557 | 11 | 1591034 | 15322 | Distribution Circuit | Environmental/External | Ice or snow | 15 | 229830 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0162055 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44557 | 333 | 1588781 | 16668 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 183348 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160895 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44557 | 16 | 1598684 | 19500 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 526500 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007757 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | JUMPER |  | 44557 | 403 | 1593516 | 13686 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 136860 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005449 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44557 | 525 | 1586800 | 5135 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 10270 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160895 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44557 | 16 | 1598682 | 19426 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 621632 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007756 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | FUSE |  | 44557 | 403 | 1592585 | 11116 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 166740 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161054 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44544 | 333 | 1569465 | 551 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 67773 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157844 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44557 | 16 | 1598681 | 19466 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 233592 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007755 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44557 | 208 | 1587023 | 16653 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 501833 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160895 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1110 | 152691110 | RECLOSER |  | 44557 | 122 | 1583750 | 17862 | Distribution Circuit | Vegetation | Tree - fell into line | 271 | 3385328 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160921 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | JUMPER |  | 44557 | 208 | 1589755 | 15164 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 530740 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160895 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | RECLOSER |  | 44557 | 519 | 1588457 | 6064 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 278176 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160895 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44557 | 357 | 1589720 | 16513 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 16513 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160895 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | JUMPER |  | 44557 | 208 | 1589702 | 15164 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 106148 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160895 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44557 | 519 | 1589729 | 12222 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 61110 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160895 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44557 | 208 | 1589699 | 15191 | Distribution Circuit | Environmental/External | Ice or snow | 51 | 774741 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160895 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | FUSE |  | 44544 | 429 | 1569587 | 791 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 25312 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158146 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | FUSE |  | 44557 | 227 | 1584254 | 16660 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 483140 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161054 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44557 | 525 | 1590935 | 15090 | Distribution Circuit | Environmental/External | Ice or snow | 45 | 679050 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160943 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | JUMPER |  | 44557 | 11 | 1595055 | 18413 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 73652 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 22-0006110 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | RECLOSER |  | 44557 | 519 | 1590783 | 18140 | Distribution Circuit | Environmental/External | Ice or snow | 102 | 1850280 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160943 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44544 | 550 | 1569764 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 32344 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158094 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44557 | 11 | 1589898 | 21230 | Distribution Circuit | Environmental/External | Ice or snow | 52 | 976708 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160895 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 2 | HIGGINS-1110 | 152691110 | FUSE |  | 44543 | 1406 | 1567839 | 1597 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 12042 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0157387 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | SWITCH |  | 44557 | 11 | 1597245 | 16670 | Distribution Circuit | Environmental/External | Ice or snow | 9 | 150030 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160895 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44557 | 519 | 1589551 | 19013 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 19013 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160943 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44557 | 519 | 1589731 | 13789 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 220624 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160895 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | SWITCH |  | 44557 | 428 | 1597150 | 18191 | Distribution Circuit | Environmental/External | Ice or snow | 3 | 54573 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0007220 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | FUSE |  | 44543 | 1415 | 1567398 | 1567 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 42309 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157346 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44557 | 507 | 1589734 | 14673 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 14673 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160895 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44556 | 2042 | 1597250 | 16922 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 50766 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0007313 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | JUMPER |  | 44556 | 2037 | 1597260 | 20051 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 20051 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0007319 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1110 | 152691110 | FUSE |  | 44545 | 2232 | 1573984 | 2580 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 38580 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 21-0158881 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1110 | 152691110 | FUSE |  | 44557 | 222 | 1591812 | 16694 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 183634 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160921 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44557 | 209 | 1587466 | 15189 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 273402 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160895 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44557 | 428 | 1598423 | 22212 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 22212 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007697 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44557 | 244 | 1589377 | 16454 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 411350 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160895 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | JUMPER |  | 44557 | 519 | 1588767 | 9500 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 311410 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160895 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44556 | 2040 | 1583612 | 19852 | Distribution Circuit | Vegetation | Tree - fell into line | 223 | 672750 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160895 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44544 | 441 | 1569610 | 688 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 54751 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157901 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44556 | 2042 | 1594668 | 19850 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 158800 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0005862 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44557 | 157 | 1591648 | 13490 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 296780 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160895 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | HIGGINS-1110 | 152691110 | FUSE |  | 44557 | 206 | 1598401 | 19857 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 436854 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007692 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1110 | 152691110 | FUSE |  | 44557 | 206 | 1598400 | 19610 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 607910 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007691 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE |  | 44557 | 2 | 1588918 | 9725 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 1030850 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161653 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | HIGGINS-1110 | 152691110 | FUSE |  | 44557 | 222 | 1596782 | 17975 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 359500 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007003 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1110 | 152691110 | FUSE |  | 44557 | 223 | 1598191 | 17910 | Distribution Circuit | Environmental/External | Ice or snow | 35 | 626850 | Strong Winds-Snow-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007604 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE |  | 44557 | 36 | 1591622 | 15071 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 45213 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005052 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE |  | 44557 | 36 | 1591515 | 13957 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 1144474 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005021 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | HIGGINS-1110 | 152691110 | FUSE |  | 44557 | 222 | 1598093 | 17933 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 179330 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007571 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE |  | 44557 | 36 | 1588930 | 14071 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 422130 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161658 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE |  | 44557 | 36 | 1589525 | 15329 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 703319 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161753 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE |  | 44556 | 2221 | 1595865 | 15490 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 913910 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0006487 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE |  | 44556 | 2356 | 1589740 | 14041 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 252738 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161753 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | JUMPER |  | 44557 | 553 | 1589967 | 18895 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 29592 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161850 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 44557 | 503 | 1589956 | 10705 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 128460 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161848 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | RECLOSER |  | 44557 | 239 | 1583926 | 19550 | Distribution Circuit | Vegetation | Tree - fell into line | 1539 | 14574972 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160938 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 44557 | 338 | 1584325 | 15199 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 235582 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161879 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | JUMPER |  | 44557 | 239 | 1592644 | 14917 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 29834 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160938 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44557 | 214 | 1587519 | 16356 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 147204 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160871 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | JUMPER |  | 44557 | 239 | 1592647 | 14901 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 44703 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160938 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 44557 | 315 | 1584327 | 14960 | Distribution Circuit | Vegetation | Tree - fell into line | 150 | 963630 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161880 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE |  | 44557 | 35 | 1586211 | 5198 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5198 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161221 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 44544 | 346 | 1569483 | 3460 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 219150 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158040 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | SWITCH |  | 44557 | 36 | 1591028 | 12079 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 531476 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160907 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE |  | 44557 | 35 | 1586199 | 5384 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 48456 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161220 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE |  | 44557 | 35 | 1586197 | 5198 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5198 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161219 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE |  | 44557 | 36 | 1591033 | 11119 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 544831 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160907 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE |  | 44557 | 36 | 1586194 | 5399 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 107980 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161218 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | FUSE |  | 44557 | 1254 | 1585773 | 11845 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 204984 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161986 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | OCB |  | 44557 | 36 | 1583420 | 6863 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 711442 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160907 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | JUMPER |  | 44557 | 214 | 1590691 | 12377 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 569342 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160871 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44557 | 214 | 1587521 | 15012 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 270216 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160871 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 44544 | 501 | 1570226 | 2026 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 67582 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158133 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | RECLOSER |  | 44556 | 2242 | 1583107 | 13623 | Distribution Circuit | Environmental/External | Ice or snow | 151 | 1395390 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160871 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | JUMPER |  | 44557 | 239 | 1587567 | 16422 | Distribution Circuit | Vegetation | Tree - fell into line | 630 | 348576 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160938 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44556 | 2242 | 1587522 | 16665 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 416625 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160871 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44543 | 2201 | 1570675 | 2352 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 58800 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157954 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 44557 | 248 | 1587033 | 12396 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 97858 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161349 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 44557 | 120 | 1587048 | 6490 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 103840 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161350 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | JUMPER |  | 44557 | 239 | 1595809 | 15336 | Distribution Circuit | Environmental/External | Ice or snow | 13 | 199368 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160938 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44556 | 2242 | 1587532 | 18368 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 753088 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160871 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 44557 | 239 | 1587053 | 13953 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 97671 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161352 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44556 | 2242 | 1587531 | 16868 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 253020 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160871 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44556 | 2142 | 1583017 | 18591 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 650685 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160871 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | JUMPER |  | 44557 | 239 | 1590758 | 13723 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 13723 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161350 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44556 | 2242 | 1587524 | 18013 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 36026 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160871 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 44557 | 239 | 1584326 | 15036 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 1022448 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160938 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | OTHER |  | 44543 | 454 | 1565722 | 310 | Distribution Circuit | Vegetation | Tree - branch fell on line | 967 | 137701 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0156929 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44556 | 2142 | 1589615 | 18591 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 334638 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160871 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 44557 | 239 | 1587569 | 15009 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 222761 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160938 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44556 | 2142 | 1589618 | 18591 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 74364 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160871 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | FUSE |  | 44557 | 316 | 1595845 | 15134 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 30268 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0006470 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 109 | 1593386 | 13800 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 165600 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | FUSE |  | 44557 | 334 | 1585335 | 12068 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 156884 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161041 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | RECLOSER |  | 44557 | 316 | 1583853 | 15127 | Distribution Circuit | Vegetation | Tree - fell into line | 1270 | 6914037 | Snow-Clear;Below 32 F | Pole-Wood | Broken- wire on ground | 21-0160948 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44556 | 2242 | 1589604 | 16689 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 133512 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160871 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44557 | 214 | 1587536 | 15366 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 138294 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160871 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 111 | 1594321 | 19588 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 156704 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0005763 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44544 | 828 | 1570174 | 1706 | Distribution Circuit | Vegetation | Tree - bark fell into line | 19 | 32414 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158185 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44556 | 2242 | 1589593 | 18412 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 1031072 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160871 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 44544 | 407 | 1569821 | 2304 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 66816 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157799 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | TRIP-SAVER |  | 44557 | 239 | 1592335 | 16759 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 2423026 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160938 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | TRIP-SAVER |  | 44544 | 408 | 1569546 | 634 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 72965 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0157806 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 44557 | 239 | 1592436 | 19567 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 802247 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160938 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44557 | 214 | 1590067 | 18116 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 271740 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160871 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44557 | 214 | 1598398 | 19331 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 902892 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007690 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44557 | 214 | 1590065 | 15337 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 874209 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160871 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 143 | 1592619 | 18218 | Distribution Circuit | Environmental/External | Ice or snow | 5 | 91090 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44557 | 214 | 1590079 | 16706 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 451062 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160871 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44557 | 214 | 1590076 | 18191 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 54573 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160871 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 109 | 1598679 | 19580 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 39160 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007762 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | JUMPER |  | 44556 | 143 | 1592613 | 16594 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 232316 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 109 | 1594305 | 18275 | Distribution Circuit | Environmental/External | Ice or snow | 6 | 109650 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005759 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | FUSE |  | 44557 | 326 | 1594966 | 15181 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 166991 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 22-0006045 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | RECLOSER |  | 44557 | 11 | 1583297 | 19721 | Distribution Circuit | Environmental/External | Ice or snow | 2757 | 10293869 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 143 | 1592616 | 16827 | Distribution Circuit | Environmental/External | Ice or snow | 6 | 100962 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44557 | 214 | 1591013 | 13672 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 355472 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0162051 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 111 | 1594318 | 19588 | Distribution Circuit | Environmental/External | Ice or snow | 104 | 1908936 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005762 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44557 | 214 | 1591017 | 17596 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 70384 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0162052 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | JUMPER |  | 44557 | 143 | 1592612 | 19508 | Distribution Circuit | Environmental/External | Ice or snow | 7 | 136556 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 143 | 1592333 | 18181 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 1090860 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 143 | 1594744 | 20769 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 1848441 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005905 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 109 | 1594310 | 18275 | Distribution Circuit | Environmental/External | Ice or snow | 10 | 182750 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005760 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | JUMPER |  | 44557 | 143 | 1585986 | 14144 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 155584 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161160 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44557 | 214 | 1591011 | 19722 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 118332 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0162050 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 143 | 1592607 | 18121 | Distribution Circuit | Environmental/External | Ice or snow | 2 | 36242 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1101 | 152031101 | FUSE |  | 44557 | 1 | 1593741 | 11160 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 145080 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0160893 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 144 | 1597627 | 18352 | Distribution Circuit | Environmental/External | Ice or snow | 6 | 110112 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007538 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | SWITCH |  | 44557 | 143 | 1590944 | 9568 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 1195908 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44556 | 54 | 1598462 | 21163 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 465586 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007730 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1101 | 152031101 | FUSE |  | 44557 | 1 | 1593750 | 16763 | Distribution Circuit | Environmental/External | Ice or snow | 57 | 952939 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160893 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 144 | 1597642 | 18248 | Distribution Circuit | Environmental/External | Ice or snow | 9 | 164232 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 112 | 1597555 | 18327 | Distribution Circuit | Environmental/External | Ice or snow | 6 | 109962 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 112 | 1591405 | 15358 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 337876 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 144 | 1597644 | 17913 | Distribution Circuit | Environmental/External | Ice or snow | 13 | 232869 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 112 | 1597554 | 18327 | Distribution Circuit | Environmental/External | Ice or snow | 4 | 73308 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 51 | 1590919 | 16660 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 999600 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 127 | 1597643 | 18248 | Distribution Circuit | Environmental/External | Ice or snow | 43 | 784664 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 112 | 1597553 | 18327 | Distribution Circuit | Environmental/External | Ice or snow | 37 | 678099 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 112 | 1592809 | 19555 | Distribution Circuit | Environmental/External | Ice or snow | 14 | 273770 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE |  | 44557 | 127 | 1596906 | 15419 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 123352 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007080 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44544 | 310 | 1570366 | 2326 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 48846 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157750 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44545 | 2317 | 1574024 | 1036 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 21756 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0158757 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | JUMPER |  | 44557 | 133 | 1595745 | 15282 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 30564 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0006423 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | JUMPER |  | 44557 | 144 | 1591414 | 15310 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 214340 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 143 | 1591645 | 15509 | Distribution Circuit | Environmental/External | Ice or snow | 44 | 682396 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44556 | 2356 | 1589990 | 15267 | Distribution Circuit | Environmental/External | Ice or snow | 59 | 900753 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161862 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 112 | 1598362 | 19705 | Distribution Circuit | Environmental/External | Ice or snow | 4 | 78820 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0007664 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 124 | 1597551 | 18315 | Distribution Circuit | Environmental/External | Ice or snow | 5 | 91575 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | TRIP-SAVER |  | 44557 | 144 | 1591417 | 16980 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 645240 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 143 | 1591639 | 8059 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 153121 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1101 | 152031101 | FUSE |  | 44557 | 1 | 1591686 | 16647 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 299646 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160893 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 144 | 1589914 | 9218 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 73744 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161836 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 144 | 1591384 | 16668 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 150012 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44544 | 136 | 1569234 | 862 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 12068 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157812 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 144 | 1591411 | 18141 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 253974 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 11 | 1591642 | 15645 | Distribution Circuit | Environmental/External | Ice or snow | 137 | 2143365 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE |  | 44557 | 127 | 1595749 | 13634 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 149974 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 22-0006426 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | OTHER |  | 44544 | 420 | 1569572 | 2571 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 9933 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0158087 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1101 | 152031101 | JUMPER |  | 44557 | 1 | 1591708 | 15386 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 15386 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160893 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 144 | 1589912 | 12194 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 402402 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161835 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 112 | 1592805 | 18371 | Distribution Circuit | Environmental/External | Ice or snow | 7 | 128597 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1101 | 152031101 | FUSE |  | 44557 | 1 | 1591689 | 15561 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 165851 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160893 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 57 | 1589923 | 18221 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 802653 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161840 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | JUMPER |  | 44557 | 143 | 1591855 | 16852 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 1482346 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | JUMPER |  | 44557 | 127 | 1592672 | 10957 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 164355 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005245 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 112 | 1592783 | 19705 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 19705 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 144 | 1589924 | 16942 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 50826 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161841 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1101 | 152031101 | FUSE |  | 44557 | 1 | 1591700 | 15394 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 15394 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160893 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 144 | 1589609 | 16763 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 905202 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161771 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 144 | 1589607 | 19458 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 155664 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161770 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 59 | 1594277 | 21118 | Distribution Circuit | Environmental/External | Ice or snow | 13 | 274534 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005750 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1101 | 152031101 | SWITCH |  | 44557 | 1 | 1590806 | 15082 | Distribution Circuit | Environmental/External | Ice or snow | 81 | 776838 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160893 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 112 | 1594275 | 21104 | Distribution Circuit | Environmental/External | Ice or snow | 76 | 1603904 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005749 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 15 | 1594286 | 21162 | Distribution Circuit | Environmental/External | Ice or snow | 23 | 486726 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005752 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 144 | 1589926 | 12128 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 218304 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161844 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | JUMPER |  | 44557 | 118 | 1592668 | 15168 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 15168 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160923 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | OTHER |  | 44544 | 310 | 1569422 | 2227 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1389 | 1172306 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157750 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | JUMPER |  | 44557 | 127 | 1591714 | 12323 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 308075 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160923 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 110 | 1594274 | 21146 | Distribution Circuit | Environmental/External | Ice or snow | 20 | 422920 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005748 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 144 | 1591366 | 13711 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 68555 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 4 | 1593559 | 15198 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 243168 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1101 | 152031101 | JUMPER |  | 44557 | 1 | 1590876 | 13613 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 244637 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160893 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 112 | 1594267 | 19733 | Distribution Circuit | Environmental/External | Ice or snow | 59 | 1164247 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005743 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 112 | 1591387 | 15111 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 528885 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 112 | 1594279 | 18100 | Distribution Circuit | Environmental/External | Ice or snow | 6 | 108600 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005751 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44556 | 2355 | 1589906 | 19846 | Distribution Circuit | Environmental/External | Ice or snow | 55 | 1091530 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161832 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 43 | 1589907 | 16850 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 421250 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161833 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 112 | 1589904 | 15254 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 823716 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161830 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 144 | 1589995 | 10890 | Distribution Circuit | Environmental/External | Ice or snow | 33 | 359370 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161865 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER |  | 44557 | 144 | 1587379 | 11016 | Distribution Circuit | Vegetation | Tree - fell into line | 140 | 1284864 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 144 | 1587330 | 13803 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 552120 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0161407 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE |  | 44557 | 17 | 1591638 | 16842 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 164044 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160923 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 144 | 1587331 | 18048 | Distribution Circuit | Environmental/External | Ice or snow | 13 | 234624 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161408 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44556 | 2159 | 1587284 | 18336 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 623424 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161390 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 112 | 1594296 | 20824 | Distribution Circuit | Environmental/External | Ice or snow | 5 | 104120 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005753 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44559 | 726 | 1587949 | 15020 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 195260 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161503 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE |  | 44557 | 401 | 1596087 | 14847 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 148354 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0006613 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | JUMPER |  | 44559 | 1129 | 1588486 | 16341 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 65364 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007784 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE |  | 44557 | 520 | 1596436 | 17862 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 482274 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0006713 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE |  | 44557 | 127 | 1591637 | 15095 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 211330 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160923 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE |  | 44557 | 401 | 1594890 | 17908 | Distribution Circuit | Environmental/External | Ice or snow | 13 | 232804 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005997 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 144 | 1586117 | 9600 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 153600 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 144 | 1586116 | 16522 | Distribution Circuit | Environmental/External | Ice or snow | 34 | 561748 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE |  | 44557 | 441 | 1594887 | 20743 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 124458 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0005994 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1101 | 152031101 | RECLOSER |  | 44544 | 316 | 1569443 | 2279 | Distribution Circuit | Vegetation | Tree - fell into line | 896 | 531786 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157741 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1101 | 152031101 | RECLOSER |  | 44543 | 950 | 1566268 | 1607 | Distribution Circuit | Vegetation | Tree - fell into line | 1865 | 221073 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157058 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE |  | 44557 | 133 | 1591719 | 16692 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 16692 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160923 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 144 | 1597020 | 18213 | Distribution Circuit | Environmental/External | Ice or snow | 14 | 254982 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE |  | 44544 | 224 | 1569286 | 1997 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 81877 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158227 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 144 | 1587320 | 16997 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 50991 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161404 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44559 | 1125 | 1588393 | 480 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 11040 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161622 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | SWITCH |  | 44557 | 611 | 1592215 | 12007 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 120070 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160978 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44543 | 2155 | 1568885 | 2559 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 117714 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157976 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE |  | 44557 | 401 | 1593312 | 12137 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 752494 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160978 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | SWITCH |  | 44557 | 611 | 1592213 | 12006 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 36018 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160978 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE |  | 44557 | 401 | 1591005 | 16469 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 1877466 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160978 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE |  | 44557 | 127 | 1591751 | 13506 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 853518 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160923 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44556 | 2221 | 1592515 | 14084 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 112245 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160865 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | SWITCH |  | 44556 | 1934 | 1596028 | 18231 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 398166 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0006597 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 44556 | 2258 | 1590111 | 15622 | Distribution Circuit | Environmental/External | Ice or snow | 3 | 46866 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161198 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 44556 | 2048 | 1583572 | 12646 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 164398 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161198 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44556 | 2221 | 1598313 | 19599 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 940752 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160865 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 44557 | 336 | 1584309 | 11933 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 298325 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161198 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 44557 | 24 | 1582895 | 16828 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 100968 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161198 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44556 | 2221 | 1598298 | 19459 | Distribution Circuit | Environmental/External | Ice or snow | 21 | 408639 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007634 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | OCB |  | 44557 | 133 | 1583747 | 11034 | Distribution Circuit | Vegetation | Tree - fell into line | 224 | 1496558 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160923 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 44556 | 2258 | 1583573 | 15622 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 1124784 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161198 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 44556 | 1954 | 1582930 | 10098 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 20196 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161198 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE |  | 44557 | 611 | 1593333 | 12041 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 84287 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160978 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 44557 | 427 | 1587395 | 18061 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 144488 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161198 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44556 | 2221 | 1592596 | 18136 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 580352 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160865 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 44557 | 427 | 1587393 | 12193 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 317018 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161198 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44557 | 144 | 1586111 | 15436 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 401336 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160896 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 44557 | 427 | 1587388 | 11926 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 35778 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161198 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE |  | 44557 | 611 | 1596020 | 17949 | Distribution Circuit | Environmental/External | Ice or snow | 12 | 215388 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0006594 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44556 | 2221 | 1592600 | 16672 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 207124 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160865 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44556 | 2221 | 1593991 | 12541 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 288443 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005685 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 44556 | 2258 | 1596959 | 16596 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 66384 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007096 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | RECLOSER |  | 44556 | 2221 | 1583080 | 9732 | Distribution Circuit | Vegetation | Tree - fell into line | 185 | 1533644 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160865 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44556 | 2221 | 1592510 | 11099 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 99891 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160865 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1107 | 152481107 | FUSE |  | 44557 | 248 | 1587585 | 9503 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 104533 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160932 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1107 | 152481107 | JUMPER |  | 44557 | 156 | 1590979 | 13188 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 139950 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160932 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | JUMPER |  | 44557 | 142 | 1590687 | 13583 | Distribution Circuit | Vegetation | Tree - bark fell into line | 2 | 27166 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160924 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | RECLOSER |  | 44557 | 611 | 1584233 | 12007 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 924539 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160978 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | RECLOSER |  | 44557 | 427 | 1584308 | 10908 | Distribution Circuit | Environmental/External | Ice or snow | 88 | 868617 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161198 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44557 | 444 | 1585946 | 9223 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 92230 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0160957 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1107 | 152481107 | FUSE |  | 44557 | 338 | 1590975 | 8071 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 228937 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0160932 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44556 | 2221 | 1592601 | 13766 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 68830 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160865 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | JUMPER |  | 44557 | 143 | 1592587 | 10872 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 54360 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160924 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE |  | 44556 | 1925 | 1582879 | 16952 | Distribution Circuit | Environmental/External | Ice or snow | 5 | 84760 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0006747 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 44556 | 1904 | 1587422 | 12834 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 308016 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161198 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 44556 | 1904 | 1595236 | 14047 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 98329 | Clear;32-90 F | Conductor- Overhead | On Ground | 22-0006209 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 44557 | 229 | 1593486 | 12436 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 49744 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0161198 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44556 | 2221 | 1592507 | 11241 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 562050 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0160865 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | JUMPER |  | 44556 | 2221 | 1592520 | 10864 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 120423 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0160865 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 44556 | 2359 | 1591035 | 15494 | Distribution Circuit | Environmental/External | Ice or snow | 3 | 46482 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161198 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 44556 | 1901 | 1595239 | 14043 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 28086 | Clear;32-90 F | Conductor- Overhead | On Ground | 22-0006213 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 44556 | 2359 | 1591040 | 16587 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 16587 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161198 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 44556 | 2359 | 1590096 | 15494 | Distribution Circuit | Environmental/External | Ice or snow | 5 | 77470 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161198 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 44556 | 1930 | 1595246 | 13869 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 124821 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0006215 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 44556 | 2357 | 1590091 | 15497 | Distribution Circuit | Environmental/External | Ice or snow | 59 | 914323 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161198 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44556 | 2221 | 1596640 | 15548 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 77740 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0006859 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | JUMPER |  | 44556 | 2221 | 1596546 | 15693 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 219702 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0006806 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44557 | 444 | 1585980 | 19213 | Distribution Circuit | Environmental/External | Ice or snow | 2 | 38426 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160957 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | TRIP-SAVER |  | 44544 | 647 | 1569855 | 1977 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 264918 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157949 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | FUSE |  | 44557 | 143 | 1587210 | 12246 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 330642 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161377 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | FUSE |  | 44557 | 143 | 1588766 | 10651 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 106510 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161616 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | FUSE |  | 44557 | 143 | 1588768 | 12469 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 309029 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161617 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | FUSE |  | 44557 | 143 | 1588428 | 9576 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 181944 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160924 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE |  | 44556 | 2359 | 1591041 | 15494 | Distribution Circuit | Environmental/External | Ice or snow | 2 | 30988 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161198 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER |  | 44557 | 444 | 1592573 | 17832 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 89160 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160889 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER |  | 44557 | 444 | 1592698 | 20805 | Distribution Circuit | Environmental/External | Ice or snow | 5 | 104025 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160889 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | FUSE |  | 44557 | 309 | 1585857 | 3732 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 14928 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161126 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44557 | 444 | 1590965 | 17832 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 1436979 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160889 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44557 | 444 | 1592682 | 16619 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 33238 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160889 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER |  | 44557 | 444 | 1592623 | 18065 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 54195 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160889 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER |  | 44557 | 444 | 1591663 | 16593 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 696906 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160889 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44557 | 444 | 1587185 | 12291 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 491249 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0160889 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44557 | 444 | 1587188 | 15259 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 335698 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160889 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44559 | 344 | 1588829 | 10981 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 32943 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161634 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44557 | 444 | 1587192 | 7741 | Distribution Circuit | Vegetation | Tree - grew into line | 42 | 325122 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160889 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44559 | 344 | 1590702 | 12066 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 36198 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160889 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1104 | 152481104 | RECLOSER |  | 44545 | 2006 | 1573664 | 2539 | Distribution Circuit | Vegetation | Tree - fell into line | 522 | 438989 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158632 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1105 | 152481105 | RECLOSER |  | 44559 | 344 | 1587735 | 554 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 49860 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160889 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER |  | 44559 | 344 | 1590692 | 10947 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 460602 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160889 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE |  | 44557 | 237 | 1589585 | 13847 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 207705 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161769 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44557 | 444 | 1591782 | 8070 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 96840 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160889 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44556 | 2350 | 1588507 | 3889 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 11667 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160889 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44556 | 2355 | 1586748 | 12372 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 238099 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160889 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44557 | 444 | 1587472 | 18056 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 649234 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0160889 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1105 | 152481105 | JUMPER |  | 44557 | 18 | 1586934 | 13625 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 54500 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160889 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | SWITCH |  | 44557 | 18 | 1586746 | 20845 | Distribution Circuit | Vegetation | Tree - fell into line | 482 | 5656813 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160897 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE |  | 44557 | 237 | 1589683 | 12488 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 574448 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161781 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | JUMPER |  | 44557 | 242 | 1593931 | 13860 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 69300 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0005658 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44557 | 13 | 1594167 | 12371 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 210307 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005718 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44557 | 18 | 1589861 | 8179 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 16358 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161819 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44557 | 14 | 1595899 | 15315 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 444135 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0006511 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44556 | 2256 | 1594191 | 13938 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 348450 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005724 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | DRUM-1101 | 152321101 | RECLOSER |  | 44559 | 707 | 1587919 | 10493 | Distribution Circuit | Vegetation | Tree - fell into line | 183 | 1384898 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0161489 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44557 | 18 | 1595910 | 20950 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 125700 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0006522 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44557 | 46 | 1587243 | 8085 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 258348 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160897 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44557 | 18 | 1595930 | 19505 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 78020 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0006536 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44557 | 18 | 1595912 | 22299 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 245289 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0006524 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44557 | 13 | 1590106 | 13896 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 367712 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161892 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44557 | 18 | 1590098 | 10907 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 32721 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161886 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44557 | 18 | 1590105 | 9691 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 368258 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161890 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44557 | 18 | 1598219 | 22572 | Distribution Circuit | Environmental/External | Ice or snow | 21 | 461502 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007613 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44557 | 18 | 1595933 | 21022 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 21022 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0006537 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44557 | 18 | 1598220 | 21092 | Distribution Circuit | Environmental/External | Ice or snow | 33 | 669626 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007615 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44557 | 18 | 1598223 | 20919 | Distribution Circuit | Environmental/External | Ice or snow | 12 | 251028 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007618 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44556 | 2346 | 1593979 | 12790 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 562760 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005682 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44557 | 18 | 1598225 | 21087 | Distribution Circuit | Environmental/External | Ice or snow | 4 | 84348 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007619 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44557 | 18 | 1599304 | 22602 | Distribution Circuit | Environmental/External | Ice or snow | 16 | 361632 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007994 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44557 | 18 | 1599307 | 20955 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 544830 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007995 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | TRIP-SAVER |  | 44557 | 18 | 1599308 | 22420 | Distribution Circuit | Equipment Failure/Involved | Overhead | 131 | 2937020 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007996 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44556 | 2356 | 1590907 | 13966 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 41898 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160889 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44556 | 2238 | 1598226 | 21346 | Distribution Circuit | Environmental/External | Ice or snow | 44 | 939224 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007623 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44557 | 1 | 1593988 | 12391 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 12391 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005683 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1104 | 152481104 | JUMPER |  | 44556 | 2145 | 1590928 | 6895 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 172375 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160870 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44557 | 1 | 1593994 | 16952 | Distribution Circuit | Environmental/External | Ice or snow | 108 | 1715170 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160897 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44557 | 14 | 1593992 | 12078 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 84546 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005686 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44556 | 2354 | 1590911 | 12300 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 574275 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160889 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1104 | 152481104 | FUSE |  | 44556 | 2145 | 1583046 | 15512 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 78260 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160870 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER |  | 44556 | 2354 | 1590967 | 9373 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 436998 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160889 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER |  | 44543 | 1520 | 1567855 | 1345 | Distribution Circuit | Vegetation | Tree - fell into line | 205 | 57399 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157391 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER |  | 44556 | 2354 | 1590969 | 22486 | Distribution Circuit | Environmental/External | Ice or snow | 151 | 2537128 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160889 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | OTHER |  | 44544 | 822 | 1570177 | 1656 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 51336 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157919 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER |  | 44556 | 2354 | 1597576 | 22384 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 246224 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160889 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1104 | 152481104 | JUMPER |  | 44557 | 12 | 1591896 | 12510 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 262710 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160870 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1104 | 152481104 | FUSE |  | 44557 | 12 | 1595107 | 13646 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 451836 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0006166 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44557 | 216 | 1590769 | 6688 | Distribution Circuit | Environmental/External | Ice or snow | 19 | 127072 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160897 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1104 | 152481104 | FUSE |  | 44557 | 12 | 1595656 | 13929 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 306438 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0006355 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44557 | 216 | 1590983 | 7900 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 39500 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160897 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | DRUM-1101 | 152321101 | OTHER |  | 44544 | 2002 | 1571915 | 1076 | Distribution Circuit | Equipment Failure/Involved | Overhead | 62 | 60176 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158258 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | BRUNSWICK-1104 | 152481104 | FUSE |  | 44557 | 12 | 1591909 | 15310 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 153100 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160870 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44556 | 2354 | 1593525 | 21156 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 21156 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160889 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44557 | 216 | 1590984 | 8108 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 40540 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160897 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44557 | 216 | 1591483 | 9370 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 178030 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160897 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44556 | 2354 | 1594879 | 14039 | Distribution Circuit | Environmental/External | Ice or snow | 7 | 98273 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005988 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44556 | 2354 | 1594857 | 16826 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 406816 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005975 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44557 | 216 | 1592687 | 10685 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 224385 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160897 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44544 | 810 | 1570128 | 1814 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 10504 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157987 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44557 | 216 | 1592689 | 10544 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 21088 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160897 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 2 | SPAULDING-1101 | 152251101 | FUSE |  | 44544 | 627 | 1569810 | 1897 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 37322 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158149 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | SWITCH |  | 44556 | 2354 | 1594861 | 18231 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 984253 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005978 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44556 | 2354 | 1596741 | 21238 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 2069940 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0006983 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER |  | 44556 | 2354 | 1594913 | 15449 | Distribution Circuit | Vegetation | Tree - grew into line | 29 | 448021 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005996 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER |  | 44556 | 2354 | 1594889 | 15452 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 957380 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005996 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER |  | 44556 | 2354 | 1594897 | 16889 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 50667 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005996 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SPAULDING-1101 | 152251101 | FUSE |  | 44544 | 257 | 1569350 | 5231 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 26155 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0158434 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE |  | 44543 | 2103 | 1568760 | 6359 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 267497 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158177 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE |  | 44543 | 2001 | 1568597 | 8262 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 190195 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158175 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44556 | 2354 | 1598659 | 22561 | Distribution Circuit | Environmental/External | Ice or snow | 58 | 1308538 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0007744 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | OTHER |  | 44543 | 2137 | 1569216 | 2658 | Distribution Circuit | Vegetation | Tree - branch fell on line | 301 | 701017 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157729 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE |  | 44544 | 102 | 1572893 | 5417 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 303352 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0157729 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 2 | COLUMBIA HILL-1101 | 152471101 | FUSE |  | 44559 | 630 | 1588422 | 10710 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 396270 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005038 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | OCB |  | 44544 | 450 | 1569628 | 721 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 66859 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157773 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE |  | 44543 | 1416 | 1567615 | 1485 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 142560 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157388 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1102 | 152101102 | FUSE |  | 44544 | 244 | 1574187 | 3574 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 77541 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158938 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1102 | 152101102 | FUSE |  | 44556 | 1744 | 1589811 | 10940 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 109400 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160817 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE |  | 44559 | 739 | 1587957 | 10624 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 191232 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005081 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | TRANSFORMER |  | 44544 | 450 | 1569317 | 3443 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 13772 | Clear;32-90F | Transformer (OH) | Broken- wire on ground | 21-0158497 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1102 | 152101102 | SWITCH |  | 44556 | 1744 | 1589816 | 10940 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 798620 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160817 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | OTHER |  | 44555 | 1055 | 1581301 | 297 | Distribution Circuit | Vegetation | Tree - branch fell on line | 139 | 38338 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160561 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PIKE CITY-1102 | 152201102 | OCB |  | 44557 | 1455 | 1585351 | 21742 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 565292 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161147 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE |  | 44557 | 116 | 1592659 | 19414 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 1595670 | Strong Winds-Snow-Sleet or Ice-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160974 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | SWITCH |  | 44557 | 116 | 1592673 | 19778 | Distribution Circuit | Vegetation | Tree - fell into line | 316 | 5407523 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160974 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER |  | 44559 | 620 | 1588436 | 19315 | Distribution Circuit | Vegetation | Tree - fell into line | 518 | 1267573 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160903 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1102 | 152101102 | RECLOSER |  | 44556 | 1744 | 1582780 | 25853 | Distribution Circuit | Environmental/External | Ice or snow | 46 | 631459 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160817 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1101 | 152101101 | FUSE |  | 44557 | 54 | 1600339 | 23881 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 23881 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0008602 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1101 | 152101101 | FUSE |  | 44544 | 1141 | 1570777 | 4467 | Distribution Circuit | Environmental/External | Ice or snow | 16 | 71472 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0159344 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER |  | 44557 | 30 | 1582869 | 24031 | Distribution Circuit | Vegetation | Tree - fell into line | 1004 | 4009902 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160903 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER |  | 44555 | 1639 | 1581478 | 1457 | Distribution Circuit | Equipment Failure/Involved | Overhead | 600 | 767988 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160599 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 44545 | 1345 | 1572745 | 240 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 798 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158463 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | FUSE |  | 44545 | 1844 | 1573341 | 1211 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6055 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158704 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | RECLOSER |  | 44545 | 1841 | 1573368 | 1066 | Distribution Circuit | Vegetation | Tree - fell into line | 375 | 60771 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158622 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | DUNBAR-1101 | 43071101 | FUSE |  | 44557 | 756 | 1585081 | 326 | Distribution Circuit | Equipment Failure/Involved | Overhead | 105 | 34230 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161018 | OH | Sus | 45102085 | 2021 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER |  | 44543 | 1329 | 1567379 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 436 | 88133 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157276 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | OTHER |  | 44555 | 419 | 1581093 | 736 | Distribution Circuit | Vegetation | Tree - fell into line | 387 | 75749 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 21-0160519 | OH | Sus | 31588363 | 2021 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | RECLOSER |  | 44559 | 315 | 1587697 | 869 | Distribution Circuit | Vegetation | Tree - fell into line | 387 | 336303 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161473 | OH | Sus | 35314365 | 2021 | DEC | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | OTHER |  | 44543 | 2219 | 1568948 | 566 | Distribution Circuit | Vegetation | Tree - fell into line | 493 | 112356 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 21-0157637 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | OTHER |  | 44545 | 1641 | 1573059 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 493 | 272637 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158533 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | RECLOSER |  | 44559 | 315 | 1587694 | 56 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 5936 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161473 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | SWITCH |  | 44559 | 2212 | 1589134 | 8 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 440 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0161595 | OH | Sus | 45103122 | 2021 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER |  | 44545 | 1832 | 1573316 | 1470 | Distribution Circuit | Vegetation | Tree - fell into line | 283 | 215457 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158568 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER |  | 44543 | 1746 | 1568275 | 318 | Distribution Circuit | Vegetation | Tree - branch fell on line | 813 | 139537 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157492 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | TRIP-SAVER |  | 44545 | 1712 | 1573127 | 354 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 10266 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158569 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FULTON-1107 | 42561107 | RECLOSER |  | 44545 | 1630 | 1573054 | 1110 | Distribution Circuit | Vegetation | Tree - fell into line | 183 | 51930 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158527 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FULTON-1107 | 42561107 | RECLOSER |  | 44555 | 646 | 1581136 | 526 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 26068 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0160527 | OH | Sus | 31588285 | 2021 | DEC | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER |  | 44545 | 1752 | 1573229 | 304 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 19206 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158550 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1701 | 163451701 | TRIP-SAVER |  | 44557 | 700 | 1584686 | 2910 | Distribution Circuit | Equipment Failure/Involved | Overhead | 193 | 561630 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161211 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE |  | 44557 | 337 | 1584188 | 7891 | Distribution Circuit | Vegetation | Tree - fell into line | 175 | 565282 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161056 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1701 | 163451701 | FUSE |  | 44559 | 812 | 1588047 | 3166 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 161466 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0161697 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | STANISLAUS-1701 | 162821701 | FUSE |  | 44557 | 1019 | 1585483 | 9004 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 99044 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161821 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | STANISLAUS-1702 | 162821702 | JUMPER |  | 44557 | 1124 | 1585611 | 11728 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 11728 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0005910 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | STANISLAUS-1701 | 162821701 | FUSE |  | 44557 | 1134 | 1585655 | 7716 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 76854 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161851 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | STANISLAUS-1701 | 162821701 | RECLOSER |  | 44555 | 1954 | 1581711 | 1251 | Distribution Circuit | Vegetation | Tree - fell into line | 914 | 590832 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160623 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | STANISLAUS-1701 | 162821701 | RECLOSER |  | 44557 | 220 | 1583969 | 7633 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 635278 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0160936 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1701 | 162821701 | FUSE |  | 44557 | 220 | 1585719 | 8156 | Distribution Circuit | Environmental/External | Ice or snow | 67 | 546452 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160936 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | CORRAL-1101 | 162991101 | FUSE |  | 44543 | 1551 | 1567950 | 1286 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 15346 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157543 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1701 | 162821701 | FUSE |  | 44556 | 2231 | 1583965 | 11081 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 214445 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160936 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1701 | 162821701 | SWITCH |  | 44557 | 220 | 1590113 | 8130 | Distribution Circuit | Vegetation | Tree - fell into line | 416 | 2823844 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0160936 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1701 | 163451701 | FUSE |  | 44557 | 743 | 1585024 | 6287 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 194897 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161277 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | FROGTOWN-1701 | 163451701 | FUSE |  | 44544 | 800 | 1570100 | 244 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 488 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0157947 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1701 | 162821701 | OTHER |  | 44556 | 1653 | 1582821 | 8697 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 104732 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160821 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 44557 | 807 | 1585323 | 4924 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 162492 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161181 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 44557 | 923 | 1585304 | 5755 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 69060 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161331 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44557 | 129 | 1583773 | 10941 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 66629 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160953 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44557 | 752 | 1587203 | 10334 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 542862 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161374 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44557 | 806 | 1587282 | 10361 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 620794 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0161010 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER |  | 44557 | 746 | 1585048 | 9199 | Distribution Circuit | Vegetation | Tree - fell into line | 837 | 5692353 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161003 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44556 | 2232 | s1700607 | 8328 | Distribution Circuit | Equipment Failure/Involved | Overhead | 54 | 449712 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161003 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44557 | 237 | 1584014 | 10954 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 525792 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161247 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 44557 | 457 | 1584365 | 5114 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 20456 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0161180 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44557 | 746 | 1590579 | 6287 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 326924 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161003 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44555 | 2208 | 1581870 | 1082 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 77904 | Clear;32-90 F | Transformer (OH) | Broken- wire on ground | 21-0160653 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44557 | 549 | 1586407 | 6416 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 327216 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0161272 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44557 | 1014 | 1587484 | 6151 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 264493 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161158 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER |  | 44557 | 1527 | 1586333 | 5859 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1614 | 4395063 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161158 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44557 | 549 | 1584516 | 6416 | Distribution Circuit | Vegetation | Tree - branch fell on line | 167 | 1071472 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161032 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44555 | 1933 | 1581728 | 1176 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 16464 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160632 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | SWITCH |  | 44557 | 745 | 1587289 | 2175 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 76125 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161022 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | SWITCH |  | 44557 | 745 | 1587287 | 4932 | Distribution Circuit | Environmental/External | Ice or snow | 142 | 700344 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161022 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 44559 | 809 | 1588018 | 2941 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 61761 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 21-0161648 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE |  | 44543 | 2237 | 1569034 | 1290 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 61576 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0158036 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | RECLOSER |  | 44557 | 745 | 1585051 | 1971 | Distribution Circuit | Vegetation | Tree - fell into line | 415 | 817965 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161002 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | SWITCH |  | 44557 | 642 | 1590082 | 12074 | Distribution Circuit | Environmental/External | Ice or snow | 182 | 1533479 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160983 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | SALT SPRINGS-2102 | 163692102 | FUSE |  | 44543 | 2144 | 1571434 | 2482 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 44676 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158097 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 44557 | 642 | 1586087 | 8973 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 475569 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161184 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | RECLOSER |  | 44557 | 838 | 1585853 | 4424 | Distribution Circuit | Vegetation | Tree - fell into line | 150 | 663600 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161022 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | JUMPER |  | 44557 | 811 | 1589865 | 9069 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 126966 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161236 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | JUMPER |  | 44557 | 811 | 1589857 | 7809 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 195225 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0161236 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | OTHER |  | 44559 | 1124 | 1588418 | 7686 | Distribution Circuit | Equipment Failure/Involved | Overhead | 198 | 229115 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161566 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER |  | 44557 | 642 | 1584616 | 6294 | Distribution Circuit | Environmental/External | Ice or snow | 1522 | 1519801 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160983 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 44557 | 838 | 1586043 | 12106 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 36318 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161022 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | SWITCH |  | 44557 | 838 | 1589537 | 4979 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 477984 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161022 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE |  | 44557 | 838 | 1586177 | 8712 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 226512 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161213 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 44557 | 550 | 1588967 | 7634 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 221386 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161677 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE |  | 44557 | 808 | 1587212 | 12171 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 265250 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0161378 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER |  | 44557 | 804 | 1585099 | 2961 | Distribution Circuit | Environmental/External | Ice or snow | 166 | 491526 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161009 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER |  | 44557 | 657 | 1584673 | 13304 | Distribution Circuit | Environmental/External | Ice or snow | 91 | 1210664 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0161423 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER |  | 44557 | 838 | 1586339 | 10577 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 71687 | Clear;32-90 F | Anchor or Guy | Broken- wire on ground | 21-0161262 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE |  | 44557 | 808 | 1585766 | 11684 | Distribution Circuit | Environmental/External | Ice or snow | 72 | 729927 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161106 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | JUMPER |  | 44557 | 838 | 1588937 | 10531 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 707393 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161022 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44557 | 756 | 1587546 | 7643 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 38215 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0161448 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | JUMPER |  | 44557 | 756 | 1588986 | 6229 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 154728 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0161678 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 44557 | 643 | 1584610 | 10614 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 742980 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161446 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | JUMPER |  | 44557 | 813 | 1585151 | 2027 | Distribution Circuit | Vegetation | Tree - fell into line | 177 | 358779 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161014 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER |  | 44557 | 756 | 1584581 | 4909 | Distribution Circuit | Vegetation | Tree - fell into line | 644 | 3064163 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0161007 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | SWITCH |  | 44557 | 804 | 1588169 | 7446 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 379746 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161009 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | SWITCH |  | 44557 | 838 | 1586074 | 6288 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 767136 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161022 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44557 | 756 | 1588349 | 9128 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 73024 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161541 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | SWITCH |  | 44557 | 804 | 1588717 | 13432 | Distribution Circuit | Environmental/External | Ice or snow | 86 | 1150436 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161009 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44557 | 651 | 1586273 | 9229 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 27687 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161241 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | OCB |  | 44557 | 823 | s1699171 | 2100 | Distribution Circuit | Vegetation | Tree - fell into line | 784 | 993379 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161014 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | Yes
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | OTHER |  | 44543 | 1218 | 1570263 | 1654 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 4039 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0158043 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 44557 | 812 | 1586053 | 9249 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 295968 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161175 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE |  | 44557 | 748 | 1585058 | 6377 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 248703 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0161274 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | TRIP-SAVER |  | 44557 | 716 | 1586341 | 10724 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 414635 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161260 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | RECLOSER |  | 44543 | 1846 | 1568471 | 227 | Distribution Circuit | Vegetation | Tree - fell into line | 679 | 54313 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0157540 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE |  | 44557 | 823 | 1587161 | 6330 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 126600 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161365 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44544 | 426 | 1569581 | 784 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 7808 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0157930 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER |  | 44557 | 717 | 1584770 | 13588 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 509327 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160995 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | JUMPER |  | 44557 | 756 | 1589653 | 7603 | Distribution Circuit | Vegetation | Tree - fell into line | 246 | 1643102 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161007 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 44557 | 403 | 1585963 | 16622 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 905120 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161009 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | OCB |  | 44559 | 1536 | s1699449 | 21 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 126 | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 21-0161022 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44557 | 359 | 1592551 | 14924 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 164164 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0005215 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44557 | 756 | 1589761 | 12021 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 84147 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161793 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 44543 | 1221 | 1567081 | 504 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 6191 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0157351 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44557 | 717 | 1592553 | 13523 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 189322 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 22-0005218 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 44557 | 756 | 1590421 | 10514 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 378504 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161945 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | SWITCH |  | 44557 | 623 | 1590395 | 13341 | Distribution Circuit | Vegetation | Tree - fell into line | 230 | 2287137 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0161007 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 44557 | 448 | 1584805 | 9462 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 141930 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160972 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER |  | 44557 | 524 | 1584227 | 13836 | Distribution Circuit | Environmental/External | Ice or snow | 303 | 3439129 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0160972 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 44557 | 756 | 1590546 | 10479 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 764967 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161007 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44557 | 756 | 1593756 | 13331 | Distribution Circuit | Environmental/External | Ice or snow | 82 | 1093142 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161007 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | SWITCH |  | 44557 | 756 | 1590618 | 12117 | Distribution Circuit | Vegetation | Tree - fell into line | 127 | 1294357 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161007 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | TIGER CREEK-0201 | 161380201 | SWITCH |  | 44557 | 1650 | 1586088 | 13150 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 21242 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161187 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER |  | 44557 | 233 | 1584019 | 13618 | Distribution Circuit | Equipment Failure/Involved | Overhead | 353 | 3809820 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160937 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | SWITCH |  | 44557 | 315 | 1595213 | 13740 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 961800 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161007 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | TRIP-SAVER |  | 44556 | 2147 | 1583061 | 15072 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 1657920 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160872 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER |  | 44557 | 433 | 1584322 | 13438 | Distribution Circuit | Vegetation | Tree - branch fell on line | 318 | 2437389 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160956 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER |  | 44557 | 233 | 1593978 | 13780 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 68900 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161007 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER |  | 44557 | 36 | 1595112 | 13879 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 124911 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161007 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44557 | 233 | 1593986 | 13797 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 110376 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161007 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER |  | 44557 | 233 | 1593990 | 12380 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 74280 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161007 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER |  | 44557 | 724 | 1590678 | 7770 | Distribution Circuit | Vegetation | Tree - fell into line | 185 | 1437450 | Fog-Rain-Strong Winds-Snow-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161978 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 44557 | 419 | 1596685 | 16698 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 300564 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161022 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 44557 | 724 | 1591456 | 12003 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 601710 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 22-0005005 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44557 | 705 | 1591624 | 11845 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 47380 | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 22-0005049 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | TRIP-SAVER |  | 44556 | 2243 | 1583108 | 15072 | Distribution Circuit | Vegetation | Tree - branch fell on line | 160 | 2411520 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160886 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 44557 | 123 | 1596153 | 15074 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 497442 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0006621 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 44557 | 9 | 1583055 | 14132 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 211980 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160892 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 44556 | 133 | 1581988 | 587 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 30524 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0160678 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44557 | 402 | 1591627 | 12393 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 193701 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 22-0005050 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 44557 | 123 | 1594760 | 12604 | Distribution Circuit | Vegetation | Tree - fell into line | 317 | 3995468 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0161022 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER |  | 44557 | 126 | 1583742 | 16306 | Distribution Circuit | Vegetation | Tree - fell into line | 784 | 12208692 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160922 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | OTHER |  | 44557 | 1454 | 1585940 | 113 | Distribution Circuit | Vegetation | Tree - branch fell on line | 212 | 23956 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161145 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2102 | 254452102 | JUMPER |  | 44557 | 1235 | 1587372 | 1735 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 3470 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161415 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2101 | 252192101 | FUSE |  | 44557 | 928 | 1585321 | 3216 | Distribution Circuit | Vegetation | Tree - fell into line | 172 | 301849 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161195 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | JUMPER |  | 44557 | 820 | 1587597 | 3450 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10350 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0161013 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | JUMPER |  | 44557 | 819 | 1585652 | 1851 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3702 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161081 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE |  | 44557 | 2141 | 1586360 | 981 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 29187 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161276 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2101 | 252192101 | FUSE |  | 44557 | 1036 | 1585516 | 2859 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 94230 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161320 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER |  | 44557 | 2149 | 1586519 | 2486 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 278432 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161327 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44557 | 2149 | 1588698 | 2578 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 51560 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161327 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | FUSE |  | 44557 | 1048 | 1585627 | 259 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 14245 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161101 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44557 | 2149 | 1588701 | 3736 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 7472 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161327 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44557 | 2149 | 1588702 | 8215 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 21607 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161327 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | FUSE |  | 44557 | 1100 | 1585736 | 3135 | Distribution Circuit | Vegetation | Tree - fell into line | 263 | 824505 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161167 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | OTHER |  | 44556 | 453 | 1582365 | 493 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 20809 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160737 | OH | Sus | 0 | 2021 | DEC | Yes | Open Circuit | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 44557 | 1055 | 1585566 | 3024 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 108864 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 21-0161310 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | RECLOSER |  | 44557 | 1019 | 1585487 | 1761 | Distribution Circuit | Environmental/External | Ice or snow | 152 | 267672 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161068 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER |  | 44557 | 1039 | 1585527 | 6087 | Distribution Circuit | Vegetation | Tree - fell into line | 690 | 1116800 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161071 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER |  | 44544 | 713 | 1569907 | 1851 | Distribution Circuit | Equipment Failure/Involved | Overhead | 160 | 268189 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157826 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | FUSE |  | 44557 | 616 | 1585848 | 4974 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 100890 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161136 | OH | Sus | 0 | 2021 | DEC | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER |  | 44557 | 616 | 1584566 | 2005 | Distribution Circuit | Environmental/External | Ice or snow | 1612 | 951936 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0160979 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 44544 | 540 | 1569722 | 717 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 4199 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158125 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE |  | 44543 | 2055 | 1568754 | 506 | Distribution Circuit | Vegetation | Tree - fell into line | 259 | 131054 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0157627 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | FUSE |  | 44557 | 720 | 1584778 | 633 | Distribution Circuit | Vegetation | Tree - fell into line | 464 | 189292 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0161015 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | CURTIS-1705 | 163351705 | FUSE |  | 44557 | 1452 | 1586389 | 4688 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 83809 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161266 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | CURTIS-1705 | 163351705 | FUSE |  | 44557 | 728 | 1584791 | 3951 | Distribution Circuit | Vegetation | Tree - fell into line | 346 | 1367046 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161098 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44555 | 2239 | 1590093 | 8067 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 121005 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161883 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | JUMPER |  | 44555 | 1959 | 1582072 | 7201 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 14402 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160675 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44555 | 2239 | 1586768 | 7896 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 181608 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161335 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER |  | 44557 | 522 | 1587214 | 2198 | Distribution Circuit | Vegetation | Tree - fell into line | 524 | 1151752 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161380 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44555 | 2239 | 1582611 | 9353 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 121589 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160648 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | SWITCH |  | 44557 | 523 | 1587183 | 3898 | Distribution Circuit | Environmental/External | Ice or snow | 406 | 1582588 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161369 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44555 | 2239 | 1589539 | 9421 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 207262 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161757 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER |  | 44557 | 522 | 1587295 | 6566 | Distribution Circuit | Environmental/External | Ice or snow | 216 | 1242148 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161397 | OH | Sus | 0 | 2021 | DEC | Yes | None | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44557 | 523 | 1585682 | 5028 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 30168 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161091 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44555 | 2239 | 1582058 | 9410 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 467343 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160673 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44557 | 523 | 1586250 | 3898 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 124736 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161233 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 44544 | 523 | 1569737 | 635 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 46990 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0157884 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44555 | 2054 | 1581897 | 10831 | Distribution Circuit | Vegetation | Tree - fell into line | 263 | 2848553 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0160648 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44557 | 409 | 1585507 | 7864 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 220192 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160973 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44555 | 1959 | 1582166 | 824 | Distribution Circuit | Vegetation | Tree - fell into line | 241 | 198584 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160648 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44557 | 528 | 1585347 | 6461 | Distribution Circuit | Vegetation | Tree - fell into line | 211 | 1363271 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0161045 | OH | Sus | 0 | 2021 | DEC | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44557 | 528 | 1588811 | 7565 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 143735 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161630 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44557 | 523 | 1586146 | 6566 | Distribution Circuit | Environmental/External | Ice or snow | 26 | 170716 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160964 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | JUMPER |  | 44557 | 523 | 1586245 | 7919 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 31676 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0160964 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | JUMPER |  | 44557 | 523 | 1587622 | 9204 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 286429 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161460 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44557 | 523 | 1585884 | 10442 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 62652 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161138 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | JUMPER |  | 44557 | 523 | 1587639 | 7919 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 451383 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0161463 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44555 | 2133 | 1581866 | 753 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 75300 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160648 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | SWITCH |  | 44559 | 1430 | 1588882 | 5752 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 569448 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0161647 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44557 | 1321 | 1585803 | 5786 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 160062 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161597 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER |  | 44555 | 2146 | 1581868 | 11080 | Distribution Circuit | Vegetation | Tree - fell into line | 507 | 431715 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160643 | OH | Sus | 45101667 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44557 | 522 | 1584877 | 6756 | Distribution Circuit | Vegetation | Tree - fell into line | 316 | 2134296 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0160973 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | CURTIS-1704 | 163351704 | FUSE |  | 44559 | 1623 | 1588832 | 2752 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 11008 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161808 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER |  | 44555 | 2207 | 1581884 | 1213 | Distribution Circuit | Vegetation | Tree - fell into line | 2840 | 610113 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0160657 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | OTHER |  | 44559 | 735 | 1587963 | 1945 | Distribution Circuit | Vegetation | Tree - fell into line | 395 | 294328 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161532 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | FUSE |  | 44555 | 2149 | 1581799 | 5131 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 25655 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160858 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44557 | 102 | 1584146 | 8238 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 461328 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161177 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44557 | 221 | 1585679 | 9134 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 657648 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161089 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44555 | 2146 | 1585688 | 11080 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 188360 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161092 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44555 | 2146 | 1589826 | 11081 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 587293 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161814 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | OTHER |  | 44555 | 2146 | 1586275 | 11080 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 88640 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161242 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44555 | 2146 | 1590003 | 11080 | Distribution Circuit | Environmental/External | Ice or snow | 129 | 1429320 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0161867 | OH | Sus | 0 | 2021 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44544 | 554 | 1571329 | 1966 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 102232 | Clear;32-90F | Insulator | Broken- wire on ground | 21-0158088 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | OTHER |  | 44555 | 1855 | 1581615 | 11290 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 519856 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0160615 | OH | Sus | 45101639 | 2021 | DEC | Yes | Line to Ground | Yes | Yes
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | OTHER |  | 44543 | 2245 | 1569001 | 1142 | Distribution Circuit | Equipment Failure/Involved | Overhead | 692 | 787880 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 21-0157749 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE |  | 44557 | 1152 | 1586439 | 4634 | Distribution Circuit | Environmental/External | Ice or snow | 28 | 129374 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161547 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER |  | 44544 | 1820 | 1571756 | 1176 | Distribution Circuit | Vegetation | Tree - branch fell on line | 692 | 813700 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0158215 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | OTHER |  | 44559 | 721 | 1589039 | 3587 | Distribution Circuit | Environmental/External | Ice or snow | 155 | 555985 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0161692 | OH | Sus | 0 | 2021 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | FUSE |  | 44215 | 15 | 1214191 | 951 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 16167 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0010068 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | FUSE |  | 44215 | 853 | 1215368 | 282 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 1692 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010509 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | FUSE |  | 44223 | 231 | 1232342 | 3299 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 39167 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016490 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | FUSE |  | 44215 | 1414 | 1217929 | 1626 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11291 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011108 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | FUSE |  | 44223 | 644 | 1233283 | 1996 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 8507 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016101 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | RECLOSER |  | 44215 | 1655 | 1217739 | 422 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 52750 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011034 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | FUSE |  | 44223 | 2039 | 1239031 | 1303 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 24757 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017593 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE |  | 44222 | 2223 | 1231012 | 2166 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 121296 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017092 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 44223 | 41 | 1232244 | 2214 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 58072 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016681 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 44222 | 48 | 1231545 | 3592 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 56817 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016202 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | SWITCH |  | 44223 | 112 | 1233712 | 1106 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 99540 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 21-0015454 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 44223 | 108 | 1235547 | 1938 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 73644 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016254 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 44223 | 128 | 1235561 | 1914 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 11484 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016259 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 44223 | 741 | 1236979 | 1840 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 35680 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016714 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 44223 | 126 | 1234733 | 2015 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 28210 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016000 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 44223 | 1539 | 1236424 | 1578 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 17358 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016741 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | OCB |  | 44222 | 2220 | 1229570 | 1060 | Distribution Circuit | Vegetation | Tree - fell into line | 4842 | 349405 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0015224 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | RECLOSER |  | 44223 | 128 | 1231910 | 844 | Distribution Circuit | Vegetation | Tree - fell into line | 217 | 183148 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0015501 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2105 | 83692105 | SWITCH |  | 44215 | 738 | 1216604 | 2083 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 39577 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010333 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 44215 | 845 | 1218279 | 4472 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 17888 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0012446 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 44215 | 907 | 1216032 | 4330 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 177530 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010823 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 44215 | 743 | 1217517 | 2168 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 6504 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010951 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | RECLOSER |  | 44215 | 745 | 1215528 | 3669 | Distribution Circuit | Vegetation | Tree - fell into line | 436 | 637795 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010340 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 44215 | 631 | 1215089 | 3669 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 91725 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011310 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | 83500401 | 83500401 | FUSE |  | 44215 | 607 | 1216493 | 2223 | Distribution Circuit | Vegetation | Tree - branch fell on line | 75 | 166725 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010899 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 44215 | 846 | 1215901 | 2130 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 25560 | Clear;32-90 F | Transformer (OH) | Broken- wire on ground | 21-0011250 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 44215 | 723 | 1217235 | 3340 | Distribution Circuit | Vegetation | Tree - branch fell on line | 32 | 106880 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011017 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 44215 | 859 | 1217236 | 3041 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 66902 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011889 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 44215 | 752 | 1216503 | 6250 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 40810 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010620 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 44215 | 723 | 1217704 | 3340 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 3340 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011020 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 44215 | 1843 | 1218262 | 2810 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 126280 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011664 | OH | Sus | 0 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 44215 | 512 | 1214819 | 815 | Distribution Circuit | Equipment Failure/Involved | Overhead | 344 | 169471 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0010780 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE |  | 44224 | 1535 | 1240109 | 1306 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 23508 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017818 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 44215 | 633 | 1215935 | 3561 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 98082 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010436 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | SWITCH |  | 44215 | 723 | 1217954 | 3340 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 53440 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011113 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 44223 | 126 | 1231867 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 22680 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016100 | OH | Sus | 0 | 2021 | JAN | Yes |  | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE |  | 44215 | 533 | 1214870 | 1928 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 15424 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011245 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 44224 | 1634 | 1240197 | 842 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 53608 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017905 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 44215 | 909 | 1217826 | 1753 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 8765 | Strong Winds-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011067 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 44223 | 121 | 1234911 | 909 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4545 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016057 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 44214 | 2358 | 1217778 | 4096 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 97716 | Strong Winds-Clear;32-90 F | Conductor- Overhead | On Ground | 21-0011046 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 44214 | 2326 | 1213347 | 2619 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 159759 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010189 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 44215 | 2 | 1217772 | 3858 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 57870 | Strong Winds-Clear;32-90 F | Conductor- Overhead | On Ground | 21-0011044 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 44214 | 1941 | 1212896 | 2844 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 8859 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009848 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 44215 | 436 | 1219708 | 5007 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 65091 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011981 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | JUMPER |  | 44215 | 436 | 1219782 | 4890 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 19560 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0012028 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 44221 | 7 | 1222992 | 703 | Distribution Circuit | Vegetation | Tree - branch fell on line | 558 | 164396 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0013541 | OH | Sus | 44633345 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 44214 | 2221 | 1213127 | 8619 | Distribution Circuit | Vegetation | Tree - fell into line | 665 | 3239677 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009874 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 44222 | 2227 | 1232023 | 1002 | Distribution Circuit | Vegetation | Tree - branch fell on line | 60 | 60120 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0015951 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 44215 | 436 | 1219785 | 5091 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 280071 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0012031 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 44215 | 436 | 1219345 | 5082 | Distribution Circuit | Vegetation | Tree - grew into line | 38 | 193116 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0011788 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 44215 | 436 | 1220292 | 3982 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 67694 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0012297 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 44215 | 435 | 1215430 | 4870 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 48700 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011695 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 44215 | 37 | 1219307 | 3953 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 59295 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0011783 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44215 | 37 | 1218968 | 3720 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 100440 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011602 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 44214 | 2159 | 1213043 | 5590 | Distribution Circuit | Equipment Failure/Involved | Overhead | 77 | 430430 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009860 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 44215 | 37 | 1219202 | 3808 | Distribution Circuit | Vegetation | Tree - branch fell on line | 120 | 456960 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011721 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | SWITCH |  | 44215 | 436 | 1217767 | 3018 | Distribution Circuit | Vegetation | Tree - fell into line | 1024 | 2380932 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011043 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 44215 | 1025 | 1217223 | 499 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 10479 | Strong Winds-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011105 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 44215 | 37 | 1213185 | 2534 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 40944 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009963 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2106 | 83622106 | TRIP-SAVER |  | 44215 | 436 | 1221404 | 7614 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 251262 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0012859 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE |  | 44215 | 845 | 1215897 | 2070 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 10350 | Strong Winds-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010764 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44215 | 20 | 1218159 | 3948 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 63168 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011232 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44214 | 2221 | 1221232 | 6791 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 20373 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0012795 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44215 | 500 | 1218940 | 3734 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 140337 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011589 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 44215 | 411 | 1214560 | 2105 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 23155 | Strong Winds; | Conductor- Overhead | Broken- wire on ground | 21-0010153 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44223 | 245 | 1232391 | 637 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 8281 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0015778 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44215 | 17 | 1218160 | 3951 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 11853 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011233 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | RECLOSER |  | 44215 | 339 | 1217867 | 6340 | Distribution Circuit | Equipment Failure/Involved | Overhead | 306 | 1210924 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011076 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | SWITCH |  | 44215 | 411 | 1216277 | 2105 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 65255 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010153 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44215 | 441 | 1218925 | 3532 | Distribution Circuit | Equipment Failure/Involved | Overhead | 163 | 377099 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011575 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 44215 | 408 | 1214549 | 2235 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 109530 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010643 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER |  | 44215 | 458 | 1217999 | 3490 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6980 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011127 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 44221 | 759 | 1223696 | 343 | Distribution Circuit | Vegetation | Tree - fell into line | 2398 | 306988 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0013669 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER |  | 44215 | 440 | 1214789 | 1996 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 144618 | Clear;32-90 F | Pole-Wood | Broken- wire on object | 21-0010191 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44214 | 2221 | 1220174 | 5418 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 92106 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0012261 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44223 | 46 | 1231559 | 703 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 11951 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0015710 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE |  | 44223 | 2356 | 1238548 | 676 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2704 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017127 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 44215 | 339 | 1218188 | 3718 | Distribution Circuit | Equipment Failure/Involved | Overhead | 79 | 293722 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011076 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44214 | 2221 | 1217479 | 6597 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 219065 | Strong Winds-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010929 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44215 | 104 | 1218142 | 2590 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 155400 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0011223 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 44215 | 339 | 1218187 | 6340 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 12680 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011076 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | SWITCH |  | 44215 | 339 | 1219124 | 6340 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 843220 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011691 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | JUMPER |  | 44214 | 2221 | 1221794 | 7899 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 31596 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 21-0013267 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | JUMPER |  | 44215 | 339 | 1221803 | 6711 | Distribution Circuit | Vegetation | Tree - branch fell on line | 188 | 10690 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0011076 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER |  | 44214 | 2343 | 1214356 | 5267 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2906 | 8809273 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010168 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | JUMPER |  | 44215 | 41 | 1221607 | 6799 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 61191 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0013207 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 44215 | 20 | 1213589 | 3948 | Distribution Circuit | Vegetation | Tree - branch fell on line | 361 | 1363694 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009947 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44215 | 419 | 1218716 | 6457 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 6457 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010159 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44215 | 416 | 1219299 | 5266 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 136916 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011753 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44215 | 17 | 1221136 | 5263 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 105260 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0012724 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44215 | 441 | 1219301 | 5061 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 126525 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011756 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44223 | 614 | 1233126 | 698 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 11866 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0016234 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER |  | 44214 | 2343 | 1219159 | 5542 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 88672 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011705 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44214 | 2256 | 1220138 | 4090 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 331290 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0012240 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 44214 | 2343 | 1219220 | 5937 | Distribution Circuit | Vegetation | Tree - branch fell on line | 102 | 386968 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011728 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44215 | 140 | 1217674 | 3795 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 208725 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011010 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44214 | 2343 | 1217122 | 2670 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 8010 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0010787 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44214 | 2221 | 1220008 | 6957 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6957 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0012161 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | JUMPER |  | 44214 | 2343 | 1217762 | 4237 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 25422 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011040 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 44214 | 2343 | 1219380 | 6808 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 108928 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011815 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER |  | 44215 | 419 | 1219136 | 6434 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 6434 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011697 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44214 | 2358 | 1220656 | 5007 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 20028 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0012541 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | JUMPER |  | 44215 | 537 | 1219267 | 3536 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 48474 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011744 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | JUMPER |  | 44215 | 339 | 1220123 | 6326 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 37956 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0012237 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44224 | 631 | 1238626 | 516 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 8772 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017284 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44214 | 2343 | 1220179 | 5157 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 82512 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0012262 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44215 | 421 | 1220180 | 4861 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 92984 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0012263 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 44214 | 2343 | 1219384 | 5482 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 109302 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011817 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44214 | 2256 | 1220078 | 5015 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 50150 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0012211 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 44223 | 1027 | 1234876 | 388 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 3262 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016196 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44214 | 1001 | 1212381 | 532 | Distribution Circuit | Vegetation | Tree - branch fell on line | 85 | 37226 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009704 | OH | Sus | 44628039 | 2021 | JAN | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44214 | 2255 | 1220632 | 6455 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 548675 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0012051 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 44214 | 2343 | 1219386 | 5227 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 31362 | Clear;32-90 F | Insulator | Broken- wire on ground | 21-0011819 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44215 | 114 | 1221325 | 6352 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 31760 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0012828 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | OTHER |  | 44214 | 2343 | 1220083 | 5267 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 10534 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0012217 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | SWITCH |  | 44215 | 441 | 1221273 | 5108 | Distribution Circuit | Vegetation | Tree - fell into line | 203 | 1036924 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0012778 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER |  | 44215 | 548 | 1215194 | 4971 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1051 | 4815798 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010366 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44214 | 2358 | 1221170 | 5317 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 47853 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0012755 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 44215 | 553 | 1213479 | 4876 | Distribution Circuit | Vegetation | Tree - branch fell on line | 473 | 2306348 | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 21-0010219 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 44223 | 2049 | 1237733 | 89 | Distribution Circuit | Vegetation | Tree - fell into line | 584 | 51976 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016912 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | TRIP-SAVER |  | 44215 | 224 | 1218141 | 5218 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 151322 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011221 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44214 | 2358 | 1221172 | 5444 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 27220 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0012051 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44223 | 2049 | 1237885 | 302 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 15100 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0016971 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44215 | 401 | 1221126 | 6241 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 49928 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0012716 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44215 | 401 | 1221124 | 6385 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 140470 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0012715 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44215 | 217 | 1218112 | 4934 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 9868 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011199 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44215 | 212 | 1218117 | 4939 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 39512 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011201 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44215 | 203 | 1218119 | 4948 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 277088 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011202 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 44215 | 704 | 1213861 | 3636 | Distribution Circuit | Equipment Failure/Involved | Overhead | 721 | 1753036 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010295 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44215 | 6 | 1218124 | 5217 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 198246 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011209 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44215 | 10 | 1219191 | 5219 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 184840 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011719 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44215 | 10 | 1218969 | 5219 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 5219 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011601 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44215 | 255 | 1220507 | 5054 | Distribution Circuit | Vegetation | Tree - branch fell on line | 146 | 512540 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0012439 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44215 | 12 | 1221146 | 5217 | Distribution Circuit | Vegetation | Tree - branch fell on line | 32 | 166944 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0012734 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44215 | 10 | 1219138 | 5337 | Distribution Circuit | Equipment Failure/Involved | Overhead | 91 | 485667 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011698 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44215 | 224 | 1218127 | 5139 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5139 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011210 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44215 | 626 | 1215046 | 2199 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 92040 | Strong Winds-Clear;32-90 F | Conductor- Overhead | On Ground | 21-0011650 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44221 | 2240 | 1225431 | 835 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 12482 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 21-0014252 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44215 | 623 | 1217801 | 4512 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 76704 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011056 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 44215 | 658 | 1218771 | 5130 | Distribution Circuit | Vegetation | Tree - fell into line | 561 | 2836753 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011729 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | TRIP-SAVER |  | 44215 | 52 | 1218072 | 5496 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 120912 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011174 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44215 | 52 | 1218726 | 6720 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 120960 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011482 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER |  | 44215 | 52 | 1221370 | 6713 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6713 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0012850 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | TRIP-SAVER |  | 44215 | 122 | 1218125 | 4906 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 310184 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0010143 | OH | Sus | 35226315 | 2021 | JAN | Yes | None | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44215 | 38 | 1218470 | 3819 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 179493 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011348 | OH | Sus | 44627315 | 2021 | JAN | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44215 | 121 | 1218018 | 3722 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 14888 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0011146 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | JUMPER |  | 44215 | 121 | 1218015 | 3718 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 89232 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0011142 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44215 | 124 | 1218076 | 2477 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 71833 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011176 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44214 | 2335 | 1217159 | 3828 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 122496 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010799 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44222 | 1716 | 1226639 | 2884 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 130841 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0014890 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44224 | 1100 | 1239403 | 1035 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 5175 | Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017876 | OH | Sus | 35227618 | 2021 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER |  | 44223 | 132 | 1231923 | 2381 | Distribution Circuit | Equipment Failure/Involved | Overhead | 248 | 176225 | Strong Winds-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015496 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER |  | 44215 | 353 | 1214228 | 4926 | Distribution Circuit | Vegetation | Tree - fell into line | 465 | 1212925 | Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 21-0010143 | OH | Sus | 35226315 | 2021 | JAN | Yes | Force Out | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 44214 | 2358 | 1213412 | 5001 | Distribution Circuit | Equipment Failure/Involved | Overhead | 722 | 2120642 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009932 | OH | Sus | 35226315 | 2021 | JAN | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44214 | 1649 | 1212821 | 3170 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3170 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009799 | OH | Sus | 44627317 | 2021 | JAN | Yes | None | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 44214 | 950 | 1212195 | 493 | Distribution Circuit | Vegetation | Tree - branch fell on line | 337 | 30511 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009632 | OH | Sus | 31528401 | 2021 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | SWITCH |  | 44215 | 353 | 1218123 | 3525 | Distribution Circuit | Vegetation | Tree - fell into line | 680 | 718607 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010143 | OH | Sus | 35226315 | 2021 | JAN | Yes | Multi-Fault | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44223 | 1200 | 1236669 | 2982 | Distribution Circuit | Environmental/External | Ice or snow | 14 | 41748 | Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016837 | OH | Sus | 35227618 | 2021 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER |  | 44215 | 132 | 1213779 | 3730 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 341510 | Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010069 | OH | Sus | 35226315 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 2 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 44215 | 945 | 1216235 | 2110 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 282740 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010548 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 44215 | 16 | 1213554 | 3928 | Distribution Circuit | Vegetation | Tree - fell into line | 1205 | 1761114 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 21-0009943 | OH | Sus | 44627315 | 2021 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | LOS GATOS-1108 | 82021108 | FUSE |  | 44215 | 749 | 1215595 | 3399 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 23793 | Strong Winds-Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010842 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | OTHER |  | 44221 | 115 | 1223103 | 609 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 12931 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0013574 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE |  | 44215 | 155 | 1214992 | 2336 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 14016 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010533 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | OTHER |  | 44222 | 1911 | 1227191 | 291 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2454 | 52546 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0014918 | OH | Sus | 44634639 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | STELLING-1110 | 83481110 | RECLOSER |  | 44215 | 128 | 1213875 | 2647 | Distribution Circuit | Vegetation | Tree - fell into line | 210 | 555870 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009998 | OH | Sus | 35226315 | 2021 | JAN | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | MORAGA-1104 | 13801104 | OCB |  | 44214 | 2314 | 1213286 | 956 | Distribution Circuit | Vegetation | Tree - fell into line | 602 | 216667 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0009908 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | ROSSMOOR-1101 | 14161101 | FUSE |  | 44214 | 2314 | 1213290 | 240 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 4320 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009933 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAKLAND X-1106 | 12541106 | FUSE |  | 44222 | 2220 | 1234514 | 2087 | Distribution Circuit | Vegetation | Tree - branch fell on line | 58 | 113066 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0015931 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 2 | OAKLAND J-1102 | 12091102 | JUMPER |  | 44222 | 2238 | 1232679 | 2144 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 63505 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0015791 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 2 | BOSTON-0401 | 13320401 | OTHER |  | 44215 | 322 | 1214410 | 437 | Distribution Circuit | Equipment Failure/Involved | Overhead | 314 | 124442 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010158 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | JUMPER |  | 44215 | 351 | 1215050 | 1427 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 34089 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010244 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | OTHER |  | 44215 | 946 | 1216517 | 422 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1266 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0010704 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE |  | 44215 | 401 | 1214532 | 2103 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 96738 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0011410 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | OTHER |  | 44215 | 337 | 1214456 | 933 | Distribution Circuit | Equipment Failure/Involved | Overhead | 474 | 334202 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010251 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 2 | OAKLAND K-1102 | 12101102 | OCB |  | 44215 | 646 | 1215189 | 411 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1340 | 357711 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010280 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | SPRUCE-0402 | 13340402 | FUSE |  | 44215 | 726 | 1215589 | 591 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 12411 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010529 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | WALDO-0402 | 13350402 | FUSE |  | 44215 | 344 | 1214493 | 922 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 81136 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010502 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | EL CERRITO G-1105 | 12501105 | FUSE |  | 44215 | 648 | 1215170 | 430 | Distribution Circuit | Company Initiated | Improper Construction | 136 | 58480 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010425 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | EL CERRITO G-1105 | 12501105 | FUSE |  | 44215 | 1215 | 1217017 | 442 | Distribution Circuit | Equipment Failure/Involved | Overhead | 117 | 51714 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010755 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-0001 | 254060001 | RECLOSER |  | 44215 | 543 | 1214847 | 2096 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 19 | 39729 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009491 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 44223 | 1409 | 1235969 | 1286 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1286 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016440 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 44222 | 2010 | 1227816 | 1267 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 8869 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016339 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE |  | 44222 | 2027 | 1230434 | 5350 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 160500 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016041 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE |  | 44222 | 2212 | 1235269 | 5508 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 159732 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0016161 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | JUMPER |  | 44222 | 2208 | 1235279 | 5367 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 80505 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016166 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | RECLOSER |  | 44222 | 2037 | 1228079 | 5614 | Distribution Circuit | Vegetation | Tree - fell into line | 307 | 1723498 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0014994 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | JUMPER |  | 44222 | 2057 | 1228299 | 900 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 49505 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015168 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE |  | 44222 | 2037 | 1243071 | 5614 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 16842 | Clear;32-90F | Conductor- Overhead | On Ground | 21-0019265 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | FUSE |  | 44222 | 2220 | 1243162 | 8265 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 60110 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019285 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | FUSE |  | 44214 | 2237 | 1213174 | 1044 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8352 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010064 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HIGHLANDS-1103 | 43361103 | SWITCH |  | 44223 | 646 | 1242001 | 6627 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 92778 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0016763 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | JUMPER |  | 44222 | 1938 | 1242149 | 8032 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 24096 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0018533 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | JUMPER |  | 44222 | 1938 | 1242157 | 7140 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 7140 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0018537 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | OTHER |  | 44222 | 2240 | 1236420 | 5405 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 122623 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016561 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | OTHER |  | 44222 | 2240 | 1235148 | 989 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1978 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016119 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | Yes
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER |  | 44214 | 2247 | 1213187 | 791 | Distribution Circuit | Vegetation | Tree - fell into line | 826 | 151636 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009880 | OH | Sus | 0 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | FUSE |  | 44222 | 2240 | 1235155 | 6900 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 41400 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016123 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | KONOCTI-1102 | 43311102 | FUSE |  | 44223 | 1259 | 1235677 | 5789 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 34734 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0018265 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | KONOCTI-1102 | 43311102 | RECLOSER |  | 44215 | 142 | 1214075 | 818 | Distribution Circuit | Vegetation | Tree - fell into line | 305 | 100272 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010034 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | KONOCTI-1108 | 43311108 | RECLOSER |  | 44222 | 2234 | 1230405 | 816 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1030 | 840480 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015345 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | UKIAH-1114 | 42771114 | JUMPER |  | 44224 | 1145 | 1239521 | 4240 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 4240 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017460 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | FUSE |  | 44222 | 2101 | 1228380 | 3768 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 90432 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016231 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HARTLEY-1101 | 43211101 | FUSE |  | 44222 | 2243 | 1236897 | 5022 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 18227 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016693 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | UKIAH-1114 | 42771114 | FUSE |  | 44222 | 2134 | 1228980 | 2321 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 148544 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0017466 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | UKIAH-1114 | 42771114 | FUSE |  | 44222 | 2129 | 1228786 | 5606 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5606 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019352 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 42871101 | SWITCH |  | 44222 | 2203 | 1236046 | 2295 | Distribution Circuit | Vegetation | Tree - fell into line | 174 | 399330 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016453 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 42871101 | RECLOSER |  | 44222 | 2206 | 1229340 | 4149 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 285695 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0015199 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE |  | 44223 | 1047 | 1236761 | 5933 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 71196 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 21-0019914 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE |  | 44222 | 2203 | 1236064 | 2556 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 104796 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016458 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | UKIAH-1111 | 42771111 | FUSE |  | 44222 | 2000 | 1227767 | 5576 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 219524 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016364 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | UKIAH-1111 | 42771111 | FUSE |  | 44222 | 2000 | 1236947 | 2636 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5272 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016704 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | CALPELLA-1101 | 43411101 | FUSE |  | 44224 | 1916 | 1240614 | 2727 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 220992 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017957 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | CALPELLA-1101 | 43411101 | FUSE |  | 44223 | 1834 | 1240635 | 3998 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 179910 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017960 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | MENDOCINO-1101 | 42951101 | RECLOSER |  | 44222 | 2140 | 1229051 | 3594 | Distribution Circuit | Vegetation | Tree - fell into line | 575 | 1268005 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015153 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | MENDOCINO-1101 | 42951101 | FUSE |  | 44222 | 2138 | 1229260 | 5162 | Distribution Circuit | Vegetation | Tree - fell into line | 139 | 403790 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017766 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | MENDOCINO-1101 | 42951101 | RECLOSER |  | 44222 | 2046 | 1227688 | 7065 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 305169 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015027 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | MENDOCINO-1101 | 42951101 | FUSE |  | 44222 | 2052 | 1236833 | 5638 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 45104 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016677 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 44222 | 1858 | 1227095 | 854 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 11102 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0014970 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | FUSE |  | 44222 | 2144 | 1245455 | 9546 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 28638 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0020598 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | FUSE |  | 44222 | 2153 | 1245453 | 9666 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 927936 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0020596 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | FUSE |  | 44222 | 2144 | 1245452 | 9961 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 89649 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0020595 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | FUSE |  | 44222 | 2149 | 1236939 | 6890 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 330720 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016702 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | FUSE |  | 44222 | 2153 | 1236935 | 8382 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 326898 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016698 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE |  | 44222 | 1645 | 1243983 | 8758 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 8758 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0020020 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE |  | 44222 | 1645 | 1243982 | 8758 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 78822 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0020019 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MENDOCINO-1101 | 42951101 | FUSE |  | 44222 | 2052 | 1244144 | 8256 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 417744 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0020033 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE |  | 44222 | 1645 | 1226477 | 8758 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 113854 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0020017 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 44222 | 1947 | 1245021 | 9916 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 19832 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0020404 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE |  | 44223 | 1809 | 1237088 | 4447 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 57415 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0017894 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | JUMPER |  | 44222 | 2144 | 1229054 | 1205 | Distribution Circuit | Vegetation | Tree - fell into line | 193 | 134544 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016203 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | Yes
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 44222 | 1946 | 1245015 | 9917 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 138838 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0020402 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MENDOCINO-1101 | 42951101 | OTHER |  | 44222 | 2000 | 1241042 | 8267 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 262875 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0018147 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | JUMPER |  | 44222 | 1946 | 1247280 | 12554 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 12554 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0021498 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | FUSE |  | 44222 | 2016 | 1240988 | 7198 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7198 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0018136 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 44222 | 2131 | 1241837 | 8240 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 41200 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0018396 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER |  | 44222 | 1743 | 1226702 | 70 | Distribution Circuit | Vegetation | Tree - fell into line | 369 | 25830 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0014773 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 44222 | 1946 | 1231656 | 12615 | Distribution Circuit | Vegetation | Tree - fell into line | 201 | 1897568 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0015125 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | RECLOSER |  | 44222 | 2033 | 1226800 | 2782 | Distribution Circuit | Vegetation | Tree - fell into line | 234 | 640943 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0014986 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | JUMPER |  | 44222 | 2055 | 1243859 | 7983 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 47898 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019981 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | JUMPER |  | 44222 | 1812 | 1243868 | 8194 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 8194 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019982 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 44222 | 2124 | 1228711 | 8014 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 248434 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019944 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER |  | 44222 | 1926 | 1226497 | 6823 | Distribution Circuit | Vegetation | Tree - fell into line | 339 | 1761964 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0014875 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER |  | 44222 | 2055 | 1226779 | 11345 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 889466 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015035 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE |  | 44222 | 1815 | 1240507 | 9806 | Distribution Circuit | Environmental/External | Ice or snow | 132 | 1294392 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0017914 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE |  | 44222 | 2001 | 1240509 | 9977 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 59862 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017916 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE |  | 44222 | 1853 | 1240514 | 8344 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 41720 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017918 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE |  | 44222 | 1608 | 1241369 | 8669 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 69352 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0018226 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | RECLOSER |  | 44222 | 1610 | 1226414 | 7059 | Distribution Circuit | Vegetation | Tree - branch fell on line | 247 | 1208116 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0014716 | OH | Sus | 0 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE |  | 44222 | 1618 | 1242425 | 8331 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 241599 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0018657 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE |  | 44222 | 1610 | 1242247 | 6951 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 257187 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0018592 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | JUMPER |  | 44222 | 1608 | 1243760 | 8572 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 51432 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019949 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE |  | 44222 | 1608 | 1242432 | 5783 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 34698 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0018659 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER |  | 44222 | 2133 | 1226824 | 8259 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 255071 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015124 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE |  | 44222 | 1608 | 1242347 | 9785 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 58710 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0018632 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 44222 | 1926 | 1231553 | 6916 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 269724 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0015430 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | JUMPER |  | 44222 | 1608 | 1242271 | 7287 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 14574 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0018606 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE |  | 44222 | 1612 | 1243484 | 8638 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 129570 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019371 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 44222 | 1648 | 1241537 | 6981 | Distribution Circuit | Vegetation | Tree - fell into line | 143 | 998283 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0014875 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 44222 | 1935 | 1243893 | 6997 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 83964 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019995 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | JUMPER |  | 44222 | 1608 | 1242264 | 8805 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 8805 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0018602 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 44222 | 2117 | 1228607 | 11238 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 67428 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 21-0020540 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER |  | 44222 | 1637 | 1226459 | 11667 | Distribution Circuit | Environmental/External | Ice or snow | 98 | 1069966 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0014737 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 44222 | 1926 | 1243285 | 11070 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 33210 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 21-0019324 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 44222 | 1637 | 1246401 | 10199 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 193781 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0021031 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 44222 | 1637 | 1243875 | 10199 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 30597 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019989 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | OTHER |  | 44222 | 1926 | 1242921 | 8683 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 109763 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019213 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 44222 | 1926 | 1242925 | 9944 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 278432 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019215 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 44222 | 1637 | 1243874 | 11666 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 116660 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019988 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 44222 | 1839 | 1226823 | 1372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 27440 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015204 | OH | Sus | 0 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 44222 | 1637 | 1243872 | 11666 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 151658 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019987 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 44222 | 1637 | 1243869 | 11667 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 175005 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019985 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44222 | 1612 | 1244785 | 10156 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 40624 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0020305 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | RECLOSER |  | 44222 | 1612 | 1226409 | 11153 | Distribution Circuit | Vegetation | Tree - fell into line | 281 | 1125901 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0014715 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44222 | 1843 | 1240527 | 8475 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 144075 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017924 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44222 | 1843 | 1242404 | 9897 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 227631 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0018642 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44222 | 1843 | 1237317 | 7181 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 136439 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016799 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44222 | 1843 | 1240592 | 9647 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 9647 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0017948 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44222 | 1843 | 1240603 | 8291 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 124365 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017950 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44222 | 1843 | 1237229 | 8572 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 8572 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016782 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44222 | 1843 | 1240586 | 8306 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 299016 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017943 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44222 | 1843 | 1237407 | 9448 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 47240 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016814 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44222 | 1843 | 1240557 | 6979 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 153538 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0017935 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44222 | 1843 | 1237409 | 7047 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 119799 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016817 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44222 | 1843 | 1237371 | 6909 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 462903 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016808 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44222 | 1843 | 1237336 | 5718 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 45744 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016804 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 44222 | 1927 | 1237462 | 6918 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 159114 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0016838 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 44222 | 1832 | 1243189 | 7034 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 63306 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019295 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44222 | 1843 | 1238874 | 10144 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 436192 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017216 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 44222 | 1832 | 1242297 | 6932 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 55456 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0018559 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 44222 | 1832 | 1242189 | 7108 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 277212 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0018559 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 44222 | 1927 | 1244146 | 8620 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 68960 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0018559 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 44222 | 1832 | 1244216 | 9744 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 97440 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0020046 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 44222 | 1932 | 1244217 | 8624 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 43120 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0020047 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 44222 | 1719 | 1242203 | 5814 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 98838 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0018567 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 44222 | 1719 | 1236576 | 8346 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 33384 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016604 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 44222 | 1719 | 1242197 | 8643 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 527223 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0018564 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 44222 | 1719 | 1243099 | 13097 | Distribution Circuit | Equipment Failure/Involved | Overhead | 96 | 1257312 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019275 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 44214 | 616 | 1212113 | 2014 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 6042 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0009700 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 44214 | 248 | 1212078 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3600 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009573 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 44222 | 2216 | 1226525 | 5303 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 53030 | Clear;32-90F | Conductor- Overhead | On Ground | 21-0019198 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE |  | 44222 | 1939 | 1240113 | 7057 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 28228 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0014993 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE |  | 44222 | 2017 | 1240097 | 5611 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 112117 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0014993 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER |  | 44222 | 2017 | 1227876 | 4224 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 143616 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0014993 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 44221 | 1027 | 1224145 | 159 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 477 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0013792 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER |  | 44224 | 1745 | 1240385 | 222 | Distribution Circuit | Vegetation | Tree - fell into line | 146 | 32412 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017859 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER |  | 44222 | 1708 | 1226433 | 8712 | Distribution Circuit | Vegetation | Tree - fell into line | 347 | 215664 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0014752 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 44222 | 2044 | 1240293 | 6803 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 312938 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015469 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | JUMPER |  | 44222 | 2200 | 1240337 | 5445 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 10890 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0017844 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | JUMPER |  | 44222 | 2200 | 1240334 | 5475 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 32850 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017844 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 44222 | 1541 | 1226346 | 289 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 27455 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0014749 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER |  | 44215 | 1023 | 1216422 | 1571 | Distribution Circuit | Vegetation | Tree - fell into line | 144 | 226224 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010594 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER |  | 44222 | 2021 | 1227932 | 4251 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 136080 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0014954 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | BRIDGEVILLE-1102 | 192461102 | FUSE |  | 44223 | 1700 | 1227831 | 4429 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 36239 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016739 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER |  | 44215 | 546 | 1214919 | 1057 | Distribution Circuit | Vegetation | Tree - fell into line | 319 | 80153 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010215 | OH | Sus | 0 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | FUSE |  | 44215 | 210 | 1216743 | 2325 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 46500 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010683 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER |  | 44222 | 1255 | 1226028 | 235 | Distribution Circuit | Equipment Failure/Involved | Overhead | 210 | 7772 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 21-0014550 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | RECLOSER |  | 44222 | 2003 | 1227772 | 5366 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 120802 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0014932 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | FUSE |  | 44222 | 2003 | 1242121 | 5505 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 49545 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0018514 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | MAPLE CREEK-1101 | 192101101 | OCB |  | 44222 | 1430 | 1226154 | 2824 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 71384 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0014621 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | HARRIS-1109 | 192431109 | FUSE |  | 44222 | 1633 | 1226438 | 1518 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 39468 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0014910 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | FUSE |  | 44223 | 854 | 1234154 | 3417 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 13668 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016293 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | FUSE |  | 44222 | 1744 | 1226692 | 5626 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 22504 | Clear;32-90F | Conductor- Overhead | On Ground | 21-0019185 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | FUSE |  | 44222 | 1434 | 1226450 | 4354 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 39186 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0014731 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44222 | 1853 | 1240057 | 8540 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 187845 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017745 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER |  | 44222 | 1853 | 1227205 | 9847 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 212533 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0014845 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 44223 | 2106 | 1237774 | 2679 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 10716 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017031 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 44224 | 1515 | 1240050 | 3055 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3055 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0017742 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 44222 | 1856 | 1240277 | 7084 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 141680 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0017824 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
LOS PADRES | Tier 2 | BUELLTON-1101 | 183041101 | FUSE |  | 44215 | 1223 | 1217455 | 382 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 2674 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0010922 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
LOS PADRES | Tier 2 | SISQUOC-1102 | 182811102 | FUSE |  | 44221 | 5 | 1222977 | 2273 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 16934 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0013737 | OH | Sus | 44634413 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
LOS PADRES | Tier 2 | MORRO BAY-1102 | 183011102 | FUSE |  | 44221 | 1518 | 1224849 | 737 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 28743 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0014145 | OH | Sus | 0 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
LOS PADRES | Tier 2 | GOLDTREE-1107 | 182581107 | OCB |  | 44223 | 1642 | 1236737 | 592 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 18989 | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 21-0016644 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE |  | 44223 | 939 | 1233840 | 1976 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 5928 | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 21-0015925 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | RECLOSER |  | 44223 | 1241 | 1235590 | 1384 | Distribution Circuit | Vegetation | Tree - fell into line | 369 | 197607 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0016265 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE |  | 44223 | 1345 | 1235887 | 1774 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 92248 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0016703 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | RECLOSER |  | 44215 | 1142 | 1216804 | 589 | Distribution Circuit | Vegetation | Tree - fell into line | 783 | 64893 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 21-0010709 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE |  | 44223 | 1252 | 1235654 | 1710 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 138510 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0016684 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | RECLOSER |  | 44223 | 251 | 1232418 | 436 | Distribution Circuit | Vegetation | Tree - fell into line | 1579 | 233641 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0015564 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | RECLOSER |  | 44223 | 1951 | 1237135 | 1448 | Distribution Circuit | Vegetation | Tree - fell into line | 1822 | 865463 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0016859 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE |  | 44223 | 1253 | 1235963 | 2120 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 40280 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017834 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | CAMBRIA-1102 | 182771102 | FUSE |  | 44223 | 1138 | 1235242 | 1627 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 135041 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0016371 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2110 | 183052110 | FUSE |  | 44223 | 1826 | 1237143 | 2783 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 5566 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0017465 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | SAUSALITO-1102 | 42491102 | JUMPER |  | 44214 | 2043 | 1212926 | 1128 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 17761 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009854 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | SAN RAFAEL-1109 | 42011109 | FUSE |  | 44215 | 1447 | 1217443 | 1332 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 23976 | Strong Winds-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011088 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | Yes
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | JUMPER |  | 44215 | 216 | 1214175 | 949 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2813 | Strong Winds-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010771 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 44223 | 1542 | 1235569 | 649 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3894 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0016568 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 44215 | 421 | 1214621 | 845 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 56615 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0010406 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 44222 | 2030 | 1228038 | 365 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 12410 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0015136 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER |  | 44222 | 2121 | 1228665 | 1307 | Distribution Circuit | Vegetation | Tree - fell into line | 140 | 172251 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0015097 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | PUEBLO-1105 | 43291105 | OTHER |  | 44214 | 537 | 1212105 | 428 | Distribution Circuit | Vegetation | Tree - fell into line | 148 | 34744 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009586 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SILVERADO-2105 | 43432105 | FUSE |  | 44215 | 441 | 1214705 | 800 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4000 | Strong Winds-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010761 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1102 | 42711102 | RECLOSER |  | 44214 | 435 | 1212094 | 495 | Distribution Circuit | Vegetation | Tree - branch fell on line | 70 | 7113 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009557 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER |  | 44215 | 331 | 1214440 | 537 | Distribution Circuit | Vegetation | Tree - fell into line | 739 | 356565 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0010126 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE |  | 44214 | 854 | 1212242 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4230 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009698 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | CALISTOGA-1101 | 42711101 | RECLOSER |  | 44214 | 530 | 1212104 | 466 | Distribution Circuit | Vegetation | Tree - fell into line | 161 | 75026 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009559 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 44222 | 1721 | 1226654 | 1243 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 10010 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0014840 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | FUSE |  | 44224 | 1240 | 1239630 | 2830 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5660 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017527 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | JUMPER |  | 44224 | 1701 | 1242467 | 2719 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5438 | Snow; | Conductor- Overhead | Broken- wire on ground | 21-0018674 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER |  | 44224 | 516 | 1238542 | 2281 | Distribution Circuit | Vegetation | Tree - fell into line | 285 | 340772 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017132 | OH | Sus | 0 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | JUMPER |  | 44224 | 520 | 1242454 | 3692 | Distribution Circuit | Vegetation | Tree - fell into line | 410 | 1513720 | Snow; | Conductor- Overhead | Broken- wire on ground | 21-0018667 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | FUSE |  | 44224 | 516 | 1243450 | 5064 | Distribution Circuit | Environmental/External | Ice or snow | 3 | 15192 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019364 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ELK CREEK-1101 | 102781101 | FUSE |  | 44222 | 2221 | 1239247 | 2572 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 15432 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017321 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | FUSE |  | 44215 | 633 | 1215104 | 2358 | Distribution Circuit | Vegetation | Tree - fell into line | 331 | 496901 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0010281 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | SWITCH |  | 44215 | 218 | 1214923 | 2767 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 80243 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0010216 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1104 | 102831104 | FUSE |  | 44214 | 421 | 1212092 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 9792 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0009558 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | CORNING-1102 | 103331102 | FUSE |  | 44224 | 1003 | 1239240 | 445 | Distribution Circuit | Environmental/External | Ice or snow | 8 | 1798 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017650 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | OCB |  | 44223 | 159 | 1232087 | 891 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2336 | 1346507 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015526 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER |  | 44222 | 2237 | 1229899 | 2699 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1092 | 2083969 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015259 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | CORNING-1102 | 103331102 | FUSE |  | 44223 | 653 | 1233339 | 3321 | Distribution Circuit | Environmental/External | Ice or snow | 12 | 23136 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0015832 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | FUSE |  | 44215 | 1112 | 1216627 | 336 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 6384 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0010794 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | FUSE |  | 44223 | 2156 | 1238955 | 1034 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 112064 | Clear;32-90F | Conductor- Overhead | On Ground | 21-0017313 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | OTHER |  | 44214 | 2259 | 1214854 | 836 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 23408 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0010198 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | FUSE |  | 44224 | 1741 | 1240369 | 1162 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 21736 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017945 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | ORO FINO-1102 | 103031102 | RECLOSER |  | 44215 | 944 | 1216245 | 516 | Distribution Circuit | Vegetation | Tree - fell into line | 312 | 82044 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0010539 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER |  | 44214 | 2248 | 1213192 | 584 | Distribution Circuit | Vegetation | Tree - fell into line | 973 | 68678 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0009881 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER |  | 44214 | 2318 | 1213322 | 397 | Distribution Circuit | Vegetation | Tree - fell into line | 199 | 58879 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009923 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE |  | 44223 | 136 | 1231931 | 685 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3425 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015916 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER |  | 44223 | 120 | 1231849 | 2153 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 135657 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015476 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | OTHER |  | 44221 | 502 | 1223363 | 566 | Distribution Circuit | Vegetation | Tree - fell into line | 779 | 429455 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0013592 | OH | Sus | 44634092 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | JESSUP-1101 | 103441101 | RECLOSER |  | 44222 | 2307 | 1230339 | 3478 | Distribution Circuit | Environmental/External | Ice or snow | 354 | 561892 | Strong Winds-Snow-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015318 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1101 | 103401101 | FUSE |  | 44223 | 1340 | 1235865 | 286 | Distribution Circuit | Vegetation | Tree - bark fell into line | 35 | 10010 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016376 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1101 | 103401101 | FUSE |  | 44224 | 1438 | 1239916 | 1429 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 28580 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017937 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1102 | 103401102 | FUSE |  | 44223 | 329 | 1232739 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 33604 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015647 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1102 | 103401102 | JUMPER |  | 44223 | 528 | 1232927 | 2379 | Distribution Circuit | Vegetation | Tree - fell into line | 234 | 204990 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015701 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 3 | KESWICK-1101 | 103451101 | FUSE |  | 44222 | 2144 | 1231018 | 2310 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 27720 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016079 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | RECLOSER |  | 44223 | 416 | 1232826 | 994 | Distribution Circuit | Environmental/External | Ice or snow | 630 | 534388 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015713 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KESWICK-1101 | 103451101 | OCB |  | 44222 | 2144 | 1229089 | 6471 | Distribution Circuit | Environmental/External | Ice or snow | 740 | 1143391 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015159 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | RECLOSER |  | 44223 | 533 | 1232967 | 738 | Distribution Circuit | Environmental/External | Ice or snow | 432 | 209470 | Clear;32-90 F | Transformer (OH) | Broken- wire on ground | 21-0015680 | OH | Sus | 0 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE |  | 44223 | 11 | 1234501 | 3802 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 220516 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015929 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE |  | 44222 | 2226 | 1234480 | 2795 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 128570 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0015924 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1102 | 103381102 | OTHER |  | 44223 | 108 | 1231709 | 2280 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 61560 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0015548 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | JUMPER |  | 44223 | 215 | 1236411 | 2431 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4862 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016557 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | FUSE |  | 44223 | 1350 | 1236105 | 1690 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 16900 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0016469 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | FUSE |  | 44223 | 135 | 1232354 | 872 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3488 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016072 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | RECLOSER |  | 44222 | 2226 | 1229732 | 5395 | Distribution Circuit | Vegetation | Tree - fell into line | 643 | 2013424 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015244 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | FUSE |  | 44222 | 2226 | 1239522 | 2758 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 11032 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017461 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | FUSE |  | 44222 | 2226 | 1239906 | 3726 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 59616 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017660 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1101 | 103381101 | RECLOSER |  | 44222 | 2034 | 1227783 | 4165 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 297924 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0014987 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | JUMPER |  | 44222 | 2226 | 1236423 | 2221 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 2221 | Snow-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016563 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | FUSE |  | 44222 | 2226 | 1241513 | 4058 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 16232 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0018281 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1102 | 103561102 | FUSE |  | 44222 | 2303 | 1230274 | 4017 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 301275 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017670 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE |  | 44223 | 400 | 1232641 | 603 | Distribution Circuit | Vegetation | Tree - fell into line | 104 | 68050 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015779 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | FUSE |  | 44222 | 2148 | 1242868 | 6795 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 693090 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019201 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | FUSE |  | 44222 | 2101 | 1243072 | 8466 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 237048 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019267 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | FUSE |  | 44223 | 116 | 1240367 | 3968 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 51584 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0017854 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | JUMPER |  | 44224 | 1453 | 1239936 | 1443 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 23088 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0017682 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | RECLOSER |  | 44223 | 116 | 1231813 | 8200 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 336976 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015464 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 44215 | 224 | 1214443 | 951 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1902 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010127 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | JUMPER |  | 44223 | 1039 | 1234914 | 1743 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1743 | Strong Winds; | Pole-Wood | Broken- wire on ground | 21-0016060 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 44223 | 933 | 1234476 | 1777 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 26655 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016279 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | OTHER |  | 44214 | 1007 | 1212401 | 532 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 29140 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009656 | OH | Sus | 44628037 | 2021 | JAN | Yes | Open Circuit | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | RECLOSER |  | 44214 | 2323 | 1213334 | 2525 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 126107 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009913 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER |  | 44214 | 2303 | 1213261 | 339 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 7797 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009890 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 44214 | 2341 | 1217422 | 1940 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 56260 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010908 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | TRIP-SAVER |  | 44222 | 2047 | 1228221 | 527 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 27404 | Strong Winds; | Conductor- Overhead | On Ground | 21-0015206 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 44223 | 712 | 1233425 | 339 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2373 | Strong Winds; | Conductor- Overhead | Broken- wire on ground | 21-0015827 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 44215 | 30 | 1213674 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1895 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010078 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 44222 | 2100 | 1229631 | 418 | Distribution Circuit | Equipment Failure/Involved | Overhead | 111 | 36368 | Strong Winds; | Conductor- Overhead | Broken- wire on ground | 21-0015231 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER |  | 44214 | 2215 | 1213153 | 3812 | Distribution Circuit | Vegetation | Tree - branch fell on line | 261 | 203724 | Strong Winds-Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009907 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 44215 | 32 | 1214103 | 569 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 22100 | Strong Winds-Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0010039 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER |  | 44215 | 959 | 1214200 | 716 | Distribution Circuit | Equipment Failure/Involved | Overhead | 244 | 154509 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010555 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 44223 | 206 | 1232107 | 1426 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 41354 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016363 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER |  | 44215 | 219 | 1218104 | 2092 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 50208 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011198 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1104 | 24251104 | FUSE |  | 44215 | 212 | 1216345 | 1381 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 23477 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011085 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 44215 | 240 | 1214363 | 1381 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 30382 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0011053 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | TRIP-SAVER |  | 44222 | 2144 | 1229084 | 1283 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 53886 | Strong Winds; | Conductor- Overhead | Broken- wire on ground | 21-0015559 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | HALF MOON BAY-1101 | 24101101 | OTHER |  | 44215 | 1404 | 1217800 | 1376 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 27192 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011218 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 2 | SNEATH LANE-1106 | 22721106 | FUSE |  | 44215 | 454 | 1214799 | 567 | Distribution Circuit | Equipment Failure/Involved | Overhead | 120 | 68040 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010195 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
SACRAMENTO | Tier 2 | BROWNS VALLEY-1101 | 152921101 | TRIP-SAVER |  | 44222 | 1858 | 1226656 | 2570 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 59110 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015209 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SAN JOSE | Tier 2 | SWIFT-2110 | 83392110 | RECLOSER |  | 44215 | 635 | 1213208 | 2610 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 265669 | Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010257 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SAN JOSE | Tier 2 | MC KEE-1103 | 83531103 | OTHER |  | 44215 | 700 | 1215278 | 858 | Distribution Circuit | Vegetation | Tree - fell into line | 155 | 67998 | Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010452 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 44223 | 915 | 1234584 | 487 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 36259 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0015947 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 44215 | 115 | 1213909 | 601 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 13823 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010382 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 44223 | 928 | 1234435 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 9494 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0015917 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 44221 | 1141 | 1224340 | 184 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 10304 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0013927 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | RECLOSER |  | 44215 | 1035 | 1216483 | 163 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 17115 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010618 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 44223 | 1044 | 1235118 | 426 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 6816 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016139 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | Yes
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 44222 | 1106 | 1226025 | 448 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 448 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0014549 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | OTHER |  | 44221 | 126 | 1223043 | 881 | Distribution Circuit | Vegetation | Tree - fell into line | 369 | 20015 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0013682 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | FUSE |  | 44214 | 2248 | 1213191 | 807 | Distribution Circuit | Vegetation | Tree - fell into line | 189 | 18617 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010007 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | JUMPER |  | 44221 | 1420 | 1224725 | 94 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 2250 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0013999 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 44221 | 508 | 1223369 | 722 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 12274 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0013624 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 44223 | 649 | 1233327 | 546 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 15352 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016189 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 44223 | 331 | 1232550 | 917 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 14672 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0015807 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | Yes
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER |  | 44222 | 1850 | 1227019 | 1364 | Distribution Circuit | Vegetation | Tree - fell into line | 667 | 687980 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0014824 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 44221 | 554 | 1223453 | 684 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 15048 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0013871 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER |  | 44224 | 2008 | 1240623 | 761 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1164 | 75020 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017959 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | RECLOSER |  | 44223 | 331 | 1232541 | 633 | Distribution Circuit | Vegetation | Tree - fell into line | 618 | 225024 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0015601 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | ECHO SUMMIT-1101 | 158031101 | RECLOSER |  | 44215 | 1403 | 1217323 | 266 | Distribution Circuit | Equipment Failure/Involved | Overhead | 78 | 8214 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010869 | OH | Sus | 0 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44215 | 407 | 1214541 | 728 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 12376 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010573 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | OTHER |  | 44215 | 1011 | 1216521 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 669 | 74519 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010790 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44221 | 609 | 1223464 | 1864 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 14912 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0014080 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | LINCOLN-1101 | 153701101 | FUSE |  | 44222 | 2042 | 1234025 | 1338 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 5352 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016406 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | RECLOSER |  | 44223 | 2143 | 1237831 | 1078 | Distribution Circuit | Vegetation | Tree - fell into line | 267 | 220094 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016962 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER |  | 44221 | 4 | 1222982 | 2147 | Distribution Circuit | Vegetation | Tree - fell into line | 831 | 1044329 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0013545 | OH | Sus | 44633340 | 2021 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 2 | PENRYN-1105 | 152561105 | FUSE |  | 44215 | 1319 | 1217221 | 339 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 4407 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010975 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44221 | 2155 | 1225369 | 1143 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 23973 | Clear;32-90F | Cutout- fuse holder | Broken- wire on ground | 21-0014492 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | JUMPER |  | 44224 | 1216 | 1240069 | 1799 | Distribution Circuit | Environmental/External | Ice or snow | 90 | 160266 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017820 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44224 | 1000 | 1239227 | 685 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3425 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017673 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | OTHER |  | 44221 | 900 | 1224119 | 260 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 520 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0013786 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE |  | 44221 | 547 | 1223441 | 811 | Distribution Circuit | Vegetation | Tree - branch fell on line | 117 | 94887 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0013869 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1107 | 152691107 | FUSE |  | 44223 | 819 | 1233887 | 341 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 1991 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016007 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | RECLOSER |  | 44221 | 28 | 1222999 | 989 | Distribution Circuit | Vegetation | Tree - fell into line | 547 | 517834 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0013546 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1110 | 152691110 | FUSE |  | 44222 | 1947 | 1227562 | 1044 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 30276 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0015927 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1110 | 152691110 | FUSE |  | 44221 | 634 | 1223521 | 798 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 24738 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0013970 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 2 | HIGGINS-1110 | 152691110 | FUSE |  | 44221 | 650 | 1223557 | 781 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 15620 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0013797 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE |  | 44221 | 46 | 1223019 | 715 | Distribution Circuit | Vegetation | Tree - fell into line | 267 | 65541 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0013598 | OH | Sus | 31528834 | 2021 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE |  | 44221 | 337 | 1224107 | 990 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11076 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0014073 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 44221 | 655 | 1223560 | 602 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 11852 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0013757 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 44221 | 349 | 1224083 | 847 | Distribution Circuit | Vegetation | Tree - branch fell on line | 96 | 54612 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0013770 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 44222 | 1958 | 1227753 | 1452 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7260 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016105 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 44221 | 540 | 1223404 | 767 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 25194 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0013636 | OH | Sus | 35227541 | 2021 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | FUSE |  | 44223 | 157 | 1232043 | 629 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 33337 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0015704 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER |  | 44222 | 1759 | 1226753 | 1269 | Distribution Circuit | Vegetation | Tree - fell into line | 2891 | 2117109 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0014783 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE |  | 44215 | 548 | 1214912 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 6803 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010524 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1102 | 152301102 | RECLOSER |  | 44224 | 2244 | 1240766 | 1052 | Distribution Circuit | Vegetation | Tree - fell into line | 362 | 363083 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0018068 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | FUSE |  | 44222 | 2334 | 1230706 | 951 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 53256 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0015888 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | DRUM-1101 | 152321101 | JUMPER |  | 44215 | 829 | 1216130 | 258 | Distribution Circuit | Vegetation | Tree - fell into line | 194 | 16128 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010494 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE |  | 44215 | 4 | 1213435 | 815 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 13285 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010477 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44215 | 140 | 1213869 | 924 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 27720 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010110 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44215 | 48 | 1214339 | 971 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 27188 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010111 | OH | Sus | 44629093 | 2021 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 2 | SPAULDING-1101 | 152251101 | OTHER |  | 44224 | 1730 | 1241215 | 2766 | Distribution Circuit | Equipment Failure/Involved | Overhead | 85 | 116422 | Snow-Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0018317 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44224 | 732 | 1239405 | 4828 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 38624 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017389 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER |  | 44223 | 2258 | 1239283 | 5342 | Distribution Circuit | Vegetation | Tree - fell into line | 582 | 864087 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017352 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE |  | 44215 | 842 | 1215885 | 1660 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 87980 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010604 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE |  | 44215 | 810 | 1215665 | 2044 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 59276 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010804 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE |  | 44215 | 840 | 1214938 | 445 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 24920 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010453 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44215 | 911 | 1216050 | 377 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3393 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010727 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE |  | 44223 | 858 | 1234179 | 1757 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 8785 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016528 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE |  | 44222 | 2340 | 1230775 | 759 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 27324 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016028 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PIKE CITY-1102 | 152201102 | OCB |  | 44224 | 518 | 1239690 | 6153 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 166131 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017584 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE |  | 44222 | 2340 | 1230882 | 1030 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 89610 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016180 | OH | Sus | 0 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1102 | 152101102 | FUSE |  | 44224 | 1646 | 1243507 | 4163 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 37467 | Snow-Strong Winds-Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019374 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1102 | 152101102 | RECLOSER |  | 44215 | 22 | 1213700 | 2400 | Distribution Circuit | Vegetation | Tree - fell into line | 165 | 196649 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009959 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 44215 | 1004 | 1216306 | 517 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 5847 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010739 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER |  | 44215 | 331 | 1214425 | 607 | Distribution Circuit | Vegetation | Tree - branch fell on line | 185 | 65855 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010122 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | RECLOSER |  | 44223 | 2014 | 1237609 | 1135 | Distribution Circuit | Equipment Failure/Involved | Overhead | 837 | 282798 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 21-0016881 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE |  | 44222 | 2000 | 1235396 | 1435 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 20090 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016207 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
SONOMA | Tier 3 | MOLINO-1101 | 42571101 | SWITCH |  | 44223 | 1545 | 1236487 | 12 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 1140 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015258 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | DUNBAR-1103 | 43071103 | FUSE |  | 44215 | 439 | 1214692 | 475 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3325 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010240 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | DUNBAR-1101 | 43071101 | FUSE |  | 44215 | 154 | 1214097 | 916 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2748 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010120 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER |  | 44222 | 2223 | 1229709 | 989 | Distribution Circuit | Vegetation | Tree - fell into line | 255 | 144133 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015258 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 44222 | 2201 | 1229318 | 1130 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 4520 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015742 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE |  | 44215 | 838 | 1215848 | 562 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 2811 | Clear;32-90 F | Transformer (OH) | Broken- wire on ground | 21-0010644 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER |  | 44222 | 2148 | 1229202 | 959 | Distribution Circuit | Vegetation | Tree - fell into line | 359 | 277103 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015177 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER |  | 44215 | 522 | 1214841 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 143 | 22766 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010196 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | TRIP-SAVER |  | 44222 | 2148 | 1229139 | 977 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 64482 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0015382 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE |  | 44221 | 1130 | 1224312 | 588 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 4116 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0013978 | OH | Sus | 31528913 | 2021 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 44214 | 2252 | 1213201 | 733 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 25655 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009964 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | RECLOSER |  | 44222 | 1855 | 1227063 | 875 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1242 | 127152 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0014841 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 44215 | 822 | 1215729 | 305 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2440 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010545 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER |  | 44222 | 2202 | 1229448 | 948 | Distribution Circuit | Vegetation | Tree - branch fell on line | 275 | 131226 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015261 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 44223 | 2207 | 1237872 | 839 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 45306 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017011 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER |  | 44215 | 28 | 1213521 | 551 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 23693 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009976 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 44222 | 1918 | 1227258 | 503 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 46779 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0014960 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 44224 | 1455 | 1239941 | 423 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2961 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017757 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 44223 | 1214 | 1229742 | 440 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 4400 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0016230 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 44223 | 2045 | 1237701 | 983 | Distribution Circuit | Vegetation | Tree - fell into line | 179 | 175957 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0016959 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | GEYSERVILLE-1102 | 42891102 | FUSE |  | 44222 | 2151 | 1234721 | 2266 | Distribution Circuit | Environmental/External | Ice or snow | 19 | 43054 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0015991 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | GEYSERVILLE-1102 | 42891102 | FUSE |  | 44224 | 1147 | 1239509 | 1843 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 22221 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0017453 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | CLOVERDALE-1102 | 42821102 | FUSE |  | 44223 | 1001 | 1234647 | 1924 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 38480 | Clear;32-90 F | Pole-Wood | Broken- wire on object | 21-0015969 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | CLOVERDALE-1102 | 42821102 | FUSE |  | 44222 | 2020 | 1227912 | 3933 | Distribution Circuit | Environmental/External | Ice or snow | 16 | 62928 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0015174 | OH | Sus | 0 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | JUMPER |  | 44222 | 1747 | 1226780 | 1134 | Distribution Circuit | Equipment Failure/Involved | Overhead | 216 | 42084 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0014790 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | Yes
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER |  | 44221 | 809 | 1223725 | 1183 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1546 | 570510 | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 21-0013680 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44224 | 141 | 1240083 | 7979 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 231391 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017756 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 44222 | 1954 | 1227677 | 2697 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 32364 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0015152 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 44222 | 2005 | 1227847 | 1171 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 28104 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0015237 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1701 | 162821701 | FUSE |  | 44223 | 1658 | 1238400 | 7010 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 553790 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0017094 | OH | Sus | 0 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1701 | 162821701 | FUSE |  | 44223 | 1930 | 1237453 | 6858 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 425175 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017025 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | OTHER |  | 44223 | 2253 | 1237954 | 8328 | Distribution Circuit | Vegetation | Tree - fell into line | 377 | 3122673 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017016 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44224 | 133 | 1238266 | 9147 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 274410 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017100 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44224 | 1254 | 1243091 | 8869 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 150773 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017550 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44224 | 1254 | 1247367 | 10219 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 490512 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017550 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44224 | 148 | 1238292 | 8235 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 304695 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0017469 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER |  | 44224 | 115 | 1238204 | 9755 | Distribution Circuit | Vegetation | Tree - fell into line | 661 | 6448055 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017052 | OH | Sus | 0 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44223 | 1608 | 1236578 | 8733 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 611310 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 21-0016665 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44223 | 2344 | 1238557 | 8276 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 289660 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0017135 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44223 | 2344 | 1246481 | 9303 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 186060 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017016 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER |  | 44223 | 2344 | 1243059 | 8308 | Distribution Circuit | Vegetation | Tree - fell into line | 442 | 3672136 | Clear;32-90F | Conductor- Overhead | On Ground | 21-0017016 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | SWITCH |  | 44223 | 1705 | 1243974 | 11041 | Distribution Circuit | Equipment Failure/Involved | Overhead | 260 | 2657036 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 21-0020015 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | SWITCH |  | 44224 | 244 | 1241964 | 3846 | Distribution Circuit | Vegetation | Tree - fell into line | 351 | 1349946 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0017078 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44223 | 2341 | 1241967 | 9377 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 403211 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017078 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44215 | 1157 | 1216885 | 1541 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6164 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010797 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER |  | 44223 | 1705 | 1243945 | 10213 | Distribution Circuit | Vegetation | Tree - fell into line | 159 | 1623867 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017034 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44223 | 1705 | 1243878 | 10149 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 213129 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0019991 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44215 | 813 | 1215295 | 270 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 5670 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 21-0010394 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER |  | 44215 | 819 | 1215606 | 2961 | Distribution Circuit | Vegetation | Tree - fell into line | 1095 | 397382 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010397 | OH | Sus | 0 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE |  | 44224 | 808 | 1244210 | 7426 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 22278 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0017252 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 44215 | 1859 | 1217953 | 1027 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1027 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0011180 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44215 | 758 | 1216582 | 2029 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 110170 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010647 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44215 | 317 | 1214377 | 774 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 21548 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010266 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44215 | 717 | 1216152 | 629 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 74222 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010504 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44215 | 1919 | 1217987 | 4219 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 33752 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0011208 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | SWITCH |  | 44215 | 812 | 1216626 | 1907 | Distribution Circuit | Vegetation | Tree - fell into line | 271 | 516797 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0010397 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE |  | 44224 | 808 | 1243456 | 6231 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 93465 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017252 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | TRIP-SAVER |  | 44215 | 600 | 1214965 | 2050 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 229600 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010345 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44215 | 1220 | 1216978 | 1817 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 136275 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010832 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 44215 | 819 | 1218561 | 3076 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 46140 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0011383 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER |  | 44215 | 411 | 1214552 | 2223 | Distribution Circuit | Equipment Failure/Involved | Overhead | 207 | 460161 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0010182 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | CALAVERAS CEMENT-1101 | 162211101 | OTHER |  | 44221 | 526 | 1224366 | 898 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4490 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0013680 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE |  | 44221 | 325 | 1223243 | 654 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 8525 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0013820 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 44223 | 201 | 1232322 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 8738 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0015686 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 44215 | 1717 | 1217783 | 138 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 2346 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011070 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | JUMPER |  | 44222 | 58 | 1225470 | 526 | Distribution Circuit | Vegetation | Tree - fell into line | 280 | 52292 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0014249 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | OCB |  | 44221 | 349 | 1223291 | 883 | Distribution Circuit | Vegetation | Tree - fell into line | 1376 | 247531 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0013586 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | RECLOSER |  | 44215 | 917 | 1216087 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 2799 | 890430 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010491 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | SALT SPRINGS-2102 | 163692102 | RECLOSER |  | 44214 | 618 | 1212119 | 703 | Distribution Circuit | Vegetation | Tree - fell into line | 2008 | 275749 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0009579 | OH | Sus | 0 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | SALT SPRINGS-2102 | 163692102 | RECLOSER |  | 44215 | 105 | 1213868 | 6834 | Distribution Circuit | Vegetation | Tree - fell into line | 2008 | 529098 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 21-0009979 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | SALT SPRINGS-2101 | 163692101 | RECLOSER |  | 44215 | 207 | 1214058 | 6506 | Distribution Circuit | Vegetation | Tree - fell into line | 800 | 4672651 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0010048 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | SALT SPRINGS-2101 | 163692101 | FUSE |  | 44215 | 55 | 1214860 | 6595 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 72545 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0010200 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 44221 | 437 | 1223338 | 616 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1848 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 21-0013821 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | SALT SPRINGS-2101 | 163692101 | FUSE |  | 44215 | 147 | 1214423 | 6646 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 112982 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0010121 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | SALT SPRINGS-2101 | 163692101 | FUSE |  | 44215 | 207 | 1220316 | 8133 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 97596 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0012305 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | TIGER CREEK-0201 | 161380201 | FUSE |  | 44224 | 1316 | 1242878 | 2904 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 2904 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019205 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | OTHER |  | 44224 | 801 | 1238876 | 3326 | Distribution Circuit | Vegetation | Tree - branch fell on line | 320 | 389008 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017246 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 44224 | 1433 | 1239902 | 4122 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 91698 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0017754 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | JUMPER |  | 44224 | 836 | 1243015 | 4686 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 164010 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019255 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER |  | 44224 | 836 | 1238757 | 4686 | Distribution Circuit | Vegetation | Tree - fell into line | 136 | 637296 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017330 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER |  | 44223 | 2330 | 1238088 | 4012 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 437308 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017020 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 44224 | 804 | 1243665 | 4851 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 150381 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019899 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | TRIP-SAVER |  | 44224 | 836 | 1243666 | 4797 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 335790 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0019900 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 44223 | 2330 | 1243280 | 6821 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 484291 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0019320 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 44224 | 31 | 1238378 | 5171 | Distribution Circuit | Vegetation | Tree - fell into line | 316 | 1634036 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017133 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | SALT SPRINGS-2101 | 163692101 | RECLOSER |  | 44215 | 216 | 1214163 | 3711 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 14844 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0010056 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 44224 | 31 | 1242633 | 5383 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 91511 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0018705 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 44223 | 2330 | 1244065 | 6821 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 109136 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0020023 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | TRIP-SAVER |  | 44223 | 2330 | 1243681 | 6821 | Distribution Circuit | Equipment Failure/Involved | Overhead | 48 | 327408 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0019909 | OH | Sus | 0 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 44223 | 2330 | 1243281 | 6821 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 81852 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0019321 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | SALT SPRINGS-2101 | 163692101 | FUSE |  | 44215 | 216 | 1219427 | 7727 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 355442 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0010056 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | JUMPER |  | 44221 | 18 | 1224516 | 1082 | Distribution Circuit | Vegetation | Tree - branch fell on line | 247 | 35745 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0013937 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | Yes
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | RECLOSER |  | 44214 | 2302 | 1213243 | 5081 | Distribution Circuit | Vegetation | Tree - branch fell on line | 306 | 778066 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009888 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1103 | 252531103 | RECLOSER |  | 44214 | 2302 | 1213746 | 6878 | Distribution Circuit | Vegetation | Tree - branch fell on line | 153 | 600240 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009480 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | JUMPER |  | 44215 | 904 | 1219258 | 4431 | Distribution Circuit | Vegetation | Tree - branch fell on line | 100 | 43827 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011742 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2102 | 254432102 | RECLOSER |  | 44214 | 2306 | 1213264 | 8311 | Distribution Circuit | Vegetation | Tree - fell into line | 1048 | 4727046 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0009891 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | RECLOSER |  | 44214 | 2320 | s1593847 | 3939 | Distribution Circuit | Vegetation | Tree - branch fell on line | 446 | 1037024 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009888 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1102 | 252531102 | RECLOSER |  | 44215 | 149 | 1214081 | 6754 | Distribution Circuit | Vegetation | Tree - branch fell on line | 93 | 484696 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010033 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER |  | 44215 | 115 | 1213919 | 2368 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 210752 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009988 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER |  | 44214 | 2319 | 1213298 | 6715 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 328317 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0009902 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | JUMPER |  | 44214 | 2319 | 1222445 | 9416 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 37664 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009902 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE |  | 44224 | 116 | 1238248 | 824 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 61800 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017155 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | JUMPER |  | 44214 | 2319 | 1221255 | 8020 | Distribution Circuit | Vegetation | Tree - bark fell into line | 28 | 224560 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009902 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | JUMPER |  | 44214 | 2306 | 1220244 | 5518 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 397296 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009891 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | SWITCH |  | 44214 | 2306 | 1220170 | 6921 | Distribution Circuit | Vegetation | Tree - branch fell on line | 150 | 1038150 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009891 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | SWITCH |  | 44215 | 115 | 1221916 | 9508 | Distribution Circuit | Equipment Failure/Involved | Overhead | 351 | 3337128 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0009988 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | SWITCH |  | 44214 | 2354 | 1222847 | 9632 | Distribution Circuit | Equipment Failure/Involved | Overhead | 310 | 2985920 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0009929 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1102 | 254421102 | FUSE |  | 44214 | 2341 | 1218781 | 3855 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 161910 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0010086 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44215 | 8 | 1217493 | 3430 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 236606 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009944 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | JUMPER |  | 44214 | 2354 | 1222828 | 9596 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 9596 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0009929 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44215 | 8 | 1217644 | 6852 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 82224 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009944 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER |  | 44214 | 2354 | 1222846 | 8532 | Distribution Circuit | Vegetation | Tree - fell into line | 145 | 1237140 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009929 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | SWITCH |  | 44214 | 2354 | 1219950 | 8507 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 501913 | Strong Winds-Clear;32-90 F | Conductor- Overhead | On Ground | 21-0009929 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | SWITCH |  | 44214 | 2348 | 1219932 | 8513 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 42565 | Strong Winds-Clear;32-90 F | Conductor- Overhead | On Ground | 21-0009929 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44214 | 2354 | s1595458 | 8461 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 541504 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009929 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | JUMPER |  | 44214 | 2354 | 1222269 | 8461 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 78357 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009929 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44214 | 2354 | 1219711 | 6936 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 138720 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009929 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1101 | 254421101 | JUMPER |  | 44215 | 912 | 1217448 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3094 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010941 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | SWITCH |  | 44214 | 2354 | 1221684 | 6936 | Distribution Circuit | Vegetation | Tree - branch fell on line | 72 | 499392 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009929 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44214 | 2354 | 1219907 | 8100 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 226800 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009929 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44214 | 2354 | s1595454 | 6367 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 95505 | Strong Winds-Clear;32-90 F | Conductor- Overhead | On Ground | 21-0009929 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | JUMPER |  | 44214 | 2354 | 1221864 | 8317 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 108121 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009929 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER |  | 44214 | 2354 | 1213394 | 6368 | Distribution Circuit | Vegetation | Tree - branch fell on line | 61 | 388448 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0009929 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44215 | 8 | 1219680 | 6742 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 222486 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0009944 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER |  | 44215 | 8 | 1218792 | 4871 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 38968 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009944 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | FUSE |  | 44215 | 8 | 1217490 | 6568 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 1221648 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009944 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | JUMPER |  | 44215 | 8 | 1221796 | 8317 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 141389 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009944 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | SWITCH |  | 44215 | 8 | 1218879 | 4871 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 136388 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009944 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | FUSE |  | 44215 | 8 | 1219718 | 8316 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 249480 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0009944 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | JUMPER |  | 44214 | 2343 | 1219792 | 3735 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 52290 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009944 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44215 | 8 | 1219480 | 5138 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 102760 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009944 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | JUMPER |  | 44215 | 8 | 1220095 | 3880 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 7760 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0009944 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44215 | 8 | 1220233 | 5361 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 182274 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009944 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1101 | 254421101 | FUSE |  | 44215 | 153 | s1595118 | 3627 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 112437 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0010041 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44215 | 8 | 1220283 | 6777 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 74547 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009944 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER |  | 44214 | 2345 | 1213385 | 6905 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 6905 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009927 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | SWITCH |  | 44214 | 2346 | 1219063 | 6905 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 469540 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009944 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44224 | 1146 | 1239502 | 1781 | Distribution Circuit | Vegetation | Tree - bark fell into line | 39 | 69459 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 21-0009927 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | SWITCH |  | 44214 | 2345 | s1602525 | 19750 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 128400 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009927 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44214 | 2345 | 1245404 | 20687 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 144809 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009927 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | JUMPER |  | 44215 | 204 | 1222513 | 8149 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 700814 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE |  | 44215 | 201 | 1222510 | 8123 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 97476 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | RECLOSER |  | 44215 | 58 | 1213900 | 8261 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 401 | 3312661 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE |  | 44215 | 204 | 1222508 | 9293 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 74344 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 44215 | 58 | 1222165 | 9243 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 54 | 499122 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE |  | 44215 | 204 | 1222506 | 9343 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 93430 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 44215 | 58 | 1222164 | 9362 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 7 | 65534 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER |  | 44224 | 1517 | 1239639 | 4474 | Distribution Circuit | Vegetation | Tree - branch fell on line | 122 | 455243 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017714 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE |  | 44215 | 643 | 1217525 | 5060 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 45540 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010957 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | JUMPER |  | 44215 | 205 | 1222516 | 9428 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 94280 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | JUMPER |  | 44215 | 204 | 1222504 | 9431 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 9431 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44224 | 1517 | 1243412 | 4244 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 80636 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0009927 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 44215 | 58 | 1222163 | 8233 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 6 | 49398 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 44215 | 229 | 1214306 | 3461 | Distribution Circuit | Vegetation | Tree - branch fell on line | 63 | 131223 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010093 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE |  | 44215 | 204 | 1222502 | 8139 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 170919 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE |  | 44215 | 204 | 1222501 | 8062 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 16124 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44224 | 627 | 1238622 | 5004 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 78161 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017545 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 44215 | 58 | 1222162 | 9453 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 6 | 56718 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 44215 | 58 | 1222499 | 9391 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 13 | 122083 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 44215 | 58 | 1222160 | 10992 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 39 | 428688 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | JUMPER |  | 44215 | 58 | 1222498 | 7927 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 4 | 31708 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 44215 | 58 | 1222746 | 9638 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 29 | 279502 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 44215 | 58 | 1222747 | 9686 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 30 | 290580 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 44215 | 58 | s1596642 | 9254 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 2 | 18508 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 44215 | 58 | 1222159 | 8132 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 3 | 24396 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 44215 | 58 | 1222158 | 9277 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 12 | 111324 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 44215 | 58 | s1596448 | 8317 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 41 | 340997 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 44215 | 58 | 1222170 | 8210 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 20 | 164200 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 44215 | 58 | 1222157 | 8401 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 5 | 42005 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 44215 | 58 | 1222155 | 8348 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 8 | 66784 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 44215 | 58 | 1222156 | 7999 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 9 | 71991 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 44215 | 58 | 1222154 | 6953 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1 | 6953 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 44215 | 58 | 1222153 | 8245 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 43 | 354535 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 44215 | 58 | 1222149 | 7832 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 25 | 195800 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 44215 | 58 | 1222150 | 7742 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 4 | 30968 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 44215 | 250 | 1220318 | 4810 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 96200 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010088 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | JUMPER |  | 44215 | 58 | 1222151 | 8249 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 3 | 24747 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 44215 | 58 | 1222148 | 9672 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 27 | 261144 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009474 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | RECLOSER |  | 44215 | 246 | 1214256 | 4996 | Distribution Circuit | Vegetation | Tree - fell into line | 295 | 665968 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010088 | OH | Sus | 0 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER |  | 44214 | 2345 | 1221935 | 21219 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 806735 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009477 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | FUSE |  | 44214 | 2346 | 1222484 | 19737 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 1084869 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009927 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | FUSE |  | 44214 | 2345 | 1224705 | 11105 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 377570 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009927 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | FUSE |  | 44214 | 2346 | 1224692 | 11024 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 363792 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009927 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | JUMPER |  | 44214 | 2345 | 1226466 | 16800 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 252000 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009927 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | JUMPER |  | 44214 | 2345 | 1226453 | 16815 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 1851171 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009927 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | JUMPER |  | 44214 | 2345 | 1243529 | 18095 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 778085 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009927 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | JUMPER |  | 44214 | 2346 | 1243532 | 18094 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 434256 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0009927 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | JUMPER |  | 44214 | 2346 | 1226288 | 16784 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 33568 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0009927 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | INDIAN FLAT-1104 | 252691104 | OTHER |  | 44215 | 612 | 1215499 | 780 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 61 | 38155 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0010698 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 44215 | 450 | 1219559 | 3347 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 6694 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0010173 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | JUMPER |  | 44223 | 1900 | 1237290 | 1176 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 126942 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017072 | OH | Sus | 0 | 2021 | JAN | Yes | Open Circuit | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 44215 | 450 | 1219856 | 4814 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 72210 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010173 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE |  | 44221 | 243 | 1223111 | 867 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 53754 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0013596 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | JUMPER |  | 44215 | 1006 | 1217746 | 1745 | Distribution Circuit | Vegetation | Tree - bark fell into line | 152 | 265240 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010567 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | CURTIS-1703 | 163351703 | RECLOSER |  | 44224 | 900 | 1239271 | 9094 | Distribution Circuit | Vegetation | Tree - fell into line | 603 | 1321029 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 21-0017041 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | CURTIS-1703 | 163351703 | RECLOSER |  | 44215 | 1006 | 1216304 | 1789 | Distribution Circuit | Vegetation | Tree - branch fell on line | 451 | 406601 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010567 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | JUMPER |  | 44215 | 1110 | 1217631 | 2990 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 2990 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010666 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 44221 | 814 | 1224186 | 508 | Distribution Circuit | Equipment Failure/Involved | Overhead | 185 | 93980 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 21-0013806 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE |  | 44221 | 351 | 1223284 | 435 | Distribution Circuit | Equipment Failure/Involved | Overhead | 261 | 90068 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 21-0013688 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | FUSE |  | 44221 | 354 | 1223872 | 624 | Distribution Circuit | Equipment Failure/Involved | Overhead | 149 | 92976 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 21-0013719 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | RECLOSER |  | 44221 | 341 | 1223279 | 102 | Distribution Circuit | Vegetation | Tree - branch fell on line | 446 | 45492 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0013585 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | JUMPER |  | 44224 | 159 | 1247532 | 10724 | Distribution Circuit | Vegetation | Tree - bark fell into line | 5 | 53620 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0017492 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | JUMPER |  | 44215 | 309 | 1215421 | 3360 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 47040 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010109 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44224 | 159 | 1244109 | 9775 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 782000 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0017492 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44215 | 309 | 1217630 | 3803 | Distribution Circuit | Vegetation | Tree - branch fell on line | 85 | 323255 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0010992 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | SWITCH |  | 44215 | 309 | 1219132 | 3803 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 70812 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010175 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44215 | 505 | 1214878 | 3586 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 205720 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0011352 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER |  | 44215 | 353 | 1214496 | 3829 | Distribution Circuit | Vegetation | Tree - fell into line | 613 | 2335397 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010154 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44215 | 406 | 1217697 | 942 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 27318 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010175 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44224 | 1212 | 1244118 | 7573 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 696716 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017492 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | OCB |  | 44224 | 1212 | 1238721 | 4719 | Distribution Circuit | Vegetation | Tree - fell into line | 176 | 830544 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017492 | OH | Sus | 0 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | OCB |  | 44215 | 453 | 1214543 | 3496 | Distribution Circuit | Vegetation | Tree - fell into line | 345 | 629491 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010175 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44223 | 1934 | 1238231 | 5717 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 131491 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0017045 | OH | Sus | 0 | 2021 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44224 | 1212 | 1243709 | 6172 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 752984 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0017492 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44224 | 546 | 1244173 | 7944 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 301872 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017492 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44224 | 546 | 1244171 | 7944 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 23832 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017492 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44215 | 453 | 1219567 | 3787 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 98462 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0010175 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER |  | 44215 | 309 | 1214340 | 3379 | Distribution Circuit | Vegetation | Tree - fell into line | 1019 | 3204883 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010109 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44215 | 453 | 1219566 | 3587 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 154241 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0010175 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44223 | 1444 | 1243356 | 4476 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 322272 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0016558 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44224 | 546 | 1244170 | 10833 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 704145 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017492 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44224 | 546 | 1244169 | 7944 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 889728 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017492 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | SWITCH |  | 44224 | 159 | 1244176 | 9484 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 1242404 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0017492 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | JUMPER |  | 44224 | 526 | 1247495 | 10834 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 260016 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017492 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44224 | 526 | 1245226 | 9411 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 207042 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0017492 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44224 | 325 | 1238366 | 9515 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 204527 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017119 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | JUMPER |  | 44215 | 453 | 1221422 | 6279 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 345345 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010175 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44215 | 453 | 1221355 | 6227 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 273988 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010175 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44224 | 546 | 1244166 | 10619 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 361046 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017492 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44224 | 546 | 1244164 | 7944 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 71496 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017492 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | JUMPER |  | 44224 | 547 | 1245425 | 7943 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7943 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017492 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44224 | 159 | 1243719 | 6006 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 684684 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0017492 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44224 | 546 | 1244139 | 7843 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 211761 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017492 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44215 | 453 | 1221354 | 5117 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 220031 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010175 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44224 | 546 | 1244156 | 9395 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 403985 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0017492 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | JUMPER |  | 44215 | 453 | 1219946 | 5027 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 130702 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010175 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44215 | 406 | 1219127 | 3463 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 34630 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010175 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44224 | 546 | 1240283 | 9409 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 263452 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0017830 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44224 | 1212 | 1243715 | 8871 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 17742 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0017492 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER |  | 44215 | 453 | 1220319 | 5077 | Distribution Circuit | Vegetation | Tree - fell into line | 564 | 2863428 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010175 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44215 | 406 | 1219125 | 5199 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 77985 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010175 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER |  | 44224 | 1212 | 1242954 | 6138 | Distribution Circuit | Vegetation | Tree - fell into line | 217 | 1331946 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017492 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44224 | 1212 | 1244126 | 10128 | Distribution Circuit | Vegetation | Tree - bark fell into line | 2 | 20256 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0017492 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44215 | 434 | 1215659 | 3626 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 333592 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010496 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44215 | 436 | 1218225 | 4766 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 19064 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010165 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44224 | 1212 | 1244135 | 8910 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 80190 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 21-0017492 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | JUMPER |  | 44215 | 409 | 1217700 | 4551 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 412806 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0010165 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | JUMPER |  | 44215 | 409 | 1217117 | 5076 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5076 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0010165 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44215 | 421 | 1218717 | 3814 | Distribution Circuit | Vegetation | Tree - fell into line | 224 | 854336 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0011475 | OH | Sus | 0 | 2021 | JAN | Yes | None | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44215 | 453 | 1220116 | 5209 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 145852 | Strong Winds-Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010175 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44224 | 1212 | 1241785 | 6420 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 355632 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 21-0017017 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | PINECREST-0401 | 163160401 | RECLOSER |  | 44215 | 246 | 1214261 | 3340 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 339502 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010082 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE |  | 44215 | 254 | 1217676 | 2043 | Distribution Circuit | Vegetation | Tree - fell into line | 113 | 200267 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010098 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE |  | 44215 | 254 | 1217475 | 2043 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 69462 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0010098 | OH | Sus | 0 | 2021 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER |  | 44215 | 303 | 1214335 | 3588 | Distribution Circuit | Vegetation | Tree - branch fell on line | 104 | 373152 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010103 | OH | Sus | 0 | 2021 | JAN | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE |  | 44215 | 303 | 1219973 | 5187 | Distribution Circuit | Vegetation | Tree - bark fell into line | 33 | 171171 | Strong Winds-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0010103 | OH | Sus | 0 | 2021 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | BUCKS CREEK-1102 | 102211102 | RECLOSER |  | 44395 | 1035 | 1407367 | 164698 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 130 | 21410740 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0091389 | OH | Sus | 0 | 2021 | JUL | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | GANSNER-1101 | 103021101 | OTHER |  | 44399 | 1650 | 1411749 | 152303 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 223 | 9103736 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0093767 | OH | Sus | 0 | 2021 | JUL | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER |  | 44399 | 1856 | 1411769 | 12711 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 38133 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 21-0093777 | OH | Sus | 0 | 2021 | JUL | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1102 | 182941102 | OTHER |  | 44494 | 521 | 1516997 | 682 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 47368 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137039 | OH | Sus | 0 | 2021 | OCT | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 44493 | 1638 | 1516816 | 1106 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 27650 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137019 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 44493 | 1124 | 1510675 | 1867 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 6494 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0136396 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | OCB |  | 44493 | 1619 | 1513986 | 1526 | Distribution Circuit | Vegetation | Tree - fell into line | 923 | 77518 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136452 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | OCB |  | 44493 | 723 | 1508276 | 493 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1798 | 90303 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135694 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 44493 | 1457 | 1513131 | 2935 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 38155 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137174 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER |  | 44493 | 2010 | 1513000 | 1048 | Distribution Circuit | Vegetation | Tree - fell into line | 424 | 278752 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136623 | OH | Sus | 0 | 2021 | OCT | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2105 | 83692105 | OTHER |  | 44493 | 1538 | 1513532 | 1174 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 16082 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136376 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 44493 | 1734 | 1514429 | 1637 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 34565 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136729 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | OTHER |  | 44493 | 1323 | 1513778 | 348 | Distribution Circuit | Vegetation | Tree - fell into line | 271 | 39604 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136413 | OH | Sus | 0 | 2021 | OCT | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 44493 | 1702 | 1514207 | 1517 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 13653 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137329 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | SWITCH |  | 44493 | 2227 | 1519138 | 2395 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 19160 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137631 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 44493 | 1335 | 1512255 | 3037 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 45555 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137604 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | OTHER |  | 44493 | 1745 | 1514548 | 419 | Distribution Circuit | Vegetation | Tree - fell into line | 716 | 295356 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0136591 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | PAUL SWEET-2104 | 83252104 | JUMPER |  | 44494 | 2141 | 1520403 | 2306 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 2306 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0138607 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 44493 | 1931 | 1515155 | 2628 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 55188 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137307 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG TREES-0402 | 83050402 | FUSE |  | 44493 | 2019 | 1515454 | 2776 | Distribution Circuit | Vegetation | Tree - fell into line | 234 | 649584 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0136796 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 44480 | 1149 | 1493213 | 1700 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 102000 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0129285 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE |  | 44494 | 1245 | 1518848 | 2880 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 5760 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0138225 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | TRIP-SAVER |  | 44493 | 1820 | 1514781 | 1415 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 69335 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136681 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE |  | 44493 | 1439 | 1513001 | 1696 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 184864 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137277 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | RECLOSER |  | 44493 | 1721 | 1510162 | 2637 | Distribution Circuit | Vegetation | Tree - branch fell on line | 429 | 1006018 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136495 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44493 | 1327 | 1512134 | 2910 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 64020 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 21-0136597 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44493 | 1802 | 1514833 | 4114 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 69938 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137601 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44494 | 727 | 1517351 | 3208 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 57744 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0138559 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER |  | 44493 | 1459 | 1514519 | 209 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 3647 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136517 | OH | Sus | 0 | 2021 | OCT | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44493 | 803 | 1509083 | 1771 | Distribution Circuit | Vegetation | Tree - branch fell on line | 124 | 219604 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136385 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44494 | 1449 | 1519328 | 3011 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12044 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137716 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44493 | 1756 | 1514588 | 4299 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8598 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137719 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44493 | 1349 | 1512629 | 1711 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 13688 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0136839 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44493 | 1144 | 1510876 | 1443 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 64429 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0136255 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 44493 | 1744 | 1514552 | 2912 | Distribution Circuit | Vegetation | Tree - fell into line | 139 | 386848 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136522 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44493 | 1802 | 1514635 | 4283 | Distribution Circuit | Vegetation | Tree - branch fell on line | 32 | 137056 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0138032 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | OTHER |  | 44494 | 1716 | 1519874 | 1566 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1566 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137687 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44494 | 1837 | 1520097 | 2333 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 20997 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0138581 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | SWITCH |  | 44493 | 1721 | 1521750 | 2818 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 55560 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136495 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | OCB |  | 44493 | 1311 | 1511978 | 1597 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 4791 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136163 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | OCB |  | 44493 | 748 | 1508433 | 1920 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 58416 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135717 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44493 | 950 | 1514668 | 3263 | Distribution Circuit | Vegetation | Tree - branch fell on line | 45 | 146835 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137574 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 44493 | 932 | 1509231 | 238 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 6426 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136028 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER |  | 44493 | 927 | 1509552 | 1983 | Distribution Circuit | Vegetation | Tree - branch fell on line | 219 | 387345 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135883 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 44493 | 1528 | 1512529 | 2656 | Distribution Circuit | Vegetation | Tree - fell into line | 290 | 791596 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136364 | OH | Sus | 0 | 2021 | OCT | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 44493 | 744 | 1508408 | 508 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2540 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135836 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 44493 | 1457 | 1513137 | 2536 | Distribution Circuit | Vegetation | Tree - fell into line | 420 | 684500 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136348 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44493 | 1615 | 1514024 | 1704 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 17040 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136547 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 44480 | 1034 | 1492771 | 391 | Distribution Circuit | Vegetation | Tree - fell into line | 1682 | 559642 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0128730 | OH | Sus | 31554589 | 2021 | OCT | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | TRIP-SAVER |  | 44493 | 1456 | 1515872 | 1246 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 52332 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136430 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44493 | 919 | 1509332 | 3343 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 3343 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0138255 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 44493 | 1616 | 1513130 | 1379 | Distribution Circuit | Vegetation | Tree - fell into line | 654 | 782799 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136430 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER |  | 44494 | 2211 | 1520840 | 2709 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 19529 | Clear-Strong Winds-Rain-Combination;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0138210 | OH | Sus | 45018624 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44494 | 2300 | 1520558 | 2734 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 68350 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0138875 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44494 | 2208 | 1520448 | 1232 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 28336 | Clear-Strong Winds-Rain-Combination;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0138270 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44493 | 1118 | 1515636 | 3180 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 127200 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136674 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44494 | 2210 | 1520513 | 2753 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 55089 | Clear-Strong Winds-Rain-Combination;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0138420 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER |  | 44493 | 1028 | 1510046 | 554 | Distribution Circuit | Vegetation | Tree - fell into line | 292 | 23572 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0135958 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44493 | 558 | 1508380 | 527 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 10540 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135727 | OH | Sus | 45018624 | 2021 | OCT | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 44493 | 1527 | 1521714 | 2993 | Distribution Circuit | Vegetation | Tree - branch fell on line | 90 | 269370 | Clear-Strong Winds-Rain-Combination;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0138182 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER |  | 44493 | 947 | 1519661 | 3355 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6710 | Strong Winds-Rain-Heavy Rain-Combination;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137551 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH |  | 44493 | 958 | 1519221 | 4890 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 132030 | Strong Winds-Rain-Heavy Rain-Combination;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137404 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER |  | 44493 | 1513 | 1512950 | 2118 | Distribution Circuit | Equipment Failure/Involved | Overhead | 453 | 751270 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136345 | OH | Sus | 45018624 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44493 | 1130 | 1510682 | 3495 | Distribution Circuit | Equipment Failure/Involved | Overhead | 70 | 244650 | Strong Winds-Rain-Heavy Rain-Combination;32-90 F | Pole-Wood | Broken- wire on ground | 21-0137135 | OH | Sus | 35297228 | 2021 | OCT | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44493 | 1530 | s1679601 | 4602 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 4602 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0138781 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 44493 | 1837 | 1514930 | 6072 | Distribution Circuit | Vegetation | Tree - fell into line | 985 | 2418564 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136577 | OH | Sus | 3527230 | 2021 | OCT | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 44493 | 1353 | 1512461 | 4474 | Distribution Circuit | Vegetation | Tree - fell into line | 335 | 858352 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136249 | OH | Sus | 35297228 | 2021 | OCT | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1108 | 82021108 | OTHER |  | 44493 | 1701 | 1519229 | 2916 | Distribution Circuit | Vegetation | Tree - bark fell into line | 1200 | 225815 | Strong Winds-Rain-Heavy Rain-Combination;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137407 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | JUMPER |  | 44494 | 1240 | 1519011 | 1380 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 8949 | Strong Winds-Rain-Heavy Rain-Combination;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137633 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE |  | 44480 | 848 | 1492427 | 536 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4288 | Clear-Overcast-Combination;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0128717 | OH | Sus | 31554479 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 2 | STELLING-1110 | 83481110 | TRIP-SAVER |  | 44493 | 1901 | 1520709 | 2673 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 74844 | Clear-Strong Winds-Rain-Combination;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137838 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 2 | STELLING-1110 | 83481110 | OTHER |  | 44493 | 2201 | 1520704 | 2701 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 26742 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137836 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 2 | SARATOGA-1115 | 83371115 | FUSE |  | 44493 | 1638 | 1519935 | 2904 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 47232 | Strong Winds-Rain-Heavy Rain-Combination;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137620 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | MORAGA-1104 | 13801104 | OCB |  | 44493 | 1138 | 1510794 | 1484 | Distribution Circuit | Vegetation | Tree - fell into line | 1766 | 419420 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136043 | OH | Sus | 35297091 | 2021 | OCT | Yes | Three Phase Fault | Yes | No
DIABLO | Tier 2 | MORAGA-1102 | 13801102 | OCB |  | 44493 | 1535 | 1513525 | 1592 | Distribution Circuit | Vegetation | Tree - fell into line | 1387 | 637066 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136634 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
DIABLO | Tier 3 | ORINDA-0402 | 12350402 | FUSE |  | 44493 | 1036 | 1510041 | 273 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 16653 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136039 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | ORINDA-0401 | 12350401 | SWITCH |  | 44493 | 626 | 1508198 | 1919 | Distribution Circuit | Vegetation | Tree - fell into line | 165 | 87885 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135681 | OH | Sus | 0 | 2021 | OCT | Yes | Three Phase Fault | Yes | No
DIABLO | Tier 2 | CLAYTON-2215 | 12022215 | RECLOSER |  | 44493 | 758 | 1508525 | 600 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 17400 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135726 | OH | Sus | 0 | 2021 | OCT | Yes | Force Out | Yes | No
DIABLO | Tier 2 | ROSSMOOR-1101 | 14161101 | OTHER |  | 44494 | 1726 | 1519895 | 1145 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 37160 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137733 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 2 | OAKLAND K-1104 | 12101104 | FUSE |  | 44493 | 702 | 1507327 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 11736 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136085 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE |  | 44493 | 907 | 1509040 | 527 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 13608 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136022 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE |  | 44494 | 127 | 1516294 | 1312 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 48426 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136973 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 3 | OAKLAND K-1101 | 12101101 | OTHER |  | 44493 | 1117 | 1510492 | 1812 | Distribution Circuit | Vegetation | Tree - fell into line | 1343 | 175015 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136332 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 2 | ARLINGTON-0401 | 13700401 | OTHER |  | 44493 | 1308 | 1511544 | 670 | Distribution Circuit | Vegetation | Tree - branch fell on line | 134 | 15714 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136400 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
FRESNO | Tier 2 | AUBERRY-1101 | 254151101 | RECLOSER |  | 44480 | 2112 | 1495296 | 1171 | Distribution Circuit | Vegetation | Tree - fell into line | 823 | 842904 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0129469 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | FUSE |  | 44493 | 605 | 1507762 | 658 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 27636 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135812 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | OTHER |  | 44493 | 623 | 1508120 | 704 | Distribution Circuit | Vegetation | Tree - branch fell on line | 161 | 44800 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135674 | OH | Sus | 0 | 2021 | OCT | Yes | Open Circuit | Yes | Yes
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE |  | 44493 | 1613 | 1513829 | 4282 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 17944 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0136624 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | RECLOSER |  | 44493 | 623 | 1507896 | 1191 | Distribution Circuit | Vegetation | Tree - branch fell on line | 296 | 496410 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135663 | OH | Sus | 0 | 2021 | OCT | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | OTHER |  | 44480 | 1747 | 1494925 | 613 | Distribution Circuit | Vegetation | Tree - fell into line | 281 | 171106 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0129333 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 44493 | 750 | 1508616 | 209 | Distribution Circuit | Vegetation | Tree - branch fell on line | 141 | 5920 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135839 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 44493 | 710 | 1508214 | 301 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 5117 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135917 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 44493 | 736 | 1508483 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 8704 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136152 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 44486 | 1502 | 1499622 | 533 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 5330 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0132067 | OH | Sus | 31554914 | 2021 | OCT | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 44493 | 1149 | 1509238 | 391 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 3796 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136049 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | OTHER |  | 44493 | 204 | 1507261 | 643 | Distribution Circuit | Vegetation | Tree - branch fell on line | 225 | 97401 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135570 | OH | Sus | 0 | 2021 | OCT | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | OTHER |  | 44493 | 213 | 1507503 | 634 | Distribution Circuit | Vegetation | Tree - fell into line | 130 | 82420 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135570 | OH | Sus | 0 | 2021 | OCT | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 44494 | 1310 | 1519411 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 325 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0137448 | OH | Sus | 0 | 2021 | OCT | Yes | Force Out | Yes | No
KERN | Tier 2 | TEJON-1102 | 252931102 | SWITCH |  | 44480 | 1241 | 1493424 | 2224 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 525 | 892299 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0128371 | OH | Sus | 0 | 2021 | OCT | Yes | Force Out | Yes | No
LOS PADRES | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER |  | 44494 | 455 | 1516952 | 853 | Distribution Circuit | Vegetation | Tree - fell into line | 1042 | 316084 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136878 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE |  | 44493 | 2342 | 1516064 | 919 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 40695 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136833 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | OTHER |  | 44480 | 1546 | 1494317 | 488 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3904 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0129281 | OH | Sus | 0 | 2021 | OCT | Yes | Force Out | Yes | Yes
LOS PADRES | Tier 2 | PASO ROBLES-1104 | 182611104 | OTHER |  | 44494 | 14 | 1516133 | 1016 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2032 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136963 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | RECLOSER |  | 44493 | 403 | 1507443 | 2296 | Distribution Circuit | Vegetation | Tree - fell into line | 391 | 728952 | Strong Winds-Heavy Rain-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135624 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | TRIP-SAVER |  | 44493 | 1218 | 1511400 | 1851 | Distribution Circuit | Vegetation | Tree - fell into line | 196 | 323391 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137219 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | Yes
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | FUSE |  | 44493 | 539 | 1507612 | 3470 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 20820 | Heavy Rain-Strong Winds-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137976 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | GREENBRAE-1102 | 43091102 | FUSE |  | 44493 | 1225 | 1511346 | 3080 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 120120 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137515 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | RECLOSER |  | 44493 | 1252 | 1511733 | 1634 | Distribution Circuit | Vegetation | Tree - fell into line | 1182 | 361696 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136262 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | RECLOSER |  | 44493 | 1347 | 1509987 | 1796 | Distribution Circuit | Vegetation | Tree - fell into line | 2669 | 494104 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136226 | OH | Sus | 0 | 2021 | OCT | Yes | Three Phase Fault | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE |  | 44493 | 901 | 1508980 | 441 | Distribution Circuit | Vegetation | Tree - fell into line | 408 | 179928 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135946 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | WOODACRE-1102 | 43021102 | RECLOSER |  | 44493 | 816 | 1508657 | 1684 | Distribution Circuit | Equipment Failure/Involved | Overhead | 791 | 175734 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135942 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE |  | 44493 | 1154 | 1510956 | 1963 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 106002 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0136070 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | OLEMA-1101 | 42291101 | FUSE |  | 44494 | 1115 | 1518450 | 1651 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3161 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137423 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 44493 | 647 | 1508155 | 2031 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 26403 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135865 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 44494 | 2227 | 1520842 | 1265 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 75166 | Heavy Rain-Strong Winds-Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 21-0137968 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER |  | 44493 | 916 | 1509123 | 1046 | Distribution Circuit | Vegetation | Tree - fell into line | 1057 | 166984 | Strong Winds-Heavy Rain-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135829 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | RECLOSER |  | 44493 | 618 | 1507900 | 795 | Distribution Circuit | Equipment Failure/Involved | Overhead | 365 | 154781 | Strong Winds-Heavy Rain-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135645 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER |  | 44493 | 1247 | 1511649 | 1622 | Distribution Circuit | Vegetation | Tree - fell into line | 143 | 24394 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136132 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 44493 | 1019 | 1509855 | 1835 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 16570 | Strong Winds-Heavy Rain-Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0136405 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | OCB |  | 44486 | 2058 | 1500244 | 407 | Distribution Circuit | Equipment Failure/Involved | Overhead | 898 | 145162 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0132188 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1107 | 102911107 | RECLOSER |  | 44493 | 807 | 1508601 | 1480 | Distribution Circuit | Vegetation | Tree - fell into line | 527 | 578346 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135741 | OH | Sus | 0 | 2021 | OCT | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | BIG BEND-1102 | 103751102 | FUSE |  | 44493 | 739 | 1508400 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 42504 | Strong Winds-Heavy Rain-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136508 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | BIG BEND-1101 | 103751101 | JUMPER |  | 44493 | 1008 | 1512396 | 1552 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1552 | Strong Winds-Heavy Rain-Clear;32-90 F | Conductor- Overhead | On Ground | 21-0136214 | OH | Sus | 0 | 2021 | OCT | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | CLARK ROAD-1102 | 103091102 | JUMPER |  | 44493 | 1015 | 1515949 | 2216 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 37484 | Strong Winds-Heavy Rain-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136687 | OH | Sus | 0 | 2021 | OCT | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 3 | PARADISE-1103 | 102831103 | FUSE |  | 44493 | 1505 | 1513180 | 1125 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1125 | Strong Winds-Heavy Rain-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136416 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1104 | 102831104 | FUSE |  | 44494 | 1532 | 1519479 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 811 | Strong Winds-Heavy Rain-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137602 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | BUTTE-1105 | 103081105 | FUSE |  | 44493 | 1048 | 1510182 | 1705 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 18755 | Strong Winds-Heavy Rain-Clear;32-90 F | Conductor- Overhead | On Ground | 21-0137067 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1103 | 102831103 | FUSE |  | 44493 | 906 | 1509005 | 556 | Distribution Circuit | Vegetation | Tree - fell into line | 229 | 90288 | Strong Winds-Heavy Rain-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136052 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1105 | 102831105 | FUSE |  | 44493 | 1228 | 1511375 | 1605 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 30495 | Strong Winds-Heavy Rain-Clear;32-90 F | Conductor- Overhead | On Ground | 21-0136103 | OH | Sus | 0 | 2021 | OCT | Yes | Force Out | Yes | Yes
NORTH VALLEY | Tier 3 | PARADISE-1105 | 102831105 | FUSE |  | 44493 | 1230 | 1510158 | 1603 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 11221 | Strong Winds-Heavy Rain-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136456 | OH | Sus | 0 | 2021 | OCT | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1106 | 102831106 | OTHER |  | 44493 | 843 | 1508817 | 1377 | Distribution Circuit | Vegetation | Tree - fell into line | 2685 | 3072433 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 21-0135860 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | Yes
NORTH VALLEY | Tier 2 | BIG BEND-1101 | 103751101 | FUSE |  | 44493 | 1037 | 1510120 | 1649 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 51119 | Strong Winds-Heavy Rain-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136397 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1106 | 102831106 | JUMPER |  | 44493 | 912 | 1515587 | 1654 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6170 | Strong Winds-Heavy Rain-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136661 | OH | Sus | 0 | 2021 | OCT | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1105 | 102831105 | FUSE |  | 44493 | 809 | 1517986 | 1952 | Distribution Circuit | Vegetation | Tree - fell into line | 226 | 425405 | Strong Winds-Heavy Rain-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137052 | OH | Sus | 0 | 2021 | OCT | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1105 | 102831105 | FUSE |  | 44493 | 844 | 1516068 | 2019 | Distribution Circuit | Vegetation | Tree - fell into line | 647 | 76785 | Strong Winds-Heavy Rain-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135860 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | RECLOSER |  | 44493 | 1027 | 1509999 | 961 | Distribution Circuit | Vegetation | Tree - fell into line | 1044 | 331877 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135967 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | CHESTER-1101 | 103181101 | FUSE |  | 44486 | 1555 | 1499679 | 539 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1078 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0132075 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 44493 | 1735 | 1514473 | 2826 | Distribution Circuit | Equipment Failure/Involved | Overhead | 485 | 677629 | Strong Winds-Rain-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137565 | OH | Sus | 35296505 | 2021 | OCT | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | SWITCH |  | 44494 | 112 | 1516270 | 2172 | Distribution Circuit | Equipment Failure/Involved | Overhead | 285 | 653306 | Strong Winds-Heavy Rain-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137161 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 44493 | 1208 | 1518530 | 2956 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 20692 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137201 | OH | Sus | 0 | 2021 | OCT | Yes | Force Out | Yes | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 44493 | 1827 | 1514858 | 3979 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 27627 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0138408 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | JUMPER |  | 44493 | 1824 | 1522317 | 3988 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3988 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0138407 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER |  | 44493 | 1302 | 1515447 | 1569 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 41483 | Heavy Rain; | Conductor- Overhead | Broken- wire on ground | 21-0136633 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER |  | 44493 | 1331 | 1510737 | 3123 | Distribution Circuit | Vegetation | Tree - fell into line | 375 | 840882 | Strong Winds-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136196 | OH | Sus | 35296505 | 2021 | OCT | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 44493 | 1137 | 1518363 | 4639 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 64946 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0137151 | OH | Sus | 0 | 2021 | OCT | Yes | Three Phase Fault | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 44493 | 1135 | 1512061 | 3239 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 51824 | Strong Winds-Rain-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0138096 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE |  | 44493 | 1015 | 1510483 | 2055 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 26715 | Strong Winds-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136072 | OH | Sus | 0 | 2021 | OCT | Yes | Multi-Fault | Yes | No
SACRAMENTO | Tier 2 | NARROWS-2101 | 153132101 | OTHER |  | 44494 | 1325 | 1518981 | 2040 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2040 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0137473 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | Yes
SACRAMENTO | Tier 2 | DOBBINS-1101 | 153741101 | OTHER |  | 44493 | 1444 | 1512993 | 277 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 554 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136382 | OH | Sus | 0 | 2021 | OCT | Yes | Force Out | Yes | Yes
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 44493 | 1328 | 1512216 | 1778 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 69342 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136375 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | OTHER |  | 44493 | 1200 | 1512327 | 2873 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 11261 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136206 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | JUMPER |  | 44494 | 1645 | 1519218 | 1281 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 21777 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137583 | OH | Sus | 0 | 2021 | OCT | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER |  | 44494 | 853 | 1517847 | 1544 | Distribution Circuit | Vegetation | Tree - fell into line | 1004 | 287188 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137022 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER |  | 44480 | 1247 | 1493339 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 1005 | 214783 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0128898 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | RECLOSER |  | 44493 | 2145 | 1515730 | 2929 | Distribution Circuit | Vegetation | Tree - fell into line | 2674 | 671242 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0136701 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | CLARKSVILLE-2109 | 153612109 | FUSE |  | 44493 | 657 | 1508185 | 2161 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 71313 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0135770 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | OCB |  | 44494 | 310 | 1516805 | 2517 | Distribution Circuit | Vegetation | Tree - fell into line | 1296 | 1575225 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136848 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PENRYN-1103 | 152561103 | FUSE |  | 44493 | 1656 | 1514164 | 1166 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 17490 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0136541 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44493 | 1241 | 1511490 | 1661 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 16994 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0136548 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | RECLOSER |  | 44493 | 934 | 1508700 | 477 | Distribution Circuit | Vegetation | Tree - fell into line | 452 | 125384 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135853 | OH | Sus | 0 | 2021 | OCT | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE |  | 44493 | 1039 | 1511435 | 1765 | Distribution Circuit | Vegetation | Tree - fell into line | 874 | 33588 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136185 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | TRIP-SAVER |  | 44493 | 1036 | 1510094 | 1788 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 43188 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0136169 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | RECLOSER |  | 44493 | 840 | 1508811 | 85 | Distribution Circuit | Vegetation | Tree - fell into line | 317 | 26945 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135774 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44493 | 900 | 1508969 | 1582 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 39550 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136084 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | RECLOSER |  | 44493 | 1110 | 1513031 | 1456 | Distribution Circuit | Vegetation | Tree - fell into line | 215 | 167480 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135994 | OH | Sus | 0 | 2021 | OCT | Yes | None | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1101 | 152031101 | RECLOSER |  | 44493 | 2051 | 1515601 | 1302 | Distribution Circuit | Vegetation | Tree - fell into line | 156 | 181338 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136665 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1101 | 152031101 | FUSE |  | 44493 | 1751 | 1514896 | 2670 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 48060 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136570 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1101 | 152031101 | FUSE |  | 44493 | 1124 | 1514991 | 1941 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 16485 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0136913 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44493 | 1548 | 1513623 | 1698 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 13303 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136702 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE |  | 44493 | 1936 | 1515087 | 2714 | Distribution Circuit | Equipment Failure/Involved | Overhead | 96 | 260544 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0135692 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | FUSE |  | 44494 | 1500 | 1519386 | 1515 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4545 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137587 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44493 | 1817 | 1514819 | 2457 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 35073 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0137556 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | RECLOSER |  | 44480 | 1639 | 1494643 | 1582 | Distribution Circuit | Vegetation | Tree - fell into line | 260 | 302608 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0129258 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | RECLOSER |  | 44493 | 942 | 1509411 | 1566 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2115 | 1679474 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135874 | OH | Sus | 0 | 2021 | OCT | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | JUMPER |  | 44494 | 1156 | 1522014 | 2779 | Distribution Circuit | Vegetation | Tree - bark fell into line | 5 | 12234 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0138283 | OH | Sus | 0 | 2021 | OCT | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | JUMPER |  | 44493 | 942 | 1513682 | 1528 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 3056 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136398 | OH | Sus | 0 | 2021 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | FUSE |  | 44493 | 942 | 1511760 | 1528 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 204752 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135874 | OH | Sus | 0 | 2021 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | FUSE |  | 44493 | 942 | 1518541 | 2002 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 26026 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135874 | OH | Sus | 0 | 2021 | OCT | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER |  | 44493 | 1123 | 1514200 | 3200 | Distribution Circuit | Equipment Failure/Involved | Overhead | 454 | 908337 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136474 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1104 | 152481104 | RECLOSER |  | 44493 | 1033 | 1510024 | 2869 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 169271 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135941 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1104 | 152481104 | RECLOSER |  | 44493 | 834 | 1508752 | 1872 | Distribution Circuit | Vegetation | Tree - fell into line | 522 | 734607 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135772 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44494 | 1418 | 1519174 | 1772 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 45611 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0137772 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44493 | 1317 | 1512233 | 3052 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 48832 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137629 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | ALLEGHANY-1101 | 152101101 | RECLOSER |  | 44494 | 1131 | 1518529 | 3176 | Distribution Circuit | Equipment Failure/Involved | Overhead | 199 | 384334 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137200 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 44494 | 2235 | 1520550 | 994 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2982 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137794 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | OTHER |  | 44493 | 1121 | 1513820 | 2816 | Distribution Circuit | Equipment Failure/Involved | Overhead | 146 | 404794 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136438 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
SONOMA | Tier 2 | COTATI-1103 | 42271103 | RECLOSER |  | 44493 | 757 | 1508684 | 2012 | Distribution Circuit | Equipment Failure/Involved | Overhead | 857 | 572201 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0135821 | OH | Sus | 0 | 2021 | OCT | Yes | Multi-Fault | Yes | No
SONOMA | Tier 2 | COTATI-1105 | 42271105 | RECLOSER |  | 44493 | 717 | 1508260 | 787 | Distribution Circuit | Vegetation | Tree - fell into line | 802 | 316449 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135702 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | FUSE |  | 44493 | 548 | 1519810 | 3492 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 13968 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135725 | OH | Sus | 0 | 2021 | OCT | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | FUSE |  | 44493 | 523 | 1507589 | 2207 | Distribution Circuit | Vegetation | Tree - fell into line | 367 | 791411 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135625 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | FUSE |  | 44493 | 548 | 1515361 | 2306 | Distribution Circuit | Equipment Failure/Involved | Overhead | 142 | 327452 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135725 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | RECLOSER |  | 44493 | 548 | 1519415 | 3378 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 108096 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135725 | OH | Sus | 0 | 2021 | OCT | Yes | None | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | TRIP-SAVER |  | 44493 | 515 | 1520747 | 3482 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 250639 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0135617 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 44493 | 515 | 1519119 | 3235 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 7925 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137384 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | JUMPER |  | 44493 | 548 | s1678540 | 1914 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 21054 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135629 | OH | Sus | 0 | 2021 | OCT | Yes | None | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER |  | 44493 | 515 | 1507555 | 3718 | Distribution Circuit | Vegetation | Tree - fell into line | 1334 | 3908405 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135617 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | RECLOSER |  | 44493 | 517 | 1507571 | 3462 | Distribution Circuit | Vegetation | Tree - fell into line | 515 | 1216228 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0135620 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | SWITCH |  | 44493 | 635 | 1517596 | 1999 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 37981 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136575 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 44493 | 515 | 1520751 | 3214 | Distribution Circuit | Vegetation | Tree - branch fell on line | 107 | 343898 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135617 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | RECLOSER |  | 44493 | 731 | 1508344 | 3223 | Distribution Circuit | Vegetation | Tree - fell into line | 126 | 406098 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135705 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 44493 | 716 | 1511103 | 3238 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 16190 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136075 | OH | Sus | 0 | 2021 | OCT | Yes | None | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE |  | 44493 | 612 | 1514516 | 2107 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 21070 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135671 | OH | Sus | 0 | 2021 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | OCB |  | 44493 | 532 | 1507606 | 3703 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1130 | 1704238 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135626 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 44493 | 1125 | 1510626 | 274 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 8494 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136182 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 44493 | 1519 | 1513796 | 1305 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 10440 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136419 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE |  | 44493 | 1903 | 1517752 | 2324 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 11620 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137554 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | MONTE RIO-1111 | 42811111 | FUSE |  | 44493 | 902 | 1508971 | 601 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 11790 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136120 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | TRIP-SAVER |  | 44493 | 451 | 1507492 | 1470 | Distribution Circuit | Vegetation | Tree - fell into line | 788 | 759376 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135611 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE |  | 44493 | 1853 | 1517481 | 1436 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 72004 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137073 | OH | Sus | 0 | 2021 | OCT | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 44493 | 458 | 1510259 | 937 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 22488 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135611 | OH | Sus | 0 | 2021 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER |  | 44493 | 712 | 1508228 | 631 | Distribution Circuit | Vegetation | Tree - fell into line | 287 | 60408 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135891 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER |  | 44493 | 732 | 1508323 | 798 | Distribution Circuit | Vegetation | Tree - branch fell on line | 109 | 86982 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135977 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE |  | 44494 | 1122 | 1518476 | 1710 | Distribution Circuit | Vegetation | Tree - branch fell on line | 131 | 35976 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137273 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER |  | 44493 | 809 | 1508688 | 589 | Distribution Circuit | Vegetation | Tree - branch fell on line | 51 | 30039 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0136068 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | SANTA ROSA A-1104 | 42151104 | RECLOSER |  | 44493 | 754 | 1508509 | 2118 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 211800 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135728 | OH | Sus | 0 | 2021 | OCT | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 44494 | 1035 | 1518284 | 1632 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 14686 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137537 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER |  | 44480 | 1746 | 1494915 | 1062 | Distribution Circuit | Vegetation | Tree - fell into line | 220 | 216372 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0129330 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE |  | 44493 | 1841 | 1514933 | 4243 | Distribution Circuit | Environmental/External | Flood/Erosion | 16 | 67888 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137301 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | TRIP-SAVER |  | 44493 | 1011 | 1509997 | 1868 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 145096 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136295 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FULTON-1107 | 42561107 | FUSE |  | 44493 | 1751 | 1517937 | 1374 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4122 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137036 | OH | Sus | 0 | 2021 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 44493 | 838 | 1508776 | 4460 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 191780 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0136319 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER |  | 44493 | 619 | 1507973 | 723 | Distribution Circuit | Vegetation | Tree - fell into line | 303 | 149805 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135646 | OH | Sus | 0 | 2021 | OCT | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER |  | 44494 | 816 | 1517958 | 1701 | Distribution Circuit | Vegetation | Tree - fell into line | 458 | 121866 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137041 | OH | Sus | 0 | 2021 | OCT | Yes | Force Out | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 44493 | 1016 | 1509854 | 576 | Distribution Circuit | Vegetation | Tree - fell into line | 178 | 102528 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136056 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 44493 | 719 | 1508233 | 659 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 61287 | Clear;32-90 F | Conductor- Overhead | On Ground | 21-0135949 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CORRAL-1101 | 162991101 | RECLOSER |  | 44486 | 2302 | 1500403 | 897 | Distribution Circuit | 3rd Party | Vehicle | 322 | 69356 | Strong Winds-Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0132234 | OH | Sus | 35296048 | 2021 | OCT | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 44494 | 1038 | 1518293 | 179 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 537 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137138 | OH | Sus | 0 | 2021 | OCT | Yes | Open Circuit | Yes | Yes
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | FUSE |  | 44493 | 1828 | 1514828 | 1410 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1410 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0136613 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER |  | 44494 | 1127 | 1518511 | 407 | Distribution Circuit | Vegetation | Tree - branch fell on line | 541 | 115868 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137229 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | MARTELL-1103 | 163011103 | FUSE |  | 44480 | 1354 | 1493753 | 181 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 4887 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0129113 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | RECLOSER |  | 44494 | 137 | 1516238 | 751 | Distribution Circuit | Vegetation | Tree - fell into line | 375 | 42917 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0136802 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | MARTELL-1101 | 163011101 | RECLOSER |  | 44494 | 540 | 1517030 | 570 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 5070 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136890 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | MARTELL-1101 | 163011101 | RECLOSER |  | 44493 | 825 | 1508701 | 155 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 2897 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0135756 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE |  | 44493 | 1548 | 1513915 | 142 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 2840 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136441 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | SALT SPRINGS-2102 | 163692102 | RECLOSER |  | 44480 | 2320 | 1495372 | 944 | Distribution Circuit | Vegetation | Tree - bark fell into line | 4470 | 2637835 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 21-0129505 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | STANISLAUS-1702 | 162821702 | SWITCH |  | 44494 | 1118 | 1518466 | 1438 | Distribution Circuit | Vegetation | Tree - branch fell on line | 988 | 464691 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0137184 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | OLETA-1102 | 163541102 | FUSE |  | 44493 | 2033 | 1515511 | 921 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 71329 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 21-0136705 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | Yes
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER |  | 44494 | 419 | 1516886 | 687 | Distribution Circuit | Vegetation | Tree - fell into line | 726 | 259365 | Clear;32-90 F | Crossarm- Wood | Broken- wire on object | 21-0136865 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER |  | 44480 | 1630 | 1494504 | 1099 | Distribution Circuit | Vegetation | Tree - fell into line | 2559 | 2802043 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0129259 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE |  | 44494 | 119 | 1516277 | 1214 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4856 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0137086 | OH | Sus | 0 | 2021 | OCT | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44493 | 2253 | 1515912 | 858 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 79893 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136778 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | OTHER |  | 44493 | 1739 | 1514454 | 2683 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 124817 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0136728 | OH | Sus | 0 | 2021 | OCT | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | PIT NO 1 1101 | 103721101 | RECLOSER |  | 44449 | 521 | 1467342 | 785 | Distribution Circuit | Animal | Other | 883 | 299396 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 21-0115712 | OH | Sus | 0 | 2021 | SEP | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER |  | 44449 | 813 | 1467728 | 633 | Distribution Circuit | 3rd Party | Vehicle | 1005 | 313378 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 21-0115798 | OH | Sus | 0 | 2021 | SEP | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 44905 | 702 | 1880401 | 1813 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 14504 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138095 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE |  | 44905 | 922 | 1881113 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 23400 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0138296 | OH | Sus | 0 | 2022 | DEC | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | RECLOSER |  | 44926 | 1345 | 1904231 | 1747 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 213134 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0142598 | OH | Sus | 0 | 2022 | DEC | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | FUSE |  | 44905 | 925 | 1881164 | 1643 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 3286 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0138444 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | OCB |  | 44926 | 1349 | 1904280 | 3179 | Distribution Circuit | Vegetation | Tree - fell into line | 3568 | 1249949 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0142607 | OH | Sus | 0 | 2022 | DEC | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | OCB |  | 44905 | 1611 | 1883508 | 1267 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2450 | 976238 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0138546 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 44926 | 1313 | 1904088 | 1759 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 66842 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0142622 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE |  | 44926 | 747 | 1903296 | 0 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 56088 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0142494 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | OCB |  | 44926 | 309 | 1902974 | 849 | Distribution Circuit | Vegetation | Tree - fell into line | 4856 | 1942256 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142449 | OH | Sus | 0 | 2022 | DEC | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | OCB |  | 44926 | 1520 | 1904704 | 1871 | Distribution Circuit | Vegetation | Tree - fell into line | 5331 | 3003867 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0142633 | OH | Sus | 0 | 2022 | DEC | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE |  | 44926 | 746 | 1903222 | 480 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 40800 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0142499 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER |  | 44926 | 1333 | 1904182 | 3121 | Distribution Circuit | Vegetation | Tree - fell into line | 665 | 1433125 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0142594 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN JUSTO-1101 | 183181101 | FUSE |  | 44926 | 1654 | 1905156 | 1366 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6830 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0004354 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | RECLOSER |  | 44905 | 1156 | 1881998 | 1731 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2738 | 711759 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0138414 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 44926 | 1152 | 1903819 | 1713 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 80511 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0142624 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER |  | 44926 | 759 | 1903295 | 3147 | Distribution Circuit | Vegetation | Tree - fell into line | 434 | 446712 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0142487 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER |  | 44926 | 529 | 1903038 | 539 | Distribution Circuit | Vegetation | Tree - fell into line | 269 | 118531 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0142489 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 44905 | 1254 | 1882566 | 1635 | Distribution Circuit | Equipment Failure/Involved | Overhead | 122 | 162784 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 22-0138528 | OH | Sus | 35409029 | 2022 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | RECLOSER |  | 44926 | 947 | 1904773 | 1683 | Distribution Circuit | Environmental/External | Flood/Erosion | 451 | 283693 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0142669 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 44926 | 1620 | 1908292 | 4061 | Distribution Circuit | Vegetation | Tree - fell into line | 231 | 508727 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0004449 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 44926 | 1205 | 1903846 | 2887 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 106794 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004409 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE |  | 44926 | 12 | 1902898 | 933 | Distribution Circuit | Vegetation | Tree - fell into line | 167 | 155811 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142448 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | OTHER |  | 44905 | 844 | 1880911 | 145 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 1595 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138226 | OH | Sus | 0 | 2022 | DEC | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 44926 | 524 | 1905289 | 2486 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 124300 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0142720 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | Yes
CENTRAL COAST | Tier 2 | PAUL SWEET-2106 | 83252106 | FUSE |  | 44926 | 1259 | 1904138 | 1425 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 12825 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0142846 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 44926 | 831 | 1910032 | 3418 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 71778 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142720 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 44926 | 1214 | 1910044 | 3303 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3303 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142720 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER |  | 44905 | 2332 | 1885273 | 942 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 16512 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138829 | OH | Sus | 0 | 2022 | DEC | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44926 | 748 | 1903287 | 4837 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 25303 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0142563 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44905 | 1529 | 1883387 | 1411 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 28220 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0138582 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 44905 | 1636 | 1883587 | 1392 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 37584 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138714 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | TRIP-SAVER |  | 44926 | 1829 | 1905541 | 2012 | Distribution Circuit | Environmental/External | Flood/Erosion | 49 | 73761 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0004484 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44926 | 1448 | 1904516 | 2776 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 28441 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0004559 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 44905 | 700 | 1880720 | 400 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 800 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138126 | OH | Sus | 0 | 2022 | DEC | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44926 | 1050 | 1903654 | 2933 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 23464 | Clear;32-90 F | Conductor- Overhead | Broken- wire on object | 22-0142617 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 44926 | 1134 | 1903738 | 1655 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 23930 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0142581 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 44926 | 1505 | 1905050 | 3911 | Distribution Circuit | Environmental/External | Flood/Erosion | 186 | 227946 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142916 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | OTHER |  | 44926 | 450 | 1902999 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 39186 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142481 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | JUMPER |  | 44926 | 1602 | 1905114 | 3011 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 18273 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004346 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 2 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 44905 | 1159 | 1882180 | 1540 | Distribution Circuit | Vegetation | Tree - fell into line | 547 | 282337 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0138363 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER |  | 44905 | 824 | 1881394 | 688 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3440 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138235 | OH | Sus | 0 | 2022 | DEC | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44905 | 821 | 1880737 | 681 | Distribution Circuit | Vegetation | Tree - fell into line | 677 | 275430 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0138342 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44926 | 1857 | 1905713 | 2423 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 55004 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0004513 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44926 | 1333 | 1904676 | 1685 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 138170 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0142703 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | RECLOSER |  | 44926 | 1352 | 1904288 | 1580 | Distribution Circuit | Vegetation | Tree - fell into line | 742 | 851656 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0142601 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | RECLOSER |  | 44905 | 1146 | 1881893 | 1510 | Distribution Circuit | Vegetation | Tree - branch fell on line | 741 | 142314 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0138153 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44926 | 1645 | 1907649 | 2700 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 26448 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0004433 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | OCB |  | 44926 | 730 | 1903197 | 1973 | Distribution Circuit | Vegetation | Tree - fell into line | 2322 | 431346 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142478 | OH | Sus | 0 | 2022 | DEC | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 44926 | 1535 | 1904851 | 1591 | Distribution Circuit | Equipment Failure/Involved | Overhead | 290 | 382210 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0142662 | OH | Sus | 0 | 2022 | DEC | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 44905 | 1309 | 1882523 | 1734 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 176868 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0138455 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44905 | 1009 | 1884267 | 1925 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 19250 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138716 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44905 | 1112 | 1881717 | 3097 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 21679 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138945 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 44905 | 1022 | 1881491 | 2836 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 14180 | Clear;32-90 F | Conductor- Overhead | On Ground | 22-0138994 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44905 | 1044 | 1881626 | 375 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 2625 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0138371 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER |  | 44926 | 746 | 1903260 | 6060 | Distribution Circuit | Environmental/External | Flood/Erosion | 796 | 1642120 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0142512 | OH | Sus | 35419155 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44905 | 1158 | 1881941 | 322 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 10626 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0138456 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44905 | 1358 | 1882752 | 1319 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 44846 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0138533 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44926 | 715 | 1903125 | 2067 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 16536 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004430 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 44926 | 746 | 1903230 | 2372 | Distribution Circuit | Vegetation | Tree - fell into line | 479 | 230136 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142483 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 44905 | 849 | 1880962 | 628 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 20724 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138154 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44905 | 953 | 1881335 | 537 | Distribution Circuit | Vegetation | Tree - branch fell on line | 45 | 24165 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0138442 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | TRIP-SAVER |  | 44905 | 857 | 1881008 | 1950 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 42900 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0138600 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44926 | 646 | 1903098 | 3441 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 110112 | Clear;32-90F | Conductor- Overhead | On Ground | 22-0142480 | OH | Sus | 31634035 | 2022 | DEC | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44926 | 1825 | 1909404 | 2660 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 18620 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004630 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | TRANSFORMER |  | 44926 | 2159 | 1907130 | 2771 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 25766 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004230 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44926 | 1825 | 1908968 | 2740 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 54800 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142797 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44905 | 854 | 1882393 | 3227 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 38724 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 22-0138398 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 44905 | 821 | 1880745 | 613 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1136 | 161962 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138134 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | JUMPER |  | 44926 | 1646 | 1905079 | 3996 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 7992 | Clear;32-90F | Conductor- Overhead | Broken- wire on object | 23-0004268 | OH | Sus | 0 | 2022 | DEC | Yes | Force Out | Yes | Yes
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | RECLOSER |  | 44915 | 1227 | 1894336 | 956 | Distribution Circuit | 3rd Party | Vehicle | 2456 | 103549 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 22-0140770 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE |  | 44926 | 2241 | 1907687 | 2418 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 6234 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004252 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
DIABLO | Tier 2 | TASSAJARA-2112 | 14662112 | RECLOSER |  | 44926 | 1644 | 1905081 | 2999 | Distribution Circuit | Vegetation | Tree - fell into line | 1184 | 1344808 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142685 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
DIABLO | Tier 3 | TASSAJARA-2108 | 14662108 | FUSE |  | 44926 | 1234 | 1903915 | 1887 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 69819 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142705 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND X-1106 | 12541106 | FUSE |  | 44926 | 1747 | 1905275 | 2674 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 10696 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142974 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | RECLOSER |  | 44926 | 1344 | 1904230 | 3042 | Distribution Circuit | Vegetation | Tree - fell into line | 205 | 182083 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142709 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAKLAND K-1104 | 12101104 | FUSE |  | 44926 | 1245 | 1903931 | 3146 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 104152 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142657 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | FUSE |  | 44926 | 623 | 1903402 | 382 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 10696 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142503 | OH | Sus | 45612557 | 2022 | DEC | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND D-1112 | 12041112 | SWITCH |  | 44926 | 1440 | 1904492 | 2762 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 140862 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142661 | OH | Sus | 0 | 2022 | DEC | Yes | Force Out | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | FUSE |  | 44905 | 2333 | 1884258 | 948 | Distribution Circuit | Vegetation | Tree - fell into line | 361 | 269609 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138758 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | OTHER |  | 44905 | 611 | 1880349 | 526 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 10729 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138077 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 44905 | 426 | 1880375 | 650 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 7800 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138069 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER |  | 44905 | 409 | 1880294 | 517 | Distribution Circuit | Vegetation | Tree - fell into line | 371 | 152117 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138047 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 44905 | 542 | 1880333 | 278 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 6672 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138072 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER |  | 44926 | 1519 | 1904736 | 411 | Distribution Circuit | Equipment Failure/Involved | Overhead | 84 | 20742 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142634 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | JUMPER |  | 44926 | 715 | 1903124 | 3232 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9818 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142538 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 44905 | 248 | 1880253 | 841 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 10682 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 22-0138343 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | FUSE |  | 44905 | 1258 | 1882454 | 2875 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 4945 | Clear;32-90F | Insulator | Broken- wire on object | 22-0138570 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | BRIDGEVILLE-1102 | 192461102 | FUSE |  | 44905 | 2316 | 1884461 | 1064 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2128 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138753 | OH | Sus | 0 | 2022 | DEC | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | FUSE |  | 44905 | 810 | 1880630 | 2183 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 8732 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138732 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HUMBOLDT BAY-1102 | 192341102 | FUSE |  | 44905 | 338 | 1880288 | 2014 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 8056 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138060 | OH | Sus | 0 | 2022 | DEC | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER |  | 44905 | 118 | 1880153 | 815 | Distribution Circuit | Vegetation | Tree - fell into line | 1274 | 699327 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138032 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER |  | 44905 | 449 | 1880304 | 2031 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 111908 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138049 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | OCEANO-1104 | 182601104 | RECLOSER |  | 44905 | 2028 | 1884145 | 2575 | Distribution Circuit | Equipment Failure/Involved | Overhead | 772 | 711360 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138684 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 3 | SAN LUIS OBISPO-1104 | 182631104 | FUSE |  | 44905 | 1942 | 1884049 | 3991 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 39910 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0139262 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
LOS PADRES | Tier 3 | ATASCADERO-1103 | 182541103 | FUSE |  | 44905 | 1944 | 1884056 | 1180 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 49560 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138896 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2110 | 183052110 | FUSE |  | 44926 | 1352 | 1904370 | 1286 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 23148 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142642 | OH | Sus | 0 | 2022 | DEC | Yes | Three Phase Fault | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | RECLOSER |  | 44905 | 1222 | 1882329 | 387 | Distribution Circuit | Vegetation | Tree - fell into line | 382 | 64752 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138378 | OH | Sus | 31630223 | 2022 | DEC | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | RECLOSER |  | 44926 | 1901 | 1905778 | 1340 | Distribution Circuit | Vegetation | Tree - fell into line | 382 | 62952 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142780 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | RECLOSER |  | 44905 | 642 | 1880379 | 318 | Distribution Circuit | Vegetation | Tree - branch fell on line | 204 | 61243 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138070 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE |  | 44915 | 1539 | 1894528 | 328 | Distribution Circuit | Vegetation | Tree - fell into line | 156 | 24548 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0140801 | OH | Sus | 31633601 | 2022 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE |  | 44905 | 726 | 1880453 | 796 | Distribution Circuit | Vegetation | Tree - fell into line | 156 | 75252 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138159 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | BIG BEND-1101 | 103751101 | RECLOSER |  | 44905 | 1021 | 1881519 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 312 | 93362 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138281 | OH | Sus | 0 | 2022 | DEC | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1105 | 102831105 | FUSE |  | 44905 | 909 | 1880603 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 7632 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138180 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER |  | 44905 | 1106 | 1881706 | 1488 | Distribution Circuit | Vegetation | Tree - fell into line | 633 | 237366 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 22-0138305 | OH | Sus | 0 | 2022 | DEC | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | WILDWOOD-1101 | 103611101 | FUSE |  | 44905 | 953 | 1881328 | 1575 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 7875 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138411 | OH | Sus | 0 | 2022 | DEC | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | WILDWOOD-1101 | 103611101 | FUSE |  | 44905 | 845 | 1881352 | 532 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 20216 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138228 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | PIT NO 3-2101 | 103732101 | RECLOSER |  | 44905 | 838 | 1880898 | 735 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 7251 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138142 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE |  | 44926 | 606 | 1903769 | 3615 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 59097 | Strong Winds-Rain; | Conductor- Overhead | On Ground | 22-0142555 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 44926 | 1528 | 1904749 | 1841 | Distribution Circuit | Vegetation | Tree - branch fell on line | 78 | 143598 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0004370 | OH | Sus | 0 | 2022 | DEC | Yes | Force Out | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 44926 | 1621 | 1904965 | 2010 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 90450 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0004350 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 2 | MENLO-1102 | 24131102 | JUMPER |  | 44926 | 1134 | 1903887 | 3123 | Distribution Circuit | Equipment Failure/Involved | Overhead | 123 | 91281 | Strong Winds-Rain; | Conductor- Overhead | Broken- wire on ground | 22-0142572 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1102 | 24131102 | FUSE |  | 44926 | 1439 | 1904491 | 1578 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 12624 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0004452 | OH | Sus | 0 | 2022 | DEC | Yes | Open Circuit | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER |  | 44926 | 639 | 1909866 | 3123 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 55203 | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0004709 | OH | Sus | 0 | 2022 | DEC | Yes | Open Circuit | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER |  | 44926 | 910 | 1903462 | 17756 | Distribution Circuit | Vegetation | Tree - branch fell on line | 68 | 343876 | Strong Winds-Rain; | Conductor- Overhead | Broken- wire on ground | 22-0142515 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 44905 | 1116 | 1881728 | 467 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 6538 | Heavy Rain-Strong Winds-Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0138490 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | HONCUT-1102 | 103211102 | FUSE |  | 44926 | 1853 | 1905663 | 2790 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 22320 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004312 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
SAN JOSE | Tier 2 | MORGAN HILL-2111 | 83242111 | FUSE |  | 44905 | 1103 | 1881688 | 412 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 11967 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138452 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | CLARKSVILLE-2103 | 153612103 | FUSE |  | 44926 | 2114 | 1906736 | 1250 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 56250 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004403 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | JUMPER |  | 44905 | 721 | 1880431 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 1224 | 41105 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0138129 | OH | Sus | 0 | 2022 | DEC | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 3 | DIAMOND SPRINGS-1105 | 152261105 | FUSE |  | 44926 | 2052 | 1906603 | 891 | Distribution Circuit | 3rd Party | Vehicle | 37 | 19496 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142989 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 44926 | 1 | 1902894 | 656 | Distribution Circuit | Vegetation | Tree - fell into line | 293 | 100678 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142451 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2105 | 153652105 | JUMPER |  | 44926 | 2057 | 1906752 | 1523 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1523 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004367 | OH | Sus | 0 | 2022 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER |  | 44926 | 1745 | 1905295 | 2786 | Distribution Circuit | Vegetation | Tree - fell into line | 1101 | 1480956 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142725 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 44905 | 1451 | 1883004 | 1406 | Distribution Circuit | Vegetation | Tree - fell into line | 3016 | 311325 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0138488 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 44926 | 838 | 1903390 | 3403 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 57851 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0004474 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PENRYN-1103 | 152561103 | FUSE |  | 44926 | 2015 | 1909334 | 2434 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 42054 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004624 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | FLINT-1101 | 152531101 | RECLOSER |  | 44926 | 2116 | 1906766 | 1289 | Distribution Circuit | Vegetation | Tree - fell into line | 228 | 114446 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 22-0142898 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | RECLOSER |  | 44926 | 1919 | 1905888 | 2404 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 211552 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004294 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER |  | 44926 | 2239 | 1907429 | 2353 | Distribution Circuit | Vegetation | Tree - fell into line | 874 | 1049560 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142965 | OH | Sus | 0 | 2022 | DEC | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | FUSE |  | 44926 | 2205 | 1907169 | 2396 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 67088 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004670 | OH | Sus | 0 | 2022 | DEC | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | FUSE |  | 44926 | 2106 | 1906730 | 2319 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 30147 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004677 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44926 | 2220 | 1908674 | 2576 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2576 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004440 | OH | Sus | 0 | 2022 | DEC | Yes | None | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER |  | 44926 | 1504 | 1907978 | 1410 | Distribution Circuit | Vegetation | Tree - fell into line | 2714 | 3557048 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004311 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | FUSE |  | 44926 | 2130 | 1906854 | 2509 | Distribution Circuit | Vegetation | Tree - fell into line | 221 | 198513 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004422 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44926 | 2314 | 1907501 | 2343 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 25773 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004679 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 44905 | 1246 | 1882399 | 355 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 18105 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0138498 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | FUSE |  | 44926 | 1640 | 1905056 | 280 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 8120 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142710 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44926 | 2056 | 1906615 | 2327 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 51194 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004360 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | FUSE |  | 44905 | 1343 | 1882870 | 1351 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 12187 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0138583 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE |  | 44926 | 1632 | 1905038 | 1187 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 9496 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142757 | OH | Sus | 0 | 2022 | DEC | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44926 | 2253 | 1907455 | 1003 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6018 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0004228 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | COTATI-1104 | 42271104 | FUSE |  | 44905 | 945 | 1881318 | 574 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 4018 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 22-0138295 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | FUSE |  | 44926 | 1552 | 1904866 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2268 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0142690 | OH | Sus | 0 | 2022 | DEC | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | OTHER |  | 44926 | 1613 | 1904934 | 267 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 267 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0142684 | OH | Sus | 45612880 | 2022 | DEC | Yes | Line to Ground | Yes | Yes
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | OTHER |  | 44905 | 1313 | 1882514 | 1474 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 15597 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138476 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | Yes
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | RECLOSER |  | 44905 | 852 | 1881210 | 2054 | Distribution Circuit | Vegetation | Tree - fell into line | 229 | 387658 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 22-0138219 | OH | Sus | 0 | 2022 | DEC | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER |  | 44905 | 522 | 1880319 | 421 | Distribution Circuit | Vegetation | Tree - branch fell on line | 565 | 118993 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138054 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | RECLOSER |  | 44905 | 957 | 1881374 | 4422 | Distribution Circuit | Vegetation | Tree - fell into line | 182 | 262243 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 22-0138232 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER |  | 44905 | 831 | 1881056 | 414 | Distribution Circuit | Vegetation | Tree - branch fell on line | 76 | 30558 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138172 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 44905 | 936 | 1881312 | 688 | Distribution Circuit | Vegetation | Tree - branch fell on line | 92 | 63296 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138463 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER |  | 44905 | 1711 | 1883787 | 289 | Distribution Circuit | Vegetation | Tree - fell into line | 166 | 29022 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138620 | OH | Sus | 0 | 2022 | DEC | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER |  | 44926 | 1217 | 1903871 | 175 | Distribution Circuit | Vegetation | Tree - fell into line | 2692 | 182904 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142569 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | OCB |  | 44926 | 1851 | 1905676 | 1420 | Distribution Circuit | Vegetation | Tree - fell into line | 3007 | 2571474 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0142760 | OH | Sus | 0 | 2022 | DEC | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 44905 | 852 | 1881014 | 298 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 4517 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0138260 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | OTHER |  | 44926 | 1458 | 1904907 | 242 | Distribution Circuit | Vegetation | Tree - fell into line | 1779 | 155290 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0142631 | OH | Sus | 0 | 2022 | DEC | Yes | Open Circuit | Yes | No
YOSEMITE | Tier 2 | WOODWARD-2108 | 255292108 | FUSE |  | 44905 | 2025 | 1884127 | 972 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 47628 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0138744 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | RECLOSER |  | 44926 | 1856 | 1905749 | 1176 | Distribution Circuit | Vegetation | Tree - fell into line | 2258 | 431578 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0142771 | OH | Sus | 0 | 2022 | DEC | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | FUSE |  | 44905 | 2208 | 1884403 | 952 | Distribution Circuit | Vegetation | Tree - fell into line | 261 | 109209 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 22-0138808 | OH | Sus | 0 | 2022 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | RECLOSER |  | 44810 | 1033 | 1801698 | 293 | Distribution Circuit | Vegetation | Tree - fell into line | 849 | 87909 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 22-0106392 | OH | Sus | 31615345 | 2022 | SEP | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 44811 | 547 | 1803969 | 161 | Distribution Circuit | Vegetation | Tree - fell into line | 279 | 44919 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0107132 | OH | Sus | 0 | 2022 | SEP | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER |  | 44811 | 1502 | 1804705 | 413 | Distribution Circuit | Vegetation | Tree - fell into line | 452 | 165918 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0107533 | OH | Sus | 31615353 | 2022 | SEP | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER |  | 44811 | 151 | 1803884 | 726 | Distribution Circuit | Equipment Failure/Involved | Overhead | 870 | 450048 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 22-0107108 | OH | Sus | 0 | 2022 | SEP | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | TRANSFORMER |  | 44984 | 1106 | 2011694 | 1601 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 9606 | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0036315 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | FUSE |  | 44984 | 1609 | 2012964 | 1420 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 126380 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0036675 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | JUMPER |  | 44978 | 1416 | 1991432 | 1351 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 16020 | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0031291 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | OCB |  | 44984 | 1902 | 2013598 | 1744 | Distribution Circuit | Equipment Failure/Involved | Overhead | 859 | 161070 | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0036739 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 44978 | 1903 | 1995334 | 2741 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 76748 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0032230 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 44984 | 1132 | 2012007 | 1773 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 72693 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036461 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER |  | 44978 | 1740 | 1994143 | 1945 | Distribution Circuit | Vegetation | Tree - fell into line | 279 | 432655 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031647 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER |  | 44978 | 1407 | 1991279 | 38 | Distribution Circuit | Equipment Failure/Involved | Overhead | 325 | 12350 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0031165 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER |  | 44981 | 551 | 2003057 | 3636 | Distribution Circuit | Vegetation | Tree - fell into line | 434 | 160555 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033690 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER |  | 44978 | 1557 | 1992851 | 2189 | Distribution Circuit | Vegetation | Tree - fell into line | 269 | 444571 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031469 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 44978 | 1407 | 1991849 | 559 | Distribution Circuit | Equipment Failure/Involved | Overhead | 109 | 60931 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031165 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 44980 | 149 | 1998774 | 2513 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 5026 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0033085 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 44978 | 1511 | 1992661 | 2770 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2770 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032728 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 44978 | 1542 | 1992691 | 2787 | Distribution Circuit | Vegetation | Tree - branch fell on line | 123 | 279127 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031925 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 44981 | 731 | 2003802 | 3229 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 19374 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035353 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | RECLOSER |  | 44983 | 1802 | 2010532 | 1064 | Distribution Circuit | Vegetation | Tree - branch fell on line | 353 | 148016 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035893 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | 83500401 | 83500401 | FUSE |  | 44980 | 1041 | 1999281 | 2789 | Distribution Circuit | Vegetation | Tree - branch fell on line | 53 | 147817 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033319 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | OTHER |  | 44983 | 1420 | 2010197 | 772 | Distribution Circuit | Vegetation | Tree - branch fell on line | 112 | 80470 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035809 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 44978 | 1838 | 1995030 | 2692 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 148060 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032771 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44978 | 1408 | 1995927 | 4245 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 131595 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031865 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER |  | 44978 | 1408 | 1998402 | 7375 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7375 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032659 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | RECLOSER |  | 44978 | 1519 | 1992363 | 1737 | Distribution Circuit | Vegetation | Tree - fell into line | 267 | 463779 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031346 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44978 | 2320 | 1996229 | 903 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 18963 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031969 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | SWITCH |  | 44981 | 626 | s1817086 | 3275 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 16365 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034176 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 44981 | 357 | 2010124 | 5186 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 82976 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035741 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 44978 | 1525 | 1992454 | 1660 | Distribution Circuit | Vegetation | Tree - fell into line | 213 | 52602 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031357 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 44981 | 414 | s1817085 | 3630 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 39930 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034174 | OH | Sus | 0 | 2023 | FEB | Yes |  | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 44981 | 357 | 2006011 | 3626 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 36260 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034314 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | TRIP-SAVER |  | 44981 | 356 | 2006080 | 4827 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 236523 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034330 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44981 | 430 | 2002546 | 2285 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 9140 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034339 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 44980 | 2154 | 2005835 | 3802 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 45624 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034245 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44980 | 809 | 2009096 | 7711 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 84821 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035430 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | TRIP-SAVER |  | 44978 | 1358 | 2000082 | 5984 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 269280 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033343 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 44985 | 919 | 2014635 | 1437 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 122981 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037242 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 44981 | 1503 | 2005954 | 1520 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 94240 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034299 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44981 | 1545 | 2006093 | 2835 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 28350 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0035084 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 44978 | 1358 | 2005457 | 5984 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 143616 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034130 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 44978 | 1338 | 1990865 | 3148 | Distribution Circuit | Vegetation | Tree - fell into line | 914 | 2876072 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031258 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44981 | 1851 | 2006757 | 2616 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 60168 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034505 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44985 | 342 | 2015251 | 1990 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 45770 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0037338 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | RECLOSER |  | 44978 | 1358 | 1991168 | 6047 | Distribution Circuit | Vegetation | Tree - branch fell on line | 307 | 1452509 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0031147 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 44980 | 2154 | 2008438 | 3616 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 65088 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035219 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44981 | 1852 | 2006765 | 4524 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 76908 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034507 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 44981 | 438 | 2001412 | 6782 | Distribution Circuit | Vegetation | Tree - fell into line | 332 | 1897671 | Overcast-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0033647 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44981 | 1853 | 2006766 | 4389 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 43890 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034508 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44981 | 1854 | 2006769 | 3886 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 128238 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034509 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44984 | 2020 | 2013857 | 900 | Distribution Circuit | Vegetation | Tree - branch fell on line | 82 | 73800 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036837 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER |  | 44978 | 1341 | 1994942 | 7050 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 70059 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031713 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER |  | 44978 | 1718 | 1997782 | 3023 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 39958 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032409 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44978 | 1442 | 1999190 | 6949 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 382195 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033003 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | SWITCH |  | 44978 | 1341 | 1998237 | 6987 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 733635 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0032596 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER |  | 44982 | 1653 | 2011686 | 4367 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 216729 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036210 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | JUMPER |  | 44980 | 2154 | 2008439 | 4333 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4333 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035224 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 44981 | 2054 | 2007179 | 3817 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 19085 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035125 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 44978 | 1449 | 1997111 | 2927 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 181474 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032180 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 44983 | 1711 | 2010411 | 2674 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 8022 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036168 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 44980 | 2109 | 2007025 | 4023 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 20115 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034563 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | RECLOSER |  | 44978 | 1224 | 1990315 | 4832 | Distribution Circuit | Vegetation | Tree - fell into line | 621 | 2598624 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031021 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 44980 | 2109 | 2007022 | 3824 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 11472 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034560 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 44980 | 2109 | 2007004 | 3763 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 11289 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034558 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER |  | 44980 | 2055 | 2016447 | 8087 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 16174 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037666 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 44980 | 2154 | 2008432 | 3668 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 7336 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035215 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | RECLOSER |  | 44981 | 1740 | 2006514 | 1346 | Distribution Circuit | Vegetation | Tree - fell into line | 221 | 277096 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034448 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44981 | 501 | 2006910 | 6519 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 104304 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034546 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 44980 | 2109 | 2006195 | 1403 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 23851 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034357 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 44978 | 1252 | 1997751 | 3089 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 52513 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0032401 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | OCB |  | 44978 | 1443 | 1991842 | 3247 | Distribution Circuit | Vegetation | Tree - fell into line | 1128 | 3304248 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031288 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | OCB |  | 44981 | 500 | 2002630 | 959 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1264 | 1179857 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033657 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 44981 | 434 | 2002537 | 1954 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 22473 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034006 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | SWITCH |  | 44980 | 2055 | 2004457 | 7098 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 276822 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033854 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44982 | 1446 | 2008747 | 5707 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 68484 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035308 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44981 | 503 | 2008880 | 6548 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 32740 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035368 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 44985 | 24 | 2014062 | 3935 | Distribution Circuit | Vegetation | Tree - fell into line | 306 | 198429 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037039 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 44980 | 2109 | 2007042 | 5506 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 11012 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0034564 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 44981 | 2101 | 2007187 | 1329 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 35883 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035072 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44982 | 1606 | 2008874 | 5353 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 26765 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035366 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44981 | 627 | 2003659 | 1915 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 65110 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034449 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44978 | 1549 | 1993027 | 3171 | Distribution Circuit | Vegetation | Tree - fell into line | 130 | 412230 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032977 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44980 | 2202 | 2009844 | 7036 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 541772 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035648 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44983 | 503 | 2009845 | 5042 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 35294 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035650 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 44978 | 1224 | 2005334 | 4832 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 154624 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034101 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 44982 | 647 | 2007745 | 6084 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 30420 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035115 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 44981 | 2111 | 2007197 | 6776 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 33880 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0035655 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 44978 | 1434 | 1991816 | 10178 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 388077 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031250 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44980 | 2316 | 2000906 | 2743 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 54860 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035563 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44981 | 438 | 2013373 | 6624 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 46368 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036700 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44981 | 354 | 2010180 | 7590 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 402270 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035764 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44985 | 1956 | 2016725 | 1194 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 11940 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037786 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44980 | 2202 | 2008545 | 7036 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 70360 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0035269 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44978 | 1631 | 1993270 | 4131 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 28917 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0032805 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44981 | 354 | 2012828 | 6826 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 34130 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036577 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44981 | 438 | 2010460 | 6782 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 345882 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035885 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44981 | 442 | 2013452 | 7493 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 29972 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036706 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 44981 | 612 | 2003308 | 1956 | Distribution Circuit | Vegetation | Tree - fell into line | 1535 | 913296 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033712 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44981 | 354 | 2013578 | 7590 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 30360 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036732 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 44978 | 1726 | 1991642 | 4438 | Distribution Circuit | Vegetation | Tree - fell into line | 219 | 698355 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031593 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | TRIP-SAVER |  | 44981 | 1140 | 2005218 | 3017 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 42238 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035158 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44978 | 1258 | 1998487 | 4706 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 127062 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032690 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44978 | 1434 | 2012203 | 13136 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 207969 |  | Conductor- Overhead | Broken- wire on ground | 23-0036369 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 44978 | 1321 | 1990666 | 4559 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 169064 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031099 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44978 | 1619 | 1995784 | 5919 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 266355 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031834 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44981 | 619 | 2008721 | 4670 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 658470 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035300 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 44981 | 555 | 2003072 | 3497 | Distribution Circuit | Vegetation | Tree - fell into line | 318 | 657896 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033693 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 44978 | 1521 | 2008274 | 7487 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 434246 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035157 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44981 | 621 | 2008269 | 4689 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 121914 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035154 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44978 | 1521 | 2008281 | 8609 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 172180 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035163 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER |  | 44978 | 1409 | 1997811 | 7397 | Distribution Circuit | Vegetation | Tree - fell into line | 139 | 17397 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0032425 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44981 | 939 | 2004844 | 1976 | Distribution Circuit | Vegetation | Tree - branch fell on line | 74 | 146224 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034020 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44981 | 640 | 2006038 | 3303 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 184968 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034323 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER |  | 44978 | 1838 | 1996609 | 8411 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 8483 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032350 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44978 | 1322 | 2008556 | 10138 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 182484 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035272 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44981 | 1747 | 2006488 | 6934 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6934 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035635 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | JUMPER |  | 44981 | 1241 | 2005156 | 5822 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 29110 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0035315 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44978 | 1409 | 1998313 | 4494 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 107856 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032625 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44981 | 1232 | 2005387 | 4532 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 18128 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035317 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44978 | 1409 | 1998129 | 5854 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 87810 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0032569 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER |  | 44978 | 1409 | 1998165 | 5855 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 40985 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0032578 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44981 | 724 | 2003760 | 1795 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 37695 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033870 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 44978 | 1747 | 1994536 | 7083 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 191241 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031693 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44978 | 1701 | 2010287 | 8604 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 51552 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035818 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 44982 | 1608 | 1998614 | 1338 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 32407 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035377 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44981 | 1223 | 2010278 | 3190 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 9570 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035815 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44981 | 1128 | 2009233 | 4258 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 85160 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035454 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44978 | 1510 | 2010361 | 8580 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 25740 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035840 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | TRIP-SAVER |  | 44978 | 1413 | 2010360 | 10237 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 225214 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035839 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44981 | 503 | 2010357 | 6385 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 351175 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035835 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44981 | 1129 | 2010192 | 10361 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 362635 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035775 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44981 | 730 | 2010353 | 7540 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 135720 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035834 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44981 | 1134 | 2010191 | 6129 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 79677 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035774 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44981 | 1158 | 2009950 | 7564 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 22692 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035694 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 44981 | 652 | 2003171 | 3468 | Distribution Circuit | Vegetation | Tree - fell into line | 383 | 1322829 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033735 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 44981 | 658 | 2002504 | 10716 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 21432 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033737 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44982 | 1418 | 2018133 | 7265 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 87180 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038091 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44981 | 427 | 2018402 | 10867 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 184739 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038229 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | BIG BASIN-1102 | 82841102 | FUSE |  | 44981 | 703 | 2019392 | 10711 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 10711 | Clear;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0038575 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44981 | 307 | 2020356 | 15243 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 15243 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0039013 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44981 | 307 | 2019263 | 14911 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 29822 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0038538 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44981 | 307 | 2019255 | 14128 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 324944 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038533 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44981 | 1430 | 2016401 | 7503 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 112545 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037652 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44981 | 324 | 2011009 | 9137 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 73096 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033630 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44981 | 307 | 2013168 | 14910 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 1477418 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036650 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44981 | 447 | 2006189 | 10775 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 305512 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034351 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44981 | 421 | 2011917 | 7982 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 103766 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036290 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44981 | 34 | 2020047 | 12352 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 284096 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038852 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER |  | 44981 | 259 | 2011944 | 9120 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 18240 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036299 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER |  | 44981 | 447 | 2002559 | 9571 | Distribution Circuit | Vegetation | Tree - fell into line | 350 | 2712272 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033649 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44981 | 410 | 2012029 | 12335 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 12335 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036314 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44981 | 23 | 2018700 | 12338 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 795922 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038343 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER |  | 44981 | 410 | 2012471 | 11095 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 11095 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036459 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44981 | 410 | 2010780 | 12319 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 123043 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035932 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44981 | 32 | 2019737 | 10926 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 131112 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038737 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44980 | 2323 | 2000917 | 12367 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 1156518 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0033527 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER |  | 44981 | 923 | 2018360 | 12371 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 24742 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038205 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | SWITCH |  | 44978 | 1829 | 1998033 | 1950 | Distribution Circuit | Vegetation | Tree - fell into line | 691 | 1101940 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032528 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44981 | 34 | 2018079 | 9763 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 419809 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038062 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44981 | 28 | 2019151 | 11186 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 268464 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038472 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH |  | 44981 | 410 | 2012924 | 13797 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 820443 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036600 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44981 | 410 | 2011736 | 10815 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 262189 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0036229 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44981 | 438 | 2010859 | 8564 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 453892 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035951 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44981 | 410 | 2009873 | 9289 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 74312 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0035664 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | TRIP-SAVER |  | 44981 | 28 | 2010307 | 11245 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 236145 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035821 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44981 | 33 | 2010864 | 12605 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 189075 | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0035953 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44980 | 2055 | 2010830 | 11455 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 34365 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035946 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44981 | 28 | 2010832 | 11245 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 146185 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035947 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER |  | 44981 | 410 | 2016480 | 6773 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 13546 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037672 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44981 | 410 | 2010165 | 5171 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 72394 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035756 | OH | Sus | 35427380 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44981 | 407 | 2010738 | 10890 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 392040 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035925 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER |  | 44981 | 410 | 2010685 | 6756 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 40536 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0035898 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44981 | 259 | 2010524 | 11581 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 173715 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035894 | OH | Sus | 35427380 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44981 | 335 | 2010874 | 10089 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 221958 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035959 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44981 | 704 | 2010866 | 10567 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 372040 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035954 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER |  | 44980 | 1953 | 2000370 | 11323 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 226310 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033428 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER |  | 44981 | 340 | 2019101 | 10591 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 95319 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0038457 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44978 | 1407 | 1991264 | 1889 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 21860 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031397 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44981 | 334 | 2010887 | 9645 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 114174 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035962 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44980 | 2103 | 2014978 | 8032 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 24096 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037262 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44981 | 33 | 2010871 | 12469 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 420528 |  | Conductor- Overhead | Broken- wire on ground | 23-0035957 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER |  | 44978 | 1829 | 2012199 | 10141 | Distribution Circuit | Environmental/External | Ice or snow | 62 | 628742 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036365 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44980 | 1919 | 2010401 | 12999 | Distribution Circuit | Environmental/External | Ice or snow | 13 | 168987 | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0035858 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44981 | 304 | 2005721 | 2466 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 17262 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033597 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44981 | 1510 | 2006550 | 1752 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 47304 | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0034460 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER |  | 44978 | 1829 | 2016320 | 16848 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 84240 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037622 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER |  | 44978 | 1829 | 2016319 | 16848 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 33696 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037622 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44978 | 1323 | 2016507 | 13242 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 66210 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037681 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER |  | 44982 | 405 | 2007616 | 7260 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 126660 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035379 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44978 | 1323 | 2016282 | 14606 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 29212 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037614 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER |  | 44978 | 1839 | 2016298 | 12671 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 164723 |  | Conductor- Overhead | Broken- wire on ground | 23-0037619 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER |  | 44978 | 1532 | 1992542 | 1404 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1138 | 205814 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031368 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER |  | 44981 | 32 | 2001322 | 8349 | Distribution Circuit | Environmental/External | Ice or snow | 78 | 268950 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033525 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER |  | 44981 | 210 | 2022883 | 13895 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 13895 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035848 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH |  | 44981 | 432 | 2010375 | 12141 | Distribution Circuit | Environmental/External | Ice or snow | 108 | 1319250 | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0035848 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44981 | 216 | 2009540 | 9585 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 9585 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035576 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE |  | 44978 | 1457 | 1992038 | 653 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 52240 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031709 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | SARATOGA-1103 | 83371103 | OTHER |  | 44981 | 211 | 2001784 | 14224 | Distribution Circuit | Equipment Failure/Involved | Overhead | 161 | 266759 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033589 | OH | Sus | 45680844 | 2023 | FEB | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44981 | 359 | 2021692 | 12221 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 134431 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0039617 | OH | Sus | 35427382 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | SARATOGA-1103 | 83371103 | FUSE |  | 44981 | 250 | 2005858 | 13997 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 55988 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033589 | OH | Sus | 45680844 | 2023 | FEB | Yes | Multi-Fault | Yes | No
DE ANZA | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44981 | 359 | 2021690 | 12181 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 60905 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039616 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44981 | 359 | 2021010 | 12332 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 123320 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039333 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44981 | 359 | 2021687 | 12156 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 328212 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039615 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | STELLING-1110 | 83481110 | FUSE |  | 44981 | 359 | 2006239 | 13691 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 27382 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034372 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
DE ANZA | Tier 3 | STELLING-1110 | 83481110 | RECLOSER |  | 44981 | 359 | 2016476 | 11696 | Distribution Circuit | Equipment Failure/Involved | Overhead | 216 | 2344655 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037670 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | STELLING-1110 | 83481110 | FUSE |  | 44981 | 427 | 2018287 | 9550 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 95500 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0038176 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | ROSSMOOR-1101 | 14161101 | FUSE |  | 44978 | 1618 | 1993081 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 18409 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0031574 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
FRESNO | Tier 2 | SAND CREEK-1103 | 254601103 | RECLOSER |  | 44982 | 243 | 2007526 | 9418 | Distribution Circuit | Equipment Failure/Involved | Overhead | 288 | 1036861 | Overcast-Fog-Snow;Below 32 F | Connector or Splice (OH) | Broken- wire on ground | 23-0035030 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | FUSE |  | 44982 | 222 | 2019103 | 7938 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 23814 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035170 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | RECLOSER |  | 44982 | 1100 | s1841389 | 6235 | Distribution Circuit | Vegetation | Tree - branch fell on line | 142 | 952476 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035170 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
FRESNO | Tier 2 | SAND CREEK-1103 | 254601103 | FUSE |  | 44982 | 1804 | 2013067 | 4135 | Distribution Circuit | Environmental/External | Ice or snow | 64 | 242472 | Drizzle-Strong Winds-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036622 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
FRESNO | Tier 2 | SAND CREEK-1103 | 254601103 | FUSE |  | 44982 | 211 | 2008658 | 922 | Distribution Circuit | Environmental/External | Ice or snow | 51 | 47022 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035280 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | SAND CREEK-1103 | 254601103 | RECLOSER |  | 44982 | 317 | 2007574 | 3598 | Distribution Circuit | Environmental/External | Ice or snow | 469 | 397553 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035025 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | FUSE |  | 44982 | 351 | 2019099 | 9272 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 185440 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035170 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | TRIP-SAVER |  | 44982 | 222 | 2008308 | 6753 | Distribution Circuit | Vegetation | Tree - branch fell on line | 44 | 297132 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035170 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | RECLOSER |  | 44982 | 832 | 2007761 | 6284 | Distribution Circuit | Vegetation | Tree - branch fell on line | 258 | 1283529 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0035078 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | FUSE |  | 44982 | 706 | 2018840 | 10696 | Distribution Circuit | Environmental/External | Ice or snow | 25 | 267400 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035170 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | OCB |  | 44982 | 1253 | s1841391 | 7561 | Distribution Circuit | Vegetation | Tree - branch fell on line | 182 | 856024 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0035170 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
FRESNO | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER |  | 44978 | 2123 | 1996040 | 2396 | Distribution Circuit | Vegetation | Tree - fell into line | 359 | 310543 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0031899 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
FRESNO | Tier 2 | TIVY VALLEY-1107 | 252941107 | RECLOSER |  | 44982 | 156 | 2007481 | 1917 | Distribution Circuit | Vegetation | Tree - branch fell on line | 519 | 311804 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035017 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
FRESNO | Tier 2 | DUNLAP-1103 | 254061103 | FUSE |  | 44982 | 117 | 2010243 | 6276 | Distribution Circuit | Environmental/External | Ice or snow | 8 | 50208 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035024 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-1103 | 254061103 | FUSE |  | 44982 | 311 | 2010007 | 5043 | Distribution Circuit | Environmental/External | Ice or snow | 9 | 45387 | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 23-0035024 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
FRESNO | Tier 2 | TIVY VALLEY-1107 | 252941107 | FUSE |  | 44982 | 214 | 2007501 | 9626 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 127261 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035906 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | Yes
FRESNO | Tier 2 | BALCH NO 1-1101 | 252501101 | RECLOSER |  | 44982 | 133 | 2007477 | 5257 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 5257 | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0035015 | OH | Sus | 35427376 | 2023 | FEB | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | AUBERRY-1101 | 254151101 | FUSE |  | 44982 | 237 | 2007521 | 3503 | Distribution Circuit | Environmental/External | Ice or snow | 7 | 24521 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035911 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | AUBERRY-1101 | 254151101 | OTHER |  | 44981 | 1937 | 2006881 | 4043 | Distribution Circuit | Equipment Failure/Involved | Overhead | 108 | 221472 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035732 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | AUBERRY-1101 | 254151101 | FUSE |  | 44981 | 1902 | 2006826 | 5364 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 64368 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035693 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
FRESNO | Tier 2 | AUBERRY-1101 | 254151101 | RECLOSER |  | 44981 | 2120 | 2007220 | 1100 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 1100 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034521 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
FRESNO | Tier 2 | AUBERRY-1101 | 254151101 | RECLOSER |  | 44981 | 1918 | 2006828 | 3880 | Distribution Circuit | Vegetation | Tree - fell into line | 499 | 113590 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034521 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | AUBERRY-1101 | 254151101 | RECLOSER |  | 44984 | 643 | 2011194 | 3030 | Distribution Circuit | Environmental/External | Ice or snow | 348 | 566814 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036061 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
FRESNO | Tier 2 | KERCKHOFF-1101 | 252561101 | FUSE |  | 44982 | 119 | 2007461 | 1080 | Distribution Circuit | Environmental/External | Ice or snow | 49 | 52920 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035155 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
FRESNO | Tier 2 | AUBERRY-1101 | 254151101 | FUSE |  | 44981 | 2138 | 2012888 | 10907 | Distribution Circuit | Environmental/External | Ice or snow | 72 | 720308 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 23-0036061 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | OTHER |  | 44985 | 551 | 2014155 | 396 | Distribution Circuit | Vegetation | Tree - fell into line | 229 | 13944 | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0037087 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | Yes
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE |  | 44982 | 1248 | 2012763 | 4469 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 40221 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0033599 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE |  | 44982 | 1006 | 2008163 | 3295 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 19770 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035853 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 44980 | 2043 | 2005910 | 4125 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 26355 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034457 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE |  | 44982 | 1009 | 2008471 | 3172 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 19032 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035958 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | JUMPER |  | 44981 | 353 | 2008463 | 3614 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3614 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033599 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | HIGHLANDS-1103 | 43361103 | FUSE |  | 44981 | 319 | 2008829 | 2533 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 7599 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035344 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44980 | 1801 | 2000200 | 1049 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6294 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033443 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | HIGHLANDS-1103 | 43361103 | FUSE |  | 44981 | 347 | 2011742 | 6581 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 52648 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036234 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | JUMPER |  | 44985 | 930 | 2014656 | 1886 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3772 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037482 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | Yes
HUMBOLDT | Tier 2 | HIGHLANDS-1103 | 43361103 | RECLOSER |  | 44981 | 320 | 2002118 | 7957 | Distribution Circuit | Equipment Failure/Involved | Overhead | 870 | 2694428 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0033605 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARCIA-0401 | 43040401 | RECLOSER |  | 44981 | 214 | 2001837 | 2588 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 23292 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0033578 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE |  | 44980 | 2053 | 2009846 | 9897 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 257322 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035651 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE |  | 44980 | 2053 | 2008720 | 11176 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 67056 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035299 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | SWITCH |  | 44980 | 2053 | 2008740 | 6868 | Distribution Circuit | Environmental/External | Ice or snow | 36 | 247248 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035304 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | FUSE |  | 44980 | 2116 | 2009896 | 8221 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 32884 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035675 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE |  | 44980 | 1948 | 2006194 | 6933 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 176384 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034356 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | KONOCTI-1102 | 43311102 | FUSE |  | 44980 | 2116 | 2006840 | 8221 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 189083 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0034526 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | RECLOSER |  | 44980 | 2053 | 2000379 | 6869 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 336581 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033435 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE |  | 44980 | 2106 | 2010251 | 8322 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 8322 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035805 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE |  | 44980 | 2106 | 2010251 | 8322 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 8322 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035805 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE |  | 44981 | 722 | 2003624 | 2048 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 14336 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034292 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | HIGHLANDS-1104 | 43361104 | FUSE |  | 44981 | 308 | 2009998 | 4978 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 159296 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035706 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | KONOCTI-1102 | 43311102 | SWITCH |  | 44981 | 240 | 2008419 | 2400 | Distribution Circuit | Vegetation | Tree - branch fell on line | 116 | 278400 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0033468 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | KONOCTI-1102 | 43311102 | JUMPER |  | 44980 | 2207 | 2009084 | 8021 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 8421 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035425 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | KONOCTI-1102 | 43311102 | FUSE |  | 44982 | 1821 | 2009141 | 4210 | Distribution Circuit | Equipment Failure/Involved | Overhead | 74 | 144860 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035451 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOPLAND-1101 | 42251101 | OTHER |  | 44981 | 1237 | 2005415 | 2863 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 99890 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034158 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | KONOCTI-1102 | 43311102 | OTHER |  | 44984 | 1543 | 2012905 | 2843 | Distribution Circuit | Environmental/External | Ice or snow | 1183 | 109614 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036652 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | HIGHLANDS-1102 | 43361102 | FUSE |  | 44981 | 739 | 2005226 | 3147 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2592 | 530473 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0034065 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | KONOCTI-1108 | 43311108 | TRIP-SAVER |  | 44978 | 1945 | 1994870 | 1042 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 164636 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031944 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | HOPLAND-1101 | 42251101 | FUSE |  | 44985 | 746 | 2014310 | 6502 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 36468 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037309 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | HOPLAND-1101 | 42251101 | FUSE |  | 44980 | 422 | 2005132 | 3756 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 341796 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0034034 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | KONOCTI-1108 | 43311108 | FUSE |  | 44981 | 1128 | 2005176 | 3099 | Distribution Circuit | Environmental/External | Ice or snow | 9 | 27891 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035319 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | CLEAR LAKE-1101 | 42141101 | FUSE |  | 44981 | 207 | 2009848 | 7924 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 166404 | Clear;Below 32 F | Connector or Splice (OH) | Broken- wire on ground | 23-0035652 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE |  | 44980 | 1729 | 2000141 | 7323 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 461349 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035112 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | REDBUD-1101 | 43191101 | FUSE |  | 44981 | 100 | 2006570 | 2342 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 96022 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0034461 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | REDBUD-1101 | 43191101 | OCB |  | 44981 | 100 | 2006271 | 1068 | Distribution Circuit | Vegetation | Tree - fell into line | 1489 | 1590252 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0034395 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | HARTLEY-1101 | 43211101 | JUMPER |  | 44980 | 2034 | 2005388 | 2486 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 9944 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033520 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | HOPLAND-1101 | 42251101 | FUSE |  | 44981 | 921 | 2004608 | 2160 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 29586 | Clear;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0034542 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | HARTLEY-1101 | 43211101 | JUMPER |  | 44980 | 2034 | 2009828 | 9646 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 19292 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035646 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | HARTLEY-1101 | 43211101 | FUSE |  | 44981 | 129 | 2005719 | 3527 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 31743 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0034209 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | FUSE |  | 44981 | 653 | 2003652 | 12077 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 277771 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038193 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | UKIAH-1114 | 42771114 | FUSE |  | 44982 | 1924 | 2009317 | 2876 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 143800 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035816 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | UKIAH-1114 | 42771114 | JUMPER |  | 44982 | 1950 | 2009445 | 2825 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 45872 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035564 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | LUCERNE-1103 | 43351103 | JUMPER |  | 44981 | 1743 | 2014887 | 5410 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 21640 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037236 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | LUCERNE-1103 | 43351103 | RECLOSER |  | 44981 | 4 | 2004397 | 2586 | Distribution Circuit | Equipment Failure/Involved | Overhead | 997 | 2550936 | Overcast-Snow;Below 32 F | Connector or Splice (OH) | Broken- wire on ground | 23-0033408 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 42871101 | OCB |  | 44980 | 1954 | 2000404 | 7171 | Distribution Circuit | Equipment Failure/Involved | Overhead | 735 | 3699170 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0033411 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE |  | 44980 | 1951 | 2009215 | 5531 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 22640 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035444 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 42871101 | JUMPER |  | 44985 | 1000 | 2014970 | 1900 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 17070 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037256 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE |  | 44980 | 1954 | 2010152 | 6997 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 139940 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035750 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE |  | 44980 | 1954 | 2015586 | 7001 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 84012 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037386 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE |  | 44980 | 1951 | 2014921 | 7000 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 70000 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037240 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER |  | 44978 | 1317 | 1990598 | 1565 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 46950 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031083 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE |  | 44980 | 1951 | 2010203 | 9430 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 94300 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035784 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 44980 | 2310 | 2004295 | 951 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 52820 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033820 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 44981 | 1036 | 2005092 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 750 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034009 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 44978 | 1057 | 1990128 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1320 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031177 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | CALPELLA-1101 | 43411101 | RECLOSER |  | 44981 | 2 | 2001103 | 2302 | Distribution Circuit | Environmental/External | Ice or snow | 389 | 247578 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033513 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | CALPELLA-1101 | 43411101 | JUMPER |  | 44981 | 1738 | 2006546 | 1536 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3072 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034459 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | MENDOCINO-1101 | 42951101 | RECLOSER |  | 44985 | 417 | 2014111 | 3708 | Distribution Circuit | Vegetation | Tree - fell into line | 739 | 240364 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037048 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 44978 | 1055 | 1990124 | 513 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 7290 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031017 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER |  | 44978 | 1130 | 1990179 | 1440 | Distribution Circuit | Vegetation | Tree - fell into line | 371 | 22900 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0030965 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | MENDOCINO-1101 | 42951101 | RECLOSER |  | 44981 | 426 | 2002507 | 3272 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 277012 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0033642 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | FUSE |  | 44985 | 426 | 2016780 | 3363 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 97527 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0037728 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | FUSE |  | 44984 | 1712 | 2013223 | 3989 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 19945 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037641 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER |  | 44985 | 1115 | 2014256 | 220 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 5060 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037272 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | OTHER |  | 44984 | 811 | 2011940 | 518 | Distribution Circuit | Vegetation | Tree - fell into line | 241 | 92579 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036298 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | Yes
HUMBOLDT | Tier 3 | MENDOCINO-1101 | 42951101 | FUSE |  | 44985 | 423 | 2019734 | 5020 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 256020 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038731 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 3 | MENDOCINO-1101 | 42951101 | FUSE |  | 44984 | 915 | 2011570 | 7711 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 161931 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036564 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | SWITCH |  | 44985 | 541 | 2015927 | 3261 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 19566 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037495 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | MENDOCINO-1101 | 42951101 | FUSE |  | 44982 | 1940 | 2009349 | 11153 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 28593 | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0035502 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | FUSE |  | 44985 | 541 | 2016118 | 3261 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 19566 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037576 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | FUSE |  | 44981 | 1306 | 2002414 | 1494 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8964 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034369 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER |  | 44984 | 812 | 2011373 | 465 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 45105 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036118 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER |  | 44980 | 703 | 2000856 | 3512 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 249352 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0033740 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 44978 | 1422 | 1995641 | 1580 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 9480 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031806 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER |  | 44978 | 1551 | 1992808 | 2323 | Distribution Circuit | Vegetation | Tree - fell into line | 138 | 161544 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0031416 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | FUSE |  | 44985 | 541 | 2019843 | 5036 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 40288 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0038780 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 44984 | 1009 | 2011737 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 28755 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036509 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | RECLOSER |  | 44981 | 31 | 2001317 | 1168 | Distribution Circuit | Vegetation | Tree - fell into line | 571 | 430706 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033529 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 44978 | 1634 | 1993238 | 1351 | Distribution Circuit | Vegetation | Tree - fell into line | 200 | 230974 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0031669 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER |  | 44985 | 442 | 2014119 | 808 | Distribution Circuit | Equipment Failure/Involved | Overhead | 811 | 393278 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037049 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER |  | 44980 | 1717 | 2000126 | 9555 | Distribution Circuit | Vegetation | Tree - fell into line | 655 | 1198611 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033352 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 44985 | 442 | 2016002 | 3344 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10032 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037532 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | OTHER |  | 44981 | 1825 | 2006627 | 2912 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 7594 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035279 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 44981 | 23 | 2009322 | 3689 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 55621 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035474 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 44980 | 1717 | 2006316 | 4213 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 117964 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034414 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 44985 | 449 | 2016325 | 4760 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 133280 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037624 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | JUMPER |  | 44980 | 1717 | 2006335 | 2941 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 26469 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034419 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 44985 | 801 | 2016370 | 3388 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10164 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037639 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 44982 | 215 | 2007565 | 8054 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 10409 | Partly Cloudy-Fog;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0035358 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | LAYTONVILLE-1102 | 42681102 | JUMPER |  | 44980 | 2039 | 2020492 | 11006 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 33018 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0039051 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 44980 | 1723 | 2009085 | 12748 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 101984 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035426 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44982 | 2104 | 2009658 | 8552 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 51312 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035856 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44980 | 2017 | 2001390 | 2911 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 17466 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033532 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | RECLOSER |  | 44980 | 1916 | 2000300 | 12489 | Distribution Circuit | Vegetation | Tree - fell into line | 642 | 1887138 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0033398 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 44978 | 1535 | 1991894 | 2567 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 10268 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032366 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44984 | 718 | 2013331 | 3419 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 64961 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036689 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 44980 | 1844 | 2000266 | 1390 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 16680 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033412 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44980 | 1912 | 2009230 | 11188 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 600048 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035448 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 44981 | 1008 | 2004907 | 524 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4192 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034056 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44980 | 1901 | 2009309 | 9614 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 57684 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035469 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 44984 | 826 | 2011395 | 4791 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 47910 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036632 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | JUMPER |  | 44984 | 816 | 2013330 | 4639 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4639 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036688 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | RECLOSER |  | 44980 | 1535 | 1999889 | 8291 | Distribution Circuit | Vegetation | Tree - fell into line | 262 | 1208006 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033294 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 44980 | 1535 | 2006738 | 14588 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 175056 |  | Conductor- Overhead | Broken- wire on ground | 23-0034497 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 44980 | 1535 | 2020178 | 14588 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 87528 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0038936 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 44980 | 1535 | 2006755 | 14588 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 175056 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034503 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 44980 | 1535 | 2008751 | 14588 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 350112 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035310 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 44980 | 1042 | 2023587 | 16163 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 48489 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0040290 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 44980 | 1042 | 2022162 | 16250 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 48750 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0039884 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 44980 | 1042 | 2015991 | 7572 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 45432 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037525 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 44980 | 1042 | 2010382 | 11942 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 131362 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035851 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 44980 | 1450 | 2009805 | 18943 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 113658 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035636 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 44982 | 1100 | 2009242 | 10275 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 82200 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035456 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 44980 | 1042 | 2015402 | 12082 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 48328 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037357 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | JUMPER |  | 44982 | 2046 | 2022411 | 12854 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 12854 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0039970 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | JUMPER |  | 44982 | 1823 | 2009909 | 2837 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2837 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035678 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 44980 | 1042 | 2019542 | 12082 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 36246 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0038640 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER |  | 44980 | 1450 | 1999868 | 18943 | Distribution Circuit | Vegetation | Tree - fell into line | 441 | 3654902 | Overcast;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0033285 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 44982 | 1000 | 2009247 | 3018 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3018 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035458 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 44978 | 1328 | 1991346 | 373 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2611 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031467 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 44982 | 1544 | 2008830 | 3019 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6038 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035920 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE |  | 44984 | 1552 | 2013333 | 4392 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 17568 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036690 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE |  | 44980 | 1935 | 2010090 | 15807 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 63228 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035731 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER |  | 44984 | 655 | 2012311 | 4770 | Distribution Circuit | Vegetation | Tree - fell into line | 226 | 439293 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036074 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 44985 | 1643 | 2021667 | 5471 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 93007 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0039600 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER |  | 44985 | 445 | 2014125 | 5751 | Distribution Circuit | Vegetation | Tree - fell into line | 632 | 2017763 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037050 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 44985 | 702 | 2019853 | 3467 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 52005 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038783 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1122 | 192321122 | FUSE |  | 44980 | 2031 | 2021597 | 12668 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 152016 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039569 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | FUSE |  | 44985 | 508 | 2030907 | 17957 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 125699 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043043 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 44985 | 449 | 2018467 | 6681 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 126939 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038258 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER |  | 44985 | 645 | 2014197 | 3506 | Distribution Circuit | Environmental/External | Ice or snow | 476 | 1404004 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037071 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER |  | 44981 | 347 | 2002268 | 9723 | Distribution Circuit | Vegetation | Tree - branch fell on line | 386 | 2020421 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0033615 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 3 | BRIDGEVILLE-1102 | 192461102 | JUMPER |  | 44985 | 1408 | 2018388 | 4267 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 32827 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0038220 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER |  | 44985 | 506 | 2014137 | 16637 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 250936 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037051 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | FUSE |  | 44985 | 1635 | 2016502 | 4395 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 17580 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0038306 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1102 | 192461102 | RECLOSER |  | 44980 | 851 | 1999038 | 624 | Distribution Circuit | Vegetation | Tree - fell into line | 248 | 70532 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0032941 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1102 | 192461102 | OTHER |  | 44984 | 733 | 2011387 | 2100 | Distribution Circuit | Vegetation | Tree - fell into line | 261 | 137258 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036126 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE |  | 44980 | 520 | 1998840 | 678 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 7458 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033088 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | MAPLE CREEK-1101 | 192101101 | FUSE |  | 44984 | 931 | 2012301 | 3466 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10398 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036424 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | MAPLE CREEK-1101 | 192101101 | OCB |  | 44984 | 931 | 2011661 | 3229 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 70695 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036203 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44985 | 851 | 2014402 | 6191 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 166557 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037710 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1121 | 192021121 | FUSE |  | 44980 | 644 | 2006842 | 3552 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 49728 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034527 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1121 | 192021121 | FUSE |  | 44980 | 644 | 2008694 | 3552 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 31968 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035290 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1121 | 192021121 | RECLOSER |  | 44980 | 644 | 1998889 | 3552 | Distribution Circuit | Vegetation | Tree - fell into line | 139 | 323610 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032856 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 44984 | 1021 | 2011765 | 7620 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 198120 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036433 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1102 | 192171102 | RECLOSER |  | 44984 | 940 | 2016490 | 4525 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 9050 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037675 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 44984 | 1720 | 2013291 | 7150 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7150 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036678 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER |  | 44980 | 939 | 1999122 | 11984 | Distribution Circuit | Vegetation | Tree - bark fell into line | 590 | 1295580 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0032982 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 44980 | 2146 | 2010154 | 8386 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 83860 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035752 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 44980 | 939 | 2009352 | 10034 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 220748 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035481 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | JUMPER |  | 44980 | 939 | 2010703 | 7673 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7673 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032982 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | JUMPER |  | 44980 | 2146 | 2010160 | 15550 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 46650 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035753 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 44980 | 1051 | 2010162 | 17494 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 114724 | Overcast;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035754 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | Yes
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 44980 | 939 | 2009354 | 10566 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 126792 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035483 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 44980 | 907 | 1999713 | 11943 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 322461 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033257 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 44985 | 449 | 2015581 | 4966 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 19864 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037382 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 44985 | 1056 | 2014944 | 7675 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 222575 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037524 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
KERN | Tier 3 | SISQUOC-1102 | 182811102 | TRIP-SAVER |  | 44984 | 1000 | 2011718 | 63532 | Distribution Circuit | Environmental/External | Ice or snow | 4 | 193577 | Overcast-Fog;32-90 F | Conductor- Overhead | On Ground | 23-0036225 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | ZACA-1102 | 182681102 | FUSE |  | 44982 | 806 | 2007842 | 3246 | Distribution Circuit | 3rd Party | Other | 14 | 18584 | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0035146 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | PURISIMA-1101 | 182971101 | FUSE |  | 44981 | 511 | 2003221 | 424 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 4240 | Overcast-Drizzle-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0033704 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2113 | 183052113 | SWITCH |  | 44981 | 2122 | 2010827 | 6953 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 27812 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0035944 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | MORRO BAY-1102 | 183011102 | JUMPER |  | 44978 | 1958 | 1995724 | 1202 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 8002 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031920 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
LOS PADRES | Tier 3 | ATASCADERO-1103 | 182541103 | FUSE |  | 44982 | 1615 | 2008905 | 4420 | Distribution Circuit | Equipment Failure/Involved | Overhead | 102 | 11086 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035496 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2113 | 183052113 | FUSE |  | 44981 | 2122 | 2009787 | 2738 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 38332 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0035631 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2113 | 183052113 | FUSE |  | 44981 | 2122 | 2010199 | 6760 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 27040 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035778 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
LOS PADRES | Tier 3 | TEMPLETON-2113 | 183052113 | FUSE |  | 44981 | 2122 | 2009484 | 3932 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 19660 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035569 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
LOS PADRES | Tier 3 | TEMPLETON-2113 | 183052113 | RECLOSER |  | 44981 | 2122 | 2007224 | 4037 | Distribution Circuit | Environmental/External | Ice or snow | 394 | 545003 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034663 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 3 | TEMPLETON-2113 | 183052113 | FUSE |  | 44981 | 2122 | 2009895 | 5435 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 16305 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035673 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE |  | 44978 | 1504 | 1992112 | 1726 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 45814 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031356 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | CAMBRIA-1102 | 182771102 | FUSE |  | 44978 | 1608 | 1993039 | 1495 | Distribution Circuit | Vegetation | Tree - fell into line | 1253 | 237107 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031648 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | CHOLAME-2102 | 182562102 | FUSE |  | 44981 | 2238 | 2009452 | 7715 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 15430 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0035565 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
LOS PADRES | Tier 2 | CHOLAME-2102 | 182562102 | JUMPER |  | 44981 | 2232 | 2009454 | 2605 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 221425 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035566 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | CHOLAME-2102 | 182562102 | RECLOSER |  | 44981 | 2232 | 2010229 | 6768 | Distribution Circuit | Environmental/External | Ice or snow | 5 | 25227 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035797 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
LOS PADRES | Tier 2 | CHOLAME-2102 | 182562102 | TRIP-SAVER |  | 44981 | 2238 | 2010405 | 3628 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 65304 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035860 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | CHOLAME-2102 | 182562102 | JUMPER |  | 44981 | 2238 | 2010398 | 3832 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 76640 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035857 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | SAN MIGUEL-1106 | 182661106 | FUSE |  | 44978 | 1842 | 1995063 | 1048 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3728 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031956 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
MISSION | Tier 2 | VASCO-1102 | 13751102 | FUSE |  | 44981 | 1524 | 2008151 | 1456 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 2912 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035120 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
MISSION | Tier 3 | SAN RAMON-2108 | 14232108 | FUSE |  | 44981 | 632 | 2003468 | 613 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 11034 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034027 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | RECLOSER |  | 44978 | 1253 | 1990476 | 1719 | Distribution Circuit | Vegetation | Tree - branch fell on line | 204 | 300060 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031055 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | FUSE |  | 44978 | 1555 | 1992819 | 1625 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 45500 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031622 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE |  | 44978 | 1459 | 1992057 | 1334 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 34684 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031602 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1104 | 42011104 | FUSE |  | 44978 | 1924 | 1995507 | 2321 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 102465 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031893 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | Yes
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE |  | 44978 | 1236 | 1991721 | 2957 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 84820 | Partly Cloudy-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0031245 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | RECLOSER |  | 44978 | 49 | -1996076 | 2963 | Distribution Circuit | Vegetation | Tree - fell into line | 103 | 210148 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031914 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 44978 | 1558 | 1992846 | 3014 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 201938 | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031744 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER |  | 44978 | 1244 | 1990436 | 1476 | Distribution Circuit | Vegetation | Tree - fell into line | 233 | 158712 | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031044 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER |  | 44984 | 1320 | 2012416 | 781 | Distribution Circuit | Vegetation | Tree - bark fell into line | 142 | 110902 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036462 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 44981 | 222 | 2005369 | 4735 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 47350 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034110 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2104 | 43292104 | FUSE |  | 44981 | 729 | 2004432 | 3496 | Distribution Circuit | Vegetation | Tree - branch fell on line | 70 | 224952 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034250 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | MONTICELLO-1101 | 43051101 | TRIP-SAVER |  | 44980 | 2329 | 2001675 | 2120 | Distribution Circuit | Equipment Failure/Involved | Overhead | 175 | 201170 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034389 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | PUEBLO-1105 | 43291105 | FUSE |  | 44980 | 2206 | 2000804 | 5457 | Distribution Circuit | Environmental/External | Ice or snow | 100 | 468304 | Overcast-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034329 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2103 | 43432103 | SWITCH |  | 44982 | 1256 | 2008465 | 3139 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 9417 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035238 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
NORTH BAY | Tier 2 | MONTICELLO-1101 | 43051101 | OTHER |  | 44981 | 109 | 2001496 | 6738 | Distribution Circuit | Equipment Failure/Involved | Overhead | 197 | 1154646 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033560 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SILVERADO-2105 | 43432105 | FUSE |  | 44981 | 653 | 2014920 | 6081 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 125960 | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0037243 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | JUMPER |  | 44980 | 2303 | 2010296 | 6875 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 33362 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035819 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | RECLOSER |  | 44981 | 33 | 2001334 | 2490 | Distribution Circuit | Vegetation | Tree - branch fell on line | 106 | 146284 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033530 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 44980 | 2301 | 2010143 | 6803 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 109163 |  | Pole-Wood | Broken- wire on ground | 23-0035747 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER |  | 44980 | 2139 | 2000708 | 11233 | Distribution Circuit | 3rd Party | Vehicle | 720 | 2875624 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0033473 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 44980 | 2139 | 2008517 | 4412 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 44120 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035258 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 44978 | 2020 | 1995863 | 877 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 7893 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031921 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 44980 | 2230 | 2008482 | 4372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 39348 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035245 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE |  | 44978 | 1434 | 1991789 | 1294 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6470 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0031464 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE |  | 44981 | 119 | 2001549 | 7747 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 77193 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035134 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 44983 | 1810 | 2021395 | 9899 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 148485 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039500 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 44983 | 1810 | 2021385 | 7119 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 42714 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039495 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 44985 | 754 | 2020636 | 5090 | Distribution Circuit | 3rd Party | Vehicle | 43 | 218870 | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0039177 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 44983 | 1810 | 2021566 | 9980 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 39920 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039550 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | JUMPER |  | 44983 | 1703 | 2010412 | 7106 | Distribution Circuit | Vegetation | Tree - fell into line | 138 | 955518 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035896 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 44983 | 2110 | 2018918 | 8431 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 177051 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038402 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 44983 | 2110 | 2018910 | 8399 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 33596 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038401 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | BANGOR-1101 | 103191101 | FUSE |  | 44985 | 1019 | 2014820 | 7240 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 72400 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037608 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 44985 | 755 | 2021025 | 5072 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 30432 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039233 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | OCB |  | 44984 | 1957 | 2013746 | 4272 | Distribution Circuit | Vegetation | Tree - fell into line | 668 | 2848140 | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0036764 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | JUMPER |  | 44984 | 1752 | 2021679 | 8436 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 16872 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039603 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | JUMPER |  | 44984 | 1752 | 2021681 | 8436 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 16872 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039605 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1107 | 102911107 | RECLOSER |  | 44981 | 959 | 2004228 | 1184 | Distribution Circuit | Vegetation | Tree - fell into line | 268 | 47397 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033935 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 44983 | 1441 | 2012290 | 8879 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 106548 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036418 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 44981 | 947 | 2004840 | 1599 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 19188 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035069 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 44985 | 902 | 2020177 | 6256 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 93840 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038935 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | FUSE |  | 44984 | 1957 | 2020464 | 5483 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 54830 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0039043 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 44984 | 909 | 2011559 | 4688 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 37504 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036201 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE |  | 44985 | 934 | 2020171 | 6224 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 51536 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038931 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 44983 | 1345 | 2013181 | 10171 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 20342 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036653 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 44985 | 842 | 2020080 | 3318 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 192444 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038882 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | JUMPER |  | 44984 | 1956 | 2018017 | 4257 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 25542 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0038050 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE |  | 44981 | 835 | 2004251 | 588 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 3552 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0034107 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE |  | 44984 | 1032 | 2020057 | 6028 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 60280 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0038861 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 44985 | 842 | 2019688 | 5823 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 15935 | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0038698 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | FUSE |  | 44984 | 1754 | 2013362 | 4379 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 87580 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036714 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | FUSE |  | 44985 | 842 | 2019691 | 4806 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 9612 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038701 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER |  | 44985 | 1330 | 2014466 | 2984 | Distribution Circuit | Vegetation | Tree - fell into line | 240 | 495029 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037471 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ELK CREEK-1101 | 102781101 | RECLOSER |  | 44981 | 359 | 2002410 | 1942 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 29130 | Clear;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0033622 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | BIG BEND-1102 | 103751102 | FUSE |  | 44981 | 814 | 2004402 | 350 | Distribution Circuit | Equipment Failure/Involved | Overhead | 85 | 29750 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0034188 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ELK CREEK-1101 | 102781101 | FUSE |  | 44981 | 925 | 2006593 | 1949 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 9394 | Clear;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0034473 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | CLARK ROAD-1102 | 103091102 | JUMPER |  | 44981 | 741 | 2003573 | 494 | Distribution Circuit | Environmental/External | Ice or snow | 160 | 74763 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033847 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 3 | CLARK ROAD-1102 | 103091102 | FUSE |  | 44981 | 1612 | 2006205 | 1530 | Distribution Circuit | Environmental/External | Ice or snow | 36 | 55080 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035150 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | BIG BEND-1101 | 103751101 | RECLOSER |  | 44981 | 830 | 2004254 | 1537 | Distribution Circuit | Vegetation | Tree - fell into line | 150 | 215983 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033825 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1103 | 102831103 | INTERRUPTER |  | 44978 | 1436 | 1991727 | 724 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 9061 | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0031363 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | BUTTE-1105 | 103081105 | TRIP-SAVER |  | 44981 | 922 | 2004703 | 3230 | Distribution Circuit | Environmental/External | Ice or snow | 55 | 177650 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034368 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | BIG BEND-1101 | 103751101 | RECLOSER |  | 44985 | 846 | 2014185 | 1869 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 3738 | Overcast-Fog-Snow-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0037129 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | NOTRE DAME-1104 | 102041104 | OTHER |  | 44981 | 528 | 2002898 | 934 | Distribution Circuit | Vegetation | Tree - fell into line | 181 | 193071 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033949 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 3 | PARADISE-1105 | 102831105 | RECLOSER |  | 44985 | 855 | 2014509 | 674 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3565 | 174884 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0037149 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1105 | 102831105 | FUSE |  | 44981 | 603 | 2003200 | 1852 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7408 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034354 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1105 | 102831105 | FUSE |  | 44981 | 735 | 2005549 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 8086 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034145 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | NOTRE DAME-1104 | 102041104 | FUSE |  | 44981 | 436 | 2005424 | 3394 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 50910 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034128 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | NOTRE DAME-1104 | 102041104 | JUMPER |  | 44981 | 524 | 2008333 | 2211 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2211 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035179 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | JUMPER |  | 44981 | 158 | 2009379 | 3903 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 19515 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 23-0035492 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE |  | 44981 | 152 | 2009209 | 3891 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 15564 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035443 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | NOTRE DAME-1104 | 102041104 | FUSE |  | 44983 | 1231 | 2013068 | 1763 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5289 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036626 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | JUMPER |  | 44981 | 306 | 2009204 | 3815 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 34317 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035441 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER |  | 44981 | 237 | 2001866 | 2411 | Distribution Circuit | Equipment Failure/Involved | Overhead | 383 | 674587 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0033592 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE |  | 44981 | 647 | 2015129 | 7796 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 132532 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037311 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | SYCAMORE CREEK-1111 | 102971111 | FUSE |  | 44982 | 937 | 2008509 | 1688 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6752 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035256 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | SYCAMORE CREEK-1111 | 102971111 | FUSE |  | 44982 | 937 | 2008412 | 1655 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4965 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035207 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | FUSE |  | 44984 | 1126 | 2011973 | 274 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 2740 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036472 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | JUMPER |  | 44978 | 1618 | 1994916 | 606 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 14492 | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031701 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 2 | TYLER-1105 | 103571105 | FUSE |  | 44981 | 1408 | 2005921 | 2638 | Distribution Circuit | Environmental/External | Ice or snow | 11 | 29018 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034504 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | TYLER-1105 | 103571105 | FUSE |  | 44982 | 1802 | 2009088 | 302 | Distribution Circuit | 3rd Party | Gun Shot | 5 | 1422 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035489 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | RED BLUFF-1103 | 103541103 | FUSE |  | 44981 | 648 | 2006260 | 1933 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 13531 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034383 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | RAWSON-1103 | 103531103 | FUSE |  | 44981 | 530 | 2004958 | 1997 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 7988 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033973 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | RED BLUFF-1101 | 103541101 | FUSE |  | 44981 | 520 | 2005593 | 831 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 7479 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034169 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | RED BLUFF-1104 | 103541104 | RECLOSER |  | 44981 | 831 | 2003300 | 2138 | Distribution Circuit | Equipment Failure/Involved | Overhead | 340 | 466388 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033837 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE |  | 44981 | 446 | 2002605 | 1877 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 47811 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034541 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE |  | 44981 | 756 | 2004022 | 3092 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 34463 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035355 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER |  | 44981 | 257 | 2002079 | 3703 | Distribution Circuit | Environmental/External | Ice or snow | 147 | 530690 | Clear;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0033598 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | PANORAMA-1102 | 103461102 | RECLOSER |  | 44981 | 535 | 2002951 | 2845 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2512 | 345204 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033680 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | JUMPER |  | 44982 | 818 | 2009470 | 1862 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 26462 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035567 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | FUSE |  | 44985 | 1136 | 2015110 | 563 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 563 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0037480 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | DESCHUTES-1101 | 103351101 | OTHER |  | 44981 | 1746 | 2006654 | 216 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 432 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034485 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | GIRVAN-1102 | 103401102 | FUSE |  | 44981 | 724 | 2003277 | 435 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 10440 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034256 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1104 | 103521104 | OTHER |  | 44981 | 424 | s1817427 | 1915 | Distribution Circuit | Equipment Failure/Involved | Overhead | 386 | 294608 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034572 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | RECLOSER |  | 44981 | 506 | 2002710 | 539 | Distribution Circuit | Equipment Failure/Involved | Overhead | 536 | 248719 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033662 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE |  | 44981 | 437 | 2002466 | 837 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 11084 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034298 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1101 | 103381101 | TRIP-SAVER |  | 44981 | 705 | 2003640 | 2050 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 98908 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035314 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | RECLOSER |  | 44981 | 105 | 2001523 | 5054 | Distribution Circuit | Vegetation | Tree - fell into line | 382 | 1560301 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0033550 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | RECLOSER |  | 44981 | 400 | 2002417 | 3715 | Distribution Circuit | Vegetation | Tree - bark fell into line | 400 | 769600 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0033624 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | RECLOSER |  | 44981 | 126 | 2001668 | 3900 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 273900 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0033566 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | JUMPER |  | 44982 | 2053 | 2009429 | 917 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 917 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035508 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 44980 | 1030 | s1816272 | 383 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 383 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033065 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 44978 | 1421 | 1991508 | 4360 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 142101 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031536 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE |  | 44980 | 1729 | 2000187 | 2983 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 106092 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033421 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER |  | 44978 | 1249 | 1990552 | 4805 | Distribution Circuit | Vegetation | Tree - fell into line | 156 | 749040 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031176 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 44982 | 824 | 2008050 | 3416 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 23912 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0035278 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 44981 | 1701 | 2008225 | 2702 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 56742 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035277 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE |  | 44984 | 1205 | 2012157 | 3127 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 6254 | Rain | Conductor- Overhead | Broken- wire on ground | 23-0036536 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | TRIP-SAVER |  | 44981 | 257 | 2006825 | 3623 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 129994 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034522 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1102 | 24131102 | FUSE |  | 44982 | 1332 | 2008549 | 4310 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 11220 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035318 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1102 | 24131102 | FUSE |  | 44981 | 809 | 2004114 | 1953 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 13833 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035247 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | Yes
PENINSULA | Tier 2 | MENLO-1102 | 24131102 | RECLOSER |  | 44981 | 312 | 2001838 | 3538 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 27726 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033600 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 44980 | 1958 | 2000413 | 1466 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 14660 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033842 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 44981 | 1022 | 2004945 | 1858 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5574 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034290 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER |  | 44981 | 747 | 2003924 | 603 | Distribution Circuit | Vegetation | Tree - fell into line | 192 | 5420 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033775 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER |  | 44981 | 928 | 2004932 | 5968 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 291389 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033999 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
PENINSULA | Tier 3 | HALF MOON BAY-1101 | 24101101 | FUSE |  | 44981 | 926 | 2004657 | 3336 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 46704 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034048 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
PENINSULA | Tier 3 | SAN CARLOS-1103 | 24181103 | FUSE |  | 44980 | 1055 | 1999294 | 3091 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 15455 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0033060 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 3 | DOBBINS-1101 | 153741101 | RECLOSER |  | 44985 | 2303 | 2017230 | 890 | Distribution Circuit | Vegetation | Tree - fell into line | 455 | 404950 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037853 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 3 | DOBBINS-1101 | 153741101 | FUSE |  | 44985 | 1254 | 2018171 | 4647 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 195174 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038107 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 3 | DOBBINS-1101 | 153741101 | FUSE |  | 44985 | 2303 | 2018180 | 3927 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 39270 | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0038110 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SAN JOSE | Tier 2 | SWIFT-2110 | 83392110 | FUSE |  | 44981 | 1104 | 2008822 | 3216 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 35376 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035408 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | TRANSFORMER |  | 44984 | 2005 | 2013753 | 1139 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1139 | Clear;Below 32 F | Transformer (OH) | Broken- wire on ground | 23-0037156 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 44984 | 1855 | 2018969 | 9801 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 523646 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038417 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 44984 | 1722 | 2015894 | 2954 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 41356 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037486 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 44985 | 1010 | 2014799 | 1947 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 109032 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037491 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 44985 | 1539 | 2016446 | 2649 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 7947 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037665 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 44981 | 1926 | 2006841 | 955 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 955 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034653 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | TRANSFORMER |  | 44981 | 1356 | 2005729 | 1270 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1270 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0034439 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | JUMPER |  | 44985 | 2000 | 2018905 | 1485 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1485 | Overcast-Fog;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0038399 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 44985 | 2103 | s1820438 | 1422 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 21330 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0037791 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 44985 | 1743 | 2016362 | 5682 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 270238 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037842 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 44985 | 2108 | 2020302 | 6897 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 255189 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038994 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 44985 | 1955 | 2018204 | 5683 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 107977 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038121 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 44985 | 1953 | 2017050 | 5685 | Distribution Circuit | Vegetation | Tree - fell into line | 159 | 773748 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037761 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 44985 | 2103 | 2018194 | 5689 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 699747 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038120 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 44985 | 1949 | 2019689 | 5763 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 103734 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038700 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1111 | 153081111 | OTHER |  | 44984 | 1351 | 2012586 | 285 | Distribution Circuit | Vegetation | Tree - branch fell on line | 882 | 49266 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036530 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | PLACERVILLE-1112 | 153081112 | SWITCH |  | 44984 | 1348 | 2012573 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 1238 | 175580 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036485 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | DIAMOND SPRINGS-1107 | 152261107 | FUSE |  | 44978 | 1453 | 1991982 | 643 | Distribution Circuit | 3rd Party | Vehicle | 44 | 28292 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0031476 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 44985 | 2014 | 2018675 | 3741 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 44919 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038335 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 44985 | 1952 | 2018887 | 3895 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 27265 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038396 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 44985 | 1952 | 2018251 | 8168 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 98016 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038151 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 44985 | 1952 | 2018806 | 4253 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 106325 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038370 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 44985 | 1258 | 2015639 | 4658 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 74528 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037466 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 44985 | 1954 | 2018820 | 5420 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 439020 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038377 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 44985 | 1955 | 2018497 | 4257 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 221364 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038274 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE |  | 44985 | 1952 | 2018682 | 4244 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 29708 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038337 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER |  | 44984 | 2028 | 2013793 | 9660 | Distribution Circuit | Vegetation | Tree - fell into line | 1291 | 1993303 |  | Conductor- Overhead | Broken- wire on ground | 23-0036774 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 44984 | 1356 | 2014316 | 1373 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 28833 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037097 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 44985 | 1955 | 2019571 | 7014 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 453930 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038653 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 44985 | 1303 | 2015651 | 7407 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 185175 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037590 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 44985 | 1245 | 2015672 | 8825 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 347669 | Overcast-Fog-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037417 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 2 | PENRYN-1107 | 152561107 | FUSE |  | 44981 | 407 | 2002443 | 548 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1644 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033884 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 44985 | 1952 | 2021588 | 6983 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 8 | 55864 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039565 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 44985 | 1323 | 2018447 | 7337 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 234784 | Overcast-Fog-Snow-Strong Winds;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0038249 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 44985 | 1329 | 2015711 | 7376 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 81136 | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0037585 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 44985 | 1954 | 2021095 | 6981 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 167544 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039366 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 44985 | 1955 | 2021753 | 7068 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 106020 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039633 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44981 | 1534 | 2006036 | 331 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 4634 | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0034492 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44984 | 1515 | 2012826 | 1528 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 21392 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036736 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44984 | 1653 | 2021563 | 6058 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 121160 | Overcast-Fog-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039549 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | JUMPER |  | 44984 | 1653 | 2021957 | 12902 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 289113 | Overcast-Fog-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039731 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44984 | 1653 | 2021569 | 12961 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 240117 | Overcast-Fog-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039551 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44985 | 26 | 2014063 | 10963 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 100988 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037540 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44985 | 2147 | 2017078 | 7975 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 75713 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040003 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44984 | 1849 | 2013573 | 1426 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 27094 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037394 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44985 | 2208 | 2017141 | 3569 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3569 | Partly Cloudy-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037843 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER |  | 44985 | 1710 | 2016324 | 2747 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 445014 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037625 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44981 | 1336 | 2005689 | 211 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 1477 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034322 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44985 | 1859 | 2016499 | 4166 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 133356 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037755 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44985 | 1710 | 2020126 | 7088 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 85056 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039074 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44984 | 1653 | 2018980 | 4413 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 105912 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038421 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44985 | 1710 | 2018904 | 7090 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 85110 | Overcast-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038398 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44984 | 1610 | 2018603 | 8736 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 297024 | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0038307 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44985 | 1217 | 2015406 | 8740 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 390769 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039964 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44984 | 1212 | 2021805 | 11733 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 293325 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039661 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44984 | 1610 | 2018598 | 9768 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 214896 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038305 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44984 | 1610 | 2022416 | 8803 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 246484 | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0039972 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44984 | 1610 | 2015540 | 11414 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 11414 | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0037378 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44984 | 1610 | 2015504 | 9981 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 149715 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037371 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44984 | 1610 | 2015682 | 10192 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 580944 | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0037426 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44984 | 1610 | 2022891 | 10183 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 61098 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040080 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44984 | 1047 | 2024703 | 12034 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 12034 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040726 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | JUMPER |  | 44984 | 1047 | 2011901 | 12063 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4216 | 5663307 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036619 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44984 | 1047 | 2022418 | 11980 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 23960 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039973 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44984 | 1047 | 2022910 | 13512 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 108096 | Clear;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0040084 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44984 | 1047 | 2011856 | 13194 | Distribution Circuit | Vegetation | Tree - fell into line | 174 | 2295756 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038315 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE |  | 44985 | 1158 | 2021857 | 7527 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 338715 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039702 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 2 | FORESTHILL-1102 | 152181102 | FUSE |  | 44985 | 1151 | 2021854 | 7397 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 59176 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0039701 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44984 | 1350 | 2016263 | 10050 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 301500 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037610 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44984 | 1350 | 2020372 | 5865 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 152490 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039022 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44984 | 1509 | 2018431 | 11646 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 46584 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038244 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44984 | 1350 | 2018320 | 11824 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 889769 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038187 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44984 | 1350 | 2018316 | 10330 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 20660 | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0038184 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44983 | 2152 | 2010980 | 11222 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 33666 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0036184 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44984 | 1350 | 2018311 | 11603 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 475723 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0038181 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44984 | 1520 | 2022788 | 8672 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 329536 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040066 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE |  | 44985 | 1151 | 2022765 | 8619 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 17238 | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0040058 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE |  | 44985 | 955 | 2021852 | 8803 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 466559 | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0039699 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44985 | 1151 | 2018952 | 7553 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 52871 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038412 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44985 | 953 | 2023998 | 9051 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 298683 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040433 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE |  | 44985 | 1151 | 2021853 | 8761 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 8761 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0039700 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44985 | 1155 | 2018966 | 7592 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 706056 | Overcast-Fog-Snow;Below 32 F | Pole - Tower- steel | Broken- wire on ground | 23-0038416 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44985 | 1025 | 2018911 | 7543 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 196118 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0038400 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 2 | HIGGINS-1110 | 152691110 | JUMPER |  | 44985 | 1349 | 2015773 | 162 | Distribution Circuit | Equipment Failure/Involved | Overhead | 96 | 14940 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037450 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | Yes
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44985 | 955 | 2018920 | 6209 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 173852 | Overcast-Fog-Snow;Below 32 F | Other | Broken- wire on ground | 23-0038403 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | RECLOSER |  | 44985 | 2108 | 2017028 | 3811 | Distribution Circuit | Vegetation | Tree - fell into line | 592 | 959771 | Partly Cloudy-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037775 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44985 | 953 | 2021370 | 7587 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 189675 | Clear;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0039483 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 44985 | 955 | 2023958 | 9021 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 9021 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0040420 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | FUSE |  | 44984 | 1555 | 2012463 | 2772 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 47124 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036623 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | FUSE |  | 44978 | 1639 | 1993310 | 1291 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 32160 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031824 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 44981 | 1054 | 2004949 | 383 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 766 | Clear;32-90F | Transformer (OH) | Broken- wire on ground | 23-0034037 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | JUMPER |  | 44985 | 1659 | 2018399 | 7016 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 14003 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038226 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | RECLOSER |  | 44985 | 1641 | 2016226 | 5301 | Distribution Circuit | Vegetation | Tree - fell into line | 2121 | 904643 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037611 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | FUSE |  | 44984 | 1306 | 2012384 | 251 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 32379 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036534 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | FUSE |  | 44983 | 1711 | 2010410 | 307 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 3684 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035924 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE |  | 44985 | 2138 | 2017085 | 7088 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 141760 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039907 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 44985 | 1616 | 2016159 | 3042 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 97291 | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0038585 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | RECLOSER |  | 44981 | 727 | 2003780 | 290 | Distribution Circuit | Equipment Failure/Involved | Overhead | 337 | 63124 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0033760 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44985 | 1323 | 2018413 | 8799 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 70392 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038237 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44985 | 1711 | 2023974 | 8650 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 86500 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0040429 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44984 | 1655 | 2013189 | 8702 | Distribution Circuit | Vegetation | Tree - grew into line | 129 | 1122558 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038234 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44985 | 1331 | 2018407 | 8753 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 166307 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038233 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | TRIP-SAVER |  | 44985 | 2356 | 2017274 | 2425 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 373450 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0038303 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | RECLOSER |  | 44984 | 1846 | 2013838 | 9843 | Distribution Circuit | Vegetation | Tree - fell into line | 534 | 2000519 |  | Conductor- Overhead | Broken- wire on ground | 23-0036731 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44984 | 1845 | 2023967 | 8600 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 129000 | Overcast-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 23-0040423 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44984 | 1653 | 2020078 | 10082 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 110902 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038878 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44984 | 1221 | 2021818 | 11651 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 273766 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039678 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44984 | 1221 | 2021820 | 10334 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 41336 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0039679 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44981 | 943 | 2004823 | 306 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 6263 | Clear;32-90F | Transformer (OH) | Broken- wire on ground | 23-0034000 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44984 | 1221 | 2021822 | 11714 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 35142 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0039682 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | SHADY GLEN-1102 | 152431102 | JUMPER |  | 44984 | 1221 | 2023969 | 11445 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 11445 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0040426 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1340 | 2031950 | 17021 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 799987 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043346 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1340 | 2024158 | 17022 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 204264 | Overcast-Snow;Below 32 F | Conductor- Overhead | On Ground | 23-0040524 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1615 | 2020500 | 15652 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 939120 |  | Conductor- Overhead | Broken- wire on ground | 23-0039053 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1354 | 2024779 | 15926 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 382224 | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0040789 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44985 | 1310 | 2020486 | 14580 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 116640 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039050 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1326 | 2024165 | 14654 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 820624 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040529 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE |  | 44985 | 1517 | 2016014 | 4181 | Distribution Circuit | Equipment Failure/Involved | Overhead | 97 | 405557 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0038932 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1310 | 2025759 | 11805 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 318735 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041280 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1619 | 2022864 | 14536 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 654120 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040072 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1101 | 152031101 | FUSE |  | 44984 | 2044 | 2013834 | 17002 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 391046 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039069 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44985 | 722 | 2022876 | 9134 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 164412 | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0040075 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1340 | 2026958 | 15939 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 812889 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0041821 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1340 | 2026958 | 15939 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 812889 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0041821 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1302 | 2025078 | 14596 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 744396 | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0040910 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1302 | 2025643 | 11883 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 11883 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041214 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1340 | 2025070 | 11611 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 325108 | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0040905 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1349 | 2025075 | 13369 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 227273 | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0040909 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1607 | 2024151 | 13013 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 39039 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0040498 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1345 | 2025638 | 13048 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 769832 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041211 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44983 | 1846 | 2010728 | 1249 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 14988 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035956 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1340 | 2025072 | 11563 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 11563 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0040908 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44981 | 1217 | 2005329 | 350 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2100 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0034159 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1349 | 2025071 | 14660 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 87960 | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0040907 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1340 | 2024155 | 17416 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 957880 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040521 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1348 | 2024156 | 15912 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 397800 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040522 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1340 | 2021969 | 16056 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 867024 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039776 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1606 | 2022877 | 11641 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 384153 | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0040076 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1606 | 2022877 | 11641 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 384153 | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0040076 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1326 | 2024154 | 13243 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 291346 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040520 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1606 | 2024098 | 14465 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 578600 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 23-0040467 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1606 | 2024098 | 14465 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 578600 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 23-0040467 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1342 | 2024164 | 15857 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 539138 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040528 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44983 | 2130 | 2024088 | 15490 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 77450 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0040460 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44983 | 2130 | 2024091 | 15645 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 62580 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0040461 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44983 | 2130 | 2024112 | 15526 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 15526 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0040469 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1516 | 2025088 | 11582 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 138984 | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0040916 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1524 | 2025083 | 11493 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 103437 | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0040914 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44983 | 2130 | 2023670 | 17000 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 85000 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0040330 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1249 | 2013106 | 14304 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 243168 | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0036634 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1516 | 2013277 | 10255 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 133315 | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0036676 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1515 | 2023684 | 15686 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 298034 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0040333 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44983 | 2130 | 2023473 | 17130 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 34260 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0040265 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 10 | 2011109 | 836 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2508 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036136 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44983 | 2129 | 2023456 | 9934 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 466892 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0040255 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BONNIE NOOK-1101 | 152301101 | FUSE |  | 44985 | 1620 | 2016167 | 7354 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 85019 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037612 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1606 | 2024086 | 14477 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 390879 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0040459 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1606 | 2024086 | 14477 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 390879 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0040459 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44984 | 1241 | 2025934 | 13272 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 185808 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041360 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | JUMPER |  | 44983 | 2130 | 2023475 | 15250 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 30500 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0040269 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44984 | 1241 | 2025933 | 14438 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 115504 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041359 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44984 | 1303 | 2025950 | 14217 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 28434 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0041370 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44983 | 1916 | 2025978 | 17387 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 799802 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041383 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44984 | 1249 | 2025942 | 14445 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 28890 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0041366 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | SWITCH |  | 44984 | 1303 | 2025931 | 16253 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 796397 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041355 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44984 | 1236 | 2025935 | 13213 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 264260 | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0041361 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44984 | 1140 | 2013377 | 15951 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 159510 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036702 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44983 | 1916 | 2025974 | 15328 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 275904 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041382 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1107 | 152481107 | FUSE |  | 44985 | 1928 | 2017553 | 4376 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 26256 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0038265 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44984 | 1303 | 2025954 | 14502 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 464064 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041374 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44984 | 1606 | 2021704 | 12549 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 326274 | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0039614 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44983 | 1916 | 2025956 | 15552 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 202176 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041375 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44984 | 1149 | 2025941 | 13072 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 326800 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041365 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44981 | 1717 | 2006396 | 1221 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 30525 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034462 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | RECLOSER |  | 44983 | 1916 | 2010805 | 11953 | Distribution Circuit | Vegetation | Tree - fell into line | 842 | 5727184 | Overcast-Fog-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0035936 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44984 | 1233 | 2012667 | 14793 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 133137 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036522 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44983 | 2010 | 2010861 | 818 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1636 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035952 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44984 | 1332 | 2012468 | 14146 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 170566 | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0036631 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44984 | 1150 | 2012089 | 14835 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 474720 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036427 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44984 | 1233 | 2026899 | 14793 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 147930 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035936 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44983 | 1916 | 2025973 | 14143 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 183859 | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0041381 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44984 | 1303 | 2025957 | 13022 | Distribution Circuit | Environmental/External | Ice or snow | 5 | 65110 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0041376 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44984 | 1641 | 2021781 | 14392 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 43176 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0039648 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44983 | 1916 | 2031661 | 18744 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 1387056 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043270 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 44983 | 1916 | 2025945 | 15276 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 137484 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041369 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | TRIP-SAVER |  | 44985 | 1954 | 2016633 | 2808 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 398736 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038659 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | FUSE |  | 44985 | 1338 | 2015745 | 11562 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 28932 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038424 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | FUSE |  | 44985 | 1954 | 2016631 | 9895 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 98950 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 23-0038131 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44984 | 1500 | 2012761 | 14748 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 235968 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036635 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44984 | 721 | 2011233 | 17541 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 245574 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036450 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | FUSE |  | 44985 | 2031 | 2018827 | 10971 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 43884 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0038769 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER |  | 44984 | 1819 | 2026999 | 14186 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 14186 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0041333 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | SWITCH |  | 44984 | 1823 | 2025869 | 12856 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 269976 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0041333 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44985 | 941 | 2022466 | 10459 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 324595 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039989 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44984 | 1148 | 2024720 | 11504 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 178784 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040743 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1105 | 152481105 | RECLOSER |  | 44984 | 1149 | 2012100 | 17210 | Distribution Circuit | Vegetation | Tree - fell into line | 1990 | 16642449 | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0036339 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44984 | 1824 | 2013536 | 11232 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 134784 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039990 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44983 | 1713 | 2010415 | 15812 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 189744 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035929 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE |  | 44985 | 1722 | 2017292 | 5490 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 76860 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037867 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE |  | 44984 | 1214 | 2020049 | 10421 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 812838 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038853 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44985 | 1053 | 2018461 | 10341 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 93069 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0038256 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44985 | 938 | 2022469 | 13969 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 502884 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039992 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1103 | 152481103 | JUMPER |  | 44984 | 2130 | 2025925 | 12684 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 88788 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0041353 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44984 | 1449 | 2026004 | 14208 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 284160 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0041385 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44984 | 635 | 2011186 | 10730 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 225330 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036148 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44984 | 1433 | 2021384 | 16116 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 48348 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0039492 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | SWITCH |  | 44984 | 1148 | 2026014 | 13297 | Distribution Circuit | Vegetation | Tree - fell into line | 440 | 5850680 | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0041388 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | Yes
SIERRA | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44984 | 1909 | 2013640 | 8598 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 87726 |  | Conductor- Overhead | Broken- wire on ground | 23-0036826 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44985 | 840 | 2016102 | 9109 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 9109 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037570 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44985 | 840 | 2022837 | 9039 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 18078 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0040069 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44984 | 1413 | 2030898 | 17226 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 155034 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 23-0043036 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER |  | 44983 | 2228 | 2010964 | 16943 | Distribution Circuit | Vegetation | Tree - fell into line | 194 | 1040285 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036041 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1104 | 152481104 | FUSE |  | 44984 | 2339 | 2018163 | 11104 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 444160 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0038103 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1104 | 152481104 | FUSE |  | 44978 | 1438 | 1991764 | 1233 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 66582 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0031448 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1104 | 152481104 | JUMPER |  | 44984 | 2339 | 2025921 | 12462 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 174468 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0041351 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER |  | 44983 | 2342 | 2011101 | 752 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 56772 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036049 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44983 | 2228 | 2030894 | 18111 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 181110 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043032 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44981 | 519 | 2003069 | 499 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 15469 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0033780 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1104 | 152481104 | FUSE |  | 44984 | 2339 | 2024002 | 9443 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 207746 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0040435 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44984 | 1247 | 2026739 | 14758 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 14758 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036414 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1104 | 152481104 | OTHER |  | 44984 | 2248 | 2013990 | 8312 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1144 | 4071513 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037035 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44984 | 1248 | 2026747 | 14408 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 86448 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036414 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44978 | 1414 | 1991825 | 1294 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6470 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031521 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44984 | 1148 | 2031439 | 17540 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 17540 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0043210 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44983 | 2201 | 2032767 | 19639 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 39278 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0043540 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER |  | 44983 | 2201 | 2032771 | 19785 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 59355 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0043541 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1102 | 152101102 | FUSE |  | 44984 | 1442 | 2020109 | 14604 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 29208 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0038889 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE |  | 44985 | 1303 | 2015734 | 8826 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 322336 | Overcast-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0038299 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | OCB |  | 44985 | 1220 | 2017699 | 13225 | Distribution Circuit | Vegetation | Tree - fell into line | 248 | 2769836 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037364 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE |  | 44985 | 1216 | 2024634 | 14352 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 489872 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0040692 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | RECLOSER |  | 44983 | 2123 | 2010957 | 16777 | Distribution Circuit | Vegetation | Tree - fell into line | 156 | 1058994 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036027 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PIKE CITY-1101 | 152201101 | JUMPER |  | 44983 | 2123 | 2024966 | 16777 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 16777 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0040876 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER |  | 44984 | 2247 | 2013966 | 15701 | Distribution Circuit | Vegetation | Tree - fell into line | 634 | 2433519 |  | Pole-Wood | Broken- wire on ground | 23-0037025 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1101 | 152101101 | JUMPER |  | 44985 | 1134 | 2023838 | 8745 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 34980 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0040384 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | ALLEGHANY-1101 | 152101101 | FUSE |  | 44985 | 1134 | 2021664 | 8759 | Distribution Circuit | Vegetation | Tree - bark fell into line | 5 | 43795 | Overcast-Fog-Snow-Strong Winds;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0039597 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 44984 | 822 | 2011382 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1800 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036236 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 44978 | 1750 | 1998249 | 2470 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 9880 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032602 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER |  | 44978 | 1732 | 1993986 | 1177 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1521 | 678908 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031103 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | OTHER |  | 44978 | 1351 | 1991145 | 1659 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 29435 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0032030 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE |  | 44978 | 1602 | 1995552 | 1449 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 23184 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031791 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE |  | 44978 | 1857 | 1995220 | 2395 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 89341 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031869 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE |  | 44978 | 1744 | 1994121 | 1467 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 117360 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032300 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE |  | 44978 | 1312 | 1993559 | 2046 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 2046 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031541 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 44978 | 1345 | 1990934 | 379 | Distribution Circuit | Vegetation | Tree - branch fell on line | 112 | 42448 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031364 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | TRIP-SAVER |  | 44978 | 1219 | 1995571 | 446 | Distribution Circuit | Vegetation | Tree - grew into line | 131 | 58426 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031796 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE |  | 44978 | 1356 | 1991129 | 201 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 4020 | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031219 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 44978 | 1244 | 1997906 | 2837 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 25533 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032472 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | TRANSFORMER |  | 44985 | 825 | 2014247 | 2123 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 42460 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037163 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | RECLOSER |  | 44978 | 1325 | 1991135 | 1662 | Distribution Circuit | Vegetation | Tree - fell into line | 252 | 433552 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031146 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 44978 | 1244 | 1994332 | 1659 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 41475 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031635 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1112 | 42751112 | JUMPER |  | 44981 | 909 | 2006240 | 4543 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 27258 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034373 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | Yes
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 44978 | 1325 | 1997654 | 2912 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 2912 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0032370 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | OTHER |  | 44978 | 1417 | 1991386 | 1304 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 30107 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031384 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | Yes
SONOMA | Tier 2 | FITCH MOUNTAIN-1112 | 42751112 | FUSE |  | 44978 | 1516 | 1992357 | 409 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 27403 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031516 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE |  | 44981 | 745 | 2003911 | 9203 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 152088 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034392 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE |  | 44981 | 102 | 2001448 | 973 | Distribution Circuit | Environmental/External | Ice or snow | 28 | 27244 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0033601 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | GEYSERVILLE-1102 | 42891102 | FUSE |  | 44981 | 33 | 2001312 | 1109 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 16635 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033786 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | CLOVERDALE-1102 | 42821102 | FUSE |  | 44981 | 1045 | 2005106 | 4106 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 189928 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034259 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | CLOVERDALE-1102 | 42821102 | FUSE |  | 44981 | 316 | 2010853 | 5051 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5051 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035948 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
SONOMA | Tier 2 | CLOVERDALE-1101 | 42821101 | FUSE |  | 44981 | 1405 | 2005950 | 7285 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 123845 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035765 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | Yes
SONOMA | Tier 2 | CLOVERDALE-1101 | 42821101 | FUSE |  | 44981 | 1009 | 2010153 | 7521 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 52647 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035751 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | GEYSERVILLE-1102 | 42891102 | FUSE |  | 44982 | 1759 | 2009078 | 5626 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 56260 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035423 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 2 | CLOVERDALE-1101 | 42821101 | FUSE |  | 44980 | 2137 | 2000728 | 2675 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 61525 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033460 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | CLOVERDALE-1101 | 42821101 | OTHER |  | 44982 | 1908 | 2009243 | 2663 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2663 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036274 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | Yes
SONOMA | Tier 2 | CLOVERDALE-1101 | 42821101 | FUSE |  | 44980 | 2105 | 2000415 | 2717 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 95026 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033448 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
SONOMA | Tier 2 | CLOVERDALE-1101 | 42821101 | FUSE |  | 44982 | 2116 | 2009357 | 1034 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 12408 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035551 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | CLOVERDALE-1101 | 42821101 | FUSE |  | 44980 | 1944 | 2005186 | 5627 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 191318 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034051 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | CLOVERDALE-1102 | 42821102 | FUSE |  | 44980 | 2037 | 2000528 | 2176 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 26112 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033489 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | CLOVERDALE-1102 | 42821102 | FUSE |  | 44982 | 1633 | 2002213 | 1147 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4588 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035380 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | Yes
SONOMA | Tier 2 | CLOVERDALE-1102 | 42821102 | FUSE |  | 44981 | 2 | 2001115 | 2381 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 42858 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0033829 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | STANISLAUS-1701 | 162821701 | RECLOSER |  | 44985 | 1119 | 2015009 | 3509 | Distribution Circuit | Vegetation | Tree - fell into line | 222 | 515745 | Overcast-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037270 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | STANISLAUS-1701 | 162821701 | RECLOSER |  | 44985 | 1550 | 2016092 | 84 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 9072 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037575 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 44984 | 1435 | 2012700 | 389 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 6613 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036613 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE |  | 44984 | 1424 | 2012678 | 1417 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3718 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036699 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER |  | 44985 | 636 | 2014184 | 4884 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 258852 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037349 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE |  | 44985 | 1552 | 2016066 | 1577 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3154 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037977 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | JUMPER |  | 44985 | 2128 | 2017511 | 1026 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2052 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037906 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | SWITCH |  | 44985 | 1208 | 2018021 | 4301 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 448546 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037349 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | OTHER |  | 44985 | 1943 | 2016599 | 5291 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 162160 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038721 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE |  | 44984 | 1543 | 2012920 | 1398 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 37746 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036616 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | OCB |  | 44981 | 1520 | 2006053 | 189 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1408 | 49295 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034248 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | OCB |  | 44985 | 1208 | 2015421 | 193 | Distribution Circuit | Unknown Cause | Patrol - not conducted | 1040 | 200720 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037345 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 44984 | 1840 | 2017886 | 2770 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 88640 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037345 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44985 | 1013 | 2020467 | 7452 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 112652 |  | Conductor- Overhead | Broken- wire on ground | 23-0039044 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE |  | 44984 | 1142 | 2012724 | 1746 | Distribution Circuit | Vegetation | Tree - branch fell on line | 49 | 85554 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036656 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 44985 | 649 | 2019140 | 4976 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 258752 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037349 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER |  | 44984 | 1831 | 2019863 | 5774 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 17322 | Clear;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0038788 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44985 | 1013 | 2020254 | 6362 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 44534 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038975 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 44985 | 1013 | 2020251 | 6272 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 777728 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038973 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44985 | 1014 | 2019988 | 6337 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 44359 | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0038841 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 44985 | 728 | 2021218 | 6537 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 1215882 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039429 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 44985 | 1013 | 2019777 | 7585 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 151700 | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0038753 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44985 | 1013 | 2022189 | 7480 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 59840 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039902 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44985 | 1013 | 2020036 | 6252 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 50016 | Overcast-Fog-Snow;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0038851 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44985 | 1013 | 2019995 | 7625 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 106750 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038843 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER |  | 44985 | 1014 | 2014179 | 6291 | Distribution Circuit | Vegetation | Tree - fell into line | 3595 | 7938552 | Overcast-Fog;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037218 | OH | Sus | 35427402 | 2023 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44984 | 1831 | 2020142 | 8669 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 8669 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0038915 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER |  | 44984 | 1707 | 2013218 | 34 | Distribution Circuit | Vegetation | Tree - fell into line | 308 | 10472 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036669 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | JUMPER |  | 44984 | 1339 | 2021233 | 7237 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7237 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0039436 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44984 | 1707 | 2013334 | 7235 | Distribution Circuit | Vegetation | Tree - fell into line | 368 | 25574 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0036669 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER |  | 44985 | 1013 | 2021559 | 6249 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 350313 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0039543 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER |  | 44985 | 544 | 2014089 | 2145 | Distribution Circuit | Equipment Failure/Involved | Overhead | 128 | 270266 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037060 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 44981 | 2202 | 2007457 | 646 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 646 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035011 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44984 | 2246 | 2015922 | 9664 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 260928 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037060 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 44985 | 544 | 2014755 | 10647 | Distribution Circuit | Equipment Failure/Involved | Overhead | 63 | 392077 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037060 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 44985 | 1208 | 2018962 | 5917 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 207095 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037349 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44985 | 544 | 2018989 | 7936 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 31744 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037060 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44985 | 544 | 2018878 | 9331 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 112339 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037060 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | SWITCH |  | 44985 | 642 | 2016754 | 1695 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 84750 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036767 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | JUMPER |  | 44985 | 642 | 2017945 | 6007 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 6007 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036767 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | OLETA-1102 | 163541102 | FUSE |  | 44984 | 1603 | 2012949 | 1364 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 16368 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0036713 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE |  | 44981 | 1838 | 2021122 | 9992 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 49960 | Overcast-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0039386 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE |  | 44981 | 1846 | 2019790 | 12341 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 24682 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034494 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | OCB |  | 44981 | 1846 | 2006633 | 9984 | Distribution Circuit | Equipment Failure/Involved | Overhead | 209 | 2086656 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034494 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE |  | 44981 | 1846 | 2021699 | 11133 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 590049 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034494 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | FUSE |  | 44981 | 1708 | 2015647 | 8391 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 142647 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034435 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE |  | 44981 | 1846 | 2006313 | 11242 | Distribution Circuit | Vegetation | Tree - fell into line | 268 | 1848859 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037696 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE |  | 44981 | 1846 | 2021691 | 11079 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 243738 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034494 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | RECLOSER |  | 44981 | 1846 | 2019551 | 11285 | Distribution Circuit | Vegetation | Tree - fell into line | 126 | 1421634 | Overcast-Heavy Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0034494 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | FUSE |  | 44981 | 1708 | 2011754 | 5837 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 23348 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034435 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1103 | 252531103 | SWITCH |  | 44981 | 1708 | 2013231 | 8393 | Distribution Circuit | Vegetation | Tree - fell into line | 213 | 1284489 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034435 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2102 | 254432102 | FUSE |  | 44982 | 700 | 2007755 | 6084 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 60840 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037990 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | Yes
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | JUMPER |  | 44981 | 1708 | 2009923 | 7145 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 114320 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034435 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1103 | 252531103 | FUSE |  | 44981 | 1708 | 2010321 | 9639 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 674730 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034435 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | SAN JOAQUIN #3 PH-1103 | 252531103 | SWITCH |  | 44981 | 1708 | 2018678 | 9964 | Distribution Circuit | Vegetation | Tree - fell into line | 150 | 1494600 | Overcast-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0034435 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE |  | 44981 | 1642 | 2006269 | 12588 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 868572 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034494 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE |  | 44981 | 1642 | 2020295 | 12588 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 377640 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038990 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | FUSE |  | 44981 | 1708 | 2009890 | 11387 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 394517 | Overcast-Heavy Rain;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0034435 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2102 | 254432102 | RECLOSER |  | 44982 | 226 | 2007516 | 5267 | Distribution Circuit | Vegetation | Tree - fell into line | 391 | 1904683 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0035019 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | RECLOSER |  | 44981 | 1708 | 2006370 | 7145 | Distribution Circuit | Equipment Failure/Involved | Overhead | 74 | 299510 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034435 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 254432104 | RECLOSER |  | 44981 | 1740 | 2006478 | 4153 | Distribution Circuit | Vegetation | Tree - branch fell on line | 764 | 853975 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034442 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE |  | 44981 | 1740 | 2008826 | 4109 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 764274 | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0034442 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE |  | 44981 | 1740 | 2008734 | 2896 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 14480 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034442 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | TRANSFORMER |  | 44981 | 1841 | 2014705 | 9859 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 77707 | Overcast-Fog-Heavy Rain;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0034496 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | JUMPER |  | 44981 | 1841 | 2008476 | 7969 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 160205 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034496 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE |  | 44981 | 1841 | 2015944 | 6753 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 366497 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034496 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE |  | 44981 | 1841 | 2008368 | 5667 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 45336 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034496 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE |  | 44981 | 1740 | 2009954 | 4158 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 89167 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034442 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | RECLOSER |  | 44981 | 2359 | 2007412 | 5513 | Distribution Circuit | Vegetation | Tree - fell into line | 339 | 1868907 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034999 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | RECLOSER |  | 44981 | 1841 | 2006504 | 5667 | Distribution Circuit | Equipment Failure/Involved | Overhead | 127 | 719709 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034496 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | RECLOSER |  | 44976 | 300 | 1988470 | 566 | Distribution Circuit | 3rd Party | Gun Shot | 2323 | 807587 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0030517 | OH | Sus | 45679421 | 2023 | FEB | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE |  | 44981 | 1841 | 2008357 | 5667 | Distribution Circuit | Vegetation | Tree - branch fell on line | 91 | 515697 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034496 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44982 | 705 | 2007769 | 6046 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 114874 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035500 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | Yes
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE |  | 44983 | 1555 | s1818945 | 2530 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 113850 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034999 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | SWITCH |  | 44981 | 1847 | 2018819 | 9968 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 867216 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034502 | OH | Sus | 45604552 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44981 | 1847 | 2014675 | 9904 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 227792 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034502 | OH | Sus | 45604552 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1102 | 254421102 | JUMPER |  | 44981 | 2054 | 2011407 | 3696 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 81312 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036140 | OH | Sus | 0 | 2023 | FEB | Yes | Open Circuit | Yes | Yes
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | JUMPER |  | 44981 | 1800 | 2010034 | 5872 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 546096 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034999 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44981 | 1847 | 2019433 | 8503 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 42515 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034502 | OH | Sus | 45604552 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE |  | 44981 | 1800 | 2011207 | 5872 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 146800 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034999 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1101 | 254421101 | RECLOSER |  | 44981 | 1906 | 2006588 | 2330 | Distribution Circuit | Vegetation | Tree - fell into line | 685 | 1493345 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034517 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1101 | 254421101 | FUSE |  | 44983 | 847 | 2009739 | 8691 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 34764 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037307 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1101 | 254421101 | JUMPER |  | 44981 | 1903 | 2008450 | 2366 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4732 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035232 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | JUMPER |  | 44981 | 1847 | 2012779 | 9804 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 215688 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034502 | OH | Sus | 45604552 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1101 | 254421101 | FUSE |  | 44981 | 1906 | 2008226 | 2729 | Distribution Circuit | Equipment Failure/Involved | Overhead | 101 | 275629 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035140 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1101 | 254421101 | RECLOSER |  | 44981 | 1906 | 2008909 | 5589 | Distribution Circuit | Equipment Failure/Involved | Overhead | 115 | 605391 |  | Crossarm- Wood | Broken- wire on ground | 23-0034517 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | FUSE |  | 44982 | 752 | 2008973 | 4725 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 259875 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035056 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44981 | 1847 | 2007338 | 8511 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 229797 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034502 | OH | Sus | 45604552 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | FUSE |  | 44982 | 752 | 2015661 | 4978 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 129428 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 23-0035056 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44981 | 1847 | 2007341 | 5734 | Distribution Circuit | Environmental/External | Ice or snow | 11 | 63074 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034502 | OH | Sus | 45604552 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44981 | 1846 | 2007401 | 8198 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 24594 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0034502 | OH | Sus | 45604552 | 2023 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44981 | 1827 | 2007826 | 9811 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 333574 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039259 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1101 | 254421101 | JUMPER |  | 44981 | 1906 | 2009079 | 3826 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 57628 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034517 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | FUSE |  | 44981 | 1821 | 2007402 | 9789 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 1086579 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039228 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1101 | 254421101 | FUSE |  | 44981 | 1906 | 2009804 | 4179 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 29253 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034517 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1103 | 254421103 | RECLOSER |  | 44982 | 752 | 2007825 | 6474 | Distribution Circuit | Vegetation | Tree - fell into line | 253 | 1211574 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0035056 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1101 | 254421101 | TRANSFORMER |  | 44981 | 1829 | 2009999 | 7210 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 7210 | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0035707 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1101 | 254421101 | JUMPER |  | 44984 | 1251 | 2020268 | 5874 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 11748 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0038981 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44982 | 1600 | 2008920 | 10106 | Distribution Circuit | Vegetation | Tree - fell into line | 139 | 1404734 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039501 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1101 | 254421101 | FUSE |  | 44981 | 1906 | 2008354 | 8502 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 263562 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034517 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1101 | 254421101 | FUSE |  | 44981 | 1906 | 2010159 | 4286 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 107150 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034517 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1101 | 254421101 | TRANSFORMER |  | 44981 | 1829 | 2010348 | 9996 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 9996 | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0035830 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | OAKHURST-1101 | 254421101 | FUSE |  | 44981 | 1906 | 2010367 | 5339 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 69407 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034517 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2102 | 254452102 | JUMPER |  | 44982 | 1802 | 2009083 | 1590 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 14310 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0035875 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1101 | 254421101 | JUMPER |  | 44981 | 1906 | 2009769 | 5311 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 63732 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034517 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 44981 | 1942 | 2014602 | 5414 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 617196 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034555 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | JUMPER |  | 44984 | 1731 | 2022840 | 8238 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 19788 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0040070 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 44985 | 1644 | 2018843 | 4546 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 72736 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037849 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE |  | 44981 | 1520 | 2005969 | 304 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 6080 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034447 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | SWITCH |  | 44985 | 2238 | 2018639 | 2609 | Distribution Circuit | Equipment Failure/Involved | Overhead | 548 | 1422532 | Overcast-Fog-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0037849 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | RECLOSER |  | 44981 | 1950 | 2006967 | 5365 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1324 | 5285932 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034555 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2101 | 252192101 | RECLOSER |  | 44982 | 513 | 2007661 | 4247 | Distribution Circuit | Equipment Failure/Involved | Overhead | 725 | 568423 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035035 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | JUMPER |  | 44981 | 1942 | 2010317 | 5638 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 16914 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0034555 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | RECLOSER |  | 44982 | 346 | 2007612 | 858 | Distribution Circuit | Equipment Failure/Involved | Overhead | 216 | 185328 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035032 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 44985 | 2238 | 2018113 | 3961 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 23766 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0037849 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 44985 | 2238 | 2018303 | 3679 | Distribution Circuit | Equipment Failure/Involved | Overhead | 48 | 176592 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037849 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | SWITCH |  | 44985 | 2238 | 2018103 | 2070 | Distribution Circuit | Vegetation | Tree - fell into line | 683 | 1169113 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037849 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2101 | 252192101 | RECLOSER |  | 44982 | 316 | 2007575 | 6519 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 231960 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035026 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 44985 | 2237 | 2018121 | 3901 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 19505 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037849 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | RECLOSER |  | 44984 | 848 | s1818911 | 168 | Distribution Circuit | 3rd Party | Vehicle | 387 | 65016 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034555 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | RECLOSER |  | 44981 | 1942 | 2006950 | 5628 | Distribution Circuit | Environmental/External | Ice or snow | 449 | 2105529 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0034552 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 44981 | 1808 | s1817991 | 4303 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 25818 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034555 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 44981 | 1652 | 2006303 | 5402 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 59422 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034555 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 44984 | 1814 | 2013520 | 1485 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 53460 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0036824 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | RECLOSER |  | 44981 | 1808 | 2006573 | 10106 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 535618 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0034464 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE |  | 44981 | 1942 | 2015030 | 8275 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 24825 | Overcast-Fog;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0034552 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 44985 | 2237 | 2021745 | 5365 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 96570 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037849 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 44985 | 1644 | 2021750 | 5747 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 68964 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037849 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER |  | 44985 | 1443 | 2015678 | 3202 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 121676 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037496 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | INDIAN FLAT-1104 | 252691104 | OCB |  | 44981 | 1941 | 2006899 | 2842 | Distribution Circuit | Equipment Failure/Involved | Overhead | 630 | 2377205 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0034539 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | OTHER |  | 44981 | 737 | 2004044 | 463 | Distribution Circuit | Equipment Failure/Involved | Overhead | 687 | 317435 | Overcast-Fog-Snow;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0033790 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 44985 | 1443 | 2022499 | 10115 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 10115 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0037496 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 44982 | 413 | 2007625 | 2144 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 150080 |  | Conductor- Overhead | Broken- wire on ground | 23-0035095 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | SWITCH |  | 44985 | 1443 | 2016422 | 8818 | Distribution Circuit | Vegetation | Tree - fell into line | 146 | 1168987 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037496 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 44982 | 733 | 2008745 | 2009 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 12054 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035095 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 44985 | 1443 | 2022392 | 7188 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 35940 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0037496 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER |  | 44985 | 1443 | 2020953 | 5849 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 157923 | Overcast-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0037496 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | BEAR VALLEY-2105 | 252192105 | SWITCH |  | 44985 | 1443 | 2025013 | 10312 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 226864 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037496 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 44982 | 107 | 2008877 | 3843 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 57645 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0035012 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 44985 | 1430 | 2023854 | 9998 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 189962 | Overcast-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0037496 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 44985 | 1443 | 2023862 | 11646 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 652176 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0037496 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 44982 | 606 | s1818259 | 3564 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 199584 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035095 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 44985 | 1618 | 2016161 | 10175 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 345950 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037891 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 44981 | 2046 | 2008804 | 2451 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 17157 | Overcast-Fog-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0035095 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | CURTIS-1703 | 163351703 | FUSE |  | 44985 | 1815 | 2021870 | 10136 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 222992 | Overcast-Snow;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0037873 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE |  | 44985 | 1552 | 2022244 | 9915 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 122037 | Overcast-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 23-0037566 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE |  | 44985 | 1601 | 2016113 | 6036 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 411938 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037873 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER |  | 44981 | 1952 | 2006940 | 2665 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3073 | 639314 | Clear;32-90 F | Insulator | Broken- wire on ground | 23-0034549 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | OCB |  | 44978 | 1557 | 1992869 | 346 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1921 | 539322 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031430 | OH | Sus | 0 | 2023 | FEB | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 44985 | 2236 | 2018838 | 2687 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 104793 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037846 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 44985 | 2236 | 2018704 | 6628 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 192212 | Overcast-Fog-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037846 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1704 | 163761704 | RECLOSER |  | 44978 | 1528 | 1992464 | 1427 | Distribution Circuit | Equipment Failure/Involved | Overhead | 367 | 111391 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0031358 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 44985 | 2236 | 2018458 | 6896 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 199984 | Overcast-Fog-Snow;Below 32 F | Connector or Splice (OH) | Broken- wire on ground | 23-0037846 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 44985 | 2321 | 2017251 | 5149 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 84519 | Overcast-Snow;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0037918 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | CURTIS-1705 | 163351705 | FUSE |  | 44985 | 1706 | 2016302 | 5851 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 263295 | Overcast-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 23-0039312 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 44985 | 1956 | 2017753 | 8317 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 320242 | Overcast-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038967 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE |  | 44985 | 712 | 2014844 | 410 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 15580 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037206 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | Yes
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44985 | 1608 | 2016355 | 4280 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 8560 | Overcast-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037588 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | FUSE |  | 44985 | 1608 | 2021356 | 5618 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 258428 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0037588 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | FUSE |  | 44985 | 1608 | 2021356 | 5618 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 258428 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0037588 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44985 | 1511 | 2020218 | 5749 | Distribution Circuit | Vegetation | Tree - fell into line | 479 | 15006 | Overcast-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037588 | OH | Sus | 0 | 2023 | FEB | Yes | None | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44985 | 1521 | 2021768 | 7389 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 118224 | Overcast-Snow-Strong Winds;Below 32 F | Pole-Wood | Broken- wire on ground | 23-0037536 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44985 | 1521 | 2021369 | 8616 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 439416 | Overcast-Snow-Strong Winds;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0037536 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44985 | 1521 | 2021979 | 5879 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 382135 | Overcast-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037536 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44984 | 802 | 2011317 | 717 | Distribution Circuit | Equipment Failure/Involved | Overhead | 54 | 38718 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0036222 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 44985 | 1059 | 2021702 | 7561 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 75610 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0039613 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44985 | 1605 | 2016067 | 5862 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 382629 | Overcast-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037564 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | CURTIS-1704 | 163351704 | FUSE |  | 44985 | 1958 | 2016682 | 5186 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 233370 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037895 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | SWITCH |  | 44985 | 1059 | 2022223 | 9125 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 118625 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0039613 | OH | Sus | 0 | 2023 | FEB | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | FUSE |  | 44985 | 2122 | 2020079 | 6941 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 111056 | Overcast-Snow;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0038699 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER |  | 44985 | 1059 | 2015488 | 5925 | Distribution Circuit | Vegetation | Tree - fell into line | 2890 | 1917990 | Overcast-Snow-Strong Winds;Below 32 F | Crossarm- Wood | Broken- wire on ground | 23-0037376 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER |  | 44985 | 1608 | 2015986 | 4259 | Distribution Circuit | Vegetation | Tree - fell into line | 1582 | 3250922 | Overcast-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0037588 | OH | Sus | 0 | 2023 | FEB | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | CURTIS-1704 | 163351704 | SWITCH |  | 44985 | 1136 | 2015047 | 19044 | Distribution Circuit | Environmental/External | Ice or snow | 15 | 104850 | Overcast-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0037287 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | Yes
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | OTHER |  | 44981 | 2109 | 2007445 | 225 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 11250 | Clear;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0035006 | OH | Sus | 0 | 2023 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | RECLOSER |  | 44930 | 1743 | 1916292 | 5658 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 537695 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006342 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | RECLOSER |  | 44933 | 901 | 1926203 | 29 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 870 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006449 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | RECLOSER |  | 44936 | 214 | 1940714 | 3804 | Distribution Circuit | Vegetation | Tree - fell into line | 410 | 1548832 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011771 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | RECLOSER |  | 44930 | 1855 | 1916351 | 2773 | Distribution Circuit | Equipment Failure/Involved | Overhead | 380 | 1053740 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006449 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | RECLOSER |  | 44933 | 2342 | 1929530 | 980 | Distribution Circuit | Equipment Failure/Involved | Overhead | 445 | 433859 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0009409 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | SWITCH |  | 44935 | 1705 | 1945362 | 2390 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 236610 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012531 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | RECLOSER |  | 44935 | 308 | 1935403 | 2602 | Distribution Circuit | Vegetation | Tree - branch fell on line | 223 | 525316 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0010734 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | SWITCH |  | 44935 | 239 | 1938921 | 3841 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 503171 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010734 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 44935 | 325 | 1935436 | 2305 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 57625 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011644 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 44936 | 1528 | 1945741 | 129 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 516 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012684 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 44933 | 2255 | 1928586 | 1341 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 53640 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009578 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 44940 | 1015 | 1953903 | 715 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 15088 | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0016178 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | RECLOSER |  | 44933 | 1416 | 1926812 | 1559 | Distribution Circuit | Equipment Failure/Involved | Overhead | 122 | 24967 | Clear;32-90F | Anchor or Guy | Broken- wire on ground | 23-0008834 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE |  | 44934 | 948 | 1932990 | 160 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 3200 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010081 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 44935 | 241 | 1937786 | 2504 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 10016 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011101 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 44930 | 1956 | 1917912 | 938 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 86296 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006806 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 44942 | 841 | 1957352 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1088 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017108 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | FUSE |  | 44935 | 337 | 1935465 | 1060 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 23320 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011010 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | FUSE |  | 44936 | 208 | 1940047 | 1462 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 138890 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011819 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | HATTON SUB | 18229 | OCB |  | 44940 | 836 | 1953363 | 930 | Distribution Circuit | Vegetation | Tree - fell into line | 505 | 136405 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0015922 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | OCB |  | 44930 | 2236 | 1919483 | 3152 | Distribution Circuit | Vegetation | Tree - fell into line | 505 | 126604 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006791 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 44935 | 2045 | 1939606 | 3951 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 51527 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012148 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 44942 | 353 | 1956749 | 678 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 25764 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016927 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 44935 | 216 | 1939766 | 2437 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 26807 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011688 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 44936 | 1103 | 1944688 | 3262 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 9786 | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0012695 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE |  | 44930 | 1507 | 1925532 | 4385 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 13155 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008544 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | JUMPER |  | 44930 | 1505 | 1922177 | 3096 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 15480 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006055 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | OTHER |  | 44935 | 1505 | 1938560 | 3097 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 37164 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011557 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE |  | 44934 | 7 | 1930410 | 1109 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 13308 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009789 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 44936 | 29 | 1945493 | 2323 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 104535 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012584 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 44942 | 342 | 1956737 | 551 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 11571 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0016911 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 44930 | 1413 | 1915460 | 2686 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 56406 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006230 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE |  | 44934 | 2 | 1930450 | 3561 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 106690 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009694 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | RECLOSER |  | 44930 | 1420 | 1914510 | 2869 | Distribution Circuit | Vegetation | Tree - fell into line | 1779 | 1149720 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006055 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | OCB |  | 44934 | 1914 | 1934547 | 2568 | Distribution Circuit | Vegetation | Tree - fell into line | 6157 | 746396 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010443 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | OCB |  | 44935 | 216 | 1935800 | 1244 | Distribution Circuit | Vegetation | Tree - fell into line | 1289 | 1601657 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010786 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | OCB |  | 44935 | 458 | 1935715 | 1193 | Distribution Circuit | Vegetation | Tree - fell into line | 2895 | 3439908 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010771 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 44934 | 1355 | 1933716 | 276 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 2760 | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0010256 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | RECLOSER |  | 44940 | 959 | 1953257 | 1018 | Distribution Circuit | Vegetation | Tree - fell into line | 310 | 150826 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0016032 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | RECLOSER |  | 44935 | 2343 | 1939812 | 3812 | Distribution Circuit | Vegetation | Tree - fell into line | 279 | 153912 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0011703 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE |  | 44934 | 106 | 1931497 | 816 | Distribution Circuit | Vegetation | Tree - branch fell on line | 144 | 99272 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009843 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE |  | 44931 | 230 | 1920381 | 1032 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 111456 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0007028 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE |  | 44931 | 1204 | 1922107 | 2732 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 24588 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007714 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | PANOCHE-1103 | 253671103 | RECLOSER |  | 44935 | 531 | 1935817 | 558 | Distribution Circuit | Vegetation | Tree - branch fell on line | 118 | 42833 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010788 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN JUSTO-1101 | 183181101 | FUSE |  | 44933 | 1558 | 1927189 | 1302 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 36456 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008924 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 44942 | 830 | 1957319 | 4845 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 18957 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017025 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | OTHER |  | 44940 | 1822 | 1955094 | 2776 | Distribution Circuit | Vegetation | Tree - fell into line | 3175 | 153499 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016386 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 44936 | 224 | 1940597 | 3723 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 174981 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0012770 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 44931 | 1241 | 1922232 | 1416 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 9912 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007678 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 44935 | 529 | 1935961 | 3720 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 126480 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010985 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 44935 | 920 | 1937240 | 1800 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 45000 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011037 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2105 | 83692105 | JUMPER |  | 44942 | 211 | 1956542 | 450 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 27288 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017031 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2105 | 83692105 | OTHER |  | 44936 | 1150 | 1944607 | 3105 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 73155 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012489 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER |  | 44935 | 535 | 1935839 | 7488 | Distribution Circuit | Vegetation | Tree - branch fell on line | 422 | 533549 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010790 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 44935 | 1156 | 1937988 | 205 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 3895 | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0011143 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER |  | 44942 | 239 | 1956574 | 2359 | Distribution Circuit | Vegetation | Tree - fell into line | 269 | 634571 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016877 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 44940 | 444 | 1952785 | 5179 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 134654 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015850 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 44942 | 538 | 1956873 | 682 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 682 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017064 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | 83500401 | 83500401 | RECLOSER |  | 44942 | 324 | 1956683 | 662 | Distribution Circuit | Vegetation | Tree - fell into line | 213 | 136302 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016893 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | PAUL SWEET-2102 | 83252102 | RECLOSER |  | 44936 | 711 | 1943213 | 5078 | Distribution Circuit | Vegetation | Tree - fell into line | 271 | 120833 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012129 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | 83500401 | 83500401 | RECLOSER |  | 44942 | 240 | 1956588 | 837 | Distribution Circuit | Vegetation | Tree - fell into line | 127 | 106299 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016880 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | 83500401 | 83500401 | RECLOSER |  | 44931 | 125 | 1920250 | 2211 | Distribution Circuit | Vegetation | Tree - fell into line | 127 | 280797 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0007060 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | OTHER |  | 44936 | 807 | 1943497 | 4997 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 109934 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012266 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | 83500401 | 83500401 | FUSE |  | 44936 | 217 | 1940331 | 6314 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 126280 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012067 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 44935 | 802 | 1936745 | 12068 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 325836 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011658 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 44930 | 1910 | 1917506 | 4069 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 245674 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0007062 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE |  | 44940 | 750 | 1953122 | 1947 | Distribution Circuit | Vegetation | Tree - fell into line | 164 | 270623 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015963 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2102 | 83252102 | FUSE |  | 44930 | 1757 | 1916486 | 1315 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 22355 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006581 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 44934 | 129 | 1931781 | 998 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 13972 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010216 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2102 | 83252102 | FUSE |  | 44930 | 1845 | 1917148 | 1111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2222 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006584 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2107 | 83252107 | FUSE |  | 44936 | 526 | 1945766 | 6511 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 117198 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012697 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2102 | 83252102 | FUSE |  | 44930 | 1321 | 1914040 | 1266 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 7596 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006037 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 44935 | 629 | 1936098 | 4789 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 244239 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010882 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 44935 | 1006 | 1937490 | 23257 | Distribution Circuit | Environmental/External | Flood/Erosion | 9 | 163005 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011450 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | SWITCH |  | 44935 | 655 | 1937797 | 4930 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 34510 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010822 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | SWITCH |  | 44935 | 655 | 1937916 | 6432 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 237984 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010822 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | SWITCH |  | 44940 | 1012 | 1954053 | 1860 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 197160 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0016045 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 44936 | 228 | 1946659 | 8151 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 48906 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013087 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE |  | 44940 | 750 | 1956111 | 4802 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 9604 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0016729 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44930 | 1221 | 1925515 | 4594 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 101068 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008543 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | RECLOSER |  | 44935 | 524 | 1935790 | 480 | Distribution Circuit | Vegetation | Tree - fell into line | 267 | 99296 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010785 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 44936 | 839 | 1943851 | 7969 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 39845 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012680 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | SWITCH |  | 44936 | 159 | 1945245 | 9472 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 56832 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012478 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER |  | 44936 | 1037 | 1947623 | 10401 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 23844 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013524 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | OTHER |  | 44936 | 158 | 1947512 | 3559 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 68260 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013489 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | OTHER |  | 44936 | 158 | 1947512 | 3559 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 68260 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013489 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44931 | 1435 | 1922791 | 327 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 6213 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007591 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44935 | 918 | 1937218 | 11949 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 238980 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011608 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44930 | 1308 | 1913964 | 1584 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 53856 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006089 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 44935 | 518 | 1945041 | 12189 | Distribution Circuit | Vegetation | Tree - fell into line | 351 | 4278339 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012395 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | RECLOSER |  | 44936 | 208 | 1940201 | 2724 | Distribution Circuit | Vegetation | Tree - fell into line | 989 | 489806 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011759 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44934 | 105 | 1931486 | 26842 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 678858 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009833 | OH | Sus | 35419572 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | JUMPER |  | 44940 | 858 | 1954046 | 1712 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 13696 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016085 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44930 | 1726 | 1920647 | 2504 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 38330 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006996 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44936 | 159 | 1944410 | 12103 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 447520 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012182 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44936 | 159 | 1943820 | 9507 | Distribution Circuit | Vegetation | Tree - fell into line | 236 | 970680 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012053 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44935 | 1136 | 1937893 | 3008 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 105280 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011190 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44936 | 158 | 1950538 | 5221 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 104420 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014679 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 44940 | 955 | 1953758 | 1502 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7510 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016565 | OH | Sus | 0 | 2023 | JAN | Yes |  | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44936 | 158 | 1950534 | 5261 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 568188 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014678 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44930 | 1221 | 1923462 | 4358 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4358 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007814 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44936 | 714 | 1943232 | 3557 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 345029 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012031 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44930 | 1258 | 1926461 | 5712 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 17136 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0008742 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44936 | 721 | 1943219 | 8079 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 341076 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012110 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44930 | 1531 | 1915066 | 1542 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 13878 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006274 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | SWITCH |  | 44936 | 202 | 1943868 | 531 | Distribution Circuit | Company Initiated | Return Circuit Normal | 172 | 91332 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011726 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44936 | 159 | 1944988 | 9521 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 390361 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012378 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44935 | 955 | 1945061 | 3126 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 12504 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012405 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 44942 | 518 | 1956858 | 769 | Distribution Circuit | Vegetation | Tree - fell into line | 416 | 88568 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016929 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 44931 | 1302 | 1922301 | 1411 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8466 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007572 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44936 | 718 | 1943255 | 4910 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 73650 | Overcast-Fog-Rain;32-90 F | Other | Broken- wire on ground | 23-0012062 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 44942 | 341 | 1956738 | 1948 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 100606 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016899 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44934 | 809 | 1933845 | 1058 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2116 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010242 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2106 | 83622106 | SWITCH |  | 44936 | 202 | 1942969 | 767 | Distribution Circuit | Vegetation | Tree - branch fell on line | 423 | 129242 | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0011726 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | JUMPER |  | 44930 | 1336 | 1926400 | 6491 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 6491 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008730 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | JUMPER |  | 44933 | 1625 | 1947477 | 11120 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 11120 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013480 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44933 | 1625 | 1947532 | 2571 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 41136 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013496 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER |  | 44930 | 2028 | 1918292 | 2406 | Distribution Circuit | Vegetation | Tree - fell into line | 232 | 106684 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007133 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 44935 | 455 | 1935709 | 2218 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 19258 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011321 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44936 | 1333 | 1945310 | 7297 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 39106 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012516 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44936 | 156 | 1949225 | 6629 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 79548 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0014218 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44936 | 1835 | 1946299 | 283 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 3396 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013079 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44936 | 646 | 1943753 | 5039 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 157744 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011724 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44936 | 1343 | 1945448 | 7202 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 122200 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012570 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2105 | 83622105 | OTHER |  | 44930 | 1308 | 1913960 | 1334 | Distribution Circuit | Vegetation | Tree - branch fell on line | 60 | 74357 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006178 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | JUMPER |  | 44930 | 1336 | 1926698 | 4494 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4494 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008810 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER |  | 44936 | 1835 | 1946722 | 8122 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 16244 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013191 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | SWITCH |  | 44930 | 1737 | 1923223 | 4326 | Distribution Circuit | Vegetation | Tree - fell into line | 241 | 1042566 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007722 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 44940 | 1304 | 1954846 | 4361 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 46098 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016335 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 44930 | 1125 | 1913501 | 1711 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 24193 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005865 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | JUMPER |  | 44930 | 1129 | 1927756 | 5791 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5791 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009025 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | TRIP-SAVER |  | 44936 | 156 | 1941448 | 4828 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 82076 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011848 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 44930 | 1134 | 1927272 | 4738 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 37904 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008944 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44936 | 159 | 1944700 | 10982 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 398734 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012248 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44930 | 1455 | 1916037 | 1749 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 86319 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007209 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 44935 | 425 | 1935618 | 12289 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 1419693 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011171 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 44930 | 1738 | 1916283 | 4123 | Distribution Circuit | Vegetation | Tree - branch fell on line | 174 | 530594 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007122 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44936 | 158 | 1949956 | 5136 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 66768 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0014434 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44936 | 1745 | 1946198 | 2900 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 118900 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012890 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44936 | 808 | 1943593 | 4958 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 257816 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012038 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44936 | 158 | 1950853 | 6497 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 25988 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014776 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44930 | 1141 | 1921977 | 6532 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 19596 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007340 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44936 | 159 | 1946053 | 5288 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 142776 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012838 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | JUMPER |  | 44930 | 1129 | 1922060 | 4692 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 9384 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0007361 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER |  | 44936 | 159 | 1945703 | 9345 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 127588 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012665 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44936 | 156 | 1949958 | 7854 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7854 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0014435 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44931 | 110 | 1920160 | 2261 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 56525 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006992 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44936 | 1624 | 1945896 | 5695 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 153765 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012810 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 44935 | 518 | 1935780 | 435 | Distribution Circuit | Environmental/External | Flood/Erosion | 257 | 111795 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0010784 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | SWITCH |  | 44936 | 646 | 1943435 | 4916 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 835720 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011724 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | SWITCH |  | 44940 | 620 | 1953249 | 2161 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 210733 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016006 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 44936 | 646 | 1943387 | 241 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 4579 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011724 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | SWITCH |  | 44930 | 1141 | 1922474 | 4183 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 150588 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007489 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 44936 | 159 | 1949844 | 8031 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 240930 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0014383 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44936 | 1058 | 1946919 | 9017 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 81153 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013357 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | RECLOSER |  | 44930 | 1233 | 1926272 | 4628 | Distribution Circuit | Vegetation | Tree - fell into line | 126 | 583128 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008558 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44936 | 646 | 1944545 | 12174 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 12174 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012204 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44930 | 1258 | 1926875 | 6675 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 220275 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008850 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | SWITCH |  | 44936 | 159 | 1944975 | 3480 | Distribution Circuit | Vegetation | Tree - fell into line | 936 | 1076838 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011724 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER |  | 44935 | 518 | 1935806 | 570 | Distribution Circuit | Environmental/External | Flood/Erosion | 9 | 5130 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010784 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER |  | 44936 | 159 | 1950552 | 8031 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 16062 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014686 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 44940 | 1030 | 1953971 | 1520 | Distribution Circuit | Vegetation | Tree - branch fell on line | 96 | 9770 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016120 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44936 | 1134 | 1944827 | 4741 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 191259 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012430 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | OTHER |  | 44940 | 835 | 1953646 | 1645 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 116460 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015994 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 44942 | 712 | 1957162 | 1988 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 7276 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017012 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 44936 | 646 | 1944591 | 273 | Distribution Circuit | Vegetation | Tree - fell into line | 220 | 60060 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011724 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER |  | 44936 | 159 | 1949644 | 9411 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 103521 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0014312 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | JUMPER |  | 44936 | 159 | 1950269 | 7858 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 110012 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014585 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | SWITCH |  | 44936 | 159 | 1947950 | 3582 | Distribution Circuit | Vegetation | Tree - fell into line | 144 | 515808 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011734 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER |  | 44936 | 1134 | 1952592 | 6116 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 18348 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012430 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 44935 | 511 | 1936570 | 6455 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 606770 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011104 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 44930 | 1233 | 1923005 | 4317 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 263337 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007660 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER |  | 44936 | 646 | 1949593 | 7827 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 931413 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0014310 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER |  | 44936 | 159 | 1947947 | 5222 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 125328 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011734 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 44930 | 1707 | 1915976 | 5342 | Distribution Circuit | Vegetation | Tree - fell into line | 1809 | 4984930 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006310 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | SWITCH |  | 44930 | 1211 | 1926627 | 5826 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 332082 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008788 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44935 | 543 | 1935875 | 10491 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 167856 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011357 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | OCB |  | 44936 | 202 | 1940042 | 2144 | Distribution Circuit | Vegetation | Tree - bark fell into line | 163 | 219589 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011734 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | OCB |  | 44930 | 1233 | 1913795 | 6053 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1740 | 1523651 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005914 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 44930 | 1707 | 1925478 | 4158 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 49896 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008529 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | RECLOSER |  | 44930 | 1134 | 1916624 | 5875 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 505250 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006380 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | RECLOSER |  | 44935 | 234 | 1935326 | 3350 | Distribution Circuit | Vegetation | Tree - fell into line | 582 | 261930 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010723 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | JUMPER |  | 44930 | 1720 | 1933200 | 5582 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 686586 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005914 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | JUMPER |  | 44935 | 519 | 1938059 | 543 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 43440 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010782 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 44930 | 1737 | 1922860 | 4208 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 50496 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007605 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | OTHER |  | 44934 | 1338 | 1933738 | 6007 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 30035 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0010199 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | JUMPER |  | 44930 | 1417 | 1933118 | 5709 | Distribution Circuit | Vegetation | Tree - fell into line | 357 | 2038113 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005914 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44940 | 900 | 1953507 | 3375 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 13500 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016175 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44930 | 1303 | 1922129 | 4194 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 79686 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007384 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44942 | 215 | 1956543 | 1988 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 37772 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017073 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER |  | 44935 | 511 | 1957816 | 12404 | Distribution Circuit | Vegetation | Tree - fell into line | 140 | 1736560 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011724 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 44940 | 906 | 1953560 | 2009 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 54243 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016107 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 44935 | 519 | 1938398 | 6444 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 244872 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010782 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 44935 | 540 | 1935872 | 668 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1336 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011431 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44930 | 1740 | 1916233 | 2385 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 66491 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007447 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44935 | 625 | 1957913 | 12330 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 1380960 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017162 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44935 | 511 | 1950955 | 12404 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 99232 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0014805 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44942 | 250 | 1956601 | 655 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 44540 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017049 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44936 | 650 | 1946548 | 7764 | Distribution Circuit | Vegetation | Tree - branch fell on line | 68 | 527952 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013487 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER |  | 44935 | 617 | 1950950 | 13454 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 100324 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014801 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 44930 | 1233 | 1932874 | 5813 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 93008 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008936 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | SWITCH |  | 44936 | 159 | 1952017 | 9224 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 534992 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011734 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER |  | 44936 | 1028 | 1944488 | 23466 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 117330 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012518 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | JUMPER |  | 44930 | 1704 | 1927215 | 5542 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 44336 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008936 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 44940 | 1337 | 1954456 | 2787 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 20519 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016271 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 44930 | 1233 | 1932974 | 5857 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 99569 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0009966 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | RECLOSER |  | 44936 | 159 | 1947684 | 3994 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 91862 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011734 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 44935 | 540 | 1956171 | 11948 | Distribution Circuit | Vegetation | Tree - branch fell on line | 44 | 525712 | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0011724 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 44936 | 159 | 1948281 | 3994 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 123814 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013751 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44935 | 511 | 1951770 | 12404 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 248080 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0015237 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | SWITCH |  | 44930 | 1233 | 1926157 | 6157 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 258594 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008542 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44930 | 1239 | 1926487 | 5584 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 39088 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008754 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 44930 | 1233 | 1924000 | 6159 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 843783 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008027 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44935 | 540 | 1950604 | 10825 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 248975 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014706 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER |  | 44935 | 806 | 1938106 | 24809 | Distribution Circuit | Environmental/External | Flood/Erosion | 13 | 113658 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012123 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER |  | 44930 | 2127 | 1921758 | 2339 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 37660 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007271 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER |  | 44936 | 206 | 1945894 | 10954 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 56587 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012783 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | RECLOSER |  | 44934 | 1943 | 1935054 | 312 | Distribution Circuit | Vegetation | Tree - fell into line | 3252 | 226286 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0010666 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44930 | 1241 | 1926561 | 5986 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 83804 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008784 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44935 | 540 | 1959608 | 12295 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 393440 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017656 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 44930 | 1336 | 1924386 | 4359 | Distribution Circuit | Vegetation | Tree - fell into line | 500 | 2175608 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008135 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 44930 | 1301 | 1913924 | 5859 | Distribution Circuit | Vegetation | Tree - fell into line | 509 | 292611 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005954 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 44936 | 202 | 1940003 | 8030 | Distribution Circuit | Vegetation | Tree - fell into line | 521 | 2979064 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011730 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44936 | 207 | s1802002 | 6690 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 207390 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011730 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44936 | 206 | 1945911 | 6721 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 33605 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012795 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44933 | 1249 | 1926605 | 282 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 9306 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008847 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | OCB |  | 44930 | 1300 | 1913974 | 6269 | Distribution Circuit | Vegetation | Tree - fell into line | 2045 | 7153968 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005964 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44931 | 1444 | 1923028 | 11707 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 398038 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0007666 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44936 | 212 | 1945134 | 6469 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 19407 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012417 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER |  | 44931 | 1334 | 1922496 | 4386 | Distribution Circuit | Vegetation | Tree - fell into line | 200 | 872760 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007498 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44930 | 1227 | 1924587 | 5640 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 101520 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008191 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44935 | 152 | 1936781 | 5239 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 106200 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011449 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 44930 | 1229 | 1924948 | 4543 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 31369 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005964 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | JUMPER |  | 44940 | 726 | 1953003 | 491 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 982 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016079 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44934 | 1556 | 1935241 | 8641 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 328358 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011641 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44940 | 939 | 1953707 | 1725 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 140162 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016127 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER |  | 44930 | 1526 | 1925227 | 4249 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 307135 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008465 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44936 | 211 | 1944880 | 6326 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 272018 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006011 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 44930 | 1336 | 1926746 | 12860 | Distribution Circuit | Vegetation | Tree - fell into line | 179 | 2301940 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006011 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER |  | 44942 | 257 | 1956868 | 2160 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 85517 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016935 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44930 | 1124 | 1933098 | 5773 | Distribution Circuit | Vegetation | Tree - fell into line | 139 | 802447 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010012 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44936 | 202 | 1948947 | 8030 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 48180 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013944 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44933 | 1840 | 1927645 | 6904 | Distribution Circuit | Vegetation | Tree - branch fell on line | 74 | 173534 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010243 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44930 | 1026 | 1913389 | 6105 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 153665 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005900 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44940 | 715 | 1952997 | 1958 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 12852 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0016081 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER |  | 44930 | 1240 | 1951698 | 13289 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 146179 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0015201 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER |  | 44930 | 1229 | 1925103 | 11801 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 70806 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008406 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 44930 | 1229 | 1926798 | 11751 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 305526 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005964 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | TRIP-SAVER |  | 44933 | 1728 | 1927316 | 9902 | Distribution Circuit | Environmental/External | Flood/Erosion | 12 | 118824 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0010093 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44930 | 1304 | 1925183 | 14535 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 87210 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008440 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44930 | 1304 | 1924908 | 11716 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 11716 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008337 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44930 | 1229 | 1925115 | 6054 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 18162 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008415 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44930 | 1229 | 1933627 | 11970 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 598500 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010163 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44935 | 844 | 1937044 | 4600 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 202400 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011098 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44930 | 727 | 1912442 | 12153 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 24931 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005656 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER |  | 44930 | 1229 | 1933622 | 11750 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 35250 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010160 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | TRIP-SAVER |  | 44930 | 1229 | 1933618 | 6066 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 133452 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010156 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44930 | 1303 | 1924724 | 5935 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 207725 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008243 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44930 | 1229 | 1925493 | 5859 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 76167 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008534 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44930 | 1304 | 1925497 | 5857 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 17571 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008535 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44940 | 1105 | 1954076 | 1678 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 20136 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016599 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44940 | 553 | 1953378 | 1977 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 27678 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016316 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | JUMPER |  | 44942 | 241 | 1957578 | 2372 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2372 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017103 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | JUMPER |  | 44930 | 1113 | 1924673 | 3416 | Distribution Circuit | Equipment Failure/Involved | Overhead | 130 | 444080 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008221 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER |  | 44940 | 958 | 1953801 | 1366 | Distribution Circuit | Equipment Failure/Involved | Overhead | 869 | 996760 | Clear;32-90F | Conductor- Overhead | On Ground | 23-0016069 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44930 | 1128 | 1919481 | 1406 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 33744 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006790 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER |  | 44936 | 208 | 1949245 | 3707 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 29640 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0014223 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 44942 | 229 | 1956566 | 976 | Distribution Circuit | Vegetation | Tree - fell into line | 338 | 76656 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016872 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44931 | 1529 | 1922957 | 1778 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 30226 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008021 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER |  | 44936 | 155 | 1949151 | 4374 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8748 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014121 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44936 | 155 | 1949150 | 6886 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 34430 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0014116 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44936 | 155 | 1949148 | 4986 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 64818 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014113 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER |  | 44936 | 206 | 1945906 | 5308 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 47772 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012792 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER |  | 44936 | 207 | 1948367 | 7963 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 95544 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0013769 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER |  | 44940 | 958 | 1954289 | 1226 | Distribution Circuit | Equipment Failure/Involved | Overhead | 202 | 47411 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016164 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH |  | 44936 | 208 | 1949273 | 5602 | Distribution Circuit | Equipment Failure/Involved | Overhead | 367 | 1771220 | Clear;32-90 F | Other | Broken- wire on ground | 23-0014230 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44940 | 1125 | 1954138 | 1910 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5730 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0016630 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH |  | 44936 | 208 | 1949272 | 3472 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 322896 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014227 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44936 | 208 | 1949745 | 5132 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 170751 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014346 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER |  | 44936 | 155 | 1948252 | 5390 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 16170 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0013745 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44936 | 203 | 1952377 | 7977 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 168345 | Clear;32-90F | Pole-Wood | Broken- wire on object | 23-0015502 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44936 | 211 | 1949258 | 6487 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 220558 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0014224 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44931 | 444 | 1924107 | 5019 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 147940 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0008068 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER |  | 44936 | 203 | 1952387 | 9846 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 19692 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015503 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44936 | 203 | 1952392 | 9846 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 9846 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0015505 | OH | Sus | 35419595 | 2023 | JAN | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 44930 | 1746 | 1916308 | 4418 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 229736 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006344 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44940 | 921 | 1955772 | 3353 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 30177 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016605 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 44936 | 208 | 1944872 | 2001 | Distribution Circuit | Vegetation | Tree - branch fell on line | 223 | 412730 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012318 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 44940 | 1126 | 1953856 | 3228 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 177540 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016113 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 44936 | 205 | 1945147 | 10929 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 860439 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012429 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
DE ANZA | Tier 2 | LOS GATOS-1106 | 82021106 | FUSE |  | 44936 | 210 | 1945296 | 5496 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 208560 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012507 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | STELLING-1110 | 83481110 | FUSE |  | 44930 | 2131 | 1925191 | 6751 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 77012 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008443 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
DE ANZA | Tier 3 | STELLING-1110 | 83481110 | JUMPER |  | 44930 | 2131 | 1925368 | 2829 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5658 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008499 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
DE ANZA | Tier 3 | STELLING-1110 | 83481110 | FUSE |  | 44942 | 743 | 1957232 | 1871 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 13097 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017297 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | LOS GATOS-1107 | 82021107 | FUSE |  | 44936 | 212 | 1944904 | 4086 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 53118 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012329 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | LOS GATOS-1107 | 82021107 | FUSE |  | 44936 | 212 | 1946645 | 6517 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 421020 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0013058 | OH | Sus | 35419593 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
DE ANZA | Tier 2 | LOS GATOS-1107 | 82021107 | FUSE |  | 44936 | 212 | 1945197 | 4007 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 432756 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012452 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
DE ANZA | Tier 3 | STELLING-1110 | 83481110 | FUSE |  | 44930 | 2131 | 1924582 | 2596 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 12980 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006688 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | LOS GATOS-1108 | 82021108 | OTHER |  | 44936 | 211 | 1946398 | 2554 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 33202 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012959 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | Yes
DE ANZA | Tier 2 | HICKS-1116 | 83431116 | FUSE |  | 44930 | 1637 | 1915371 | 1289 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 60583 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006533 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | SARATOGA-1105 | 83371105 | FUSE |  | 44942 | 639 | 1957030 | 641 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1986 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017111 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
DE ANZA | Tier 2 | SARATOGA-1106 | 83371106 | RECLOSER |  | 44936 | 236 | 1940930 | 7904 | Distribution Circuit | Vegetation | Tree - branch fell on line | 578 | 963079 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0013028 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | SARATOGA-1105 | 83371105 | OTHER |  | 44931 | 405 | 1920563 | 2167 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 76439 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006975 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | FUSE |  | 44930 | 2103 | 1918616 | 2941 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 73525 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008041 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE |  | 44930 | 1425 | 1914467 | 3128 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 34712 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006466 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | JUMPER |  | 44940 | 928 | 1954862 | 3137 | Distribution Circuit | Equipment Failure/Involved | Overhead | 506 | 102953 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016340 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | OTHER |  | 44935 | 935 | 1939535 | 1939 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 28133 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011505 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 3 | STELLING-1110 | 83481110 | RECLOSER |  | 44930 | 2133 | 1918881 | 2486 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 616298 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006688 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | STELLING-1110 | 83481110 | FUSE |  | 44942 | 250 | 1957333 | 800 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3200 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017028 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
DE ANZA | Tier 2 | STELLING-1109 | 83481109 | FUSE |  | 44930 | 1752 | 1919727 | 5723 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 11446 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006368 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | LOYOLA-1102 | 82161102 | RECLOSER |  | 44935 | 457 | 1935712 | 822 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 41383 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0010847 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
DIABLO | Tier 2 | SOBRANTE-1103 | 14671103 | FUSE |  | 44936 | 225 | 1944248 | 1296 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 103680 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012141 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | SOBRANTE-1102 | 14671102 | FUSE |  | 44936 | 230 | 1940798 | 1067 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 75757 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012606 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE |  | 44930 | 1935 | 1917771 | 3111 | Distribution Circuit | Vegetation | Tree - fell into line | 226 | 503656 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006580 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1102 | 12101102 | FUSE |  | 44930 | 1839 | 1917020 | 2739 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 51343 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006729 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAK-0401 | 12600401 | OCB |  | 44930 | 1831 | 1916929 | 1528 | Distribution Circuit | Vegetation | Tree - fell into line | 790 | 760322 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006435 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | FRANKLIN-1104 | 13921104 | RECLOSER |  | 44930 | 1736 | 1916193 | 4010 | Distribution Circuit | Equipment Failure/Involved | Overhead | 86 | 193215 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006333 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | SAND CREEK-1103 | 254601103 | OCB |  | 44936 | 623 | 1941643 | 1205 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1688 | 472210 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011946 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | FUSE |  | 44942 | 1118 | 1958459 | 2932 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5864 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017285 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER |  | 44942 | 649 | 1957100 | 2112 | Distribution Circuit | Vegetation | Tree - fell into line | 544 | 828818 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0016972 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | OTHER |  | 44935 | 1834 | 1939300 | 1117 | Distribution Circuit | Equipment Failure/Involved | Overhead | 280 | 299395 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011558 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
FRESNO | Tier 2 | AUBERRY-1102 | 254151102 | OTHER |  | 44942 | 708 | 1957161 | 664 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 3016 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0017068 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
FRESNO | Tier 2 | AUBERRY-1101 | 254151101 | RECLOSER |  | 44935 | 755 | 1936604 | 754 | Distribution Circuit | Vegetation | Tree - fell into line | 418 | 255427 | Overcast-Fog-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0010866 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 44930 | 1055 | 1926488 | 11915 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 35745 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008755 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | OCB |  | 44930 | 1055 | 1913406 | 11974 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 1180834 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005801 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 44930 | 932 | 1947530 | 11809 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 259798 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013494 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 44936 | 1217 | 1945398 | 3210 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6420 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012547 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44930 | 932 | 1949712 | 14594 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 58376 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0014370 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE |  | 44930 | 2137 | 1918953 | 1268 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 22824 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0007189 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | RECLOSER |  | 44942 | 805 | 1957295 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 61712 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017014 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 44940 | 1718 | 1954859 | 1270 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 19050 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016362 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 44930 | 1055 | 1948822 | 11835 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 106515 | Overcast-Drizzle-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0013909 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 44935 | 805 | 1936737 | 5914 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 35484 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010877 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44934 | 811 | 1933978 | 3201 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 89628 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010278 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44934 | 811 | 1933978 | 3201 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 89628 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010278 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44930 | 1122 | 1925556 | 3393 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 23751 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008554 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | JUMPER |  | 44930 | 932 | 1948483 | 14528 | Distribution Circuit | 3rd Party | Vehicle | 8 | 116224 | Heavy Rain-Strong Winds-Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0013817 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 44930 | 551 | 1912284 | 12215 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 85505 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005565 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 44930 | 932 | 1927290 | 11994 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 251874 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008947 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44934 | 1739 | 1934299 | 8288 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 140896 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010951 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | RECLOSER |  | 44930 | 829 | 1913057 | 10666 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 874612 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005613 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44934 | 1615 | 1934057 | 5897 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 141528 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013689 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44930 | 828 | 1914803 | 12017 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 24034 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006126 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44930 | 850 | 1927110 | 14977 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 254609 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008897 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44930 | 924 | 1923359 | 12074 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 205258 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007773 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44942 | 1526 | 1958442 | 217 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 3689 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017317 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE |  | 44930 | 1747 | 1921187 | 2929 | Distribution Circuit | Vegetation | Tree - fell into line | 117 | 162186 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007080 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE |  | 44936 | 341 | 1941352 | 2271 | Distribution Circuit | Vegetation | Tree - fell into line | 1123 | 488033 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011844 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44930 | 824 | 1927199 | 14860 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 133740 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008928 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 44930 | 932 | 1932962 | 10150 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 182700 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010003 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44930 | 828 | 1934102 | 14814 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 103698 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010331 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44930 | 833 | 1934110 | 14729 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 206206 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010332 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44930 | 836 | 1923337 | 14746 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 339158 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007761 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | RECLOSER |  | 44930 | 1923 | 1917619 | 2761 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1034 | 1101216 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0006481 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44930 | 824 | 1934144 | 14794 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 88764 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010342 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44930 | 824 | 1934155 | 12269 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 61345 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010344 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44930 | 824 | 1926879 | 14559 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 58236 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008853 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44930 | 824 | 1926885 | 12107 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 12107 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008855 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44930 | 844 | 1926828 | 12141 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 84987 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008841 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44930 | 824 | 1926887 | 12161 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 72966 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008856 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44930 | 828 | 1926874 | 12190 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 85330 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008849 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44930 | 824 | 1933065 | 12160 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 85120 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010001 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44930 | 805 | 1913846 | 12147 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 364410 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005924 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44930 | 824 | 1933473 | 12158 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 60790 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010115 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44930 | 824 | 1933915 | 12175 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 73050 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010258 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 44930 | 1055 | 1946007 | 14537 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 87222 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012823 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GARCIA-0401 | 43040401 | RECLOSER |  | 44930 | 1019 | 1913205 | 19116 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 172044 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0005744 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 44930 | 1314 | 1939278 | 11689 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 58445 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011523 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 44930 | 1055 | 1944971 | 14452 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 72260 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012367 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 44930 | 1055 | 1938783 | 13260 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 251940 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011417 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | OTHER |  | 44933 | 1910 | 1927784 | 940 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2820 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009140 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | FUSE |  | 44930 | 2013 | 1922588 | 4064 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 12192 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007529 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 44930 | 1112 | 1923149 | 16206 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 48618 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007696 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 44930 | 2040 | 1933484 | 12771 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 178794 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0010118 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 44930 | 1252 | 1924203 | 7439 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7439 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008090 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 44930 | 1344 | 1934306 | 7326 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 29304 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010385 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 44930 | 933 | 1923135 | 4788 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 38304 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007689 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | KONOCTI-1102 | 43311102 | RECLOSER |  | 44930 | 2051 | 1918517 | 1225 | Distribution Circuit | Equipment Failure/Involved | Overhead | 508 | 621752 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006597 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | Yes
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | TRIP-SAVER |  | 44930 | 440 | 1939095 | 13432 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 366583 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011489 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 44930 | 440 | 1939085 | 12155 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 158015 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011486 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | HOPLAND-1101 | 42251101 | FUSE |  | 44930 | 635 | 1912352 | 3628 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 103366 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0005587 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LUCERNE-1106 | 43351106 | FUSE |  | 44936 | 1110 | 1944767 | 282 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 1128 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012389 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE |  | 44936 | 533 | 1943137 | 790 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 31366 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012160 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE |  | 44933 | 2145 | 1928452 | 2548 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 95890 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010063 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 44930 | 1349 | 1924209 | 8828 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 79452 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0008091 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | FUSE |  | 44935 | 444 | 1935674 | 1938 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 83147 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011196 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | FUSE |  | 44930 | 1811 | 1916694 | 1344 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 52998 | Partly Cloudy-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006691 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | OTHER |  | 44933 | 2035 | 1928012 | 1175 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 114415 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0009202 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | RECLOSER |  | 44940 | 842 | 1953415 | 11 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 836 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015950 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | RECLOSER |  | 44935 | 8 | 1935042 | 2132 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 113587 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010659 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | FUSE |  | 44930 | 1559 | 1915006 | 4505 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 114428 | Partly Cloudy-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006649 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | FUSE |  | 44940 | 903 | 1953566 | 288 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2299 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015973 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | UKIAH-1114 | 42771114 | FUSE |  | 44933 | 1327 | 1926695 | 1599 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 15990 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010004 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | UKIAH-1113 | 42771113 | JUMPER |  | 44930 | 1340 | 1915039 | 3210 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 54570 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006176 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LUCERNE-1103 | 43351103 | FUSE |  | 44930 | 738 | 1913434 | 3459 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 124524 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0005793 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER |  | 44940 | 637 | 1952832 | 447 | Distribution Circuit | Vegetation | Tree - branch fell on line | 96 | 20272 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015849 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 44930 | 1351 | 1946021 | 8844 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 26532 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012827 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 44930 | 636 | 1912950 | 7998 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 591852 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005671 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | TRANSFORMER |  | 44934 | 1819 | 1934379 | 2486 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 2486 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011363 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 44930 | 731 | 1912472 | 4553 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 40977 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005863 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 44930 | 759 | 1913784 | 4865 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 63245 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0005911 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER |  | 44930 | 627 | 1912388 | 8858 | Distribution Circuit | Vegetation | Tree - fell into line | 1175 | 4805938 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0005557 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | SWITCH |  | 44930 | 759 | 1913373 | 4705 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 98805 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005779 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 44933 | 2014 | 1927988 | 2669 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 13345 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009249 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | JUMPER |  | 44930 | 1338 | 1924707 | 8252 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 8252 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008235 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | SWITCH |  | 44930 | 1344 | 1924726 | 4453 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 164761 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008249 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | CALPELLA-1101 | 43411101 | RECLOSER |  | 44930 | 631 | 1912349 | 5182 | Distribution Circuit | Vegetation | Tree - fell into line | 390 | 173125 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0005533 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 44930 | 2021 | 1918507 | 2236 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 315276 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007056 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 44930 | 950 | 1913065 | 3315 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 9945 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008485 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | OTHER |  | 44930 | 1735 | 1916164 | 6938 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 61987 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006433 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 44935 | 359 | 1935576 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 23230 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010804 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER |  | 44940 | 949 | 1953753 | 584 | Distribution Circuit | Vegetation | Tree - fell into line | 126 | 73584 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0016021 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 44936 | 748 | 1943475 | 606 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 10908 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012134 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER |  | 44930 | 1103 | 1913405 | 1836 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 20376 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006214 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 44930 | 1825 | 1921649 | 2670 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 104130 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007232 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 44940 | 650 | 1952957 | 357 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 22134 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015919 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 44930 | 1056 | 1922332 | 3121 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 137324 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007471 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | JUMPER |  | 44931 | 2056 | 1923878 | 2285 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 13514 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008016 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | Yes
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 44930 | 1533 | 1915864 | 2912 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 120679 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006300 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | MENDOCINO-1101 | 42951101 | RECLOSER |  | 44940 | 659 | 1952917 | 352 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 14204 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015859 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | MENDOCINO-1101 | 42951101 | RECLOSER |  | 44930 | 1140 | 1913604 | 4713 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 27967 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005861 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 44930 | 1029 | 1914426 | 1643 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 21359 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006043 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | TRIP-SAVER |  | 44930 | 1840 | 1917401 | 3823 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 171010 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007365 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | JUMPER |  | 44940 | 654 | 1953656 | 680 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1770 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015998 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | OTHER |  | 44931 | 1200 | 1922094 | 1323 | Distribution Circuit | Vegetation | Tree - fell into line | 535 | 96075 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007465 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER |  | 44940 | 709 | 1952931 | 529 | Distribution Circuit | Equipment Failure/Involved | Overhead | 652 | 191492 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015868 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1104 | 42661104 | FUSE |  | 44931 | 1550 | 1923111 | 1137 | Distribution Circuit | Vegetation | Tree - fell into line | 147 | 167139 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0008081 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | TRIP-SAVER |  | 44930 | 933 | 1914456 | 1550 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 85250 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006046 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 44930 | 1857 | 1917436 | 3990 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 10384 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007652 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 44930 | 1920 | 1917577 | 3918 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 46836 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007510 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 44936 | 56 | 1939843 | 1000 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 32000 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012104 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 44930 | 2307 | 1919657 | 764 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 26740 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007311 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 44933 | 635 | 1927523 | 4941 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 167994 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008994 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 44936 | 727 | 1943298 | 1972 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 20572 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012137 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER |  | 44933 | 1603 | 1927136 | 1563 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 120351 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008942 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 44930 | 1554 | 1914970 | 2537 | Distribution Circuit | Vegetation | Tree - fell into line | 145 | 154723 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007118 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 44930 | 1016 | 1926303 | 6117 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 103989 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008718 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 44931 | 29 | 1920048 | 2342 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 44498 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007890 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 44930 | 1601 | 1914636 | 1347 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 20205 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007412 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 44930 | 758 | 1912900 | 1922 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 46128 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005654 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | JUMPER |  | 44933 | 2253 | 1933069 | 1177 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1177 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010002 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER |  | 44930 | 1318 | 1914060 | 1895 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 193555 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005977 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 44930 | 1828 | 1917066 | 2850 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 17100 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007892 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 44930 | 1111 | 1913452 | 4560 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 18240 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005934 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 44930 | 823 | 1913458 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 7504 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005797 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 44930 | 754 | 1913135 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 586 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005723 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER |  | 44936 | 252 | 1941088 | 2051 | Distribution Circuit | Vegetation | Tree - fell into line | 153 | 96065 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011815 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER |  | 44930 | 1707 | 1915712 | 2611 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 80837 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006287 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | FUSE |  | 44930 | 520 | 1912375 | 4680 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 18720 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005528 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | JUMPER |  | 44935 | 815 | 1937153 | 540 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1080 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010931 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 44930 | 1751 | 1916391 | 4286 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 8549 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007756 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 44930 | 635 | 1912357 | 398 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 21492 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005593 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44935 | 1238 | 1937492 | 261 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1566 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011200 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 44940 | 810 | 1953177 | 662 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6620 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016075 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 44935 | 1327 | 1938302 | 1579 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1945 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0011398 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 44930 | 938 | 1914883 | 11689 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 23378 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006138 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE |  | 44936 | 1552 | 1945807 | 1275 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 33150 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012907 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 44930 | 1156 | 1923411 | 5932 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 17796 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007796 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 44930 | 844 | 1922002 | 6106 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 48848 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006134 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 44930 | 926 | 1925066 | 6082 | Distribution Circuit | Unknown Cause | Patrol - found nothing | 12 | 72984 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008393 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 44930 | 651 | 1922490 | 9269 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 148304 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0007494 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 44931 | 1350 | 1922558 | 5909 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 177270 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007516 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 44930 | 811 | 1913293 | 6474 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 16372 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005757 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 44931 | 1115 | 1921911 | 10260 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 30780 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0013603 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 44930 | 1143 | 1914946 | 4802 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4802 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006160 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 44933 | 2133 | 1932280 | 1169 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 17535 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010020 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 44930 | 1143 | 1921806 | 8692 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 52152 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007294 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 44940 | 946 | 1954704 | 1574 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 50368 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016306 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER |  | 44930 | 1005 | 1913157 | 10299 | Distribution Circuit | Vegetation | Tree - fell into line | 806 | 4218192 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0005734 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 44933 | 1952 | 1927944 | 1156 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5780 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010114 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | JUMPER |  | 44933 | 1037 | 1926384 | 441 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 882 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008775 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | JUMPER |  | 44940 | 655 | 1952901 | 197 | Distribution Circuit | Vegetation | Tree - fell into line | 1109 | 89069 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015863 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | JUMPER |  | 44940 | 1440 | 1954829 | 1430 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 14273 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016331 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 44930 | 2109 | 1925504 | 9794 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 39176 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0008538 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | JUMPER |  | 44934 | 939 | 1932964 | 4536 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 18144 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012870 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 44936 | 1329 | 1945255 | 1269 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 17766 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012504 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 44935 | 953 | 1939708 | 6172 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 61720 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011657 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 44930 | 559 | 1924637 | 13619 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 40543 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008290 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 44930 | 559 | 1924837 | 6731 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 40386 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008307 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1122 | 192321122 | FUSE |  | 44934 | 836 | 1932737 | 6335 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 38010 | Heavy Rain-Strong Winds-Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013855 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1122 | 192321122 | OTHER |  | 44940 | 727 | 1954161 | 767 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1311 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016123 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 44930 | 1005 | 1923507 | 10161 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 182898 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0007825 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 44930 | 1404 | 1933674 | 10246 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 10246 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010182 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1122 | 192321122 | FUSE |  | 44935 | 616 | 1936038 | 4968 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 59616 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013958 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | OTHER |  | 44940 | 633 | 1952847 | 557 | Distribution Circuit | Vegetation | Tree - fell into line | 1146 | 336874 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015853 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER |  | 44930 | 559 | 1912304 | 6851 | Distribution Circuit | Vegetation | Tree - fell into line | 1037 | 1758245 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005521 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 44930 | 559 | 1924495 | 9416 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 9416 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008161 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 44934 | 843 | 1932765 | 4472 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 22360 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011187 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | SWITCH |  | 44930 | 1334 | 1925539 | 5656 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 22624 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008547 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 3 | BRIDGEVILLE-1102 | 192461102 | FUSE |  | 44940 | 701 | 1954311 | 1634 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 45752 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016172 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | FUSE |  | 44931 | 104 | 1922650 | 6334 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 19002 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007547 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | BRIDGEVILLE-1102 | 192461102 | FUSE |  | 44931 | 2059 | 1923882 | 2470 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 4940 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008057 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1102 | 192461102 | RECLOSER |  | 44940 | 701 | 1952925 | 330 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 9240 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015866 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1102 | 192461102 | RECLOSER |  | 44936 | 358 | 1941465 | 2254 | Distribution Circuit | Vegetation | Tree - fell into line | 276 | 453832 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0011862 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1101 | 192461101 | RECLOSER |  | 44930 | 1709 | 1915723 | 3072 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 42404 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006286 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | RECLOSER |  | 44930 | 1058 | 1927130 | 5849 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 345091 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0005783 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | CARLOTTA-1121 | 192291121 | RECLOSER |  | 44930 | 610 | 1912330 | 10700 | Distribution Circuit | Vegetation | Tree - fell into line | 1133 | 495578 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005526 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | OTHER |  | 44934 | 2349 | 1935295 | 1147 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 73753 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010710 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
HUMBOLDT | Tier 2 | EEL RIVER-1102 | 192381102 | OTHER |  | 44934 | 2349 | 1935295 | 1147 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 73753 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010710 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
HUMBOLDT | Tier 2 | HUMBOLDT BAY-1102 | 192341102 | FUSE |  | 44930 | 557 | 1924891 | 3578 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 14312 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008332 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | HUMBOLDT BAY-1102 | 192341102 | FUSE |  | 44934 | 2329 | 1935068 | 2452 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 95628 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010909 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | HUMBOLDT BAY-1102 | 192341102 | FUSE |  | 44930 | 557 | 1912294 | 3377 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 118195 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005630 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | MAPLE CREEK-1101 | 192101101 | FUSE |  | 44931 | 1726 | 1924799 | 6986 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6986 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008292 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | HARRIS-1109 | 192431109 | FUSE |  | 44930 | 645 | 1912363 | 4974 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 59688 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005705 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | FUSE |  | 44930 | 710 | 1924256 | 7737 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 123792 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008102 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | FUSE |  | 44930 | 659 | 1922101 | 6479 | Distribution Circuit | Vegetation | Tree - fell into line | 273 | 453423 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007375 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | SWITCH |  | 44930 | 708 | 1922968 | 3713 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 460412 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006070 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | FUSE |  | 44930 | 659 | 1924401 | 7656 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 68904 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008139 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | RECLOSER |  | 44930 | 659 | 1923089 | 6479 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 310992 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007375 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | FUSE |  | 44930 | 659 | 1924484 | 6479 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 32395 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008158 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1122 | 192021122 | FUSE |  | 44930 | 659 | 1924570 | 6479 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 12958 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008189 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1121 | 192021121 | FUSE |  | 44930 | 720 | 1924768 | 6418 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 89852 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0008273 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | ARCATA-1121 | 192021121 | FUSE |  | 44930 | 720 | 1924689 | 6418 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 57762 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008228 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44936 | 136 | 1944646 | 2460 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 83640 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012231 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44930 | 518 | 1913894 | 5140 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 61680 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005945 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44936 | 142 | 1946401 | 2454 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 66258 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012960 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44930 | 523 | 1914784 | 5128 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 282040 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006122 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44936 | 136 | 1948029 | 2460 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 29520 | Heavy Rain-Strong Winds-Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013676 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | JUMPER |  | 44930 | 518 | 1916742 | 11956 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 107604 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006389 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44936 | 142 | 1945303 | 2443 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 48860 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012512 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44936 | 142 | 1941571 | 2232 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 17856 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011854 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1103 | 192171103 | OTHER |  | 44930 | 523 | 1912267 | 9351 | Distribution Circuit | Vegetation | Tree - fell into line | 2067 | 2655646 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0005511 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 3 | WILLOW CREEK-1103 | 192171103 | RECLOSER |  | 44936 | 137 | 1939860 | 2304 | Distribution Circuit | Vegetation | Tree - fell into line | 1827 | 1432074 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005511 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE |  | 44930 | 523 | 1912886 | 3523 | Distribution Circuit | Vegetation | Tree - fell into line | 226 | 796198 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0005650 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
HUMBOLDT | Tier 2 | WILLOW CREEK-1101 | 192171101 | FUSE |  | 44934 | 2120 | 1934799 | 3895 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 46740 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010569 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | CABRILLO-1104 | 183101104 | FUSE |  | 44934 | 1258 | 1933594 | 519 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 6607 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010233 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | SISQUOC-1102 | 182811102 | FUSE |  | 44935 | 2332 | 1939779 | 2177 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 88012 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0013030 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
LOS PADRES | Tier 3 | SANTA MARIA-1108 | 182671108 | RECLOSER |  | 44931 | 1313 | s1797751 | 1868 | Distribution Circuit | Vegetation | Tree - fell into line | 385 | 213404 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007531 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | OCEANO-1102 | 182601102 | FUSE |  | 44940 | 1421 | 1954545 | 254 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 5588 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016277 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
LOS PADRES | Tier 2 | OCEANO-1104 | 182601104 | FUSE |  | 44931 | 421 | 1920579 | 548 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 15892 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007093 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | OCEANO-1104 | 182601104 | FUSE |  | 44935 | 1742 | 1939124 | 977 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5854 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011517 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
LOS PADRES | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER |  | 44935 | 600 | 1935969 | 2443 | Distribution Circuit | Vegetation | Tree - fell into line | 1257 | 3070851 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010805 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 3 | SAN LUIS OBISPO-1104 | 182631104 | FUSE |  | 44935 | 951 | 1937403 | 4510 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 22550 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012789 | OH | Sus | 35419613 | 2023 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | RECLOSER |  | 44930 | 2108 | 1918674 | 1247 | Distribution Circuit | Vegetation | Tree - fell into line | 382 | 120349 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0006617 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | OTHER |  | 44930 | 2108 | 1922889 | 1363 | Distribution Circuit | Animal | Bird found | 231 | 211518 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007619 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE |  | 44935 | 615 | 1936040 | 3420 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 157515 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011678 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | CAMBRIA-1102 | 182771102 | FUSE |  | 44935 | 328 | 1935452 | 2336 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 200752 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010758 | OH | Sus | 35419613 | 2023 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | CAMBRIA-1102 | 182771102 | FUSE |  | 44930 | 2115 | 1920461 | 786 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 65238 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006960 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | CAMBRIA-1101 | 182771101 | RECLOSER |  | 44936 | 314 | 1941166 | 3651 | Distribution Circuit | Equipment Failure/Involved | Overhead | 65 | 205239 | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 23-0011824 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2110 | 183052110 | OTHER |  | 44935 | 232 | 1935234 | 5101 | Distribution Circuit | Vegetation | Tree - fell into line | 420 | 2089365 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010724 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
LOS PADRES | Tier 2 | CAMBRIA-1101 | 182771101 | FUSE |  | 44930 | 1956 | 1921945 | 4055 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 170142 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0007763 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
LOS PADRES | Tier 2 | OILFIELDS-1103 | 182391103 | FUSE |  | 44935 | 1125 | 1937849 | 1672 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 150480 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011438 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
MISSION | Tier 3 | CASTRO VALLEY-1110 | 14091110 | FUSE |  | 44935 | 1301 | 1938202 | 484 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 484 | Heavy Rain-Strong Winds-Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011302 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
MISSION | Tier 2 | NORTH DUBLIN-2103 | 14052103 | FUSE |  | 44940 | 1659 | 1954824 | 1274 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1274 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016346 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
MISSION | Tier 3 | SAN RAMON-2108 | 14232108 | FUSE |  | 44930 | 1631 | 1916032 | 1349 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 28734 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006504 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | JUMPER |  | 44934 | 5 | 1932237 | 1117 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 20809 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009825 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | RECLOSER |  | 44933 | 2341 | 1931412 | 1039 | Distribution Circuit | Vegetation | Tree - fell into line | 204 | 199606 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009802 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | RECLOSER |  | 44930 | 1709 | 1915710 | 2911 | Distribution Circuit | Vegetation | Tree - fell into line | 204 | 522228 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006285 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | RECLOSER |  | 44936 | 201 | 1939991 | 985 | Distribution Circuit | Equipment Failure/Involved | Overhead | 391 | 214567 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011743 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE |  | 44931 | 2031 | 1923957 | 1394 | Distribution Circuit | Vegetation | Tree - branch fell on line | 70 | 97580 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008094 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | RECLOSER |  | 44940 | 704 | 1952924 | 626 | Distribution Circuit | Vegetation | Tree - fell into line | 980 | 118325 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015862 | OH | Sus | 35419665 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | BOLINAS-1101 | 42261101 | RECLOSER |  | 44930 | 1706 | 1915711 | 7404 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 37020 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006284 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | BOLINAS-1101 | 42261101 | RECLOSER |  | 44930 | 1958 | 1917925 | 5557 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 111140 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006529 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 3 | BOLINAS-1101 | 42261101 | RECLOSER |  | 44930 | 1658 | 1915645 | 4271 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 25626 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006271 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE |  | 44933 | 1453 | 1926900 | 1560 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 58950 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008884 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1101 | 42011101 | FUSE |  | 44930 | 2112 | 1918299 | 2751 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 60522 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007878 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE |  | 44935 | 739 | 1936505 | 511 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 3577 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010921 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | OTHER |  | 44930 | 1712 | 1915764 | 1152 | Distribution Circuit | Vegetation | Tree - branch fell on line | 104 | 117923 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006392 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | RECLOSER |  | 44930 | 2140 | 1916801 | 2389 | Distribution Circuit | Vegetation | Tree - fell into line | 1553 | 3342556 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006698 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
NORTH BAY | Tier 2 | SAN RAFAEL-1109 | 42011109 | RECLOSER |  | 44936 | 527 | 1942704 | 505 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1779 | 422965 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011919 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | OCB |  | 44935 | 203 | 1935211 | 2329 | Distribution Circuit | Vegetation | Tree - fell into line | 3039 | 2661553 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010704 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE |  | 44933 | 1656 | 1927206 | 147 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 1617 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008930 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE |  | 44930 | 1616 | 1918458 | 1812 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 30804 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007668 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE |  | 44930 | 1712 | 1915852 | 2880 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 72000 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007746 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE |  | 44930 | 1604 | 1915087 | 1616 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 185840 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006275 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE |  | 44930 | 1421 | 1914420 | 2723 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 76244 | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 23-0006090 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | WOODACRE-1101 | 43021101 | RECLOSER |  | 44930 | 2040 | 1916291 | 2962 | Distribution Circuit | Vegetation | Tree - fell into line | 268 | 712774 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006586 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
NORTH BAY | Tier 3 | LAS GALLINAS A-1105 | 42991105 | FUSE |  | 44934 | 147 | 1931841 | 3871 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 19355 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0010169 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 44933 | 2315 | 1928946 | 2220 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 17760 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010065 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | OTHER |  | 44935 | 16 | 1935046 | 2052 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1178 | 166098 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010753 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | WOODACRE-1101 | 43021101 | FUSE |  | 44933 | 1304 | 1926625 | 1605 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 9630 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008854 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | OTHER |  | 44934 | 1345 | 1933682 | 1486 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 40201 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010247 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER |  | 44930 | 1658 | 1915624 | 5682 | Distribution Circuit | Vegetation | Tree - branch fell on line | 126 | 200379 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006267 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | JUMPER |  | 44934 | 1525 | 1933947 | 159 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 636 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010317 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | OTHER |  | 44933 | 1431 | 1927320 | 1483 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 21870 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008956 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER |  | 44930 | 1635 | 1915600 | 5679 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 607653 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006263 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE |  | 44930 | 1921 | 1917589 | 2754 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 33048 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007087 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER |  | 44936 | 643 | 1943122 | 1358 | Distribution Circuit | Vegetation | Tree - fell into line | 2196 | 542051 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0011964 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | RECLOSER |  | 44931 | 1402 | 1922607 | 1708 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 36977 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006475 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER |  | 44931 | 646 | 1920767 | 2180 | Distribution Circuit | Vegetation | Tree - fell into line | 739 | 77204 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0007018 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | OCB |  | 44930 | 2111 | 1918747 | 1055 | Distribution Circuit | Vegetation | Tree - fell into line | 706 | 744830 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006634 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | JUMPER |  | 44934 | 846 | 1932777 | 3023 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 8750 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0010202 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | Yes
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER |  | 44935 | 414 | 1935571 | 275 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 36059 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010755 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER |  | 44930 | 1758 | 1916575 | 1324 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 66956 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0006372 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | KANAKA-1101 | 103221101 | FUSE |  | 44934 | 253 | 1933946 | 3734 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 7468 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0010266 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | OTHER |  | 44934 | 809 | 1933927 | 3089 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 25153 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010263 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 2 | CLARK ROAD-1102 | 103091102 | RECLOSER |  | 44934 | 258 | 1932083 | 957 | Distribution Circuit | Vegetation | Tree - fell into line | 147 | 57924 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0009775 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | BIG BEND-1101 | 103751101 | FUSE |  | 44930 | 2245 | 1919520 | 3762 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 41382 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007562 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | BUTTE-1105 | 103081105 | RECLOSER |  | 44940 | 910 | 1953563 | 442 | Distribution Circuit | Vegetation | Tree - fell into line | 204 | 49075 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015972 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CLARK ROAD-1102 | 103091102 | OTHER |  | 44931 | 2210 | 1924253 | 1029 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 12348 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008101 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1103 | 102831103 | OTHER |  | 44934 | 524 | 1932235 | 1962 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 13719 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0009858 | OH | Sus | 35419635 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 3 | BUTTE-1105 | 103081105 | FUSE |  | 44930 | 2011 | 1918070 | 3736 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 7472 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007482 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | BUTTE-1105 | 103081105 | RECLOSER |  | 44936 | 430 | 1942126 | 811 | Distribution Circuit | Vegetation | Tree - fell into line | 200 | 70691 | Partly Cloudy-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011867 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BIG BEND-1101 | 103751101 | RECLOSER |  | 44931 | 1533 | 1922982 | 2828 | Distribution Circuit | Environmental/External | Ice or snow | 3 | 8484 | Clear;32-90 F | Conductor- Overhead | On Ground | 23-0007657 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1105 | 102831105 | FUSE |  | 44933 | 2257 | 1932333 | 2118 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 21276 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010046 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1105 | 102831105 | JUMPER |  | 44931 | 820 | 1921141 | 2140 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 23804 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007194 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1105 | 102831105 | FUSE |  | 44930 | 1929 | 1917702 | 2671 | Distribution Circuit | Vegetation | Tree - fell into line | 284 | 76583 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006536 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1105 | 102831105 | JUMPER |  | 44933 | 2258 | 1931404 | 770 | Distribution Circuit | Vegetation | Tree - fell into line | 1511 | 57267 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0009548 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | FUSE |  | 44930 | 2235 | 1920449 | 2381 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 71293 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006959 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | FUSE |  | 44930 | 2236 | 1921881 | 2379 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 11895 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007316 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1105 | 102831105 | FUSE |  | 44931 | 1836 | 1923574 | 2745 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 83796 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008190 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | FUSE |  | 44930 | 2236 | s1797340 | 2214 | Distribution Circuit | Equipment Failure/Involved | Overhead | 157 | 347598 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0006798 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | JUMPER |  | 44930 | 2042 | 1922267 | 1440 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 5760 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007441 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | OCB |  | 44930 | 2017 | 1918492 | 4076 | Distribution Circuit | Vegetation | Tree - fell into line | 724 | 1347530 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006819 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE |  | 44930 | 2006 | 1922139 | 2837 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 51066 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007413 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | JUMPER |  | 44930 | 2006 | 1922495 | 3272 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3272 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007413 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER |  | 44930 | 2032 | s1796878 | 2780 | Distribution Circuit | Vegetation | Tree - branch fell on line | 184 | 510970 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006490 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER |  | 44930 | 2029 | s1796884 | 1287 | Distribution Circuit | Equipment Failure/Involved | Overhead | 376 | 483582 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006490 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER |  | 44935 | 236 | 1935039 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 574 | 239699 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010725 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE |  | 44930 | 2011 | 1922157 | 2807 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 272279 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007415 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | RECLOSER |  | 44930 | 2022 | 1918236 | 2519 | Distribution Circuit | Vegetation | Tree - fell into line | 490 | 744364 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006571 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE |  | 44930 | 2018 | 1922168 | 3258 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 153126 | Overcast-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0007416 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | FUSE |  | 44931 | 722 | 1923267 | 3302 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 65636 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0007735 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | ORO FINO-1102 | 103031102 | RECLOSER |  | 44930 | 1928 | 1916366 | 1535 | Distribution Circuit | Equipment Failure/Involved | Overhead | 571 | 1098747 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006490 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | FUSE |  | 44930 | 1955 | 1919571 | 2408 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 53711 | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0006523 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER |  | 44930 | 1705 | 1915673 | 1096 | Distribution Circuit | Vegetation | Tree - fell into line | 671 | 143726 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006277 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER |  | 44936 | 1119 | 1944782 | 1447 | Distribution Circuit | Equipment Failure/Involved | Overhead | 748 | 871441 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012281 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | VOLTA-1101 | 102541101 | FUSE |  | 44940 | 826 | 1953279 | 1770 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 10620 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016227 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | RECLOSER |  | 44930 | 2003 | 1918024 | 1395 | Distribution Circuit | Vegetation | Tree - fell into line | 1081 | 1507995 | Overcast-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0006541 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | GIRVAN-1102 | 103401102 | FUSE |  | 44930 | 2209 | 1919253 | 968 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 20328 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007188 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | WHITMORE-1101 | 103601101 | FUSE |  | 44931 | 804 | 1921068 | 1951 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7804 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007629 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | KESWICK-1101 | 103451101 | FUSE |  | 44931 | 1245 | 1922270 | 1607 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 14463 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0007442 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1101 | 103381101 | TRIP-SAVER |  | 44940 | 755 | 1953067 | 905 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 13370 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0016072 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | OTHER |  | 44930 | 2341 | 1921226 | 614 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 6357 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007102 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 2 | RISING RIVER-1101 | 103551101 | RECLOSER |  | 44934 | 655 | 1932564 | 665 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 19950 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009879 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | FUSE |  | 44940 | 348 | 1952763 | 891 | Distribution Circuit | Vegetation | Tree - fell into line | 164 | 50380 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0015833 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | RECLOSER |  | 44935 | 548 | 1935918 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 21225 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0010800 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | RECLOSER |  | 44930 | 2257 | 1919637 | 1108 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 88276 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006846 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 44934 | 2332 | 1938400 | 2564 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 35896 | Strong Winds-Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011288 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 44933 | 742 | 1934630 | 4193 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 410914 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010460 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | OTHER |  | 44940 | 906 | 1954109 | 1997 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 71892 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016205 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 44940 | 749 | 1954337 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1800 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016185 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | RECLOSER |  | 44934 | 2322 | 1935002 | 3759 | Distribution Circuit | Vegetation | Tree - branch fell on line | 518 | 1122215 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010646 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | TRIP-SAVER |  | 44936 | 2157 | 1946667 | 6603 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 53676 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0013504 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | JUMPER |  | 44930 | 1337 | 1914906 | 2010 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 18090 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006151 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
PENINSULA | Tier 2 | MENLO-1102 | 24131102 | FUSE |  | 44935 | 1449 | 1945559 | 2247 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 103606 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012651 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 44934 | 641 | 1932357 | 3335 | Distribution Circuit | Vegetation | Tree - branch fell on line | 356 | 187660 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010076 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER |  | 44940 | 2342 | 1955338 | 1033 | Distribution Circuit | Vegetation | Tree - fell into line | 647 | 178905 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0016493 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1102 | 24131102 | FUSE |  | 44933 | 1733 | 1927386 | 1123 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 32567 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010080 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 44930 | 1425 | 1914472 | 5983 | Distribution Circuit | Equipment Failure/Involved | Overhead | 112 | 353924 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006083 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER |  | 44942 | 624 | 1956755 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 314 | 7438 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016957 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 44930 | 1520 | 1923849 | 2850 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 11400 | Strong Winds-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007939 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER |  | 44940 | 824 | 1953267 | 468 | Distribution Circuit | Vegetation | Tree - fell into line | 343 | 85298 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016057 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 44935 | 1325 | 1938289 | 4407 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 92547 | Strong Winds-Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011496 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER |  | 44930 | 1435 | 1924172 | 3262 | Distribution Circuit | Environmental/External | Water | 382 | 452617 | Strong Winds-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008112 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER |  | 44935 | 446 | 1934851 | 3652 | Distribution Circuit | Equipment Failure/Involved | Overhead | 704 | 1235038 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010764 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | WOODSIDE-1104 | 24251104 | TRIP-SAVER |  | 44942 | 734 | 1957216 | 709 | Distribution Circuit | Vegetation | Tree - fell into line | 103 | 47976 | Strong Winds-Heavy Rain-Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0017018 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1104 | 24251104 | FUSE |  | 44931 | 118 | 1920693 | 1444 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 38988 | Strong Winds-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007745 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 3 | HALF MOON BAY-1101 | 24101101 | TRIP-SAVER |  | 44936 | 154 | 1944792 | 2361 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 99162 | Strong Winds; | Conductor- Overhead | Broken- wire on ground | 23-0012284 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | HALF MOON BAY-1101 | 24101101 | FUSE |  | 44936 | 154 | 1944785 | 2028 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 32448 | Strong Winds; | Conductor- Overhead | Broken- wire on ground | 23-0012279 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | HALF MOON BAY-1101 | 24101101 | FUSE |  | 44936 | 154 | 1944773 | 3856 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 61696 | Strong Winds; | Conductor- Overhead | Broken- wire on ground | 23-0012274 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | SAN CARLOS-1104 | 24181104 | FUSE |  | 44934 | 1123 | 1933305 | 1787 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1787 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010066 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE |  | 44936 | 406 | 1943256 | 869 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 11297 | Strong Winds; | Conductor- Overhead | Broken- wire on ground | 23-0012235 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE |  | 44931 | 917 | s1798416 | 3403 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 6806 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008484 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | HALF MOON BAY-1101 | 24101101 | JUMPER |  | 44942 | 1340 | 1958399 | 251 | Distribution Circuit | Vegetation | Tree - bark fell into line | 2 | 502 | Rain; | Conductor- Overhead | On Ground | 23-0017274 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | PACIFICA-1103 | 22811103 | FUSE |  | 44930 | 1429 | 1926748 | 4476 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 13428 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008824 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | CAROLANDS-0404 | 24060404 | FUSE |  | 44936 | 1707 | 1946061 | 1123 | Distribution Circuit | Vegetation | Tree - branch fell on line | 124 | 139252 | Strong Winds; | Conductor- Overhead | Broken- wire on ground | 23-0012846 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
SACRAMENTO | Tier 2 | NARROWS-2101 | 153132101 | FUSE |  | 44931 | 10 | 1920285 | 1368 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 28728 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007542 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SAN JOSE | Tier 2 | MORGAN HILL-2105 | 83242105 | OTHER |  | 44931 | 405 | 1920555 | 2381 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 38257 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007675 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
SAN JOSE | Tier 3 | MORGAN HILL-2111 | 83242111 | FUSE |  | 44936 | 324 | 1941173 | 26538 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 26538 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012990 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SAN JOSE | Tier 3 | HICKS-2101 | 83432101 | FUSE |  | 44931 | 720 | 1922212 | 1349 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2698 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007414 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SAN JOSE | Tier 2 | SWIFT-2110 | 83392110 | RECLOSER |  | 44931 | 516 | 1920637 | 3169 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 264488 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006994 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 44934 | 210 | 1933027 | 2173 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 42845 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0009991 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | DIAMOND SPRINGS-1105 | 152261105 | FUSE |  | 44934 | 723 | 1932512 | 2252 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 13056 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010136 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE |  | 44934 | 125 | 1931720 | 2407 | Distribution Circuit | Equipment Failure/Involved | Overhead | 134 | 322538 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010387 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 44931 | 1916 | 1923711 | 868 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 6292 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007872 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | FUSE |  | 44936 | 420 | 1945545 | 2063 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 10315 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011869 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE |  | 44936 | 518 | 1942642 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 10530 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012045 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-1104 | 153651104 | TRANSFORMER |  | 44930 | 1943 | 1917798 | 2770 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5540 | Clear;32-90F | Transformer (OH) | Broken- wire on ground | 23-0008328 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | TRANSFORMER |  | 44930 | 2135 | 1920268 | 1325 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2405 | Clear;32-90 F | Transformer | Broken- wire on ground | 23-0006921 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | SWITCH |  | 44933 | 1810 | 1927476 | 1418 | Distribution Circuit | Vegetation | Tree - fell into line | 1030 | 1197021 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008986 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 44936 | 1111 | 1945160 | 1667 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 61679 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012687 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2108 | 153652108 | RECLOSER |  | 44933 | 1947 | 1927938 | 1478 | Distribution Circuit | Vegetation | Tree - fell into line | 1908 | 209108 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009056 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2110 | 153652110 | TRANSFORMER |  | 44934 | 31 | 1931650 | 2495 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2495 | Clear;32-90F | Transformer (OH) | Broken- wire on ground | 23-0011135 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 44936 | 421 | 1941946 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 70971 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012039 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | RECLOSER |  | 44936 | 421 | 1941948 | 1397 | Distribution Circuit | Vegetation | Tree - fell into line | 1153 | 453934 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011869 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | OTHER |  | 44936 | 513 | 1942622 | 2063 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 3024 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012871 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 44934 | 151 | 1931854 | 2151 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 75285 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009925 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 44936 | 659 | 1941600 | 364 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 7644 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011997 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | DIAMOND SPRINGS-1105 | 152261105 | JUMPER |  | 44930 | 2008 | 1918034 | 882 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1764 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006611 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | DIAMOND SPRINGS-1103 | 152261103 | FUSE |  | 44933 | 2311 | 1928930 | 2356 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 160208 | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0010124 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | DIAMOND SPRINGS-1107 | 152261107 | OTHER |  | 44936 | 413 | 1941636 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 4729 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012209 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 44934 | 133 | 1931772 | 2661 | Distribution Circuit | Vegetation | Tree - fell into line | 453 | 1136163 | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0009898 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | JUMPER |  | 44940 | 1331 | 1959597 | 5439 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 21756 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017635 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44930 | 2051 | 1918503 | 794 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 48434 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006769 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | Yes
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44934 | 840 | 1931858 | 2083 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 10415 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010159 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-1110 | 153081110 | OTHER |  | 44935 | 332 | 1937719 | 934 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 28190 | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011078 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | RECLOSER |  | 44942 | 1218 | 1958034 | 910 | Distribution Circuit | Vegetation | Tree - fell into line | 308 | 451944 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017179 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 44930 | 2048 | 1918518 | 1125 | Distribution Circuit | Vegetation | Tree - branch fell on line | 480 | 477670 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006595 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | FUSE |  | 44933 | 1805 | 1931125 | 1283 | Distribution Circuit | Equipment Failure/Involved | Overhead | 230 | 295090 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0009955 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 44934 | 137 | 1933817 | 2446 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 53812 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010234 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 44942 | 515 | 1960081 | 2406 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 31278 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017834 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE |  | 44942 | 1220 | 1960325 | 3149 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 91321 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017896 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER |  | 44934 | 132 | 1931818 | 2337 | Distribution Circuit | Vegetation | Tree - fell into line | 1276 | 1983006 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0009647 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 44934 | 158 | 1933211 | 2311 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 27732 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010040 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | TRIP-SAVER |  | 44942 | 1017 | 1958466 | 1979 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 229564 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017173 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 44936 | 420 | 1942018 | 2202 | Distribution Circuit | Vegetation | Tree - fell into line | 2841 | 2679319 | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011874 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 44934 | 113 | 1931673 | 1917 | Distribution Circuit | Vegetation | Tree - fell into line | 3018 | 2769564 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009593 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | OTHER |  | 44934 | 146 | 1931839 | 2174 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 23201 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010254 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | EL DORADO PH-2101 | 152762101 | RECLOSER |  | 44931 | 1655 | 1923293 | 1505 | Distribution Circuit | Environmental/External | Ice or snow | 703 | 894809 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007782 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HORSESHOE-1101 | 152571101 | FUSE |  | 44936 | 404 | 1941502 | 2354 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 56401 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012337 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HORSESHOE-1101 | 152571101 | FUSE |  | 44934 | 27 | 1930945 | 938 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 46900 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0009910 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 44934 | 31 | 1931008 | 2658 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 31896 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010281 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2102 | 152762102 | OCB |  | 44942 | 515 | 1957999 | 2406 | Distribution Circuit | Vegetation | Tree - fell into line | 1659 | 3526892 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017173 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE |  | 44936 | 429 | 1942055 | 2070 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 110022 | Partly Cloudy-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012301 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | EL DORADO PH-2101 | 152762101 | RECLOSER |  | 44940 | 1331 | 1954448 | 5957 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4094 | 9631789 | Rain; | Conductor- Overhead | Broken- wire on ground | 23-0016229 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | SWITCH |  | 44936 | 424 | 1948683 | 3639 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 469431 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013866 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44933 | 2046 | 1928032 | 2536 | Distribution Circuit | Vegetation | Tree - fell into line | 147 | 187326 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009384 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44936 | 420 | 1946060 | 3400 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 6800 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012839 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SIERRA | Tier 2 | PENRYN-1103 | 152561103 | FUSE |  | 44934 | 27 | 1930940 | 2091 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 25092 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010437 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PENRYN-1103 | 152561103 | RECLOSER |  | 44936 | 407 | 1941623 | 786 | Distribution Circuit | Vegetation | Tree - fell into line | 782 | 119325 | Partly Cloudy-Drizzle;32-90 F | Transformer (OH) | Broken- wire on ground | 23-0011894 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PENRYN-1103 | 152561103 | RECLOSER |  | 44934 | 49 | 1931323 | 1192 | Distribution Circuit | Equipment Failure/Involved | Overhead | 679 | 305686 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0009539 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44934 | 1914 | 1934517 | 4474 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 35792 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0011227 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PENRYN-1105 | 152561105 | RECLOSER |  | 44935 | 1856 | 1939304 | 1243 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 96954 | Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011547 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PENRYN-1105 | 152561105 | FUSE |  | 44934 | 102 | 1931466 | 1186 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 41510 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010224 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | LINCOLN-1101 | 153701101 | JUMPER |  | 44936 | 404 | 1946077 | 3359 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10077 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012837 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 44935 | 1427 | 1938448 | 211 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 3413 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011369 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | RECLOSER |  | 44940 | 955 | 1953769 | 663 | Distribution Circuit | Vegetation | Tree - fell into line | 315 | 24801 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016026 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44936 | 420 | 1945819 | 2074 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 31110 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012738 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER |  | 44936 | 421 | 1941932 | 609 | Distribution Circuit | Vegetation | Tree - fell into line | 291 | 177219 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011872 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | BELL-1109 | 152701109 | FUSE |  | 44936 | 415 | 1941658 | 3529 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 22789 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012078 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BELL-1109 | 152701109 | FUSE |  | 44933 | 2336 | 1930399 | 1016 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 61976 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0009499 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | RECLOSER |  | 44933 | 2338 | 1929470 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 710 | 610587 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0009410 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | BELL-1108 | 152701108 | FUSE |  | 44934 | 115 | 1931564 | 2041 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 8164 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010563 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | RECLOSER |  | 44930 | 2043 | 1918462 | 1110 | Distribution Circuit | Vegetation | Tree - fell into line | 920 | 654009 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006592 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | RECLOSER |  | 44933 | 1811 | 1927501 | 1054 | Distribution Circuit | Vegetation | Tree - fell into line | 628 | 75910 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0008990 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1107 | 152691107 | FUSE |  | 44934 | 115 | 1931567 | 1133 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 101833 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010209 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1107 | 152691107 | FUSE |  | 44930 | 1808 | 1916731 | 958 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 4429 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0006483 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1107 | 152691107 | TRIP-SAVER |  | 44930 | 1958 | 1917948 | 862 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 14400 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006680 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | FUSE |  | 44936 | 421 | 1941916 | 3689 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 47957 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0013434 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1110 | 152691110 | FUSE |  | 44930 | 2349 | 1919866 | 835 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 18409 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0007136 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 44936 | 1003 | 1944365 | 1795 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5852 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012763 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | TRIP-SAVER |  | 44936 | 423 | 1942026 | 806 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 29294 | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012101 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1106 | 152481106 | JUMPER |  | 44931 | 1000 | 1921585 | 280 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1073 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0007275 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | RECLOSER |  | 44930 | 1457 | 1914661 | 1421 | Distribution Circuit | Vegetation | Tree - fell into line | 218 | 68257 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006098 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | SHADY GLEN-1102 | 152431102 | FUSE |  | 44934 | 536 | 1932265 | 2024 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 26609 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0010099 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | TRIP-SAVER |  | 44933 | 1833 | 1927593 | 1455 | Distribution Circuit | Vegetation | Tree - branch fell on line | 154 | 224070 | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0009046 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE |  | 44930 | 1917 | 1916981 | 1099 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 98910 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006525 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44935 | 646 | 1936288 | 664 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 14608 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011137 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE |  | 44936 | 422 | 1943827 | 634 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 15216 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012056 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | RECLOSER |  | 44930 | 1819 | 1916817 | 931 | Distribution Circuit | Vegetation | Tree - fell into line | 897 | 172251 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006403 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE |  | 44935 | 28 | 1937392 | 2221 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 75514 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010988 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | FUSE |  | 44934 | 724 | 1932516 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 8624 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010014 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 44936 | 430 | 1942234 | 854 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 15242 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012259 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER |  | 44935 | 338 | 1935489 | 857 | Distribution Circuit | Vegetation | Tree - fell into line | 471 | 142317 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010749 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER |  | 44933 | 1844 | 1927634 | 1184 | Distribution Circuit | Vegetation | Tree - fell into line | 603 | 127973 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009017 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | SPAULDING-1101 | 152251101 | FUSE |  | 44940 | 911 | 1953522 | 3237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 16185 | Snow; | Conductor- Overhead | Broken- wire on ground | 23-0016780 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SIERRA | Tier 2 | SPAULDING-1101 | 152251101 | FUSE |  | 44940 | 911 | 1954838 | 2010 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 22110 | Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0015978 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SPAULDING-1101 | 152251101 | RECLOSER |  | 44940 | 911 | 1953562 | 3379 | Distribution Circuit | Equipment Failure/Involved | Overhead | 184 | 277448 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0015978 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 44931 | 2006 | 1923801 | 6779 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 13558 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008364 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER |  | 44930 | 2102 | 1918637 | 1317 | Distribution Circuit | Equipment Failure/Involved | Overhead | 142 | 164624 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006626 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
SONOMA | Tier 2 | COTATI-1105 | 42271105 | FUSE |  | 44930 | 1709 | 1922018 | 2658 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 15948 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007343 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 44930 | 1850 | 1915621 | 5816 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 34880 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006453 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1105 | 42271105 | RECLOSER |  | 44930 | 1715 | 1915769 | 2652 | Distribution Circuit | Equipment Failure/Involved | Overhead | 923 | 907300 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006345 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1102 | 42271102 | RECLOSER |  | 44930 | 859 | 1912851 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 5315 | 377617 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005652 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | SONOMA-1104 | 42721104 | FUSE |  | 44930 | 500 | 1912232 | 706 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 21886 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0005559 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | OCB |  | 44930 | 1943 | 1915540 | 1351 | Distribution Circuit | Vegetation | Tree - fell into line | 1427 | 1428200 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0006514 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
SONOMA | Tier 2 | COTATI-1105 | 42271105 | FUSE |  | 44930 | 1717 | 1916124 | 5880 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 52920 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010298 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | PENNGROVE-1101 | 43471101 | FUSE |  | 44930 | 1656 | 1915539 | 1497 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 50514 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006638 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER |  | 44936 | 816 | 1943550 | 4815 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 32180 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012037 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE |  | 44930 | 1951 | 1915904 | 4192 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 58688 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007661 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | FUSE |  | 44930 | 1724 | 1926723 | 5486 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 38402 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008817 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | JUMPER |  | 44933 | 1301 | 1934080 | 3090 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 32030 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010323 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | MOLINO-1101 | 42571101 | FUSE |  | 44934 | 1955 | 1934632 | 1338 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 17394 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010486 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | FUSE |  | 44930 | 1653 | 1915679 | 5867 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 76271 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0007940 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | RECLOSER |  | 44930 | 1530 | 1914842 | 8541 | Distribution Circuit | Vegetation | Tree - fell into line | 1309 | 4341320 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006130 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | TRIP-SAVER |  | 44930 | 1431 | 1914524 | 4181 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 321937 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006170 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 44930 | 1557 | 1924503 | 5975 | Distribution Circuit | Vegetation | Tree - fell into line | 164 | 969156 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0006331 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 44930 | 1659 | 1932879 | 7191 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 194157 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0009930 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 44930 | 1718 | 1915780 | 7258 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 226927 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007972 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | OTHER |  | 44931 | 615 | 1923901 | 3692 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 14848 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007975 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 44933 | 2315 | 1928952 | 3752 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 120064 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010095 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 44930 | 1712 | 1923517 | 4278 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 136896 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007828 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 44930 | 1849 | 1917215 | 5779 | Distribution Circuit | Vegetation | Tree - fell into line | 117 | 505665 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0007936 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 44936 | 1505 | 1945711 | 1470 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4410 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012703 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER |  | 44940 | 646 | s1808661 | 1847 | Distribution Circuit | Vegetation | Tree - fell into line | 1823 | 423587 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0015851 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER |  | 44930 | 1557 | 1915989 | 11055 | Distribution Circuit | Vegetation | Tree - fell into line | 1209 | 4490916 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0006331 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | JUMPER |  | 44930 | 1557 | 1923367 | 2993 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 8979 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007778 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | RECLOSER |  | 44930 | 1721 | 1915913 | 3886 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 143782 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008063 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 44930 | 1706 | 1922782 | 3134 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 3134 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007585 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 44930 | 1706 | 1925376 | 3134 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 56412 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008504 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 44930 | 1713 | 1922773 | 5487 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 71331 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007581 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 44934 | 1845 | 1934489 | 1527 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 83985 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010621 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 44936 | 738 | 1943359 | 1824 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 38304 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012151 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 44930 | 1731 | 1924911 | 8534 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 25602 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008338 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 44930 | 1709 | 1923027 | 5623 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 601661 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0007665 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | FUSE |  | 44930 | 1947 | 1917841 | 5729 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 91661 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008017 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 44930 | 2125 | 1918805 | 5469 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 76566 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008469 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE |  | 44935 | 1140 | 1937961 | 1778 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 28448 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011162 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE |  | 44930 | 1846 | 1917176 | 4104 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 94392 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006509 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | RECLOSER |  | 44936 | 204 | 1940156 | 2071 | Distribution Circuit | Vegetation | Tree - fell into line | 492 | 223642 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011757 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | JUMPER |  | 44931 | 1237 | 1922504 | 4471 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 49181 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007503 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | OTHER |  | 44935 | 107 | 1938075 | 3538 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 24106 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011169 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER |  | 44930 | 1555 | 1914975 | 8777 | Distribution Circuit | Vegetation | Tree - fell into line | 143 | 1255111 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006189 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | MIRABEL-1101 | 42091101 | JUMPER |  | 44930 | 955 | 1913185 | 531 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3717 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005709 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | JUMPER |  | 44940 | 1048 | 1954369 | 362 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2534 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016194 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER |  | 44940 | 1645 | 1954800 | 1342 | Distribution Circuit | Vegetation | Tree - fell into line | 1490 | 442048 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016325 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | OTHER |  | 44930 | 1610 | 1934496 | 8665 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 39770 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010436 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER |  | 44930 | 1403 | 1914096 | 11722 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1026 | 6351858 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006032 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE |  | 44935 | 323 | 1935430 | 3460 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 183380 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010767 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | RECLOSER |  | 44930 | 1616 | 1915193 | 5356 | Distribution Circuit | Vegetation | Tree - fell into line | 722 | 775642 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006205 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 44930 | 2000 | 1917949 | 9768 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 60432 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011108 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE |  | 44934 | 1155 | 1933538 | 1819 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9095 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010140 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE |  | 44930 | 1616 | 1923929 | 4632 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 240864 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008006 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | TRIP-SAVER |  | 44930 | 1331 | 1914741 | 7507 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 420392 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006116 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 44930 | 1403 | 1926814 | 11337 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 419469 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008832 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 2 | RINCON-1104 | 43321104 | OCB |  | 44930 | 1854 | 1917314 | 338 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4020 | 665256 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006501 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 44931 | 1456 | 1922851 | 5589 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 184437 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008582 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER |  | 44930 | 1456 | 1914654 | 11434 | Distribution Circuit | Vegetation | Tree - fell into line | 3566 | 6554131 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006094 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | SWITCH |  | 44930 | 1403 | 1925209 | 7492 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 104876 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0008456 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 44930 | 1403 | 1926817 | 8663 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 311868 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008836 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 44930 | 1403 | 1926825 | 9889 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 108779 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008840 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 44930 | 1659 | 1917559 | 5915 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 47320 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006470 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER |  | 44936 | 833 | 1943811 | 451 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 48411 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012060 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MONTE RIO-1111 | 42811111 | OTHER |  | 44930 | 1529 | 1915218 | 10227 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 395109 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006358 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | OTHER |  | 44930 | 2040 | 1918330 | 4164 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 84513 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007445 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 44930 | 1538 | 1916887 | 2698 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 99826 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006412 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 44930 | 1635 | 1923137 | 7075 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 955125 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0007690 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MIRABEL-1102 | 42091102 | FUSE |  | 44933 | 2235 | 1928421 | 2629 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 23661 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009759 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | OTHER |  | 44930 | 1825 | 1916869 | 5677 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 113540 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007574 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 44930 | 1534 | 1916985 | 7066 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 692468 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006422 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 44930 | 1656 | 1922830 | 1476 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 48708 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007595 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 44930 | 1403 | 1934112 | 12912 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 64560 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010333 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 44930 | 1403 | 1939025 | 11632 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 139584 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011467 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | JUMPER |  | 44930 | 1419 | 1945732 | 17306 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 17306 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012677 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE |  | 44931 | 1012 | 1921639 | 4951 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5859 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007743 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 44930 | 1424 | 1928217 | 6085 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 127785 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0009205 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 44930 | 1403 | 1944937 | 11729 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 504347 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0012352 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 44930 | 1403 | 1946086 | 13257 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 251883 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0012856 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | JUMPER |  | 44930 | 1403 | 1952504 | 14549 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 14549 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0015538 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 44930 | 1403 | 1948862 | 13189 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 232987 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013921 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 44933 | 1639 | 1927207 | 7221 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 64989 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0008932 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE |  | 44930 | 1255 | 1945455 | 14377 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 215272 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012565 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 44930 | 811 | 1913037 | 9130 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 127820 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005694 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1112 | 42751112 | FUSE |  | 44930 | 2010 | 1918054 | 5446 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 32676 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007504 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 44930 | 812 | 1913110 | 10402 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 353668 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0005712 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 44930 | 1419 | 1925129 | 10296 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 82368 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008424 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | TRIP-SAVER |  | 44930 | 1424 | 1928088 | 12922 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 503958 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0009128 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 44930 | 1419 | 1934438 | 14338 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 100366 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010420 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 44930 | 1337 | 1923873 | 8628 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 17256 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007947 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 44930 | 1438 | 1951543 | 12908 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 180712 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0015152 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 44930 | 1201 | 1923881 | 13123 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 131230 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007954 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1112 | 42751112 | RECLOSER |  | 44930 | 1732 | 1916170 | 2447 | Distribution Circuit | Vegetation | Tree - fell into line | 360 | 161139 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0006340 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 44930 | 1735 | 1920781 | 4347 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 247779 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0007016 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1112 | 42751112 | FUSE |  | 44930 | 1732 | 1927379 | 5652 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 56520 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0008966 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1112 | 42751112 | FUSE |  | 44942 | 10 | 1956458 | 671 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 42944 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0016861 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | CLOVERDALE-1102 | 42821102 | FUSE |  | 44930 | 1123 | 1913271 | 482 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 4372 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005823 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1702 | 163451702 | JUMPER |  | 44936 | 1857 | 1946344 | 1013 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 17221 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0013380 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1702 | 163451702 | RECLOSER |  | 44942 | 749 | 1957252 | 1927 | Distribution Circuit | Equipment Failure/Involved | Overhead | 127 | 194945 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0017004 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE |  | 44936 | 656 | 1943247 | 1656 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4968 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012704 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1701 | 163451701 | FUSE |  | 44931 | 942 | 1921514 | 1610 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 26850 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0007476 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | STANISLAUS-1701 | 162821701 | FUSE |  | 44930 | 1356 | 1914288 | 2679 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 42864 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006157 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | NORTH BRANCH-1101 | 163231101 | FUSE |  | 44930 | 2037 | 1918336 | 1105 | Distribution Circuit | Equipment Failure/Involved | Overhead | 366 | 53948 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006624 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 44936 | 521 | 1943922 | 1914 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 11484 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012070 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 44933 | 1824 | 1927542 | 3052 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 18312 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0010069 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 44933 | 2226 | 1928351 | 2613 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 26130 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010927 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CLAY-1103 | 163341103 | FUSE |  | 44933 | 2321 | 1933693 | 2665 | Distribution Circuit | 3rd Party | Other | 12 | 31980 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0009807 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER |  | 44934 | 2002 | 1938071 | 4099 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 209049 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0010469 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 44930 | 53 | 1912612 | 676 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 676 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0005724 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | SWITCH |  | 44942 | 917 | 1957583 | 628 | Distribution Circuit | Vegetation | Tree - fell into line | 471 | 295788 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017104 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | RECLOSER |  | 44942 | 1736 | 1958650 | 129 | Distribution Circuit | Vegetation | Tree - fell into line | 316 | 40764 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017341 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE |  | 44942 | 642 | 1958791 | 2021 | Distribution Circuit | Vegetation | Tree - fell into line | 278 | 560430 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017371 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | FUSE |  | 44942 | 1001 | 1957570 | 1798 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7192 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0017336 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | RECLOSER |  | 44942 | 1859 | 1958783 | 2503 | Distribution Circuit | Vegetation | Tree - fell into line | 400 | 220709 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0017368 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | ELECTRA-1102 | 162161102 | FUSE |  | 44931 | 1414 | 1922657 | 1496 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5984 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0007674 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | RECLOSER |  | 44936 | 435 | 1943261 | 898 | Distribution Circuit | Vegetation | Tree - fell into line | 605 | 543290 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011905 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | RECLOSER |  | 44933 | 1855 | 1927707 | 1490 | Distribution Circuit | Vegetation | Tree - fell into line | 747 | 400738 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0009047 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 44935 | 439 | 1935687 | 3782 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 434930 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011043 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE |  | 44933 | 2217 | 1937497 | 3541 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 113312 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0009569 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE |  | 44936 | 436 | 1942222 | 3361 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 57137 | Clear;32-90F | Insulator | Broken- wire on ground | 23-0013497 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE |  | 44935 | 1855 | 1939379 | 2591 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 28501 | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0013015 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 44930 | 2125 | 1918802 | 2363 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 33082 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0007321 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | MARTELL-1103 | 163011103 | RECLOSER |  | 44934 | 3 | 1930253 | 4979 | Distribution Circuit | Equipment Failure/Involved | Overhead | 139 | 173759 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0010277 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE |  | 44930 | 2037 | 1918304 | 1329 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 19935 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0006823 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | FUSE |  | 44936 | 949 | 1944308 | 294 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 4410 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012186 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | TRIP-SAVER |  | 44933 | 1832 | 1927576 | 1688 | Distribution Circuit | Vegetation | Tree - fell into line | 248 | 52024 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009081 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER |  | 44942 | 1034 | 1957697 | 1772 | Distribution Circuit | Vegetation | Tree - fell into line | 607 | 224351 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0017123 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER |  | 44936 | 435 | 1943417 | 894 | Distribution Circuit | Vegetation | Tree - fell into line | 593 | 530142 | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011905 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER |  | 44936 | 435 | 1944174 | 890 | Distribution Circuit | Vegetation | Tree - fell into line | 506 | 450340 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011905 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER |  | 44936 | 435 | 1943300 | 887 | Distribution Circuit | Vegetation | Tree - fell into line | 424 | 376088 | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011905 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER |  | 44942 | 1034 | 1957692 | 1948 | Distribution Circuit | Vegetation | Tree - fell into line | 2485 | 1144920 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0017127 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1101 | 163751101 | RECLOSER |  | 44936 | 418 | 1941845 | 2430 | Distribution Circuit | Vegetation | Tree - fell into line | 428 | 659665 | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011873 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 44930 | 1404 | 1914327 | 3022 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 33242 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006109 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER |  | 44930 | 2330 | 1920862 | 1088 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 64192 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0007029 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 44936 | 435 | 1945334 | 2078 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 49872 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011905 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | WEST POINT-1102 | 163201102 | RECLOSER |  | 44936 | 435 | 1943407 | 268 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 31624 | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011905 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | SWITCH |  | 44936 | 435 | 1943958 | 881 | Distribution Circuit | Vegetation | Tree - fell into line | 410 | 361210 | Overcast-Fog-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0011905 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 44930 | 1605 | 1915050 | 1480 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 22200 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006346 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 44942 | 1625 | 1958546 | 2694 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 134700 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017387 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | OCB |  | 44936 | 434 | 1942529 | 265 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 15105 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011905 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 44930 | 2126 | 1918811 | 1404 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 22916 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0007085 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | MARTELL-1101 | 163011101 | FUSE |  | 44936 | 414 | 1946046 | 2244 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 49368 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0011863 | OH | Sus | 0 | 2023 | JAN | Yes | None | Yes | No
STOCKTON | Tier 2 | MARTELL-1101 | 163011101 | FUSE |  | 44933 | 2211 | 1932057 | 2524 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 35336 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009709 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | OLETA-1101 | 163541101 | FUSE |  | 44934 | 26 | 1930907 | 4845 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 105392 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011441 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44933 | 2252 | 1928847 | 2303 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 26824 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010204 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | SWITCH |  | 44931 | 755 | 1921332 | 436 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 58424 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0007053 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
STOCKTON | Tier 2 | OLETA-1102 | 163541102 | RECLOSER |  | 44936 | 414 | 1941794 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 876 | 203232 | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0011885 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | OLETA-1102 | 163541102 | JUMPER |  | 44936 | 414 | 1945810 | 2224 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 37808 | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011885 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | OLETA-1101 | 163541101 | FUSE |  | 44930 | 1615 | 1915157 | 1576 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5600 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006457 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE |  | 44936 | 431 | 1942144 | 2313 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 27756 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012555 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | JUMPER |  | 44934 | 826 | 1933375 | 1558 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 68156 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010083 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2103 | 254432103 | FUSE |  | 44933 | 1013 | 1926319 | 296 | Distribution Circuit | Equipment Failure/Involved | Overhead | 96 | 12936 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0008760 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 254432104 | RECLOSER |  | 44936 | 616 | 1942993 | 3448 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1068 | 108166 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011949 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE |  | 44935 | 1030 | 1937640 | 266 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 20482 | Clear;32-90F | Conductor- Overhead | On Ground | 23-0011139 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | COARSEGOLD-2102 | 254432102 | RECLOSER |  | 44936 | 437 | 1942284 | 844 | Distribution Circuit | Equipment Failure/Involved | Overhead | 425 | 209316 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011883 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER |  | 44936 | 558 | 1944321 | 651 | Distribution Circuit | Vegetation | Tree - fell into line | 468 | 168550 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011937 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44936 | 600 | 1942948 | 1788 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 25992 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012096 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2102 | 254452102 | FUSE |  | 44931 | 653 | 1920796 | 787 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 21458 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0007187 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2101 | 252192101 | RECLOSER |  | 44930 | 2342 | 1919862 | 2311 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 95040 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0006883 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 44936 | 546 | 1942774 | 2097 | Distribution Circuit | Vegetation | Tree - fell into line | 169 | 354393 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0012258 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2101 | 252192101 | JUMPER |  | 44934 | 1101 | 1933237 | 434 | Distribution Circuit | Equipment Failure/Involved | Overhead | 258 | 1462 | Clear;32-90F | Connector or Splice (OH) | Broken- wire on ground | 23-0010219 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | Yes
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 44931 | 1424 | 1922708 | 1459 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2918 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0007563 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER |  | 44930 | 2350 | 1920012 | 1265 | Distribution Circuit | Vegetation | Tree - fell into line | 313 | 168310 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006879 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 44931 | 151 | 1920312 | 653 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1959 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006974 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER |  | 44935 | 540 | 1935901 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 77400 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010835 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 44933 | 2348 | 1929618 | 1218 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 18270 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0010131 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE |  | 44936 | 500 | 1942576 | 2050 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 10022 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0012988 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE |  | 44936 | 513 | 1942648 | 3380 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 125060 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0013320 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | CURTIS-1703 | 163351703 | OTHER |  | 44934 | 454 | 1934232 | 2054 | Distribution Circuit | Vegetation | Tree - fell into line | 606 | 1151622 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0010362 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER |  | 44934 | 241 | 1932066 | 1942 | Distribution Circuit | Vegetation | Tree - fell into line | 1260 | 1090837 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0009801 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER |  | 44936 | 438 | 1942333 | 3706 | Distribution Circuit | Equipment Failure/Involved | Overhead | 962 | 634580 | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0011889 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1705 | 163781705 | JUMPER |  | 44935 | 1108 | 1937771 | 1690 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1690 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011412 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | RECLOSER |  | 44936 | 444 | 1942407 | 887 | Distribution Circuit | Vegetation | Tree - fell into line | 673 | 219896 | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011897 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | JUMPER |  | 44942 | 1220 | 1958018 | 1565 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2675 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017273 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | FUSE |  | 44934 | 209 | 1931995 | 2204 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 88160 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0010270 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | FUSE |  | 44933 | 1854 | 1927661 | 706 | Distribution Circuit | Vegetation | Tree - fell into line | 225 | 64140 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0009284 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 44933 | 1828 | 1927555 | 1107 | Distribution Circuit | Vegetation | Tree - fell into line | 256 | 85264 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0009080 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44942 | 1103 | 1957761 | 1461 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 15639 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017339 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | RECLOSER |  | 44933 | 2259 | 1928621 | 2276 | Distribution Circuit | Vegetation | Tree - fell into line | 441 | 248544 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0009367 | OH | Sus | 0 | 2023 | JAN | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER |  | 44936 | 447 | 1942567 | 2198 | Distribution Circuit | Vegetation | Tree - fell into line | 431 | 297449 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0011902 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER |  | 44934 | 31 | 1931025 | 2183 | Distribution Circuit | Vegetation | Tree - fell into line | 272 | 362083 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0009574 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | FUSE |  | 44936 | 439 | 1942340 | 1956 | Distribution Circuit | Vegetation | Tree - fell into line | 117 | 228852 | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0012807 | OH | Sus | 0 | 2023 | JAN | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44942 | 1159 | 1957937 | 321 | Distribution Circuit | Vegetation | Tree - fell into line | 362 | 81552 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017281 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | OTHER |  | 44934 | 816 | 1934724 | 2179 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 8716 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0010474 | OH | Sus | 0 | 2023 | JAN | Yes | Open Circuit | Yes | Yes
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44934 | 31 | 1931007 | 3554 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 62269 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0010444 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | FUSE |  | 44930 | 2257 | 1918788 | 789 | Distribution Circuit | Vegetation | Tree - bark fell into line | 27 | 21303 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006812 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44942 | 141 | 1956520 | 442 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 9740 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0016871 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44936 | 446 | 1944475 | 835 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 35905 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011898 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 44936 | 446 | 1944562 | 1935 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 34830 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0011898 | OH | Sus | 0 | 2023 | JAN | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | TRANSFORMER |  | 44935 | 1155 | 1937382 | 1670 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 6680 | Clear;32-90F | Transformer (OH) | Broken- wire on ground | 23-0011194 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 44934 | 28 | 1934049 | 2446 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 136976 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0009603 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | STANISLAUS-1701 | 162821701 | OCB |  | 44930 | 2140 | 1919033 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 2176 | 1196055 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0006702 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER |  | 44942 | 906 | 1957423 | 630 | Distribution Circuit | Vegetation | Tree - fell into line | 491 | 200052 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0017056 | OH | Sus | 0 | 2023 | JAN | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | FUSE |  | 45006 | 1730 | 2059845 | 1105 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1105 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050005 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | OTHER |  | 44999 | 1014 | 2045112 | 3260 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 55247 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046043 | OH | Sus | 0 | 2023 | MAR | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | RECLOSER |  | 44999 | 904 | 2035394 | 2079 | Distribution Circuit | Vegetation | Tree - fell into line | 304 | 321442 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044585 | OH | Sus | 35431808 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | RECLOSER |  | 44994 | 2007 | 2028649 | 1395 | Distribution Circuit | Vegetation | Tree - fell into line | 378 | 155630 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0042504 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | FUSE |  | 44999 | 1040 | 2035295 | 1948 | Distribution Circuit | Vegetation | Tree - fell into line | 295 | 192673 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045289 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE |  | 44999 | 900 | 2046940 | 3167 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 266028 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046594 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | SWITCH |  | 44999 | 909 | 2040645 | 2089 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 189217 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044589 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 44994 | 1736 | 2032459 | 5747 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 229880 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043471 | OH | Sus | 35431167 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | RECLOSER |  | 44994 | 1759 | 2028313 | 8759 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 687648 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0042398 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | FUSE |  | 44994 | 1727 | 2032302 | 4172 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 66752 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043419 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | FUSE |  | 44994 | 1727 | 2032306 | 4137 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 91014 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0043420 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | FUSE |  | 45006 | 1255 | 2054707 | 401 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 8822 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049710 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | SWITCH |  | 44999 | 909 | 2037483 | 3257 | Distribution Circuit | Vegetation | Tree - fell into line | 1687 | 3200536 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044589 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | FUSE |  | 44999 | 909 | 2035856 | 1852 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 175940 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044685 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | FUSE |  | 44994 | 2019 | 2029179 | 3630 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 278034 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042510 | OH | Sus | 0 | 2023 | MAR | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | OCB |  | 44999 | 909 | 2035243 | 1852 | Distribution Circuit | Vegetation | Tree - fell into line | 1359 | 2304260 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044589 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1101 | 182291101 | OCB |  | 44994 | 1727 | 2028242 | 2847 | Distribution Circuit | Vegetation | Tree - fell into line | 3500 | 5747167 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042371 | OH | Sus | 35431167 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | OCB |  | 44994 | 2022 | 2029262 | 4403 | Distribution Circuit | Vegetation | Tree - fell into line | 1732 | 5258906 | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042519 | OH | Sus | 35431167 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | OCB |  | 44999 | 951 | 2035617 | 3030 | Distribution Circuit | Vegetation | Tree - fell into line | 732 | 2007990 | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0044636 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 45006 | 1426 | 2056682 | 419 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 15922 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049798 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | JUMPER |  | 44999 | 2010 | 2044639 | 1369 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8214 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045844 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE |  | 44999 | 1000 | 2035731 | 3351 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 35176 | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045876 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 44999 | 2010 | 2044653 | 1127 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 23667 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045851 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | JUMPER |  | 44999 | 1113 | 2049322 | 4476 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 22380 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047266 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 44999 | 1119 | 2044386 | 4772 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 62036 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045780 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | RECLOSER |  | 44999 | 1059 | s1824892 | 4113 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 127503 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044762 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 44994 | 1853 | 2032456 | 4354 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 26124 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043469 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE |  | 44999 | 951 | 2039649 | 3200 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 38400 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045086 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 44994 | 1845 | 2031107 | 4362 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 91602 | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0043129 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 44999 | 1119 | 2047486 | 4597 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 73552 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046811 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | OCB |  | 44994 | 1837 | 2028740 | 3046 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4884 | 6190135 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042443 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | OCB |  | 44999 | 1111 | 2036645 | 3405 | Distribution Circuit | Vegetation | Tree - fell into line | 5195 | 1513102 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044789 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | OCB |  | 44999 | 1140 | 2037464 | 1158 | Distribution Circuit | Vegetation | Tree - fell into line | 1043 | 986748 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044869 | OH | Sus | 0 | 2023 | MAR | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | OCB |  | 44994 | 1853 | 2028721 | 4354 | Distribution Circuit | Vegetation | Tree - branch fell on line | 938 | 417211 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042451 | OH | Sus | 0 | 2023 | MAR | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | OCB |  | 44999 | 1121 | 2036735 | 4728 | Distribution Circuit | Vegetation | Tree - branch fell on line | 631 | 2215378 | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044805 | OH | Sus | 0 | 2023 | MAR | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | OCB |  | 44994 | 1745 | 2028882 | 3070 | Distribution Circuit | Vegetation | Tree - fell into line | 5351 | 16139464 | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0042465 | OH | Sus | 0 | 2023 | MAR | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 44999 | 919 | 2036405 | 3502 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 175100 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044764 | OH | Sus | 0 | 2023 | MAR | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE |  | 44999 | 1151 | 2037688 | 4434 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 120517 | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045999 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE |  | 44994 | 1837 | 2029708 | 2846 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 136608 | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0042641 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | RECLOSER |  | 44999 | 1048 | 2036154 | 4705 | Distribution Circuit | Vegetation | Tree - fell into line | 601 | 2745374 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044729 | OH | Sus | 0 | 2023 | MAR | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | JUMPER |  | 44994 | 1825 | 2031538 | 4367 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 52404 | Partly Cloudy;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0043241 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE |  | 44994 | 1732 | 2028290 | 3049 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 118911 | Overcast;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0042435 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE |  | 44999 | 1305 | 2045306 | 3181 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 101792 | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046081 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE |  | 44994 | 1745 | 2032175 | 4017 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 128544 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043395 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE |  | 44999 | 1007 | 2044096 | 1975 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 37525 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045733 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE |  | 44999 | 1947 | 2044540 | 4075 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 122250 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045823 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | SWITCH |  | 44994 | 1838 | 2033174 | 5260 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 94680 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043669 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE |  | 44999 | 823 | 2035319 | 2058 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 45276 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044600 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE |  | 44999 | 1922 | 2044458 | 1455 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 128040 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045891 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE |  | 45006 | 1319 | 2055198 | 1505 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 111370 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050434 | OH | Sus | 45704997 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 45006 | 1250 | 2060898 | 1617 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 17787 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050170 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 45006 | 1422 | 2061475 | 1525 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 154025 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050298 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | RECLOSER |  | 45006 | 1248 | 2054599 | 7513 | Distribution Circuit | Equipment Failure/Involved | Overhead | 167 | 208542 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049660 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | OTHER |  | 45006 | 1318 | 2061518 | 3000 | Distribution Circuit | Vegetation | Tree - fell into line | 267 | 328326 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050308 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2105 | 83692105 | RECLOSER |  | 45006 | 1418 | 2054506 | 3117 | Distribution Circuit | Vegetation | Tree - fell into line | 1053 | 2971010 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049633 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | RECLOSER |  | 44999 | 1158 | 2037836 | 4446 | Distribution Circuit | Vegetation | Tree - fell into line | 3197 | 815438 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044910 | OH | Sus | 0 | 2023 | MAR | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER |  | 45006 | 1338 | 2055695 | 2883 | Distribution Circuit | Vegetation | Tree - fell into line | 279 | 233187 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049589 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER |  | 44999 | 1613 | 2042186 | 255 | Distribution Circuit | Vegetation | Tree - fell into line | 428 | 109140 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045535 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 45006 | 1504 | 2060507 | 2608 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 49552 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050201 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 45006 | 807 | 2053645 | 3207 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 25656 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049420 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | 83500401 | 83500401 | OTHER |  | 45006 | 1329 | 2055462 | 1313 | Distribution Circuit | Vegetation | Tree - fell into line | 213 | 276861 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049937 | OH | Sus | 0 | 2023 | MAR | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 2 | 83500401 | 83500401 | RECLOSER |  | 45006 | 1225 | 2054394 | 4279 | Distribution Circuit | Vegetation | Tree - fell into line | 127 | 543433 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049422 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 45006 | 1316 | 2064992 | 7462 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 129717 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051511 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | RECLOSER |  | 45006 | 1249 | 2055586 | 5713 | Distribution Circuit | Vegetation | Tree - fell into line | 449 | 106126 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050044 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 45006 | 1313 | 2064982 | 7259 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 29036 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051507 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 45006 | 2202 | 2061172 | 1026 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 27702 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050720 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | GREEN VALLEY-2101 | 83192101 | OTHER |  | 45006 | 1554 | 2057461 | 4129 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 89741 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051022 | OH | Sus | 0 | 2023 | MAR | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 44999 | 1821 | 2044095 | 202 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 11568 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045877 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 44999 | 1216 | 2044469 | 2851 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 17106 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045807 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2107 | 83252107 | FUSE |  | 45006 | 1253 | 2055276 | 3164 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 30313 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050617 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 44999 | 1028 | 2035907 | 3317 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 151339 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044937 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 45006 | 1444 | 2062798 | 1915 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 70855 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050704 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 45006 | 1301 | 2062204 | 3268 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 251636 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050466 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 45006 | 1316 | 2065267 | 7282 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 454584 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051586 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 45006 | 1321 | 2055269 | 4419 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 22095 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050271 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 45006 | 1926 | 2061560 | 2852 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 59892 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050313 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 45006 | 806 | 2053644 | 7546 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 15092 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049597 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | FUSE |  | 44999 | 2057 | 2044769 | 2765 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 16590 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046422 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE |  | 44999 | 1304 | 2039844 | 4211 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 16844 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045728 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44999 | 501 | 2035167 | 2186 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 54230 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044536 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44999 | 912 | 2035418 | 522 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 11484 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044704 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | RECLOSER |  | 45006 | 945 | 2053858 | 3440 | Distribution Circuit | Vegetation | Tree - fell into line | 267 | 116200 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049200 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | RECLOSER |  | 44994 | 2214 | 2029536 | 1116 | Distribution Circuit | Vegetation | Tree - fell into line | 267 | 169854 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042597 | OH | Sus | 0 | 2023 | MAR | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | RECLOSER |  | 45006 | 1316 | 2059148 | 3229 | Distribution Circuit | Vegetation | Tree - fell into line | 176 | 568304 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049923 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 44999 | 1141 | 2037377 | 3012 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 75300 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045307 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | SWITCH |  | 45006 | 1301 | 2062285 | 4237 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 410989 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050510 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 45006 | 1344 | 2062794 | 4542 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 13626 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050702 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | JUMPER |  | 45006 | 1344 | 2062809 | 4454 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 26724 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050708 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 44999 | 1148 | 2037631 | 4495 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 121365 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045797 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | JUMPER |  | 45006 | 1240 | 2063033 | 7429 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7429 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0050780 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 45006 | 1239 | 2060484 | 2957 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 84329 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050112 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER |  | 45006 | 1728 | 2062522 | 5421 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 52141 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050608 | OH | Sus | 0 | 2023 | MAR | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 2 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 45006 | 1239 | 2056043 | 1628 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 94096 | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049578 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44999 | 1945 | 2044531 | 2479 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 2479 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046493 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | SWITCH |  | 45006 | 1316 | 2059650 | 3229 | Distribution Circuit | Vegetation | Tree - branch fell on line | 72 | 232488 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049923 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 44999 | 629 | 2035614 | 2151 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 129060 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044635 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 44999 | 1146 | 2037603 | 2825 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 45200 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046398 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 45006 | 1239 | 2066805 | 5935 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5935 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052445 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 45006 | 1318 | 2055173 | 3222 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 144990 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050619 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 45006 | 1341 | 2056720 | 4549 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 40301 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050568 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER |  | 45006 | 1840 | 2059991 | 2967 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 227039 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0050029 | OH | Sus | 0 | 2023 | MAR | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | RECLOSER |  | 45006 | 1313 | 2054694 | 4437 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 221839 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049483 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 45006 | 1319 | 2055196 | 4265 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 27200 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049822 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2105 | 83622105 | FUSE |  | 45006 | 1247 | 2054676 | 5665 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 130295 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050523 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 45006 | 1724 | 2059431 | 4129 | Distribution Circuit | Vegetation | Tree - fell into line | 1265 | 1395902 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049942 | OH | Sus | 0 | 2023 | MAR | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44999 | 2317 | 2044960 | 2448 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 14688 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046383 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 45006 | 1239 | 2066018 | 7358 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 80938 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051865 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 45006 | 1300 | 2065822 | 5999 | Distribution Circuit | Vegetation | Tree - fell into line | 209 | 1253791 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049467 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 45006 | 1239 | 2058809 | 6063 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 84882 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049894 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 45006 | 1300 | 2063166 | 4293 | Distribution Circuit | Vegetation | Tree - fell into line | 121 | 214933 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050846 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE |  | 45006 | 1239 | 2064627 | 7399 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 51793 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051374 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 44999 | 1142 | 2037509 | 1807 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 269243 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044853 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 45006 | 1340 | 2055845 | 7452 | Distribution Circuit | Vegetation | Tree - fell into line | 214 | 523386 | Partly Cloudy-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049583 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 45006 | 1738 | 2059571 | 3039 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 57741 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049959 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 45006 | 1238 | 2061818 | 1982 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 11892 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050354 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 45006 | 1803 | 2059762 | 2745 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 164700 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050244 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 44999 | 1348 | 2041086 | 3092 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 95336 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046217 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 45006 | 1239 | 2066979 | 7486 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 209608 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052481 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 44999 | 1022 | 2035864 | 368 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 6256 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044931 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER |  | 45006 | 1305 | 2067155 | 7290 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 36450 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049864 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER |  | 45006 | 1305 | 2054948 | 1717 | Distribution Circuit | Vegetation | Tree - fell into line | 203 | 315008 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049864 | OH | Sus | 0 | 2023 | MAR | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | SWITCH |  | 45006 | 1305 | 2063594 | 6119 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 526234 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049864 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 45006 | 1305 | 2063586 | 6009 | Distribution Circuit | Vegetation | Tree - fell into line | 239 | 1436151 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049864 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER |  | 45006 | 1239 | 2065912 | 6168 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 715488 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049467 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 45006 | 934 | 2065976 | 6340 | Distribution Circuit | Vegetation | Tree - fell into line | 390 | 2449102 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051847 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 45006 | 1259 | 2065397 | 6062 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 66682 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051620 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 45006 | 1239 | 2066448 | 5856 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 322080 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052008 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 45006 | 1259 | 2066783 | 6085 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 158210 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052439 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 44999 | 1304 | 2040166 | 1392 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 36192 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046229 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 45006 | 1239 | 2056182 | 6082 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 42574 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049594 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 45006 | 1259 | 2064314 | 8761 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 34907 | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051238 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER |  | 45006 | 1239 | 2065863 | 6082 | Distribution Circuit | Vegetation | Tree - fell into line | 289 | 1757698 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049467 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | RECLOSER |  | 45006 | 1237 | 2054447 | 6078 | Distribution Circuit | Vegetation | Tree - fell into line | 293 | 1780854 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049432 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 45006 | 1239 | 2063898 | 5856 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 17568 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051041 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | RECLOSER |  | 45006 | 1239 | 2065812 | 6174 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 407484 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049467 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER |  | 45006 | 1255 | 2065919 | 7520 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 635445 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049467 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 45006 | 1239 | 2062686 | 7070 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 21210 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050653 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 44999 | 1331 | 2041628 | 3157 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 7300 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045564 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 45006 | 1239 | 2067720 | 7509 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 202743 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052673 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 45006 | 1239 | 2067178 | 7493 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 157353 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0052526 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 45006 | 1158 | 2063675 | 8668 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 466170 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0050991 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 44999 | 1253 | 2039510 | 2822 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 169320 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046024 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 45006 | 1357 | 2056185 | 1693 | Distribution Circuit | Vegetation | Tree - fell into line | 294 | 389288 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049605 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 44999 | 1104 | 2036318 | 1786 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 60724 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046305 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | JUMPER |  | 45006 | 1158 | 2067875 | 8814 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 44070 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052706 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | OTHER |  | 45006 | 1237 | 2067042 | 7523 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 246879 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052495 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 45006 | 1240 | 2066208 | 6154 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 61540 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051935 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 45006 | 1158 | 2065277 | 7572 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 219588 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051591 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | SWITCH |  | 45006 | 1239 | 2065571 | 6906 | Distribution Circuit | Vegetation | Tree - branch fell on line | 100 | 690600 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051684 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 45006 | 1237 | 2067024 | 8853 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 256789 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0052491 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 45006 | 1239 | 2067631 | 8661 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 43305 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052658 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 45006 | 1239 | 2067628 | 8661 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 43305 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052657 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | RECLOSER |  | 45006 | 1158 | 2065867 | 7664 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 176272 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049467 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 45006 | 1158 | 2065869 | 7664 | Distribution Circuit | Vegetation | Tree - branch fell on line | 200 | 1532800 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049467 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 45006 | 1158 | 2066826 | 8877 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 275187 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052452 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | JUMPER |  | 45006 | 1237 | 2067814 | 9113 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 118469 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0052691 | OH | Sus | 35431731 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45006 | 833 | 2063622 | 6290 | Distribution Circuit | Vegetation | Tree - bark fell into line | 15 | 94350 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050970 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45006 | 833 | 2063152 | 4395 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 30765 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050837 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | SWITCH |  | 45006 | 1158 | 2067905 | 8783 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 131745 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0052709 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45006 | 833 | 2064383 | 4580 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 151140 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051279 | OH | Sus | 35431731 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45006 | 833 | 2062460 | 6228 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 292716 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050584 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45006 | 833 | 2062521 | 5825 | Distribution Circuit | Vegetation | Tree - bark fell into line | 108 | 392038 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050607 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44994 | 1940 | 2029043 | 1000 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 14000 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042537 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45006 | 833 | 2064933 | 8800 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 8800 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051489 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 44994 | 1805 | 2028462 | 2510 | Distribution Circuit | Vegetation | Tree - fell into line | 635 | 764971 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042406 | OH | Sus | 0 | 2023 | MAR | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | SWITCH |  | 45006 | 833 | 2064225 | 6173 | Distribution Circuit | Vegetation | Tree - fell into line | 161 | 993853 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051214 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | TRIP-SAVER |  | 44999 | 1004 | 2035737 | 3339 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 96831 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044847 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | JUMPER |  | 45006 | 833 | 2063478 | 5107 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5107 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050941 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45006 | 833 | 2066507 | 7405 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 370250 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052022 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45006 | 833 | 2065817 | 6173 | Distribution Circuit | Vegetation | Tree - bark fell into line | 33 | 203709 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051782 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45006 | 833 | 2064930 | 7862 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 70758 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051486 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45006 | 833 | 2062120 | 6336 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 221760 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050428 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | SWITCH |  | 45006 | 1253 | 2063744 | 6047 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 44593 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049510 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45006 | 833 | 2066873 | 7646 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 206442 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0052465 | OH | Sus | 35431731 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44999 | 1216 | 2044621 | 2755 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 85405 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046167 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45006 | 833 | 2066568 | 9209 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 313106 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0052038 | OH | Sus | 35431731 | 2023 | MAR | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | SWITCH |  | 45006 | 833 | 2064984 | 6173 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 975334 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051214 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45006 | 833 | 2066485 | 8867 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 17734 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052015 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | JUMPER |  | 45006 | 833 | 2066099 | 7839 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 23517 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051893 | OH | Sus | 35431731 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 45006 | 833 | 2065788 | 6173 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 345688 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051772 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1241 | 2065021 | 6091 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 176639 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051520 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45006 | 833 | 2066420 | 8784 | Distribution Circuit | Vegetation | Tree - bark fell into line | 2 | 17568 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052002 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1241 | 2066028 | 7271 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 276298 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051872 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | JUMPER |  | 45006 | 833 | 2063461 | 6041 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 42287 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0050933 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | JUMPER |  | 45006 | 833 | 2063453 | 5825 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 139800 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050930 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44999 | 1025 | 2035896 | 1482 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 109668 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045039 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45006 | 833 | 2064683 | 6110 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 201630 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051394 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1241 | 2066022 | 6091 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6091 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051867 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45006 | 833 | 2064820 | 6217 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 603049 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051431 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45006 | 833 | 2064824 | 6217 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 242463 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051433 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45006 | 833 | 2066067 | 9345 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 149520 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051886 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 45006 | 1241 | 2054539 | 6091 | Distribution Circuit | Vegetation | Tree - fell into line | 160 | 974560 | Partly Cloudy-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049448 | OH | Sus | 0 | 2023 | MAR | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 45006 | 833 | 2064977 | 7925 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 459650 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051505 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 44999 | 1855 | 2044303 | 1418 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 188594 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045772 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45006 | 833 | 2065562 | 7925 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 206050 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051677 | OH | Sus | 35431731 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45006 | 833 | 2063398 | 6237 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 124740 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0050916 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1255 | 2064959 | 7110 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 92430 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051497 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | TRIP-SAVER |  | 45006 | 1253 | 2064736 | 7239 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 304038 | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051409 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1253 | 2065749 | 6008 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 96128 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051754 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1253 | 2065843 | 6005 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 198165 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051799 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | JUMPER |  | 45006 | 1639 | 2069142 | 9787 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 9787 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053104 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45006 | 833 | 2065565 | 9184 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 119392 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051679 | OH | Sus | 35431731 | 2023 | MAR | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 44999 | 1023 | 2046340 | 3277 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 128684 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0046394 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | JUMPER |  | 45006 | 833 | 2064716 | 6207 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 18621 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051404 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45006 | 833 | 2065864 | 9184 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 119392 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051806 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER |  | 45006 | 1630 | 2069128 | 9796 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 186520 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0053104 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1255 | 2064953 | 7110 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 398160 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051495 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45006 | 833 | 2065564 | 7925 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 388325 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051678 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1253 | 2062861 | 6047 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 18141 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050722 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER |  | 45006 | 1253 | 2065103 | 7112 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 7112 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051539 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1255 | 2062262 | 7110 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 106650 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050492 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1254 | 2062865 | 6046 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6046 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050724 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1255 | 2062789 | 7110 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 170640 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0050700 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1253 | 2064401 | 7475 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 14950 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051286 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1255 | 2067637 | 8725 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 183225 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0052659 | OH | Sus | 35431731 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1253 | 2062870 | 6047 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 72564 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050725 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1253 | 2065979 | 6004 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 126084 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051849 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER |  | 44999 | 2025 | 2044662 | 2451 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 24507 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045946 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | SWITCH |  | 45006 | 1253 | 2062873 | 6095 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 652165 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049510 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1253 | 2065367 | 6095 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 30475 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051616 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44999 | 946 | 2035567 | 3354 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10062 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044773 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1253 | 2063397 | 7527 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 22581 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050915 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1253 | 2066285 | 7179 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 358950 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051982 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1253 | 2066521 | 7656 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 344520 | Overcast-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0052024 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | SWITCH |  | 45006 | 1253 | 2064740 | 6005 | Distribution Circuit | Vegetation | Tree - fell into line | 193 | 1158965 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051410 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1253 | 2066455 | 8564 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 299740 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052012 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1253 | 2065683 | 6097 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 85358 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051725 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1253 | 2066001 | 7089 | Distribution Circuit | Vegetation | Tree - bark fell into line | 3 | 21267 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051855 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1259 | 2066169 | 7397 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 29588 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051917 | OH | Sus | 35431731 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 45006 | 1259 | 2066089 | 9864 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 480120 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051889 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1253 | 2065837 | 7159 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 250565 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051794 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1253 | 2065832 | 7162 | Distribution Circuit | Vegetation | Tree - bark fell into line | 18 | 128916 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051791 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1253 | 2065983 | 7295 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 94835 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051850 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1253 | 2066472 | 7244 | Distribution Circuit | Vegetation | Tree - branch fell on line | 64 | 463616 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052013 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45006 | 1256 | 2066056 | 7251 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 21753 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051884 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 45006 | 1253 | 2055316 | 6870 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 212970 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049511 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 45006 | 833 | 2055208 | 6407 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 172989 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049503 | OH | Sus | 0 | 2023 | MAR | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 44994 | 2025 | 2029821 | 990 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 13860 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042690 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | BIG BASIN-1102 | 82841102 | JUMPER |  | 45006 | 833 | 2067047 | 7737 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 54159 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0052496 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 45006 | 1254 | 2054691 | 3166 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 22162 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050876 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 45006 | 1308 | 2056382 | 2260 | Distribution Circuit | Vegetation | Tree - fell into line | 295 | 226922 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050620 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44999 | 1127 | 2049375 | 4518 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 189756 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047307 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER |  | 44999 | 1150 | 2042962 | 3238 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 58284 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044963 | OH | Sus | 35431722 | 2023 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER |  | 45006 | 1252 | 2062682 | 2828 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 2828 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050651 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44999 | 1058 | 2048745 | 5986 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 89790 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0047105 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER |  | 44999 | 1058 | 2048439 | 3784 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 45468 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044748 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER |  | 45006 | 1244 | 2057256 | 1454 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 42166 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 23-0049460 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER |  | 45006 | 1244 | 2060015 | 1713 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 56529 | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049460 | OH | Sus | 0 | 2023 | MAR | Yes | Multi-Fault | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44999 | 1058 | 2049133 | 4770 | Distribution Circuit | Vegetation | Tree - branch fell on line | 70 | 333900 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047226 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 44999 | 1122 | 2049058 | 6055 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 78715 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0047203 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44999 | 841 | 2049767 | 6448 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 32240 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 23-0047475 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 44994 | 2140 | 2031620 | 4050 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4050 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043260 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 45006 | 1255 | 2054562 | 1701 | Distribution Circuit | Vegetation | Tree - fell into line | 1442 | 1352916 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049460 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 44999 | 1150 | 2036460 | 4670 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1327 | 1112229 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044963 | OH | Sus | 35431722 | 2023 | MAR | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 44999 | 1032 | 2035946 | 4793 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 184066 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044703 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 45006 | 1257 | 2054820 | 3267 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 110924 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0049469 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 44999 | 1056 | 2036223 | 6313 | Distribution Circuit | Vegetation | Tree - branch fell on line | 119 | 597369 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044742 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | LOS GATOS-1101 | 82021101 | FUSE |  | 44999 | 755 | 2047045 | 4581 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 18324 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046608 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
DE ANZA | Tier 2 | LOS GATOS-1101 | 82021101 | RECLOSER |  | 44999 | 1138 | 2037499 | 4400 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 109926 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 23-0044903 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
DE ANZA | Tier 2 | SARATOGA-1106 | 83371106 | FUSE |  | 44999 | 1106 | 2042359 | 4499 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 175131 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045365 | OH | Sus | 0 | 2023 | MAR | Yes | Three Phase Fault | Yes | No
DE ANZA | Tier 2 | SARATOGA-1104 | 83371104 | FUSE |  | 44999 | 1118 | 2049326 | 4663 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 27978 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044833 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE |  | 44999 | 1213 | 2038317 | 1787 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 103646 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045312 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | RECLOSER |  | 45006 | 1351 | 2054969 | 2919 | Distribution Circuit | Equipment Failure/Involved | Overhead | 133 | 260846 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049571 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | No
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE |  | 44999 | 1148 | 2037725 | 3348 | Distribution Circuit | Equipment Failure/Involved | Overhead | 99 | 137903 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046120 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
DE ANZA | Tier 2 | SARATOGA-1107 | 83371107 | FUSE |  | 45006 | 1305 | 2060577 | 20715 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 165720 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050128 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | STELLING-1110 | 83481110 | TRIP-SAVER |  | 45006 | 1305 | 2060611 | 1697 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 72971 | Overcast-Rain;32-90 F | Conductor- Overhead | On Ground | 23-0049481 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | No
DIABLO | Tier 2 | TASSAJARA-2104 | 14662104 | RECLOSER |  | 44999 | 1303 | 2042464 | 4456 | Distribution Circuit | Vegetation | Tree - fell into line | 138 | 258728 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046666 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | TASSAJARA-2112 | 14662112 | FUSE |  | 44999 | 1137 | 2038554 | 3283 | Distribution Circuit | Equipment Failure/Involved | Overhead | 163 | 513387 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046352 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | MORAGA SUB | 1380 | RECLOSER |  | 45006 | 1617 | 2058056 | 1399 | Distribution Circuit | Vegetation | Tree - fell into line | 1762 | 897633 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050056 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | SOBRANTE-1102 | 14671102 | FUSE |  | 45006 | 1710 | 2059144 | 2582 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 205715 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050566 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
DIABLO | Tier 2 | ROSSMOOR-1101 | 14161101 | JUMPER |  | 45006 | 1048 | 2063200 | 3160 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 25280 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050859 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
DIABLO | Tier 2 | SOBRANTE-1103 | 14671103 | JUMPER |  | 45006 | 1647 | 2062862 | 3051 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 45765 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050723 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | No
DIABLO | Tier 2 | ROSSMOOR-1101 | 14161101 | FUSE |  | 45006 | 1607 | 2058089 | 2555 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 81760 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050872 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAKLAND J-1105 | 12091105 | RECLOSER |  | 44999 | 1305 | 2040006 | 2106 | Distribution Circuit | Vegetation | Tree - fell into line | 2813 | 884043 | Overcast-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045514 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAKLAND X-1106 | 12541106 | RECLOSER |  | 45006 | 1407 | 2056331 | 4536 | Distribution Circuit | Vegetation | Tree - fell into line | 513 | 1018369 | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 23-0049611 | OH | Sus | 0 | 2023 | MAR | Yes | Multi-Fault | Yes | No
EAST BAY | Tier 3 | OAKLAND X-1106 | 12541106 | RECLOSER |  | 45006 | 1626 | 2061917 | 2664 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 11088 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051393 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | PALO SECO-0401 | 13180401 | FUSE |  | 44999 | 850 | 2035370 | 309 | Distribution Circuit | Vegetation | Tree - fell into line | 307 | 87130 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044645 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | RECLOSER |  | 45006 | 1647 | 2061746 | 2150 | Distribution Circuit | Vegetation | Tree - fell into line | 293 | 548505 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050666 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | RECLOSER |  | 45006 | 1639 | 2058539 | 4366 | Distribution Circuit | Vegetation | Tree - fell into line | 685 | 2398300 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050280 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
EAST BAY | Tier 2 | OAKLAND X-1101 | 12541101 | FUSE |  | 45006 | 1622 | 2058122 | 1658 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 74610 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050794 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAKLAND K-1104 | 12101104 | RECLOSER |  | 45006 | 1647 | 2058737 | 5251 | Distribution Circuit | Equipment Failure/Involved | Overhead | 418 | 647168 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049962 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE |  | 45006 | 1610 | 2057825 | 4216 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 265608 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0050929 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE |  | 45006 | 1836 | 2061194 | 4116 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 121862 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050866 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE |  | 45006 | 1904 | 2060212 | 3020 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 105700 | Partly Cloudy;32-90 F | Pole-Wood | Broken- wire on ground | 23-0051016 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE |  | 45006 | 1954 | 2060510 | 2756 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 135044 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051043 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | FLORENCE-0401 | 12690401 | RECLOSER |  | 44999 | 1343 | 2041023 | 3148 | Distribution Circuit | Vegetation | Tree - branch fell on line | 494 | 388352 | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045702 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAKLAND K-1103 | 12101103 | FUSE |  | 45006 | 1550 | 2059576 | 4199 | Distribution Circuit | Equipment Failure/Involved | Overhead | 142 | 339898 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049960 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1103 | 12101103 | FUSE |  | 45006 | 1420 | 2056428 | 3523 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 162058 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049774 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1102 | 12101102 | FUSE |  | 45006 | 1634 | 2061449 | 4402 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 30814 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050293 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND K-1102 | 12101102 | RECLOSER |  | 45006 | 2301 | 2061291 | 2744 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1340 | 777003 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050277 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND D-1112 | 12041112 | FUSE |  | 44994 | 2125 | 2029468 | 1144 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 29744 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042613 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | RIDGE-0402 | 12840402 | OTHER |  | 45006 | 1645 | 2058611 | 2641 | Distribution Circuit | Equipment Failure/Involved | Overhead | 807 | 505633 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0050061 | OH | Sus | 0 | 2023 | MAR | Yes | Open Circuit | Yes | Yes
EAST BAY | Tier 2 | EL CERRITO G-1105 | 12501105 | RECLOSER |  | 45006 | 1844 | 2061085 | 3318 | Distribution Circuit | Vegetation | Tree - fell into line | 1996 | 2538617 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050256 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | OAK-0401 | 12600401 | FUSE |  | 45006 | 1935 | 2060393 | 4160 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 160536 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050951 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | EL CERRITO G-1105 | 12501105 | RECLOSER |  | 45006 | 1609 | 2061078 | 4215 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1076 | 440178 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050233 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | EL CERRITO G-1105 | 12501105 | FUSE |  | 45006 | 2130 | 2061041 | 1380 | Distribution Circuit | Equipment Failure/Involved | Overhead | 136 | 200960 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051017 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
FRESNO | Tier 2 | AUBERRY-1102 | 254151102 | OCB |  | 44999 | 1122 | 2036982 | 563 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1657 | 124963 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044810 | OH | Sus | 35431654 | 2023 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 44999 | 1010 | 2043726 | 475 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2850 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0045651 | OH | Sus | 0 | 2023 | MAR | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44994 | 1609 | 2027935 | 115 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 805 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0042317 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | JUMPER |  | 44999 | 1252 | 2042783 | 1555 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 9086 |  | Conductor- Overhead | Broken- wire on ground | 23-0045449 | OH | Sus | 0 | 2023 | MAR | Yes | Open Circuit | Yes | Yes
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44999 | 713 | 2035294 | 362 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 4706 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044559 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44999 | 1732 | 2043958 | 1134 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2268 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045693 | OH | Sus | 0 | 2023 | MAR | Yes | Open Circuit | Yes | Yes
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 44999 | 910 | 2035433 | 372 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 22320 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0044660 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARCIA-0401 | 43040401 | RECLOSER |  | 44994 | 1716 | 2028223 | 1508 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 13572 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042365 | OH | Sus | 0 | 2023 | MAR | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 44999 | 1803 | 2046294 | 1446 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 43380 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045718 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | OTHER |  | 44999 | 1803 | 2043982 | 1153 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 98201 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045718 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 44999 | 1058 | 2036339 | 330 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 18810 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044894 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | RECLOSER |  | 44999 | 1224 | 2038408 | 455 | Distribution Circuit | Vegetation | Tree - fell into line | 914 | 387465 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044999 | OH | Sus | 0 | 2023 | MAR | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 44994 | 1621 | 2028079 | 1061 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6366 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0042363 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 44994 | 1434 | 2027784 | 203 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 6496 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0042311 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 44994 | 1822 | 2028907 | 1018 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2036 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042455 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE |  | 44999 | 1311 | 2040093 | 425 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 2585 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045438 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 44999 | 900 | 2035483 | 520 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4680 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0044611 | OH | Sus | 0 | 2023 | MAR | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER |  | 44999 | 1203 | 2038135 | 180 | Distribution Circuit | Vegetation | Tree - fell into line | 254 | 45016 |  | Conductor- Overhead | Broken- wire on ground | 23-0044947 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE |  | 44999 | 2226 | 2044914 | 988 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 46098 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046190 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LOW GAP-1101 | 192411101 | FUSE |  | 45006 | 1128 | 2054126 | 302 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 906 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049334 | OH | Sus | 31640137 | 2023 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BRIDGEVILLE-1102 | 192461102 | OTHER |  | 45006 | 132 | 2053516 | 209 | Distribution Circuit | Equipment Failure/Involved | Overhead | 172 | 36875 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049062 | OH | Sus | 31640255 | 2023 | MAR | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | BRIDGEVILLE-1102 | 192461102 | RECLOSER |  | 44999 | 1808 | 2044049 | 1415 | Distribution Circuit | Vegetation | Tree - fell into line | 275 | 245009 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045721 | OH | Sus | 0 | 2023 | MAR | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 44994 | 2012 | 2028996 | 956 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 4511 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042513 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | MORRO BAY-1102 | 183011102 | FUSE |  | 45006 | 1853 | 2060150 | 1442 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 80750 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0050148 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
LOS PADRES | Tier 3 | TEMPLETON-2113 | 183052113 | FUSE |  | 45006 | 908 | 2053755 | 421 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 5909 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049378 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | RECLOSER |  | 44999 | 1140 | 2037502 | 392 | Distribution Circuit | Vegetation | Tree - fell into line | 372 | 66360 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044881 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE |  | 44999 | 1028 | 2035944 | 464 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4640 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0044832 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
MISSION | Tier 3 | CAYETANO-2109 | 14422109 | SWITCH |  | 44999 | 1349 | 2044446 | 1588 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 84164 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045803 | OH | Sus | 35431491 | 2023 | MAR | Yes | Line to Line | Yes | No
MISSION | Tier 3 | CAYETANO-2109 | 14422109 | FUSE |  | 44999 | 1349 | 2044470 | 4232 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 38088 | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0045808 | OH | Sus | 0 | 2023 | MAR | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 3 | ALTO-1125 | 42031125 | FUSE |  | 45006 | 1653 | 2061939 | 1464 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 17568 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050391 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | TRIP-SAVER |  | 45006 | 1602 | 2057713 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 197 | 220640 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050108 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | ALTO-1122 | 42031122 | FUSE |  | 44999 | 1201 | 2037982 | 775 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 58900 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045376 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1101 | 42011101 | OTHER |  | 44994 | 2043 | 2029318 | 970 | Distribution Circuit | Vegetation | Tree - branch fell on line | 44 | 17631 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042812 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | RECLOSER |  | 45006 | 1454 | 2056778 | 1542 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 144948 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049703 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE |  | 45006 | 1452 | 2056722 | 1373 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 57666 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049970 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE |  | 44994 | 1814 | 2028496 | 419 | Distribution Circuit | Vegetation | Tree - bark fell into line | 202 | 83225 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0042458 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | WOODACRE-1102 | 43021102 | RECLOSER |  | 44999 | 1019 | 2035862 | 573 | Distribution Circuit | Equipment Failure/Involved | Overhead | 792 | 343178 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044682 | OH | Sus | 35431693 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE |  | 44999 | 1033 | 2035887 | 1857 | Distribution Circuit | Vegetation | Tree - branch fell on line | 168 | 87641 | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045912 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE |  | 44999 | 1105 | 2036484 | 1866 | Distribution Circuit | Vegetation | Tree - fell into line | 232 | 432912 | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045294 | OH | Sus | 35431693 | 2023 | MAR | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE |  | 44994 | 1808 | 2028472 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 232 | 119248 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042480 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE |  | 45006 | 1449 | 2056700 | 1801 | Distribution Circuit | Vegetation | Tree - branch fell on line | 232 | 123658 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049891 | OH | Sus | 0 | 2023 | MAR | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | FUSE |  | 44999 | 933 | 2041405 | 1827 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 67599 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045418 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | OCB |  | 44999 | 935 | 2035558 | 2115 | Distribution Circuit | Vegetation | Tree - fell into line | 1242 | 343212 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044625 | OH | Sus | 35431693 | 2023 | MAR | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE |  | 44999 | 1322 | 2042084 | 1022 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 23506 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045315 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 44994 | 2115 | 2029405 | 1360 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 95670 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042923 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 45006 | 1508 | 2056927 | 1256 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 84152 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050041 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 44999 | 1220 | 2038474 | 1419 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 19866 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045668 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 44999 | 1348 | 2042633 | 1283 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 37207 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045741 | OH | Sus | 35431693 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE |  | 44999 | 1533 | 2044873 | 1669 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 26704 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045920 | OH | Sus | 0 | 2023 | MAR | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1109 | 102911109 | FUSE |  | 44999 | 1512 | 2042664 | 1383 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 16596 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045552 | OH | Sus | 0 | 2023 | MAR | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1107 | 102911107 | FUSE |  | 44994 | 2246 | 2029627 | 536 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 8732 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042706 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1107 | 102911107 | FUSE |  | 44999 | 1653 | 2043576 | 1527 | Distribution Circuit | Equipment Failure/Involved | Overhead | 120 | 22760 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045745 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1107 | 102911107 | RECLOSER |  | 44999 | 1659 | 2043638 | 118 | Distribution Circuit | Equipment Failure/Involved | Overhead | 243 | 28674 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045625 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1107 | 102911107 | FUSE |  | 44999 | 1622 | 2043233 | 1538 | Distribution Circuit | Environmental/External | Flood/Erosion | 29 | 7698 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045777 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER |  | 44999 | 1614 | 2043196 | 1361 | Distribution Circuit | Vegetation | Tree - fell into line | 458 | 594194 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045538 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | WYANDOTTE-1103 | 102911103 | RECLOSER |  | 44999 | 1604 | 2043133 | 294 | Distribution Circuit | Vegetation | Tree - fell into line | 442 | 129948 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045523 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | CLARK ROAD-1102 | 103091102 | RECLOSER |  | 44999 | 1726 | 2043773 | 1086 | Distribution Circuit | Vegetation | Tree - fell into line | 262 | 269412 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045669 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1103 | 102831103 | FUSE |  | 44999 | 1622 | 2043283 | 1510 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 43859 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045580 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1103 | 102831103 | OTHER |  | 45006 | 844 | 2053802 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 2190 | 26118 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049181 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 3 | BIG BEND-1101 | 103751101 | OTHER |  | 45006 | 643 | 2053576 | 272 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1632 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0049162 | OH | Sus | 0 | 2023 | MAR | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 2 | SYCAMORE CREEK-1111 | 102971111 | RECLOSER |  | 44999 | 1628 | 2043307 | 1722 | Distribution Circuit | Equipment Failure/Involved | Overhead | 533 | 833512 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045569 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | COTTONWOOD-1102 | 102931102 | OTHER |  | 44994 | 2227 | 2030600 | 1150 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 73600 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0042891 | OH | Sus | 0 | 2023 | MAR | Yes | Open Circuit | Yes | Yes
NORTH VALLEY | Tier 2 | OREGON TRAIL-1103 | 103521103 | RECLOSER |  | 44994 | 1916 | 2028784 | 1601 | Distribution Circuit | Equipment Failure/Involved | Overhead | 601 | 186447 | Overcast-Fog-Heavy Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0042462 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | RECLOSER |  | 44994 | 1955 | 2029160 | 163 | Distribution Circuit | Equipment Failure/Involved | Overhead | 484 | 75757 | Overcast-Heavy Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 23-0042498 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE |  | 44994 | 1846 | -2029160 | 1306 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 58770 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042682 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1101 | 103381101 | TRIP-SAVER |  | 44994 | 1858 | 2028764 | 1525 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 111586 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042505 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | STILLWATER-1101 | 103561101 | RECLOSER |  | 44994 | 2101 | 2029391 | 2472 | Distribution Circuit | Company Initiated | Other Circuits | 33 | 81576 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042565 | OH | Sus | 0 | 2023 | MAR | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE |  | 44994 | 1844 | 2028635 | 4099 | Distribution Circuit | Vegetation | Tree - fell into line | 199 | 666560 | Overcast-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0042569 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | ANTLER-1101 | 103271101 | FUSE |  | 44994 | 2101 | 2031396 | 2399 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 67172 | Overcast-Fog-Snow;32-90 F | Pole-Wood | Broken- wire on ground | 23-0043203 | OH | Sus | 0 | 2023 | MAR | Yes | Open Circuit | Yes | No
NORTH VALLEY | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE |  | 44994 | 1851 | 2028684 | 7387 | Distribution Circuit | Environmental/External | Ice or snow | 32 | 236384 | Overcast-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 23-0043765 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | TRIP-SAVER |  | 45006 | 1327 | 2057304 | 1640 | Distribution Circuit | Vegetation | Tree - branch fell on line | 107 | 175480 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049768 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | JUMPER |  | 45006 | 1620 | 2062671 | 2856 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 19992 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050643 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | SWITCH |  | 44999 | 1200 | 2044491 | 3299 | Distribution Circuit | Vegetation | Tree - fell into line | 418 | 253226 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045813 | OH | Sus | 0 | 2023 | MAR | Yes | Open Circuit | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | RECLOSER |  | 45006 | 1303 | 2055024 | 5825 | Distribution Circuit | Vegetation | Tree - fell into line | 448 | 2074343 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049568 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 44999 | 919 | 2035470 | 4804 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 19216 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0044962 | OH | Sus | 0 | 2023 | MAR | Yes | Multi-Fault | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 44994 | 1719 | 2028231 | 511 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 14819 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0042422 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER |  | 44999 | 1124 | 2044450 | 4514 | Distribution Circuit | Equipment Failure/Involved | Overhead | 60 | 237537 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045804 | OH | Sus | 0 | 2023 | MAR | Yes | Open Circuit | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 45006 | 1337 | 2066245 | 5998 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 413862 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0051953 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1104 | 24251104 | TRIP-SAVER |  | 44999 | 1013 | 2035773 | 3328 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 56576 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046301 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1104 | 24251104 | FUSE |  | 45006 | 1343 | 2062310 | 1729 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 48412 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050521 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | EMERALD LAKE-0401 | 24080401 | FUSE |  | 44999 | 1723 | 2043762 | 2815 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 222866 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046927 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | LAS PULGAS-0401 | 24120401 | JUMPER |  | 45006 | 1602 | 2059986 | 1397 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 26543 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050028 | OH | Sus | 0 | 2023 | MAR | Yes | Open Circuit | Yes | No
PENINSULA | Tier 2 | SAN CARLOS-1104 | 24181104 | RECLOSER |  | 44999 | 1153 | 2037749 | 3513 | Distribution Circuit | Vegetation | Tree - bark fell into line | 192 | 322688 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046314 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1101 | 24101101 | SWITCH |  | 44994 | 1730 | 2028262 | 2567 | Distribution Circuit | Vegetation | Tree - bark fell into line | 20 | 51340 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0042605 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | No
PENINSULA | Tier 2 | PACIFICA-1103 | 22811103 | RECLOSER |  | 45006 | 1013 | 2056745 | 4749 | Distribution Circuit | Vegetation | Tree - fell into line | 771 | 1274876 | Overcast-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0049693 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
SACRAMENTO | Tier 2 | VACAVILLE-1104 | 63601104 | FUSE |  | 44994 | 2232 | 2029598 | 2288 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 43472 | Clear;32-90F | Crossarm- Wood | Broken- wire on ground | 23-0043247 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 3 | DOBBINS-1101 | 153741101 | FUSE |  | 44999 | 1437 | 2042432 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2560 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045549 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
SAN JOSE | Tier 2 | MORGAN HILL-2105 | 83242105 | FUSE |  | 44999 | 1306 | 2043927 | 1854 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 3708 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045684 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
SAN JOSE | Tier 2 | MORGAN HILL-2111 | 83242111 | FUSE |  | 44999 | 1257 | 2046370 | 1698 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 54336 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046407 | OH | Sus | 0 | 2023 | MAR | Yes | Three Phase Fault | Yes | No
SAN JOSE | Tier 2 | MILPITAS-1109 | 82831109 | FUSE |  | 44999 | 1234 | 2038991 | 3429 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 75438 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0047222 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
SAN JOSE | Tier 2 | MILPITAS-1109 | 82831109 | FUSE |  | 45006 | 1922 | 2060315 | 1700 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 37400 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0050448 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | FUSE |  | 44999 | 1216 | 2038331 | 1851 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9255 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045519 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 44999 | 1041 | 2036029 | 1780 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 154860 | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045284 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 44999 | 1145 | 2038083 | 508 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2540 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044936 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 44999 | 1522 | 2042750 | 1651 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 203073 | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045565 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 44999 | 1129 | 2037159 | 209 | Distribution Circuit | Vegetation | Tree - fell into line | 190 | 39710 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0045110 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER |  | 44999 | 1132 | 2037179 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 410 | 108875 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044842 | OH | Sus | 0 | 2023 | MAR | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | CLARKSVILLE-2104 | 153612104 | FUSE |  | 44999 | 1410 | 2041834 | 1211 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 16051 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045594 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1110 | 153081110 | FUSE |  | 44999 | 1209 | 2041896 | 1875 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 18750 | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045344 | OH | Sus | 0 | 2023 | MAR | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 44999 | 1808 | 2043997 | 1245 | Distribution Circuit | Vegetation | Tree - fell into line | 1041 | 92145 | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045724 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 44999 | 1623 | 2043253 | 1532 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 32172 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045716 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE |  | 44999 | 1208 | 2038155 | 276 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2208 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045246 | OH | Sus | 0 | 2023 | MAR | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | BELL-1109 | 152701109 | FUSE |  | 44999 | 1549 | 2043006 | 1406 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 18278 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045774 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1110 | 152691110 | RECLOSER |  | 44999 | 1401 | 2041735 | 1733 | Distribution Circuit | Vegetation | Tree - fell into line | 2707 | 792668 | Overcast-Drizzle-Strong Winds;32-90 F | Crossarm- Steel | Broken- wire on ground | 23-0045281 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 45006 | 1847 | 2060046 | 1045 | Distribution Circuit | 3rd Party | Vehicle | 142 | 148390 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0050086 | OH | Sus | 0 | 2023 | MAR | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | FUSE |  | 44999 | 1616 | 2043189 | 1521 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 80613 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045643 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44994 | 1257 | 2027539 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 640 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0042145 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | JUMPER |  | 44994 | 1300 | 2027890 | 3135 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 9405 | Clear;32-90F | Pole-Wood | Broken- wire on ground | 23-0042349 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 44994 | 1711 | 2028301 | 2729 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 40935 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0043052 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
SIERRA | Tier 3 | GRASS VALLEY-1101 | 152031101 | FUSE |  | 44994 | 1048 | 2027399 | 1722 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 36162 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042052 | OH | Sus | 0 | 2023 | MAR | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE |  | 44999 | 1600 | 2043150 | 1378 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8268 | Overcast-Fog-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045617 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER |  | 44994 | 2102 | 2030062 | 2242 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 11906 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042909 | OH | Sus | 0 | 2023 | MAR | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE |  | 44999 | 1419 | 2042006 | 1662 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 8310 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045630 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | RECLOSER |  | 44999 | 1714 | 2043753 | 1497 | Distribution Circuit | Vegetation | Tree - fell into line | 262 | 348214 | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 23-0045662 | OH | Sus | 0 | 2023 | MAR | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE |  | 44999 | 1405 | 2041765 | 2736 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 10096 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045433 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 44994 | 1920 | 2028967 | 983 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 37354 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0042484 | OH | Sus | 0 | 2023 | MAR | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER |  | 44999 | 1142 | 2037645 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 31266 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044932 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | FUSE |  | 45006 | 2105 | 2060831 | 1089 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 140671 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0050242 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | DUNBAR-1101 | 43071101 | RECLOSER |  | 44999 | 2138 | 2044719 | 921 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 93021 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045906 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | No
SONOMA | Tier 3 | DUNBAR-1101 | 43071101 | FUSE |  | 44999 | 2048 | 2046175 | 1077 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8616 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0046333 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 44999 | 1132 | 2037209 | 452 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 5876 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045379 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | JUMPER |  | 44994 | 2000 | 2029346 | 792 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 792 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0042566 | OH | Sus | 0 | 2023 | MAR | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE |  | 44999 | 957 | 2042169 | 1646 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6584 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045325 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | TRIP-SAVER |  | 44999 | 1022 | 2036689 | 640 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 28160 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0045056 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | RECLOSER |  | 44999 | 945 | 2035725 | 120 | Distribution Circuit | Vegetation | Tree - bark fell into line | 27 | 3240 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044670 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | JUMPER |  | 44999 | 1002 | 2037349 | 324 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 648 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044844 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER |  | 44994 | 2253 | 2029650 | 1056 | Distribution Circuit | Environmental/External | Flood/Erosion | 37 | 38608 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 23-0042654 | OH | Sus | 0 | 2023 | MAR | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE |  | 44999 | 618 | 2035193 | 743 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 23033 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0044508 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MIRABEL-1102 | 42091102 | FUSE |  | 44999 | 1520 | 2042765 | 401 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 2601 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045447 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | JUMPER |  | 45006 | 2234 | 2062466 | 1299 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 10920 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on object | 23-0050587 | OH | Sus | 0 | 2023 | MAR | Yes | Open Circuit | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | OTHER |  | 45006 | 1345 | 2056947 | 237 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 237 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049718 | OH | Sus | 0 | 2023 | MAR | Yes | Open Circuit | Yes | Yes
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER |  | 44999 | 324 | 2035161 | 910 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 35490 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044467 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | Valley Springs 1101 | 168891101 | FUSE |  | 44994 | 1552 | 2027953 | 269 | Distribution Circuit | Equipment Failure/Involved | Overhead | 498 | 46830 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0042304 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | ELECTRA-1102 | 162161102 | FUSE |  | 45006 | 1700 | 2058895 | 359 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 553 | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049990 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 44999 | 1108 | 2036739 | 1665 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 99900 | Overcast-Drizzle;32-90 F | Crossarm- Wood | Broken- wire on ground | 23-0045411 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | MARTELL-1101 | 163011101 | FUSE |  | 44999 | 918 | 2035466 | 298 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 25330 | Clear;32-90F | Conductor- Overhead | Broken- wire on ground | 23-0044675 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 44999 | 1000 | 2035666 | 362 | Distribution Circuit | Vegetation | Tree - branch fell on line | 335 | 121270 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0044775 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | OAKHURST-1103 | 254421103 | FUSE |  | 44994 | 54 | 2027145 | 585 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 19890 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0041906 | OH | Sus | 0 | 2023 | MAR | Yes | Force Out | Yes | Yes
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 45006 | 1045 | 2054004 | 459 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 19278 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0049375 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | OCB |  | 44999 | 1527 | 2042778 | 178 | Distribution Circuit | 3rd Party | Vehicle | 3105 | 342827 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0045455 | OH | Sus | 0 | 2023 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE |  | 45178 | 1516 | 2214289 | 1519 | Distribution Circuit | Environmental/External | Lightning | 107 | 162533 | Partly Cloudy-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0114571 | OH | Sus | 0 | 2023 | SEP | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER |  | 45178 | 1749 | 2213994 | 35 | Distribution Circuit | Company Initiated | Coordination failure | 847 | 29645 | Partly Cloudy-Lightning;32-90 F | Conductor- Overhead | Broken- wire on ground | 23-0114492 | OH | Sus | 0 | 2023 | SEP | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | FUSE |  | 45640 | 715 | 2662915 | 4723 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 108629 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146574 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | FUSE |  | 45640 | 657 | 2663358 | 6203 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 12406 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0146695 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | HATTON-1101 | 182291101 | FUSE |  | 45640 | 1053 | 2660763 | 1886 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 182942 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146117 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | RECLOSER |  | 45640 | 656 | 2654173 | 7152 | Distribution Circuit | Vegetation | Tree - fell into line | 298 | 300965 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145240 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | LAURELES-1111 | 182371111 | RECLOSER |  | 45640 | 730 | 2654634 | 3104 | Distribution Circuit | Vegetation | Tree - fell into line | 839 | 1449247 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145213 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 45640 | 622 | 2659107 | 3516 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 31644 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145697 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 45640 | 629 | 2658690 | 681 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 27921 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145635 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | OCB |  | 45640 | 629 | 2653666 | 3502 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2068 | 1142896 | Overcast-Drizzle-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0145143 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 45640 | 635 | 2659446 | 3425 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 44525 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145668 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | JUMPER |  | 45640 | 653 | 2658909 | 3397 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 74734 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145668 | OH | Sus | 0 | 2024 | DEC | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE |  | 45640 | 635 | 2658960 | 1990 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 75620 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145679 | OH | Sus | 0 | 2024 | DEC | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 45640 | 1007 | 2657072 | 3170 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 96955 | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0146508 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 45640 | 1011 | 2657119 | 2977 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 47632 | Partly Cloudy-Fog;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0146528 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 45640 | 727 | 2654374 | 1977 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 45021 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145429 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE |  | 45640 | 631 | 2653409 | 1994 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 169490 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146256 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE |  | 45640 | 619 | 2660623 | 3716 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 196948 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0146085 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE |  | 45640 | 843 | 2655537 | 3425 | Distribution Circuit | Vegetation | Tree - fell into line | 103 | 202121 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145733 | OH | Sus | 35605675 | 2024 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | OTHER |  | 45640 | 713 | 2654176 | 5479 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6248 | 1444579 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145318 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 45640 | 844 | 2661072 | 2045 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 44961 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146195 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE |  | 45640 | 1031 | 2657603 | 3054 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 18324 | Overcast-Fog-Drizzle;32-90 F | Pole-Wood | Broken- wire on ground | 24-0146427 | OH | Sus | 35605675 | 2024 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 45640 | 820 | 2661444 | 1975 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 41475 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146262 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2107 | 83622107 | FUSE |  | 45640 | 635 | 2658868 | 1855 | Distribution Circuit | Vegetation | Tree - branch fell on line | 60 | 77436 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145665 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | OTHER |  | 45640 | 650 | 2657781 | 625 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 40338 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145495 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER |  | 45640 | 1422 | 2659699 | 1339 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 2678 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146123 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 45640 | 1403 | 2659617 | 1319 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 16026 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146136 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2105 | 83692105 | SWITCH |  | 45640 | 2010 | 2660417 | 2520 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 25200 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146006 | OH | Sus | 35605675 | 2024 | DEC | Yes | Force Out | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 45640 | 628 | 2653383 | 3453 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 236870 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146355 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE |  | 45640 | 644 | 2653903 | 1687 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 18557 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145725 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | TRIP-SAVER |  | 45640 | 912 | 2656237 | 3320 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 207832 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146409 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER |  | 45640 | 645 | 2653920 | 2124 | Distribution Circuit | Vegetation | Tree - branch fell on line | 136 | 250920 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145811 | OH | Sus | 0 | 2024 | DEC | Yes | Open Circuit | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 45640 | 633 | 2654202 | 4703 | Distribution Circuit | Vegetation | Tree - fell into line | 789 | 630832 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145200 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 45640 | 1724 | 2660330 | 2808 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 41816 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146421 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 45640 | 630 | 2653818 | 1767 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 111718 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145316 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 45640 | 635 | 2654147 | 3416 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 113448 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146259 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45640 | 627 | 2653839 | 3668 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 11004 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0146479 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45640 | 635 | 2661251 | 3346 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 127148 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146217 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | JUMPER |  | 45640 | 651 | 2661673 | 3261 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 41367 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146327 | OH | Sus | 0 | 2024 | DEC | Yes | None | Yes | Yes
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 45640 | 612 | 2653232 | 1898 | Distribution Circuit | Vegetation | Tree - fell into line | 174 | 330252 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145117 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 45640 | 623 | 2661180 | 2075 | Distribution Circuit | Equipment Failure/Involved | Overhead | 131 | 289772 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146199 | OH | Sus | 0 | 2024 | DEC | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45640 | 623 | 2662051 | 3523 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 116259 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146426 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45640 | 635 | 2661817 | 3559 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 32031 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146358 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN SUB | 8284 | OCB |  | 45640 | 637 | 2653600 | 2320 | Distribution Circuit | Vegetation | Tree - fell into line | 933 | 1967004 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145139 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 45640 | 638 | 2659839 | 2181 | Distribution Circuit | Vegetation | Tree - fell into line | 531 | 1158111 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145858 | OH | Sus | 0 | 2024 | DEC | Yes | None | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | SWITCH |  | 45640 | 1703 | 2660250 | 126 | Distribution Circuit | Vegetation | Tree - branch fell on line | 132 | 13592 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145146 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER |  | 45640 | 649 | 2653738 | 612 | Distribution Circuit | Vegetation | Tree - fell into line | 290 | 70203 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145146 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 45640 | 641 | 2659609 | 789 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 17358 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145151 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 45640 | 642 | 2654743 | 1940 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 23280 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145151 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 45640 | 642 | 2659236 | 750 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 21000 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145151 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
DIABLO | Tier 2 | ALHAMBRA-1105 | 14101105 | FUSE |  | 45640 | 1050 | 2658030 | 1622 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 9354 | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145955 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | SAN LEANDRO-1109 | 13111109 | FUSE |  | 45640 | 1013 | 2657171 | 503 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 29174 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145614 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
EAST BAY | Tier 3 | OAKLAND X-1104 | 12541104 | RECLOSER |  | 45640 | 1013 | 2657166 | 1878 | Distribution Circuit | Vegetation | Tree - fell into line | 711 | 99235 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145443 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
EAST BAY | Tier 2 | EL CERRITO G-1105 | 12501105 | FUSE |  | 45640 | 1358 | 2659592 | 387 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 8127 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145772 | OH | Sus | 0 | 2024 | DEC | Yes | Force Out | Yes | No
EAST BAY | Tier 2 | EL CERRITO G-1105 | 12501105 | RECLOSER |  | 45640 | 1505 | 2659823 | 313 | Distribution Circuit | Equipment Failure/Involved | Overhead | 594 | 185922 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146059 | OH | Sus | 0 | 2024 | DEC | Yes | Force Out | Yes | No
HUMBOLDT | Tier 2 | REDBUD-1102 | 43191102 | OTHER |  | 45640 | 1227 | 2658883 | 274 | Distribution Circuit | Vegetation | Tree - fell into line | 485 | 7050 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145715 | OH | Sus | 0 | 2024 | DEC | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 45640 | 922 | 2656452 | 475 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2375 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145547 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOPLAND-1101 | 42251101 | OTHER |  | 45640 | 450 | 2653922 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 306 | 7214 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145158 | OH | Sus | 0 | 2024 | DEC | Yes | Open Circuit | Yes | Yes
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | JUMPER |  | 45640 | 829 | 2655150 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4630 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145434 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE |  | 45640 | 940 | 2656811 | 298 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 3278 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145591 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE |  | 45640 | 939 | 2656579 | 445 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 4895 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145694 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE |  | 45640 | 927 | 2656434 | 293 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 6895 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145525 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2110 | 183052110 | FUSE |  | 45640 | 924 | 2656522 | 316 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 5372 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145464 | OH | Sus | 0 | 2024 | DEC | Yes | Three Phase Fault | Yes | No
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | FUSE |  | 45640 | 913 | 2656272 | 1993 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 191328 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0146070 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | ALTO-1124 | 42031124 | FUSE |  | 45640 | 1348 | 2659547 | 1717 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 180285 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145928 | OH | Sus | 0 | 2024 | DEC | Yes | Force Out | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE |  | 45640 | 1154 | 2658650 | 1758 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 45708 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145627 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | SAN RAFAEL-1109 | 42011109 | RECLOSER |  | 45640 | 1031 | 2657869 | 2990 | Distribution Circuit | Vegetation | Tree - fell into line | 1425 | 458526 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145537 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | OCB |  | 45640 | 935 | 2656596 | 3282 | Distribution Circuit | Vegetation | Tree - fell into line | 3036 | 656694 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145414 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE |  | 45640 | 925 | 2656408 | 3376 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 33760 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146302 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 45640 | 11 | 2652927 | 3602 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 62114 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145199 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER |  | 45640 | 934 | 2656481 | 3417 | Distribution Circuit | Vegetation | Tree - fell into line | 765 | 1947051 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145388 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | PUEBLO-1104 | 43291104 | FUSE |  | 45640 | 934 | 2656581 | 1661 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 61457 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145515 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | SILVERADO-2102 | 43432102 | RECLOSER |  | 45640 | 1157 | 2658584 | 509 | Distribution Circuit | Equipment Failure/Involved | Overhead | 131 | 30823 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145686 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | BANGOR-1101 | 103191101 | RECLOSER |  | 45640 | 811 | 2654849 | 1651 | Distribution Circuit | Equipment Failure/Involved | Overhead | 425 | 419913 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145246 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER |  | 45640 | 813 | 2654856 | 3139 | Distribution Circuit | Equipment Failure/Involved | Overhead | 363 | 919461 | Overcast-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145892 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CLARK ROAD-1102 | 103091102 | RECLOSER |  | 45640 | 827 | 2655264 | 707 | Distribution Circuit | Equipment Failure/Involved | Overhead | 163 | 94721 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145292 | OH | Sus | 0 | 2024 | DEC | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | FUSE |  | 45640 | 40 | 2652760 | 731 | Distribution Circuit | Vegetation | Tree - fell into line | 165 | 120615 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145049 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | RECLOSER |  | 45640 | 146 | 2652835 | 815 | Distribution Circuit | Vegetation | Tree - fell into line | 542 | 396143 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145039 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1102 | 103381102 | FUSE |  | 45640 | 1934 | 2660525 | 142 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 568 | Clear-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0146072 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 45640 | 556 | 2656334 | 1826 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 100430 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145091 | OH | Sus | 46416356 | 2024 | DEC | Yes | None | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER |  | 45640 | 607 | 2653256 | 1800 | Distribution Circuit | Equipment Failure/Involved | Overhead | 314 | 226814 | Strong Winds-Heavy Rain | Conductor- Overhead | Broken- wire on ground | 24-0145138 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER |  | 45640 | 601 | 2653196 | 2337 | Distribution Circuit | Vegetation | Tree - fell into line | 341 | 733163 | Strong Winds-Heavy Rain | Conductor- Overhead | Broken- wire on ground | 24-0145133 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
SAN JOSE | Tier 2 | MORGAN HILL-2105 | 83242105 | RECLOSER |  | 45640 | 850 | 2655933 | 1734 | Distribution Circuit | Equipment Failure/Involved | Overhead | 164 | 208369 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145333 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
SAN JOSE | Tier 3 | MORGAN HILL-2111 | 83242111 | RECLOSER |  | 45640 | 838 | 2655380 | 650 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 11700 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145677 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 45640 | 1214 | 2659714 | 1516 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 34868 | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145816 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 45640 | 902 | 2656035 | 717 | Distribution Circuit | Vegetation | Tree - branch fell on line | 36 | 21068 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145493 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 45640 | 1207 | 2658677 | 1346 | Distribution Circuit | Vegetation | Tree - bark fell into line | 21 | 28266 | Overcast-Fog-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145834 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | FUSE |  | 45640 | 1157 | 2658363 | 373 | Distribution Circuit | Vegetation | Tree - bark fell into line | 18 | 6714 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145710 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 45640 | 912 | 2656368 | 1463 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 103873 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145946 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | DIAMOND SPRINGS-1103 | 152261103 | FUSE |  | 45640 | 1147 | 2658508 | 1478 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 81845 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145791 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER |  | 45640 | 1025 | 2657539 | 483 | Distribution Circuit | Vegetation | Tree - fell into line | 410 | 54815 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145471 | OH | Sus | 0 | 2024 | DEC | Yes | Multi-Fault | Yes | No
SIERRA | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE |  | 45640 | 1209 | 2658698 | 1514 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 26061 | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145879 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE |  | 45640 | 1129 | 2659360 | 2659 | Distribution Circuit | Vegetation | Tree - fell into line | 4870 | 2070129 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145756 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE |  | 45640 | 1138 | 2658420 | 1687 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 11004 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145927 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE |  | 45640 | 37 | 2652746 | 769 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5383 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145048 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 45640 | 828 | 2655156 | 536 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2680 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145638 | OH | Sus | 0 | 2024 | DEC | Yes | Force Out | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 45640 | 1215 | 2658779 | 344 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1720 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145774 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE |  | 45640 | 1140 | 2658510 | 1620 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4860 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146075 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 45640 | 1218 | 2658814 | 1394 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 79458 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145979 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | FUSE |  | 45640 | 445 | 2652959 | 556 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7228 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145106 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE |  | 45640 | 1352 | 2659574 | 1474 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8844 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145976 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | FUSE |  | 45640 | 1201 | 2659637 | 1389 | Distribution Circuit | Vegetation | Tree - fell into line | 905 | 113816 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145787 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HIGGINS-1107 | 152691107 | JUMPER |  | 45640 | 1153 | 2659630 | 1463 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 3432 | Overcast-Fog-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145781 | OH | Sus | 0 | 2024 | DEC | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | JUMPER |  | 45640 | 1205 | 2660003 | 280 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 840 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145901 | OH | Sus | 0 | 2024 | DEC | Yes | Open Circuit | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER |  | 45640 | 202 | 2652870 | 961 | Distribution Circuit | Vegetation | Tree - fell into line | 990 | 339382 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145044 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | TRIP-SAVER |  | 45640 | 728 | 2654378 | 743 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 105506 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145252 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER |  | 45640 | 820 | 2655015 | 442 | Distribution Circuit | Vegetation | Tree - fell into line | 1239 | 117978 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145281 | OH | Sus | 0 | 2024 | DEC | Yes | Multi-Fault | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 45640 | 950 | 2659444 | 684 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 16416 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145754 | OH | Sus | 0 | 2024 | DEC | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 45640 | 938 | 2659453 | 1988 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3976 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145757 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 45640 | 950 | 2660181 | 1810 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 32580 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145945 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | JUMPER |  | 45640 | 1246 | 2659727 | 2850 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 8550 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145821 | OH | Sus | 0 | 2024 | DEC | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | RECLOSER |  | 45640 | 950 | 2656927 | 288 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 29088 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145418 | OH | Sus | 0 | 2024 | DEC | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 45640 | 1011 | 2661384 | 2145 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 27885 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145491 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | TRIP-SAVER |  | 45640 | 1010 | 2658435 | 1479 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 94656 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145585 | OH | Sus | 0 | 2024 | DEC | Yes | Force Out | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 45640 | 1011 | 2659580 | 1631 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 57085 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145766 | OH | Sus | 0 | 2024 | DEC | Yes | None | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER |  | 45640 | 1011 | 2657317 | 1576 | Distribution Circuit | Vegetation | Tree - fell into line | 401 | 215979 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145491 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 45640 | 1128 | 2658345 | 1720 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 189200 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145713 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER |  | 45640 | 559 | 2653182 | 775 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 18937 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145105 | OH | Sus | 0 | 2024 | DEC | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER |  | 45640 | 1025 | 2657454 | 498 | Distribution Circuit | Vegetation | Tree - branch fell on line | 234 | 89492 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145497 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1701 | 163451701 | OTHER |  | 45640 | 914 | 2659818 | 474 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 474 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145848 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE |  | 45640 | 831 | 2659262 | 1666 | Distribution Circuit | Vegetation | Tree - fell into line | 177 | 118148 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145297 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER |  | 45640 | 1914 | 2660505 | 1323 | Distribution Circuit | Vegetation | Tree - fell into line | 553 | 181571 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146042 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1701 | 162821701 | FUSE |  | 45640 | 904 | 2660356 | 1831 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 38451 | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0146093 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 45640 | 828 | 2655125 | 1831 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 23948 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145880 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 45640 | 825 | 2661093 | 2005 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 42105 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145279 | OH | Sus | 0 | 2024 | DEC | Yes | Open Circuit | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER |  | 45640 | 825 | 2660277 | 1990 | Distribution Circuit | Vegetation | Tree - fell into line | 213 | 313418 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145279 | OH | Sus | 0 | 2024 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER |  | 45640 | 719 | 2654309 | 1888 | Distribution Circuit | Vegetation | Tree - fell into line | 1222 | 881959 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145175 | OH | Sus | 0 | 2024 | DEC | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 45640 | 651 | 2653749 | 0 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 12504 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 24-0145249 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | JUMPER |  | 45640 | 811 | 2654826 | 576 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 9216 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145406 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | Yes
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 45640 | 719 | 2658839 | 1706 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 54592 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145175 | OH | Sus | 0 | 2024 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 45640 | 727 | 2658192 | 763 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 95375 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145303 | OH | Sus | 0 | 2024 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER |  | 45640 | 727 | 2659825 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 202 | 103424 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145303 | OH | Sus | 0 | 2024 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 45640 | 835 | 2655300 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 8460 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145408 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 45640 | 1845 | 2660458 | 1418 | Distribution Circuit | Equipment Failure/Involved | Overhead | 118 | 167324 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146061 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 45640 | 823 | 2655055 | 1524 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 20369 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145773 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE |  | 45640 | 741 | 2659831 | 2001 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 150075 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145853 | OH | Sus | 0 | 2024 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 45640 | 1834 | 2661088 | 1157 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 55536 | Overcast-Snow;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146225 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | SWITCH |  | 45640 | 824 | 2657588 | 0 | Distribution Circuit | Vegetation | Tree - fell into line | 1405 | 202039 | Overcast-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0145310 | OH | Sus | 0 | 2024 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 45640 | 723 | 2660374 | 1944 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 27830 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145298 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | RECLOSER |  | 45640 | 827 | 2655183 | 1750 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 68116 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145286 | OH | Sus | 0 | 2024 | DEC | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER |  | 45640 | 727 | 2655413 | 1677 | Distribution Circuit | Equipment Failure/Involved | Overhead | 594 | 431514 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145298 | OH | Sus | 0 | 2024 | DEC | Yes | Force Out | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 45640 | 727 | 2659777 | 925 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 15725 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145303 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 45640 | 2345 | 2660783 | 0 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 12597 | Partly Cloudy-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0146236 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | MARTELL-1101 | 163011101 | JUMPER |  | 45640 | 828 | 2660042 | 1527 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4581 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145319 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | SALT SPRINGS-2102 | 163692102 | RECLOSER |  | 45640 | 745 | 2655077 | 2063 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2020 | 1953206 | Overcast-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145509 | OH | Sus | 0 | 2024 | DEC | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER |  | 45640 | 827 | 2655323 | 1791 | Distribution Circuit | Vegetation | Tree - branch fell on line | 75 | 108425 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145344 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE |  | 45640 | 829 | 2655180 | 1747 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 216628 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146100 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | MARTELL-1101 | 163011101 | FUSE |  | 45640 | 841 | 2657561 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 13386 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145723 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER |  | 45640 | 722 | 2654320 | 522 | Distribution Circuit | Vegetation | Tree - branch fell on line | 245 | 51210 | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0145179 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | PINE GROVE-1102 | 163751102 | SWITCH |  | 45640 | 756 | 2657987 | 674 | Distribution Circuit | Vegetation | Tree - fell into line | 246 | 165804 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145217 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | PINE GROVE-1102 | 163751102 | JUMPER |  | 45640 | 756 | 2659155 | 630 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5670 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145217 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1101 | 163201101 | FUSE |  | 45640 | 727 | 2661041 | 2120 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 16258 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145294 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | FUSE |  | 45640 | 723 | 2660241 | 1663 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 21619 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145294 | OH | Sus | 0 | 2024 | DEC | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | OLETA-1102 | 163541102 | FUSE |  | 45640 | 842 | 2655505 | 1780 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 79225 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145965 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 45640 | 907 | 2656249 | 1618 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 14562 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146198 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE |  | 45640 | 902 | 2656036 | 2000 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 12000 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145920 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MARIPOSA-2101 | 254452101 | RECLOSER |  | 45640 | 900 | 2656125 | 1845 | Distribution Circuit | Vegetation | Tree - fell into line | 202 | 342613 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145341 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER |  | 45640 | 837 | 2655481 | 2048 | Distribution Circuit | Vegetation | Tree - fell into line | 544 | 701226 | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0145320 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER |  | 45640 | 1406 | 2658466 | 1509 | Distribution Circuit | Equipment Failure/Involved | Overhead | 229 | 34969 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145784 | OH | Sus | 0 | 2024 | DEC | Yes | Force Out | Yes | Yes
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER |  | 45640 | 831 | 2655404 | 836 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 56808 | Overcast-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0145295 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | CURTIS-1703 | 163351703 | FUSE |  | 45640 | 805 | 2655053 | 1852 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 24076 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145644 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | FUSE |  | 45640 | 639 | 2653535 | 476 | Distribution Circuit | Vegetation | Tree - branch fell on line | 148 | 70448 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145243 | OH | Sus | 0 | 2024 | DEC | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1705 | 163351705 | FUSE |  | 45640 | 738 | 2654525 | 1932 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 24240 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145958 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER |  | 45640 | 808 | 2654780 | 1829 | Distribution Circuit | Equipment Failure/Involved | Overhead | 387 | 59169 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145239 | OH | Sus | 0 | 2024 | DEC | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | RACETRACK-1703 | 163761703 | RECLOSER |  | 45640 | 729 | 2654401 | 1774 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3116 | 534947 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145188 | OH | Sus | 0 | 2024 | DEC | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | FUSE |  | 45640 | 802 | 2654736 | 479 | Distribution Circuit | Equipment Failure/Involved | Overhead | 232 | 108712 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145582 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | FUSE |  | 45640 | 2211 | 2660707 | 1065 | Distribution Circuit | Vegetation | Tree - fell into line | 315 | 237555 | Partly Cloudy-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0146172 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | FUSE |  | 45640 | 802 | 2658937 | 617 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 51211 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145671 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | CURTIS-1704 | 163351704 | RECLOSER |  | 45640 | 730 | 2654408 | 0 | Distribution Circuit | Vegetation | Tree - fell into line | 1312 | 883703 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145190 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 45640 | 1037 | 2657713 | 1760 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5280 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145637 | OH | Sus | 0 | 2024 | DEC | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1702 | 163351702 | FUSE |  | 45640 | 645 | 2653633 | 564 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 17484 | Overcast-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0145300 | OH | Sus | 0 | 2024 | DEC | Yes | Multi-Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 45640 | 808 | 2654790 | 1750 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 213500 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145930 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | CURTIS-1702 | 163351702 | FUSE |  | 45640 | 1213 | 2660329 | 1539 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 29241 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145990 | OH | Sus | 0 | 2024 | DEC | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | OTHER |  | 45640 | 653 | 2653764 | 0 | Distribution Circuit | Vegetation | Tree - branch fell on line | 610 | 119910 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145263 | OH | Sus | 0 | 2024 | DEC | Yes | None | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER |  | 45640 | 739 | 2654596 | 880 | Distribution Circuit | Vegetation | Tree - fell into line | 1241 | 260047 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145203 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | FUSE |  | 45640 | 755 | 2654686 | 169 | Distribution Circuit | Vegetation | Tree - fell into line | 331 | 55938 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145402 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | SWITCH |  | 45640 | 1536 | 2656853 | 1484 | Distribution Circuit | Vegetation | Tree - fell into line | 249 | 73542 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0145885 | OH | Sus | 0 | 2024 | DEC | Yes | Force Out | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 45640 | 748 | 2659245 | 1897 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 55302 | Overcast-Rain-Strong Winds;32-90 F | Transformer (OH) | Broken- wire on ground | 24-0145734 | OH | Sus | 0 | 2024 | DEC | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER |  | 45640 | 749 | 2654641 | 997 | Distribution Circuit | Vegetation | Tree - bark fell into line | 805 | 802585 | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0145206 | OH | Sus | 0 | 2024 | DEC | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | JOLON-1103 | 182981103 | FUSE |  | 45326 | 1401 | 2341039 | 5954 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 17862 | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0021354 | OH | Sus | 0 | 2024 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | SWITCH |  | 45326 | 606 | 2360501 | 10529 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 947610 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0022241 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | FUSE |  | 45326 | 606 | 2361243 | 7550 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 45300 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022464 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 45326 | 439 | 2334364 | 6301 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 371759 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022158 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | SWITCH |  | 45326 | 2048 | 2354138 | 5290 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 312110 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021016 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 45326 | 633 | 2336330 | 6105 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 12210 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019390 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1102 | 182941102 | FUSE |  | 45326 | 633 | 2369290 | 7863 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7863 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023871 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1102 | 182941102 | FUSE |  | 45326 | 634 | 2369829 | 7774 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 23322 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026180 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | HATTON-1102 | 182291102 | RECLOSER |  | 45326 | 917 | 2335252 | 3106 | Distribution Circuit | Equipment Failure/Involved | Overhead | 573 | 1779738 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019373 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | OTTER-1101 | 182941101 | RECLOSER |  | 45326 | 634 | 2369379 | 7916 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 245396 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026021 | OH | Sus | 0 | 2024 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | RECLOSER |  | 45326 | 634 | 2334645 | 6104 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 54936 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019175 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | JUMPER |  | 45326 | 142 | 2372304 | 9197 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 294304 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027181 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 45326 | 136 | 2334200 | 8257 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 429364 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019115 | OH | Sus | 0 | 2024 | FEB | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | OTTER-1101 | 182941101 | FUSE |  | 45326 | 606 | 2356014 | 7987 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 415324 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021348 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | FUSE |  | 45326 | 755 | 2335796 | 1937 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 46488 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021356 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | HATTON-1102 | 182291102 | OCB |  | 45326 | 920 | 2336293 | 9205 | Distribution Circuit | Vegetation | Tree - branch fell on line | 929 | 1714142 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019564 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 45326 | 902 | 2365311 | 4801 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 28806 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020459 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2203 | 182852203 | FUSE |  | 45326 | 1025 | 2337184 | 6133 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 59838 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021700 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 45326 | 902 | 2364170 | 4930 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 226780 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020459 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | FUSE |  | 45326 | 1244 | 2370139 | 6009 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 24036 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026295 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 45326 | 902 | 2364176 | 4880 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 190320 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020459 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 45326 | 902 | 2368558 | 6213 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 186390 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020459 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 45326 | 902 | 2368556 | 6237 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 99792 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020459 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | OCB |  | 45326 | 1651 | 2347659 | 5700 | Distribution Circuit | Vegetation | Tree - bark fell into line | 3631 | 5263589 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020437 | OH | Sus | 0 | 2024 | FEB | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | OCB |  | 45326 | 902 | 2337248 | 7467 | Distribution Circuit | Vegetation | Tree - fell into line | 1616 | 5375599 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020459 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | FUSE |  | 45326 | 931 | 2370013 | 6259 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 100144 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019877 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | FUSE |  | 45326 | 902 | 2360900 | 5025 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 180900 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0022363 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | OTHER |  | 45326 | 931 | 2364294 | 6176 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6176 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019877 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER |  | 45326 | 746 | 2358710 | 4772 | Distribution Circuit | Vegetation | Tree - fell into line | 490 | 2313528 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019877 | OH | Sus | 0 | 2024 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 2 | PACIFIC GROVE-0422 | 182440422 | FUSE |  | 45326 | 1040 | 2337429 | 4802 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 460992 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023277 | OH | Sus | 0 | 2024 | FEB | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER |  | 45326 | 1515 | 2364848 | 4725 | Distribution Circuit | Vegetation | Tree - fell into line | 455 | 2062296 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019877 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE |  | 45326 | 821 | 2335563 | 4891 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 9782 | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024201 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 45326 | 1833 | 2350949 | 5312 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 58432 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022844 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 45326 | 740 | 2334985 | 565 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 39550 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019291 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 45326 | 1619 | 2347435 | 4189 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 121481 | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022895 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | ROB ROY-2104 | 83692104 | FUSE |  | 45326 | 1845 | 2351328 | 4290 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 24590 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023040 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2102 | 83252102 | FUSE |  | 45326 | 1326 | 2340126 | 2907 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 22051 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020031 | OH | Sus | 0 | 2024 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 45326 | 848 | 2335728 | 5925 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 109236 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020400 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2102 | 83252102 | FUSE |  | 45326 | 843 | 2335665 | 1607 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 8035 | Overcast-Fog-Heavy Rain;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0019720 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2105 | 83252105 | FUSE |  | 45326 | 1811 | 2350491 | 5881 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 46784 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022045 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 45326 | 1740 | 2349420 | 5486 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 104234 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024056 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 45326 | 348 | 2334721 | 1869 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 24297 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019387 | OH | Sus | 0 | 2024 | FEB | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE |  | 45326 | 811 | 2360438 | 2152 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 154944 | Overcast-Fog-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0022222 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 45326 | 711 | 2371217 | 8964 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 206172 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026826 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 45326 | 502 | 2334404 | 2049 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 63519 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019339 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 45326 | 1021 | 2337104 | 6005 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 78065 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026080 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 45326 | 711 | 2334849 | 7812 | Distribution Circuit | Vegetation | Tree - fell into line | 528 | 3151431 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019201 | OH | Sus | 0 | 2024 | FEB | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER |  | 45326 | 823 | 2335342 | 6255 | Distribution Circuit | Equipment Failure/Involved | Overhead | 76 | 439782 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019464 | OH | Sus | 0 | 2024 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 45326 | 1414 | 2358206 | 1787 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 69693 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021644 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2104 | 83252104 | JUMPER |  | 45326 | 1717 | 2368358 | 6674 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6674 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024611 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | SWITCH |  | 45326 | 1515 | 2361321 | 4207 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 155879 | Clear;32-90 F | Conductor- Overhead | On Ground | 24-0022483 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2103 | 83622103 | RECLOSER |  | 45326 | 818 | 2335321 | 1864 | Distribution Circuit | Vegetation | Tree - fell into line | 719 | 722563 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019283 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 45326 | 1726 | 2352264 | 1280 | Distribution Circuit | Vegetation | Tree - fell into line | 237 | 303360 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020835 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 45326 | 1529 | 2361363 | 4237 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 254220 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022496 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER |  | 45326 | 1628 | 2361910 | 2822 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 11288 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022424 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | SWITCH |  | 45326 | 601 | 2364847 | 4879 | Distribution Circuit | Vegetation | Tree - fell into line | 157 | 766003 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021577 | OH | Sus | 0 | 2024 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER |  | 45326 | 820 | 2336343 | 1598 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 14062 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019392 | OH | Sus | 0 | 2024 | FEB | Yes | Open Circuit | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 45326 | 1628 | 2361742 | 2649 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 31788 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022424 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | OTHER |  | 45326 | 1631 | 2365038 | 5855 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 368865 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023584 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER |  | 45326 | 1400 | 2344273 | 7156 | Distribution Circuit | Vegetation | Tree - branch fell on line | 915 | 4035233 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022587 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 45326 | 711 | 2371210 | 9240 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 101640 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026821 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | PAUL SWEET-2106 | 83252106 | OTHER |  | 45326 | 658 | 2334798 | 7518 | Distribution Circuit | Vegetation | Tree - bark fell into line | 8 | 60144 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019317 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 45326 | 1544 | s1913442 | 5491 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 5491 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024205 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | TRIP-SAVER |  | 45326 | 607 | 2334867 | 7793 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 448117 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0024640 | OH | Sus | 0 | 2024 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 45326 | 903 | 2361602 | 5312 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 53120 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022573 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | CAMP EVERS-2105 | 83622105 | FUSE |  | 45326 | 1546 | 2344410 | 2994 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 122754 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022534 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE |  | 45326 | 823 | 2370362 | 7592 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 22776 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026376 | OH | Sus | 0 | 2024 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | SWITCH |  | 45326 | 903 | 2359711 | 3239 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 80975 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022004 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | JUMPER |  | 45326 | 1256 | 2369643 | 6159 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 30795 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026137 | OH | Sus | 0 | 2024 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | RECLOSER |  | 45326 | 823 | 2338873 | 4973 | Distribution Circuit | Vegetation | Tree - fell into line | 138 | 686274 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020395 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER |  | 45326 | 1730 | 2349015 | 4338 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 321012 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021918 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | Yes
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 45326 | 754 | 2335127 | 6297 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 1057896 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024608 | OH | Sus | 0 | 2024 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE |  | 45326 | 706 | 2340167 | 7817 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7817 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019851 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | POINT MORETTI-1101 | 82931101 | JUMPER |  | 45326 | 711 | 2361083 | 7812 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 78120 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019851 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 45326 | 1400 | 2368227 | 7048 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 56384 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024563 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | SWITCH |  | 45326 | 1507 | 2359430 | 4526 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 391188 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021918 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 45326 | 1207 | 2338828 | 5840 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 325582 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019975 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER |  | 45326 | 713 | 2334854 | 3503 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 53775 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019206 | OH | Sus | 0 | 2024 | FEB | Yes | Three Phase Fault | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 45326 | 1400 | 2368306 | 7048 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 126864 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021577 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | RECLOSER |  | 45326 | 1606 | 2346612 | 5550 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 174930 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020378 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 45326 | 1400 | 2368549 | 5674 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 113480 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021577 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 45326 | 1316 | 2368302 | 5637 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 101466 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021577 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BURNS-2101 | 183582101 | FUSE |  | 45326 | 1316 | 2368543 | 5801 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 23204 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021577 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER |  | 45326 | 849 | 2335745 | 3470 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 274130 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022580 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE |  | 45326 | 1722 | 2361440 | 5228 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 120244 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022532 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 45326 | 707 | 2359148 | 4850 | Distribution Circuit | Vegetation | Tree - fell into line | 1701 | 8110422 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021615 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE |  | 45326 | 1650 | 2368213 | 7232 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 36160 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024561 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE |  | 45326 | 837 | 2365315 | 4786 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 23930 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022587 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 45326 | 849 | 2364658 | 6221 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 43547 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023466 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | CAMP EVERS-2105 | 83622105 | SWITCH |  | 45326 | 837 | 2364462 | 7727 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 517709 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022587 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 45326 | 949 | 2365522 | 6237 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 492723 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021615 | OH | Sus | 0 | 2024 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | SWITCH |  | 45326 | 949 | 2359145 | 4414 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 322222 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021615 | OH | Sus | 0 | 2024 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45326 | 949 | 2365865 | 4616 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 230800 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023864 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45326 | 949 | 2361336 | 6359 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 89026 | Clear-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0022485 | OH | Sus | 0 | 2024 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45326 | 949 | 2365307 | 4833 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 9666 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021615 | OH | Sus | 0 | 2024 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER |  | 45326 | 1855 | 2365586 | 6839 | Distribution Circuit | Vegetation | Tree - fell into line | 143 | 977977 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021615 | OH | Sus | 0 | 2024 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45326 | 949 | 2365581 | 4626 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 23130 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023732 | OH | Sus | 0 | 2024 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45326 | 928 | 2336299 | 6265 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 344575 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023832 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER |  | 45326 | 935 | 2368973 | 6194 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 43358 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0025009 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45326 | 937 | 2368980 | 7247 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 152187 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0025053 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45326 | 937 | 2365848 | 6057 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 72684 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023856 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | SWITCH |  | 45326 | 937 | 2365331 | 5279 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 621025 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021622 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45326 | 937 | 2368710 | 6273 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 125460 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024697 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER |  | 45326 | 937 | 2368714 | 7756 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 286972 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021622 | OH | Sus | 0 | 2024 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45326 | 937 | 2369008 | 6154 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 289238 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0025148 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE |  | 45326 | 937 | 2368928 | 6125 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 42875 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024844 | OH | Sus | 0 | 2024 | FEB | Yes | Force Out | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1102 | 82841102 | TRIP-SAVER |  | 45326 | 937 | 2368915 | 6258 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 137676 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024811 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 45326 | 745 | 2335654 | 7619 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 131456 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019555 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 45326 | 812 | s1917073 | 5148 | Distribution Circuit | Equipment Failure/Involved | Overhead | 116 | 437913 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0029438 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 45326 | 836 | 2335515 | 4759 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 52678 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019565 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE |  | 45326 | 1509 | 2365762 | 4279 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 98417 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023816 | OH | Sus | 0 | 2024 | FEB | Yes | Force Out | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE |  | 45326 | 1014 | 2364092 | 4901 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 49010 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0023256 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER |  | 45326 | 1014 | 2364731 | 4781 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 19124 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023489 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE |  | 45326 | 1722 | 2359197 | 2922 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 8766 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021880 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER |  | 45326 | 1534 | 2343128 | 5738 | Distribution Circuit | Vegetation | Tree - fell into line | 943 | 3980568 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020202 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER |  | 45326 | 1428 | 2341690 | 7441 | Distribution Circuit | Vegetation | Tree - branch fell on line | 52 | 268434 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020130 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER |  | 45326 | 1406 | 2369967 | 6214 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 49766 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026238 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | Yes
DE ANZA | Tier 2 | LOS GATOS-1108 | 82021108 | FUSE |  | 45326 | 2146 | 2354982 | 2665 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 239850 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022508 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | SARATOGA-1107 | 83371107 | RECLOSER |  | 45326 | 1412 | 2341229 | 5924 | Distribution Circuit | Vegetation | Tree - branch fell on line | 168 | 429051 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019963 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | STELLING-1110 | 83481110 | SWITCH |  | 45326 | 1403 | 2360693 | 3240 | Distribution Circuit | Vegetation | Tree - bark fell into line | 205 | 664200 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022307 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | STELLING-1110 | 83481110 | FUSE |  | 45326 | 1403 | 2360676 | 5891 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 58910 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022301 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
DE ANZA | Tier 2 | STELLING-1110 | 83481110 | FUSE |  | 45326 | 1403 | 2361914 | 3173 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 31730 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022648 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
DIABLO | Tier 3 | TASSAJARA-2104 | 14662104 | OTHER |  | 45326 | 1721 | 2355626 | 2762 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 34161 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021267 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | Yes
EAST BAY | Tier 2 | PALO SECO-0401 | 13180401 | FUSE |  | 45326 | 29 | 2334153 | 1039 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 59223 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019093 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | EL CERRITO G-1112 | 12501112 | RECLOSER |  | 45326 | 1305 | 2339657 | 260 | Distribution Circuit | Equipment Failure/Involved | Overhead | 42 | 10920 | Overcast-Strong Winds;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0019787 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
EAST BAY | Tier 2 | FAIRVIEW-2207 | 13432207 | OTHER |  | 45326 | 1955 | 2350660 | 1115 | Distribution Circuit | Equipment Failure/Involved | Overhead | 132 | 42032 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020947 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | Yes
FRESNO | Tier 2 | DUNLAP-1102 | 254061102 | RECLOSER |  | 45326 | 1530 | 2343628 | 2850 | Distribution Circuit | Equipment Failure/Involved | Overhead | 309 | 116885 | Overcast-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020197 | OH | Sus | 0 | 2024 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | JUMPER |  | 45326 | 630 | 2360605 | 9065 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 9065 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022282 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 45326 | 457 | 2360732 | 12233 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 366990 | Strong Winds-Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022315 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 45326 | 630 | 2359715 | 10720 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 21440 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022008 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 45326 | 630 | 2336525 | 6372 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 140184 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019417 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 45326 | 457 | 2364087 | 9498 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 18996 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023253 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 45326 | 630 | 2336943 | 5119 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 55896 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019460 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 45326 | 457 | 2364382 | 5253 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 346698 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019139 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE |  | 45326 | 457 | 2359323 | 7956 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 7956 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021920 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | MIDDLETOWN-1101 | 43141101 | RECLOSER |  | 45326 | 1916 | 2352379 | 5454 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 211209 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020848 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1111 | 42841111 | FUSE |  | 45326 | 955 | 2355219 | 6048 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 36288 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021208 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 45326 | 642 | 2359035 | 4629 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 74064 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021835 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | SWITCH |  | 45326 | 642 | 2344878 | 7501 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 142519 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020264 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 3 | MIDDLE RIVER-1101 | 162091101 | FUSE |  | 45326 | 1821 | 2360826 | 5757 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 184224 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022343 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE |  | 45326 | 1824 | 2360810 | 8554 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 417848 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022335 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 45326 | 848 | 2370003 | 9156 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 155652 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026247 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 45326 | 844 | 2368177 | 9222 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 82998 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024544 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | OTHER |  | 45326 | 841 | 2335618 | 8982 | Distribution Circuit | Vegetation | Tree - fell into line | 1064 | 886058 | Overcast-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0019322 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 45326 | 843 | 2334343 | 7626 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 205902 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022141 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | SWITCH |  | 45326 | 1819 | 2364212 | 2856 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 199920 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020710 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | RECLOSER |  | 45326 | 1630 | 2365096 | 5670 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 130410 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020710 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | RECLOSER |  | 45326 | 232 | 2334273 | 6349 | Distribution Circuit | Vegetation | Tree - fell into line | 855 | 3534755 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019107 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | JUMPER |  | 45326 | 722 | 2365684 | 6013 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6013 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023776 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | OTHER |  | 45326 | 1011 | 2336962 | 8728 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 142773 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020547 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | FUSE |  | 45326 | 724 | 2365691 | 6128 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 85792 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023779 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | JUMPER |  | 45326 | 724 | 2365695 | 6209 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 55881 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023781 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | FUSE |  | 45326 | 450 | 2367279 | 6547 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 144034 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024275 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | FUSE |  | 45326 | 450 | 2365120 | 7580 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 248328 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019133 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | FUSE |  | 45326 | 724 | 2365687 | 6374 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 44618 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023778 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | TRIP-SAVER |  | 45326 | 450 | 2365137 | 7699 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 123184 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019133 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | FUSE |  | 45326 | 450 | 2365341 | 9386 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 769652 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023650 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | FUSE |  | 45326 | 450 | 2365353 | 6446 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 264286 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023653 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER |  | 45326 | 450 | 2334376 | 10491 | Distribution Circuit | Vegetation | Tree - fell into line | 809 | 3097083 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019133 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE |  | 45326 | 534 | 2334470 | 4778 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 272346 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019709 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | HIGHLANDS 1101 | 43361101 | FUSE |  | 45326 | 2336 | 2355784 | 3528 | Distribution Circuit | Vegetation | Tree - branch fell on line | 242 | 326232 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022099 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 45326 | 552 | 2337648 | 7616 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 30464 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0019547 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | KONOCTI-1102 | 43311102 | RECLOSER |  | 45326 | 1802 | 2350356 | 1149 | Distribution Circuit | Vegetation | Tree - fell into line | 391 | 437917 | Overcast-Fog-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0020659 | OH | Sus | 0 | 2024 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | HIGHLANDS-1104 | 43361104 | FUSE |  | 45326 | 1858 | 2351636 | 1449 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 119379 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021834 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HIGHLANDS-1102 | 43361102 | FUSE |  | 45326 | 2309 | 2355754 | 1080 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2677 | 291029 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021556 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | HOPLAND-1101 | 42251101 | FUSE |  | 45326 | 1742 | 2349556 | 5838 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 5838 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022632 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | HOPLAND-1101 | 42251101 | FUSE |  | 45326 | 616 | 2334597 | 278 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 20025 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019360 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE |  | 45326 | 914 | 2336056 | 5906 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 94496 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019818 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | PHILO-1101 | 42601101 | FUSE |  | 45326 | 2203 | 2360017 | 6927 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 436401 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022082 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | REDBUD-1101 | 43191101 | FUSE |  | 45326 | 2015 | 2353736 | 4118 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 123540 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021626 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | LUCERNE-1106 | 43351106 | TRIP-SAVER |  | 45326 | 1454 | 2342332 | 1559 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 169931 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020234 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | FUSE |  | 45326 | 2023 | 2366503 | 8582 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 51492 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024007 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | RECLOSER |  | 45326 | 1922 | 2352722 | 9726 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 38904 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020890 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | FUSE |  | 45326 | 928 | 2361383 | 10343 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 264094 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022505 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | RECLOSER |  | 45326 | 928 | 2336360 | 7448 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 123066 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019428 | OH | Sus | 0 | 2024 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 45326 | 648 | 2334711 | 7819 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 16025 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019754 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | FUSE |  | 45326 | 915 | 2338442 | 7557 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 158697 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019428 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | LUCERNE-1106 | 43351106 | FUSE |  | 45326 | 1020 | 2337097 | 5844 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 149928 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019666 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | UKIAH-1115 | 42771115 | FUSE |  | 45326 | 1350 | 2340434 | 5991 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 13718 | Partly Cloudy-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020152 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | PHILO-1102 | 42601102 | FUSE |  | 45326 | 2207 | 2357115 | 7990 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 207740 | Partly Cloudy-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0021509 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 45326 | 550 | 2368209 | 7959 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 15918 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024556 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 45326 | 1959 | 2359644 | 5410 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 70330 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021987 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 45326 | 2058 | 2364447 | 2467 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 59208 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023381 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | CALPELLA-1101 | 43411101 | RECLOSER |  | 45326 | 1257 | 2339600 | 4493 | Distribution Circuit | Vegetation | Tree - fell into line | 507 | 868573 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020008 | OH | Sus | 0 | 2024 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | ELK-1101 | 42981101 | FUSE |  | 45326 | 1418 | 2361357 | 6265 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 56385 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022495 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | JUMPER |  | 45326 | 2158 | 2359220 | 5432 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 65184 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021890 | OH | Sus | 0 | 2024 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 45326 | 2158 | 2359199 | 4135 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 12405 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021881 | OH | Sus | 0 | 2024 | FEB | Yes | Open Circuit | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 45326 | 443 | 2334363 | 485 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3395 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019266 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER |  | 45326 | 2110 | 2354659 | 5527 | Distribution Circuit | Vegetation | Tree - fell into line | 2209 | 6231812 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021100 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 45326 | 2141 | 2359963 | 5723 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5723 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022064 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 45326 | 2142 | 2359800 | 4125 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 90750 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0022021 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 45326 | 2142 | 2358544 | 4063 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 178772 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021721 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 45326 | 1411 | 2341119 | 1801 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 126043 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021879 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 45326 | 2217 | 2355915 | 5299 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 84784 | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021332 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 45326 | 2130 | 2361489 | 5277 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 179418 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022548 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE |  | 45326 | 2155 | 2361157 | 6651 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 106416 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022437 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER |  | 45326 | 1355 | 2340764 | 5674 | Distribution Circuit | Vegetation | Tree - fell into line | 1066 | 1383224 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019926 | OH | Sus | 0 | 2024 | FEB | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | BIG RIVER-1101 | 43081101 | TRIP-SAVER |  | 45326 | 2204 | 2361346 | 5622 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 219258 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022488 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 45326 | 1912 | 2365388 | 6695 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 87035 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023670 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 45326 | 1410 | 2338326 | 7251 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 36255 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020062 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | FUSE |  | 45326 | 2323 | 2355661 | 7980 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 39900 | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021938 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | FUSE |  | 45326 | 2208 | 2355184 | 4081 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 204050 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022223 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 45326 | 1203 | 2338787 | 3135 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 11187 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019812 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 45326 | 1119 | 2338099 | 385 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 23870 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019718 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 45326 | 1912 | 2371528 | 7019 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 119323 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026940 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 45326 | 936 | 2336411 | 7549 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 28107 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020291 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | FUSE |  | 45326 | 1403 | 2360846 | 8352 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 109334 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022350 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 45326 | 1912 | 2364132 | 7095 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 14190 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023268 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER |  | 45326 | 934 | 2336398 | 1638 | Distribution Circuit | Vegetation | Tree - fell into line | 144 | 47619 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019295 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 45326 | 1912 | 2362054 | 8429 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 126435 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022692 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE |  | 45326 | 1016 | 2340367 | 4515 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4515 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019889 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 45326 | 1912 | 2363604 | 5669 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5669 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023078 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 45326 | 1912 | 2361942 | 5122 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 477680 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021541 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | JUMPER |  | 45326 | 1912 | 2357469 | 4230 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 160740 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021541 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE |  | 45326 | 836 | 2369325 | 5857 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 17571 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026007 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 45326 | 1312 | 2339824 | 6037 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 32321 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020244 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1103 | 42661103 | FUSE |  | 45326 | 2123 | 2354791 | 8111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 11480 | Overcast-Fog-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0022393 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 45326 | 1051 | 2339135 | 7217 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 108255 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019693 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 45326 | 1421 | 2341393 | 7242 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 14484 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020389 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 45326 | 1912 | 2361259 | 6991 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 41946 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022469 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | SWITCH |  | 45326 | 1912 | 2360564 | 8528 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 102336 | Overcast-Heavy Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0022268 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
HUMBOLDT | Tier 2 | LAYTONVILLE-1101 | 42681101 | RECLOSER |  | 45326 | 1532 | 2344017 | 1618 | Distribution Circuit | Vegetation | Tree - fell into line | 466 | 152611 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020588 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE |  | 45326 | 1318 | 2339952 | 128 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 1280 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019944 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER |  | 45326 | 2247 | 2355530 | 2140 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 203300 | Overcast-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0021289 | OH | Sus | 0 | 2024 | FEB | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 3 | BRIDGEVILLE-1102 | 192461102 | FUSE |  | 45326 | 1000 | 2336782 | 686 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 28812 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019828 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | BUELLTON-1101 | 183041101 | RECLOSER |  | 45326 | 1439 | 2341961 | 1691 | Distribution Circuit | Equipment Failure/Involved | Overhead | 179 | 184082 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020756 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | ZACA-1102 | 182681102 | OCB |  | 45326 | 840 | 2335581 | 2018 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1442 | 318893 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019324 | OH | Sus | 35528784 | 2024 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | OCEANO-1102 | 182601102 | RECLOSER |  | 45326 | 1025 | 2340979 | 2074 | Distribution Circuit | Vegetation | Tree - fell into line | 492 | 516762 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021349 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | OCEANO-1102 | 182601102 | OTHER |  | 45326 | 801 | 2360908 | 3061 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1982 | 29327 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022366 | OH | Sus | 46179674 | 2024 | FEB | Yes | Open Circuit | Yes | Yes
LOS PADRES | Tier 2 | OCEANO-1104 | 182601104 | RECLOSER |  | 45326 | 857 | 2335801 | 572 | Distribution Circuit | Vegetation | Tree - fell into line | 859 | 264012 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019340 | OH | Sus | 0 | 2024 | FEB | Yes | Multi-Fault | Yes | No
LOS PADRES | Tier 2 | OCEANO-1104 | 182601104 | FUSE |  | 45326 | 857 | 2337628 | 572 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 8580 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019544 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | OCEANO-1104 | 182601104 | JUMPER |  | 45326 | 857 | 2339365 | 1467 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1467 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019730 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | ATASCADERO-1103 | 182541103 | RECLOSER |  | 45326 | 1211 | 2338881 | 1316 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 119401 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019966 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | ATASCADERO-1103 | 182541103 | OTHER |  | 45326 | 1137 | 2342397 | 1888 | Distribution Circuit | Vegetation | Tree - bark fell into line | 88 | 10398 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020086 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | Yes
LOS PADRES | Tier 2 | ATASCADERO-1101 | 182541101 | FUSE |  | 45326 | 1240 | 2339282 | 537 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 6444 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020617 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE |  | 45326 | 945 | 2336542 | 1458 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 75480 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019650 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE |  | 45326 | 1115 | 2344445 | 1323 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 18522 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020240 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2111 | 183052111 | RECLOSER |  | 45326 | 1112 | 2337955 | 1413 | Distribution Circuit | Vegetation | Tree - fell into line | 1644 | 872328 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019685 | OH | Sus | 0 | 2024 | FEB | Yes | Three Phase Fault | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | OTHER |  | 45326 | 1730 | 2349069 | 1566 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 17226 | Partly Cloudy-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020641 | OH | Sus | 0 | 2024 | FEB | Yes | Open Circuit | Yes | No
LOS PADRES | Tier 2 | PERRY-1101 | 183071101 | FUSE |  | 45326 | 1317 | 2343517 | 2851 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 71275 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020185 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 3 | PERRY-1101 | 183071101 | FUSE |  | 45326 | 1229 | 2339174 | 2905 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 40670 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020490 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
LOS PADRES | Tier 2 | TEMPLETON-2110 | 183052110 | FUSE |  | 45326 | 909 | 2348507 | 1815 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 41745 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020538 | OH | Sus | 0 | 2024 | FEB | Yes | Multi-Fault | Yes | No
LOS PADRES | Tier 2 | PERRY-1104 | 183071104 | FUSE |  | 45326 | 831 | 2357870 | 3353 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 131809 | Overcast-Heavy Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0022645 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | ALTO-1120 | 42031120 | FUSE |  | 45326 | 1510 | 2342781 | 4139 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 264896 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020560 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | ALTO-1125 | 42031125 | FUSE |  | 45326 | 1500 | 2353545 | 4341 | Distribution Circuit | Vegetation | Tree - branch fell on line | 123 | 533943 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020945 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 2 | BOLINAS-1101 | 42261101 | RECLOSER |  | 45326 | 1336 | 2340186 | 10079 | Distribution Circuit | Equipment Failure/Involved | Overhead | 228 | 809552 | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019859 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | BOLINAS-1101 | 42261101 | RECLOSER |  | 45326 | 1445 | 2342262 | 10053 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 201060 | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020074 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE |  | 45326 | 1728 | 2349855 | 4181 | Distribution Circuit | Vegetation | Tree - branch fell on line | 126 | 76701 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020735 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | OCB |  | 45326 | 2317 | 2355695 | 1243 | Distribution Circuit | Vegetation | Tree - branch fell on line | 631 | 784333 | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021278 | OH | Sus | 0 | 2024 | FEB | Yes | Three Phase Fault | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1102 | 43021102 | OCB |  | 45326 | 1456 | 2342627 | 3014 | Distribution Circuit | Vegetation | Tree - bark fell into line | 3042 | 4987518 | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020103 | OH | Sus | 0 | 2024 | FEB | Yes | Three Phase Fault | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | RECLOSER |  | 45326 | 1515 | 2341923 | 9795 | Distribution Circuit | Vegetation | Tree - fell into line | 625 | 3292098 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020146 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | WOODACRE-1101 | 43021101 | FUSE |  | 45326 | 1441 | 2348334 | 7236 | Distribution Circuit | Vegetation | Tree - branch fell on line | 110 | 795960 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020503 | OH | Sus | 0 | 2024 | FEB | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | FUSE |  | 45326 | 1448 | 2342147 | 7251 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 520442 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020516 | OH | Sus | 0 | 2024 | FEB | Yes | Three Phase Fault | Yes | No
NORTH BAY | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER |  | 45326 | 1418 | 2341383 | 4504 | Distribution Circuit | Vegetation | Tree - fell into line | 128 | 575808 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019974 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | PUEBLO-2103 | 43292103 | FUSE |  | 45326 | 1833 | 2350941 | 8171 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 98052 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026924 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 2 | MONTICELLO-1101 | 43051101 | OTHER |  | 45326 | 1912 | 2352125 | 1024 | Distribution Circuit | Vegetation | Tree - branch fell on line | 133 | 127042 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021205 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | SILVERADO-2102 | 43432102 | RECLOSER |  | 45326 | 1706 | 2350283 | 5756 | Distribution Circuit | Equipment Failure/Involved | Overhead | 754 | 1206078 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021389 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | RECLOSER |  | 45326 | 1455 | 2357959 | 4278 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 238459 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021604 | OH | Sus | 0 | 2024 | FEB | Yes | Multi-Fault | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 45326 | 1116 | 2337976 | 6713 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 107408 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024585 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER |  | 45326 | 2219 | 2355252 | 2601 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1060 | 1443092 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021219 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | RECLOSER |  | 45326 | 1108 | 2337894 | 3001 | Distribution Circuit | Vegetation | Tree - fell into line | 357 | 582930 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019577 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | CALISTOGA-1101 | 42711101 | RECLOSER |  | 45326 | 2054 | 2358035 | 4131 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 170843 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021618 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 45326 | 2035 | 2353911 | 5442 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 150282 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022615 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 45326 | 1943 | 2352989 | 6889 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6889 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0025070 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 45326 | 2028 | 2353843 | 4276 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 179592 | Clear-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 24-0022111 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE |  | 45326 | 2045 | 2362761 | 5403 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 86448 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021015 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER |  | 45326 | 1936 | 2352972 | 4088 | Distribution Circuit | Equipment Failure/Involved | Overhead | 199 | 624913 | Overcast-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020898 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER |  | 45326 | 2045 | 2353851 | 5265 | Distribution Circuit | Equipment Failure/Involved | Overhead | 445 | 816097 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021015 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 2 | WYANDOTTE-1107 | 102911107 | RECLOSER |  | 45326 | 2010 | 2353616 | 1682 | Distribution Circuit | Vegetation | Tree - fell into line | 524 | 824938 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020955 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER |  | 45326 | 2015 | 2353725 | 3949 | Distribution Circuit | Vegetation | Tree - fell into line | 459 | 1569963 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020967 | OH | Sus | 0 | 2024 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | BIG BEND-1102 | 103751102 | RECLOSER |  | 45326 | 2049 | 2347789 | 7037 | Distribution Circuit | Vegetation | Tree - fell into line | 236 | 688537 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021020 | OH | Sus | 0 | 2024 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | BUTTE-1105 | 103081105 | FUSE |  | 45326 | 1947 | 2357291 | 4019 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 61904 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023191 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1105 | 102831105 | FUSE |  | 45326 | 1959 | 2358354 | 4105 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 20525 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021680 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | PARADISE-1105 | 102831105 | FUSE |  | 45326 | 1959 | 2358905 | 2891 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 98294 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021803 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | NOTRE DAME-1104 | 102041104 | RECLOSER |  | 45326 | 2004 | 2353145 | 5462 | Distribution Circuit | Equipment Failure/Involved | Overhead | 138 | 341855 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021013 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | OTHER |  | 45326 | 2040 | 2356686 | 3794 | Distribution Circuit | Vegetation | Tree - fell into line | 165 | 444666 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021466 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1101 | 103031101 | JUMPER |  | 45326 | 2038 | 2356046 | 4275 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 64125 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021358 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | ORO FINO-1102 | 103031102 | OCB |  | 45326 | 2038 | 2354687 | 4171 | Distribution Circuit | Vegetation | Tree - fell into line | 1919 | 3549887 | Overcast-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0021098 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
NORTH VALLEY | Tier 3 | BUCKS CREEK-1103 | 102211103 | RECLOSER |  | 45326 | 1956 | 2353589 | 2679 | Distribution Circuit | Vegetation | Tree - fell into line | 314 | 826586 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021544 | OH | Sus | 0 | 2024 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | RECLOSER |  | 45326 | 2219 | 2355277 | 2823 | Distribution Circuit | Vegetation | Tree - fell into line | 297 | 684717 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021254 | OH | Sus | 0 | 2024 | FEB | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | OTHER |  | 45326 | 2128 | 2354849 | 740 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 28378 | Overcast-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021232 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | Yes
NORTH VALLEY | Tier 3 | VOLTA-1102 | 102541102 | RECLOSER |  | 45326 | 2107 | 2354656 | 962 | Distribution Circuit | Vegetation | Tree - fell into line | 483 | 174089 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021099 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
NORTH VALLEY | Tier 2 | FRENCH GULCH-1102 | 103381102 | RECLOSER |  | 45326 | 2301 | 2355577 | 2248 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 29912 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021258 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | WHITMORE-1101 | 103601101 | RECLOSER |  | 45326 | 2353 | 2355831 | 763 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 83062 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021314 | OH | Sus | 0 | 2024 | FEB | Yes | Three Phase Fault | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | TRIP-SAVER |  | 45326 | 1229 | 2339943 | 6009 | Distribution Circuit | Equipment Failure/Involved | Overhead | 107 | 630561 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020956 | OH | Sus | 0 | 2024 | FEB | Yes | Multi-Fault | Yes | Yes
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 45326 | 1147 | 2338612 | 7408 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 242356 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0025138 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE |  | 45326 | 1344 | 2367830 | 7130 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 99820 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024437 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE |  | 45326 | 1407 | 2365361 | 6046 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 42322 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023654 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 45326 | 1339 | 2370516 | 5996 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 17988 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019890 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | RECLOSER |  | 45326 | 1358 | 2338241 | 6154 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 704750 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019929 | OH | Sus | 0 | 2024 | FEB | Yes | Multi-Fault | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE |  | 45326 | 1318 | 2367423 | 4669 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 70035 | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024300 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE |  | 45326 | 1429 | 2355571 | 4499 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 130471 | Strong Winds | Conductor- Overhead | Broken- wire on ground | 24-0021255 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 45326 | 1921 | 2347420 | 6122 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 73341 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020840 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | Yes
PENINSULA | Tier 3 | MENLO-1102 | 24131102 | FUSE |  | 45326 | 1436 | 2342052 | 8383 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 50298 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023544 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 45326 | 1247 | 2369952 | 8449 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 25347 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026235 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 45326 | 1531 | 2344114 | 5544 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 27720 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021202 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER |  | 45326 | 1322 | 2345494 | 5880 | Distribution Circuit | Vegetation | Tree - fell into line | 233 | 1198343 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020442 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 45326 | 1210 | 2369902 | 6080 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 48640 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026205 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 45326 | 1704 | 2368451 | 5494 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 71422 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024630 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER |  | 45326 | 1444 | 2342039 | 4332 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2296 | 7690523 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020042 | OH | Sus | 0 | 2024 | FEB | Yes | Force Out | Yes | Yes
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER |  | 45326 | 1341 | 2338860 | 4747 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 189880 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019882 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE |  | 45326 | 1341 | 2368458 | 5941 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 11882 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 24-0024635 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
PENINSULA | Tier 3 | WOODSIDE-1101 | 24251101 | TRIP-SAVER |  | 45326 | 934 | 2336387 | 6108 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 256536 | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019499 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
PENINSULA | Tier 2 | WOODSIDE-1104 | 24251104 | FUSE |  | 45326 | 1322 | 2339956 | 2877 | Distribution Circuit | Equipment Failure/Involved | Overhead | 454 | 1306158 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020281 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
PENINSULA | Tier 2 | CAROLANDS-0404 | 24060404 | FUSE |  | 45326 | 1230 | 2344649 | 4556 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 18224 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023344 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BROWNS VALLEY-1101 | 152921101 | FUSE |  | 45326 | 2022 | 2359948 | 6734 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 40404 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022059 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 45326 | 1913 | 2352175 | 6661 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 113752 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022294 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SACRAMENTO | Tier 2 | BANGOR-1101 | 103191101 | FUSE |  | 45326 | 1847 | 2351414 | 5453 | Distribution Circuit | Equipment Failure/Involved | Overhead | 60 | 90885 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0022619 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE |  | 45326 | 1603 | 2345237 | 1614 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 7206 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020692 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | FUSE |  | 45326 | 1746 | 2349646 | 2774 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 81151 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021714 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-1110 | 153081110 | OTHER |  | 45326 | 1933 | 2354344 | 2600 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 17850 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021051 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | APPLE HILL-1104 | 153661104 | RECLOSER |  | 45326 | 1523 | 2343408 | 4465 | Distribution Circuit | Vegetation | Tree - fell into line | 1502 | 1594401 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020191 | OH | Sus | 0 | 2024 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE |  | 45326 | 2230 | 2355520 | 2153 | Distribution Circuit | Equipment Failure/Involved | Overhead | 90 | 193770 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021702 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 45326 | 1915 | 2357805 | 1566 | Distribution Circuit | Vegetation | Tree - fell into line | 998 | 1098510 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020704 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | JUMPER |  | 45326 | 1915 | 2364891 | 5639 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5804 | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020704 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE |  | 45326 | 1624 | 2346301 | 2607 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 117820 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020704 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE |  | 45326 | 1551 | 2344612 | 7337 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 8297 | Partly Cloudy-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020910 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | LINCOLN-1101 | 153701101 | FUSE |  | 45326 | 1630 | 2352244 | 7060 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 41700 | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020831 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | FUSE |  | 45326 | 1713 | 2357554 | 5834 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 17502 | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 24-0023790 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | FUSE |  | 45326 | 1700 | 2348094 | 7273 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 58184 | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 24-0023721 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | JUMPER |  | 45326 | 1700 | 2366718 | 7463 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 34136 | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024076 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | PENRYN-1105 | 152561105 | FUSE |  | 45326 | 1639 | 2355596 | 7211 | Distribution Circuit | Vegetation | Tree - fell into line | 613 | 1293493 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020372 | OH | Sus | 0 | 2024 | FEB | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | WISE-1102 | 152271102 | FUSE |  | 45326 | 1644 | 2359931 | 4490 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 166130 | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022048 | OH | Sus | 0 | 2024 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 45326 | 2020 | 2351604 | 2582 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 7746 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023442 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | BELL-1107 | 152701107 | FUSE |  | 45326 | 1719 | 2348508 | 3075 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 144525 | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023748 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BELL-1109 | 152701109 | FUSE |  | 45326 | 1706 | 2348122 | 3106 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 338554 | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022272 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BELL-1108 | 152701108 | FUSE |  | 45326 | 1612 | 2360650 | 4294 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 94468 | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020344 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | FUSE |  | 45326 | 1538 | 2360382 | 4600 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 349600 | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0022202 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | FORESTHILL-1102 | 152181102 | FUSE |  | 45326 | 1619 | 2346047 | 5753 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 46024 | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022275 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE |  | 45326 | 1946 | 2353086 | 4031 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 205145 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023476 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE |  | 45326 | 1819 | 2350582 | 5440 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 163200 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021811 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | FUSE |  | 45326 | 1800 | 2350049 | 4478 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 143296 | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020854 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | RECLOSER |  | 45326 | 1553 | 2345101 | 1429 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 168622 | Clear-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020337 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE |  | 45326 | 2203 | 2355108 | 4105 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 233985 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023336 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 45326 | 1928 | 2352683 | 5425 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 151900 | Overcast-Drizzle-Strong Winds;32-90 F | Transformer (OH) | Broken- wire on ground | 24-0023680 | OH | Sus | 0 | 2024 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | HIGGINS-1107 | 152691107 | FUSE |  | 45326 | 1540 | 2344062 | 4411 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 44110 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021009 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE |  | 45326 | 1553 | 2359833 | 2742 | Distribution Circuit | Equipment Failure/Involved | Overhead | 108 | 296136 | Partly Cloudy-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022026 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | JUMPER |  | 45326 | 1553 | 2360668 | 7186 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 57488 | Partly Cloudy-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0022298 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | FUSE |  | 45326 | 1825 | 2350765 | 5341 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 127348 | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023638 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 45326 | 1540 | 2344101 | 7323 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 44406 | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020472 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | WEIMAR-1101 | 152491101 | FUSE |  | 45326 | 1908 | 2352044 | 5498 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 80928 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023282 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE |  | 45326 | 2204 | 2355138 | 5134 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 66742 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022612 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE |  | 45326 | 1618 | 2345995 | 7322 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 128350 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024444 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | RECLOSER |  | 45326 | 1557 | 2345212 | 7092 | Distribution Circuit | Vegetation | Tree - fell into line | 959 | 3178058 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020370 | OH | Sus | 0 | 2024 | FEB | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | JUMPER |  | 45326 | 1557 | 2351068 | 7315 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 80465 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020725 | OH | Sus | 0 | 2024 | FEB | Yes | Force Out | Yes | No
SIERRA | Tier 2 | HIGGINS-1103 | 152691103 | JUMPER |  | 45326 | 1940 | 2355248 | 6909 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 20727 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021213 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | HIGGINS-1104 | 152691104 | FUSE |  | 45326 | 2219 | 2355240 | 5371 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 220211 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022283 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 45326 | 1904 | 2358155 | 5335 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 26675 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021629 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | JUMPER |  | 45326 | 1652 | 2364739 | 6936 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6936 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023493 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE |  | 45326 | 2054 | 2358982 | 6795 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 74745 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021822 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 45326 | 1652 | 2362205 | 7013 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 98182 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022766 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | OTHER |  | 45326 | 1705 | 2348090 | 4483 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 71466 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021018 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | OTHER |  | 45326 | 1525 | 2349154 | 4627 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 309131 | Overcast;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020557 | OH | Sus | 0 | 2024 | FEB | Yes | Open Circuit | Yes | Yes
SIERRA | Tier 2 | GRASS VALLEY-1101 | 152031101 | RECLOSER |  | 45326 | 2323 | 2354808 | 4053 | Distribution Circuit | Equipment Failure/Involved | Overhead | 403 | 983002 | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021346 | OH | Sus | 0 | 2024 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | GRASS VALLEY-1101 | 152031101 | RECLOSER |  | 45326 | 2222 | s1911859 | 5268 | Distribution Circuit | Vegetation | Tree - fell into line | 173 | 311064 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022184 | OH | Sus | 0 | 2024 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE |  | 45326 | 1634 | 2350854 | 7103 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 160085 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020702 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER |  | 45326 | 1652 | 2347833 | 6993 | Distribution Circuit | Vegetation | Tree - fell into line | 3667 | 6576077 | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020540 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | JUMPER |  | 45326 | 1623 | 2365039 | 7102 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 42612 | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0023585 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | NARROWS-2105 | 153132105 | RECLOSER |  | 45326 | 1729 | 2349137 | 5704 | Distribution Circuit | Vegetation | Tree - fell into line | 3639 | 6793777 | Overcast-Rain-Strong Winds;32-90 F | Switch (OH) | Broken- wire on ground | 24-0020688 | OH | Sus | 0 | 2024 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE |  | 45326 | 1723 | 2348717 | 5713 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 148538 | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 24-0020614 | OH | Sus | 0 | 2024 | FEB | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1107 | 152481107 | FUSE |  | 45326 | 1942 | 2352961 | 4256 | Distribution Circuit | Vegetation | Tree - fell into line | 199 | 846944 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022125 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE |  | 45326 | 2057 | 2360868 | 6982 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 27928 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022359 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | NARROWS-2102 | 153132102 | RECLOSER |  | 45326 | 1929 | 2352798 | 4274 | Distribution Circuit | Vegetation | Tree - fell into line | 1169 | 2153746 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021305 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | OTHER |  | 45326 | 1907 | 2364912 | 5775 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 100715 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023555 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 2 | BRUNSWICK-1110 | 152481110 | FUSE |  | 45326 | 1924 | 2349037 | 5494 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 252724 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026084 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1104 | 152481104 | JUMPER |  | 45326 | 1656 | 2360955 | 5705 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 34230 | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0022376 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE |  | 45326 | 1659 | 2359823 | 1407 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 97083 | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0022025 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE |  | 45326 | 2107 | 2359806 | 5447 | Distribution Circuit | Vegetation | Tree - fell into line | 230 | 968770 | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0022022 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE |  | 45326 | 2106 | 2359127 | 6863 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 13726 | Overcast-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0023460 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1104 | 152481104 | FUSE |  | 45326 | 1809 | 2350270 | 5781 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 75153 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022541 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1104 | 152481104 | FUSE |  | 45326 | 1921 | 2352531 | 5680 | Distribution Circuit | Vegetation | Tree - fell into line | 203 | 532240 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022530 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER |  | 45326 | 1626 | 2347868 | 5458 | Distribution Circuit | Vegetation | Tree - fell into line | 1411 | 2804549 | Partly Cloudy-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020479 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | OCB |  | 45326 | 1853 | 2351552 | 6593 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1165 | 3206443 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020804 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE |  | 45326 | 1635 | 2361956 | 6842 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6842 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022661 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER |  | 45326 | 431 | 2334355 | 2446 | Distribution Circuit | Vegetation | Tree - fell into line | 185 | 369038 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019126 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 45326 | 1444 | 2356525 | 4359 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 231027 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021444 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE |  | 45326 | 428 | 2362068 | 6600 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 6600 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022698 | OH | Sus | 0 | 2024 | FEB | Yes | Open Circuit | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE |  | 45326 | 1753 | 2358808 | 6992 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 48944 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022708 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE |  | 45326 | 2135 | 2359536 | 2495 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 12475 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020416 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 45326 | 1450 | 2351409 | 1446 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 36150 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020768 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | FUSE |  | 45326 | 1430 | 2366541 | 8580 | Distribution Circuit | 3rd Party | Other | 1 | 8580 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024028 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | COTATI-1103 | 42271103 | RECLOSER |  | 45326 | 1646 | s1944950 | 4467 | Distribution Circuit | Vegetation | Tree - fell into line | 342 | 125766 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019078 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | SONOMA-1103 | 42721103 | RECLOSER |  | 45326 | 1714 | 2348400 | 1042 | Distribution Circuit | Vegetation | Tree - fell into line | 1370 | 465844 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020512 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | SONOMA-1105 | 42721105 | FUSE |  | 45326 | 650 | 2334728 | 9374 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 110187 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019369 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1105 | 42271105 | RECLOSER |  | 45326 | 1527 | 2368904 | 5653 | Distribution Circuit | Vegetation | Tree - fell into line | 225 | 1119201 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020194 | OH | Sus | 0 | 2024 | FEB | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 2 | COTATI-1105 | 42271105 | RECLOSER |  | 45326 | 425 | 2334350 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 229 | 88805 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019124 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | COTATI-1105 | 42271105 | RECLOSER |  | 45326 | 1527 | 2343382 | 6936 | Distribution Circuit | Vegetation | Tree - fell into line | 1446 | 5418801 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020194 | OH | Sus | 0 | 2024 | FEB | Yes | Multi-Fault | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | JUMPER |  | 45326 | 1516 | 2364227 | 4376 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4376 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020246 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | FUSE |  | 45326 | 1446 | 2369401 | 7703 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 92436 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0026029 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | JUMPER |  | 45326 | 1529 | 2372399 | 8566 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 25698 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027270 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | SWITCH |  | 45326 | 1529 | 2372371 | 8731 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 43655 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027230 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER |  | 45326 | 1624 | 2350951 | 8452 | Distribution Circuit | Vegetation | Tree - fell into line | 2045 | 7079762 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020713 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1101 | 42571101 | FUSE |  | 45326 | 1529 | 2365497 | 7343 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 58744 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023703 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 2 | MOLINO-1101 | 42571101 | RECLOSER |  | 45326 | 1529 | 2343733 | 2990 | Distribution Circuit | Vegetation | Tree - fell into line | 2139 | 4047371 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020246 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | TRIP-SAVER |  | 45326 | 1418 | 2360232 | 5932 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 371004 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022151 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 45326 | 1615 | 2367192 | 7234 | Distribution Circuit | Vegetation | Tree - fell into line | 165 | 1193610 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020713 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER |  | 45326 | 1526 | 2345084 | 7380 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 59040 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020438 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1101 | 42571101 | JUMPER |  | 45326 | 1537 | 2364519 | 4498 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8996 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020246 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 45326 | 1445 | 2367190 | 4608 | Distribution Circuit | Vegetation | Tree - branch fell on line | 82 | 377856 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020713 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1101 | 42571101 | FUSE |  | 45326 | 1516 | 2364522 | 4084 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 16336 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020246 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | JUMPER |  | 45326 | 1527 | 2368977 | 5943 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 17829 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0025039 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 45326 | 2006 | 2367185 | 5421 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 32526 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024251 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 45326 | 1848 | 2364256 | 4462 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 8924 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023319 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 45326 | 1453 | 2364181 | 7049 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 91637 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023289 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 45326 | 1858 | 2359445 | 5237 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 125688 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021940 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 45326 | 1456 | 2370701 | 7166 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 394130 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026516 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 45326 | 1556 | 2370156 | 7313 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 153573 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026304 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 2 | MOLINO-1102 | 42571102 | FUSE |  | 45326 | 1528 | 2345630 | 8869 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 168511 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024553 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 45326 | 1612 | 2364843 | 5485 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 219400 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023528 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | FUSE |  | 45326 | 1620 | 2364796 | 4510 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 308728 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023517 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | JUMPER |  | 45326 | 1620 | 2364853 | 4295 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4295 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023532 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | SWITCH |  | 45326 | 1000 | 2337506 | 8970 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 699660 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019530 | OH | Sus | 0 | 2024 | FEB | Yes | Force Out | Yes | No
SONOMA | Tier 2 | DUNBAR-1103 | 43071103 | FUSE |  | 45326 | 1138 | 2335662 | 6229 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 205535 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019636 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE |  | 45326 | 1718 | 2348866 | 5609 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 33654 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021218 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | RINCON-1104 | 43321104 | FUSE |  | 45326 | 1717 | 2348535 | 4042 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 440578 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022112 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE |  | 45326 | 1628 | 2368211 | 6936 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 27744 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0024559 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | MIRABEL-1101 | 42091101 | FUSE |  | 45326 | 1459 | 2361702 | 6021 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 54189 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022593 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | MIRABEL-1101 | 42091101 | FUSE |  | 45326 | 1623 | 2361675 | 5717 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5717 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022589 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | MIRABEL-1101 | 42091101 | FUSE |  | 45326 | 1622 | 2368203 | 5742 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 51678 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024554 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONROE-2103 | 43302103 | FUSE |  | 45326 | 1322 | 2339934 | 1342 | Distribution Circuit | Vegetation | Tree - fell into line | 219 | 293898 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019930 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | RINCON-1101 | 43321101 | FUSE |  | 45326 | 1621 | 2363974 | 6845 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 321715 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023221 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | JUMPER |  | 45326 | 1710 | 2370601 | 5788 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 11576 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026485 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 45326 | 1728 | 2348934 | 8406 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 201744 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026794 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 45326 | 1927 | 2345756 | 6913 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 41478 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024679 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER |  | 45326 | 1553 | 2344923 | 7368 | Distribution Circuit | Vegetation | Tree - fell into line | 3479 | 7886778 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020289 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | TRIP-SAVER |  | 45326 | 1458 | 2364622 | 7197 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 333063 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023451 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE |  | 45326 | 1805 | 2365442 | 7075 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 113200 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0023682 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE |  | 45326 | 414 | 2334341 | 6632 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 139272 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019153 | OH | Sus | 0 | 2024 | FEB | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | JUMPER |  | 45326 | 1613 | 2371926 | 8567 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 17134 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027074 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | RECLOSER |  | 45326 | 1735 | 2350892 | 4567 | Distribution Circuit | Vegetation | Tree - branch fell on line | 723 | 1384056 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020718 | OH | Sus | 0 | 2024 | FEB | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE |  | 45326 | 653 | 2334796 | 4580 | Distribution Circuit | Vegetation | Tree - fell into line | 223 | 1015251 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019292 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER |  | 45326 | 1517 | 2343623 | 5566 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 205942 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026201 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE |  | 45326 | 1735 | 2368884 | 5461 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 10922 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0024743 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | FULTON-1107 | 42561107 | FUSE |  | 45326 | 559 | 2334608 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5325 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019203 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | TRIP-SAVER |  | 45326 | 1544 | 2356700 | 5782 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 626518 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023459 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 45326 | 1614 | 2345765 | 5910 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 94560 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026059 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 45326 | 1836 | 2369860 | 8230 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 41150 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026188 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | TRIP-SAVER |  | 45326 | 1836 | 2369869 | 9778 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 195560 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026191 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | FULTON-1107 | 42561107 | FUSE |  | 45326 | 1738 | 2349406 | 5385 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 43080 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023671 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE |  | 45326 | 1710 | 2361943 | 2873 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 129285 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020289 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | RECLOSER |  | 45326 | 1330 | 2337208 | 6076 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 729380 | Clear;32-90 F | Conductor- Overhead | On Ground | 24-0019838 | OH | Sus | 0 | 2024 | FEB | Yes | Force Out | Yes | Yes
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 45326 | 1836 | 2372119 | 9778 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 88002 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027128 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 45326 | 2358 | 2352393 | 5236 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 481712 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021409 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 45326 | 1407 | 2360201 | 9009 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 234234 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022145 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 45326 | 1629 | 2343008 | 8773 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 390693 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021113 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1113 | 42811113 | JUMPER |  | 45326 | 1610 | 2371652 | 8484 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 8484 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026976 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE |  | 45326 | 1407 | 2372669 | 11696 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 187136 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027357 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | RINCON-1103 | 43321103 | FUSE |  | 45326 | 404 | 2334328 | 706 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 13686 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019171 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 45326 | 1407 | 2372705 | 9975 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 79800 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027370 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | JUMPER |  | 45326 | 43 | 2373468 | 12335 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 12335 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0027646 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | JUMPER |  | 45326 | 43 | 2373016 | 11108 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 144404 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0027462 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER |  | 45326 | 22 | 2333989 | 11596 | Distribution Circuit | Vegetation | Tree - fell into line | 318 | 2886571 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019072 | OH | Sus | 35529034 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 45326 | 37 | 2334168 | 9777 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 48885 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019172 | OH | Sus | 31683233 | 2024 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | FULTON-1107 | 42561107 | RECLOSER |  | 45326 | 1811 | 2350975 | 5641 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 270067 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022140 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | FULTON-1107 | 42561107 | FUSE |  | 45326 | 1827 | 2350818 | 5785 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 242970 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0026507 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 45326 | 1407 | 2372697 | 10188 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 30564 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027366 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 45326 | 1424 | 2372878 | 10088 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 70616 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027435 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 45326 | 1407 | 2372713 | 8761 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 17522 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027372 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER |  | 45326 | 1825 | 2350935 | 6035 | Distribution Circuit | Vegetation | Tree - fell into line | 221 | 207547 | Overcast-Heavy Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021137 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 45326 | 1805 | 2365749 | 9609 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 134526 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023807 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | Yes
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE |  | 45326 | 1407 | 2373166 | 11579 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 104211 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027580 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | OTHER |  | 45326 | 2225 | 2365317 | 8255 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 833755 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0023668 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | Yes
SONOMA | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | JUMPER |  | 45326 | 1937 | 2372856 | 8600 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 17200 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027425 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | JUMPER |  | 45326 | 1407 | 2372741 | 11596 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 34788 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027383 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 45326 | 733 | 2337630 | 787 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 49581 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0019546 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
SONOMA | Tier 2 | FORT ROSS-1121 | 42851121 | JUMPER |  | 45326 | 1407 | 2372773 | 11596 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 11596 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0027404 | OH | Sus | 0 | 2024 | FEB | Yes | None | Yes | No
SONOMA | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE |  | 45326 | 1845 | 2351317 | 4335 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 407490 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021983 | OH | Sus | 0 | 2024 | FEB | Yes | Three Phase Fault | Yes | No
SONOMA | Tier 2 | GEYSERVILLE-1102 | 42891102 | FUSE |  | 45326 | 1433 | 2349428 | 5790 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 23160 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020579 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
SONOMA | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE |  | 45326 | 1827 | 2358323 | 4523 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 203535 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021901 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | FROGTOWN-1702 | 163451702 | OTHER |  | 45326 | 1749 | 2349639 | 1326 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6464 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020962 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | Yes
STOCKTON | Tier 2 | CORRAL-1102 | 162991102 | FUSE |  | 45326 | 1752 | 2349720 | 935 | Distribution Circuit | Vegetation | Tree - bark fell into line | 52 | 48620 | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021093 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | CORRAL-1101 | 162991101 | FUSE |  | 45326 | 1445 | 2345092 | 3115 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 24920 | Partly Cloudy-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022367 | OH | Sus | 0 | 2024 | FEB | Yes | Three Phase Fault | Yes | No
STOCKTON | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE |  | 45326 | 1951 | 2353157 | 1446 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4338 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0021823 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 45326 | 1522 | 2345715 | 1409 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 67632 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020323 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER |  | 45326 | 1954 | 2353378 | 985 | Distribution Circuit | Vegetation | Tree - fell into line | 420 | 213234 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020971 | OH | Sus | 0 | 2024 | FEB | Yes | Open Circuit | Yes | No
STOCKTON | Tier 2 | CLAY-1103 | 163341103 | FUSE |  | 45326 | 1754 | 2350035 | 397 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3573 | Overcast-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020996 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 2 | MARTELL-1102 | 163011102 | RECLOSER |  | 45326 | 1608 | 2345435 | 1063 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1138 | 288690 | Partly Cloudy-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020531 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | ELECTRA-1101 | 162161101 | TRIP-SAVER |  | 45326 | 1959 | 2353343 | 1341 | Distribution Circuit | Vegetation | Tree - fell into line | 248 | 77508 | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021230 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | MARTELL-1102 | 163011102 | RECLOSER |  | 45326 | 1335 | 2340161 | 640 | Distribution Circuit | Vegetation | Tree - branch fell on line | 64 | 6678 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0019849 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
STOCKTON | Tier 3 | WEST POINT-1102 | 163201102 | JUMPER |  | 45326 | 1735 | 2360238 | 1508 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4524 | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0022159 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | CURTIS-1703 | 163351703 | RECLOSER |  | 45326 | 1540 | 2344386 | 1383 | Distribution Circuit | Vegetation | Tree - fell into line | 610 | 600145 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020287 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | FUSE |  | 45326 | 1751 | 2349637 | 1571 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 95831 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0021158 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER |  | 45326 | 1736 | 2350011 | 1206 | Distribution Circuit | Equipment Failure/Involved | Overhead | 150 | 57576 | Overcast-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0020966 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 2 | PEORIA FLAT-1705 | 163781705 | FUSE |  | 45326 | 1424 | 2341467 | 276 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1380 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020198 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER |  | 45326 | 1732 | 2349288 | 1673 | Distribution Circuit | Vegetation | Tree - fell into line | 2882 | 527666 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020867 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | MIWUK-1701 | 163661701 | FUSE |  | 45326 | 1408 | 2341032 | 1854 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 34378 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0020154 | OH | Sus | 0 | 2024 | FEB | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2201 | 182852201 | OCB |  | 45352 | 235 | 2391724 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 1939 | 115078 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0035822 | OH | Sus | 31685408 | 2024 | MAR | Yes | Multi-Fault | Yes | No
CENTRAL COAST | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE |  | 45352 | 2205 | 2393802 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3360 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036745 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER |  | 45352 | 2041 | 2393423 | 641 | Distribution Circuit | Equipment Failure/Involved | Overhead | 175 | 41543 | Overcast-Drizzle-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036517 | OH | Sus | 31685464 | 2024 | MAR | Yes | Line to Ground | Yes | Yes
HUMBOLDT | Tier 2 | GUALALA-1112 | 42841112 | FUSE |  | 45352 | 2221 | 2393853 | 1110 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 7770 | Overcast-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036952 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | MIDDLETOWN-1101 | 43141101 | TRIP-SAVER |  | 45352 | 2044 | 2393441 | 820 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 80360 | Clear-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036767 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 3 | WILLITS-1104 | 42661104 | RECLOSER |  | 45352 | 1825 | 2392785 | 1066 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 64016 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036381 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER |  | 45352 | 1830 | 2392817 | 1193 | Distribution Circuit | Vegetation | Tree - fell into line | 869 | 461132 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036383 | OH | Sus | 0 | 2024 | MAR | Yes | Multi-Fault | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | RECLOSER |  | 45352 | 1943 | 2392843 | 1397 | Distribution Circuit | Vegetation | Tree - fell into line | 198 | 192867 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036422 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE |  | 45352 | 1844 | 2393476 | 1525 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 9150 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036422 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 45352 | 1645 | 2392546 | 1097 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8776 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036622 | OH | Sus | 0 | 2024 | MAR | Yes | Three Phase Fault | Yes | No
HUMBOLDT | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER |  | 45352 | 1019 | 2391944 | 538 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 21442 | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0035998 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
HUMBOLDT | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE |  | 45352 | 1438 | 2392303 | 1464 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 19032 | Clear-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 24-0036969 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | FRUITLAND-1141 | 192311141 | FUSE |  | 45352 | 1550 | 2392950 | 1410 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 135360 | Overcast-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036254 | OH | Sus | 0 | 2024 | MAR | Yes | None | Yes | No
HUMBOLDT | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER |  | 45352 | 1543 | 2392451 | 2919 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 75894 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036241 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Line | Yes | No
HUMBOLDT | Tier 2 | HOOPA-1101 | 192401101 | FUSE |  | 45352 | 1749 | 2392487 | 1105 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 11050 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036384 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE |  | 45352 | 1700 | 2392557 | 444 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 19092 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036368 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2105 | 43432105 | RECLOSER |  | 45352 | 2002 | 2393260 | 1421 | Distribution Circuit | Equipment Failure/Involved | Overhead | 134 | 134742 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on object | 24-0036436 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | FUSE |  | 45352 | 1959 | 2393747 | 1150 | Distribution Circuit | Vegetation | Tree - fell into line | 187 | 215050 | Overcast-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036733 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
NORTH VALLEY | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER |  | 45352 | 2345 | 2394078 | 4000 | Distribution Circuit | Vegetation | Tree - fell into line | 174 | 246286 | Overcast-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0036609 | OH | Sus | 0 | 2024 | MAR | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER |  | 45352 | 2320 | 2393974 | 2503 | Distribution Circuit | Vegetation | Tree - fell into line | 636 | 511378 | Overcast-Snow-Strong Winds;Below 32 F | Pole-Wood | Broken- wire on ground | 24-0036594 | OH | Sus | 0 | 2024 | MAR | Yes | Multi-Fault | Yes | No
NORTH VALLEY | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER |  | 45352 | 2327 | s1921645 | 944 | Distribution Circuit | Vegetation | Tree - fell into line | 606 | 572064 | Clear;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0036594 | OH | Sus | 0 | 2024 | MAR | Yes | Three Phase Fault | Yes | No
NORTH VALLEY | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | FUSE |  | 45352 | 1945 | s1921559 | 2650 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 66330 | Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0036515 | OH | Sus | 0 | 2024 | MAR | Yes | Three Phase Fault | Yes | No
PENINSULA | Tier 2 | MENLO-1103 | 24131103 | FUSE |  | 45352 | 1825 | 2392779 | 370 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2590 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036545 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
SAN JOSE | Tier 3 | MORGAN HILL-2111 | 83242111 | RECLOSER |  | 45352 | 348 | 2391741 | 497 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 9753 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0035824 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | FUSE |  | 45352 | 2236 | 2393882 | 1242 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 45622 | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0036818 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE |  | 45352 | 2337 | 2394556 | 841 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 9251 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | On Ground | 24-0036750 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER |  | 45352 | 2108 | 2393592 | 1097 | Distribution Circuit | Vegetation | Tree - fell into line | 411 | 297240 | Overcast-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036504 | OH | Sus | 0 | 2024 | MAR | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER |  | 45352 | 2139 | 2393678 | 1177 | Distribution Circuit | Vegetation | Tree - fell into line | 294 | 243443 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036523 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | AUBURN-1101 | 152161101 | FUSE |  | 45352 | 1847 | 2392857 | 960 | Distribution Circuit | Equipment Failure/Involved | Overhead | 138 | 130504 | Overcast;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0036444 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER |  | 45352 | 2243 | 2393891 | 2680 | Distribution Circuit | Vegetation | Tree - fell into line | 1037 | 1688686 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036565 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE |  | 45352 | 2152 | 2393725 | 1291 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 63259 | Overcast-Rain-Strong Winds;32-90 F | Transformer (OH) | Broken- wire on ground | 24-0036910 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE |  | 45352 | 1848 | 2392855 | 1407 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 15477 | Overcast;32-90 F | Pole-Wood | Broken- wire on ground | 24-0036435 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HALSEY-1102 | 152241102 | FUSE |  | 45352 | 2320 | 2393967 | 1063 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 114804 | Overcast-Fog;32-90 F | Pole-Wood | Broken- wire on ground | 24-0036783 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | HALSEY-1101 | 152241101 | FUSE |  | 45352 | 2142 | 2393661 | 1131 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 24882 | Overcast-Fog;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036880 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | RECLOSER |  | 45352 | 1905 | 2392900 | 958 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2184 | 361984 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036403 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | WEIMAR-1102 | 152491102 | FUSE |  | 45352 | 2049 | 2393452 | 1000 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 12000 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036584 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | FORESTHILL-1101 | 152181101 | RECLOSER |  | 45352 | 1757 | 2392738 | 1480 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 108257 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036363 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1101 | 152031101 | FUSE |  | 45352 | 2151 | 2393726 | 2185 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 92226 | Overcast-Fog-Rain-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0036732 | OH | Sus | 0 | 2024 | MAR | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | SHADY GLEN-1102 | 152431102 | RECLOSER |  | 45352 | 2149 | 2393692 | 920 | Distribution Circuit | Vegetation | Tree - fell into line | 770 | 700907 | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0036608 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE |  | 45352 | 2146 | 2393677 | 999 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 45972 | Overcast-Fog-Drizzle-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0036582 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 3 | SHADY GLEN-1102 | 152431102 | FUSE |  | 45352 | 2149 | 2394950 | 2321 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 9284 | Overcast-Fog-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0036924 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | GRASS VALLEY-1103 | 152031103 | OTHER |  | 45352 | 1908 | 2393269 | 1194 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 34110 | Overcast-Fog-Rain-Strong Winds;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0036428 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | Yes
SIERRA | Tier 3 | BRUNSWICK-1102 | 152481102 | RECLOSER |  | 45352 | 1822 | 2392936 | 1250 | Distribution Circuit | Vegetation | Tree - fell into line | 672 | 584520 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036378 | OH | Sus | 0 | 2024 | MAR | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER |  | 45352 | 2331 | 2394708 | 1101 | Distribution Circuit | Vegetation | Tree - fell into line | 460 | 313184 | Overcast-Fog-Heavy Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036531 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1105 | 152481105 | RECLOSER |  | 45352 | 2147 | 2393702 | 2694 | Distribution Circuit | Vegetation | Tree - fell into line | 1914 | 2764131 | Overcast-Fog-Heavy Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0036531 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | NARROWS-2102 | 153132102 | FUSE |  | 45352 | 1748 | 2392720 | 1095 | Distribution Circuit | Vegetation | Tree - fell into line | 248 | 271560 | Overcast-Fog-Drizzle;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036412 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | DRUM-1101 | 152321101 | RECLOSER |  | 45352 | 1906 | 2392923 | 4232 | Distribution Circuit | Vegetation | Tree - fell into line | 174 | 317040 | Overcast-Fog-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0036410 | OH | Sus | 0 | 2024 | MAR | Yes | Multi-Fault | Yes | No
SIERRA | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE |  | 45352 | 2249 | 2393902 | 893 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 40185 | Overcast-Fog-Rain;32-90 F | Crossarm- Wood | Broken- wire on ground | 24-0036619 | OH | Sus | 0 | 2024 | MAR | Yes | Three Phase Fault | Yes | No
SIERRA | Tier 3 | DRUM-1101 | 152321101 | FUSE |  | 45352 | 1906 | 2395162 | 4232 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 63480 | Overcast-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036980 | OH | Sus | 0 | 2024 | MAR | Yes | None | Yes | No
SIERRA | Tier 3 | BRUNSWICK-1103 | 152481103 | OTHER |  | 45352 | 1822 | 2392807 | 1508 | Distribution Circuit | Vegetation | Tree - fell into line | 471 | 372673 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036386 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 3 | DRUM-1101 | 152321101 | FUSE |  | 45352 | 1906 | 2395389 | 4238 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 67808 | Overcast-Snow-Strong Winds;Below 32 F | Crossarm- Wood | Broken- wire on ground | 24-0036410 | OH | Sus | 0 | 2024 | MAR | Yes | None | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE |  | 45352 | 549 | 2391770 | 4977 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 308574 | Overcast-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0036100 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE |  | 45352 | 844 | 2391866 | 7608 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 213024 | Overcast-Snow-Strong Winds;Below 32 F | Pole-Wood | Broken- wire on ground | 24-0036240 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | TAMARACK-1101 | 152291101 | FUSE |  | 45352 | 1210 | 2392040 | 5967 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 334152 | Overcast-Fog-Snow-Strong Winds;Below 32 F | Crossarm- Wood | Broken- wire on ground | 24-0036202 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Line | Yes | No
SIERRA | Tier 2 | SPAULDING-1101 | 152251101 | FUSE |  | 45352 | 1946 | 2394157 | 2551 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 45918 | Overcast-Snow-Strong Winds;Below 32 F | Transformer (OH) | Broken- wire on ground | 24-0036632 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | SPAULDING-1101 | 152251101 | RECLOSER |  | 45352 | 2332 | 2393072 | 95 | Distribution Circuit | Equipment Failure/Involved | Overhead | 155 | 14725 | Overcast-Snow-Strong Winds;Below 32 F | Transformer (OH) | Broken- wire on ground | 24-0036602 | OH | Sus | 0 | 2024 | MAR | Yes | Force Out | Yes | No
SIERRA | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE |  | 45352 | 2124 | 2393632 | 1132 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 35420 | Overcast-Fog-Rain-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036558 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
SIERRA | Tier 2 | ALLEGHANY-1101 | 152101101 | SWITCH |  | 45352 | 1727 | 2395133 | 2704 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 256880 | Overcast-Snow-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0036334 | OH | Sus | 0 | 2024 | MAR | Yes | None | Yes | No
SONOMA | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER |  | 45352 | 2103 | 2393564 | 147 | Distribution Circuit | Vegetation | Tree - fell into line | 1571 | 219604 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036495 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 45352 | 2354 | 2394174 | 1356 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 36469 | Heavy Rain-Strong Winds-Rain-Clear;32-90 F | Pole-Wood | Broken- wire on ground | 24-0036940 | OH | Sus | 35534413 | 2024 | MAR | Yes | Multi-Fault | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | SWITCH |  | 45352 | 2100 | 2394101 | 1159 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 32452 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036620 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE |  | 45352 | 2100 | 2393519 | 226 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 5876 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036618 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | FUSE |  | 45352 | 1936 | 2393611 | 1230 | Distribution Circuit | Vegetation | Tree - fell into line | 757 | 303727 | Partly Cloudy-Rain;32-90 F | Pole-Wood | Broken- wire on ground | 24-0036593 | OH | Sus | 3554413 | 2024 | MAR | Yes | Line to Line | Yes | No
SONOMA | Tier 3 | MIRABEL-1102 | 42091102 | RECLOSER |  | 45352 | 1939 | 2392996 | 1149 | Distribution Circuit | Vegetation | Tree - branch fell on line | 179 | 212473 | Partly Cloudy-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036450 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE |  | 45352 | 1944 | 2393048 | 1113 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 17808 | Clear-Strong Winds;32-90 F | Pole-Wood | Broken- wire on ground | 24-0036470 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 3 | STANISLAUS-1702 | 162821702 | TRIP-SAVER |  | 45352 | 2212 | 2393959 | 933 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 80504 | Overcast-Fog-Heavy Rain-Strong Winds;32-90 F | Bushing | Broken- wire on ground | 24-0036588 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
STOCKTON | Tier 2 | SALT SPRINGS-2102 | 163692102 | RECLOSER |  | 45352 | 1626 | 2392521 | 342 | Distribution Circuit | Vegetation | Tree - fell into line | 2019 | 48522 | Overcast-Fog-Snow-Strong Winds;Below 32 F | Pole-Wood | Broken- wire on ground | 24-0036276 | OH | Sus | 0 | 2024 | MAR | Yes | Three Phase Fault | Yes | No
YOSEMITE | Tier 2 | CURTIS-1703 | 163351703 | FUSE |  | 45352 | 1413 | 2392273 | 317 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 6023 | Overcast-Fog-Rain;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036232 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER |  | 45352 | 2340 | 2395405 | 2412 | Distribution Circuit | Vegetation | Tree - fell into line | 344 | 712191 | Clear-Strong Winds;Below 32 F | Pole-Wood | Broken- wire on ground | 24-0036601 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE |  | 45352 | 2340 | 2395399 | 2384 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 317410 | Clear-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0037012 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE |  | 45352 | 2340 | s1922151 | 3795 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 53130 | Clear-Strong Winds;Below 32 F | Conductor- Overhead | Broken- wire on ground | 24-0037012 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER |  | 45352 | 1812 | 2392753 | 1311 | Distribution Circuit | Environmental/External | Ice or snow | 1536 | 925712 | Overcast-Fog-Snow-Strong Winds;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0036374 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Ground | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER |  | 45352 | 2252 | 2393857 | 2552 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 266764 | Overcast-Fog-Snow-Strong Winds;Below 32 F | Pole-Wood | Broken- wire on ground | 24-0036573 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Line | Yes | No
YOSEMITE | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE |  | 45352 | 2229 | 2396211 | 3959 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 190032 | Clear-Strong Winds;Below 32 F | Pole-Wood | Broken- wire on ground | 24-0036573 | OH | Sus | 0 | 2024 | MAR | Yes | Line to Line | Yes | No
CENTRAL COAST | Tier 2 | VIEJO-2204 | 182852204 | OCB |  | 45601 | 1843 | 2614703 | 366 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8532 | 2131434 | Clear;32-90 F | Connector or Splice (OH) | Broken- wire on ground | 24-0132279 | OH | Sus | 46381935 | 2024 | NOV | Yes | Line to Ground | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | SWITCH |  | 45601 | 2311 | 2615125 | 1072 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 59 | 63248 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0131208 | OH | Sus | 0 | 2024 | NOV | Yes | None | Yes | No
CENTRAL COAST | Tier 3 | ROB ROY-2104 | 83692104 | FUSE |  | 45601 | 2311 | 2617170 | 1436 | Distribution Circuit | Vegetation | Tree - branch fell on line | 49 | 70364 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0131208 | OH | Sus | 0 | 2024 | NOV | Yes | Force Out | Yes | No
DE ANZA | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER |  | 45601 | 2329 | 2615151 | 2186 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 133 | 290738 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on object | 24-0131754 | OH | Sus | 0 | 2024 | NOV | Yes | Force Out | Yes | No
SONOMA | Tier 3 | SONOMA-1103 | 42721103 | RECLOSER |  | 45601 | 1947 | 2614810 | 2623 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 139 | 339791 | Partly Cloudy;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0131826 | OH | Sus | 0 | 2024 | NOV | Yes | None | Yes | No
HUMBOLDT | Tier 2 | FORT BRAGG A-1102 | 42761102 | OTHER |  | 45582 | 1009 | 2596992 | 251 | Distribution Circuit | 3rd Party | Vehicle | 495 | 58498 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0124479 | OH | Sus | 31713064 | 2024 | OCT | Yes | Line to Ground | Yes | Yes
NORTH BAY | Tier 3 | SILVERADO-2104 | 43432104 | SWITCH |  | 45582 | 1830 | 2597733 | 4001 | Distribution Circuit | Wildfire Mitigation | Public Safety Power Shut-off | 1710 | 6114838 | Clear;32-90 F | Conductor- Overhead | Broken- wire on ground | 24-0123684 | OH | Sus | 0 | 2024 | OCT | Yes | Force Out | Yes | No

## Metric 3.01
Metric 3.01: Wires Down MEDs (Distribution)
Definition | (# Events/HFTD Circuit Miles (D))*1000
2022 HFTD Circuit Miles (D) | 25270.5
2023 HFTD Circuit Miles (D) | 25059.94
2024 HFTD Circuit Miles (D) | 24878.17
2025 HFTD Circuit Miles (D) | 24673.07
2025 Target | 107.4958
Year | WD Events | WD Events/1,000 Miles
2013 | 131 | 5.1839
2014 | 440 | 17.4116
2015 | 388 | 15.3539
2016 | 180 | 7.1229
2017 | 1724 | 68.2218
2018 | 116 | 4.5903
2019 | 1622 | 64.1855
2020 | 529 | 20.9335
2021 | 2048 | 81.0431
2022 | 162 | 6.4106
2023 | 2354 | 93.9348
2024 | 744 | 29.9057
2025 (Jan-Jun) | 0 | 0
|  | 34.1628 | STD
|  | 39.1702 | Average
|  | 73.333 | 1 STD
| Target 2025/2029 | 107.4958 | 2 STD

## HFTD WD MED Summary
HFTD WIRE-DOWN OUTAGE DETAILS (2013 - June 2025)
System | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
SYSTEM | 2013 | 0 | 0 | 0 | 40 | 0 | 1 | 0 | 0 | 0 | 0 | 90 | 0 | 131
SYSTEM | 2014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 438 | 440
SYSTEM | 2015 | 0 | 284 | 0 | 1 | 0 | 5 | 7 | 0 | 0 | 2 | 0 | 89 | 388
SYSTEM | 2016 | 0 | 49 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 0 | 180
SYSTEM | 2017 | 924 | 483 | 0 | 112 | 0 | 2 | 0 | 0 | 13 | 140 | 0 | 50 | 1724
SYSTEM | 2018 | 0 | 0 | 55 | 0 | 0 | 0 | 8 | 0 | 0 | 5 | 48 | 0 | 116
SYSTEM | 2019 | 330 | 1024 | 0 | 0 | 0 | 11 | 0 | 1 | 6 | 122 | 128 | 0 | 1622
SYSTEM | 2020 | 60 | 120 | 235 | 0 | 0 | 0 | 0 | 63 | 21 | 30 | 0 | 0 | 529
SYSTEM | 2021 | 756 | 0 | 0 | 0 | 0 | 0 | 3 | 10 | 2 | 239 | 0 | 1038 | 2048
SYSTEM | 2022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 158 | 162
SYSTEM | 2023 | 943 | 973 | 436 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2354
SYSTEM | 2024 | 0 | 486 | 74 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 177 | 744
SYSTEM | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0
System | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
10-Year Averages (2015-2024) | Count of Events | 301.3 | 341.9 | 91.9 | 11.3 | 0 | 1.8 | 1.8 | 7.4 | 4.8 | 55.2 | 18.1 | 151.2 | 986.7
| Monthly Percentage | 30.54% | 34.65% | 9.314% | 1.145% | 0% | 0.1824% | 0.1824% | 0.75% | 0.4865% | 5.594% | 1.834% | 15.32% | 100%
System | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Targets | 2025 | 32.8251 | 37.2482 | 10.012 | 1.2311 | 0 | 0.1961 | 0.1961 | 0.80619 | 0.52294 | 6.0138 | 1.9719 | 16.4725 | 107.4958
System | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Events | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0
Monthly Metric | 2025 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0
YTD Metric | 2025 | 0 | 0 | 0 | 0 | 0 | 0

## OH Dlines in HFTD
Source: Extracted from EDGIS as of 1/1/2025.
CIRCUITNAME | CIRCUITID | TOTALMILES | T3MILES | T2MILES | Z1MILES | T1MILES
18TH STREET 0401 | 22390401 | 1.28 |  |  |  | 1.28
18TH STREET 0402 | 22390402 | 1.82 |  |  |  | 1.82
21ST AVENUE 0401 | 22550401 | 1.92 |  |  |  | 1.92
21ST AVENUE 0402 | 22550402 | 3.37 |  |  |  | 3.37
21ST AVENUE 0403 | 22550403 | 1.9 |  |  |  | 1.9
6TH AVENUE 0401 | 22530401 | 1.27 |  |  |  | 1.27
6TH AVENUE 0402 | 22530402 | 1.22 |  |  |  | 1.22
6TH AVENUE 0403 | 22530403 | 1.79 |  |  |  | 1.79
7TH STANDARD 2101 | 254582101 | 2.21 |  |  |  | 2.21
7TH STANDARD 2102 | 254582102 | 16.49 |  |  |  | 16.49
7TH STANDARD 2103 | 254582103 | 22.55 |  |  |  | 22.55
7TH STANDARD 2104 | 254582104 | 0.03 |  |  |  | 0.03
8TH AVENUE 0401 | 12670401 | 4.92 |  |  |  | 4.92
ACTON 0401 | 22470401 | 3.88 |  |  |  | 3.88
ACTON 0402 | 22470402 | 4.47 |  |  |  | 4.47
AIRWAYS 1101 | 252041101 | 0.96 |  |  |  | 0.96
AIRWAYS 1102 | 252041102 | 7.55 |  |  |  | 7.55
AIRWAYS 1103 | 252041103 | 7.51 |  |  |  | 7.51
AIRWAYS 1104 | 252041104 | 1.78 |  |  |  | 1.78
AIRWAYS 1105 | 252041105 | 1.37 |  |  |  | 1.37
AIRWAYS 1106 | 252041106 | 7.4 |  |  |  | 7.4
AIRWAYS 1107 | 252041107 | 43.32 |  |  |  | 43.32
AIRWAYS 1108 | 252041108 | 11.68 |  |  |  | 11.68
ALHAMBRA 1101 | 14101101 | 8.4 |  |  |  | 8.4
ALHAMBRA 1102 | 14101102 | 14.22 |  | 0.16 |  | 14.06
ALHAMBRA 1105 | 14101105 | 44.68 | 0.85 | 36.44 |  | 7.39
ALLEGHANY 1101 | 152101101 | 76.47 | 31.58 | 27.12 | 9.8 | 7.97
ALLEGHANY 1102 | 152101102 | 17.6 | 17.6 |  |  | 0
ALMADEN 1101 | 82311101 | 18.46 |  |  | 0 | 18.46
ALMADEN 1102 | 82311102 | 21.95 |  |  |  | 21.95
ALMADEN 1110 | 82311110 | 8.5 |  |  |  | 8.5
ALMADEN 1111 | 82311111 | 9.82 |  |  | 0.04 | 9.78
ALPAUGH 1103 | 254001103 | 26.89 |  |  |  | 26.89
ALPAUGH 1104 | 254001104 | 51.55 |  |  |  | 51.55
ALPAUGH 1106 | 254001106 | 52.4 |  |  |  | 52.4
ALPINE 1101 | 163561101 | 0.9 |  |  | 0.82 | 0.08
ALTO 1120 | 42031120 | 20.5 |  | 3.96 |  | 16.54
ALTO 1121 | 42031121 | 15.42 |  |  | 0.34 | 15.08
ALTO 1122 | 42031122 | 22.38 | 9.12 | 3.72 | 0.18 | 9.36
ALTO 1123 | 42031123 | 10.36 |  | 0.47 |  | 9.89
ALTO 1124 | 42031124 | 35.01 | 27.95 |  |  | 7.06
ALTO 1125 | 42031125 | 44.89 | 26.39 | 10.98 |  | 7.52
AMES 1101 | 83901101 | 0.12 |  |  |  | 0.12
AMES 1102 | 83901102 | 3.3 |  |  |  | 3.3
ANDERSON 1101 | 103261101 | 19.87 |  | 10.93 |  | 8.94
ANDERSON 1102 | 103261102 | 3.29 |  |  |  | 3.29
ANDERSON 1103 | 103261103 | 28.38 |  | 4.86 |  | 23.52
ANGIOLA 1102 | 252151102 | 0.15 |  |  |  | 0.15
ANGIOLA 1104 | 252151104 | 0.18 |  |  |  | 0.18
ANGIOLA 1123 | 252151123 | 101.91 |  |  |  | 101.91
ANITA 1101 | 102841101 | 34.64 |  |  |  | 34.64
ANITA 1102 | 102841102 | 30.82 |  |  |  | 30.82
ANITA 1105 | 102841105 | 16.86 |  |  |  | 16.86
ANITA 1106 | 102841106 | 94.67 |  | 0.48 |  | 94.19
ANNAPOLIS 1101 | 42861101 | 50.83 |  | 50.83 |  | 0
ANTELOPE 1101 | 252021101 | 40.18 |  | 0.92 |  | 39.26
ANTELOPE 1102 | 252021102 | 25.53 |  |  |  | 25.53
ANTLER 1101 | 103271101 | 58.91 | 8.17 | 49.64 |  | 1.1
APPLE HILL 1103 | 153661103 | 59.87 | 14.79 | 35.14 | 0.01 | 9.93
APPLE HILL 1104 | 153661104 | 95.33 | 55.39 | 35.31 |  | 4.63
APPLE HILL 2102 | 153662102 | 359.63 | 123.35 | 223.49 | 0.06 | 12.73
ARANA 0401 | 83010401 | 3.49 |  |  |  | 3.49
ARANA 0402 | 83010402 | 3 |  |  |  | 3
ARBUCKLE 1101 | 62081101 | 60.53 |  |  |  | 60.53
ARBUCKLE 1102 | 62081102 | 59.19 |  |  |  | 59.19
ARBUCKLE 1104 | 62081104 | 56.71 |  |  |  | 56.71
ARCATA 1105 | 192021105 | 44.09 |  |  |  | 44.09
ARCATA 1106 | 192021106 | 10.27 |  |  |  | 10.27
ARCATA 1121 | 192021121 | 29.08 |  | 6.84 |  | 22.24
ARCATA 1122 | 192021122 | 68.43 |  | 20.44 |  | 47.99
ARCATA 1123 | 192021123 | 5.99 |  |  |  | 5.99
ARCATA 1124 | 192021124 | 0 |  |  |  | 0
ARLINGTON 0401 | 13700401 | 4.18 |  | 0.94 |  | 3.24
ARVIN 1101 | 253801101 | 27.51 |  | 0.1 |  | 27.41
ARVIN 1102 | 253801102 | 17.55 |  |  |  | 17.55
ARVIN 1103 | 253801103 | 20.56 |  |  |  | 20.56
ASHLAN AVE 1102 | 252051102 | 13.28 |  |  |  | 13.28
ASHLAN AVE 1103 | 252051103 | 9.33 |  |  |  | 9.33
ASHLAN AVE 1104 | 252051104 | 13.81 |  |  |  | 13.81
ASHLAN AVE 1106 | 252051106 | 17.06 |  |  |  | 17.06
ASHLAN AVE 1107 | 252051107 | 8.36 |  |  |  | 8.36
ASHLAN AVE 1108 | 252051108 | 11.03 |  |  |  | 11.03
ASHLAN AVE 1109 | 252051109 | 14.55 |  |  |  | 14.55
ASHLAN AVE 1111 | 252051111 | 7.96 |  |  |  | 7.96
ASHLAN AVE 1112 | 252051112 | 9.19 |  |  |  | 9.19
ASHLAN AVE 1113 | 252051113 | 9.67 |  |  |  | 9.67
ASHLAN AVE 1114 | 252051114 | 8.4 |  |  |  | 8.4
ASHLAN AVE 1116 | 252051116 | 19.17 |  |  |  | 19.17
ASHLAN AVE 2101 | 252052101 | 2.23 |  |  |  | 2.23
ASHLAN AVE 2105 | 252052105 | 16.43 |  |  |  | 16.43
ASHLAN AVE 2110 | 252052110 | 6.76 |  |  |  | 6.76
ASHLAN AVE 2115 | 252052115 | 5.53 |  |  |  | 5.53
ASHLAN AVE 2117 | 252052117 | 1.88 |  |  |  | 1.88
ASHLAN AVE 2118 | 252052118 | 9.59 |  |  |  | 9.59
ASHLAN AVE 2119 | 252052119 | 14.1 |  |  |  | 14.1
ATASCADERO 1101 | 182541101 | 33.6 | 0.79 | 16.96 |  | 15.85
ATASCADERO 1102 | 182541102 | 17.46 |  | 3.41 |  | 14.05
ATASCADERO 1103 | 182541103 | 127.91 | 37.15 | 56.11 |  | 34.65
ATWATER 1102 | 253611102 | 84.49 |  |  |  | 84.49
ATWATER 1103 | 253611103 | 23.24 |  |  |  | 23.24
ATWATER 1104 | 253611104 | 12.93 |  |  |  | 12.93
ATWATER 1105 | 253611105 | 6.86 |  |  |  | 6.86
ATWATER 1106 | 253611106 | 36.74 |  |  |  | 36.74
ATWATER 1107 | 253611107 | 30.38 |  |  |  | 30.38
ATWATER 1108 | 253611108 | 61.16 |  |  |  | 61.16
AUBERRY 1101 | 254151101 | 241.27 | 32.36 | 206.61 |  | 2.3
AUBERRY 1102 | 254151102 | 128.8 |  | 128.8 |  | 0
AUBURN 1101 | 152161101 | 4.93 |  | 3.14 |  | 1.79
AUBURN 1102 | 152161102 | 8.95 |  | 2.97 | 0.03 | 5.95
AVENA 1701 | 163571701 | 90.87 |  |  |  | 90.87
AVENA 1702 | 163571702 | 80.51 |  |  |  | 80.51
AVENAL 2101 | 255002101 | 67.87 |  |  |  | 67.87
AVENAL 2102 | 255002102 | 2.46 |  |  |  | 2.46
AVENAL 2103 | 255002103 | 2.45 |  |  |  | 2.45
BABEL 0401 | 13850401 | 3.09 |  |  |  | 3.09
BAHIA 1101 | 43251101 | 3.06 |  |  |  | 3.06
BAHIA 1102 | 43251102 | 14.22 |  |  |  | 14.22
BAHIA 1103 | 43251103 | 11.08 |  |  |  | 11.08
BAHIA 1104 | 43251104 | 18.32 |  |  |  | 18.32
BAHIA 1105 | 43251105 | 14.07 |  |  |  | 14.07
BAIR 1103 | 24261103 | 0.53 |  |  |  | 0.53
BAIR 1105 | 24261105 | 2.28 |  |  |  | 2.28
BAKERSFIELD 1101 | 253371101 | 7.5 |  |  |  | 7.5
BAKERSFIELD 1102 | 253371102 | 17.71 |  |  |  | 17.71
BAKERSFIELD 1105 | 253371105 | 6.49 |  |  |  | 6.49
BAKERSFIELD 1106 | 253371106 | 11.85 |  |  |  | 11.85
BAKERSFIELD 1107 | 253371107 | 3.69 |  |  |  | 3.69
BAKERSFIELD 1110 | 253371110 | 5.98 |  |  |  | 5.98
BAKERSFIELD 1114 | 253371114 | 15.85 |  |  |  | 15.85
BAKERSFIELD 1115 | 253371115 | 5.72 |  |  |  | 5.72
BAKERSFIELD 1116 | 253371116 | 16.82 |  |  |  | 16.82
BAKERSFIELD 1118 | 253371118 | 11.44 |  |  |  | 11.44
BAKERSFIELD 2104 | 253372104 | 37.74 |  |  |  | 37.74
BAKERSFIELD 2106 | 253372106 | 31.93 |  |  |  | 31.93
BAKERSFIELD 2107 | 253372107 | 0 |  |  |  | 0
BAKERSFIELD 2109 | 253372109 | 27.69 |  |  |  | 27.69
BALCH NO 1 1101 | 252501101 | 14.57 |  | 14.57 |  | 0
BALFOUR 1101 | 14321101 | 50.09 |  |  |  | 50.09
BANCROFT 0401 | 13030401 | 5.06 |  | 0 |  | 5.06
BANCROFT 0402 | 13030402 | 4.59 |  | 0.12 |  | 4.47
BANGOR 1101 | 103191101 | 197.96 | 1.73 | 187.97 |  | 8.26
BANTA 1101 | 162471101 | 0.06 |  |  |  | 0.06
BANTA 1102 | 162471102 | 0.05 |  |  |  | 0.05
BANTA 1103 | 162471103 | 0.13 |  |  |  | 0.13
BARRETT 0401 | 13020401 | 6.63 |  |  |  | 6.63
BARRETT 0402 | 13020402 | 6 |  |  |  | 6
BARRY 1101 | 152111101 | 32.06 |  |  |  | 32.06
BARRY 1102 | 152111102 | 17.82 |  |  |  | 17.82
BARRY 1103 | 152111103 | 33.13 |  |  |  | 33.13
BARTON 1101 | 253571101 | 6 |  |  |  | 6
BARTON 1102 | 253571102 | 4.5 |  |  |  | 4.5
BARTON 1104 | 253571104 | 9.41 |  |  |  | 9.41
BARTON 1105 | 253571105 | 4.82 |  |  |  | 4.82
BARTON 1106 | 253571106 | 5.96 |  |  |  | 5.96
BARTON 1108 | 253571108 | 19.11 |  |  |  | 19.11
BARTON 1109 | 253571109 | 4.48 |  |  |  | 4.48
BARTON 1110 | 253571110 | 16.61 |  |  |  | 16.61
BARTON 1111 | 253571111 | 15.69 |  |  |  | 15.69
BARTON 1112 | 253571112 | 3.35 |  |  |  | 3.35
BARTON 1114 | 253571114 | 12.89 |  |  |  | 12.89
BARTON 1115 | 253571115 | 13.06 |  |  |  | 13.06
BARTON 1116 | 253571116 | 9.35 |  |  |  | 9.35
BASALT 1101 | 42461101 | 10.93 |  |  |  | 10.93
BASALT 1104 | 42461104 | 0.69 |  |  |  | 0.69
BASALT 1105 | 42461105 | 1.43 |  |  |  | 1.43
BASALT 1106 | 42461106 | 69.12 |  | 2.01 | 0.06 | 67.05
BAY MEADOWS 1102 | 24011102 | 4.97 |  |  |  | 4.97
BAY MEADOWS 1103 | 24011103 | 6.88 |  |  |  | 6.88
BAY MEADOWS 1104 | 24011104 | 16.81 |  |  |  | 16.81
BAY MEADOWS 1105 | 24011105 | 6.68 |  |  |  | 6.68
BAY MEADOWS 1106 | 24011106 | 0.86 |  |  |  | 0.86
BAY MEADOWS 1107 | 24011107 | 3.18 |  |  |  | 3.18
BAY MEADOWS 1108 | 24011108 | 1.05 |  |  |  | 1.05
BAY MEADOWS 2101 | 24012101 | 18.02 |  |  |  | 18.02
BAY MEADOWS 2102 | 24012102 | 14.32 |  | 3.99 |  | 10.33
BAY MEADOWS 2103 | 24012103 | 0 |  |  |  | 0
BAYWOOD 1101 | 182801101 | 29 |  | 3.34 |  | 25.66
BEACH (Q) 0402 | 22340402 | 2.04 |  |  |  | 2.04
BEAR VALLEY 2101 | 252192101 | 168.58 |  | 102.25 |  | 66.33
BEAR VALLEY 2105 | 252192105 | 154.8 | 7.42 | 147.37 |  | 0.01
BECK STREET 0401 | 12640401 | 1.59 |  |  |  | 1.59
BELL 1107 | 152701107 | 50.93 |  | 43.02 |  | 7.91
BELL 1108 | 152701108 | 63.13 |  | 51.14 |  | 11.99
BELL 1109 | 152701109 | 18.2 |  | 14.06 |  | 4.14
BELL 1110 | 152701110 | 11.24 |  | 0.16 |  | 11.08
BELLE HAVEN 0401 | 24020401 | 9.46 |  |  |  | 9.46
BELLE HAVEN 0402 | 24020402 | 4.69 |  |  |  | 4.69
BELLE HAVEN 0403 | 24020403 | 5.53 |  |  |  | 5.53
BELLE HAVEN 0404 | 24020404 | 8.66 |  |  |  | 8.66
BELLE HAVEN 0405 | 24020405 | 7.41 |  |  |  | 7.41
BELLE HAVEN 0406 | 24020406 | 9.32 |  |  |  | 9.32
BELLE HAVEN 0407 | 24020407 | 6.33 |  |  |  | 6.33
BELLE HAVEN 0408 | 24020408 | 5.22 |  |  |  | 5.22
BELLE HAVEN 0409 | 24020409 | 3.64 |  |  |  | 3.64
BELLE HAVEN 1101 | 24021101 | 1.58 |  |  |  | 1.58
BELLE HAVEN 1102 | 24021102 | 1.46 |  |  |  | 1.46
BELLE HAVEN 1103 | 24021103 | 1.8 |  |  |  | 1.8
BELLE HAVEN 1104 | 24021104 | 5.68 |  |  |  | 5.68
BELLE HAVEN 1105 | 24021105 | 10.61 |  |  |  | 10.61
BELLE HAVEN 1106 | 24021106 | 15.71 |  |  |  | 15.71
BELLE HAVEN 1107 | 24021107 | 1.27 |  |  |  | 1.27
BELLEVUE 1102 | 43181102 | 62.99 |  | 0.16 |  | 62.83
BELLEVUE 1104 | 43181104 | 12.54 |  |  |  | 12.54
BELLEVUE 2101 | 43182101 | 66.04 | 7.03 | 19.06 |  | 39.95
BELLEVUE 2103 | 43182103 | 5.71 |  |  |  | 5.71
BELLEVUE 2105 | 43182105 | 4.02 |  |  |  | 4.02
BELLEVUE 2107 | 43182107 | 11.33 |  |  |  | 11.33
BELMONT 0401 | 24030401 | 5.91 |  |  |  | 5.91
BELMONT 0402 | 24030402 | 7 |  |  |  | 7
BELMONT 0403 | 24030403 | 4.65 |  |  |  | 4.65
BELMONT 0406 | 24030406 | 5.06 |  |  |  | 5.06
BELMONT 1102 | 24031102 | 15.33 |  |  |  | 15.33
BELMONT 1103 | 24031103 | 18.69 |  | 3.39 |  | 15.3
BELMONT 1104 | 24031104 | 7.06 |  |  |  | 7.06
BELMONT 1105 | 24031105 | 0.64 |  |  |  | 0.64
BELMONT 1106 | 24031106 | 1.64 |  |  |  | 1.64
BELMONT 1107 | 24031107 | 0.97 |  |  |  | 0.97
BELMONT 1110 | 24031110 | 24.27 |  | 0.11 |  | 24.16
BELRIDGE 1A 1101 | 254371101 | 0.09 |  |  |  | 0.09
BELRIDGE 1B 1101 | 254381101 | 0.01 |  |  |  | 0.01
BEN LOMOND 0401 | 83040401 | 23.09 | 23.09 |  |  | 0
BEN LOMOND 1101 | 83041101 | 15.2 | 15.2 |  |  | 0
BERESFORD 0401 | 24040401 | 1.09 |  |  |  | 1.09
BERESFORD 0402 | 24040402 | 2.38 |  |  |  | 2.38
BERESFORD 0403 | 24040403 | 12.25 |  | 5.43 |  | 6.82
BERESFORD 0404 | 24040404 | 5.78 |  |  |  | 5.78
BERKELEY F 0401 | 12060401 | 0 |  |  |  | 0
BERKELEY F 0402 | 12060402 | 2.14 |  | 0.14 |  | 2
BERKELEY F 0403 | 12060403 | 2.19 |  |  |  | 2.19
BERKELEY F 0404 | 12060404 | 3.72 |  |  |  | 3.72
BERKELEY F 0405 | 12060405 | 0.97 |  |  |  | 0.97
BERKELEY F 0406 | 12060406 | 3.86 |  |  |  | 3.86
BERKELEY F 0407 | 12060407 | 0 |  |  |  | 0
BERKELEY F 0408 | 12060408 | 0.8 |  |  |  | 0.8
BERKELEY F 0409 | 12060409 | 3.66 |  |  |  | 3.66
BERKELEY F 0410 | 12060410 | 2.91 |  |  |  | 2.91
BERKELEY F 0411 | 12060411 | 4.5 |  |  |  | 4.5
BERKELEY F 1102 | 12061102 | 0.33 |  |  |  | 0.33
BERKELEY F 1103 | 12061103 | 5.27 | 1.97 |  |  | 3.3
BERKELEY F 1104 | 12061104 | 2.06 |  |  |  | 2.06
BERKELEY F 1105 | 12061105 | 11.39 |  | 1.78 |  | 9.61
BERKELEY T 0401 | 12660401 | 2.68 |  |  |  | 2.68
BERKELEY T 0402 | 12660402 | 1.36 |  |  |  | 1.36
BERKELEY T 0403 | 12660403 | 0.87 |  |  |  | 0.87
BERKELEY T 0404 | 12660404 | 0.35 |  |  |  | 0.35
BERRENDA A 1101 | 254261101 | 0.02 |  |  |  | 0.02
BERRENDA C 0401 | 254480401 | 0.02 |  |  |  | 0.02
BETHEL BANK 0401 | 18150401 | 0.78 |  |  |  | 0.78
BIG BASIN 1101 | 82841101 | 55.25 | 55.25 |  |  | 0
BIG BASIN 1102 | 82841102 | 63.74 | 60.74 | 3 |  | 0
BIG BEND 1101 | 103751101 | 56.93 | 42.5 | 14.43 |  | 0
BIG BEND 1102 | 103751102 | 18.18 | 18.07 |  |  | 0.11
BIG MEADOWS 2101 | 102812101 | 138.23 |  | 84.73 | 3.38 | 50.12
BIG RIVER 1101 | 43081101 | 86.02 |  | 70.02 | 1.61 | 14.39
BIOLA 1101 | 252211101 | 90.32 |  |  |  | 90.32
BIOLA 1102 | 252211102 | 32.44 |  |  |  | 32.44
BIOLA 1103 | 252211103 | 80.26 |  |  |  | 80.26
BIOLA 1104 | 252211104 | 50.13 |  |  |  | 50.13
BLACKWELL 1102 | 254681102 | 30.45 |  |  |  | 30.45
BLACKWELL 2101 | 254682101 | 22.74 |  |  |  | 22.74
BLUE LAKE 1101 | 192181101 | 7.32 |  |  | 0.31 | 7.01
BLUE LAKE 1102 | 192181102 | 69.01 |  |  |  | 69.01
BOGARD 1101 | 103301101 | 0.51 |  | 0.51 |  | 0
BOGUE 1102 | 153781102 | 17.83 |  |  |  | 17.83
BOGUE 1103 | 153781103 | 16.24 |  |  |  | 16.24
BOGUE 1104 | 153781104 | 8.97 |  |  |  | 8.97
BOGUE 1105 | 153781105 | 10.52 |  |  |  | 10.52
BOGUE 1106 | 153781106 | 27.99 |  |  |  | 27.99
BOGUE 1107 | 153781107 | 15.9 |  |  |  | 15.9
BOGUE 1108 | 153781108 | 32.66 |  |  |  | 32.66
BOLINAS 1101 | 42261101 | 51.69 | 27.22 | 7.51 |  | 16.96
BOLTHOUSE FARMS 1101 | 258181101 | 0.02 |  |  |  | 0.02
BONITA 1101 | 255391101 | 59.3 |  |  |  | 59.3
BONITA 1102 | 255391102 | 33.56 |  |  |  | 33.56
BONITA 1103 | 255391103 | 39.52 |  |  |  | 39.52
BONNIE NOOK 1101 | 152301101 | 1.69 | 1.69 |  |  | 0
BONNIE NOOK 1102 | 152301102 | 43.11 | 43.11 |  |  | 0
BONNIE NOOK 1103 | 152301103 | 0.11 | 0.11 |  |  | 0
BORDEN 1101 | 255121101 | 68.21 |  |  |  | 68.21
BORDEN 1102 | 255121102 | 23.02 |  |  |  | 23.02
BORDEN 1103 | 255121103 | 86.35 |  |  |  | 86.35
BORONDA 1101 | 182461101 | 7.39 |  |  |  | 7.39
BORONDA 1102 | 182461102 | 4.35 |  |  |  | 4.35
BOWLES 1101 | 253531101 | 69.19 |  |  |  | 69.19
BOWLES 1102 | 253531102 | 33.35 |  |  |  | 33.35
BOWLES 1103 | 253531103 | 26.74 |  |  |  | 26.74
BOWLES 1104 | 253531104 | 41.61 |  |  |  | 41.61
BRENTWOOD 2104 | 14592104 | 4.27 |  |  |  | 4.27
BRENTWOOD 2105 | 14592105 | 79.14 |  | 10.38 |  | 68.76
BRENTWOOD 2106 | 14592106 | 5.72 |  |  |  | 5.72
BRENTWOOD 2108 | 14592108 | 6.1 |  |  |  | 6.1
BRENTWOOD 2109 | 14592109 | 1.28 |  |  |  | 1.28
BRENTWOOD 2110 | 14592110 | 3.44 |  |  |  | 3.44
BRENTWOOD 2111 | 14592111 | 7.34 |  |  |  | 7.34
BRENTWOOD 2112 | 14592112 | 94.58 |  |  |  | 94.58
BRENTWOOD 2113 | 14592113 | 8.18 |  |  |  | 8.18
BRIDGEVILLE 1101 | 192461101 | 25.22 | 4.67 | 18.31 |  | 2.24
BRIDGEVILLE 1102 | 192461102 | 43.31 | 20.66 | 10.29 |  | 12.36
BRITTON 1104 | 83611104 | 1.19 |  |  |  | 1.19
BRITTON 1105 | 83611105 | 4.96 |  |  |  | 4.96
BRITTON 1106 | 83611106 | 3.78 |  |  |  | 3.78
BRITTON 1107 | 83611107 | 5.51 |  |  |  | 5.51
BRITTON 1108 | 83611108 | 1.73 |  |  |  | 1.73
BRITTON 1109 | 83611109 | 2.44 |  |  |  | 2.44
BRITTON 1110 | 83611110 | 11.69 |  |  |  | 11.69
BRITTON 1111 | 83611111 | 1.27 |  |  |  | 1.27
BRITTON 1112 | 83611112 | 1.85 |  |  |  | 1.85
BRITTON 1113 | 83611113 | 1.36 |  |  |  | 1.36
BRITTON 1114 | 83611114 | 5.03 |  |  |  | 5.03
BRITTON 1115 | 83611115 | 1.12 |  |  |  | 1.12
BROOKSIDE 0401 | 13210401 | 3.73 |  |  |  | 3.73
BROWNS VALLEY 1101 | 152921101 | 66.48 |  | 44.24 |  | 22.24
BRUNSWICK 1102 | 152481102 | 54.31 | 47.01 | 4.71 | 0.05 | 2.54
BRUNSWICK 1103 | 152481103 | 66.21 | 40.61 | 17.97 | 0.06 | 7.57
BRUNSWICK 1104 | 152481104 | 58 | 26.22 | 29.75 |  | 2.03
BRUNSWICK 1105 | 152481105 | 118.53 | 114.08 | 4.2 |  | 0.25
BRUNSWICK 1106 | 152481106 | 172.8 | 114.38 | 48.91 | 0.36 | 9.15
BRUNSWICK 1107 | 152481107 | 19.57 | 3.13 | 5.72 |  | 10.72
BRUNSWICK 1110 | 152481110 | 32.99 |  | 22.82 |  | 10.17
BUCKS CREEK 1103 | 102211103 | 13 | 10.04 | 2.67 | 0.19 | 0.1
BUELLTON 1101 | 183041101 | 104.37 | 4.82 | 72.66 |  | 26.89
BUELLTON 1102 | 183041102 | 28.27 |  | 15.97 |  | 12.3
BUENA VISTA 1101 | 182261101 | 0.72 |  |  |  | 0.72
BUENA VISTA 1102 | 182261102 | 11.15 |  |  |  | 11.15
BUENA VISTA 1103 | 182261103 | 7.61 |  |  |  | 7.61
BUENA VISTA 1104 | 182261104 | 3.97 |  |  |  | 3.97
BUENA VISTA 1106 | 182261106 | 12.95 |  |  |  | 12.95
BULLARD 1101 | 253961101 | 14.39 |  |  |  | 14.39
BULLARD 1102 | 253961102 | 4.05 |  |  |  | 4.05
BULLARD 1103 | 253961103 | 8.16 |  |  |  | 8.16
BULLARD 1104 | 253961104 | 8.06 |  |  |  | 8.06
BULLARD 1105 | 253961105 | 3.47 |  |  |  | 3.47
BULLARD 1106 | 253961106 | 3.69 |  |  |  | 3.69
BULLARD 1107 | 253961107 | 2.42 |  |  |  | 2.42
BULLARD 1108 | 253961108 | 1.63 |  |  |  | 1.63
BULLARD 1109 | 253961109 | 5.43 |  |  |  | 5.43
BULLARD 1110 | 253961110 | 4.23 |  |  |  | 4.23
BULLARD 1113 | 253961113 | 5.23 |  |  |  | 5.23
BULLARD 2111 | 253962111 | 4.45 |  |  |  | 4.45
BULLARD 2112 | 253962112 | 11.14 |  |  |  | 11.14
BULLARD 2114 | 253962114 | 4.96 |  |  |  | 4.96
BURLINGAME 0401 | 24050401 | 3.16 |  |  |  | 3.16
BURLINGAME 0402 | 24050402 | 5.89 |  |  |  | 5.89
BURLINGAME 0403 | 24050403 | 3.93 |  |  |  | 3.93
BURLINGAME 0404 | 24050404 | 4.04 |  |  |  | 4.04
BURLINGAME 0405 | 24050405 | 3.31 |  |  |  | 3.31
BURLINGAME 2101 | 24052101 | 6.83 |  |  |  | 6.83
BURNEY 1101 | 103311101 | 47.43 |  | 38.41 |  | 9.02
BURNEY 1102 | 103311102 | 6.73 |  | 3.28 | 0.03 | 3.42
BURNS 2101 | 183582101 | 29.17 | 29.17 |  |  | 0
BUTTE 1103 | 103081103 | 60.61 |  |  |  | 60.61
BUTTE 1104 | 103081104 | 64.72 |  |  |  | 64.72
BUTTE 1105 | 103081105 | 37.7 | 26.51 | 3.44 |  | 7.75
BUTTE 1106 | 103081106 | 11.91 |  |  |  | 11.91
BUTTE 1107 | 103081107 | 109.55 |  |  |  | 109.55
CABRILLO 1103 | 183101103 | 101.85 |  | 57.19 |  | 44.66
CABRILLO 1104 | 183101104 | 76.12 |  | 30.28 |  | 45.84
CADET 1101 | 254821101 | 0.03 |  |  |  | 0.03
CAL WATER 1102 | 255451102 | 22.4 |  | 3.72 |  | 18.68
CAL WATER 1103 | 255451103 | 12.26 |  |  |  | 12.26
CALAVERAS CEMENT 1101 | 162211101 | 246.07 | 7.31 | 221.81 |  | 16.95
CALFLAX 1102 | 253441102 | 20.43 |  |  |  | 20.43
CALFLAX 1103 | 253441103 | 28.83 |  |  |  | 28.83
CALFLAX 1104 | 253441104 | 18.63 |  |  |  | 18.63
CALFLAX 1106 | 253441106 | 8.09 |  |  |  | 8.09
CALFLAX 1107 | 253441107 | 27.36 |  |  |  | 27.36
CALIFORNIA AVE 1102 | 252281102 | 11.39 |  |  |  | 11.39
CALIFORNIA AVE 1103 | 252281103 | 7.74 |  |  |  | 7.74
CALIFORNIA AVE 1104 | 252281104 | 4.51 |  |  |  | 4.51
CALIFORNIA AVE 1106 | 252281106 | 9.88 |  |  |  | 9.88
CALIFORNIA AVE 1108 | 252281108 | 9.58 |  |  |  | 9.58
CALIFORNIA AVE 1110 | 252281110 | 11.13 |  |  |  | 11.13
CALIFORNIA AVE 1111 | 252281111 | 6.66 |  |  |  | 6.66
CALIFORNIA AVE 1112 | 252281112 | 4.93 |  |  |  | 4.93
CALIFORNIA AVE 1113 | 252281113 | 6.56 |  |  |  | 6.56
CALIFORNIA AVE 1114 | 252281114 | 19.47 |  |  |  | 19.47
CALIFORNIA AVE 1116 | 252281116 | 11.83 |  |  |  | 11.83
CALIFORNIA AVE 1117 | 252281117 | 1.27 |  |  |  | 1.27
CALISTOGA 1101 | 42711101 | 114.49 | 82.3 | 15.4 |  | 16.79
CALISTOGA 1102 | 42711102 | 45.59 | 22.29 | 1.54 |  | 21.76
CALPELLA 1101 | 43411101 | 101.6 | 4.03 | 78.17 | 0.04 | 19.36
CALPELLA 1102 | 43411102 | 7.55 |  | 1.79 |  | 5.76
CALPINE 1144 | 48011144 | 29.69 | 27.47 | 2.22 |  | 0
CALPINE 1146 | 48011146 | 5.78 | 5.78 |  |  | 0
CAMDEN 1102 | 252301102 | 40.25 |  |  |  | 40.25
CAMDEN 1103 | 252301103 | 128.08 |  |  |  | 128.08
CAMDEN 1104 | 252301104 | 77.61 |  |  |  | 77.61
CAMDEN 1105 | 252301105 | 58.76 |  |  |  | 58.76
CAMP EVERS 2103 | 83622103 | 61.35 | 44.91 | 0.83 |  | 15.61
CAMP EVERS 2104 | 83622104 | 36.57 | 26.72 | 0.58 |  | 9.27
CAMP EVERS 2105 | 83622105 | 78.51 | 73.52 | 2.13 |  | 2.86
CAMP EVERS 2106 | 83622106 | 79.86 | 75.74 | 0.06 |  | 4.06
CAMP EVERS 2107 | 83622107 | 41.1 | 32.19 | 2.95 |  | 5.96
CAMPHORA 0401 | 182070401 | 0.43 |  |  |  | 0.43
CAMPHORA 1101 | 182071101 | 51.97 |  | 3.91 |  | 48.06
CANAL 1101 | 252091101 | 46.77 |  |  |  | 46.77
CANAL 1102 | 252091102 | 15.38 |  |  |  | 15.38
CANAL 1103 | 252091103 | 53.8 |  |  |  | 53.8
CANAL 1104 | 252091104 | 10.57 |  |  |  | 10.57
CANAL 1105 | 252091105 | 16.75 |  |  |  | 16.75
CANAL 1106 | 252091106 | 7.88 |  |  |  | 7.88
CANTUA 1101 | 253591101 | 24.6 |  |  |  | 24.6
CANTUA 1102 | 253591102 | 47.77 |  |  |  | 47.77
CANTUA 1103 | 253591103 | 35.77 |  |  |  | 35.77
CANTUA 1104 | 253591104 | 0.15 |  |  |  | 0.15
CANTUA 1105 | 253591105 | 15.13 |  |  |  | 15.13
CANTUA 1106 | 253591106 | 0.12 |  |  |  | 0.12
CAPAY 1101 | 102111101 | 48.93 |  |  |  | 48.93
CAPAY 1102 | 102111102 | 75.05 |  |  |  | 75.05
CARLOTTA 1121 | 192291121 | 52.07 |  | 21.12 | 0.03 | 30.92
CARNATION 2101 | 255282101 | 0.01 |  |  |  | 0.01
CARNERAS 1102 | 252321102 | 16.88 |  |  |  | 16.88
CARNERAS 1103 | 252321103 | 41.81 |  |  |  | 41.81
CAROLANDS 0401 | 24060401 | 4.56 |  |  |  | 4.56
CAROLANDS 0402 | 24060402 | 0.03 |  |  |  | 0.03
CAROLANDS 0403 | 24060403 | 13.35 |  |  |  | 13.35
CAROLANDS 0404 | 24060404 | 10.18 |  | 4.14 |  | 6.04
CARQUINEZ 1103 | 43281103 | 14.78 |  |  |  | 14.78
CARQUINEZ 1104 | 43281104 | 0.38 |  |  |  | 0.38
CARQUINEZ 1105 | 43281105 | 5.73 |  |  |  | 5.73
CARRIZO PLAINS 1101 | 253461101 | 106.47 |  |  |  | 106.47
CARUTHERS 1101 | 252371101 | 82.2 |  |  |  | 82.2
CARUTHERS 1102 | 252371102 | 69.89 |  |  |  | 69.89
CARUTHERS 1104 | 252371104 | 80.82 |  |  |  | 80.82
CARUTHERS 1105 | 252371105 | 57.12 |  |  |  | 57.12
CASSERLY 0401 | 83110401 | 3.07 |  |  |  | 3.07
CASSIDY 2107 | 254272107 | 59.55 |  |  |  | 59.55
CASSIDY 2108 | 254272108 | 33.57 |  |  |  | 33.57
CASTRO 0401 | 22480401 | 2.94 |  |  |  | 2.94
CASTRO 0402 | 22480402 | 2.63 |  |  |  | 2.63
CASTRO VALLEY 1102 | 14091102 | 22.11 |  | 1.15 |  | 20.96
CASTRO VALLEY 1103 | 14091103 | 15.77 |  |  |  | 15.77
CASTRO VALLEY 1104 | 14091104 | 7.39 |  |  |  | 7.39
CASTRO VALLEY 1105 | 14091105 | 30.31 |  | 2.18 |  | 28.13
CASTRO VALLEY 1107 | 14091107 | 16.15 |  |  |  | 16.15
CASTRO VALLEY 1108 | 14091108 | 38.9 | 12.59 | 4.18 |  | 22.13
CASTRO VALLEY 1109 | 14091109 | 10.11 |  |  |  | 10.11
CASTRO VALLEY 1110 | 14091110 | 24.84 | 15.61 | 6.69 |  | 2.54
CASTRO VALLEY 1111 | 14091111 | 8.56 | 1.9 | 3.92 |  | 2.74
CASTROVILLE 2103 | 182352103 | 81.24 |  |  |  | 81.24
CASTROVILLE 2104 | 182352104 | 51.13 |  |  |  | 51.13
CATLETT 1101 | 153761101 | 0.03 |  |  |  | 0.03
CATLETT 1102 | 153761102 | 106.1 |  |  |  | 106.1
CATLETT 1105 | 153761105 | 53.87 |  |  |  | 53.87
CAWELO B 1101 | 252621101 | 0.01 |  |  |  | 0.01
CAWELO C 1101 | 252631101 | 0.02 |  |  |  | 0.02
CAYETANO 2109 | 14422109 | 49.28 | 12.08 | 21.31 |  | 15.89
CAYETANO 2111 | 14422111 | 12.26 |  | 5.36 |  | 6.9
CAYUCOS 1101 | 182551101 | 46.14 |  | 0.46 |  | 45.68
CAYUCOS 1102 | 182551102 | 57.39 | 9.06 | 4.99 |  | 43.34
CEDAR CREEK 1101 | 103321101 | 109.67 | 20.99 | 88.68 |  | 0
CELERON 1101 | 255271101 | 0.15 |  |  |  | 0.15
CHALLENGE 1101 | 103201101 | 48.26 | 48.02 | 0.23 |  | 0.01
CHALLENGE 1102 | 103201102 | 62.95 | 60.31 | 2.64 |  | 0
CHANNEL 1101 | 163071101 | 9.95 |  |  |  | 9.95
CHANNEL 1102 | 163071102 | 8.34 |  |  |  | 8.34
CHARCA 1102 | 254501102 | 60.58 |  |  |  | 60.58
CHARCA 1103 | 254501103 | 36.99 |  |  |  | 36.99
CHARCA 1106 | 254501106 | 18.14 |  |  |  | 18.14
CHEROKEE 1101 | 163651101 | 19.89 |  |  |  | 19.89
CHEROKEE 1102 | 163651102 | 36.25 |  |  |  | 36.25
CHESTER 1101 | 103181101 | 8.2 |  | 2.12 | 0.04 | 6.04
CHESTER 1102 | 103181102 | 5.31 |  | 2.32 |  | 2.99
CHICO A 0401 | 102050401 | 2.21 |  |  |  | 2.21
CHICO A 0402 | 102050402 | 5.68 |  |  |  | 5.68
CHICO A 1101 | 102051101 | 2.97 |  |  |  | 2.97
CHICO A 1102 | 102051102 | 9.36 |  |  |  | 9.36
CHICO A 1103 | 102051103 | 4.88 |  |  |  | 4.88
CHICO B 1101 | 102491101 | 4.59 |  |  |  | 4.59
CHICO B 1103 | 102491103 | 7.33 |  |  |  | 7.33
CHICO B 1105 | 102491105 | 9.67 |  |  |  | 9.67
CHICO B 1106 | 102491106 | 2.04 |  |  |  | 2.04
CHICO C 0401 | 102650401 | 2.78 |  |  |  | 2.78
CHOLAME 1101 | 182561101 | 97.54 |  | 0.22 |  | 97.32
CHOLAME 2102 | 182562102 | 215.36 |  | 59.05 |  | 156.31
CHOWCHILLA 1101 | 254101101 | 63.02 |  |  |  | 63.02
CHOWCHILLA 1102 | 254101102 | 13.16 |  |  |  | 13.16
CHOWCHILLA 1103 | 254101103 | 49.12 |  |  |  | 49.12
CHOWCHILLA 1104 | 254101104 | 80.11 |  |  |  | 80.11
CHOWCHILLA 1105 | 254101105 | 9.76 |  |  |  | 9.76
CHOWCHILLA 1106 | 254101106 | 54.75 |  |  |  | 54.75
CLARK ROAD 1101 | 103091101 | 0 |  |  |  | 0
CLARK ROAD 1102 | 103091102 | 116.38 | 31.05 | 72.42 |  | 12.91
CLARKSVILLE 2103 | 153612103 | 50.08 | 19.62 | 10.52 |  | 19.94
CLARKSVILLE 2104 | 153612104 | 75.44 | 41.3 | 21.5 | 0.07 | 12.57
CLARKSVILLE 2105 | 153612105 | 13.08 | 5.53 | 4.76 |  | 2.79
CLARKSVILLE 2106 | 153612106 | 1.39 |  | 0.48 |  | 0.91
CLARKSVILLE 2109 | 153612109 | 12.26 | 1.99 | 1.96 |  | 8.31
CLARKSVILLE 2110 | 153612110 | 7.84 |  |  |  | 7.84
CLAY 1101 | 163341101 | 40.45 |  | 26.41 | 0.04 | 14
CLAY 1102 | 163341102 | 2.08 |  | 0.82 |  | 1.26
CLAY 1103 | 163341103 | 112.93 |  | 49.78 |  | 63.15
CLAYTON 1103 | 12021103 | 4.42 |  |  |  | 4.42
CLAYTON 1104 | 12021104 | 13.45 |  |  |  | 13.45
CLAYTON 2211 | 12022211 | 10.19 |  |  |  | 10.19
CLAYTON 2212 | 12022212 | 56.92 | 27.14 | 18.68 |  | 11.1
CLAYTON 2213 | 12022213 | 4.84 |  | 2.51 |  | 2.33
CLAYTON 2214 | 12022214 | 5.93 |  |  |  | 5.93
CLAYTON 2215 | 12022215 | 29.13 | 2.92 | 3.78 |  | 22.43
CLAYTON 2216 | 12022216 | 18.77 |  |  |  | 18.77
CLAYTON 2217 | 12022217 | 20.24 |  |  |  | 20.24
CLAYTON 2218 | 12022218 | 8.35 |  |  |  | 8.35
CLEAR LAKE 1101 | 42141101 | 68.95 |  | 7.08 |  | 61.87
CLEAR LAKE 1102 | 42141102 | 75.96 | 6.05 | 9.06 | 0.11 | 60.74
CLOVERDALE 1101 | 42821101 | 36.69 |  | 24.33 |  | 12.36
CLOVERDALE 1102 | 42821102 | 103.84 | 47.04 | 28.23 |  | 28.57
CLOVIS 1101 | 254081101 | 3.98 |  |  |  | 3.98
CLOVIS 1102 | 254081102 | 24.09 |  |  |  | 24.09
CLOVIS 1103 | 254081103 | 1.95 |  |  |  | 1.95
CLOVIS 1104 | 254081104 | 0.54 |  |  |  | 0.54
CLOVIS 1105 | 254081105 | 7.74 |  |  |  | 7.74
CLOVIS 1106 | 254081106 | 5.02 |  |  |  | 5.02
CLOVIS 1107 | 254081107 | 9.87 |  |  |  | 9.87
CLOVIS 1108 | 254081108 | 12.9 |  |  |  | 12.9
CLOVIS 2109 | 254082109 | 3.89 |  |  |  | 3.89
CLOVIS 2110 | 254082110 | 11.55 |  |  |  | 11.55
CLOVIS 2111 | 254082111 | 8.77 |  |  |  | 8.77
CMC 1101 | 183111101 | 2.01 |  | 2.01 |  | 0
CMC 1102 | 183111102 | 0.49 |  | 0.49 |  | 0
COALINGA NO 1 1106 | 252161106 | 9.01 |  |  |  | 9.01
COALINGA NO 1 1107 | 252161107 | 4.04 |  |  |  | 4.04
COALINGA NO 1 1108 | 252161108 | 60.01 |  |  |  | 60.01
COALINGA NO 1 1109 | 252161109 | 25.83 |  |  | 0.22 | 25.61
COALINGA NO 2 1104 | 252381104 | 0.16 |  |  |  | 0.16
COALINGA NO 2 1105 | 252381105 | 75.91 |  |  | 0.19 | 75.72
COALINGA NO 2 1106 | 252381106 | 42.53 |  |  |  | 42.53
COALINGA NO 2 1107 | 252381107 | 38.21 |  |  |  | 38.21
COARSEGOLD 2102 | 254432102 | 73.14 | 58.18 | 14.96 |  | 0
COARSEGOLD 2103 | 254432103 | 122.71 |  | 93.34 | 1.59 | 27.78
COARSEGOLD 2104 | 254432104 | 264.79 | 2.83 | 243.06 | 11.91 | 6.99
COLONY 1101 | 162231101 | 19 |  |  |  | 19
COLONY 1102 | 162231102 | 51.56 |  |  |  | 51.56
COLUMBIA HILL 1101 | 152471101 | 89.72 | 72.07 | 17.65 |  | 0
COLUMBUS 1103 | 253951103 | 7.88 |  |  |  | 7.88
COLUMBUS 1104 | 253951104 | 10.24 |  |  |  | 10.24
COLUMBUS 1105 | 253951105 | 16.08 |  |  |  | 16.08
COLUMBUS 1106 | 253951106 | 14.38 |  |  |  | 14.38
COLUMBUS 1109 | 253951109 | 5.58 |  |  |  | 5.58
COLUMBUS 1110 | 253951110 | 13.22 |  |  |  | 13.22
COLUSA 1101 | 62021101 | 56.51 |  |  |  | 56.51
COLUSA 1103 | 62021103 | 5.04 |  |  |  | 5.04
COLUSA 1104 | 62021104 | 6.56 |  |  |  | 6.56
COLUSA 1105 | 62021105 | 44.76 |  |  |  | 44.76
COLUSA JUNCTION 1101 | 62071101 | 29.04 |  |  |  | 29.04
CONCORD NO 1 0401 | 12960401 | 4.8 |  |  |  | 4.8
CONCORD NO 1 0402 | 12960402 | 3.8 |  |  |  | 3.8
CONTRA COSTA 2103 | 13652103 | 16.41 |  |  |  | 16.41
CONTRA COSTA 2104 | 13652104 | 9.22 |  |  |  | 9.22
CONTRA COSTA 2105 | 13652105 | 14.33 |  |  |  | 14.33
CONTRA COSTA 2106 | 13652106 | 3.2 |  |  |  | 3.2
CONTRA COSTA 2107 | 13652107 | 12.72 |  |  |  | 12.72
CONTRA COSTA 2108 | 13652108 | 0.88 |  |  |  | 0.88
CONTRA COSTA 2109 | 13652109 | 14.24 |  |  |  | 14.24
CONTRA COSTA 2110 | 13652110 | 0.39 |  |  |  | 0.39
CONTRA COSTA 2112 | 13652112 | 0.04 |  |  |  | 0.04
CONTRA COSTA 2113 | 13652113 | 14.22 |  |  |  | 14.22
CONTRA COSTA 2114 | 13652114 | 1.91 |  |  |  | 1.91
CONTRA COSTA 2115 | 13652115 | 6.79 |  |  |  | 6.79
CONTRA COSTA 2116 | 13652116 | 14.16 |  |  |  | 14.16
COPPERMINE 1104 | 252411104 | 103.04 |  | 9.04 |  | 94
COPPERMINE 1106 | 252411106 | 7.89 |  |  |  | 7.89
COPPERMINE 1112 | 252411112 | 15.89 |  |  |  | 15.89
COPPERMINE 2110 | 252412110 | 0 |  |  |  | 0
COPUS 1102 | 253871102 | 31.24 |  |  |  | 31.24
COPUS 1103 | 253871103 | 24.41 |  |  |  | 24.41
COPUS 1104 | 253871104 | 39.19 |  |  |  | 39.19
CORCORAN 1101 | 252171101 | 0.52 |  |  |  | 0.52
CORCORAN 1102 | 252171102 | 0.04 |  |  |  | 0.04
CORCORAN 1104 | 252171104 | 26.75 |  |  |  | 26.75
CORCORAN 1106 | 252171106 | 45.77 |  |  |  | 45.77
CORCORAN 1108 | 252171108 | 23.63 |  |  |  | 23.63
CORCORAN 1112 | 252171112 | 45.05 |  |  |  | 45.05
CORCORAN 1116 | 252171116 | 56.29 |  |  |  | 56.29
CORCORAN 1117 | 252171117 | 0.54 |  |  |  | 0.54
CORCORAN 1118 | 252171118 | 52.39 |  |  |  | 52.39
CORDELIA 1101 | 62701101 | 0.02 |  |  |  | 0.02
CORDELIA 1102 | 62701102 | 0.04 |  |  |  | 0.04
CORDELIA 1104 | 62701104 | 61.99 |  |  |  | 61.99
CORDELIA 1110 | 62701110 | 8.92 |  |  |  | 8.92
CORDELIA 1112 | 62701112 | 16.12 |  |  |  | 16.12
CORNING 1101 | 103331101 | 142.76 |  | 49.27 |  | 93.49
CORNING 1102 | 103331102 | 164.46 |  | 51.76 |  | 112.7
CORNING 1103 | 103331103 | 66.95 |  |  |  | 66.95
CORNING 1104 | 103331104 | 113.42 |  |  |  | 113.42
CORONA 1101 | 43491101 | 22.85 |  |  |  | 22.85
CORONA 1102 | 43491102 | 1.38 |  |  |  | 1.38
CORONA 1103 | 43491103 | 17.54 |  | 0.46 |  | 17.08
CORRAL 1101 | 162991101 | 172.38 |  | 119.7 |  | 52.68
CORRAL 1102 | 162991102 | 62.8 |  | 47.58 |  | 15.22
CORRAL 1103 | 162991103 | 80.9 |  | 17.72 |  | 63.18
CORTINA 1101 | 63121101 | 59.28 |  | 1.25 |  | 58.03
COTATI 1102 | 42271102 | 34.72 |  | 15.66 |  | 19.06
COTATI 1103 | 42271103 | 111.01 |  | 84.12 |  | 26.89
COTATI 1104 | 42271104 | 19.38 |  | 8.45 |  | 10.93
COTATI 1105 | 42271105 | 112.3 |  | 43.05 |  | 69.25
COTTLE 1701 | 163711701 | 100.28 |  |  |  | 100.28
COTTLE 1702 | 163711702 | 37.16 |  |  |  | 37.16
COTTLE 1703 | 163711703 | 27.37 |  |  |  | 27.37
COTTLE 1704 | 163711704 | 14.76 |  |  |  | 14.76
COTTLE 1707 | 163711707 | 47.31 |  |  |  | 47.31
COTTLE 1708 | 163711708 | 129.6 |  |  |  | 129.6
COTTONWOOD 1101 | 102931101 | 99.96 |  | 68.97 |  | 30.99
COTTONWOOD 1102 | 102931102 | 53.98 |  | 28.34 |  | 25.64
COTTONWOOD 1103 | 102931103 | 160.52 |  | 133.78 |  | 26.74
COUNTRY CLUB 0401 | 163120401 | 2.16 |  |  |  | 2.16
COUNTRY CLUB 0402 | 163120402 | 5.15 |  |  |  | 5.15
COUNTRY CLUB 0403 | 163120403 | 2.7 |  |  |  | 2.7
COUNTRY CLUB 1101 | 163121101 | 12.07 |  |  |  | 12.07
COUNTRY CLUB 1102 | 163121102 | 1.34 |  |  |  | 1.34
COUNTRY CLUB 1103 | 163121103 | 6.27 |  |  |  | 6.27
COUNTRY CLUB 1104 | 163121104 | 7.26 |  |  |  | 7.26
COUNTRY CLUB 1105 | 163121105 | 1.65 |  |  |  | 1.65
COUNTRY CLUB 1106 | 163121106 | 9.03 |  |  |  | 9.03
COVELO 1101 | 43061101 | 120.9 |  | 17.63 | 0.93 | 102.34
CRESSEY 2103 | 254702103 | 152.75 |  |  |  | 152.75
CRESSEY 2104 | 254702104 | 87.83 |  |  |  | 87.83
CRESTA 1101 | 102251101 | 1.77 | 0.49 | 1.28 |  | 0
CROWS LANDING 1101 | 163251101 | 44.61 |  |  |  | 44.61
CROWS LANDING 1102 | 163251102 | 3.17 |  |  |  | 3.17
CURTIS 1701 | 163351701 | 18 |  | 10.29 |  | 7.71
CURTIS 1702 | 163351702 | 117.34 | 22.01 | 87.14 | 0.68 | 7.51
CURTIS 1703 | 163351703 | 198.01 | 17.44 | 177.26 |  | 3.31
CURTIS 1704 | 163351704 | 84.35 | 25.71 | 58.07 |  | 0.57
CURTIS 1705 | 163351705 | 88.16 | 14.4 | 69.7 | 0.16 | 3.9
CUYAMA 1103 | 253141103 | 77.68 |  | 2.58 |  | 75.1
CUYAMA 1104 | 253141104 | 18.02 |  |  |  | 18.02
CUYAMA 2101 | 253142101 | 29.85 |  |  |  | 29.85
CUYAMA 2102 | 253142102 | 68.93 |  | 3.22 |  | 65.71
DAIRYLAND 1102 | 252421102 | 81.62 |  |  |  | 81.62
DAIRYLAND 1105 | 252421105 | 64.89 |  |  |  | 64.89
DAIRYLAND 1109 | 252421109 | 46.75 |  |  |  | 46.75
DAIRYLAND 1110 | 252421110 | 37.57 |  |  |  | 37.57
DAIRYLAND 1111 | 252421111 | 26.82 |  |  |  | 26.82
DAIRYLAND 1112 | 252421112 | 62.34 |  |  |  | 62.34
DAIRYLAND 1113 | 252421113 | 83.57 |  |  |  | 83.57
DAIRYVILLE 1101 | 103341101 | 43.06 |  |  |  | 43.06
DALY CITY 0401 | 22640401 | 5.68 |  |  |  | 5.68
DALY CITY 1101 | 22641101 | 3.42 |  |  |  | 3.42
DALY CITY 1102 | 22641102 | 7.56 |  |  |  | 7.56
DALY CITY 1103 | 22641103 | 4.76 |  |  |  | 4.76
DALY CITY 1104 | 22641104 | 10.4 |  |  |  | 10.4
DALY CITY 1105 | 22641105 | 10.67 |  |  |  | 10.67
DALY CITY 1106 | 22641106 | 10.09 |  |  |  | 10.09
DALY CITY 1107 | 22641107 | 5.33 |  |  |  | 5.33
DALY CITY 1108 | 22641108 | 2.98 |  |  |  | 2.98
DALY CITY 1109 | 22641109 | 6.25 |  |  |  | 6.25
DALY CITY 1110 | 22641110 | 1.82 |  |  |  | 1.82
DALY CITY 1111 | 22641111 | 7.05 |  |  |  | 7.05
DALY CITY 1112 | 22641112 | 14.07 |  |  |  | 14.07
DALY CITY 1115 | 22641115 | 0.03 |  |  |  | 0.03
DAVIS 1101 | 62041101 | 37.46 |  |  |  | 37.46
DAVIS 1102 | 62041102 | 6.48 |  |  |  | 6.48
DAVIS 1103 | 62041103 | 5.86 |  |  |  | 5.86
DAVIS 1104 | 62041104 | 5.77 |  |  |  | 5.77
DAVIS 1105 | 62041105 | 8.04 |  |  |  | 8.04
DAVIS 1106 | 62041106 | 42.9 |  |  |  | 42.9
DAVIS 1107 | 62041107 | 84.28 |  |  |  | 84.28
DAVIS 1108 | 62041108 | 3.38 |  |  |  | 3.38
DAVIS 1109 | 62041109 | 4.46 |  |  |  | 4.46
DAVIS 1110 | 62041110 | 1.88 |  |  |  | 1.88
DAVIS 1111 | 62041111 | 7.28 |  |  |  | 7.28
DAVIS 1112 | 62041112 | 46.71 |  |  |  | 46.71
DAYTON ROAD 0401 | 102940401 | 2.13 |  |  |  | 2.13
DEEPWATER 1105 | 63621105 | 5.53 |  |  |  | 5.53
DEEPWATER 1106 | 63621106 | 0.06 |  |  |  | 0.06
DEEPWATER 1107 | 63621107 | 24.85 |  |  |  | 24.85
DEEPWATER 1108 | 63621108 | 0.07 |  |  |  | 0.07
DEEPWATER 1109 | 63621109 | 4.81 |  |  |  | 4.81
DEEPWATER 1110 | 63621110 | 6.22 |  |  |  | 6.22
DEL MAR 1103 | 152581103 | 12.65 |  |  |  | 12.65
DEL MAR 1104 | 152581104 | 0 |  |  |  | 0
DEL MAR 2105 | 152582105 | 13.9 |  |  |  | 13.9
DEL MAR 2106 | 152582106 | 3.1 |  |  |  | 3.1
DEL MAR 2109 | 152582109 | 7.3 |  | 2.24 |  | 5.06
DEL MAR 2110 | 152582110 | 1.95 |  |  |  | 1.95
DEL MONTE 2101 | 182222101 | 14.9 |  | 0.49 |  | 14.41
DEL MONTE 2102 | 182222102 | 16.24 |  | 0.66 |  | 15.58
DEL MONTE 2103 | 182222103 | 36.82 |  | 12.25 | 3.01 | 21.56
DEL MONTE 2104 | 182222104 | 59.14 |  | 43.67 |  | 15.47
DEL MONTE 2105 | 182222105 | 20.21 |  | 1.05 |  | 19.16
DELEVAN 1101 | 69551101 | 0.6 |  |  |  | 0.6
DELEVAN 1102 | 69551102 | 0.61 |  |  |  | 0.61
DESCHUTES 1101 | 103351101 | 130.38 | 7.5 | 99.43 |  | 23.45
DESCHUTES 1104 | 103351104 | 112.55 |  | 59.94 |  | 52.61
DEVILS DEN 1101 | 253451101 | 44.65 |  |  |  | 44.65
DEVILS DEN 1102 | 253451102 | 33 |  |  |  | 33
DIAMOND SPRINGS 1103 | 152261103 | 53.4 | 10.21 | 22.97 | 0.87 | 19.35
DIAMOND SPRINGS 1104 | 152261104 | 18.15 | 7.52 | 4.87 |  | 5.76
DIAMOND SPRINGS 1105 | 152261105 | 131.27 | 75.13 | 47.66 |  | 8.48
DIAMOND SPRINGS 1106 | 152261106 | 120.3 |  | 109.86 | 1.01 | 9.43
DIAMOND SPRINGS 1107 | 152261107 | 56.77 | 33.81 | 17.76 | 0.28 | 4.92
DINUBA 1102 | 254091102 | 21.64 |  |  |  | 21.64
DINUBA 1104 | 254091104 | 143.16 |  |  |  | 143.16
DINUBA 1105 | 254091105 | 43.01 |  |  |  | 43.01
DINUBA 1106 | 254091106 | 10.33 |  |  |  | 10.33
DIVIDE 1101 | 182571101 | 14.89 |  |  | 0.58 | 14.31
DIVIDE 1102 | 182571102 | 47.86 |  |  |  | 47.86
DIVIDE 1103 | 182571103 | 20.68 |  | 2.39 |  | 18.29
DIXON 1102 | 62061102 | 10.88 |  |  |  | 10.88
DIXON 1103 | 62061103 | 120.53 |  |  | 0.05 | 120.48
DIXON 1104 | 62061104 | 11.69 |  |  |  | 11.69
DIXON 1105 | 62061105 | 23.81 |  |  |  | 23.81
DIXON 1106 | 62061106 | 8.52 |  |  |  | 8.52
DIXON LANDING 2101 | 14722101 | 10.72 |  |  |  | 10.72
DIXON LANDING 2102 | 14722102 | 10.82 |  |  |  | 10.82
DIXON LANDING 2103 | 14722103 | 2.81 |  |  |  | 2.81
DIXON LANDING 2105 | 14722105 | 1.67 |  |  |  | 1.67
DIXON LANDING 2109 | 14722109 | 10.64 |  |  |  | 10.64
DIXON LANDING 2111 | 14722111 | 0.13 |  |  |  | 0.13
DOBBINS 1101 | 153741101 | 81.73 | 26.59 | 54.03 |  | 1.11
DOLAN ROAD 1101 | 182381101 | 68.96 |  | 2.77 |  | 66.19
DOLAN ROAD 1102 | 182381102 | 0.45 |  |  |  | 0.45
DOLAN ROAD 1103 | 182381103 | 3 |  |  |  | 3
DOLAN ROAD 1104 | 182381104 | 5.03 |  |  |  | 5.03
DOS PALOS 1101 | 254041101 | 75.89 |  |  |  | 75.89
DOS PALOS 1102 | 254041102 | 0.21 |  |  |  | 0.21
DRUM 1101 | 152321101 | 18.39 | 18.35 | 0.04 |  | 0
DUMBARTON 1102 | 14471102 | 16.54 |  |  |  | 16.54
DUMBARTON 1103 | 14471103 | 1.47 |  |  |  | 1.47
DUMBARTON 1104 | 14471104 | 11.56 |  |  |  | 11.56
DUMBARTON 1106 | 14471106 | 7.3 |  |  |  | 7.3
DUMBARTON 1107 | 14471107 | 10.44 |  |  |  | 10.44
DUMBARTON 1108 | 14471108 | 3.94 |  |  |  | 3.94
DUMBARTON 1109 | 14471109 | 3.73 |  |  |  | 3.73
DUMBARTON 1110 | 14471110 | 6.99 |  |  |  | 6.99
DUMBARTON 2111 | 14472111 | 6.25 |  |  |  | 6.25
DUNBAR 1101 | 43071101 | 53.84 | 26.7 | 2.59 |  | 24.55
DUNBAR 1102 | 43071102 | 61.96 | 7.12 | 42.31 |  | 12.53
DUNBAR 1103 | 43071103 | 60.02 | 20.73 | 14.59 |  | 24.7
DUNLAP 1102 | 254061102 | 55.24 |  | 55.24 |  | 0
DUNLAP 1103 | 254061103 | 71 |  | 71 |  | 0
DUNNIGAN 1101 | 63811101 | 36.92 |  |  |  | 36.92
DUNNIGAN 1102 | 63811102 | 39.27 |  |  |  | 39.27
DUNNIGAN 1103 | 63811103 | 46.98 |  | 1.92 |  | 45.06
EAST GRAND 0401 | 22570401 | 4.79 |  |  |  | 4.79
EAST GRAND 0404 | 22570404 | 3.86 |  |  |  | 3.86
EAST GRAND 1101 | 22571101 | 7.95 |  |  |  | 7.95
EAST GRAND 1102 | 22571102 | 2.23 |  |  |  | 2.23
EAST GRAND 1103 | 22571103 | 1.51 |  |  |  | 1.51
EAST GRAND 1104 | 22571104 | 16.21 |  |  |  | 16.21
EAST GRAND 1105 | 22571105 | 9 |  |  |  | 9
EAST GRAND 1106 | 22571106 | 0.32 |  |  |  | 0.32
EAST GRAND 1107 | 22571107 | 13.58 |  |  |  | 13.58
EAST GRAND 1108 | 22571108 | 3.89 |  |  |  | 3.89
EAST GRAND 1109 | 22571109 | 1.48 |  |  |  | 1.48
EAST GRAND 1110 | 22571110 | 3.35 |  |  |  | 3.35
EAST GRAND 1111 | 22571111 | 0.76 |  |  |  | 0.76
EAST GRAND 1114 | 22571114 | 0 |  |  |  | 0
EAST GRAND 1115 | 22571115 | 0 |  |  |  | 0
EAST GRANDE 1116 | 22571116 | 0.61 |  |  |  | 0.61
EAST GRANDE 1117 | 22571117 | 0.01 |  |  |  | 0.01
EAST MARYSVILLE 1105 | 152331105 | 53.31 |  |  |  | 53.31
EAST MARYSVILLE 1107 | 152331107 | 8.3 |  |  |  | 8.3
EAST MARYSVILLE 1108 | 152331108 | 63.7 |  |  |  | 63.7
EAST NICOLAUS 1101 | 152151101 | 68.89 |  |  |  | 68.89
EAST NICOLAUS 1102 | 152151102 | 58.01 |  |  |  | 58.01
EAST NICOLAUS 1103 | 152151103 | 93.4 |  |  |  | 93.4
EAST QUINCY 1101 | 102551101 | 17.52 | 1.69 | 2.06 |  | 13.77
EAST STOCKTON 0401 | 163130401 | 8.47 |  |  |  | 8.47
EAST STOCKTON 0402 | 163130402 | 9.86 |  |  |  | 9.86
EAST STOCKTON 1101 | 163131101 | 14.57 |  |  |  | 14.57
EAST STOCKTON 1102 | 163131102 | 16.16 |  |  |  | 16.16
ECHO SUMMIT 1101 | 158031101 | 14.82 |  | 5.94 | 3.48 | 5.4
EDENVALE 1101 | 82951101 | 9.68 |  |  |  | 9.68
EDENVALE 1102 | 82951102 | 5.74 |  | 0.52 |  | 5.22
EDENVALE 1103 | 82951103 | 0.31 |  |  |  | 0.31
EDENVALE 2105 | 82952105 | 37.25 |  | 2.32 |  | 34.93
EDENVALE 2106 | 82952106 | 16.97 |  |  |  | 16.97
EDENVALE 2107 | 82952107 | 0.07 |  |  |  | 0.07
EDENVALE 2108 | 82952108 | 2.88 |  |  |  | 2.88
EDENVALE 2109 | 82952109 | 2.47 |  |  |  | 2.47
EDENVALE 2110 | 82952110 | 0 |  |  |  | 0
EDENVALE 2112 | 82952112 | 1.34 |  |  |  | 1.34
EDENVALE 2113 | 82952113 | 2.41 |  |  |  | 2.41
EDES 1101 | 13681101 | 8.68 |  |  |  | 8.68
EDES 1102 | 13681102 | 4.3 |  |  |  | 4.3
EDES 1103 | 13681103 | 12.56 |  |  |  | 12.56
EDES 1105 | 13681105 | 3.61 |  |  |  | 3.61
EDES 1110 | 13681110 | 4.97 |  |  |  | 4.97
EDES 1111 | 13681111 | 4.22 |  |  |  | 4.22
EDES 1112 | 13681112 | 16.94 | 0.58 | 14.64 |  | 1.72
EDES 1113 | 13681113 | 4.47 |  |  |  | 4.47
EDES 1114 | 13681114 | 6.4 |  |  |  | 6.4
EEL RIVER 1102 | 192381102 | 143.85 |  | 40.04 | 0.02 | 103.79
EEL RIVER 1103 | 192381103 | 59.36 |  | 3.13 |  | 56.23
EIGHT MILE 2101 | 163912101 | 73.22 |  |  |  | 73.22
EIGHT MILE 2102 | 163912102 | 29.28 |  |  |  | 29.28
EIGHT MILE 2103 | 163912103 | 0.01 |  |  |  | 0.01
EIGHT MILE 2104 | 163912104 | 1.36 |  |  |  | 1.36
EIGHT MILE 2105 | 163912105 | 0.49 |  |  |  | 0.49
EIGHT MILE 2106 | 163912106 | 32.24 |  |  |  | 32.24
EL CAPITAN 0004 | 253880004 | 0.01 |  |  |  | 0.01
EL CAPITAN 1102 | 253881102 | 9.31 |  |  |  | 9.31
EL CAPITAN 1103 | 253881103 | 67.73 |  |  |  | 67.73
EL CAPITAN 1104 | 253881104 | 49.54 |  |  |  | 49.54
EL CAPITAN 1105 | 253881105 | 4.84 |  |  |  | 4.84
EL CAPITAN 1106 | 253881106 | 17.69 |  |  |  | 17.69
EL CAPITAN 2109 | 253882109 | 7.54 |  |  |  | 7.54
EL CAPITAN 2110 | 253882110 | 8.88 |  |  |  | 8.88
EL CERRITO G 1101 | 12501101 | 10.14 |  |  |  | 10.14
EL CERRITO G 1102 | 12501102 | 7.78 |  |  |  | 7.78
EL CERRITO G 1103 | 12501103 | 10.78 |  |  |  | 10.78
EL CERRITO G 1104 | 12501104 | 7.88 |  |  |  | 7.88
EL CERRITO G 1105 | 12501105 | 34.31 | 5.58 | 21.49 |  | 7.24
EL CERRITO G 1106 | 12501106 | 4.7 |  |  |  | 4.7
EL CERRITO G 1107 | 12501107 | 3.7 |  |  |  | 3.7
EL CERRITO G 1108 | 12501108 | 15.8 |  | 0 |  | 15.8
EL CERRITO G 1109 | 12501109 | 8.08 |  |  |  | 8.08
EL CERRITO G 1110 | 12501110 | 13.59 |  | 0.69 |  | 12.9
EL CERRITO G 1111 | 12501111 | 16.38 |  | 0.2 |  | 16.18
EL CERRITO G 1112 | 12501112 | 24.66 | 1.65 | 0.35 |  | 22.66
EL CERRITO G 1113 | 12501113 | 11.51 |  | 0.1 |  | 11.41
EL CERRITO G 1114 | 12501114 | 7.24 |  |  |  | 7.24
EL DORADO PH 2101 | 152762101 | 134.67 | 98.7 | 25.51 | 8.09 | 2.37
EL DORADO PH 2102 | 152762102 | 34.02 | 34.02 |  |  | 0
EL NIDO 1101 | 252451101 | 57.63 |  |  |  | 57.63
EL NIDO 1102 | 252451102 | 59.32 |  |  |  | 59.32
EL NIDO 1103 | 252451103 | 61.11 |  |  |  | 61.11
EL NIDO 1104 | 252451104 | 87.08 |  |  |  | 87.08
EL PATIO 1101 | 82921101 | 0.81 |  |  |  | 0.81
EL PATIO 1102 | 82921102 | 1.64 |  |  |  | 1.64
EL PATIO 1103 | 82921103 | 13.18 |  |  |  | 13.18
EL PATIO 1104 | 82921104 | 12.01 |  |  |  | 12.01
EL PATIO 1105 | 82921105 | 7.02 |  |  |  | 7.02
EL PATIO 1107 | 82921107 | 15.76 |  |  |  | 15.76
EL PATIO 1108 | 82921108 | 6.76 |  |  |  | 6.76
EL PATIO 1109 | 82921109 | 10.59 |  |  |  | 10.59
EL PATIO 1111 | 82921111 | 0.03 |  |  |  | 0.03
EL PATIO 1112 | 82921112 | 19.58 |  |  |  | 19.58
EL PATIO 1113 | 82921113 | 4.77 |  |  |  | 4.77
EL PATIO 1114 | 82921114 | 0.53 |  |  |  | 0.53
EL PATIO 1116 | 82921116 | 8.73 |  |  |  | 8.73
EL PATIO 1117 | 82921117 | 4.19 |  |  | 0.06 | 4.13
EL PATIO 1118 | 82921118 | 11 |  |  |  | 11
EL PATIO 1119 | 82921119 | 8.27 |  |  |  | 8.27
EL PECO 1102 | 253981102 | 52.21 |  |  |  | 52.21
EL PECO 1105 | 253981105 | 90.38 |  |  |  | 90.38
EL PECO 1106 | 253981106 | 50.3 |  |  |  | 50.3
ELECTRA 1101 | 162161101 | 80.15 |  | 76.61 |  | 3.54
ELECTRA 1102 | 162161102 | 19.48 |  | 16.9 |  | 2.58
ELK 1101 | 42981101 | 106.66 |  | 73.16 | 0.28 | 33.22
ELK CREEK 1101 | 102781101 | 158.88 |  | 68.21 |  | 90.67
ELK HILLS 1104 | 252441104 | 57.5 |  |  |  | 57.5
ELK HILLS 1106 | 252441106 | 21.59 |  |  |  | 21.59
EMBARCADERO (Z) 1112 | 22871112 | 0 |  |  |  | 0
EMBARCADERO (Z) 1113 | 22871113 | 0.32 |  |  |  | 0.32
EMBARCADERO (Z) 1114 | 22871114 | 0 |  |  |  | 0
EMBARCADERO (Z) 1115 | 22871115 | 0.24 |  |  |  | 0.24
EMBARCADERO (Z) 1116 | 22871116 | 1.02 |  |  |  | 1.02
EMBARCADERO (Z) 1118 | 22871118 | 0.01 |  |  |  | 0.01
EMBARCADERO (Z) 1119 | 22871119 | 0 |  |  |  | 0
EMBARCADERO (Z) 1120 | 22871120 | 0.32 |  |  |  | 0.32
EMBARCADERO (Z) 1122 | 22871122 | 0.01 |  |  |  | 0.01
EMBARCADERO (Z) 1123 | 22871123 | 0.36 |  |  |  | 0.36
EMERALD LAKE 0401 | 24080401 | 12.92 | 2.1 | 6.88 |  | 3.94
EMERALD LAKE 0402 | 24080402 | 6.57 |  | 6.57 |  | 0
ERTA 0403 | 83510403 | 2.99 |  |  |  | 2.99
ERTA 0404 | 83510404 | 6.52 |  |  |  | 6.52
ESQUON 1101 | 102171101 | 70.06 |  |  |  | 70.06
ESQUON 1102 | 102171102 | 50.86 |  |  |  | 50.86
ESQUON 1103 | 102171103 | 7.78 |  |  |  | 7.78
ESTUDILLO 0401 | 13480401 | 4.86 |  | 0.79 |  | 4.07
EUREKA A 1103 | 192121103 | 10.55 |  |  |  | 10.55
EUREKA A 1106 | 192121106 | 1.85 |  |  |  | 1.85
EUREKA A 1107 | 192121107 | 4.52 |  |  |  | 4.52
EUREKA E 1101 | 192331101 | 13.43 |  |  |  | 13.43
EUREKA E 1104 | 192331104 | 27.1 |  | 0.03 |  | 27.07
EUREKA E 1105 | 192331105 | 7.35 |  |  |  | 7.35
EVERGREEN 2101 | 82012101 | 2.53 |  |  |  | 2.53
EVERGREEN 2102 | 82012102 | 10.75 |  |  |  | 10.75
EVERGREEN 2103 | 82012103 | 19.19 |  |  |  | 19.19
EVERGREEN 2104 | 82012104 | 3.57 |  |  |  | 3.57
EVERGREEN 2105 | 82012105 | 4.64 |  |  |  | 4.64
FAIRHAVEN 1103 | 192451103 | 9.43 |  |  |  | 9.43
FAIRHAVEN 1104 | 192451104 | 3.33 |  |  |  | 3.33
FAIRMOUNT 0401 | 12650401 | 6.48 |  | 2.17 |  | 4.31
FAIRMOUNT 0402 | 12650402 | 4.9 |  |  |  | 4.9
FAIRVIEW 2206 | 13432206 | 14.32 |  |  |  | 14.32
FAIRVIEW 2207 | 13432207 | 50.72 |  | 20.93 |  | 29.79
FAIRVIEW 2208 | 13432208 | 10.08 |  |  |  | 10.08
FAIRWAY 1103 | 182061103 | 6.82 |  |  |  | 6.82
FAIRWAY 1104 | 182061104 | 22.91 |  |  |  | 22.91
FAIRWAY 1106 | 182061106 | 4.54 |  |  |  | 4.54
FAIRWAY 1107 | 182061107 | 19.43 |  |  |  | 19.43
FAIRWAY 1108 | 182061108 | 11.13 |  |  |  | 11.13
FAMOSO 1101 | 252461101 | 39.05 |  |  |  | 39.05
FAMOSO 1102 | 252461102 | 27.38 |  |  |  | 27.38
FAMOSO 1103 | 252461103 | 28.72 |  |  |  | 28.72
FAMOSO 1105 | 252461105 | 10.07 |  |  |  | 10.07
FAMOSO 1107 | 252461107 | 18.86 |  |  |  | 18.86
FELLOWS 2103 | 254242103 | 26.77 |  |  |  | 26.77
FELLOWS 2104 | 254242104 | 77.29 |  |  |  | 77.29
FIGARDEN 2102 | 254552102 | 23.25 |  |  |  | 23.25
FIGARDEN 2103 | 254552103 | 5.49 |  |  |  | 5.49
FIGARDEN 2104 | 254552104 | 1.76 |  |  |  | 1.76
FIGARDEN 2105 | 254552105 | 12.66 |  |  |  | 12.66
FIGARDEN 2107 | 254552107 | 5.52 |  |  |  | 5.52
FIGARDEN 2108 | 254552108 | 4.64 |  |  |  | 4.64
FIGARDEN 2109 | 254552109 | 3.91 |  |  |  | 3.91
FIGARDEN 2110 | 254552110 | 15.92 |  |  |  | 15.92
FIGARDEN 2111 | 254552111 | 4.83 |  |  |  | 4.83
FIGARDEN 2112 | 254552112 | 31.41 |  |  |  | 31.41
FIGARDEN 2113 | 254552113 | 11.3 |  |  |  | 11.3
FIREBAUGH 1101 | 253471101 | 93.46 |  |  |  | 93.46
FIREBAUGH 1102 | 253471102 | 52.74 |  |  |  | 52.74
FIREBAUGH 1103 | 253471103 | 75.73 |  |  |  | 75.73
FITCH MOUNTAIN 1111 | 42751111 | 29.67 |  | 0.29 | 0.03 | 29.35
FITCH MOUNTAIN 1112 | 42751112 | 0.01 |  |  |  | 0.01
FITCH MOUNTAIN 1113 | 42751113 | 145.61 | 30.8 | 46.2 | 0.25 | 68.36
FLINT 1101 | 152531101 | 14.65 |  | 2.45 | 0.53 | 11.67
FLINT 1102 | 152531102 | 0.12 |  | 0.12 |  | 0
FLORENCE 0401 | 12690401 | 4.33 |  | 0.83 |  | 3.5
FMC 1105 | 83871105 | 4.81 |  |  |  | 4.81
FMC 1108 | 83871108 | 1.42 |  |  |  | 1.42
FMC 1109 | 83871109 | 1.03 |  |  |  | 1.03
FMC 1111 | 83871111 | 1.39 |  |  |  | 1.39
FMC 1112 | 83871112 | 11.83 |  |  |  | 11.83
FOOTHILL 1101 | 182951101 | 39.48 |  | 18.9 |  | 20.58
FOOTHILL 1102 | 182951102 | 15.64 |  | 7.61 |  | 8.03
FORESTHILL 1101 | 152181101 | 59.33 | 59.28 | 0.05 |  | 0
FORESTHILL 1102 | 152181102 | 29.51 | 21.74 | 7.77 |  | 0
FORT BRAGG A 1101 | 42761101 | 81.11 |  | 70.45 |  | 10.66
FORT BRAGG A 1102 | 42761102 | 81.68 |  | 66.14 | 0.18 | 15.36
FORT BRAGG A 1103 | 42761103 | 2.68 |  | 0.07 |  | 2.61
FORT BRAGG A 1104 | 42761104 | 39.15 |  | 25.06 |  | 14.09
FORT ORD 1101 | 182401101 | 16.98 |  |  |  | 16.98
FORT ORD 2105 | 182402105 | 7.22 |  |  |  | 7.22
FORT ORD 2106 | 182402106 | 24.03 |  | 2.2 |  | 21.83
FORT ORD 2107 | 182402107 | 19.01 |  | 3.72 |  | 15.29
FORT ORD 2108 | 182402108 | 0.9 |  |  |  | 0.9
FORT ROSS 1121 | 42851121 | 93.83 | 21.98 | 70.08 |  | 1.77
FORT SEWARD 1121 | 192321121 | 48.14 |  | 36.19 |  | 11.95
FORT SEWARD 1122 | 192321122 | 22.09 |  | 17.68 |  | 4.41
FRANKLIN 1101 | 13921101 | 9.37 |  | 1.27 |  | 8.1
FRANKLIN 1102 | 13921102 | 4.46 |  |  |  | 4.46
FRANKLIN 1103 | 13921103 | 12.31 |  |  |  | 12.31
FRANKLIN 1104 | 13921104 | 14.61 |  | 7.41 |  | 7.2
FREMONT 1103 | 14351103 | 3.26 |  |  |  | 3.26
FREMONT 1104 | 14351104 | 21.54 |  | 1.08 | 0.8 | 19.66
FREMONT 1107 | 14351107 | 15.15 |  |  |  | 15.15
FREMONT 1108 | 14351108 | 4.89 |  |  |  | 4.89
FREMONT 1109 | 14351109 | 13.68 |  |  |  | 13.68
FREMONT 1110 | 14351110 | 10.36 |  |  |  | 10.36
FREMONT 1112 | 14351112 | 0.18 |  |  |  | 0.18
FRENCH CAMP 1101 | 163291101 | 15.51 |  |  |  | 15.51
FRENCH CAMP 1102 | 163291102 | 87.23 |  |  |  | 87.23
FRENCH CAMP 1103 | 163291103 | 1.23 |  |  |  | 1.23
FRENCH CAMP 1104 | 163291104 | 5.61 |  |  |  | 5.61
FRENCH GULCH 1101 | 103381101 | 15.99 |  | 15.99 |  | 0
FRENCH GULCH 1102 | 103381102 | 18.78 |  | 18.68 |  | 0.1
FROGTOWN 1701 | 163451701 | 71.24 | 6.65 | 63.41 |  | 1.18
FROGTOWN 1702 | 163451702 | 228.76 |  | 203.65 |  | 25.11
FRUITLAND 1141 | 192311141 | 26.41 |  | 23.43 |  | 2.98
FRUITLAND 1142 | 192311142 | 67.08 |  | 57.07 | 0.03 | 9.98
FRUITVALE 1101 | 253391101 | 3.34 |  |  |  | 3.34
FRUITVALE 1103 | 253391103 | 11.77 |  |  |  | 11.77
FRUITVALE 1104 | 253391104 | 11.22 |  |  |  | 11.22
FRUITVALE 1105 | 253391105 | 3.39 |  |  |  | 3.39
FRUITVALE 1106 | 253391106 | 9.52 |  |  |  | 9.52
FRUITVALE 1108 | 253391108 | 9.01 |  |  |  | 9.01
FULTON 1101 | 42561101 | 4.17 |  |  |  | 4.17
FULTON 1102 | 42561102 | 61.52 | 1.64 | 26.37 |  | 33.51
FULTON 1103 | 42561103 | 0.01 |  |  |  | 0.01
FULTON 1104 | 42561104 | 8.43 |  | 0.41 |  | 8.02
FULTON 1105 | 42561105 | 41.67 |  |  |  | 41.67
FULTON 1106 | 42561106 | 5.35 |  |  |  | 5.35
FULTON 1107 | 42561107 | 47.38 | 34.2 | 0.01 |  | 13.17
GABILAN 1101 | 182331101 | 72.79 |  | 4.55 | 0 | 68.24
GABILAN 1102 | 182331102 | 9.8 |  |  |  | 9.8
GALLO 1101 | 254901101 | 0.72 |  |  |  | 0.72
GALLO 1102 | 254901102 | 0.08 |  |  |  | 0.08
GANSNER 1101 | 103021101 | 44.36 | 3 | 30.67 |  | 10.69
GANSO 1103 | 254541103 | 39.5 |  |  |  | 39.5
GANSO 1104 | 254541104 | 37.46 |  |  |  | 37.46
GARBERVILLE 1101 | 192221101 | 145.89 |  | 66.32 |  | 79.57
GARBERVILLE 1102 | 192221102 | 136.75 |  | 122.14 |  | 14.61
GARBERVILLE 1103 | 192221103 | 2.21 |  | 0.47 |  | 1.74
GARCIA 0401 | 43040401 | 0.01 |  | 0.01 |  | 0
GARDNER 0401 | 254930401 | 0.02 |  |  |  | 0.02
GATES 1101 | 253931101 | 15.5 |  |  |  | 15.5
GATES 1102 | 253931102 | 41.84 |  |  |  | 41.84
GATES 1104 | 253931104 | 0.03 |  |  |  | 0.03
GATES 1105 | 253931105 | 39.75 |  |  |  | 39.75
GATES 1106 | 253931106 | 45.31 |  |  |  | 45.31
GATES 1107 | 253931107 | 2.52 |  |  |  | 2.52
GATES 1108 | 253931108 | 2.57 |  |  |  | 2.57
GATES 1109 | 253931109 | 0.3 |  |  |  | 0.3
GATES 1110 | 253931110 | 42.83 |  |  |  | 42.83
GATES 1111 | 253931111 | 26.77 |  |  |  | 26.77
GATES 1112 | 253931112 | 0 |  |  |  | 0
GERBER 1101 | 103391101 | 30.32 |  |  |  | 30.32
GERBER 1102 | 103391102 | 71.39 |  |  |  | 71.39
GEYSERVILLE 1101 | 42891101 | 142.84 |  | 72.3 |  | 70.54
GEYSERVILLE 1102 | 42891102 | 118.86 | 20.32 | 33.92 |  | 64.62
GIFFEN 1102 | 253151102 | 41.47 |  |  |  | 41.47
GIFFEN 1103 | 253151103 | 49.37 |  |  |  | 49.37
GIFFEN 1106 | 253151106 | 2.18 |  |  |  | 2.18
GIFFEN 1107 | 253151107 | 2.66 |  |  |  | 2.66
GILL 0401 | 13550401 | 3.26 |  |  |  | 3.26
GILL 0402 | 13550402 | 3.85 |  |  |  | 3.85
GIRVAN 1101 | 103401101 | 106.4 | 42.22 | 58.79 |  | 5.39
GIRVAN 1102 | 103401102 | 76.33 | 33.67 | 10.86 | 0.03 | 31.77
GLENN 1101 | 102601101 | 137.37 |  | 0.26 |  | 137.11
GLENWOOD 0404 | 24090404 | 6.08 |  |  |  | 6.08
GLENWOOD 0405 | 24090405 | 5.74 |  |  |  | 5.74
GLENWOOD 0406 | 24090406 | 2.34 |  |  |  | 2.34
GLENWOOD 1101 | 24091101 | 5.43 |  |  |  | 5.43
GLENWOOD 1102 | 24091102 | 7.2 |  |  |  | 7.2
GOLDTREE 1105 | 182581105 | 11.78 |  | 6.79 |  | 4.99
GOLDTREE 1107 | 182581107 | 3.53 |  | 0.94 |  | 2.59
GOLDTREE 1108 | 182581108 | 21.78 |  | 3.45 | 0.04 | 18.29
GONZALES 1101 | 182131101 | 25.9 |  | 3.89 |  | 22.01
GONZALES 1102 | 182131102 | 0.73 |  |  |  | 0.73
GONZALES 1103 | 182131103 | 5.48 |  |  |  | 5.48
GONZALES 1104 | 182131104 | 54.34 |  | 0.74 |  | 53.6
GOOSE LAKE 1101 | 254201101 | 0.54 |  |  |  | 0.54
GOOSE LAKE 1103 | 254201103 | 73.95 |  |  |  | 73.95
GOOSE LAKE 1106 | 254201106 | 66.38 |  |  |  | 66.38
GOOSE LAKE 2104 | 254202104 | 47.36 |  |  |  | 47.36
GRAND ISLAND 2223 | 62462223 | 95.2 |  |  |  | 95.2
GRAND ISLAND 2224 | 62462224 | 62.16 |  |  |  | 62.16
GRAND ISLAND 2225 | 62462225 | 68.83 |  |  |  | 68.83
GRAND ISLAND 2226 | 62462226 | 21 |  |  |  | 21
GRAND ISLAND 2227 | 62462227 | 157.84 |  |  |  | 157.84
GRANT 1102 | 14381102 | 4.42 |  |  |  | 4.42
GRANT 1103 | 14381103 | 3.04 |  |  |  | 3.04
GRANT 1104 | 14381104 | 23.77 |  |  |  | 23.77
GRANT 1105 | 14381105 | 14.05 |  |  |  | 14.05
GRANT 1106 | 14381106 | 17.1 |  |  |  | 17.1
GRANT 1107 | 14381107 | 5.26 |  |  |  | 5.26
GRANT 1108 | 14381108 | 22.66 |  |  |  | 22.66
GRASS VALLEY 1101 | 152031101 | 24.83 | 7.73 | 14.38 | 1 | 1.72
GRASS VALLEY 1102 | 152031102 | 5.82 |  | 0.06 | 0.04 | 5.72
GRASS VALLEY 1103 | 152031103 | 87.81 |  | 86.2 |  | 1.61
GRAYS FLAT 0401 | 102530401 | 9.29 |  | 9.29 |  | 0
GREEN VALLEY 2101 | 83192101 | 156.26 | 32.72 | 7.64 |  | 115.9
GREEN VALLEY 2102 | 83192102 | 46.21 |  |  |  | 46.21
GREEN VALLEY 2103 | 83192103 | 68.76 |  |  | 0.09 | 68.67
GREEN VALLEY 2104 | 83192104 | 30.29 |  |  |  | 30.29
GREENBRAE 1101 | 43091101 | 1.82 |  |  |  | 1.82
GREENBRAE 1102 | 43091102 | 13.47 | 5.79 |  |  | 7.68
GREENBRAE 1103 | 43091103 | 7.19 |  | 0.75 |  | 6.44
GREENBRAE 1104 | 43091104 | 18.27 |  | 0.21 |  | 18.06
GUALALA 1111 | 42841111 | 37.93 |  | 33.26 |  | 4.67
GUALALA 1112 | 42841112 | 47.36 |  | 42.92 |  | 4.44
GUERNSEY 1101 | 252661101 | 43.71 |  |  |  | 43.71
GUERNSEY 1102 | 252661102 | 40.77 |  |  |  | 40.77
GUERNSEY 1103 | 252661103 | 31.9 |  |  |  | 31.9
GUERNSEY 1104 | 252661104 | 29.99 |  |  |  | 29.99
GUERNSEY 1105 | 252661105 | 2.17 |  |  |  | 2.17
GUERNSEY 1106 | 252661106 | 37.09 |  |  |  | 37.09
GUERNSEY 1108 | 252661108 | 2.17 |  |  |  | 2.17
GUSTINE 1101 | 163111101 | 67.93 |  |  |  | 67.93
GUSTINE 1102 | 163111102 | 136.47 |  |  |  | 136.47
HAAS 2101 | 259932101 | 12.29 |  | 3.78 | 3.06 | 5.45
HALF MOON BAY 1101 | 24101101 | 47.16 | 12.63 | 12.39 |  | 22.14
HALF MOON BAY 1102 | 24101102 | 48.22 | 5.57 | 2.87 |  | 39.78
HALF MOON BAY 1103 | 24101103 | 166.84 | 1.49 | 122.52 |  | 42.83
HALLS FLAT 1101 | 108011101 | 0.01 |  | 0.01 |  | 0
HALSEY 1101 | 152241101 | 68.4 |  | 68.4 |  | 0
HALSEY 1102 | 152241102 | 67.89 |  | 57.59 | 2.67 | 7.63
HAMILTON A 1101 | 102121101 | 36.78 |  |  |  | 36.78
HAMILTON A 1102 | 102121102 | 40.1 |  |  |  | 40.1
HAMILTON BRANCH 1101 | 102361101 | 34.42 |  | 24.28 | 2.16 | 7.98
HAMMER 1101 | 163301101 | 5.54 |  |  |  | 5.54
HAMMER 1102 | 163301102 | 2.77 |  |  |  | 2.77
HAMMER 1103 | 163301103 | 3.78 |  |  |  | 3.78
HAMMER 1104 | 163301104 | 10.69 |  |  |  | 10.69
HAMMER 1105 | 163301105 | 10.87 |  |  |  | 10.87
HAMMER 1106 | 163301106 | 7.25 |  |  |  | 7.25
HAMMER 1108 | 163301108 | 6.03 |  |  |  | 6.03
HAMMER 1109 | 163301109 | 3.86 |  |  |  | 3.86
HAMMONDS 1101 | 253401101 | 35.08 |  |  |  | 35.08
HAMMONDS 1102 | 253401102 | 72.89 |  |  |  | 72.89
HAMMONDS 1104 | 253401104 | 25.17 |  |  |  | 25.17
HARDING 0401 | 163310401 | 1.03 |  |  |  | 1.03
HARDING 0402 | 163310402 | 3.95 |  |  |  | 3.95
HARDING 0403 | 163310403 | 1.53 |  |  |  | 1.53
HARDING 0404 | 163310404 | 2.72 |  |  |  | 2.72
HARDING 0405 | 163310405 | 2.94 |  |  |  | 2.94
HARDING 0406 | 163310406 | 3.19 |  |  |  | 3.19
HARDWICK 1101 | 253711101 | 72.35 |  |  |  | 72.35
HARDWICK 1102 | 253711102 | 98.04 |  |  |  | 98.04
HARRIS 1108 | 192431108 | 32.89 |  | 1.71 |  | 31.18
HARRIS 1109 | 192431109 | 50.26 |  | 14.43 |  | 35.83
HARTER 1102 | 152851102 | 4.35 |  |  |  | 4.35
HARTER 1104 | 152851104 | 7.29 |  |  |  | 7.29
HARTER 1105 | 152851105 | 23.53 |  |  |  | 23.53
HARTER 1106 | 152851106 | 2.03 |  |  |  | 2.03
HARTER 1107 | 152851107 | 10.28 |  |  |  | 10.28
HARTLEY 1101 | 43211101 | 70.18 |  | 35 |  | 35.18
HARTLEY 1102 | 43211102 | 31.19 |  | 5.27 |  | 25.92
HATTON 1101 | 182291101 | 33.04 | 2.68 | 17.72 |  | 12.64
HATTON 1102 | 182291102 | 22.51 |  | 11.38 |  | 11.13
HAYWARD O 0401 | 12240401 | 3.31 |  |  |  | 3.31
HENRIETTA 1104 | 252681104 | 35.96 |  |  |  | 35.96
HENRIETTA 1106 | 252681106 | 46.18 |  |  |  | 46.18
HENRIETTA 1108 | 252681108 | 22.64 |  |  |  | 22.64
HENRIETTA 1110 | 252681110 | 85.74 |  |  |  | 85.74
HERDLYN 1102 | 163741102 | 78.92 |  |  |  | 78.92
HERDLYN 1103 | 163741103 | 93.73 |  |  |  | 93.73
HICKS 1108 | 83431108 | 12.13 |  |  | 0.61 | 11.52
HICKS 1109 | 83431109 | 15.1 |  |  |  | 15.1
HICKS 1110 | 83431110 | 8.08 |  |  | 0.11 | 7.97
HICKS 1111 | 83431111 | 21.95 |  |  |  | 21.95
HICKS 1112 | 83431112 | 4.46 |  |  |  | 4.46
HICKS 1113 | 83431113 | 19.33 |  |  |  | 19.33
HICKS 1114 | 83431114 | 9.59 |  |  |  | 9.59
HICKS 1115 | 83431115 | 15.5 |  | 0.05 |  | 15.45
HICKS 1116 | 83431116 | 34.35 |  | 13.92 |  | 20.43
HICKS 2101 | 83432101 | 39.85 | 2.03 | 10.07 | 0.24 | 27.51
HICKS 2102 | 83432102 | 3.92 |  |  |  | 3.92
HICKS 2103 | 83432103 | 21.11 | 4.79 | 2.08 |  | 14.24
HICKS 2105 | 83432105 | 11.65 |  |  |  | 11.65
HICKS 2111 | 83432111 | 4.59 |  |  |  | 4.59
HIGGINS 1103 | 152691103 | 148.64 |  | 143.81 | 3.45 | 1.38
HIGGINS 1104 | 152691104 | 88.14 |  | 72.63 | 10.51 | 5
HIGGINS 1107 | 152691107 | 32.62 |  | 17.95 | 0.01 | 14.66
HIGGINS 1108 | 152691108 | 0.02 |  |  |  | 0.02
HIGGINS 1109 | 152691109 | 87.22 |  | 83.4 |  | 3.82
HIGGINS 1110 | 152691110 | 57.3 |  | 48.93 |  | 8.37
HIGHLANDS 1101 | 43361101 | 0.03 |  | 0.03 |  | 0
HIGHLANDS 1102 | 43361102 | 61.77 | 9.37 | 27.98 |  | 24.42
HIGHLANDS 1103 | 43361103 | 121.57 |  | 107.97 | 0.87 | 12.73
HIGHLANDS 1104 | 43361104 | 30.67 |  | 13.35 |  | 17.32
HIGHWAY 1101 | 42651101 | 11.19 |  |  |  | 11.19
HIGHWAY 1102 | 42651102 | 17.3 |  |  |  | 17.3
HIGHWAY 1103 | 42651103 | 6.36 |  |  |  | 6.36
HIGHWAY 1104 | 42651104 | 9.59 |  |  |  | 9.59
HIGHWAY 1105 | 42651105 | 1.04 |  |  |  | 1.04
HIGHWAY 1106 | 42651106 | 15.28 |  |  |  | 15.28
HIGHWAY 1107 | 42651107 | 3.41 |  |  |  | 3.41
HILLSDALE 0401 | 24110401 | 7.46 |  |  |  | 7.46
HILLSDALE 0402 | 24110402 | 8.08 |  |  |  | 8.08
HILLSDALE 0403 | 24110403 | 3.29 |  |  |  | 3.29
HILLSDALE 0404 | 24110404 | 5.72 |  |  |  | 5.72
HILLSDALE 0405 | 24110405 | 5.96 |  |  |  | 5.96
HOLLISTER 2101 | 182492101 | 25.66 |  |  |  | 25.66
HOLLISTER 2102 | 182492102 | 107.43 |  | 27.73 |  | 79.7
HOLLISTER 2103 | 182492103 | 13.62 |  |  |  | 13.62
HOLLISTER 2104 | 182492104 | 80.7 |  | 6.17 |  | 74.53
HOLLISTER 2105 | 182492105 | 166.2 |  | 65.56 |  | 100.64
HOLLISTER 2106 | 182492106 | 38.91 |  | 8.1 | 0.06 | 30.75
HOLLISTER 2107 | 182492107 | 42.93 |  | 0.17 | 0.03 | 42.73
HOLLYWOOD 0401 | 13170401 | 5.36 |  | 2.78 |  | 2.58
HONCUT 1101 | 103211101 | 99.17 |  |  |  | 99.17
HONCUT 1102 | 103211102 | 140.65 |  | 2.57 |  | 138.08
HOOPA 1101 | 192401101 | 136.83 | 4.9 | 99.45 |  | 32.48
HOPLAND 1101 | 42251101 | 130.15 |  | 81.27 |  | 48.88
HORSESHOE 1101 | 152571101 | 35.09 |  | 3.87 |  | 31.22
HORSESHOE 1102 | 152571102 | 14.84 |  |  |  | 14.84
HORSESHOE 1103 | 152571103 | 5.27 |  |  |  | 5.27
HORSESHOE 1104 | 152571104 | 11.67 |  | 1.98 |  | 9.69
HORSESHOE 1105 | 152571105 | 2.27 |  |  |  | 2.27
HORSESHOE 1106 | 152571106 | 15.39 |  |  |  | 15.39
HUMBOLDT BAY 1101 | 192341101 | 12.94 |  |  |  | 12.94
HUMBOLDT BAY 1102 | 192341102 | 41.61 |  | 6.35 |  | 35.26
HUNTERS POINT (P) 1101 | 22331101 | 3.75 |  |  |  | 3.75
HUNTERS POINT (P) 1102 | 22331102 | 8.36 |  |  |  | 8.36
HUNTERS POINT (P) 1103 | 22331103 | 5.8 |  |  |  | 5.8
HUNTERS POINT (P) 1104 | 22331104 | 3.61 |  |  |  | 3.61
HUNTERS POINT (P) 1105 | 22331105 | 10.47 |  |  |  | 10.47
HUNTERS POINT (P) 1106 | 22331106 | 1.54 |  |  |  | 1.54
HUNTERS POINT (P) 1107 | 22331107 | 5.28 |  |  |  | 5.28
HUNTERS POINT (P) 1108 | 22331108 | 5.63 |  |  |  | 5.63
HUNTERS POINT (P) 1109 | 22331109 | 1.61 |  |  |  | 1.61
HURON 1106 | 253161106 | 17.08 |  |  |  | 17.08
HURON 1107 | 253161107 | 0.35 |  |  |  | 0.35
HURON 1108 | 253161108 | 10.29 |  |  |  | 10.29
HURON 1109 | 253161109 | 0.35 |  |  |  | 0.35
HURON 1112 | 253161112 | 13.79 |  |  |  | 13.79
HURON 1116 | 253161116 | 19.97 |  |  |  | 19.97
IGNACIO 1101 | 42481101 | 11.66 | 0.5 | 5.76 |  | 5.4
IGNACIO 1102 | 42481102 | 8.48 |  |  |  | 8.48
IGNACIO 1103 | 42481103 | 2.78 |  | 0.62 |  | 2.16
IGNACIO 1104 | 42481104 | 55.9 |  | 6.33 |  | 49.57
IGNACIO 1105 | 42481105 | 20.24 |  | 4.72 |  | 15.52
INDIAN FLAT 1104 | 252691104 | 16.07 |  | 16.07 |  | 0
INDUSTRIAL ACRES 0411 | 182300411 | 2.04 |  |  |  | 2.04
INDUSTRIAL ACRES 0412 | 182300412 | 9.82 |  |  |  | 9.82
INDUSTRIAL ACRES 0413 | 182300413 | 3.78 |  |  |  | 3.78
INDUSTRIAL ACRES 0415 | 182300415 | 1.43 |  |  |  | 1.43
IONE 1101 | 163881101 | 29.13 |  | 14.9 |  | 14.23
JACINTO 1101 | 102851101 | 76.85 |  |  | 0.09 | 76.76
JACINTO 1102 | 102851102 | 80.98 |  |  | 0.62 | 80.36
JACOBS CORNER 1101 | 254771101 | 61.77 |  |  |  | 61.77
JACOBS CORNER 1102 | 254771102 | 52.35 |  |  |  | 52.35
JAMESON 1101 | 63801101 | 0.01 |  |  |  | 0.01
JAMESON 1102 | 63801102 | 13.5 |  | 2.08 |  | 11.42
JAMESON 1103 | 63801103 | 10.84 |  | 2.19 |  | 8.65
JAMESON 1104 | 63801104 | 0.08 |  |  |  | 0.08
JAMESON 1105 | 63801105 | 49.7 |  | 3.71 |  | 45.99
JANES CREEK 1101 | 192391101 | 29.39 |  |  |  | 29.39
JANES CREEK 1102 | 192391102 | 6.22 |  |  |  | 6.22
JANES CREEK 1103 | 192391103 | 41.84 |  |  | 0.02 | 41.82
JANES CREEK 1104 | 192391104 | 2.6 |  |  |  | 2.6
JARVIS 1101 | 13501101 | 13.75 |  | 0.58 | 0.15 | 13.02
JARVIS 1103 | 13501103 | 3.43 |  |  |  | 3.43
JARVIS 1104 | 13501104 | 4.43 |  |  |  | 4.43
JARVIS 1105 | 13501105 | 7.99 |  |  |  | 7.99
JARVIS 1106 | 13501106 | 4.82 |  |  |  | 4.82
JARVIS 1107 | 13501107 | 3.28 |  |  |  | 3.28
JARVIS 1108 | 13501108 | 17.8 |  | 0.7 | 0.85 | 16.25
JARVIS 1109 | 13501109 | 4.18 |  |  |  | 4.18
JARVIS 1110 | 13501110 | 5.94 |  |  |  | 5.94
JARVIS 1111 | 13501111 | 19.02 | 0.87 | 0.03 |  | 18.12
JARVIS 1112 | 13501112 | 4.01 |  |  |  | 4.01
JERSEY ISLAND 0401 | 18320401 | 2.77 |  |  |  | 2.77
JESSUP 1101 | 103441101 | 79.58 | 0.2 | 63.59 |  | 15.79
JESSUP 1102 | 103441102 | 69.38 |  | 36.8 |  | 32.58
JESSUP 1103 | 103441103 | 36.74 |  | 2.72 | 1.12 | 32.9
JOLON 1102 | 182981102 | 105.93 |  | 65.5 |  | 40.43
JOLON 1103 | 182981103 | 18.66 |  | 12.67 |  | 5.99
JUDAH 0401 | 22400401 | 3.72 |  |  |  | 3.72
JUDAH 0402 | 22400402 | 2.08 |  |  |  | 2.08
KANAKA 1101 | 103221101 | 73.29 | 46.85 | 26.07 |  | 0.37
KASSON 1101 | 169961101 | 49.86 |  |  |  | 49.86
KASSON 1102 | 169961102 | 59.22 |  |  |  | 59.22
KEARNEY 1104 | 252701104 | 73.32 |  |  |  | 73.32
KEARNEY 1106 | 252701106 | 39.33 |  |  |  | 39.33
KEARNEY 1110 | 252701110 | 50.51 |  |  |  | 50.51
KEARNEY 1113 | 252701113 | 0.63 |  |  |  | 0.63
KEARNEY 1114 | 252701114 | 13.39 |  |  |  | 13.39
KERCKHOFF 1101 | 252561101 | 34.01 |  | 34.01 |  | 0
KERMAN 1101 | 252711101 | 145.54 |  |  |  | 145.54
KERMAN 1102 | 252711102 | 58.25 |  |  |  | 58.25
KERMAN 1103 | 252711103 | 56.68 |  |  |  | 56.68
KERMAN 1104 | 252711104 | 66.04 |  |  |  | 66.04
KERMAN 1106 | 252711106 | 75.33 |  |  |  | 75.33
KERMAN 1108 | 252711108 | 28.17 |  |  |  | 28.17
KERN OIL 1103 | 252721103 | 11.53 |  |  |  | 11.53
KERN OIL 1104 | 252721104 | 39.04 |  |  |  | 39.04
KERN OIL 1106 | 252721106 | 42.29 |  | 0.45 |  | 41.84
KERN OIL 1107 | 252721107 | 23.9 |  |  |  | 23.9
KERN OIL 1108 | 252721108 | 7.28 |  |  |  | 7.28
KERN OIL 1109 | 252721109 | 11.32 |  |  |  | 11.32
KERN OIL 1110 | 252721110 | 8.61 |  |  |  | 8.61
KERN OIL 1112 | 252721112 | 0.04 |  |  |  | 0.04
KERN OIL 1114 | 252721114 | 21.55 |  |  |  | 21.55
KERN OIL 1116 | 252721116 | 2.12 |  |  |  | 2.12
KERN POWER 2101 | 255262101 | 2.01 |  |  |  | 2.01
KERN POWER 2102 | 255262102 | 4.37 |  |  |  | 4.37
KERN POWER 2103 | 255262103 | 12.53 |  |  |  | 12.53
KERN POWER 2104 | 255262104 | 5.06 |  |  |  | 5.06
KERN POWER 2105 | 255262105 | 12.07 |  |  |  | 12.07
KESWICK 1101 | 103451101 | 47.84 | 44.48 | 3.31 |  | 0.05
KETTLEMAN HILLS 1101 | 252731101 | 34.32 |  |  |  | 34.32
KETTLEMAN HILLS 2104 | 252732104 | 29.31 |  |  |  | 29.31
KING CITY 1101 | 182031101 | 6.97 |  |  |  | 6.97
KING CITY 1102 | 182031102 | 21.42 |  |  |  | 21.42
KING CITY 1103 | 182031103 | 27.82 |  | 17.76 |  | 10.06
KING CITY 1104 | 182031104 | 13.94 |  |  |  | 13.94
KING CITY 1105 | 182031105 | 3.07 |  |  |  | 3.07
KING CITY 1106 | 182031106 | 71.75 |  |  |  | 71.75
KING CITY 1107 | 182031107 | 0.02 |  |  |  | 0.02
KING CITY 1108 | 182031108 | 0.02 |  |  |  | 0.02
KINGSBURG 1102 | 252241102 | 15.64 |  |  |  | 15.64
KINGSBURG 1108 | 252241108 | 41.17 |  |  |  | 41.17
KINGSBURG 1110 | 252241110 | 86.36 |  |  |  | 86.36
KINGSBURG 1111 | 252241111 | 82.11 |  |  |  | 82.11
KINGSBURG 1112 | 252241112 | 14.21 |  |  |  | 14.21
KINGSBURG 1113 | 252241113 | 51.6 |  |  |  | 51.6
KINGSBURG 1114 | 252241114 | 18.54 |  |  |  | 18.54
KINGSBURG 1116 | 252241116 | 113.99 |  |  |  | 113.99
KIRKER 2103 | 14452103 | 7.36 |  |  |  | 7.36
KIRKER 2104 | 14452104 | 13.27 |  |  |  | 13.27
KIRKER 2105 | 14452105 | 9.61 |  |  |  | 9.61
KIRKER 2106 | 14452106 | 18.21 |  |  |  | 18.21
KIRKER 2107 | 14452107 | 7.77 |  |  |  | 7.77
KIRKER 2108 | 14452108 | 10.14 |  |  |  | 10.14
KIRKER 2109 | 14452109 | 8.63 |  |  |  | 8.63
KNIGHTS LANDING 1101 | 62721101 | 45.13 |  |  |  | 45.13
KNIGHTS LANDING 1102 | 62721102 | 118.81 |  |  |  | 118.81
KONOCTI 1102 | 43311102 | 150.33 | 63.88 | 61.26 | 0.57 | 24.62
KONOCTI 1108 | 43311108 | 33.15 |  | 20.47 | 0.15 | 12.53
LAKEVIEW 1102 | 253411102 | 52.55 |  |  |  | 52.55
LAKEVIEW 1103 | 253411103 | 22.7 |  |  |  | 22.7
LAKEVIEW 1106 | 253411106 | 36.37 |  |  |  | 36.37
LAKEVIEW 1107 | 253411107 | 26.06 |  |  |  | 26.06
LAKEVILLE 1101 | 43371101 | 19.7 |  |  |  | 19.7
LAKEVILLE 1102 | 43371102 | 50.39 | 0.07 | 18.13 |  | 32.19
LAKEVILLE 1105 | 43371105 | 4.22 |  |  |  | 4.22
LAKEWOOD 1101 | 13531101 | 0.72 |  |  | 0.07 | 0.65
LAKEWOOD 1102 | 13531102 | 9.51 |  | 0.1 | 0.08 | 9.33
LAKEWOOD 1103 | 13531103 | 2.57 |  |  | 0.63 | 1.94
LAKEWOOD 1104 | 13531104 | 11.79 |  |  |  | 11.79
LAKEWOOD 2107 | 13532107 | 33.32 |  | 7.76 |  | 25.56
LAKEWOOD 2108 | 13532108 | 0.53 |  |  |  | 0.53
LAKEWOOD 2109 | 13532109 | 7.3 | 0.42 |  | 0.01 | 6.87
LAKEWOOD 2110 | 13532110 | 22.77 |  |  | 0.47 | 22.3
LAKEWOOD 2111 | 13532111 | 2.33 |  |  |  | 2.33
LAKEWOOD 2112 | 13532112 | 8.95 |  |  |  | 8.95
LAKEWOOD 2223 | 13532223 | 9.19 |  |  |  | 9.19
LAKEWOOD 2224 | 13532224 | 31.6 | 0.82 |  | 0.47 | 30.31
LAKEWOOD 2225 | 13532225 | 3.28 |  |  |  | 3.28
LAKEWOOD 2226 | 13532226 | 8.06 |  |  |  | 8.06
LAKEWOOD 2227 | 13532227 | 7.93 | 0.03 |  |  | 7.9
LAMMERS 1101 | 162771101 | 9.67 |  |  |  | 9.67
LAMMERS 1102 | 162771102 | 3.57 |  |  |  | 3.57
LAMMERS 1103 | 162771103 | 6.48 |  |  |  | 6.48
LAMMERS 1104 | 162771104 | 2.88 |  |  |  | 2.88
LAMMERS 1105 | 162771105 | 1.77 |  |  |  | 1.77
LAMMERS 1106 | 162771106 | 2.29 |  |  |  | 2.29
LAMMERS 1107 | 162771107 | 9.11 |  |  |  | 9.11
LAMMERS 1108 | 162771108 | 1.11 |  |  |  | 1.11
LAMONT 1102 | 253911102 | 45.06 |  |  |  | 45.06
LAMONT 1103 | 253911103 | 26.93 |  |  |  | 26.93
LAMONT 1104 | 253911104 | 76.63 |  | 4.72 |  | 71.91
LAMONT 1105 | 253911105 | 36.88 |  |  |  | 36.88
LAMONT 1106 | 253911106 | 22.52 |  |  |  | 22.52
LAMONT 1107 | 253911107 | 46.21 |  |  |  | 46.21
LARKIN (Y) 1107 | 22801107 | 2.37 |  |  |  | 2.37
LARKIN (Y) 1108 | 22801108 | 0.1 |  |  |  | 0.1
LARKIN (Y) 1109 | 22801109 | 0.3 |  |  |  | 0.3
LARKIN (Y) 1110 | 22801110 | 0.23 |  |  |  | 0.23
LARKIN (Y) 1111 | 22801111 | 0.12 |  |  |  | 0.12
LARKIN (Y) 1119 | 22801119 | 1.73 |  |  |  | 1.73
LARKIN (Y) 1120 | 22801120 | 2.12 |  |  |  | 2.12
LARKIN (Y) 1127 | 22801127 | 1.53 |  |  |  | 1.53
LARKIN (Y) 1128 | 22801128 | 0.11 |  |  |  | 0.11
LARKIN (Y) 1135 | 22801135 | 1.68 |  |  |  | 1.68
LARKIN (Y) 1136 | 22801136 | 1.3 |  |  |  | 1.3
LARKIN (Y) 1137 | 22801137 | 0.01 |  |  |  | 0.01
LARKIN (Y) 1138 | 22801138 | 1.48 |  |  |  | 1.48
LARKIN (Y) 1140 | 22801140 | 0.11 |  |  |  | 0.11
LARKIN (Y) 1141 | 22801141 | 0.03 |  |  |  | 0.03
LAS GALLINAS A 1103 | 42991103 | 5.28 |  |  |  | 5.28
LAS GALLINAS A 1104 | 42991104 | 14.95 |  | 0.32 |  | 14.63
LAS GALLINAS A 1105 | 42991105 | 18.34 | 7.19 | 2.85 |  | 8.3
LAS GALLINAS A 1106 | 42991106 | 15.85 | 0.02 | 1.16 | 0.02 | 14.65
LAS GALLINAS A 1107 | 42991107 | 8.06 |  | 0.02 |  | 8.04
LAS PALMAS 1101 | 254921101 | 0.27 |  |  |  | 0.27
LAS POSITAS 2103 | 14402103 | 2.99 |  |  |  | 2.99
LAS POSITAS 2104 | 14402104 | 11.42 |  |  |  | 11.42
LAS POSITAS 2105 | 14402105 | 3.76 |  |  |  | 3.76
LAS POSITAS 2106 | 14402106 | 18.08 |  |  |  | 18.08
LAS POSITAS 2107 | 14402107 | 11.25 |  |  |  | 11.25
LAS POSITAS 2108 | 14402108 | 20.03 |  | 6.78 |  | 13.25
LAS POSITAS 2109 | 14402109 | 11.55 |  |  |  | 11.55
LAS POSITAS 2110 | 14402110 | 19.73 |  |  |  | 19.73
LAS PULGAS 0401 | 24120401 | 8.94 |  | 1.98 |  | 6.96
LAS PULGAS 0402 | 24120402 | 2.58 |  |  |  | 2.58
LAS PULGAS 0403 | 24120403 | 7.9 |  |  |  | 7.9
LAS PULGAS 0404 | 24120404 | 4.08 |  |  |  | 4.08
LATHROP 0402 | 163030402 | 0.04 |  |  |  | 0.04
LAURELES 1111 | 182371111 | 106.36 | 5.72 | 99.55 |  | 1.09
LAURELES 1112 | 182371112 | 43.21 |  | 33.09 |  | 10.12
LAWNDALE 0401 | 22440401 | 4.75 |  |  |  | 4.75
LAWNDALE 0402 | 22440402 | 4.77 |  |  |  | 4.77
LAWRENCE 1102 | 83421102 | 0.08 |  |  |  | 0.08
LAWRENCE 1103 | 83421103 | 0.22 |  |  |  | 0.22
LAWRENCE 1104 | 83421104 | 9.36 |  |  |  | 9.36
LAWRENCE 1105 | 83421105 | 1.07 |  |  |  | 1.07
LAWRENCE 1106 | 83421106 | 2.3 |  |  |  | 2.3
LAWRENCE 1107 | 83421107 | 4.64 |  |  |  | 4.64
LAWRENCE 1108 | 83421108 | 0.86 |  |  |  | 0.86
LAWRENCE 1109 | 83421109 | 1.98 |  |  |  | 1.98
LAWRENCE 1110 | 83421110 | 3.88 |  |  |  | 3.88
LAWRENCE 1111 | 83421111 | 3.71 |  |  |  | 3.71
LAWRENCE 1112 | 83421112 | 11.13 |  |  |  | 11.13
LAWRENCE 1113 | 83421113 | 5.7 |  |  |  | 5.7
LAYTONVILLE 1101 | 42681101 | 93.66 |  | 65.87 | 0.03 | 27.76
LAYTONVILLE 1102 | 42681102 | 120.84 | 3.38 | 102.57 |  | 14.89
LE GRAND 1104 | 255361104 | 56.8 |  |  |  | 56.8
LE GRAND 1106 | 255361106 | 59.82 |  |  |  | 59.82
LE GRAND 1110 | 255361110 | 91.91 |  |  |  | 91.91
LE GRAND 1112 | 255361112 | 68.87 |  |  |  | 68.87
LEMOORE 1101 | 253601101 | 41.73 |  |  |  | 41.73
LEMOORE 1102 | 253601102 | 11.2 |  |  |  | 11.2
LEMOORE 1103 | 253601103 | 14.46 |  |  |  | 14.46
LEMOORE 1104 | 253601104 | 49.98 |  |  |  | 49.98
LEMOORE 1105 | 253601105 | 12.04 |  |  |  | 12.04
LERDO 1110 | 253491110 | 11.98 |  |  |  | 11.98
LERDO 1111 | 253491111 | 36.14 |  |  |  | 36.14
LERDO 1112 | 253491112 | 38.61 |  |  |  | 38.61
LERDO 1113 | 253491113 | 38.48 |  |  |  | 38.48
LERDO 1114 | 253491114 | 10.21 |  |  |  | 10.21
LERDO 1115 | 253491115 | 15.74 |  |  |  | 15.74
LERDO 1116 | 253491116 | 31.84 |  |  |  | 31.84
LINCOLN 1101 | 153701101 | 49.93 |  | 15.88 |  | 34.05
LINCOLN 1102 | 153701102 | 9.59 |  |  |  | 9.59
LINCOLN 1104 | 153701104 | 127.98 |  | 25.95 |  | 102.03
LINCOLN 1105 | 153701105 | 32.11 |  |  |  | 32.11
LINCOLN 2108 | 153702108 | 1.66 |  |  |  | 1.66
LINCOLN 2109 | 153702109 | 0.82 |  |  |  | 0.82
LINDEN 1101 | 162071101 | 34.86 |  |  |  | 34.86
LINDEN 1103 | 162071103 | 60.12 |  |  |  | 60.12
LINDEN 1104 | 162071104 | 72.63 |  |  |  | 72.63
LIVE OAK 1101 | 153771101 | 44.63 |  |  |  | 44.63
LIVE OAK 1102 | 153771102 | 25.81 |  |  |  | 25.81
LIVE OAK 1104 | 153771104 | 113.38 |  |  |  | 113.38
LIVERMORE 1101 | 12141101 | 6.06 |  |  |  | 6.06
LIVERMORE 1102 | 12141102 | 4.24 |  |  |  | 4.24
LIVERMORE 1103 | 12141103 | 4.68 |  |  |  | 4.68
LIVERMORE 1104 | 12141104 | 8.64 |  |  |  | 8.64
LIVINGSTON 1101 | 252261101 | 103.27 |  |  |  | 103.27
LIVINGSTON 1102 | 252261102 | 13.57 |  |  |  | 13.57
LIVINGSTON 1104 | 252261104 | 50.77 |  |  |  | 50.77
LIVINGSTON 1105 | 252261105 | 88.88 |  |  |  | 88.88
LIVINGSTON 1106 | 252261106 | 62.09 |  |  |  | 62.09
LLAGAS 2101 | 83182101 | 102.21 |  | 21.39 |  | 80.82
LLAGAS 2102 | 83182102 | 12.72 |  |  |  | 12.72
LLAGAS 2103 | 83182103 | 16.78 |  |  |  | 16.78
LLAGAS 2104 | 83182104 | 30.12 |  | 2.68 |  | 27.44
LLAGAS 2105 | 83182105 | 17.76 | 0.12 | 0.46 |  | 17.18
LLAGAS 2106 | 83182106 | 32.27 |  | 1.18 |  | 31.09
LLAGAS 2107 | 83182107 | 22.41 | 3.63 | 2.65 |  | 16.13
LOCKEFORD 2101 | 163682101 | 90.95 |  |  |  | 90.95
LOCKEFORD 2102 | 163682102 | 249.88 |  |  |  | 249.88
LOCKHEED NO 1 1105 | 82991105 | 0.47 |  |  |  | 0.47
LOCKHEED NO 2 1103 | 83001103 | 0.52 |  |  |  | 0.52
LOCKHEED NO 2 1106 | 83001106 | 0.37 |  |  |  | 0.37
LOCKHEED NO 2 1107 | 83001107 | 0.77 |  |  |  | 0.77
LOCKHEED NO 2 1108 | 83001108 | 1.25 |  |  |  | 1.25
LODI 1101 | 162111101 | 44.35 |  |  |  | 44.35
LODI 1102 | 162111102 | 97.3 |  |  |  | 97.3
LOGAN CREEK 2101 | 103142101 | 163.72 |  |  | 2.58 | 161.14
LOGAN CREEK 2102 | 103142102 | 242.22 |  | 3.48 |  | 238.74
LOGAN CREEK 2103 | 103142103 | 3.17 |  |  |  | 3.17
LOGAN CREEK 2199 | 103142199 | 0.03 |  |  |  | 0.03
LONE TREE 2101 | 13232101 | 0.28 |  |  |  | 0.28
LONE TREE 2102 | 13232102 | 14.29 |  |  |  | 14.29
LONE TREE 2105 | 13232105 | 21.53 |  | 10.65 | 0.03 | 10.85
LONE TREE 2106 | 13232106 | 1.24 |  |  |  | 1.24
LOS ALTOS 1103 | 82241103 | 6.82 |  |  |  | 6.82
LOS ALTOS 1104 | 82241104 | 13.04 |  |  |  | 13.04
LOS ALTOS 1105 | 82241105 | 2.01 |  |  |  | 2.01
LOS ALTOS 1106 | 82241106 | 9.98 |  |  |  | 9.98
LOS ALTOS 1107 | 82241107 | 2.97 |  |  |  | 2.97
LOS COCHES 1101 | 182151101 | 24.55 |  | 2.3 |  | 22.25
LOS COCHES 1102 | 182151102 | 29.18 |  |  |  | 29.18
LOS GATOS 1101 | 82021101 | 21 |  | 11.82 |  | 9.18
LOS GATOS 1102 | 82021102 | 3.15 |  | 1.09 |  | 2.06
LOS GATOS 1106 | 82021106 | 95.87 | 92.6 | 2.43 |  | 0.84
LOS GATOS 1107 | 82021107 | 93.92 | 80.4 | 12.74 |  | 0.78
LOS GATOS 1108 | 82021108 | 6.26 | 1.13 | 3.3 |  | 1.83
LOS MOLINOS 1101 | 103481101 | 55.9 |  | 0.19 |  | 55.71
LOS MOLINOS 1102 | 103481102 | 47.89 |  |  | 0.05 | 47.84
LOS OSITOS 2101 | 182082101 | 109.9 |  |  | 0.35 | 109.55
LOS OSITOS 2102 | 182082102 | 51.62 |  | 2.48 |  | 49.14
LOS OSITOS 2103 | 182082103 | 100.74 |  | 44.31 |  | 56.43
LOST HILLS 1101 | 254281101 | 0.01 |  |  |  | 0.01
LOW GAP 1101 | 192411101 | 72.34 |  | 70.63 |  | 1.71
LOYOLA 0401 | 82160401 | 8.28 |  |  |  | 8.28
LOYOLA 0403 | 82160403 | 9.03 |  |  |  | 9.03
LOYOLA 1101 | 82161101 | 19.36 |  |  |  | 19.36
LOYOLA 1102 | 82161102 | 51.08 |  | 0.02 |  | 51.06
LUCERNE 1103 | 43351103 | 52.86 |  | 26.79 |  | 26.07
LUCERNE 1106 | 43351106 | 47.71 |  | 36.84 |  | 10.87
MABURY 1103 | 82191103 | 8 |  |  |  | 8
MABURY 1104 | 82191104 | 14.1 |  |  |  | 14.1
MABURY 1105 | 82191105 | 5.03 |  |  |  | 5.03
MABURY 1106 | 82191106 | 15.31 |  |  |  | 15.31
MADERA 1102 | 252761102 | 0.02 |  |  |  | 0.02
MADERA 1104 | 252761104 | 12.82 |  |  |  | 12.82
MADERA 1106 | 252761106 | 8.72 |  |  |  | 8.72
MADERA 1112 | 252761112 | 12.29 |  |  |  | 12.29
MADERA 1114 | 252761114 | 11.58 |  |  |  | 11.58
MADERA 1116 | 252761116 | 20.03 |  |  |  | 20.03
MADERA 1118 | 252761118 | 8.92 |  |  |  | 8.92
MADERA 1119 | 252761119 | 112.5 |  |  |  | 112.5
MADISON 1103 | 63171103 | 71.48 |  |  | 0.06 | 71.42
MADISON 1105 | 63171105 | 86.16 |  | 0.18 | 0.02 | 85.96
MADISON 2101 | 63172101 | 167.59 |  | 5.27 | 0.31 | 162.01
MAGUNDEN 1101 | 252771101 | 19.61 |  |  |  | 19.61
MAGUNDEN 1104 | 252771104 | 8.14 |  |  |  | 8.14
MAGUNDEN 1105 | 252771105 | 11.73 |  |  |  | 11.73
MAGUNDEN 1106 | 252771106 | 7.4 |  |  |  | 7.4
MAGUNDEN 1108 | 252771108 | 30.56 |  | 3.86 |  | 26.7
MAGUNDEN 2108 | 252772108 | 41.86 |  |  |  | 41.86
MAGUNDEN 2109 | 252772109 | 14.49 |  |  |  | 14.49
MAINE PRAIRIE 0401 | 68670401 | 0.06 |  |  |  | 0.06
MALAGA 1101 | 254251101 | 3.55 |  |  |  | 3.55
MALAGA 1102 | 254251102 | 55.51 |  |  |  | 55.51
MALAGA 1103 | 254251103 | 4.44 |  |  |  | 4.44
MALAGA 1104 | 254251104 | 15.46 |  |  |  | 15.46
MALAGA 1105 | 254251105 | 0.64 |  |  |  | 0.64
MALAGA 1106 | 254251106 | 8.97 |  |  |  | 8.97
MALAGA 1107 | 254251107 | 2.67 |  |  |  | 2.67
MALAGA 1108 | 254251108 | 21.88 |  |  |  | 21.88
MALAGA 1109 | 254251109 | 3.35 |  |  |  | 3.35
MALAGA 1110 | 254251110 | 30.8 |  |  |  | 30.8
MALAGA 1111 | 254251111 | 7.08 |  |  |  | 7.08
MANCHESTER 1101 | 253921101 | 11.88 |  |  |  | 11.88
MANCHESTER 1102 | 253921102 | 13.7 |  |  |  | 13.7
MANCHESTER 1103 | 253921103 | 12.13 |  |  |  | 12.13
MANCHESTER 1104 | 253921104 | 4.06 |  |  |  | 4.06
MANCHESTER 1105 | 253921105 | 9.07 |  |  |  | 9.07
MANCHESTER 1106 | 253921106 | 14.93 |  |  |  | 14.93
MANCHESTER 1107 | 253921107 | 8.73 |  |  |  | 8.73
MANCHESTER 1108 | 253921108 | 14.81 |  |  |  | 14.81
MANCHESTER 1109 | 253921109 | 15.16 |  |  |  | 15.16
MANCHESTER 1110 | 253921110 | 14.49 |  |  |  | 14.49
MANCHESTER 1111 | 253921111 | 13.28 |  |  |  | 13.28
MANCHESTER 1112 | 253921112 | 16.01 |  |  |  | 16.01
MANTECA 1701 | 162611701 | 6.17 |  |  |  | 6.17
MANTECA 1702 | 162611702 | 14.15 |  |  |  | 14.15
MANTECA 1703 | 162611703 | 15.75 |  |  |  | 15.75
MANTECA 1704 | 162611704 | 7.58 |  |  |  | 7.58
MANTECA 1705 | 162611705 | 35.06 |  |  |  | 35.06
MANTECA 1706 | 162611706 | 7.52 |  |  |  | 7.52
MANTECA 1707 | 162611707 | 7.98 |  |  |  | 7.98
MANTECA 1708 | 162611708 | 9.16 |  |  |  | 9.16
MAPLE 0401 | 13520401 | 3.67 |  |  |  | 3.67
MAPLE CREEK 1101 | 192101101 | 32.81 |  | 9.29 | 0.45 | 23.07
MARICOPA 1101 | 254211101 | 37.74 |  |  |  | 37.74
MARICOPA 1102 | 254211102 | 37.66 |  |  |  | 37.66
MARINA (F) 0401 | 22780401 | 0.53 |  |  |  | 0.53
MARINA (F) 0402 | 22780402 | 0.49 |  |  |  | 0.49
MARINA (F) 0403 | 22780403 | 0.04 |  |  |  | 0.04
MARINA (F) 0404 | 22780404 | 0.37 |  |  |  | 0.37
MARINA (F) 0405 | 22780405 | 0.14 |  |  |  | 0.14
MARINA (F) 0407 | 22780407 | 1.42 |  |  |  | 1.42
MARINA (F) 0408 | 22780408 | 0.53 |  |  |  | 0.53
MARINA (F) 1101 | 22781101 | 0.05 |  |  |  | 0.05
MARINA (F) 1102 | 22781102 | 0 |  |  |  | 0
MARINA (F) 1103 | 22781103 | 0.98 |  |  |  | 0.98
MARIPOSA 2101 | 254452101 | 243.58 | 66 | 172.65 | 0.07 | 4.86
MARIPOSA 2102 | 254452102 | 257.16 | 56.91 | 187.3 | 0.05 | 12.9
MARTELL 1101 | 163011101 | 82.12 |  | 69.84 |  | 12.28
MARTELL 1102 | 163011102 | 12.15 |  | 6.92 |  | 5.23
MARTELL 1103 | 163011103 | 29.44 |  | 20.34 | 0.02 | 9.08
MARYSVILLE 1102 | 152011102 | 7.58 |  |  |  | 7.58
MARYSVILLE 1103 | 152011103 | 12.43 |  |  |  | 12.43
MARYSVILLE 1104 | 152011104 | 5.33 |  |  |  | 5.33
MARYSVILLE 1105 | 152011105 | 8.55 |  |  |  | 8.55
MARYSVILLE 1106 | 152011106 | 3.42 |  |  |  | 3.42
MARYSVILLE 1107 | 152011107 | 8.43 |  |  |  | 8.43
MARYSVILLE 1108 | 152011108 | 51.81 |  |  |  | 51.81
MAXWELL 1102 | 62881102 | 60.69 |  |  |  | 60.69
MAXWELL 1105 | 62881105 | 88.95 |  | 3.9 |  | 85.05
MAXWELL 1106 | 62881106 | 29.61 |  |  |  | 29.61
MC ARTHUR 1101 | 103491101 | 179.96 |  | 65.01 | 2.81 | 112.14
MC ARTHUR 1102 | 103491102 | 30.25 |  | 1.1 | 0.19 | 28.96
MC CALL 1101 | 254121101 | 97.23 |  |  |  | 97.23
MC CALL 1102 | 254121102 | 25.21 |  |  |  | 25.21
MC CALL 1103 | 254121103 | 15.1 |  |  |  | 15.1
MC CALL 1104 | 254121104 | 16.72 |  |  |  | 16.72
MC CALL 1105 | 254121105 | 15.24 |  |  |  | 15.24
MC CALL 1106 | 254121106 | 74.28 |  |  |  | 74.28
MC CALL 1107 | 254121107 | 82.92 |  |  |  | 82.92
MC CALL 1108 | 254121108 | 58.65 |  |  |  | 58.65
MC FARLAND 1101 | 253181101 | 14.01 |  |  |  | 14.01
MC FARLAND 1102 | 253181102 | 42.07 |  |  |  | 42.07
MC FARLAND 1104 | 253181104 | 42.34 |  |  |  | 42.34
MC FARLAND 1105 | 253181105 | 19.23 |  |  |  | 19.23
MC KEE 1103 | 83531103 | 22.09 |  | 0.58 |  | 21.51
MC KEE 1104 | 83531104 | 15.54 |  |  |  | 15.54
MC KEE 1105 | 83531105 | 8.39 |  |  |  | 8.39
MC KEE 1106 | 83531106 | 15.26 |  |  |  | 15.26
MC KEE 1107 | 83531107 | 38.27 |  | 2.68 |  | 35.59
MC KEE 1108 | 83531108 | 10.47 |  | 0.66 |  | 9.81
MC KEE 1109 | 83531109 | 1.77 |  |  |  | 1.77
MC KEE 1110 | 83531110 | 1.67 |  |  |  | 1.67
MC KEE 1111 | 83531111 | 24.53 |  | 8.71 |  | 15.82
MC KEE 1112 | 83531112 | 18.99 |  |  |  | 18.99
MC MULLIN 1104 | 254411104 | 62.04 |  |  |  | 62.04
MC MULLIN 1105 | 254411105 | 58.01 |  |  |  | 58.01
MC MULLIN 1106 | 254411106 | 94.45 |  |  |  | 94.45
MCKITTRICK 1101 | 252781101 | 51.39 |  |  |  | 51.39
MEADOW LANE 2102 | 14302102 | 0.01 |  |  |  | 0.01
MEADOW LANE 2103 | 14302103 | 19.04 |  |  |  | 19.04
MEADOW LANE 2104 | 14302104 | 4.16 |  |  |  | 4.16
MEADOW LANE 2105 | 14302105 | 14.4 |  |  | 0.03 | 14.37
MEADOW LANE 2106 | 14302106 | 23.3 | 0.74 | 0.11 |  | 22.45
MEADOW LANE 2107 | 14302107 | 8.48 |  |  |  | 8.48
MEADOW LANE 2108 | 14302108 | 23.97 |  |  |  | 23.97
MEADOW LANE 2109 | 14302109 | 0.58 |  |  |  | 0.58
MEADOW LANE 2110 | 14302110 | 6.61 |  |  |  | 6.61
MENDOCINO 1101 | 42951101 | 74.7 | 13.34 | 18.67 |  | 42.69
MENDOCINO 1102 | 42951102 | 0.05 |  |  |  | 0.05
MENDOTA 1101 | 252311101 | 14.9 |  |  |  | 14.9
MENDOTA 1102 | 252311102 | 98.22 |  |  |  | 98.22
MENDOTA 1103 | 252311103 | 15.35 |  |  |  | 15.35
MENDOTA 1104 | 252311104 | 54.68 |  |  |  | 54.68
MENLO 0401 | 24130401 | 7.21 |  |  |  | 7.21
MENLO 0402 | 24130402 | 7.58 |  |  |  | 7.58
MENLO 0403 | 24130403 | 7.64 |  |  |  | 7.64
MENLO 0404 | 24130404 | 8.21 |  |  |  | 8.21
MENLO 1101 | 24131101 | 1.51 |  |  |  | 1.51
MENLO 1102 | 24131102 | 63.76 | 0.01 | 28.3 |  | 35.45
MENLO 1103 | 24131103 | 56.4 |  | 39.11 |  | 17.29
MENLO 1104 | 24131104 | 16.85 |  |  |  | 16.85
MERCED 1108 | 252801108 | 69.6 |  |  |  | 69.6
MERCED 1114 | 252801114 | 58.12 |  |  | 0.02 | 58.1
MERCED 1116 | 252801116 | 77.75 |  |  |  | 77.75
MERCED 2101 | 252802101 | 40.24 |  |  |  | 40.24
MERCED 2102 | 252802102 | 26.05 |  |  |  | 26.05
MERCED FALLS 1102 | 252811102 | 153.73 |  | 93.6 |  | 60.13
MERIDIAN 1101 | 62541101 | 57.79 |  |  |  | 57.79
MERIDIAN 1102 | 62541102 | 71.95 |  |  |  | 71.95
MESA 1101 | 182821101 | 82.5 | 11.15 | 37.91 |  | 33.44
MESA 1102 | 182821102 | 35.28 |  |  |  | 35.28
MESA 1103 | 182821103 | 75.93 |  | 10 | 1.95 | 63.98
MESA 1104 | 182821104 | 34.94 |  |  |  | 34.94
METTLER 1109 | 163701109 | 20.43 |  |  |  | 20.43
METTLER 1110 | 163701110 | 38.08 |  |  |  | 38.08
MIDDLE RIVER 1101 | 162091101 | 31.37 |  |  |  | 31.37
MIDDLE RIVER 1102 | 162091102 | 32 |  |  |  | 32
MIDDLE RIVER 1103 | 162091103 | 28.63 |  |  |  | 28.63
MIDDLETOWN 1101 | 43141101 | 100.52 | 75.29 | 9.14 | 0.71 | 15.38
MIDDLETOWN 1102 | 43141102 | 48.12 | 0.04 | 36.19 |  | 11.89
MIDDLETOWN 1103 | 43141103 | 38.52 | 4.85 | 13.86 |  | 19.81
MIDWAY 1101 | 252611101 | 60.25 |  |  |  | 60.25
MIDWAY 1102 | 252611102 | 52.82 |  |  |  | 52.82
MIDWAY 1103 | 252611103 | 30.93 |  |  |  | 30.93
MIDWAY 1104 | 252611104 | 36.9 |  |  |  | 36.9
MILLBRAE 0401 | 22690401 | 2.82 |  |  |  | 2.82
MILLBRAE 0403 | 22690403 | 4.96 |  |  |  | 4.96
MILLBRAE 0404 | 22690404 | 7.11 |  |  |  | 7.11
MILLBRAE 1101 | 22691101 | 3.95 |  |  |  | 3.95
MILLBRAE 1102 | 22691102 | 4.8 |  |  |  | 4.8
MILLBRAE 1103 | 22691103 | 0.18 |  |  |  | 0.18
MILLBRAE 1104 | 22691104 | 15.85 |  |  |  | 15.85
MILLBRAE 1105 | 22691105 | 0.26 |  |  |  | 0.26
MILLBRAE 1106 | 22691106 | 3.66 |  |  |  | 3.66
MILLBRAE 1107 | 22691107 | 4.8 |  |  |  | 4.8
MILLBRAE 1108 | 22691108 | 14.26 |  |  |  | 14.26
MILPITAS 1101 | 82831101 | 4.1 |  |  |  | 4.1
MILPITAS 1103 | 82831103 | 0.07 |  |  |  | 0.07
MILPITAS 1104 | 82831104 | 1.03 |  |  |  | 1.03
MILPITAS 1105 | 82831105 | 4.83 |  | 0.07 |  | 4.76
MILPITAS 1106 | 82831106 | 3.14 |  |  |  | 3.14
MILPITAS 1108 | 82831108 | 13.47 |  | 0.02 |  | 13.45
MILPITAS 1109 | 82831109 | 49.42 |  | 29.7 |  | 19.72
MILPITAS 2110 | 82832110 | 10.39 |  |  |  | 10.39
MILPITAS 2111 | 82832111 | 0.58 |  |  |  | 0.58
MILPITAS 2112 | 82832112 | 0.87 |  |  |  | 0.87
MILPITAS 2113 | 82832113 | 0.12 |  |  |  | 0.12
MILPITAS 2114 | 82832114 | 0.17 |  |  |  | 0.17
MIRA VISTA 0401 | 12330401 | 8.85 |  |  |  | 8.85
MIRA VISTA 0403 | 12330403 | 7.14 |  |  |  | 7.14
MIRABEL 1101 | 42091101 | 50.47 | 19.07 | 8.95 |  | 22.45
MIRABEL 1102 | 42091102 | 57.52 | 31.74 | 4.83 |  | 20.95
MISSION (X) 0401 | 22010401 | 1.64 |  |  |  | 1.64
MISSION (X) 1102 | 22011102 | 0.17 |  |  |  | 0.17
MISSION (X) 1108 | 22011108 | 5.3 |  |  |  | 5.3
MISSION (X) 1109 | 22011109 | 1.13 |  |  |  | 1.13
MISSION (X) 1110 | 22011110 | 5.88 |  |  |  | 5.88
MISSION (X) 1113 | 22011113 | 2.76 |  |  |  | 2.76
MISSION (X) 1116 | 22011116 | 3.05 |  |  |  | 3.05
MISSION (X) 1118 | 22011118 | 0.6 |  |  |  | 0.6
MISSION (X) 1124 | 22011124 | 0.71 |  |  |  | 0.71
MISSION (X) 1125 | 22011125 | 0.97 |  |  |  | 0.97
MISSION (X) 1127 | 22011127 | 0.57 |  |  |  | 0.57
MISSION (X) 1128 | 22011128 | 0.8 |  |  |  | 0.8
MIWUK 1701 | 163661701 | 76.24 | 74.7 | 1.54 |  | 0
MIWUK 1702 | 163661702 | 74.63 | 71.99 | 2.64 |  | 0
MOLINO 1101 | 42571101 | 90.17 | 7.16 | 26.49 |  | 56.52
MOLINO 1102 | 42571102 | 161.63 | 90.09 | 19.9 |  | 51.64
MOLINO 1103 | 42571103 | 78.55 |  |  | 0.05 | 78.5
MOLINO 1104 | 42571104 | 61.25 |  | 2.38 |  | 58.87
MONARCH 0401 | 162300401 | 3.26 |  |  |  | 3.26
MONARCH 0402 | 162300402 | 2.88 |  |  |  | 2.88
MONARCH 0403 | 162300403 | 4.62 |  |  |  | 4.62
MONROE 1104 | 43301104 | 5.26 |  |  |  | 5.26
MONROE 1105 | 43301105 | 10.71 |  |  |  | 10.71
MONROE 1106 | 43301106 | 13.51 |  |  |  | 13.51
MONROE 2102 | 43302102 | 4.8 |  |  |  | 4.8
MONROE 2103 | 43302103 | 11.7 | 0.45 |  |  | 11.25
MONROE 2107 | 43302107 | 10.46 | 0.61 |  |  | 9.85
MONTAGUE 2101 | 83892101 | 0.88 |  |  |  | 0.88
MONTAGUE 2102 | 83892102 | 0.81 |  |  |  | 0.81
MONTAGUE 2103 | 83892103 | 0.94 |  |  |  | 0.94
MONTAGUE 2104 | 83892104 | 0.85 |  |  |  | 0.85
MONTAGUE 2105 | 83892105 | 0.78 |  |  |  | 0.78
MONTAGUE 2108 | 83892108 | 2.14 |  |  |  | 2.14
MONTAGUE 2109 | 83892109 | 0.81 |  |  |  | 0.81
MONTE RIO 1111 | 42811111 | 64.02 | 43.75 | 13.46 |  | 6.81
MONTE RIO 1112 | 42811112 | 19.7 | 19.7 |  |  | 0
MONTE RIO 1113 | 42811113 | 61.2 | 61.2 |  |  | 0
MONTICELLO 1101 | 43051101 | 123.87 |  | 108.48 | 0.04 | 15.35
MORAGA 1101 | 13801101 | 37.7 | 19.7 | 11.31 |  | 6.69
MORAGA 1102 | 13801102 | 13.38 | 2.92 | 2.12 |  | 8.34
MORAGA 1103 | 13801103 | 17.53 | 0.12 | 2.04 | 0.02 | 15.35
MORAGA 1104 | 13801104 | 21.24 | 0.01 | 13.69 |  | 7.54
MORAGA 1105 | 13801105 | 19.74 | 6.87 | 0.81 |  | 12.06
MORGAN HILL 2103 | 83242103 | 0.95 |  |  |  | 0.95
MORGAN HILL 2104 | 83242104 | 23.61 |  | 8.22 |  | 15.39
MORGAN HILL 2105 | 83242105 | 81.77 | 14.01 | 35.74 |  | 32.02
MORGAN HILL 2106 | 83242106 | 39.15 |  | 0.12 |  | 39.03
MORGAN HILL 2108 | 83242108 | 13.13 |  |  |  | 13.13
MORGAN HILL 2109 | 83242109 | 23.26 |  |  |  | 23.26
MORGAN HILL 2110 | 83242110 | 32.59 |  | 2.21 |  | 30.38
MORGAN HILL 2111 | 83242111 | 71.35 | 15.96 | 35.37 |  | 20.02
MORMON 1101 | 163211101 | 65.92 |  |  |  | 65.92
MORMON 1102 | 163211102 | 68.7 |  |  |  | 68.7
MORMON 1103 | 163211103 | 23.53 |  |  |  | 23.53
MORRO BAY 1101 | 183011101 | 46.02 | 0.49 | 4.91 |  | 40.62
MORRO BAY 1102 | 183011102 | 57.68 | 4.03 | 17.29 |  | 36.36
MOSHER 2104 | 163722104 | 0.01 |  |  |  | 0.01
MOSHER 2107 | 163722107 | 3.13 |  |  |  | 3.13
MOSHER 2108 | 163722108 | 1.88 |  |  |  | 1.88
MOSHER 2110 | 163722110 | 2.19 |  |  |  | 2.19
MOSHER 2111 | 163722111 | 17.72 |  |  |  | 17.72
MOUNTAIN QUARRIES 2101 | 152282101 | 215.63 | 22.75 | 191.92 |  | 0.96
MOUNTAIN VIEW 1102 | 82031102 | 14.31 |  |  |  | 14.31
MOUNTAIN VIEW 1103 | 82031103 | 2.84 |  |  |  | 2.84
MOUNTAIN VIEW 1104 | 82031104 | 8.08 |  |  |  | 8.08
MOUNTAIN VIEW 1105 | 82031105 | 9.44 |  |  |  | 9.44
MOUNTAIN VIEW 1106 | 82031106 | 7.37 |  |  |  | 7.37
MOUNTAIN VIEW 1107 | 82031107 | 19.42 |  |  |  | 19.42
MOUNTAIN VIEW 1108 | 82031108 | 14.7 |  |  |  | 14.7
MOUNTAIN VIEW 1109 | 82031109 | 10.03 |  |  |  | 10.03
MOUNTAIN VIEW 1110 | 82031110 | 9.4 |  |  |  | 9.4
MOUNTAIN VIEW 1111 | 82031111 | 1.74 |  |  |  | 1.74
MOUNTAIN VIEW 1112 | 82031112 | 0.97 |  |  |  | 0.97
MOUNTAIN VIEW 1113 | 82031113 | 4.03 |  |  |  | 4.03
MOUNTAIN VIEW 1114 | 82031114 | 6.62 |  |  |  | 6.62
MT EDEN 1101 | 13761101 | 6.69 |  |  |  | 6.69
MT EDEN 1102 | 13761102 | 9 |  |  |  | 9
MT EDEN 1103 | 13761103 | 13.17 |  |  |  | 13.17
MT EDEN 1104 | 13761104 | 14.04 |  |  |  | 14.04
MT EDEN 1105 | 13761105 | 6.92 |  |  |  | 6.92
MT EDEN 1106 | 13761106 | 5.21 |  |  |  | 5.21
MT EDEN 1107 | 13761107 | 6.1 |  |  |  | 6.1
MT EDEN 1108 | 13761108 | 24.83 |  |  |  | 24.83
MT EDEN 1109 | 13761109 | 17.04 |  |  |  | 17.04
MT EDEN 1110 | 13761110 | 1.73 |  |  |  | 1.73
MT EDEN 1111 | 13761111 | 3.25 |  |  |  | 3.25
MT EDEN 1112 | 13761112 | 15.27 |  |  |  | 15.27
MT EDEN 1113 | 13761113 | 3.45 |  |  |  | 3.45
MT EDEN 1114 | 13761114 | 3.99 |  |  |  | 3.99
NAPA 1102 | 42021102 | 32.6 |  | 0.27 |  | 32.33
NAPA 1103 | 42021103 | 14.95 |  |  |  | 14.95
NAPA 1105 | 42021105 | 15.61 |  |  |  | 15.61
NAPA 1106 | 42021106 | 1.26 |  |  |  | 1.26
NAPA 1109 | 42021109 | 11.65 |  |  |  | 11.65
NAPA 1110 | 42021110 | 13.33 |  |  |  | 13.33
NAPA 1112 | 42021112 | 52.03 |  | 19.3 | 0.01 | 32.72
NARROWS 2101 | 153132101 | 61.05 |  | 61.05 |  | 0
NARROWS 2102 | 153132102 | 117.9 |  | 93.86 | 0.28 | 23.76
NARROWS 2104 | 153132104 | 0 |  | 0 |  | 0
NARROWS 2105 | 153132105 | 196.5 |  | 176.82 | 0.58 | 19.1
NARROWS PH 1151 | 153131151 | 0.2 |  | 0.2 |  | 0
NEW HOPE 1101 | 162081101 | 38.17 |  |  |  | 38.17
NEW HOPE 1102 | 162081102 | 50.86 |  |  |  | 50.86
NEWARK 12KV 1101 | 12221101 | 1.44 |  |  |  | 1.44
NEWARK 12KV 1102 | 12221102 | 8.44 |  |  |  | 8.44
NEWARK 12KV 1103 | 12221103 | 18.17 |  |  |  | 18.17
NEWARK 12KV 1104 | 12221104 | 0.22 |  |  |  | 0.22
NEWARK 12KV 1105 | 12221105 | 3.18 |  |  |  | 3.18
NEWARK 12KV 1106 | 12221106 | 18.36 |  |  |  | 18.36
NEWARK 12KV 1107 | 12221107 | 21.49 |  |  |  | 21.49
NEWARK 12KV 1108 | 12221108 | 0.95 |  |  |  | 0.95
NEWARK 21KV 2102 | 12232102 | 2.7 |  |  |  | 2.7
NEWARK 21KV 2103 | 12232103 | 17.77 |  |  |  | 17.77
NEWARK 21KV 2104 | 12232104 | 4.99 |  |  |  | 4.99
NEWARK 21KV 2105 | 12232105 | 2.52 |  |  |  | 2.52
NEWARK 21KV 2107 | 12232107 | 7.08 |  |  |  | 7.08
NEWARK 21KV 2108 | 12232108 | 4.82 |  |  |  | 4.82
NEWARK 21KV 2109 | 12232109 | 0 |  |  |  | 0
NEWARK 21KV 2110 | 12232110 | 3.14 |  |  |  | 3.14
NEWARK 21KV 2111 | 12232111 | 0 |  |  |  | 0
NEWBURG 1131 | 192151131 | 31.06 |  | 5.66 |  | 25.4
NEWBURG 1132 | 192151132 | 22.39 |  | 1.29 |  | 21.1
NEWBURG 1133 | 192151133 | 16.96 |  | 2.38 |  | 14.58
NEWHALL 1109 | 254461109 | 73.83 |  |  |  | 73.83
NEWHALL 1111 | 254461111 | 54.26 |  |  |  | 54.26
NEWMAN 1101 | 162741101 | 41.04 |  |  |  | 41.04
NEWMAN 1102 | 162741102 | 9.55 |  |  |  | 9.55
NEWMAN 1105 | 162741105 | 42.75 |  |  |  | 42.75
NEWMAN 1106 | 162741106 | 43.96 |  |  |  | 43.96
NORCO 1101 | 254691101 | 34.02 |  |  |  | 34.02
NORCO 1102 | 254691102 | 7.67 |  |  |  | 7.67
NORD 1103 | 103071103 | 18.45 |  |  |  | 18.45
NORD 1104 | 103071104 | 51.16 |  |  |  | 51.16
NORD 1105 | 103071105 | 7 |  |  |  | 7
NORD 1106 | 103071106 | 10.87 |  |  |  | 10.87
NORIEGA 0401 | 22510401 | 1.56 |  |  |  | 1.56
NORIEGA 0402 | 22510402 | 1.77 |  |  |  | 1.77
NORTECH 2106 | 82462106 | 0.39 |  |  |  | 0.39
NORTECH 2107 | 82462107 | 0.1 |  |  |  | 0.1
NORTECH 2109 | 82462109 | 3.14 |  |  |  | 3.14
NORTECH 2110 | 82462110 | 9.5 |  |  |  | 9.5
NORTECH 2111 | 82462111 | 0.71 |  |  |  | 0.71
NORTH DUBLIN 2101 | 14052101 | 1.87 |  | 1.4 |  | 0.47
NORTH DUBLIN 2103 | 14052103 | 21.74 |  | 18.66 |  | 3.08
NORTH TOWER 1102 | 42041102 | 18.77 |  |  |  | 18.77
NORTH TOWER 1103 | 42041103 | 13.13 |  |  |  | 13.13
NORTH TOWER 1104 | 42041104 | 19.92 |  |  |  | 19.92
NORTH TOWER 1108 | 42041108 | 13.26 |  |  |  | 13.26
NORTH TOWER 2101 | 42042101 | 4.42 |  | 0.52 |  | 3.9
NORTH TOWER 2104 | 42042104 | 4.21 |  |  |  | 4.21
NOTRE DAME 1101 | 102041101 | 1.6 |  |  |  | 1.6
NOTRE DAME 1102 | 102041102 | 13.96 |  |  |  | 13.96
NOTRE DAME 1103 | 102041103 | 7.83 |  | 0.54 |  | 7.29
NOTRE DAME 1104 | 102041104 | 37.72 | 17.96 | 9.74 |  | 10.02
NOVATO 1101 | 42211101 | 3.48 |  | 0.6 |  | 2.88
NOVATO 1102 | 42211102 | 0.53 |  |  |  | 0.53
NOVATO 1103 | 42211103 | 2.96 |  |  |  | 2.96
NOVATO 1104 | 42211104 | 24.42 |  | 3.46 |  | 20.96
OAK 0401 | 12600401 | 5.45 |  | 3.46 |  | 1.99
OAK PARK 0401 | 163270401 | 2.52 |  |  |  | 2.52
OAK PARK 0402 | 163270402 | 0.51 |  |  |  | 0.51
OAKHURST 1101 | 254421101 | 91.25 | 2.56 | 87.84 |  | 0.85
OAKHURST 1102 | 254421102 | 16.35 | 1.18 | 11.33 | 1.31 | 2.53
OAKHURST 1103 | 254421103 | 123.55 | 80.76 | 40.13 | 0.36 | 2.3
OAKLAND C 1108 | 12011108 | 2.05 |  |  |  | 2.05
OAKLAND C 1109 | 12011109 | 3.3 |  |  |  | 3.3
OAKLAND C 1110 | 12011110 | 1.23 |  |  |  | 1.23
OAKLAND C 1112 | 12011112 | 1.2 |  |  |  | 1.2
OAKLAND C 1113 | 12011113 | 2.71 |  |  |  | 2.71
OAKLAND C 1114 | 12011114 | 3.43 |  |  |  | 3.43
OAKLAND C 1115 | 12011115 | 1.19 |  |  |  | 1.19
OAKLAND C 1116 | 12011116 | 2.5 |  |  |  | 2.5
OAKLAND C 1117 | 12011117 | 2.98 |  |  |  | 2.98
OAKLAND C 1118 | 12011118 | 3.34 |  |  |  | 3.34
OAKLAND C 1119 | 12011119 | 0.43 |  |  |  | 0.43
OAKLAND C 1120 | 12011120 | 2.97 |  |  |  | 2.97
OAKLAND C 1121 | 12011121 | 1.93 |  |  |  | 1.93
OAKLAND C 1132 | 12011132 | 1.24 |  |  |  | 1.24
OAKLAND C 1133 | 12011133 | 0.59 |  |  |  | 0.59
OAKLAND C 1134 | 12011134 | 1.3 |  |  |  | 1.3
OAKLAND D 0406 | 12040406 | 3.08 |  |  |  | 3.08
OAKLAND D 0407 | 12040407 | 0.33 |  |  |  | 0.33
OAKLAND D 0408 | 12040408 | 4.03 |  |  |  | 4.03
OAKLAND D 0410 | 12040410 | 2.77 |  |  |  | 2.77
OAKLAND D 1101 | 12041101 | 0 |  |  |  | 0
OAKLAND D 1102 | 12041102 | 2.86 |  |  |  | 2.86
OAKLAND D 1103 | 12041103 | 0.44 |  |  |  | 0.44
OAKLAND D 1104 | 12041104 | 5.92 |  |  |  | 5.92
OAKLAND D 1105 | 12041105 | 8.6 |  |  |  | 8.6
OAKLAND D 1106 | 12041106 | 8.85 |  |  |  | 8.85
OAKLAND D 1107 | 12041107 | 2.51 |  |  |  | 2.51
OAKLAND D 1110 | 12041110 | 5.49 |  |  |  | 5.49
OAKLAND D 1111 | 12041111 | 7.84 |  |  |  | 7.84
OAKLAND D 1112 | 12041112 | 10.67 | 1.96 | 0.41 |  | 8.3
OAKLAND D 1115 | 12041115 | 2.64 |  |  |  | 2.64
OAKLAND D 1116 | 12041116 | 2.57 |  |  |  | 2.57
OAKLAND D 1117 | 12041117 | 0.5 |  |  |  | 0.5
OAKLAND D 1130 | 12041130 | 6.69 |  |  |  | 6.69
OAKLAND D 1131 | 12041131 | 7.76 |  |  |  | 7.76
OAKLAND D 1132 | 12041132 | 2.88 |  |  |  | 2.88
OAKLAND D 1133 | 12041133 | 3.02 |  |  |  | 3.02
OAKLAND D 1134 | 12041134 | 9.75 |  |  |  | 9.75
OAKLAND D 1202 | 12041202 | 0.24 |  |  |  | 0.24
OAKLAND I 0401 | 12080401 | 3.31 |  |  |  | 3.31
OAKLAND I 0402 | 12080402 | 5.13 |  |  |  | 5.13
OAKLAND J 0401 | 12090401 | 4.55 |  |  |  | 4.55
OAKLAND J 0403 | 12090403 | 6.35 |  |  |  | 6.35
OAKLAND J 0408 | 12090408 | 4.59 |  |  |  | 4.59
OAKLAND J 0409 | 12090409 | 3.02 |  |  |  | 3.02
OAKLAND J 1101 | 12091101 | 10.57 |  |  |  | 10.57
OAKLAND J 1102 | 12091102 | 18.5 |  | 6.02 |  | 12.48
OAKLAND J 1103 | 12091103 | 2.78 |  |  |  | 2.78
OAKLAND J 1104 | 12091104 | 6.89 |  |  |  | 6.89
OAKLAND J 1105 | 12091105 | 20.39 |  | 1.53 |  | 18.86
OAKLAND J 1106 | 12091106 | 18.16 |  | 1.89 |  | 16.27
OAKLAND J 1108 | 12091108 | 9.34 |  |  |  | 9.34
OAKLAND J 1109 | 12091109 | 0.04 |  |  |  | 0.04
OAKLAND J 1110 | 12091110 | 2.13 |  |  |  | 2.13
OAKLAND J 1111 | 12091111 | 4.71 |  |  |  | 4.71
OAKLAND J 1112 | 12091112 | 5.54 |  |  |  | 5.54
OAKLAND J 1114 | 12091114 | 0 |  |  |  | 0
OAKLAND J 1115 | 12091115 | 3.9 |  |  |  | 3.9
OAKLAND J 1116 | 12091116 | 23.63 |  | 0.48 |  | 23.15
OAKLAND J 1117 | 12091117 | 13.2 |  |  |  | 13.2
OAKLAND J 1118 | 12091118 | 14.03 |  | 0.31 |  | 13.72
OAKLAND K 1101 | 12101101 | 7.28 | 1.09 | 1.46 |  | 4.73
OAKLAND K 1102 | 12101102 | 14.91 | 14.91 |  |  | 0
OAKLAND K 1103 | 12101103 | 10.77 | 1.13 | 4.84 |  | 4.8
OAKLAND K 1104 | 12101104 | 14.96 | 9.58 | 5.38 |  | 0
OAKLAND L 1101 | 12111101 | 5.78 |  |  |  | 5.78
OAKLAND L 1102 | 12111102 | 1.3 |  |  |  | 1.3
OAKLAND L 1103 | 12111103 | 4.71 |  |  |  | 4.71
OAKLAND L 1105 | 12111105 | 2.44 |  |  |  | 2.44
OAKLAND L 1106 | 12111106 | 0.37 |  |  |  | 0.37
OAKLAND L 1107 | 12111107 | 1.47 |  |  |  | 1.47
OAKLAND L 1108 | 12111108 | 0 |  |  |  | 0
OAKLAND X 0401 | 12540401 | 5.55 |  |  |  | 5.55
OAKLAND X 0402 | 12540402 | 1.77 |  |  |  | 1.77
OAKLAND X 1101 | 12541101 | 5.29 |  | 0.5 |  | 4.79
OAKLAND X 1102 | 12541102 | 6.39 |  |  |  | 6.39
OAKLAND X 1103 | 12541103 | 7.78 |  |  |  | 7.78
OAKLAND X 1104 | 12541104 | 13.31 | 10.76 | 1.35 |  | 1.2
OAKLAND X 1105 | 12541105 | 19.51 |  | 2.52 |  | 16.99
OAKLAND X 1106 | 12541106 | 22.95 | 4.14 | 10.86 |  | 7.95
OAKLAND X 1107 | 12541107 | 12.91 |  |  |  | 12.91
OAKLAND X 1109 | 12541109 | 7.15 |  |  |  | 7.15
OAKLAND X 1110 | 12541110 | 0.43 |  |  |  | 0.43
OAKLAND X 1111 | 12541111 | 1.09 |  |  |  | 1.09
OAKLAND X 1112 | 12541112 | 3.94 |  |  |  | 3.94
OAKLAND X 1114 | 12541114 | 5.11 |  |  |  | 5.11
OAKLAND X 1115 | 12541115 | 12.68 |  |  |  | 12.68
OCEAN 0401 | 22580401 | 3.73 |  |  |  | 3.73
OCEAN 0402 | 22580402 | 3.02 |  |  |  | 3.02
OCEANO 1102 | 182601102 | 54.2 |  | 37.16 |  | 17.04
OCEANO 1103 | 182601103 | 11.39 |  | 1.11 |  | 10.28
OCEANO 1104 | 182601104 | 112.42 | 6.75 | 78.95 | 0.07 | 26.65
OCEANO 1105 | 182601105 | 22.2 |  | 0.04 |  | 22.16
OCEANO 1106 | 182601106 | 29.53 |  | 1.96 |  | 27.57
OCEANO 1108 | 182601108 | 11.18 |  |  |  | 11.18
OILFIELDS 1102 | 182391102 | 39.41 |  |  |  | 39.41
OILFIELDS 1103 | 182391103 | 144.52 |  | 116.72 |  | 27.8
OLD RIVER 1101 | 252821101 | 42.02 |  |  |  | 42.02
OLD RIVER 1102 | 252821102 | 49.42 |  |  |  | 49.42
OLD RIVER 1103 | 252821103 | 35.39 |  |  |  | 35.39
OLD RIVER 1104 | 252821104 | 58.52 |  |  |  | 58.52
OLD RIVER 1105 | 252821105 | 15.46 |  |  |  | 15.46
OLEMA 1101 | 42291101 | 122.8 | 15.4 | 55.11 |  | 52.29
OLETA 1101 | 163541101 | 117.44 | 4.66 | 85.25 | 0.51 | 27.02
OLETA 1102 | 163541102 | 98.84 |  | 56.23 |  | 42.61
OLIVEHURST 1101 | 152901101 | 21.89 |  |  |  | 21.89
OLIVEHURST 1102 | 152901102 | 6.05 |  |  |  | 6.05
OLIVEHURST 1103 | 152901103 | 47 |  |  |  | 47
OLIVEHURST 1104 | 152901104 | 11.43 |  |  |  | 11.43
OLIVEHURST 1105 | 152901105 | 54.02 |  |  |  | 54.02
OREGON TRAIL 1102 | 103521102 | 49.3 |  | 44.94 |  | 4.36
OREGON TRAIL 1103 | 103521103 | 107.62 |  | 104.68 |  | 2.94
OREGON TRAIL 1104 | 103521104 | 73.34 |  | 60.51 |  | 12.83
ORICK 1101 | 192261101 | 7.88 |  |  | 0.07 | 7.81
ORICK 1102 | 192261102 | 23.28 |  |  |  | 23.28
ORLAND B 1101 | 102701101 | 29.31 |  |  |  | 29.31
ORLAND B 1102 | 102701102 | 20.1 |  |  |  | 20.1
ORLAND B 1103 | 102701103 | 95.1 |  |  |  | 95.1
ORO FINO 1101 | 103031101 | 31.45 | 31.45 |  |  | 0
ORO FINO 1102 | 103031102 | 109.43 | 83.14 | 26.28 |  | 0.01
ORO LOMA 1102 | 255371102 | 0.95 |  |  |  | 0.95
ORO LOMA 1103 | 255371103 | 0.97 |  |  |  | 0.97
ORO LOMA 1106 | 255371106 | 73.03 |  |  |  | 73.03
ORO LOMA 1108 | 255371108 | 56.3 |  |  |  | 56.3
ORO LOMA 1115 | 255371115 | 73.24 |  |  |  | 73.24
ORO LOMA 1116 | 255371116 | 24.67 |  |  |  | 24.67
ORO LOMA 1117 | 255371117 | 49.05 |  |  |  | 49.05
ORO LOMA 1118 | 255371118 | 43.04 |  |  |  | 43.04
OROSI 1101 | 252841101 | 50.37 |  |  |  | 50.37
OROSI 1102 | 252841102 | 34.99 |  | 0.8 |  | 34.19
OROSI 1103 | 252841103 | 37.84 |  |  |  | 37.84
OROSI 1104 | 252841104 | 56.02 |  |  |  | 56.02
OROVILLE 0402 | 102520402 | 1.6 |  |  |  | 1.6
OROVILLE 0403 | 102520403 | 2.06 |  |  |  | 2.06
OROVILLE 1101 | 102521101 | 23.53 |  |  |  | 23.53
OROVILLE 1102 | 102521102 | 6.32 |  |  |  | 6.32
OROVILLE 1103 | 102521103 | 28.8 |  |  |  | 28.8
OROVILLE 1104 | 102521104 | 9.6 |  |  |  | 9.6
ORTIGA 1105 | 254311105 | 42.63 |  |  |  | 42.63
ORTIGA 1106 | 254311106 | 53.55 |  |  |  | 53.55
OTTER 1101 | 182941101 | 26.98 | 14.55 | 7.16 |  | 5.27
OTTER 1102 | 182941102 | 53.51 | 4.38 | 48.03 |  | 1.1
PACIFIC GROVE 0421 | 182440421 | 3.4 |  |  |  | 3.4
PACIFIC GROVE 0422 | 182440422 | 6.93 |  | 0.13 |  | 6.8
PACIFIC GROVE 0423 | 182440423 | 1.73 |  |  |  | 1.73
PACIFIC GROVE 0424 | 182440424 | 9.07 |  |  |  | 9.07
PACIFIC PIPE GRAPEVI 1101 | 255441101 | 0.02 |  |  |  | 0.02
PACIFICA 1101 | 22811101 | 9.25 | 0.07 | 0.74 |  | 8.44
PACIFICA 1102 | 22811102 | 20.18 | 1.34 | 1.37 |  | 17.47
PACIFICA 1103 | 22811103 | 14.16 | 0.19 | 0.77 |  | 13.2
PACIFICA 1104 | 22811104 | 7.28 |  | 0.7 |  | 6.58
PALMER 1101 | 183031101 | 62.72 |  | 39.49 |  | 23.23
PALO SECO 0401 | 13180401 | 4.75 |  | 4.73 |  | 0.02
PANAMA 2101 | 253422101 | 38.64 |  |  |  | 38.64
PANAMA 2102 | 253422102 | 32.87 |  |  |  | 32.87
PANOCHE 1101 | 253671101 | 32.16 |  |  |  | 32.16
PANOCHE 1102 | 253671102 | 42.75 |  |  |  | 42.75
PANOCHE 1103 | 253671103 | 122.6 |  | 44.24 |  | 78.36
PANORAMA 1101 | 103461101 | 38.59 |  | 12.44 |  | 26.15
PANORAMA 1102 | 103461102 | 85.39 |  | 30.01 | 0.21 | 55.17
PARADISE 1103 | 102831103 | 16.06 | 3.31 | 12.73 |  | 0.02
PARADISE 1104 | 102831104 | 12.17 | 8.41 | 1.2 |  | 2.56
PARADISE 1105 | 102831105 | 24.73 | 24.55 |  |  | 0.18
PARADISE 1106 | 102831106 | 3.6 | 3.04 |  |  | 0.56
PARKWAY 1101 | 42051101 | 7.14 |  |  |  | 7.14
PARKWAY 1102 | 42051102 | 0 |  |  |  | 0
PARKWAY 1103 | 42051103 | 6.72 |  |  |  | 6.72
PARLIER 1102 | 252291102 | 28.12 |  |  |  | 28.12
PARLIER 1103 | 252291103 | 40.96 |  |  |  | 40.96
PARLIER 1104 | 252291104 | 50.01 |  |  |  | 50.01
PARLIER 1105 | 252291105 | 21.45 |  |  |  | 21.45
PARSONS 0402 | 13660402 | 4.76 |  |  |  | 4.76
PASO ROBLES 1101 | 182611101 | 6.68 |  |  |  | 6.68
PASO ROBLES 1102 | 182611102 | 4.93 |  |  |  | 4.93
PASO ROBLES 1103 | 182611103 | 62.15 |  | 38.59 |  | 23.56
PASO ROBLES 1104 | 182611104 | 65.49 |  | 37.12 | 1.57 | 26.8
PASO ROBLES 1106 | 182611106 | 8.67 |  |  |  | 8.67
PASO ROBLES 1107 | 182611107 | 36.54 |  | 0.27 |  | 36.27
PASO ROBLES 1108 | 182611108 | 12.89 |  |  |  | 12.89
PAUL SWEET 2101 | 83252101 | 28.45 |  |  |  | 28.45
PAUL SWEET 2102 | 83252102 | 18.05 | 3.72 | 0.73 |  | 13.6
PAUL SWEET 2103 | 83252103 | 16.99 |  |  |  | 16.99
PAUL SWEET 2104 | 83252104 | 38.46 | 17.22 |  |  | 21.24
PAUL SWEET 2105 | 83252105 | 41.02 | 6.79 | 0.8 |  | 33.43
PAUL SWEET 2106 | 83252106 | 51.65 | 30.47 | 5.18 |  | 16
PAUL SWEET 2107 | 83252107 | 49.71 | 4.04 | 4.24 |  | 41.43
PAUL SWEET 2108 | 83252108 | 20.91 |  |  |  | 20.91
PAUL SWEET 2109 | 83252109 | 23.56 | 0.85 | 2.02 |  | 20.69
PEABODY 2102 | 63642102 | 7.56 |  |  |  | 7.56
PEABODY 2104 | 63642104 | 6.77 |  |  |  | 6.77
PEABODY 2105 | 63642105 | 60.17 |  |  |  | 60.17
PEABODY 2106 | 63642106 | 1.08 |  | 0.39 |  | 0.69
PEABODY 2107 | 63642107 | 193.05 |  |  |  | 193.05
PEABODY 2108 | 63642108 | 2.56 |  |  |  | 2.56
PEABODY 2109 | 63642109 | 3.63 |  |  |  | 3.63
PEABODY 2112 | 63642112 | 3.28 |  |  |  | 3.28
PEABODY 2113 | 63642113 | 8.1 |  | 1.36 |  | 6.74
PEACHTON 1101 | 103241101 | 68.61 |  |  |  | 68.61
PEACHTON 1102 | 103241102 | 67.71 |  |  |  | 67.71
PEACHTON 1103 | 103241103 | 61.41 |  |  |  | 61.41
PEASE 1101 | 153751101 | 6.71 |  |  |  | 6.71
PEASE 1102 | 153751102 | 4 |  |  |  | 4
PEASE 1103 | 153751103 | 97.85 |  |  |  | 97.85
PEASE 1104 | 153751104 | 62.61 |  |  |  | 62.61
PEASE 1105 | 153751105 | 8.29 |  |  |  | 8.29
PENNGROVE 1101 | 43471101 | 42.01 |  | 20.3 |  | 21.71
PENRYN 1103 | 152561103 | 80.48 |  | 67.37 |  | 13.11
PENRYN 1105 | 152561105 | 91.48 |  | 33.84 |  | 57.64
PENRYN 1106 | 152561106 | 25.96 |  | 0.81 |  | 25.15
PENRYN 1107 | 152561107 | 83.9 |  | 35.82 |  | 48.08
PENTLAND 1101 | 255311101 | 0.02 |  |  |  | 0.02
PEORIA 1701 | 163781701 | 112.29 |  | 100.99 |  | 11.3
PEORIA 1704 | 163781704 | 108.4 |  | 58.95 |  | 49.45
PEORIA 1705 | 163781705 | 42.4 |  | 34.17 | 0.2 | 8.03
PERRY 1101 | 183071101 | 83.57 | 7.19 | 58.23 | 3.12 | 15.03
PERRY 1104 | 183071104 | 62.36 |  | 43.92 | 0.14 | 18.3
PETALUMA A 0411 | 42120411 | 3.09 |  |  |  | 3.09
PETALUMA A 0413 | 42120413 | 2.41 |  |  |  | 2.41
PETALUMA C 1101 | 42631101 | 0.51 |  |  |  | 0.51
PETALUMA C 1102 | 42631102 | 4.23 |  |  |  | 4.23
PETALUMA C 1105 | 42631105 | 10.67 |  |  |  | 10.67
PETALUMA C 1106 | 42631106 | 9 |  |  |  | 9
PETALUMA C 1108 | 42631108 | 118.72 |  | 75.86 |  | 42.86
PETALUMA C 1109 | 42631109 | 66.66 |  | 48.77 |  | 17.89
PETALUMA C 1110 | 42631110 | 0.25 |  |  |  | 0.25
PETROL 1101 | 252541101 | 0.03 |  |  |  | 0.03
PHILO 1101 | 42601101 | 96.23 |  | 76.51 |  | 19.72
PHILO 1102 | 42601102 | 105.89 |  | 88.28 |  | 17.61
PIERCY 2109 | 83912109 | 19.91 |  |  |  | 19.91
PIERCY 2110 | 83912110 | 22.56 |  | 15.1 |  | 7.46
PIERCY 2111 | 83912111 | 0.91 |  |  |  | 0.91
PIKE CITY 1101 | 152201101 | 34.07 | 34.07 |  |  | 0
PIKE CITY 1102 | 152201102 | 9.52 | 9.52 |  |  | 0
PINE GROVE 1101 | 163751101 | 71.49 |  | 71.49 |  | 0
PINE GROVE 1102 | 163751102 | 172.5 | 82.02 | 90.48 |  | 0
PINECREST 0401 | 163160401 | 3.16 | 1.12 | 1.95 | 0.08 | 0.01
PINEDALE 2101 | 252852101 | 1.43 |  |  |  | 1.43
PINEDALE 2102 | 252852102 | 2.77 |  |  |  | 2.77
PINEDALE 2103 | 252852103 | 2 |  |  |  | 2
PINEDALE 2105 | 252852105 | 1.76 |  |  |  | 1.76
PINEDALE 2106 | 252852106 | 6.85 |  |  |  | 6.85
PINEDALE 2107 | 252852107 | 1.6 |  |  |  | 1.6
PINEDALE 2109 | 252852109 | 5.75 |  |  |  | 5.75
PINEDALE 2110 | 252852110 | 0.18 |  |  |  | 0.18
PINEDALE 2111 | 252852111 | 0.76 |  |  |  | 0.76
PIPER BANK 0401 | 18120401 | 1.57 |  |  |  | 1.57
PIT NO 1 1101 | 103721101 | 52.98 |  | 29.56 | 0.35 | 23.07
PIT NO 3 2101 | 103732101 | 48.22 |  | 47.44 |  | 0.78
PIT NO 5 1101 | 101321101 | 23.57 |  | 23.57 |  | 0
PIT NO 7 1101 | 103501101 | 2.79 |  | 2.79 |  | 0
PITTSBURG 0401 | 12160401 | 1.05 |  |  |  | 1.05
PITTSBURG 0402 | 12160402 | 1.9 |  |  |  | 1.9
PLACER 1101 | 152461101 | 7.71 |  | 1.26 |  | 6.45
PLACER 1102 | 152461102 | 2.08 |  | 1.87 |  | 0.21
PLACER 1103 | 152461103 | 29.66 |  | 12.19 | 0.14 | 17.33
PLACER 1104 | 152461104 | 13.46 |  | 0.52 | 0.02 | 12.92
PLACERVILLE 1109 | 153081109 | 11.03 |  | 10.73 | 0.01 | 0.29
PLACERVILLE 1110 | 153081110 | 34.46 | 0.76 | 32.68 | 1.02 | 0
PLACERVILLE 1111 | 153081111 | 16.75 |  | 14.78 | 0.59 | 1.38
PLACERVILLE 1112 | 153081112 | 30.01 |  | 27.72 | 1.12 | 1.17
PLACERVILLE 2106 | 153082106 | 272.23 | 178.11 | 93.85 |  | 0.27
PLAINFIELD 1101 | 63441101 | 33.64 |  |  |  | 33.64
PLAINFIELD 1105 | 63441105 | 61.68 |  |  |  | 61.68
PLAINFIELD 1106 | 63441106 | 22.06 |  |  |  | 22.06
PLEASANT GROVE 2103 | 152442103 | 1.88 |  |  |  | 1.88
PLEASANT GROVE 2104 | 152442104 | 2.42 |  |  |  | 2.42
PLEASANT GROVE 2107 | 152442107 | 0.02 |  |  |  | 0.02
PLEASANT GROVE 2108 | 152442108 | 2.1 |  |  |  | 2.1
PLEASANT GROVE 2110 | 152442110 | 34.81 |  |  |  | 34.81
PLUMAS 1101 | 153731101 | 32.26 |  |  |  | 32.26
PLUMAS 1102 | 153731102 | 5.67 |  |  |  | 5.67
PLUMAS 2106 | 153732106 | 31.98 |  |  |  | 31.98
PLUMAS 2107 | 153732107 | 38.62 |  |  |  | 38.62
PLYMOUTH 0401 | 22680401 | 4.73 |  |  |  | 4.73
POINT ARENA 1101 | 43381101 | 72.59 |  | 50.68 | 0.08 | 21.83
POINT MORETTI 1101 | 82931101 | 54.02 | 29.95 | 17.36 |  | 6.71
POINT PINOLE 1101 | 14261101 | 21.07 |  |  |  | 21.07
POINT PINOLE 1102 | 14261102 | 14.16 |  |  |  | 14.16
POINT PINOLE 1103 | 14261103 | 0.01 |  |  |  | 0.01
PORTOLA 0401 | 22610401 | 2.47 |  |  |  | 2.47
PORTOLA 0402 | 22610402 | 3.5 |  |  |  | 3.5
POSO MOUNTAIN 2101 | 253642101 | 59.12 |  | 48.64 |  | 10.48
POSO MOUNTAIN 2103 | 253642103 | 20.4 |  | 18.37 |  | 2.03
POSO MOUNTAIN 2104 | 253642104 | 12.3 |  | 7.77 |  | 4.53
POTRERO PP (A) 1101 | 22031101 | 7.25 |  |  |  | 7.25
POTRERO PP (A) 1102 | 22031102 | 0.47 |  |  |  | 0.47
POTRERO PP (A) 1103 | 22031103 | 1.82 |  |  |  | 1.82
POTRERO PP (A) 1104 | 22031104 | 0.3 |  |  |  | 0.3
POTRERO PP (A) 1105 | 22031105 | 1.51 |  |  |  | 1.51
POTRERO PP (A) 1107 | 22031107 | 0.98 |  |  |  | 0.98
POTRERO PP (A) 1108 | 22031108 | 3.35 |  |  |  | 3.35
POTRERO PP (A) 1109 | 22031109 | 5.3 |  |  |  | 5.3
POTRERO PP (A) 1110 | 22031110 | 5.83 |  |  |  | 5.83
POTRERO PP (A) 1112 | 22031112 | 0.98 |  |  |  | 0.98
POTRERO PP (A) 1113 | 22031113 | 1.37 |  |  |  | 1.37
POTRERO PP (A) 1114 | 22031114 | 0.07 |  |  |  | 0.07
POTRERO PP (A) 1115 | 22031115 | 0.09 |  |  |  | 0.09
POTRERO PP (A) 1116 | 22031116 | 2.23 |  |  |  | 2.23
POTRERO PP (A) 1117 | 22031117 | 4.95 |  |  |  | 4.95
POTRERO PP (A) 1118 | 22031118 | 4.33 |  |  |  | 4.33
POTRERO PP (A) 1119 | 22031119 | 3.26 |  |  |  | 3.26
POTRERO PP (A) 1121 | 22031121 | 0.17 |  |  |  | 0.17
POTTER VALLEY P H 1104 | 42281104 | 0.02 |  | 0.02 |  | 0
POTTER VALLEY P H 1105 | 42281105 | 90.01 | 3.98 | 46.65 |  | 39.38
PRUNEDALE 1107 | 182961107 | 47.11 |  |  | 0.24 | 46.87
PRUNEDALE 1110 | 182961110 | 79.98 |  | 0.24 |  | 79.74
PUEBLO 1102 | 43291102 | 8.99 |  |  | 0.09 | 8.9
PUEBLO 1103 | 43291103 | 7.98 |  |  |  | 7.98
PUEBLO 1104 | 43291104 | 50.82 |  | 28.3 | 0.05 | 22.47
PUEBLO 1105 | 43291105 | 69.25 |  | 20.16 | 0.05 | 49.04
PUEBLO 2101 | 43292101 | 11.64 |  |  |  | 11.64
PUEBLO 2102 | 43292102 | 98.24 | 21.17 | 0.74 | 0.07 | 76.26
PUEBLO 2103 | 43292103 | 76.8 | 36.86 | 8.12 |  | 31.82
PURISIMA 1101 | 182971101 | 57.74 |  | 18.19 | 0.13 | 39.42
PUTAH CREEK 1102 | 63681102 | 50.93 |  | 26.46 |  | 24.47
PUTAH CREEK 1103 | 63681103 | 36.62 |  | 3.83 | 0.61 | 32.18
PUTAH CREEK 1105 | 63681105 | 82.9 |  | 1.78 |  | 81.12
RACETRACK 1703 | 163761703 | 52.82 |  | 46.68 | 1.67 | 4.47
RACETRACK 1704 | 163761704 | 45.28 |  | 45.28 |  | 0
RADUM 1101 | 13151101 | 1.62 |  |  |  | 1.62
RADUM 1102 | 13151102 | 1.16 |  |  |  | 1.16
RADUM 1105 | 13151105 | 11.82 | 1.14 | 1.91 |  | 8.77
RAINBOW 1103 | 254441103 | 11.06 |  |  |  | 11.06
RAINBOW 1105 | 254441105 | 23.44 |  |  |  | 23.44
RAINBOW 1106 | 254441106 | 122.19 |  |  |  | 122.19
RALSTON 1101 | 24141101 | 14.53 | 0.41 | 8.59 |  | 5.53
RALSTON 1102 | 24141102 | 10.57 |  | 3.76 |  | 6.81
RANCHERS COTTON 1000 | 254801000 | 0.01 |  |  |  | 0.01
RANCHERS COTTON 1101 | 254801101 | 14.08 |  |  |  | 14.08
RANDOLPH 0401 | 22590401 | 0 |  |  |  | 0
RANDOLPH 0402 | 22590402 | 1.27 |  |  |  | 1.27
RANDOLPH 0403 | 22590403 | 3.15 |  |  |  | 3.15
RAWSON 1103 | 103531103 | 39.8 |  | 2.37 |  | 37.43
RED BLUFF 1101 | 103541101 | 74.7 |  | 47.84 |  | 26.86
RED BLUFF 1102 | 103541102 | 1.51 |  |  |  | 1.51
RED BLUFF 1103 | 103541103 | 38.14 |  | 16.84 |  | 21.3
RED BLUFF 1104 | 103541104 | 93.4 |  | 66.15 |  | 27.25
RED BLUFF 1105 | 103541105 | 37.81 |  | 13.64 |  | 24.17
REDBUD 1101 | 43191101 | 50.28 | 10.91 | 15.88 |  | 23.49
REDBUD 1102 | 43191102 | 58.52 | 0.65 | 27.86 |  | 30.01
REDWOOD CITY 0402 | 24160402 | 1.27 |  |  |  | 1.27
REDWOOD CITY 0403 | 24160403 | 2.13 |  |  |  | 2.13
REDWOOD CITY 0404 | 24160404 | 1.63 |  |  |  | 1.63
REDWOOD CITY 0405 | 24160405 | 3.5 |  |  |  | 3.5
REDWOOD CITY 0406 | 24160406 | 6.62 |  |  |  | 6.62
REDWOOD CITY 0408 | 24160408 | 5.52 |  |  |  | 5.52
REDWOOD CITY 0409 | 24160409 | 4.95 |  |  |  | 4.95
REDWOOD CITY 0410 | 24160410 | 5.45 |  |  |  | 5.45
REDWOOD CITY 1101 | 24161101 | 1.95 |  |  |  | 1.95
REDWOOD CITY 1102 | 24161102 | 1.63 |  |  |  | 1.63
REDWOOD CITY 1103 | 24161103 | 1.6 |  |  |  | 1.6
REDWOOD CITY 1104 | 24161104 | 1 |  |  |  | 1
REDWOOD CITY 1105 | 24161105 | 7.31 |  |  |  | 7.31
REEDLEY 1101 | 252341101 | 26.5 |  |  |  | 26.5
REEDLEY 1104 | 252341104 | 82.6 |  | 1.69 |  | 80.91
REEDLEY 1106 | 252341106 | 123.83 |  |  |  | 123.83
REEDLEY 1110 | 252341110 | 42.46 |  |  |  | 42.46
REEDLEY 1112 | 252341112 | 90.21 |  | 0.78 |  | 89.43
RENFRO 2101 | 254572101 | 31.21 |  |  |  | 31.21
RENFRO 2102 | 254572102 | 5.16 |  |  |  | 5.16
RENFRO 2103 | 254572103 | 26.43 |  |  |  | 26.43
RENFRO 2105 | 254572105 | 10.45 |  |  |  | 10.45
RENFRO 2107 | 254572107 | 7.88 |  |  |  | 7.88
RESEARCH 2101 | 14692101 | 7.71 |  |  |  | 7.71
RESEARCH 2102 | 14692102 | 20.84 | 2.18 |  |  | 18.66
RESEARCH 2103 | 14692103 | 0 |  |  |  | 0
RESERVATION ROAD 1101 | 182731101 | 36.97 |  | 29.09 |  | 7.88
RESERVATION ROAD 1102 | 182731102 | 58.43 |  | 19.67 |  | 38.76
RESERVE OIL 1101 | 254181101 | 2.19 |  |  |  | 2.19
RICE 1101 | 62831101 | 53.61 |  |  |  | 53.61
RICE 1102 | 62831102 | 62.32 |  |  |  | 62.32
RICE 1103 | 62831103 | 78.33 |  |  |  | 78.33
RICE 1104 | 62831104 | 33.18 |  |  | 0.24 | 32.94
RICHMOND R 1118 | 13471118 | 2.81 |  |  |  | 2.81
RICHMOND R 1119 | 13471119 | 3.65 |  |  |  | 3.65
RICHMOND R 1120 | 13471120 | 2.98 |  |  |  | 2.98
RICHMOND R 1121 | 13471121 | 4.47 |  |  |  | 4.47
RICHMOND R 1122 | 13471122 | 3.89 |  |  |  | 3.89
RICHMOND R 1123 | 13471123 | 1.29 |  |  |  | 1.29
RICHMOND R 1124 | 13471124 | 6.8 |  |  |  | 6.8
RICHMOND R 1125 | 13471125 | 10.64 |  |  |  | 10.64
RICHMOND R 1126 | 13471126 | 13.13 |  |  |  | 13.13
RICHMOND R 1127 | 13471127 | 20.35 |  |  |  | 20.35
RICHMOND R 1128 | 13471128 | 7.57 |  |  |  | 7.57
RICHMOND R 1129 | 13471129 | 13.51 |  |  |  | 13.51
RICHMOND R 1130 | 13471130 | 16.18 |  |  |  | 16.18
RIDGE 0401 | 12840401 | 2.67 |  | 2.67 |  | 0
RIDGE 0402 | 12840402 | 2.41 |  | 1.75 |  | 0.66
RINCON 1101 | 43321101 | 37.96 | 16.28 | 5.8 |  | 15.88
RINCON 1102 | 43321102 | 17.79 | 0.01 | 2.5 |  | 15.28
RINCON 1103 | 43321103 | 47.47 | 40.38 | 4.19 |  | 2.9
RINCON 1104 | 43321104 | 8.92 | 1.92 |  |  | 7
RIO BRAVO 1101 | 252861101 | 21 |  |  |  | 21
RIO BRAVO 1102 | 252861102 | 36.91 |  |  |  | 36.91
RIO BRAVO 1103 | 252861103 | 26.92 |  |  |  | 26.92
RIO BRAVO 1104 | 252861104 | 4.15 |  |  |  | 4.15
RIO BRAVO 1106 | 252861106 | 63.16 |  |  |  | 63.16
RIO DELL 1101 | 192251101 | 27.62 |  | 0.02 |  | 27.6
RIO DELL 1102 | 192251102 | 39.06 |  | 34.59 |  | 4.47
RIO DELL 1104 | 192251104 | 34.27 |  | 14.54 | 0.76 | 18.97
RIPON 1701 | 163801701 | 64.78 |  |  |  | 64.78
RIPON 1702 | 163801702 | 24.32 |  |  |  | 24.32
RIPON 1703 | 163801703 | 83.7 |  |  |  | 83.7
RIPON 1704 | 163801704 | 9.69 |  |  |  | 9.69
RISING RIVER 1101 | 103551101 | 68.87 |  | 53.7 | 0.32 | 14.85
RIVERBANK 1711 | 163191711 | 35.4 |  |  |  | 35.4
RIVERBANK 1712 | 163191712 | 54.54 |  |  |  | 54.54
RIVERBANK 1713 | 163191713 | 54.12 |  |  |  | 54.12
RIVERBANK 1714 | 163191714 | 34.25 |  |  |  | 34.25
RIVERBANK 1715 | 163191715 | 92.07 |  |  |  | 92.07
RIVERBANK 1716 | 163191716 | 26.83 |  |  |  | 26.83
ROB ROY 2104 | 83692104 | 159.69 | 39.26 | 61.95 | 0.07 | 58.41
ROB ROY 2105 | 83692105 | 66.3 | 26.88 | 11.36 |  | 28.06
ROCKLIN 1101 | 152061101 | 4.72 |  |  |  | 4.72
ROCKLIN 1102 | 152061102 | 18.67 |  |  |  | 18.67
ROCKLIN 1103 | 152061103 | 5.12 |  |  |  | 5.12
ROCKLIN 1104 | 152061104 | 3.31 |  |  |  | 3.31
ROSEDALE 1101 | 254761101 | 12.21 |  |  |  | 12.21
ROSEDALE 2102 | 254762102 | 3.72 |  |  |  | 3.72
ROSSMOOR 1101 | 14161101 | 30.65 | 2.13 | 10.78 | 0.03 | 17.71
ROSSMOOR 1102 | 14161102 | 1.45 | 0.45 |  |  | 1
ROSSMOOR 1103 | 14161103 | 2.58 |  |  |  | 2.58
ROSSMOOR 1104 | 14161104 | 19.24 |  | 0.3 |  | 18.94
ROSSMOOR 1105 | 14161105 | 4.29 |  |  |  | 4.29
ROSSMOOR 1106 | 14161106 | 16.2 | 0.58 | 2.84 | 0.06 | 12.72
ROSSMOOR 1107 | 14161107 | 10.58 | 0.03 |  |  | 10.55
ROSSMOOR 1108 | 14161108 | 13.12 | 1.97 | 3.14 | 0.05 | 7.96
ROSSMOOR 1109 | 14161109 | 14.03 | 6.39 | 1.14 |  | 6.5
ROUGH AND READY ISLA 1102 | 163081102 | 54.27 |  |  |  | 54.27
ROUND MOUNTAIN 1101 | 109001101 | 0.02 |  | 0.02 |  | 0
RUSS RANCH 1101 | 192471101 | 0.22 |  |  |  | 0.22
RUSSELL (SMUD) 2101 | 63142101 | 5.13 |  |  |  | 5.13
RUSSELL 0401 | 13310401 | 3.41 |  |  |  | 3.41
RUSSELL 0402 | 13310402 | 3.36 |  |  |  | 3.36
SALINAS 1101 | 182011101 | 8.33 |  |  |  | 8.33
SALINAS 1102 | 182011102 | 21.28 |  |  |  | 21.28
SALINAS 1103 | 182011103 | 10.83 |  |  |  | 10.83
SALINAS 1104 | 182011104 | 32.47 |  |  |  | 32.47
SALINAS 1105 | 182011105 | 10.9 |  |  |  | 10.9
SALINAS 1106 | 182011106 | 17.76 |  |  |  | 17.76
SALINAS 1107 | 182011107 | 7.21 |  |  |  | 7.21
SALINAS 1108 | 182011108 | 2.75 |  |  |  | 2.75
SALINAS 1109 | 182011109 | 20.45 |  |  |  | 20.45
SALMON CREEK 1101 | 43161101 | 47.37 | 7.21 | 15 |  | 25.16
SALT SPRINGS 2101 | 163692101 | 21.99 |  | 17.08 | 3.8 | 1.11
SALT SPRINGS 2102 | 163692102 | 51.83 | 42.09 | 9.67 | 0.07 | 0
SAN ARDO 1101 | 182191101 | 56.42 |  | 2.67 |  | 53.75
SAN ARDO 1102 | 182191102 | 124.22 |  |  |  | 124.22
SAN BENITO 2101 | 182742101 | 48.57 |  | 4.28 | 0.99 | 43.3
SAN BENITO 2102 | 182742102 | 12.96 |  |  |  | 12.96
SAN BENITO 2103 | 182742103 | 0.59 |  |  |  | 0.59
SAN BENITO 2104 | 182742104 | 51.52 |  | 26.65 |  | 24.87
SAN BERNARD 1101 | 253191101 | 36.51 |  | 1.13 |  | 35.38
SAN BERNARD 1102 | 253191102 | 17.24 |  |  |  | 17.24
SAN BERNARD 1104 | 253191104 | 9.24 |  |  |  | 9.24
SAN BRUNO 0401 | 22700401 | 3.7 |  |  |  | 3.7
SAN BRUNO 0402 | 22700402 | 3.14 |  |  |  | 3.14
SAN BRUNO 0403 | 22700403 | 5.13 |  |  |  | 5.13
SAN CARLOS 0401 | 24180401 | 1.66 |  |  |  | 1.66
SAN CARLOS 0402 | 24180402 | 4.33 |  |  |  | 4.33
SAN CARLOS 0403 | 24180403 | 6.95 |  |  |  | 6.95
SAN CARLOS 0404 | 24180404 | 8.83 |  |  |  | 8.83
SAN CARLOS 0405 | 24180405 | 8.18 |  |  |  | 8.18
SAN CARLOS 0406 | 24180406 | 6.6 |  |  |  | 6.6
SAN CARLOS 1101 | 24181101 | 1.46 |  |  |  | 1.46
SAN CARLOS 1102 | 24181102 | 0.46 |  |  |  | 0.46
SAN CARLOS 1103 | 24181103 | 16.61 |  | 3.83 |  | 12.78
SAN CARLOS 1104 | 24181104 | 22.16 |  | 10.7 |  | 11.46
SAN JOAQUIN #2 1103 | 252521103 | 80.16 | 10.34 | 69.82 |  | 0
SAN JOAQUIN #3 1101 | 252531101 | 24.35 | 22.77 | 1.57 |  | 0.01
SAN JOAQUIN #3 1102 | 252531102 | 11.41 | 5.46 | 5.95 |  | 0
SAN JOAQUIN #3 1103 | 252531103 | 56.29 | 30.63 | 25.65 |  | 0.01
SAN JOAQUIN 1106 | 252361106 | 34.24 |  |  |  | 34.24
SAN JOAQUIN 1108 | 252361108 | 41.22 |  |  |  | 41.22
SAN JOAQUIN 1112 | 252361112 | 42.7 |  |  |  | 42.7
SAN JOSE A 0403 | 82250403 | 3.99 |  |  |  | 3.99
SAN JOSE A 0404 | 82250404 | 1.71 |  |  |  | 1.71
SAN JOSE A 0405 | 82250405 | 1.9 |  |  |  | 1.9
SAN JOSE A 0407 | 82250407 | 1.84 |  |  |  | 1.84
SAN JOSE A 0408 | 82250408 | 2.41 |  |  |  | 2.41
SAN JOSE A 0410 | 82250410 | 4.58 |  |  |  | 4.58
SAN JOSE A 1109 | 82251109 | 0.59 |  |  |  | 0.59
SAN JOSE A 1110 | 82251110 | 9.17 |  |  |  | 9.17
SAN JOSE A 1111 | 82251111 | 0.28 |  |  |  | 0.28
SAN JOSE A 1112 | 82251112 | 10.75 |  |  |  | 10.75
SAN JOSE B 1101 | 82261101 | 0.16 |  |  |  | 0.16
SAN JOSE B 1102 | 82261102 | 0.28 |  |  |  | 0.28
SAN JOSE B 1104 | 82261104 | 0.48 |  |  |  | 0.48
SAN JOSE B 1105 | 82261105 | 13.2 |  |  |  | 13.2
SAN JOSE B 1106 | 82261106 | 0.56 |  |  |  | 0.56
SAN JOSE B 1107 | 82261107 | 9.2 |  |  |  | 9.2
SAN JOSE B 1108 | 82261108 | 8.12 |  |  |  | 8.12
SAN JOSE B 1109 | 82261109 | 0.39 |  |  |  | 0.39
SAN JOSE B 1110 | 82261110 | 13.35 |  |  |  | 13.35
SAN JOSE B 1111 | 82261111 | 0.08 |  |  |  | 0.08
SAN JOSE B 1112 | 82261112 | 8.26 |  |  |  | 8.26
SAN JOSE B 1113 | 82261113 | 0.1 |  |  |  | 0.1
SAN JOSE B 1114 | 82261114 | 0.69 |  |  |  | 0.69
SAN JOSE B 1115 | 82261115 | 0.78 |  |  |  | 0.78
SAN JOSE B 1116 | 82261116 | 4.36 |  |  |  | 4.36
SAN JOSE B 1117 | 82261117 | 3.65 |  |  |  | 3.65
SAN JUSTO 1101 | 183181101 | 55.95 |  | 37.23 | 0.24 | 18.48
SAN LEANDRO U 1101 | 13111101 | 3.91 |  |  |  | 3.91
SAN LEANDRO U 1102 | 13111102 | 12.46 |  |  |  | 12.46
SAN LEANDRO U 1103 | 13111103 | 1.94 |  |  |  | 1.94
SAN LEANDRO U 1104 | 13111104 | 6.21 |  |  |  | 6.21
SAN LEANDRO U 1105 | 13111105 | 7.75 |  |  |  | 7.75
SAN LEANDRO U 1106 | 13111106 | 12.17 |  |  |  | 12.17
SAN LEANDRO U 1107 | 13111107 | 15.1 |  |  |  | 15.1
SAN LEANDRO U 1108 | 13111108 | 8.64 |  |  |  | 8.64
SAN LEANDRO U 1109 | 13111109 | 19.92 | 0.86 | 11.65 |  | 7.41
SAN LEANDRO U 1110 | 13111110 | 19.05 |  |  |  | 19.05
SAN LEANDRO U 1111 | 13111111 | 2.31 |  |  |  | 2.31
SAN LEANDRO U 1112 | 13111112 | 4.07 |  |  |  | 4.07
SAN LEANDRO U 1113 | 13111113 | 9.83 |  |  |  | 9.83
SAN LEANDRO U 1114 | 13111114 | 29.17 |  | 9.54 |  | 19.63
SAN LEANDRO U 1115 | 13111115 | 1.47 |  |  |  | 1.47
SAN LEANDRO U 1116 | 13111116 | 3.82 |  |  |  | 3.82
SAN LEANDRO U 1151 | 13111151 | 9.61 |  |  |  | 9.61
SAN LUIS OBISPO 1101 | 182631101 | 39.55 | 10.18 | 15.21 |  | 14.16
SAN LUIS OBISPO 1102 | 182631102 | 12.37 |  | 0.63 | 0.04 | 11.7
SAN LUIS OBISPO 1103 | 182631103 | 39 |  | 20.24 | 0.63 | 18.13
SAN LUIS OBISPO 1104 | 182631104 | 84.53 | 21.35 | 37.29 | 0.88 | 25.01
SAN LUIS OBISPO 1105 | 182631105 | 15.89 |  | 1.42 |  | 14.47
SAN LUIS OBISPO 1107 | 182631107 | 49.38 | 24.63 | 21.82 |  | 2.93
SAN LUIS OBISPO 1108 | 182631108 | 10.05 |  | 2.43 |  | 7.62
SAN MATEO 0404 | 24190404 | 5.12 |  |  |  | 5.12
SAN MATEO 0407 | 24190407 | 3.63 |  |  |  | 3.63
SAN MATEO 0408 | 24190408 | 5.68 |  |  |  | 5.68
SAN MATEO 0409 | 24190409 | 3.15 |  |  |  | 3.15
SAN MATEO 0410 | 24190410 | 5.2 |  |  |  | 5.2
SAN MATEO 2101 | 24192101 | 7.26 |  |  |  | 7.26
SAN MATEO 2102 | 24192102 | 13.09 |  |  |  | 13.09
SAN MIGUEL 1104 | 182661104 | 0.28 |  |  |  | 0.28
SAN MIGUEL 1105 | 182661105 | 20.09 |  | 1.39 |  | 18.7
SAN MIGUEL 1106 | 182661106 | 74.54 |  | 37.91 |  | 36.63
SAN MIGUEL 1107 | 182661107 | 149.96 |  | 23.74 | 0.02 | 126.2
SAN PABLO 1105 | 14371105 | 18.68 |  |  |  | 18.68
SAN PABLO 1106 | 14371106 | 0.65 |  |  |  | 0.65
SAN RAFAEL 1101 | 42011101 | 27.53 | 12.25 | 1.17 |  | 14.11
SAN RAFAEL 1102 | 42011102 | 4.89 |  |  |  | 4.89
SAN RAFAEL 1103 | 42011103 | 5.89 |  |  |  | 5.89
SAN RAFAEL 1104 | 42011104 | 25.24 | 2.1 | 9.76 |  | 13.38
SAN RAFAEL 1105 | 42011105 | 23.14 |  | 1.67 |  | 21.47
SAN RAFAEL 1106 | 42011106 | 18.61 |  | 2.79 |  | 15.82
SAN RAFAEL 1107 | 42011107 | 29.16 | 18.24 | 2.98 |  | 7.94
SAN RAFAEL 1108 | 42011108 | 28.98 | 26.21 | 0.44 |  | 2.33
SAN RAFAEL 1109 | 42011109 | 29.05 |  | 9.82 |  | 19.23
SAN RAFAEL 1110 | 42011110 | 13.17 | 7.94 |  |  | 5.23
SAN RAMON 2101 | 14232101 | 1.08 |  | 0.61 |  | 0.47
SAN RAMON 2102 | 14232102 | 2.32 |  | 1.51 |  | 0.81
SAN RAMON 2103 | 14232103 | 2.78 |  |  |  | 2.78
SAN RAMON 2104 | 14232104 | 20.69 |  |  |  | 20.69
SAN RAMON 2105 | 14232105 | 3.5 |  |  |  | 3.5
SAN RAMON 2106 | 14232106 | 5.13 | 0.45 |  |  | 4.68
SAN RAMON 2107 | 14232107 | 27.46 | 14.28 | 0.17 |  | 13.01
SAN RAMON 2108 | 14232108 | 17.31 | 16.38 |  |  | 0.93
SAN RAMON 2110 | 14232110 | 0.1 |  |  |  | 0.1
SAN RAMON 2111 | 14232111 | 9.44 |  |  |  | 9.44
SAN RAMON 2114 | 14232114 | 1.61 |  |  |  | 1.61
SAN RAMON 2116 | 14232116 | 0 |  |  |  | 0
SAN RAMON 2117 | 14232117 | 1.67 |  | 0.56 |  | 1.11
SAN RAMON 2118 | 14232118 | 0.82 |  |  |  | 0.82
SAN RAMON 2119 | 14232119 | 3.03 |  | 0.59 |  | 2.44
SAND CREEK 1103 | 254601103 | 149.87 |  | 148.16 |  | 1.71
SANGER 1104 | 252351104 | 9.51 |  |  |  | 9.51
SANGER 1106 | 252351106 | 8.58 |  |  |  | 8.58
SANGER 1108 | 252351108 | 81.58 |  |  |  | 81.58
SANGER 1110 | 252351110 | 33.65 |  |  |  | 33.65
SANGER 1112 | 252351112 | 11.38 |  |  |  | 11.38
SANGER 1114 | 252351114 | 62.87 |  |  |  | 62.87
SANGER 1116 | 252351116 | 8.05 |  |  |  | 8.05
SANGER 1118 | 252351118 | 29.38 |  |  |  | 29.38
SANTA MARIA 1105 | 182671105 | 29.02 |  |  |  | 29.02
SANTA MARIA 1106 | 182671106 | 19.05 |  |  |  | 19.05
SANTA MARIA 1107 | 182671107 | 7.47 |  |  |  | 7.47
SANTA MARIA 1108 | 182671108 | 98.56 | 43.74 | 28.4 |  | 26.42
SANTA MARIA 1109 | 182671109 | 21.04 |  |  |  | 21.04
SANTA MARIA 1110 | 182671110 | 52.8 |  |  |  | 52.8
SANTA MARIA 1111 | 182671111 | 9.51 |  |  |  | 9.51
SANTA MARIA 1112 | 182671112 | 10.52 |  |  |  | 10.52
SANTA NELLA 1101 | 254051101 | 39.36 |  |  |  | 39.36
SANTA NELLA 1102 | 254051102 | 0 |  |  |  | 0
SANTA NELLA 1104 | 254051104 | 52.53 |  |  |  | 52.53
SANTA RITA 1102 | 253541102 | 101.87 |  |  |  | 101.87
SANTA RITA 1105 | 253541105 | 61.38 |  |  |  | 61.38
SANTA ROSA A 1101 | 42151101 | 4.6 |  |  |  | 4.6
SANTA ROSA A 1102 | 42151102 | 12.11 |  |  |  | 12.11
SANTA ROSA A 1103 | 42151103 | 10.35 |  |  |  | 10.35
SANTA ROSA A 1104 | 42151104 | 56.36 | 37.63 | 5.25 |  | 13.48
SANTA ROSA A 1105 | 42151105 | 9.43 |  |  |  | 9.43
SANTA ROSA A 1106 | 42151106 | 10.04 |  |  |  | 10.04
SANTA ROSA A 1107 | 42151107 | 18.08 | 2.89 |  |  | 15.19
SANTA ROSA A 1108 | 42151108 | 6.64 |  | 0.14 |  | 6.5
SANTA ROSA A 1109 | 42151109 | 5.93 |  |  |  | 5.93
SANTA ROSA A 1110 | 42151110 | 16.58 |  |  |  | 16.58
SANTA ROSA A 1111 | 42151111 | 26.55 |  | 5.68 |  | 20.87
SANTA ROSA A 1112 | 42151112 | 12.77 |  |  |  | 12.77
SANTA TERESA 2101 | 82962101 | 0.3 |  |  |  | 0.3
SANTA YNEZ 1101 | 182721101 | 58.89 | 14.47 | 14.06 |  | 30.36
SANTA YNEZ 1102 | 182721102 | 34.01 | 4.99 | 9.02 |  | 20
SANTA YNEZ 1104 | 182721104 | 86.32 | 6.24 | 37.51 |  | 42.57
SARANAP 0401 | 13560401 | 2.47 |  |  |  | 2.47
SARATOGA 1103 | 83371103 | 10.5 |  | 4.61 |  | 5.89
SARATOGA 1104 | 83371104 | 18.16 |  | 2.92 |  | 15.24
SARATOGA 1105 | 83371105 | 16.77 |  | 10.15 |  | 6.62
SARATOGA 1106 | 83371106 | 26.93 | 1.38 | 14.14 |  | 11.41
SARATOGA 1107 | 83371107 | 45.71 | 20.56 | 14.02 |  | 11.13
SARATOGA 1108 | 83371108 | 18.8 |  |  |  | 18.8
SARATOGA 1109 | 83371109 | 25.44 |  |  | 0.01 | 25.43
SARATOGA 1110 | 83371110 | 20.22 |  |  |  | 20.22
SARATOGA 1111 | 83371111 | 23.98 |  |  |  | 23.98
SARATOGA 1112 | 83371112 | 8.49 |  |  |  | 8.49
SARATOGA 1113 | 83371113 | 25.83 |  |  |  | 25.83
SARATOGA 1114 | 83371114 | 21.29 |  |  |  | 21.29
SARATOGA 1115 | 83371115 | 13.86 |  | 2.83 |  | 11.03
SAUSALITO 0401 | 42490401 | 0.01 |  |  |  | 0.01
SAUSALITO 0402 | 42490402 | 1.16 |  |  |  | 1.16
SAUSALITO 1101 | 42491101 | 7.87 |  | 1.25 |  | 6.62
SAUSALITO 1102 | 42491102 | 20.66 |  | 9.13 |  | 11.53
SAUSALITO 1103 | 42491103 | 0.01 |  |  |  | 0.01
SCE MCFARLAND 1101 | 258111101 | 0.5 |  |  |  | 0.5
SCE REFUGIO 1701 | 188071701 | 0.08 | 0.08 |  |  | 0
SCE TEHACHAPI 1101 | 258131101 | 1.44 |  | 1.44 |  | 0
SCE TEJON TIE 1101 | 258191101 | 0.06 |  | 0.06 |  | 0
SCE VEGAS 1701 | 188881701 | 0.17 | 0.17 |  |  | 0
SCHINDLER 1104 | 252891104 | 0.01 |  |  |  | 0.01
SCHINDLER 1105 | 252891105 | 41.89 |  |  |  | 41.89
SCHINDLER 1107 | 252891107 | 1.43 |  |  |  | 1.43
SCHINDLER 1108 | 252891108 | 2.25 |  |  |  | 2.25
SCHINDLER 1109 | 252891109 | 1.7 |  |  |  | 1.7
SCHINDLER 1110 | 252891110 | 49.17 |  |  |  | 49.17
SCHINDLER 1111 | 252891111 | 41.64 |  |  |  | 41.64
SCHINDLER 1112 | 252891112 | 48.85 |  |  |  | 48.85
SCHINDLER 1114 | 252891114 | 59.01 |  |  |  | 59.01
SCHINDLER 1116 | 252891116 | 25.73 |  |  |  | 25.73
SEACLIFF 0401 | 83500401 | 9.19 | 6.53 | 1.24 |  | 1.42
SEACLIFF 0402 | 83500402 | 1.57 | 0.07 | 0.01 |  | 1.49
SEMITROPIC 1104 | 252901104 | 27.81 |  |  |  | 27.81
SEMITROPIC 1106 | 252901106 | 27.39 |  |  |  | 27.39
SEMITROPIC 1108 | 252901108 | 2.28 |  |  |  | 2.28
SEMITROPIC 1110 | 252901110 | 37.19 |  |  |  | 37.19
SEMITROPIC 1112 | 252901112 | 26.75 |  |  |  | 26.75
SERRAMONTE 1103 | 22861103 | 13.2 |  |  |  | 13.2
SERRAMONTE 1104 | 22861104 | 12.72 |  |  |  | 12.72
SF E 0401 | 22070401 | 3.53 |  |  |  | 3.53
SF E 0405 | 22070405 | 2.2 |  |  |  | 2.2
SF E 0406 | 22070406 | 1.49 |  |  |  | 1.49
SF E 0407 | 22070407 | 0.94 |  |  |  | 0.94
SF E 0408 | 22070408 | 2.7 |  |  |  | 2.7
SF E 0409 | 22070409 | 1.82 |  |  |  | 1.82
SF E 0410 | 22070410 | 1.88 |  |  |  | 1.88
SF E 1101 | 22071101 | 1.19 |  |  |  | 1.19
SF E 1103 | 22071103 | 3.56 |  |  |  | 3.56
SF E 1105 | 22071105 | 2.43 |  |  |  | 2.43
SF E 1107 | 22071107 | 3.81 |  |  |  | 3.81
SF G 0401 | 22090401 | 0.67 |  |  |  | 0.67
SF G 0402 | 22090402 | 1.57 |  |  |  | 1.57
SF G 0403 | 22090403 | 0.72 |  |  |  | 0.72
SF G 0404 | 22090404 | 0.98 |  |  |  | 0.98
SF G 0405 | 22090405 | 1.47 |  |  |  | 1.47
SF G 0406 | 22090406 | 1.28 |  |  |  | 1.28
SF G 0407 | 22090407 | 1.36 |  |  |  | 1.36
SF G 0408 | 22090408 | 1.21 |  |  |  | 1.21
SF G 0409 | 22090409 | 1.06 |  |  |  | 1.06
SF G 0410 | 22090410 | 0.58 |  |  |  | 0.58
SF G 0412 | 22090412 | 1.1 |  |  |  | 1.1
SF G 0413 | 22090413 | 1.01 |  |  |  | 1.01
SF G 0414 | 22090414 | 0.86 |  |  |  | 0.86
SF G 1101 | 22091101 | 1.07 |  |  |  | 1.07
SF G 1102 | 22091102 | 0.57 |  |  |  | 0.57
SF H 0401 | 22100401 | 4.72 |  |  |  | 4.72
SF H 0402 | 22100402 | 4.1 |  |  |  | 4.1
SF H 0403 | 22100403 | 1.08 |  |  |  | 1.08
SF H 0404 | 22100404 | 2.75 |  |  |  | 2.75
SF H 0405 | 22100405 | 2.46 |  |  |  | 2.46
SF H 1101 | 22101101 | 6.46 |  |  |  | 6.46
SF H 1102 | 22101102 | 7 |  |  |  | 7
SF H 1103 | 22101103 | 8.7 |  |  |  | 8.7
SF H 1104 | 22101104 | 0.65 |  |  |  | 0.65
SF H 1105 | 22101105 | 15.03 |  |  |  | 15.03
SF H 1106 | 22101106 | 7.98 |  |  |  | 7.98
SF H 1107 | 22101107 | 3.81 |  |  |  | 3.81
SF H 1108 | 22101108 | 13.52 |  |  |  | 13.52
SF H 1109 | 22101109 | 4.82 |  |  |  | 4.82
SF H 1110 | 22101110 | 13.25 |  |  |  | 13.25
SF H 1111 | 22101111 | 4.23 |  |  |  | 4.23
SF J 0402 | 22220402 | 0.89 |  |  |  | 0.89
SF J 0404 | 22220404 | 0.52 |  |  |  | 0.52
SF J 0406 | 22220406 | 0.52 |  |  |  | 0.52
SF J 0407 | 22220407 | 0 |  |  |  | 0
SF J 0409 | 22220409 | 0.15 |  |  |  | 0.15
SF J 1108 | 22221108 | 0 |  |  |  | 0
SF K 0401 | 22130401 | 2.49 |  |  |  | 2.49
SF K 0402 | 22130402 | 3.33 |  |  |  | 3.33
SF K 0403 | 22130403 | 2.52 |  |  |  | 2.52
SF K 0404 | 22130404 | 0.98 |  |  |  | 0.98
SF K 0405 | 22130405 | 2.83 |  |  |  | 2.83
SF K 0406 | 22130406 | 1.72 |  |  |  | 1.72
SF K 0407 | 22130407 | 1.33 |  |  |  | 1.33
SF K 0408 | 22130408 | 1.36 |  |  |  | 1.36
SF K 0409 | 22130409 | 2.4 |  |  |  | 2.4
SF K 0410 | 22130410 | 2.18 |  |  |  | 2.18
SF K 0411 | 22130411 | 2.28 |  |  |  | 2.28
SF K 1101 | 22131101 | 6.8 |  |  |  | 6.8
SF L 0401 | 22260401 | 2.54 |  |  |  | 2.54
SF L 0402 | 22260402 | 0 |  |  |  | 0
SF L 0403 | 22260403 | 0.27 |  |  |  | 0.27
SF L 0404 | 22260404 | 0.81 |  |  |  | 0.81
SF L 0405 | 22260405 | 2.34 |  |  |  | 2.34
SF L 0406 | 22260406 | 2.14 |  |  |  | 2.14
SF L 0407 | 22260407 | 0.55 |  |  |  | 0.55
SF L 0408 | 22260408 | 2.41 |  |  |  | 2.41
SF L 0409 | 22260409 | 0.15 |  |  |  | 0.15
SF L 1101 | 22261101 | 2.39 |  |  |  | 2.39
SF L 1102 | 22261102 | 8.1 |  |  |  | 8.1
SF L 1103 | 22261103 | 1.98 |  |  |  | 1.98
SF M 0401 | 22270401 | 3.74 |  |  |  | 3.74
SF M 0402 | 22270402 | 1.98 |  |  |  | 1.98
SF M 0403 | 22270403 | 3.67 |  |  |  | 3.67
SF M 0404 | 22270404 | 3.6 |  |  |  | 3.6
SF M 0405 | 22270405 | 2.39 |  |  |  | 2.39
SF M 0406 | 22270406 | 2.92 |  |  |  | 2.92
SF N 0401 | 22280401 | 3.18 |  |  |  | 3.18
SF N 0402 | 22280402 | 1.01 |  |  |  | 1.01
SF N 0403 | 22280403 | 2.46 |  |  |  | 2.46
SF N 0405 | 22280405 | 1.07 |  |  |  | 1.07
SF N 0406 | 22280406 | 0.81 |  |  |  | 0.81
SF N 0408 | 22280408 | 3.13 |  |  |  | 3.13
SF N 1101 | 22281101 | 0.27 |  |  |  | 0.27
SF N 1102 | 22281102 | 6.17 |  |  |  | 6.17
SHADY GLEN 1101 | 152431101 | 38.43 |  | 32.05 | 0.03 | 6.35
SHADY GLEN 1102 | 152431102 | 51.51 | 24.12 | 25.6 |  | 1.79
SHAFTER 1101 | 253651101 | 0.03 |  |  |  | 0.03
SHAFTER 1102 | 253651102 | 27.76 |  |  |  | 27.76
SHAFTER 1103 | 253651103 | 39.55 |  |  |  | 39.55
SHAFTER 1104 | 253651104 | 9.64 |  |  |  | 9.64
SHAFTER 1111 | 253651111 | 24.37 |  |  |  | 24.37
SHAFTER 1112 | 253651112 | 47.85 |  |  |  | 47.85
SHARON 1101 | 255331101 | 1.55 |  |  |  | 1.55
SHEPHERD 2109 | 252062109 | 2.69 |  |  |  | 2.69
SHEPHERD 2110 | 252062110 | 8.44 |  |  |  | 8.44
SHEPHERD 2111 | 252062111 | 69.42 |  | 29.56 |  | 39.86
SHEPHERD 2112 | 252062112 | 7.25 |  |  |  | 7.25
SHINGLE SPRINGS 1103 | 153651103 | 13.68 | 4.61 | 3.11 |  | 5.96
SHINGLE SPRINGS 1104 | 153651104 | 60.19 | 37.4 | 6.67 |  | 16.12
SHINGLE SPRINGS 2105 | 153652105 | 32.8 | 26.09 | 4.4 |  | 2.31
SHINGLE SPRINGS 2108 | 153652108 | 29.78 | 7.17 | 7.84 |  | 14.77
SHINGLE SPRINGS 2109 | 153652109 | 207.31 | 107.41 | 99.26 |  | 0.64
SHINGLE SPRINGS 2110 | 153652110 | 65.3 | 55.54 | 7.38 |  | 2.38
SILVER 0401 | 22670401 | 5.06 |  |  |  | 5.06
SILVERADO 2102 | 43432102 | 103.7 | 32.14 | 22.41 |  | 49.15
SILVERADO 2103 | 43432103 | 32.57 | 10.79 | 0.03 |  | 21.75
SILVERADO 2104 | 43432104 | 142.09 | 74.1 | 38.13 |  | 29.86
SILVERADO 2105 | 43432105 | 63.69 | 34.92 | 1.72 |  | 27.05
SISQUOC 1101 | 182811101 | 26.73 |  |  |  | 26.73
SISQUOC 1102 | 182811102 | 111.66 | 31.35 | 19.61 |  | 60.7
SISQUOC 1103 | 182811103 | 50.22 | 22.65 | 2.83 |  | 24.74
SISQUOC 1104 | 182811104 | 36.28 |  |  |  | 36.28
SKAGGS ISLAND 1101 | 43341101 | 0.05 |  |  |  | 0.05
SMARTVILLE 1101 | 153791101 | 16.29 |  | 16.01 |  | 0.28
SMYRNA 1101 | 253551101 | 43.39 |  |  |  | 43.39
SMYRNA 1102 | 253551102 | 66.89 |  |  |  | 66.89
SMYRNA 1104 | 253551104 | 45.85 |  |  |  | 45.85
SMYRNA 1105 | 253551105 | 56.41 |  |  |  | 56.41
SMYRNA 1106 | 253551106 | 46.61 |  |  |  | 46.61
SNEATH LANE 1101 | 22721101 | 9.43 |  | 2.27 |  | 7.16
SNEATH LANE 1102 | 22721102 | 10.55 |  | 1.24 |  | 9.31
SNEATH LANE 1106 | 22721106 | 11.69 |  | 2.62 |  | 9.07
SNEATH LANE 1107 | 22721107 | 10.49 |  | 0.91 |  | 9.58
SO. CAL. EDISON #3 1101 | 258861101 | 8.53 | 6.11 | 2.28 |  | 0.14
SO. CAL. EDISON 1001 | 258881001 | 2.14 |  |  |  | 2.14
SOBRANTE 1101 | 14671101 | 21.4 |  | 15.01 |  | 6.39
SOBRANTE 1102 | 14671102 | 27.69 | 1.26 | 26.08 |  | 0.35
SOBRANTE 1103 | 14671103 | 11.39 | 1.82 | 7.72 |  | 1.85
SOLEDAD 2101 | 182052101 | 42.38 |  | 17.52 |  | 24.86
SOLEDAD 2102 | 182052102 | 49.14 |  | 11.67 |  | 37.47
SOLEDAD 2104 | 182052104 | 25.16 |  | 1.22 |  | 23.94
SOLEDAD 2105 | 182052105 | 49.11 |  | 4.47 |  | 44.64
SONOMA 1102 | 42721102 | 18.19 | 6.02 |  |  | 12.17
SONOMA 1103 | 42721103 | 25.54 | 12.71 |  |  | 12.83
SONOMA 1104 | 42721104 | 55.58 |  | 19.63 | 0 | 35.95
SONOMA 1105 | 42721105 | 63.08 | 3.47 | 9.94 |  | 49.67
SONOMA 1106 | 42721106 | 10.73 | 0.74 |  |  | 9.99
SONOMA 1107 | 42721107 | 52.08 |  | 3.87 |  | 48.21
SOQUEL 0402 | 83300402 | 6.63 |  |  |  | 6.63
SPAULDING 1101 | 152251101 | 23.92 | 1.18 | 19.13 | 0.51 | 3.1
SPENCE 1101 | 182201101 | 52.33 |  | 9.04 |  | 43.29
SPENCE 1102 | 182201102 | 31 |  | 2.35 |  | 28.65
SPENCE 1103 | 182201103 | 14.95 |  |  |  | 14.95
SPENCE 1104 | 182201104 | 0.01 |  |  |  | 0.01
SPENCE 1105 | 182201105 | 7.2 |  |  |  | 7.2
SPENCE 1106 | 182201106 | 0 |  |  |  | 0
SPRING GAP 1702 | 162831702 | 42.21 | 39.56 | 0.77 | 1.06 | 0.82
STAFFORD 1101 | 43201101 | 19.23 |  | 2.81 |  | 16.42
STAFFORD 1102 | 43201102 | 37.47 | 1.54 | 19.69 |  | 16.24
STAGG 1101 | 162421101 | 19.64 |  |  |  | 19.64
STAGG 1103 | 162421103 | 6.1 |  |  |  | 6.1
STAGG 1105 | 162421105 | 12.1 |  |  |  | 12.1
STAGG 1106 | 162421106 | 1.86 |  |  |  | 1.86
STAGG 2104 | 162422104 | 23.98 |  |  |  | 23.98
STAGG 2105 | 162422105 | 4.5 |  |  |  | 4.5
STAGG 2106 | 162422106 | 5.42 |  |  |  | 5.42
STAGG 2107 | 162422107 | 6.01 |  |  |  | 6.01
STAGG 2108 | 162422108 | 5.84 |  |  |  | 5.84
STANISLAUS 1701 | 162821701 | 73.59 | 22.64 | 50.69 |  | 0.26
STANISLAUS 1702 | 162821702 | 77.44 | 72.11 | 5.34 |  | -0.01
STELLING 1102 | 83481102 | 0.69 |  |  |  | 0.69
STELLING 1103 | 83481103 | 2.87 |  |  |  | 2.87
STELLING 1104 | 83481104 | 11.06 |  |  |  | 11.06
STELLING 1105 | 83481105 | 0.4 |  |  |  | 0.4
STELLING 1106 | 83481106 | 0 |  |  |  | 0
STELLING 1107 | 83481107 | 8.22 |  |  |  | 8.22
STELLING 1108 | 83481108 | 31.88 |  |  |  | 31.88
STELLING 1109 | 83481109 | 16.64 |  | 0.84 |  | 15.8
STELLING 1110 | 83481110 | 52.56 | 14.06 | 21.31 |  | 17.19
STELLING 1111 | 83481111 | 26.83 |  |  |  | 26.83
STELLING 1112 | 83481112 | 2.2 |  |  |  | 2.2
STELLING 1113 | 83481113 | 17.25 |  |  |  | 17.25
STILLWATER 1101 | 103561101 | 35.16 |  | 34.44 |  | 0.72
STILLWATER 1102 | 103561102 | 78.31 |  | 78.21 |  | 0.1
STOCKDALE 1105 | 254071105 | 5.05 |  |  |  | 5.05
STOCKDALE 1106 | 254071106 | 5.63 |  |  |  | 5.63
STOCKDALE 1108 | 254071108 | 3.85 |  |  |  | 3.85
STOCKDALE 1109 | 254071109 | 4.49 |  |  |  | 4.49
STOCKDALE 1110 | 254071110 | 6.35 |  |  |  | 6.35
STOCKDALE 1111 | 254071111 | 8.66 |  |  |  | 8.66
STOCKDALE 2105 | 254072105 | 5.02 |  |  |  | 5.02
STOCKDALE 2106 | 254072106 | 8.98 |  |  |  | 8.98
STOCKDALE 2107 | 254072107 | 9.55 |  |  |  | 9.55
STOCKDALE 2108 | 254072108 | 2.96 |  |  |  | 2.96
STOCKDALE 2109 | 254072109 | 8.59 |  |  |  | 8.59
STOCKDALE 2110 | 254072110 | 11.58 |  |  |  | 11.58
STOCKDALE 2111 | 254072111 | 2.88 |  |  |  | 2.88
STOCKDALE 2112 | 254072112 | 7.24 |  |  |  | 7.24
STOCKDALE 2113 | 254072113 | 20.65 |  |  |  | 20.65
STOCKDALE 2114 | 254072114 | 0.03 |  |  |  | 0.03
STOCKDALE 2115 | 254072115 | 24.41 |  |  |  | 24.41
STOCKTON A 0404 | 162370404 | 5.26 |  |  |  | 5.26
STOCKTON A 0405 | 162370405 | 0.39 |  |  |  | 0.39
STOCKTON A 0406 | 162370406 | 3.29 |  |  |  | 3.29
STOCKTON A 0410 | 162370410 | 6.32 |  |  |  | 6.32
STOCKTON A 1101 | 162371101 | 4.13 |  |  |  | 4.13
STOCKTON A 1102 | 162371102 | 6.54 |  |  |  | 6.54
STOCKTON A 1103 | 162371103 | 0.21 |  |  |  | 0.21
STOCKTON A 1104 | 162371104 | 15.6 |  |  |  | 15.6
STOCKTON A 1105 | 162371105 | 12.41 |  |  |  | 12.41
STOCKTON A 1106 | 162371106 | 17.71 |  |  |  | 17.71
STOCKTON A 1107 | 162371107 | 11.2 |  |  |  | 11.2
STOCKTON A 1108 | 162371108 | 9.6 |  |  |  | 9.6
STOCKTON A 1109 | 162371109 | 11.98 |  |  |  | 11.98
STOCKTON A 1110 | 162371110 | 9.65 |  |  |  | 9.65
STOCKTON A 1111 | 162371111 | 0.07 |  |  |  | 0.07
STOCKTON ACRES 0401 | 163220401 | 2.39 |  |  |  | 2.39
STOCKTON ACRES 0402 | 163220402 | 3.01 |  |  |  | 3.01
STONE 1101 | 83701101 | 20.05 |  |  |  | 20.05
STONE 1104 | 83701104 | 5.67 |  |  |  | 5.67
STONE 1107 | 83701107 | 12.17 |  |  |  | 12.17
STONE 1108 | 83701108 | 4.45 |  |  |  | 4.45
STONE 1109 | 83701109 | 8.2 |  |  |  | 8.2
STONE 1110 | 83701110 | 11.91 |  |  |  | 11.91
STONE CORRAL 1108 | 252921108 | 76.3 |  | 1.87 |  | 74.43
STONE CORRAL 1109 | 252921109 | 16.46 |  |  |  | 16.46
STONE CORRAL 1110 | 252921110 | 62.98 |  | 2.01 |  | 60.97
STOREY 1104 | 254611104 | 74.92 |  |  |  | 74.92
STOREY 1105 | 254611105 | 14.37 |  |  |  | 14.37
STOREY 1106 | 254611106 | 13.64 |  |  |  | 13.64
STOREY 1107 | 254611107 | 19.16 |  |  |  | 19.16
STOREY 1108 | 254611108 | 72.29 |  |  |  | 72.29
STOREY 1109 | 254611109 | 177.55 |  |  | 0.12 | 177.43
STOREY 1111 | 254611111 | 29.41 |  |  |  | 29.41
STROUD 1101 | 253661101 | 46.27 |  |  |  | 46.27
STROUD 1102 | 253661102 | 34.9 |  |  |  | 34.9
STROUD 1104 | 253661104 | 33.84 |  |  |  | 33.84
STUART 0401 | 13840401 | 2.96 |  |  |  | 2.96
STUART 0402 | 13840402 | 1.64 |  |  |  | 1.64
STUART 0403 | 13840403 | 3.13 |  |  |  | 3.13
STUART 0404 | 13840404 | 0.49 |  |  |  | 0.49
STUART 0405 | 13840405 | 2.58 |  |  |  | 2.58
STUART 0406 | 13840406 | 2.95 |  |  |  | 2.95
SUISUN 1101 | 62131101 | 5.51 |  |  |  | 5.51
SUISUN 1102 | 62131102 | 11.98 |  |  |  | 11.98
SUISUN 1103 | 62131103 | 2.73 |  |  |  | 2.73
SUISUN 1104 | 62131104 | 4.84 |  |  |  | 4.84
SUISUN 1105 | 62131105 | 5.11 |  |  |  | 5.11
SUISUN 1106 | 62131106 | 5.06 |  |  |  | 5.06
SUISUN 1107 | 62131107 | 9.68 |  |  |  | 9.68
SUISUN 1108 | 62131108 | 6.62 |  |  |  | 6.62
SUISUN 1109 | 62131109 | 8.09 |  |  |  | 8.09
SUISUN 1110 | 62131110 | 2.91 |  |  |  | 2.91
SUISUN 1111 | 62131111 | 0.63 |  |  |  | 0.63
SUISUN 1112 | 62131112 | 2.84 |  |  |  | 2.84
SULLIVAN 0402 | 22850402 | 3.21 |  |  |  | 3.21
SUMMIT 1101 | 152591101 | 15.22 |  | 7.22 | 2.16 | 5.84
SUMMIT 1102 | 152591102 | 5.05 |  | 5.05 |  | 0
SUNOL 1101 | 14241101 | 55.04 | 9.57 | 23.25 | 1.78 | 20.44
SWIFT 2102 | 83392102 | 2.95 |  | 0.35 |  | 2.6
SWIFT 2106 | 83392106 | 21.33 |  |  |  | 21.33
SWIFT 2107 | 83392107 | 11.95 |  | 1.9 |  | 10.05
SWIFT 2108 | 83392108 | 4.92 |  |  |  | 4.92
SWIFT 2109 | 83392109 | 5.48 |  | 0.12 |  | 5.36
SWIFT 2110 | 83392110 | 86.72 |  | 81.83 |  | 4.89
SWIFT 2111 | 83392111 | 8.59 |  |  |  | 8.59
SYCAMORE CREEK 1101 | 102971101 | 4.57 |  |  |  | 4.57
SYCAMORE CREEK 1102 | 102971102 | 7.58 |  |  |  | 7.58
SYCAMORE CREEK 1103 | 102971103 | 3.16 |  |  |  | 3.16
SYCAMORE CREEK 1104 | 102971104 | 8.15 |  |  |  | 8.15
SYCAMORE CREEK 1105 | 102971105 | 16.45 |  |  |  | 16.45
SYCAMORE CREEK 1107 | 102971107 | 6.04 |  |  |  | 6.04
SYCAMORE CREEK 1109 | 102971109 | 13.07 |  | 0.1 |  | 12.97
SYCAMORE CREEK 1110 | 102971110 | 8.47 |  |  |  | 8.47
SYCAMORE CREEK 1111 | 102971111 | 65.02 | 27.36 | 24.89 |  | 12.77
TAFT 1101 | 252081101 | 14.3 |  |  |  | 14.3
TAFT 1102 | 252081102 | 0.05 |  |  |  | 0.05
TAFT 1103 | 252081103 | 27.54 |  |  |  | 27.54
TAFT 1104 | 252081104 | 11.24 |  |  |  | 11.24
TAFT 1106 | 252081106 | 7.21 |  |  |  | 7.21
TAFT 1108 | 252081108 | 9.34 |  |  |  | 9.34
TAMARACK 1101 | 152291101 | 19.64 |  | 18.75 | 0.46 | 0.43
TAMARACK 1102 | 152291102 | 7.87 |  |  | 1.69 | 6.18
TAR FLAT 0401 | 163240401 | 3.64 | 0 | 3.17 |  | 0.47
TAR FLAT 0402 | 163240402 | 6.72 | 0.88 | 4.53 |  | 1.31
TARAVAL 0401 | 22500401 | 1.83 |  |  |  | 1.83
TARAVAL 0402 | 22500402 | 3.05 |  |  |  | 3.05
TARAVAL 0403 | 22500403 | 3.54 |  |  |  | 3.54
TASSAJARA 2103 | 14662103 | 18.05 |  | 0.2 |  | 17.85
TASSAJARA 2104 | 14662104 | 9.69 | 1.57 | 4.37 |  | 3.75
TASSAJARA 2106 | 14662106 | 2.93 |  | 0.35 |  | 2.58
TASSAJARA 2107 | 14662107 | 8.56 |  |  |  | 8.56
TASSAJARA 2108 | 14662108 | 24.22 | 1.7 |  |  | 22.52
TASSAJARA 2109 | 14662109 | 4.02 |  | 2.89 |  | 1.13
TASSAJARA 2112 | 14662112 | 20.02 | 6.79 | 3.63 |  | 9.6
TASSAJARA 2113 | 14662113 | 4.93 | 3.82 |  |  | 1.11
TECUYA 1101 | 254511101 | 0.04 |  |  |  | 0.04
TEJON 1102 | 252931102 | 83.5 |  | 35.82 |  | 47.68
TEJON 1103 | 252931103 | 31.89 |  | 2.79 |  | 29.1
TEJON 1105 | 252931105 | 30.67 |  |  |  | 30.67
TEJON 1106 | 252931106 | 36.61 |  |  |  | 36.61
TEJON 1107 | 252931107 | 0.55 |  |  |  | 0.55
TEMBLOR 1104 | 252551104 | 49.25 |  |  |  | 49.25
TEMBLOR 2103 | 252552103 | 29.89 |  |  |  | 29.89
TEMPLETON 2108 | 183052108 | 35.24 |  | 3.59 |  | 31.65
TEMPLETON 2109 | 183052109 | 217.97 |  |  | 0.08 | 217.89
TEMPLETON 2110 | 183052110 | 172.88 | 33.35 | 93.86 | 1.12 | 44.55
TEMPLETON 2111 | 183052111 | 97.4 | 13.85 | 62.89 | 0.04 | 20.62
TEMPLETON 2112 | 183052112 | 38.32 |  | 2.66 |  | 35.66
TEMPLETON 2113 | 183052113 | 321.61 | 53.37 | 143.19 | 0.05 | 125
TEMPORARY CARBONA 1101 | 169951101 | 39.16 |  |  |  | 39.16
TEMPORARY CARBONA 1102 | 169951102 | 3.44 |  |  |  | 3.44
TEMPORARY CARBONA 1104 | 169951104 | 31.73 |  |  |  | 31.73
TEMPORARY CARBONA 1105 | 169951105 | 5.3 |  |  |  | 5.3
TERMINOUS 1102 | 163021102 | 21.74 |  |  |  | 21.74
TERMINOUS 1103 | 163021103 | 40.1 |  |  |  | 40.1
TEVIS 2101 | 255322101 | 22.81 |  |  |  | 22.81
TEVIS 2102 | 255322102 | 2.14 |  |  |  | 2.14
TEVIS 2103 | 255322103 | 3.29 |  |  |  | 3.29
TEVIS 2104 | 255322104 | 17.48 |  |  |  | 17.48
TEVIS 2105 | 255322105 | 1.88 |  |  |  | 1.88
TEXACO EMIDIO 1101 | 255421101 | 0.02 |  |  |  | 0.02
TIDEWATER 2104 | 14652104 | 25.19 |  |  |  | 25.19
TIDEWATER 2105 | 14652105 | 14.07 |  |  |  | 14.07
TIDEWATER 2106 | 14652106 | 39.7 |  | 6.43 |  | 33.27
TIDEWATER 2107 | 14652107 | 21.67 |  |  |  | 21.67
TIDEWATER 2108 | 14652108 | 9.61 |  |  |  | 9.61
TIDEWATER 2109 | 14652109 | 33.13 |  |  |  | 33.13
TIDEWATER 2110 | 14652110 | 10.2 |  |  | 0.08 | 10.12
TIGER CREEK 0201 | 161380201 | 3.92 | 1.88 | 2.04 |  | 0
TIVY VALLEY 1106 | 252941106 | 27.01 |  |  |  | 27.01
TIVY VALLEY 1107 | 252941107 | 174.08 |  | 116.02 | 0.04 | 58.02
TOCALOMA 0241 | 43150241 | 0.04 |  | 0.04 |  | 0
TOKAY 1101 | 168881101 | 12.42 |  |  |  | 12.42
TRACY 0402 | 162880402 | 2.86 |  |  |  | 2.86
TRACY 0405 | 162880405 | 3.34 |  |  |  | 3.34
TRACY 1102 | 162881102 | 4.72 |  |  |  | 4.72
TRACY 1103 | 162881103 | 4.44 |  |  |  | 4.44
TRACY 1104 | 162881104 | 4.73 |  |  |  | 4.73
TRACY 1105 | 162881105 | 4.74 |  |  |  | 4.74
TRACY 1106 | 162881106 | 36.3 |  |  |  | 36.3
TRACY 1107 | 162881107 | 6.18 |  |  |  | 6.18
TRACY 1108 | 162881108 | 22.73 |  |  |  | 22.73
TRACY 1109 | 162881109 | 4.99 |  |  |  | 4.99
TRACY 1110 | 162881110 | 9.16 |  |  |  | 9.16
TRACY 1111 | 162881111 | 7.27 |  |  |  | 7.27
TRACY 1112 | 162881112 | 4.73 |  |  |  | 4.73
TRES PINOS 1111 | 183221111 | 32.92 |  | 0.11 |  | 32.81
TRES VIAS 1101 | 103251101 | 68.53 |  |  |  | 68.53
TRIDAM POWERHOUSE 2101 | 168152101 | 0.05 | 0.05 |  |  | 0
TRIMBLE 1103 | 83801103 | 2.74 |  |  |  | 2.74
TRIMBLE 1104 | 83801104 | 0.46 |  |  |  | 0.46
TRIMBLE 1105 | 83801105 | 1.44 |  |  |  | 1.44
TRIMBLE 1106 | 83801106 | 0.64 |  |  |  | 0.64
TRIMBLE 1107 | 83801107 | 1.05 |  |  |  | 1.05
TRIMBLE 1110 | 83801110 | 0.34 |  |  |  | 0.34
TRIMBLE 2115 | 83802115 | 0.31 |  |  |  | 0.31
TRIMBLE 2116 | 83802116 | 3.41 |  |  |  | 3.41
TRINIDAD 1101 | 192231101 | 26.56 |  |  |  | 26.56
TRINIDAD 1102 | 192231102 | 19.04 |  |  |  | 19.04
TUDOR 1101 | 153711101 | 31.49 |  |  |  | 31.49
TUDOR 1102 | 153711102 | 23.17 |  |  |  | 23.17
TULARE LAKE 1104 | 252951104 | 14.59 |  |  |  | 14.59
TULARE LAKE 1106 | 252951106 | 53.21 |  |  |  | 53.21
TULARE LAKE 1108 | 252951108 | 48.48 |  |  |  | 48.48
TULUCAY 1101 | 42301101 | 18.05 |  | 3.77 |  | 14.28
TUPMAN 1103 | 254561103 | 45.58 |  |  |  | 45.58
TUPMAN 1104 | 254561104 | 53.56 |  |  |  | 53.56
TUPMAN 1105 | 254561105 | 23.64 |  |  |  | 23.64
TUPMAN 1106 | 254561106 | 36.71 |  |  |  | 36.71
TWISSELMAN 1101 | 254401101 | 0.02 |  |  |  | 0.02
TWISSELMAN 1102 | 254401102 | 49.39 |  |  |  | 49.39
TWISSELMAN 1104 | 254401104 | 0.02 |  |  |  | 0.02
TWISSELMAN 2105 | 254402105 | 89.12 |  |  |  | 89.12
TYLER 1103 | 103571103 | 4.24 |  |  |  | 4.24
TYLER 1104 | 103571104 | 39.96 |  |  |  | 39.96
TYLER 1105 | 103571105 | 114.23 |  | 60.23 |  | 54
UKIAH 1111 | 42771111 | 31.96 |  | 7.84 |  | 24.12
UKIAH 1113 | 42771113 | 15.91 |  | 7.52 |  | 8.39
UKIAH 1114 | 42771114 | 104.02 |  | 53.94 | 0 | 50.08
UKIAH 1115 | 42771115 | 50.73 |  | 35.18 |  | 15.55
UPPER LAKE 1101 | 42871101 | 73.9 | 1.44 | 35.13 |  | 37.33
VACA DIXON 1101 | 63591101 | 50.54 |  | 22.69 |  | 27.85
VACA DIXON 1102 | 63591102 | 1.98 |  |  |  | 1.98
VACA DIXON 1103 | 63591103 | 127.81 |  |  | 0.03 | 127.78
VACA DIXON 1104 | 63591104 | 7.49 |  |  |  | 7.49
VACA DIXON 1105 | 63591105 | 49.85 |  | 1.41 |  | 48.44
VACA DIXON 1106 | 63591106 | 11.67 |  |  |  | 11.67
VACA DIXON 1109 | 63591109 | 2.1 |  |  |  | 2.1
VACAVILLE 1102 | 63601102 | 1 |  |  |  | 1
VACAVILLE 1103 | 63601103 | 11.21 |  |  |  | 11.21
VACAVILLE 1104 | 63601104 | 12.38 |  | 10.18 |  | 2.2
VACAVILLE 1105 | 63601105 | 2.84 |  |  |  | 2.84
VACAVILLE 1106 | 63601106 | 1.76 |  |  |  | 1.76
VACAVILLE 1107 | 63601107 | 1.87 |  |  |  | 1.87
VACAVILLE 1108 | 63601108 | 36.3 |  | 16.11 | 0 | 20.19
VACAVILLE 1109 | 63601109 | 5.25 |  | 0.72 |  | 4.53
VACAVILLE 1110 | 63601110 | 2.34 |  |  |  | 2.34
VACAVILLE 1111 | 63601111 | 4.3 |  | 1.7 |  | 2.6
VACAVILLE 1112 | 63601112 | 3.33 |  | 0.19 |  | 3.14
VALLEJO B 0411 | 42450411 | 7.09 |  |  |  | 7.09
VALLEJO B 0413 | 42450413 | 6.48 |  |  |  | 6.48
VALLEJO B 0414 | 42450414 | 8.32 |  |  |  | 8.32
VALLEJO B 0415 | 42450415 | 7.67 |  |  |  | 7.67
VALLEJO B 1101 | 42451101 | 16.36 |  |  |  | 16.36
VALLEJO B 1102 | 42451102 | 2.5 |  |  |  | 2.5
VALLEJO C 0401 | 42550401 | 2.83 |  |  |  | 2.83
VALLEY HOME 1702 | 162981702 | 55.94 |  |  |  | 55.94
VALLEY HOME 1703 | 162981703 | 128.23 |  |  |  | 128.23
VALLEY HOME 1704 | 162981704 | 38.86 |  |  |  | 38.86
Valley Springs 1101 | 168891101 | 78.67 |  | 50.91 |  | 27.76
Valley Springs 1102 | 168891102 | 9.01 |  | 7.84 |  | 1.17
VALLEY VIEW 1103 | 14341103 | 18.16 | 0.59 |  | 0.02 | 17.55
VALLEY VIEW 1105 | 14341105 | 15.04 |  | 3.97 |  | 11.07
VALLEY VIEW 1106 | 14341106 | 21.32 | 1.99 | 6.77 |  | 12.56
VASCO 1101 | 13751101 | 2.57 |  |  |  | 2.57
VASCO 1102 | 13751102 | 87.85 |  | 45.33 |  | 42.52
VASCO 1103 | 13751103 | 14.81 |  |  |  | 14.81
VASONA 1101 | 83771101 | 9.95 |  |  |  | 9.95
VASONA 1102 | 83771102 | 11.15 |  |  |  | 11.15
VASONA 1103 | 83771103 | 15.6 |  |  |  | 15.6
VASONA 1104 | 83771104 | 3.79 |  |  |  | 3.79
VASONA 1105 | 83771105 | 11.7 |  |  |  | 11.7
VASONA 1106 | 83771106 | 7.41 |  | 0.12 |  | 7.29
VASONA 1108 | 83771108 | 10.99 |  |  |  | 10.99
VICTOR 1101 | 163281101 | 18.26 |  |  |  | 18.26
VICTOR 1102 | 163281102 | 87.93 |  |  |  | 87.93
VIEJO 2201 | 182852201 | 17.38 |  | 14.64 | 0.02 | 2.72
VIEJO 2202 | 182852202 | 44.15 |  | 14.08 |  | 30.07
VIEJO 2203 | 182852203 | 23.05 |  | 3.04 |  | 20.01
VIEJO 2204 | 182852204 | 24.65 |  | 4.39 |  | 20.26
VIERRA 1701 | 162701701 | 14.8 |  |  |  | 14.8
VIERRA 1702 | 162701702 | 6.62 |  |  |  | 6.62
VIERRA 1703 | 162701703 | 5.57 |  |  |  | 5.57
VIERRA 1706 | 162701706 | 0.75 |  |  |  | 0.75
VIERRA 1707 | 162701707 | 46.37 |  |  |  | 46.37
VINA 1101 | 103581101 | 61.16 |  |  |  | 61.16
VINEYARD 2104 | 14502104 | 3.75 |  |  |  | 3.75
VINEYARD 2105 | 14502105 | 3.94 |  |  |  | 3.94
VINEYARD 2106 | 14502106 | 5.51 |  |  |  | 5.51
VINEYARD 2107 | 14502107 | 13.79 |  | 2.88 |  | 10.91
VINEYARD 2108 | 14502108 | 13.44 | 5.19 |  |  | 8.25
VINEYARD 2109 | 14502109 | 4.73 |  |  |  | 4.73
VINEYARD 2110 | 14502110 | 10.12 |  | 4.81 |  | 5.31
VIRGINIA 0401 | 13780401 | 4.09 |  |  |  | 4.09
VOLTA 1101 | 102541101 | 144.14 | 6.3 | 135.72 |  | 2.12
VOLTA 1102 | 102541102 | 129.79 | 86.99 | 41.97 |  | 0.83
WAHTOKE 1106 | 254531106 | 13.95 |  |  |  | 13.95
WAHTOKE 1107 | 254531107 | 19.21 |  |  |  | 19.21
WAHTOKE 1108 | 254531108 | 108.86 |  |  |  | 108.86
WAHTOKE 1109 | 254531109 | 7.01 |  |  |  | 7.01
WAHTOKE 1110 | 254531110 | 16 |  |  |  | 16
WAHTOKE 1111 | 254531111 | 29.98 |  |  |  | 29.98
WALDO 0401 | 13350401 | 4.25 |  | 0.33 |  | 3.92
WALDO 0402 | 13350402 | 3.46 |  | 1.22 |  | 2.24
WALL 0401 | 13740401 | 5.39 |  |  |  | 5.39
WALNUT CREEK 0403 | 12200403 | 0.51 |  |  |  | 0.51
WALNUT CREEK 0404 | 12200404 | 6.43 |  |  | 0.05 | 6.38
WARD 0401 | 12980401 | 7.93 |  |  |  | 7.93
WASCO 1101 | 252961101 | 12.22 |  |  |  | 12.22
WASCO 1102 | 252961102 | 7.82 |  |  |  | 7.82
WASCO 1104 | 252961104 | 9.87 |  |  |  | 9.87
WATERLOO 1101 | 163151101 | 58.37 |  |  |  | 58.37
WATERLOO 1102 | 163151102 | 21.87 |  |  |  | 21.87
WATERSHED 0402 | 24240402 | 1.24 | 0.02 |  |  | 1.22
WATSONVILLE 0411 | 83330411 | 2.33 |  |  |  | 2.33
WATSONVILLE 0413 | 83330413 | 1.22 |  |  |  | 1.22
WATSONVILLE 0414 | 83330414 | 1.29 |  |  |  | 1.29
WATSONVILLE 2101 | 83332101 | 102.75 |  |  |  | 102.75
WEBER 1101 | 163481101 | 3.15 |  |  |  | 3.15
WEBER 1102 | 163481102 | 18.41 |  |  |  | 18.41
WEBER 1103 | 163481103 | 1.8 |  |  |  | 1.8
WEBER 1105 | 163481105 | 21.05 |  |  |  | 21.05
WEBER 1107 | 163481107 | 12.57 |  |  |  | 12.57
WEBER 1108 | 163481108 | 0.44 |  |  |  | 0.44
WEBER 1109 | 163481109 | 53.16 |  |  |  | 53.16
WEBER 1110 | 163481110 | 12.3 |  |  |  | 12.3
WEBER 1111 | 163481111 | 19.87 |  |  |  | 19.87
WEBER 1112 | 163481112 | 0.02 |  |  |  | 0.02
WEBER 1113 | 163481113 | 2.13 |  |  |  | 2.13
WEBER 1114 | 163481114 | 9.84 |  |  |  | 9.84
WEBER 1115 | 163481115 | 14.42 |  |  |  | 14.42
WEEDPATCH 1101 | 252971101 | 21.74 |  |  |  | 21.74
WEEDPATCH 1102 | 252971102 | 18.81 |  |  |  | 18.81
WEEDPATCH 1103 | 252971103 | 18.46 |  |  |  | 18.46
WEEDPATCH 1105 | 252971105 | 0.88 |  |  |  | 0.88
WEEDPATCH 1106 | 252971106 | 64.55 |  |  |  | 64.55
WEIMAR 1101 | 152491101 | 78.53 |  | 78.53 |  | 0
WEIMAR 1102 | 152491102 | 28.3 |  | 28.3 |  | 0
WELLFIELD 1102 | 254291102 | 37.9 |  |  |  | 37.9
WELLFIELD 1103 | 254291103 | 0.32 |  |  |  | 0.32
WELLFIELD 1104 | 254291104 | 5.27 |  |  |  | 5.27
WEST FRESNO 1101 | 253731101 | 16.06 |  |  |  | 16.06
WEST FRESNO 1102 | 253731102 | 4.07 |  |  |  | 4.07
WEST FRESNO 1103 | 253731103 | 5.93 |  |  |  | 5.93
WEST FRESNO 1104 | 253731104 | 15.47 |  |  |  | 15.47
WEST FRESNO 1105 | 253731105 | 6.06 |  |  |  | 6.06
WEST FRESNO 1106 | 253731106 | 5.96 |  |  |  | 5.96
WEST FRESNO 1107 | 253731107 | 4.35 |  |  |  | 4.35
WEST FRESNO 1108 | 253731108 | 2.38 |  |  |  | 2.38
WEST FRESNO 1109 | 253731109 | 20.37 |  |  |  | 20.37
WEST FRESNO 1110 | 253731110 | 5.26 |  |  |  | 5.26
WEST FRESNO 1111 | 253731111 | 28.09 |  |  |  | 28.09
WEST FRESNO 1112 | 253731112 | 29.38 |  |  |  | 29.38
WEST LANE 1101 | 163621101 | 10.1 |  |  |  | 10.1
WEST LANE 1102 | 163621102 | 14.68 |  |  |  | 14.68
WEST LANE 1103 | 163621103 | 4.92 |  |  |  | 4.92
WEST POINT 1101 | 163201101 | 63.1 | 63.06 | 0.04 |  | 0
WEST POINT 1102 | 163201102 | 252.01 | 184.25 | 67.26 |  | 0.5
WEST SACRAMENTO 1104 | 63131104 | 10.55 |  |  |  | 10.55
WEST SACRAMENTO 1105 | 63131105 | 6.33 |  |  |  | 6.33
WEST SACRAMENTO 1106 | 63131106 | 2.03 |  |  |  | 2.03
WEST SACRAMENTO 1107 | 63131107 | 15.68 |  |  |  | 15.68
WEST SACRAMENTO 1108 | 63131108 | 9.97 |  |  |  | 9.97
WEST SACRAMENTO 1109 | 63131109 | 36.06 |  |  |  | 36.06
WEST SACRAMENTO 1110 | 63131110 | 7.26 |  |  |  | 7.26
WEST SACRAMENTO 1111 | 63131111 | 0.01 |  |  |  | 0.01
WESTLAKE 0401 | 22600401 | 0.82 |  |  |  | 0.82
WESTLAKE 0403 | 22600403 | 1.78 |  |  |  | 1.78
WESTLEY 1101 | 162671101 | 87.17 |  |  |  | 87.17
WESTLEY 1102 | 162671102 | 0.07 |  |  |  | 0.07
WESTLEY 1103 | 162671103 | 96.68 |  | 0.43 |  | 96.25
WESTPARK 1101 | 253701101 | 11.41 |  |  |  | 11.41
WESTPARK 1102 | 253701102 | 3.77 |  |  |  | 3.77
WESTPARK 1103 | 253701103 | 15.73 |  |  |  | 15.73
WESTPARK 1104 | 253701104 | 10.44 |  |  |  | 10.44
WESTPARK 1105 | 253701105 | 2.3 |  |  |  | 2.3
WESTPARK 1106 | 253701106 | 2.77 |  |  |  | 2.77
WESTPARK 1107 | 253701107 | 5.3 |  |  |  | 5.3
WESTPARK 1108 | 253701108 | 21.18 |  |  |  | 21.18
WESTPARK 1109 | 253701109 | 9.91 |  |  |  | 9.91
WESTPARK 1110 | 253701110 | 13.06 |  |  |  | 13.06
WESTPARK 1111 | 253701111 | 5.25 |  |  |  | 5.25
WESTPARK 1112 | 253701112 | 6.93 |  |  |  | 6.93
WHEATLAND 1101 | 152811101 | 0 |  |  |  | 0
WHEATLAND 1102 | 152811102 | 30.11 |  |  |  | 30.11
WHEATLAND 1104 | 152811104 | 113.93 |  |  |  | 113.93
WHEATLAND 1105 | 152811105 | 75.22 |  | 10.81 |  | 64.41
WHEELER RIDGE 1101 | 253481101 | 50.73 |  |  |  | 50.73
WHEELER RIDGE 1102 | 253481102 | 34.39 |  |  |  | 34.39
WHEELER RIDGE 1103 | 253481103 | 39.16 |  |  |  | 39.16
WHISMAN 1101 | 83631101 | 5.09 |  |  |  | 5.09
WHISMAN 1102 | 83631102 | 1.77 |  |  |  | 1.77
WHISMAN 1103 | 83631103 | 2.68 |  |  |  | 2.68
WHISMAN 1104 | 83631104 | 0 |  |  |  | 0
WHISMAN 1105 | 83631105 | 0.94 |  |  |  | 0.94
WHISMAN 1106 | 83631106 | 7.2 |  |  |  | 7.2
WHISMAN 1107 | 83631107 | 0.13 |  |  |  | 0.13
WHISMAN 1108 | 83631108 | 7.09 |  |  |  | 7.09
WHISMAN 1110 | 83631110 | 1.95 |  |  |  | 1.95
WHISMAN 1111 | 83631111 | 2.2 |  |  |  | 2.2
WHITMORE 1101 | 103601101 | 91.11 | 31.8 | 59.31 |  | 0
WILDWOOD 1101 | 103611101 | 32.07 |  | 32.07 |  | 0
WILKINS SLOUGH 1101 | 62771101 | 52.82 |  |  |  | 52.82
WILKINS SLOUGH 1102 | 62771102 | 62.33 |  |  |  | 62.33
WILKINS SLOUGH 1103 | 62771103 | 34.5 |  |  |  | 34.5
WILLIAMS 1101 | 62051101 | 32.73 |  |  |  | 32.73
WILLIAMS 1102 | 62051102 | 99.22 |  |  |  | 99.22
WILLITS 1102 | 42661102 | 11.32 |  | 4.8 |  | 6.52
WILLITS 1103 | 42661103 | 154.87 | 50.05 | 91.57 |  | 13.25
WILLITS 1104 | 42661104 | 95.94 | 50.96 | 36.35 |  | 8.63
WILLOW CREEK 1101 | 192171101 | 56.58 | 25.96 | 20.09 |  | 10.53
WILLOW CREEK 1102 | 192171102 | 9.6 | 5.32 | 4.28 |  | 0
WILLOW CREEK 1103 | 192171103 | 77.14 | 0.53 | 75.45 |  | 1.16
WILLOW PASS 1101 | 13911101 | 7.07 |  | 1.12 |  | 5.95
WILLOW PASS 1102 | 13911102 | 5.11 |  |  |  | 5.11
WILLOW PASS 2107 | 13912107 | 3.07 |  | 0.66 |  | 2.41
WILLOW PASS 2108 | 13912108 | 21.23 |  | 0.23 |  | 21
WILLOWS A 1101 | 102741101 | 4.29 |  |  |  | 4.29
WILLOWS A 1103 | 102741103 | 9.91 |  |  |  | 9.91
WILLOWS A 1104 | 102741104 | 9.44 |  |  |  | 9.44
WILSON 1101 | 254301101 | 13.28 |  |  |  | 13.28
WILSON 1102 | 254301102 | 31.33 |  |  |  | 31.33
WILSON 1103 | 254301103 | 115.68 |  |  |  | 115.68
WINDSOR 1101 | 43501101 | 8.45 |  |  |  | 8.45
WINDSOR 1102 | 43501102 | 15.67 |  |  |  | 15.67
WINDSOR 1103 | 43501103 | 11.23 |  | 2 |  | 9.23
WINTERS 1101 | 63321101 | 12.9 |  |  |  | 12.9
WINTERS 1102 | 63321102 | 35.38 |  |  |  | 35.38
WISE 1101 | 152271101 | 12.93 |  | 5.72 | 0.28 | 6.93
WISE 1102 | 152271102 | 119.32 |  | 114.31 | 0.22 | 4.79
WISHON 1101 | 251511101 | 7.18 | 3.43 | 3.75 |  | 0
WOLFE 1104 | 83671104 | 6.81 |  |  |  | 6.81
WOLFE 1105 | 83671105 | 7.29 |  |  |  | 7.29
WOLFE 1106 | 83671106 | 9.1 |  |  |  | 9.1
WOLFE 1107 | 83671107 | 9.77 |  |  |  | 9.77
WOLFE 1109 | 83671109 | 8.97 |  |  |  | 8.97
WOLFE 1110 | 83671110 | 2.04 |  |  |  | 2.04
WOLFE 1113 | 83671113 | 17.46 |  |  |  | 17.46
WOLFE 1114 | 83671114 | 2.93 |  |  |  | 2.93
WOOD 0401 | 13380401 | 3.39 |  | 0.23 |  | 3.16
WOODACRE 1101 | 43021101 | 38.17 | 22.8 | 7.8 |  | 7.57
WOODACRE 1102 | 43021102 | 31.14 | 19.35 | 11.42 |  | 0.37
WOODLAND 1101 | 62031101 | 7.23 |  |  |  | 7.23
WOODLAND 1102 | 62031102 | 13.61 |  |  |  | 13.61
WOODLAND 1103 | 62031103 | 1.23 |  |  |  | 1.23
WOODLAND 1104 | 62031104 | 5.96 |  |  |  | 5.96
WOODLAND 1105 | 62031105 | 2.64 |  |  |  | 2.64
WOODLAND 1106 | 62031106 | 28.06 |  |  |  | 28.06
WOODLAND 1107 | 62031107 | 11.23 |  |  |  | 11.23
WOODLAND 1108 | 62031108 | 21.3 |  |  |  | 21.3
WOODLAND 1109 | 62031109 | 10.79 |  |  |  | 10.79
WOODLAND 1110 | 62031110 | 10.96 |  |  |  | 10.96
WOODLAND 1111 | 62031111 | 0.26 |  |  |  | 0.26
WOODLAND 1112 | 62031112 | 12.91 |  |  |  | 12.91
WOODLAND 1113 | 62031113 | 20.95 |  |  |  | 20.95
WOODSIDE 1101 | 24251101 | 61.21 | 41.87 | 0.5 |  | 18.84
WOODSIDE 1102 | 24251102 | 17.28 |  | 0.06 |  | 17.22
WOODSIDE 1104 | 24251104 | 44.19 | 7.16 | 13.1 | 0.01 | 23.92
WOODSIDE 1105 | 24251105 | 6.24 |  |  |  | 6.24
WOODWARD 2101 | 255292101 | 25.9 |  |  |  | 25.9
WOODWARD 2102 | 255292102 | 1.41 |  |  |  | 1.41
WOODWARD 2104 | 255292104 | 3.61 |  |  |  | 3.61
WOODWARD 2105 | 255292105 | 0.36 |  |  |  | 0.36
WOODWARD 2106 | 255292106 | 0.26 |  |  |  | 0.26
WOODWARD 2107 | 255292107 | 8.87 |  |  |  | 8.87
WOODWARD 2108 | 255292108 | 91.42 |  | 18.39 | 1.47 | 71.56
WOODWARD 2109 | 255292109 | 1.59 |  |  |  | 1.59
WRIGHT 1110 | 254641110 | 88.16 |  |  |  | 88.16
WYANDOTTE 1102 | 102911102 | 20.86 |  | 4.33 |  | 16.53
WYANDOTTE 1103 | 102911103 | 60.76 | 36.41 | 12.04 |  | 12.31
WYANDOTTE 1105 | 102911105 | 26.41 | 0.68 | 16.47 |  | 9.26
WYANDOTTE 1106 | 102911106 | 95.13 |  | 0.55 |  | 94.58
WYANDOTTE 1107 | 102911107 | 156.73 | 9.93 | 101.75 |  | 45.05
WYANDOTTE 1109 | 102911109 | 117.65 |  | 51.86 | 0.25 | 65.54
WYANDOTTE 1110 | 102911110 | 33.72 |  | 7.69 |  | 26.03
YOSEMITE 0401 | 22490401 | 3.56 |  |  |  | 3.56
YOSEMITE 0402 | 22490402 | 2.41 |  |  |  | 2.41
YOSEMITE 0403 | 22490403 | 0 |  |  |  | 0
ZACA 1101 | 182681101 | 25.27 | 0.65 | 16.38 |  | 8.24
ZACA 1102 | 182681102 | 80.44 | 22.36 | 40.69 |  | 17.39
ZAMORA 1105 | 63191105 | 45.68 |  |  |  | 45.68
ZAMORA 1106 | 63191106 | 53.92 |  |  |  | 53.92
ZAMORA 1107 | 63191107 | 77.16 |  |  | 0.11 | 77.05
|  | 80121.92 | 6805.24 | 17867.83 | 127.67 | 55321.18
|  |  | HFTD Mileage | 24673.07