## ET-WD Details
kV Cls | kV | SAP FL | LINE NO | FACILITY NAME | YEAR | Date Out | Time Out | MED | ET Wire Down | Auto Reclose Disabled | Durn (hr:min) | Durn (mins) | Date In | Time In | Out Cls | Cause Category | Cause Detail | Secondary Cause | Comments | CAP | REGION | TOTL | Customers Affected | CESO Event | CMIN Event | SAIFI Contr | SAIDI Contr | CAIDI | System Customer Count | Fault Type | Fault Estimate | AUTO EFO SCHD | Outage Mode | HFTD | County | Division | LAT | LONG | Actual Location | Weather | Conductor | ETGIS Location | BS GS SD
69 | 70 | ETL.9360 | 70096 | CORCORAN-GUERNSEY | 2025 | 2025-01-07 02:31 | 45664.1049 | No | YES | No | 0.88472 | 1274 | 2025-01-07 23:45 | 45664.9896 | F | External Contact | Ext Cont-car pole | STRU |  | NONE | CENTRAL VALLEY | INT-18892 | 0 | 0 | 0 | 0 | 0 | 0 | 5795693 | B-C-G | 008/012 | AUTO | Single Mode | Non-HFTD | Kings | Fresno | Data available upon request | Data available upon request | Corcoran-Guernsey 70kV line STR 008/014 | Clear | 266.8 AAC | Data available upon request | SD
69 | 60 | ETL.7860 | 60434 | CROW CREEK SW STA-NEWMAN | 2025 | 2025-01-10 23:42 | 45667.9875 | No | YES | No | 0.53611 | 772 | 2025-01-11 12:34 | 45668.5236 | F | External Contact | Ext Cont-car pole | STRU |  | NONE | CENTRAL VALLEY | INT-18895-4 | 4739 | 4739 | 145240 | 0.00081768 | 0.02506 | 31 | 5795693 | C-A | 013/006 | AUTO | Dependent Mode Initiating | Non-HFTD | Stanislaus | Yosemite |  |  | Crow Creek SW STA-Newman 60kV line STR 12/15 | Clear | 266.8 AAC |  | BS
69 | 70 | ETL.8970 | 70115 | COPUS-OLD RIVER | 2025 | 2025-01-16 12:44 | 45673.5306 | No | YES | No | 0.15486 | 223 | 2025-01-16 16:27 | 45673.6854 | F | Equipment Failure | Equip Fail-conductor | COND |  | 130749646 | CENTRAL VALLEY | INT-18904 | 220 | 220 | 16564 | 3.7959e-05 | 0.002858 | 75 | 5795693 | A-G | 018/303 | AUTO | Single Mode | Non-HFTD | Kern | Kern |  |  | Copus-Old River 70kV line STR 018/298 | Clear | 3/0 AAC |  | BS
69 | 60 | ETL.6560 | 60048 | COOLEY LANDING-LOS ALTOS | 2025 | 2025-01-18 18:07 | 45675.7549 | No | YES | No | 1900-01-02 18:27 | 5427 | 2025-01-22 12:34 | 45679.5236 | C | Equipment Failure | Equip Fail-conductor | COND |  | 130774864 | SOUTH BAY AND CENTRAL COAST | INT-18910 | 0 | 0 | 0 | 0 | 0 | 0 | 5795693 | A-B | 004/033 | AUTO | Single Mode | Non-HFTD | Santa Clara | De Anza |  |  | Cooley Landing-Los Altos 60kV line STR 004/032 | Clear | 4/0 CU |  | BS
69 | 70 | ETL.8670 | 70122 | JAYNE SW STA-COALINGA #1 | 2025 | 2025-01-22 05:30 | 45679.2292 | No | YES | No | 0.62083 | 894 | 2025-01-22 20:24 | 45679.85 | F | External Contact | Ext Cont-car pole | STRU |  | NONE | CENTRAL VALLEY | INT-18912 | 0 | 0 | 0 | 0 | 0 | 0 | 5795693 | C-A-G | 007/004 | AUTO | Single Mode | Non-HFTD | Fresno | Fresno |  |  | Jayne SW STA-Coalinga #1-70kV line STR 007/001 | Clear | 336.4 AAC |  | GS
69 | 70 | ETL.9260 | 70086 | TIVY VALLEY-REEDLEY | 2025 | 2025-01-25 00:55 | 45682.0382 | No | YES | No | 0.30625 | 441 | 2025-01-25 08:16 | 45682.3444 | F | Equipment Failure | Equip Fail-conductor | COND |  | NONE | CENTRAL VALLEY | INT-18917 | 0 | 0 | 0 | 0 | 0 | 0 | 5795693 | C-G | 035/005 | AUTO | Single Mode | Non-HFTD | Fresno | Fresno |  |  | Tivy Valley-Reedley 70kV STR 035/003 | Clear | 397.5 AAC |  | GS
69 | 60 | ETL.6310 | 60019 | CASCADE-BENTON-DESCHUTES | 2025 | 2025-01-25 10:27 | 45682.4354 | No | YES | No | 0.34792 | 501 | 2025-01-25 18:48 | 45682.7833 | F | Equipment Failure | Equip Fail-conductor | COND |  | NONE | NORTH VALLEY AND SIERRA | INT-18919 | 276 | 876 | 104754 | 0.00015115 | 0.018074 | 120 | 5795693 | C | Could not determine | AUTO | Single Mode | Non-HFTD | Shasta | North Valey |  |  | Cascade-Benton-Deschutes 60kV line STR 009/195 | Clear | 4/0 AAC |  | GS
69 | 60 | ETL.8060 | 60206 | SPAULDING-SUMMIT | 2025 | 2025-02-04 11:26 | 45692.4764 | No | YES | No | 0.21736 | 313 | 2025-02-04 16:39 | 45692.6937 | F | Weather | Weather-snow/ ice | COND |  | NONE | NORTH VALLEY AND SIERRA | INT-18939 | 2008 | 2008 | 659034 | 0.00034646 | 0.11371 | 652 | 5795693 | B-C | 000/007 | AUTO | Single Mode | Tier 2 | Nevada | Sierra |  |  | Cisco Grove 60kV Tap STR 000/007 | Storm | 2 ACSR |  | SD
69 | 60 | ETL.6760 | 60070 | DRUM-GRASS VALLEY-WEIMAR | 2025 | 2025-02-06 23:02 | 45694.9597 | No | YES | No | 0.79653 | 1147 | 2025-02-07 18:09 | 45695.7562 | F | Tree | Tree-failure | COND |  | NONE | NORTH VALLEY AND SIERRA | INT-18950-1 | 3609 | 3609 | 68571 | 0.0006227 | 0.011831 | 38 | 5795693 |  | B023/521 | AUTO | Dependent Mode Initiating | Tier 3 | Nevada | Sierra |  |  | Drum-Grass Valley-Weimar 60kV line STR B022/492 | Rain | 2/0 CU |  | SD
69 | 70 | ETL.8500 | 70008 | BORDEN-COPPERMINE | 2025 | 2025-02-08 01:41 | 45696.0701 | No | YES | No | 0.22639 | 326 | 2025-02-08 07:07 | 45696.2965 | F | Equipment Failure | Equip Fail-conductor | COND |  | 130834460 | CENTRAL VALLEY | T25-004757 | 6003 | 6003 | 258129 | 0.0010358 | 0.044538 | 43 | 5795693 | A-G | 016/007 | AUTO | Single Mode | Non-HFTD | Madera | Yosemite |  |  | Borden-Coppermine 70kV line STR :018/004 | Clear | 397.5 AAC |  | BS
69 | 60 | ETL.7460 | 60141 | MANTECA #1 | 2025 | 2025-02-12 21:55 | 45700.9132 | No | YES | No | 0.56806 | 818 | 2025-02-13 11:33 | 45701.4812 | F | Equipment Failure | Equip Fail-conductor | COND |  | NONE | CENTRAL VALLEY | INT-18957-1 | 1736 | 1736 | 31248 | 0.00029953 | 0.0053916 | 18 | 5795693 | B-C | 006/098 | AUTO | Single Mode | Non-HFTD | San Joaquin | Stockton |  |  | Manteca #1-60kV line STR 6/108 | Rain | 1/0 AAC |  | GS
69 | 60 | ETL.2060 | 60389 | FORT BRAGG-ELK | 2025 | 2025-02-13 13:39 | 45701.5687 | No | YES | No | 1899-12-31 02:07 | 1567 | 2025-02-14 15:46 | 45702.6569 | F | Tree | Tree-failure | COND |  | NONE | NORTH COAST | INT-18969 | 2605 | 0 | 0 | 0 | 0 | 0 | 5795693 | C-A-G | 006/007 | AUTO | Single Mode | Tier 2 | Mendocino | Humboldt |  |  | Fort Bragg-Elk 60kV line STR 007/000 | Storm | 397.5 AAC |  | SD
69 | 60 | ETL.6380 | 60420 | KONOCTI-MIDDLETOWN | 2025 | 2025-03-06 17:56 | 45722.7472 | No | YES | No | 0.79444 | 1144 | 2025-03-07 13:00 | 45723.5417 | F | Tree | Tree-3rd party | COND |  | NONE | NORTH COAST | INT-19037 | 2581 | 0 | 0 | 0 | 0 | 0 | 5795693 | B-C | 027/004 | AUTO | Single Mode | Tier 2 | Lake | Humboldt |  |  | Konocti-Middletown 60kV line STR 027/003 | Clear | 4/0 AAC |  | GS
69 | 60 | ETL.7820 | 60181 | POTTER VALLEY-WILLITS | 2025 | 2025-03-14 05:52 | 45730.2444 | No | YES | No | 0.47292 | 681 | 2025-03-14 17:13 | 45730.7174 | F | Tree | Tree-failure | COND |  | NONE | NORTH COAST | INT-19067 | 0 | 0 | 0 | 0 | 0 | 0 | 5795693 | B-C | 008/009 | AUTO | Single Mode | Tier 3 | Mendocino | Humboldt |  |  | Potter Valley-Willits 60kV line STR 009/002 | Storm | 1/0 ACSR |  | SD
69 | 60 | ETL.8270 | 60227 | VIEJO-MONTEREY | 2025 | 2025-03-17 14:25 | 45733.6007 | No | YES | No | 1899-12-31 00:39 | 1479 | 2025-03-18 15:04 | 45734.6278 | F | Tree | Tree-failure | COND |  | NONE | SOUTH BAY AND CENTRAL COAST | INT-19077 | 0 | 0 | 0 | 0 | 0 | 0 | 5795693 | A-B-C | 000/013 | AUTO | Single Mode | Tier 2 | Monterey | Central Coast |  |  | Viejo-Monterey 60kV line STR 000/011 | Storm | 715.5 AAC |  | SD
69 | 60 | ETL.6150 | 60001 | ALMENDRA JCT-NICOLAUS | 2025 | 2025-03-31 19:02 | 45747.7931 | No | YES | No | 0.36319 | 523 | 2025-04-01 03:45 | 45748.1562 | F | Equipment Failure | Equip Fail-conductor | COND |  | NONE | NORTH VALLEY AND SIERRA | T25-007614 | 1728 | 1444 | 264419 | 0.00024915 | 0.045623 | 363 | 5795693 | N/A | N/A | EFO | Emergency Forced Outage | Non-HFTD | Sutter | Sierra |  |  | Almendra JCT-Nicolaus 60kV line STR 19/404 | Rain | 2/0 CU |  | GS
230 | 230 | ETL.9001 | 20203 | WILSON-BORDEN | 2025 | 2025-04-02 06:01 | 45749.2507 | No | YES | No | 0.45 | 648 | 2025-04-02 16:49 | 45749.7007 | F | External Contact | Ext Cont-vandalism | COND |  | NONE | CENTRAL VALLEY | T25-007668 | 2952 | 2952 | 185976 | 0.00050934 | 0.032089 | 63 | 5795693 | B-G | 093/609 | AUTO | Dependent Mode Initiating | Non-HFTD | Madera | Yosemite |  |  | Wilson-Borden #2-230kV line STR 93/612 | Clear | 500 HOLO-CU |  | GS
69 | 70 | ETL.8670 | 70122 | JAYNE SW STA-COALINGA #1 | 2025 | 2025-05-01 16:06 | 45778.6708 | No | YES | No | 0.89792 | 1293 | 2025-05-02 13:39 | 45779.5687 | F | External Contact | Ext Cont-car pole | STRU |  | NONE | CENTRAL VALLEY | INT-19159 | 0 | 0 | 0 | 0 | 0 | 0 | 5795693 | A-B-C | 001/014 | AUTO | Single Mode | Non-HFTD | Fresno | Fresno |  |  | Jayne SW STA Coalinga #1-70kV line STR 001/015 | Clear | 336.4 AAC |  | BS
69 | 70 | ETL.8440 | 70002 | ARCO-CHOLAME | 2025 | 2025-05-02 03:39 | 45779.1521 | No | YES | YES | 0.54514 | 785 | 2025-05-02 16:44 | 45779.6972 | F | Equipment Failure | Equip Fail-conductor | COND |  | NONE | CENTRAL VALLEY | INT-19162 | 1795 | 1795 | 921489 | 0.00030971 | 0.159 | 1783 | 5795693 | B-G | 014/140 | AUTO | Single Mode | Tier 2 | Kern | Kern |  |  | Arco-Cholame 70kV line (EPSS) STR 16/161 | Clear | 3/0 AAC |  | BS
69 | 60 | ETL.7920 | 60191 | SALINAS-LAGUNITAS | 2025 | 2025-05-07 15:08 | 45784.6306 | No | YES | YES | 1900-01-14 23:22 | 23002 | 2025-05-23 14:30 | 45800.6042 | C | External Contact | Ext Cont-car pole | STRU |  | NONE | SOUTH BAY AND CENTRAL COAST | INT-19175-1 | 14809 | 14809 | 3110331 | 0.0025552 | 0.53666 | 210 | 5795693 | B-G | 001/044 | AUTO | Dependent Mode Initiating | Non-HFTD | Monterey | Central Coast |  |  | Salinas-Lagunitas 60kV line STR 2/49 | Clear | 1/0 CU |  | BS
69 | 60 | ETL.7000 | 60095 | HAMILTON BRANCH-CHESTER | 2025 | 2025-05-11 13:56 | 45788.5806 | No | YES | YES | 0.71736 | 1033 | 2025-05-12 07:09 | 45789.2979 | F | Tree | Tree-failure | STRU |  | NONE | NORTH VALLEY AND SIERRA | INT-19181 | 1669 | 1669 | 1803193 | 0.00028797 | 0.31113 | 1080 | 5795693 | C-A | 009/195 | AUTO | Single Mode | Non-HFTD | Plumas | North Valley |  |  | Hamilton Branch-Chester 60kV line (EPSS) (HFRA) STR 011/245 | Clear | 397.5 ACSR |  | BS
115 | 115 | ETL.temp | 10550 | TESLA-VIERRA | 2025 | 2025-05-22 14:40 | 45799.6111 | No | YES | No | 1900-01-01 20:49 | 4129 | 2025-05-25 11:29 | 45802.4785 | F | Equipment Failure | Equip Fail-structure-line | STRU |  | NONE | CENTRAL VALLEY | INT-19197-1 | 0 | 0 | 0 | 0 | 0 | 0 | 5795693 | B-G | 000/001 | AUTO | Dependent Mode Initiating | Non-HFTD | Alameda | Mission |  |  | Tesla-Vierra 115kV line relayed and tested NG. On the trouble Vierra-Tesla Motors 115kV line and Vierra 115kV Bus #1 de-energized | Clear | 1113 AAC |  | GS
115 | 115 | ETL.2170 | 10143 | MADISON-VACA | 2025 | 2025-06-14 17:10 | 45822.7153 | No | YES | YES | 0.27153 | 391 | 2025-06-14 23:41 | 45822.9868 | F | External Contact | Ext Cont-car pole | STRU |  | None | NORTH VALLEY AND SIERRA | INT-19243 | 4110 | 4110 | 622362 | 0.00070915 | 0.10738 | 151 | 5795693 | C-G | 038/238 | AUTO | Common Mode | Non-HFTD | Yolo | Sacramento |  |  | Madison-Vaca 115kV line (HFRA) STR 005/062 | Clear | 3/0 CU |  | BS
115 | 115 | ETL.3470 | 10281 | RIO OSO-WOODLAND #2 | 2025 | 2025-06-14 17:10 | 45822.7153 | No | YES | YES | 1899-12-31 05:49 | 1789 | 2025-06-15 22:59 | 45823.9576 | F | External Contact | Ext Cont-car pole | STRU |  | None | NORTH VALLEY AND SIERRA | INT-19244 | 1328 | 1328 | 164672 | 0.00022914 | 0.028413 | 124 | 5795693 | A-G | 003/052 | AUTO | Common Mode | Non-HFTD | Yolo | Sacramento |  |  | Rio Oso-Woodland #2-115kv line STR 005/062 | Clear | 715.5 AAC |  | BS
*Note: data puled from the Transmission Outage Database on July 16, 2025

## 2022 ET-WD Details
Count | Count Excl MEDs | HFTD | REGION | TL Area | kV Cls | kV | SAP FL | LINE NO | FACILITY | YEAR | Date Out | Time Out | MED | ET Wire Down | Auto Reclose Disabled | Durn (hr:min) | Durn (mins) | Date In | Time In | Out Cls | Cause Category | Cause Detail | Secondary Cause | Comments | CAP | REGION | TOTL | Customers Affected | CESO/ Event | CMIN/ Event | SAIFI Contr | SAIDI Contr | CAIDI | System Customer Count | Fault Type | Fault Estimate | AUTO / EFO / SCHD | Outage Mode | HFTD | County | Division | LAT | LONG | Actual Location | Weaher | Conductor | ET-GIS Location | ET-GIS Location | ET-GIS Location | Conductor Rating
1 | 1 | Tier 3 | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.6760 | 60070 | DRUM-GRASS VALLEY-WEIMAR | 2022 | 2022-01-02 21:41 | 44563.9035 | No | YES | No | 1899-12-31 15:49 | 2389 | 2022-01-04 13:30 | 44565.5625 | F | Tree | Tree-failure | COND | Relayed - 01/02/22, 2141 Drum-GV-Weimar 60kV (tier 2/3) relayed, tested NG; Weimar #1 momentarily de-energized & Alta & Ox Bow PHs separated; 2145 Drum to Alta PH tested OK via autos restoring Bonnie Nook & Alta PH; MOM Forest Hill (CEMO=1,358), Bonnie Nook (1,044) & Weimar (2,286); SUS Shady Glen (CESO=1,462; CMIN=71,708), Cape Horn & Rollins PH; weather clear; 2145 Drum to Alta PH tested OK via autos restoring Alta PH; 2214 Rollins to Weimar tested OK restoring Cape Horn, Shady Glen & Rollins PH; A-G fault 0.7 mi from Shady Glen toward Rollins PH near B16/372 or 3.0 mi from Shady Glen toward Weimar near 018/421, w/in 3 mi; 01/03/22 patrol finds ET-WD between poles 11/264-265 (Bonnie Nook to Cape Horn); 01/03/22, 1652 Grass Valley-Rollins PH returned to service after tree removed at 23/521, 23/522 & B21/482, ET-WD repaired at B21/466 & B21/469 between B21/468 & B21/469, B21/469 & B21/470, broken xarm replaced at B20/454 & poles B21/468, B21/469 replaced; 01/04/22, 1330 Bonnie Nook-Cape Horn returned to service | NONE | NORTH VALLEY AND SIERRA | INT-15591-1 | 8669 | 1462 | 71708 | 0.0004718 | 0.059249 | 125.58 | 5631636 | A-G | B016/372 | AUTO | Dependent Mode-initiating | Tier 3 | Nevada | Sierra | Data available upon request | Data available upon request | Drum-GV-Weimar, B21/469 | Clear | 2/0-7,CU | Data available upon request | YES | 441 WN (B)
2 | 2 | Non-HFTD | CENTRAL VALLEY | SOUTH | 69 | 70 | ETL.9350 | 70120 | GLASS-BIOLA-MADERA | 2022 | 2022-01-05 05:11 | 44566.216 | No | YES | No | 0.57222 | 824 | 2022-01-05 18:55 | 44566.7882 | F | External Contact | Ext Cont-car pole | STRU | Relayed - 01/05/22, 0511 Glass-Biola-Madera 70kV relayed, tested NG; SUS El Peco (CESO=1,156; CMIN=105,150) & Canadaigua Winery; MOM Bonita (CEMO=1,636) which auto-transferred to its alt source; fog; A-G fault 6 mi from Madera near 027/12A, +/-3 mi; 0633 Glass to Canandaigua Jct returned restoring Canandaigua; 0640 Madera to Biola returned restoring El Peco; 0805 to 1855 Bonita Jct to Trigo Jct cleared to repair ET-WD & BONITA-1102 under build wire down at 027/012A & replace 027/12A & 027/14 caused by car (tractor) pole; CAP 122552394 | 122552394 | CENTRAL VALLEY | INT-15599 | 2792 | 1156 | 105150 | 0.00020527 | 0.018671 | 90.9602 | 5631636 | A-G | 027/12A | AUTO | Single Mode | non-HFTD | Madera | Yosemite |  |  | GLASS-BIOLA-MADERA, 027/012A | Fog | 715.5-37,AAC |  | No | 482 WN (B)
3 | 3 | Tier 3 | SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | ETL.7380 | 60133 | LAURELES-OTTER | 2022 | 2022-01-21 19:54 | 44582.8292 | No | YES | No | 1900-01-08 19:53 | 14153 | 2022-01-31 15:47 | 44592.6576 | C | Disaster | Disaster-fire | STRU | Relayed - 01/21/22, 1954 Laureles-Otter 60kV (tier 2/3) relayed, did not test; SUS Otter (CESO=1,110; CMIN=2,044,884); weather clear; A-G fault 3 mi from Otter near 12/7, +/-3 mi; 'Colorado' fire is north of Otter & burning towards sub; Public Safety Specialist on scene coordinating w/ CAL FIRE which is restricting PG&E access due to fire-fighting efforts; 01/31/22, 1547 Laureles-Otter returned to service after replacing burnt poles 14/5, 14/7, 15/1-15/6 & repairing ET-WD at 14/6, restoring ET to Otter | NONE | SOUTH BAY AND CENTRAL COAST | INT-15624-2 | 1110 | 1110 | 2044884 | 0.0001971 | 0.36311 | 1842.2378 | 5631636 | A-G | 012/007 | AUTO | Single Mode | Tier 3 | Monterey | Central Coast |  |  | Laureles-Otter, 12/7 | Clear | 4/0-7,AAC |  | No | 432 WN (B)
4 | 4 | Non-HFTD | NORTH COAST | NORTH | 115 | 115 | ETL.3810 | 10315 | SONOMA-PUEBLO | 2022 | 2022-01-22 01:45 | 44583.0729 | No | YES | No | 0.44375 | 639 | 2022-01-22 12:24 | 44583.5167 | F | Tree | Tree-failure | COND | Relayed - 01/22/22, 0145 Sonoma-Pueblo 115kV (tier 2/3) relayed, tested NG; no customers interrupted; wind; C-A fault 2.5 mi from Sonoma near 2/10, +/-1 mi; 1224 Line returned to service after crew repaired one phase ET-WD between poles 2/4-5; per TL Supv eucalyptus failed from outside RoW | NONE | NORTH COAST | INT-15629 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | C-A | 002/004 | AUTO | Single Mode | non-HFTD | Sonoma | Sonoma |  |  | Sonoma-Pueblo, 2/4 | Wind | 397.5-19,AAC |  | No | 666 WN (B)
5 | 5 | Non-HFTD | NORTH COAST | NORTH | 69 | 60 | ETL.6890 | 60083 | FULTON-HOPLAND | 2022 | 2022-01-22 05:48 | 44583.2417 | No | YES | No | 0.45764 | 659 | 2022-01-22 16:47 | 44583.6993 | F | Equipment Failure | Equip Fail-conductor | COND | Relayed - 01/22/22, 0548 Fulton-Hopland 60kV (tier 2/3) relayed, tested NG; no customers interrupted; wind; B-C-G fault 6.5 mi from Fitch Mountain Jct toward Hopland near 16/0, +/-2 mi; 1047 Fitch Mountain Jct to Cloverdale Jct cleared to repair ET-WD between poles 14/11 & 15/0; 1/23/22, 1647 line returned to service after 2 phases of downed conductor repaired between poles 14/11 & 15/0 - the 2 phases dropped into Russian River crossing so crew took opportunity to replace the 3rd conductor as well | NONE | NORTH COAST | INT-15634 | 0 | 0 | 0 | 0 | 0 | 0 | 5631636 | B-C-G | 016/000 | AUTO | Single Mode | non-HFTD | Sonoma | Sonoma |  |  | Fulton-Hopland, 14/11 | Wind | 4/0-7,AAC |  | No | 443 WN (B)
6 | 6 | Non-HFTD | CENTRAL VALLEY | SOUTH | 69 | 70 | ETL.9210 | 70081 | TAFT-CUYAMA #2 | 2022 | 2022-01-22 12:14 | 44583.5097 | No | YES | No | 0.39097 | 563 | 2022-01-22 21:37 | 44583.9007 | F | Equipment Failure | Equip Fail-conductor | COND | Relayed - 01/22/22, 1214 Taft-Cuyama #2-70kV relayed, tested NG; SUS Cuyama #2-70/12kV transformer (CESO=295; CMIN=34,810); wind; A-B-C fault 9.5 mi from Taft near 9/86, +/-1 mi; 2137 line returned normal after ET-WD repaired between 10/91-92; sent to ATS for testing | NONE | CENTRAL VALLEY | INT-15636 | 295 | 295 | 34810 | 5.2383e-05 | 0.0061812 | 118 | 5631636 | A-B-C | 009/086 | AUTO | Single Mode | non-HFTD | San Luis Obispo | Kern |  |  | Taft-Cuyama #2, 010/091 | Wind | 2-7/1,ACSR |  | No | 329 WN (B)
7 | 7 | Non-HFTD | CENTRAL VALLEY | SOUTH | 69 | 70 | ETL.8851 | 70114 | MARICOPA-COPUS | 2022 | 2022-02-16 08:50 | 44608.3681 | No | YES | No | 0.39236 | 565 | 2022-02-16 18:15 | 44608.7604 | F | Equipment Failure | Equip Fail-conductor | COND | Relayed - 02/16/22, 0850 Maricopa-Copus 70kV relayed, did not test & Copus-Old River 70kV de-energized; SUS Gardner (CESO=1; CMIN=567), Maricopa-W (offline), Basic School, Pentland (1; 570), S-Kern & Copus (127; 2,032); 0856 Unable to test from Maricopa due to control fails; 0901 Copus-Old River returned to service restoring Copus & S-Kern; 0904 Maricopa-Copus manually tested NG & Copus-Old River de-energized due to phase imbalance; SUS Gardner, Maricopa-W, Basic School, Pentland; 0906 Coups-Old River returned to service; MOM Copus & S-Kern; A-C fault 1.5 mi from Maricopa near 1/26, +/-0.2 mi; 1815 Maricopa-Copus returned to service after ET-WD repaired at 1/31 restoring Gardner, Maricopa W, Basic School & Pentland; unknown cause, conductor broke 6"outside of a twist sleeve, sent to ATS for analysis | NONE | CENTRAL VALLEY | INT-15679-1 | 129 | 129 | 3169 | 2.2906e-05 | 0.00056271 | 24.5659 | 5631636 | A-C | 001/026 | AUTO | Dependent Mode-initiating | non-HFTD | Kern | Kern |  |  | Maricopa-Copus at 1/31 | Clear | 3/0-7,AAC |  | No | 381 WN (B)
8 | 8 | Non-HFTD | CENTRAL VALLEY | SOUTH | 115 | 115 | ETL.4200 | 10358 | WILSON-ORO LOMA | 2022 | 2022-03-02 21:31 | 44622.8965 | No | YES | No | 0.43681 | 629 | 2022-03-03 08:00 | 44623.3333 | F | External Contact | Ext Cont-car pole | COND | Relayed - 03/02/22, 2131 Wilson-Oro Loma 115kV relayed, tested NG; SUS El Nido (CESO=1,757; CMIN=250,802) & Teresina PV; weather clear; A-G fault 14 mi from Oro Loma near 025/009, +/- 3 mi; 2245 T-Man on site, pole 025/012 needs to be replaced due to car pole w/ ET-WD; 2352 Wilson to El Nido Jct energized restoring El Nido; 03/03/22, 0800 Wilson-Oro Loma (Oro Loma to El Nido) returned to service; CAP 123045935 | 123045935 | CENTRAL VALLEY | INT-15704 | 1757 | 1757 | 250802 | 0.00030958 | 0.044191 | 142.7445 | 5675418 | A-G | 025/009 | AUTO | Single Mode | non-HFTD | Fresno | Yosemite |  |  | Wilson-Oro Loma 025/012 | Clear | 397.5-19,AAC |  | No | 600 WN (B)
9 | 9 | Tier 2 | CENTRAL VALLEY | SOUTH | 69 | 70 | ETL.8440 | 70002 | ARCO-CHOLAME | 2022 | 2022-03-28 07:19 | 44648.3049 | No | YES | No | 0.33264 | 479 | 2022-03-28 15:18 | 44648.6375 | F | External Contact | Ext Cont-vandalism | COND | Relayed - 03/28/22, 0719 Arco-Cholame 70kV (tier 2/3) relayed, tested NG; SUS Devils Den (CESO=52; CMIN=624), Cholame (1,569; 398,376), Berrenda A (1; 12), Berrenda C & Antelope (170; 2,040); high winds, rain; 0731 Arco to Antelope manually tested OK restoring ET to Devils Den, Berrenda A, Berrenda C & Antelope; multi-terminal line, B-G fault near 011/116 or near 002/028 on Antelope Tap, +/-2 mi; 1315 ET restored to Cholame from alt source; 1518 Arco-Cholame normal after 1 span ET-WD replaced between poles 13/126-127; CAP 123204599 | 123204599 | CENTRAL VALLEY | INT-15748 | 1792 | 1792 | 401052 | 0.00031575 | 0.070665 | 223.8013 | 5675418 | B-G | 011/116 | AUTO | Single Mode | Tier 2 | Kern | Kern |  |  | Arco-Cholame 13/126 | Wind, rain | 3/0-7,AAC |  | No | 381 WN (B)
10 | 10 | Non-HFTD | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.6320 | 60021 | CENTERVILLE-TABLE MTN | 2022 | 2022-04-11 11:00 | 44662.4583 | No | YES | No | 0.73194 | 1054 | 2022-04-12 04:34 | 44663.1903 | F | Equipment Failure | Equip Fail-structure-line | STRU | Relayed - 04/11/22, 1100 Centerville-TM 60kV (tier 2/3) relayed, tested NG; Ameresco Cogen separated; no customers interrupted; lightning; 1319 Centerville-Durham Jct manually tested OK restoring Ameresco Cogen; 1540 TM-Durham Jct cleared to replace ET-WD & poles 11/187, 11/188 & 11/189 damaged by windstorm; 04/12/22, 0434 Centerville-TM returned to service | NONE | NORTH VALLEY AND SIERRA | INT-15793 | 1 | 0 | 0 | 0 | 0 | 0 | 5675418 | NA | NA | AUTO | Single Mode | non-HFTD | Butte | North Valley |  |  | Centerville-Table Mtn 11/187 | Lightning | 4/0-7,AAC |  | YES | 297 SN (N); 345 SE (A); 443 WN (B)
11 | 11 | Non-HFTD | BAY AREA | CENTRAL | 69 | 60 | ETL.7050 | 60100 | HERDLYN-BALFOUR | 2022 | 2022-04-27 02:15 | 44678.0938 | No | YES | No | 0.34722 | 500 | 2022-04-27 10:35 | 44678.441 | F | Equipment Failure | Equip Fail-connector/ hardware | COND | Relayed - 04/27/22, 0215 Herdlyn-Balfour 60kV relayed, tested NG; SUS Westside Irrigation, McDonald Island & Middle River (CESO=231; CMIN=111,317); weather clear; multi-terminal line, C-G fault 1.6 mi from Balfour near pole 09/191 or 2.8 mi from Middle River Jct toward Middle River near pole 002/053 or 0 mi from Bixler near pole 000/012, +/- 2 mi; 0501 Herdlyn to Balfour Jct manually tested OK restoring Westside Irrigation; Middle River Jct SW-7 opened isolating Middle River tap to repair failed connector & ET-WD between poles 3/74-75; 1035 Line returned normal; CAP 123440783 | 123440783 | BAY AREA | INT-15855 | 234 | 231 | 111317 | 4.0702e-05 | 0.019614 | 481.8918 | 5675418 | C-G | 002/053 | AUTO | Single Mode | non-HFTD | Contra Costa | Diablo |  |  | Middle River Tap 3/74 | Clear | 3-3,CU |  | No | 162 SN (N); 187 SE (A); 236 WN (B)
12 | 12 | Non-HFTD | BAY AREA | CENTRAL | 115 | 115 | ETL.3980 | 10474 | TESLA-SCHULTE SW STA #1 | 2022 | 2022-04-27 21:05 | 44678.8785 | No | YES | No | 1899-12-31 14:29 | 2309 | 2022-04-29 11:34 | 44680.4819 | F | Equipment Failure | Equip Fail-connector/ hardware | COND | Relayed - 04/27/22, 2105 Tesla-Schulte #1-115kV relayed, tested NG; SUS AEC (2); weather clear w/ high winds; C-A-G fault at or near AEC Site 300 2nd sub, +/-2 mi; fault location in vicinity of Corral fire which is ~5 acres in size, near AEC; 2344 AEC Site & AEC #2-115kV tap cleared to repair ET-WD near pole 2/5 of AEC SITE #2 Tap; 2355 Tesla to Schulte SW STA section manually tested OK & returned to service; Corral fire has been contained, but restoration delayed due to access problems & high winds; 04/29/22, 1134 Line returned to service after downed conductor repaired near pole 2/5 at AEC #2 tap; per T-SAFE meeting, installed shunt splices over new sleeves; also installed new armor rod and dampers; new high voltage signs installed as well | NONE | CENTRAL VALLEY | INT-15859 | 2 | 0 | 0 | 0 | 0 | 0 | 5675418 | C-A-G | AEC Site 300 2nd sub | AUTO | Single Mode | non-HFTD San Joaquin Stockton 4/0-NA,ALUM Lat: 37.66484, Long: -121.54136 | San Joaquin | Stockton |  |  | AEC SITE #2 Tap pole 2/5 | Clear, winds | 4/0-NA,ALUM |  | No | 297 SN (N); 345 SE (A); 443 WN (B)
13 | 13 | Non-HFTD | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.8426 | 60408 | PEACHTON-PEASE | 2022 | 2022-04-29 04:05 | 44680.1701 | No | YES | No | 0.35 | 504 | 2022-04-29 12:29 | 44680.5201 | F | External Contact | Ext Cont-car pole | COND | Relayed - 04/29/22, 0405 Peachton-Pease 60kV relayed, tested NG; 0409 Peachton-Encinal manually tested OK; MOM Gridley & Live Oak (CEMO=4,573); SUS Encinal; weather clear; Encinal-Pease remains out; B-C-G fault 5.96 mi from Pease (Encinal Tap) near 000/005, +/-1 mi; 0616 Encinal SW-65 opened isolating car pole w/ ET-WD between 0/5-6; 0631 Peachton-Pease restored; 1229 Encinal tap returned to service, restoring Encinal after crew repaired downed conductors between poles 0/5-6 damaged by car | NONE | NORTH VALLEY AND SIERRA | INT-15861 | 4573 | 0 | 0 | 0 | 0 | 0 | 5675418 | B-C-G | 000/005 | AUTO | Single Mode | non-HFTD San Joaquin Stockton 4/0-NA,ALUM Lat: 37.66484, Long: -121.54136 | Sutter | Sierra |  |  | Encinal tap 0/5 | Clear | 4-7,CU |  | YES | 137 SN (N); 157 SE (A); 198 WN (B)
14 | 14 | Non-HFTD | CENTRAL VALLEY | CENTRAL | 69 | 60 | ETL.7870 | 60186 | SALADO-NEWMAN #2 | 2022 | 2022-05-04 00:12 | 44685.0083 | No | YES | No | 0.78125 | 1125 | 2022-05-04 18:57 | 44685.7896 | F | External Contact | Ext Cont-car pole | COND | Relayed - 05/04/22, 0012 Salado-Newman #2-60kV relayed, tested NG; MOM Crows Landing (CEMO=278); weather clear; C-G & B-C fault 0 mi from Patterson JCT near 31/584, +/-1 mi; confirmed car pole at 31/578; 0420 Salado to Patterson restored; 0422 Newman to Patterson JCT restored; 1857 Patterson Jct section returned to service after crew repaired 3 phases of ET-WD & replaced pole 31/578 damaged by car | NONE | CENTRAL VALLEY | INT-15873 | 278 | 0 | 0 | 0 | 0 | 0 | 5675418 | C-G | 031/584 | AUTO | Single Mode | non-HFTD | Stanislaus | Yosemite |  |  | Salado-Newman #2 31/578 | Clear | 397.5-19,AAC |  | No | 343 SN (N); 399 SE (A); 514 WN (B)
15 | 15 | Non-HFTD | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.6920 | 60087 | GLENN #1 | 2022 | 2022-05-06 23:47 | 44687.991 | No | YES | No | 0.68333 | 984 | 2022-05-07 16:11 | 44688.6743 | F | External Contact | Ext Cont-car pole | COND | Relayed - 05/06/22, 2347 Glenn #1-60kV relayed, tested NG; on the trouble Elk Creek 6kV tap de-energized & Stoney Gorge separated; SUS Willow A (CESO=3,224; CMIN=116,064) & Elk Creek (900; 96,150); weather clear; 2356 Glenn to Willow A manually tested NG; 2358 Glenn to Elk Creek Jct 29 manually tested NG; 05/07/22, 0015 Glenn to Elk Creek Jct 27 manually tested NG; 0026 Elk Creek Jct to Willow A energized OK restoring Willow A from alt source; 0029 Elk Creek tap manually tested OK per EPSS procedure restoring Elk Creek; B-C-G fault 13.7 mi from Glenn near 14/280, +/-1 mi; 0334 to 1611 Glenn to Elk Creek Jct cleared to replace pole 14/283 & ET-WD damaged by car | NONE | NORTH VALLEY AND SIERRA | INT-15879 | 4124 | 4124 | 212214 | 0.00072664 | 0.037392 | 51.4583 | 5675418 | B-C-G | 014/280 | AUTO | Single Mode | non-HFTD | Glenn | North Valley |  |  | Glenn #1 14/283 | Clear | 2/0-7,CU |  | No | 631 SN (N); 742 SE (A); 972 WN (B)
16 | 16 | Non-HFTD | CENTRAL VALLEY | SOUTH | 115 | 115 | ETL.3640 | 10298 | SEMITROPIC-MIDWAY #2 | 2022 | 2022-05-25 14:05 | 44706.5868 | No | YES | No | 0.51736 | 745 | 2022-05-26 02:30 | 44707.1042 | F | External Contact | Ext Cont-car pole | STRU | Relayed - 05/25/22, 1405 Semitropic-Midway #2-115kV relayed, tested NG due to car pole at 0/9 & 0/10; SUS Goose Lake (CESO=740; CMIN=203,500), Goose Lake PV, Wildwood Solar & Semitropic Storage; Semitropic Water District Cogen, Goose Lake PV & Wildwood Solar separated on the trouble; weather clear; A-G evolved to A-B-C fault after NG test 0.68 mi from Semitropic toward Wildwood Solar near 0/9 or on section of line owned by Semitropic Storage Water District, +/-1 mi; 1654 Semitropic to Semitropic H2O District returned to service restoring Semitropic H2O District; 05/26/22, 0230 Semitropic-Midway #2 returned to service after structures 0/9 & 0/10 and associated ET-WD replaced; ET restored to Goose Lake, Goose Lake PV & Wildwood Solar; CAP 123695976 | 123695976 | CENTRAL VALLEY | INT-15938 | 743 | 740 | 203500 | 0.00013039 | 0.035856 | 275 | 5675418 | A-B-C | 000/009 | AUTO | Single Mode | non-HFTD | Kern | Kern |  |  | Semitropic-Midway #2 at 0/9 | Clear | 266.8-7,AAC |  | No | 343 SN (N); 399 SE (A); 514 WN (B)
17 | 17 | Non-HFTD | CENTRAL VALLEY | CENTRAL | 69 | 60 | ETL.8140 | 60214 | STOCKTON A-WEBER #3 | 2022 | 2022-05-25 17:48 | 44706.7417 | No | YES | No | 0.18889 | 272 | 2022-05-25 22:20 | 44706.9306 | F | Equipment Failure | Equip Fail-connector/ hardware | COND | Relayed - 05/25/22, 1748 Stockton A-Weber #3-60kV relayed, tested OK; MOM Mormon, E-Stockton, West Lane, Oak Park & Sumiden; Weber-Mormon Jct 60kV (Mormon Jct-Linden) de-energized; weather clear; 1749 Line again relayed, but tested NG; SUS Mormon (CESO=4,194; CMIN=331,242), E-Stockton (5,507; 345,125), West Lane (6,114; 1,984,858), Oak Park (550; 31,900) & Sumiden; Weber-Mormon Jct 60kV (Mormon Jct-Linden) de-energized; 1847 Stockton A-Weber #3 (Weber-Oak Park Jct) manually tested OK restoring Weber-Mormon Jct, Mormon, E-Stockton, Oak Park & Sumiden; 2051 to 2220 Oak Park Jct-West Lane cleared to replace NG connector & 1 span ET-WD between B3/94-95 restoring West Lane | NONE | CENTRAL VALLEY | INT-15940 | 16366 | 16365 | 2693125 | 0.0028835 | 0.47452 | 164.5661 | 5675418 | A-G | 005/033 | AUTO | Single Mode | non-HFTD | San Joaquin | Stockton |  |  | Stockton A-Weber #3 betw B3/94-95 | Clear | 715.5-37,AAC |  | No | 631 SN (N); 742 SE (A); 972 WN (B)
18 | 18 | Non-HFTD | CENTRAL VALLEY | SOUTH | 69 | 70 | ETL.8440 | 70002 | ARCO-CHOLAME | 2022 | 2022-05-29 05:00 | 44710.2083 | No | YES | No | 0.58681 | 845 | 2022-05-29 19:05 | 44710.7951 | F | Equipment Failure | Equip Fail-conductor | COND | Forced - 05/29/22, 0500 Arco-Cholame-70kV forced out to open jumpers at dead on Berrenda C tap at pole 001/026 to repair 1 phase of ET-WD on line side of Berrenda C SW-75; SUS Devils Den (CESO=118; CMIN=1,534), Antelope (100; 1,300), Cholame (1,572; 23,580), Berrenda A & Berrenda C; 0518 Line returned to service restoring Devils Den, Antelope, Cholame & Berrenda A; 1905 Berrenda C tap returned to service restoring Berrenda C | NONE | CENTRAL VALLEY | T22-010653 | 1790 | 1790 | 26414 | 0.0003154 | 0.0046541 | 14.7564 | 5675418 | NA | NA | EFO | Emergency Forced Outage | non-HFTD | Kern | Kern |  |  | Berrenda C Tap pole 1/26 | Clear | 4/0-7,AAC |  | No | 297 SN (N); 345 SE (A); 443 WN (B)
19 | 19 | Non-HFTD | CENTRAL VALLEY | SOUTH | 69 | 70 | ETL.9020 | 70062 | ORO LOMA-CANAL #1 | 2022 | 2022-06-01 16:19 | 44713.6799 | No | YES | No | 0.47708 | 687 | 2022-06-02 03:46 | 44714.1569 | F | External Contact | Ext Cont-car pole | STRU | Relayed - 06/01/22, 1619 Oro Loma-Canal #1-70kV relayed, Oro Loma-Santa Rita tested NG & Santa Rita-Canal tested OK; MOM Santa Rita (CEMO=932); SUS Dos Palos (CESO=2,437; CMIN=320,481); weather clear; 1640 Oro Loma-Dos Palos manually tested OK restoring Dos Palos after isolating reported car pole; A-B fault 9.76 mi from Oro Loma near 11/03, +/-3 mi; one phase ET-WD & broke & 3-12kV phases on ground; HAWC reported small 20'x20' fire that's been extinguished (Elgin Incident #2CA011840); 1954 Dos Palos-Santa Rita cleared to replace pole 11/15 damaged by car; 06/02/22, 0346 Line returned to service; CAP 123737145 | 123737145 | CENTRAL VALLEY | INT-15955 | 3369 | 2437 | 320481 | 0.0004294 | 0.056468 | 131.5064 | 5675418 | A-B | 011/003 | AUTO | Single Mode | non-HFTD | Merced | Yosemite |  |  | Oro Loma-Canal #1 11/15 | Clear | 3/0-7,AAC |  | No | 257 SN (N); 298 SE (A); 381 WN (B); 407 WE ( C)
20 | 20 | Tier 3 | NORTH COAST | NORTH | 115 | 115 | ETL.4392 | 10445 | EAGLE ROCK-FULTON-SILVERADO | 2022 | 2022-06-16 05:24 | 44728.225 | No | YES | YES | 0.59306 | 854 | 2022-06-16 19:38 | 44728.8181 | F | Equipment Failure | Equip Fail-conductor | COND | Relayed - 06/16/22, 0524 Eagle Rock-Fulton-Silverado 115kV (tier 2/3) relayed, did not test, auto reclosing c/out for wildfire risk; on the trouble Silverado-Fulton Jct 115kV de-energized (tier 2/3, EPSS line); MOM Rincon (CEMO=14,656) & Silverado (8,421); SUS to Monticello (CESO=1,442; CMIN=172,697) & Monticello PH (offline); weather clear; B-G fault 2.75 mi from Eagle Rock near 003/017, +/-2 mi; 0656 Silverado-Fulton Jct returned to service restoring Monticello & Monticello PH (offline); 1105 to 1938 ER-Fulton-Silverado cleared to repair 1 phase ET-WD between towers 3/16-16B | NONE | NORTH COAST | INT-16006 | 24520 | 1442 | 172697 | 0.00025408 | 0.030429 | 119.7621 | 5675418 | B-G | 003/017 | AUTO | Dependent Mode-initiating | Tier 3 | Sonoma | Humboldt |  |  | Eagle Rock-Fulton-Silverado 3/16 | Clear | 1113-61,AAC |  | No | 825 SN (N); 975 SE (A); 1287 WN (B); 1378 WE ( C)
21 | 21 | Non-HFTD | CENTRAL VALLEY | SOUTH | 115 | 115 | ETL.1890 | 10115 | KERCKHOFF-CLOVIS-SANGER #1 | 2022 | 2022-06-22 07:08 | 44734.2972 | No | YES | YES | 0.99444 | 1432 | 2022-06-23 07:00 | 44735.2917 | F | Equipment Failure | Equip Fail-structure-line | STRU | Relayed - 06/22/22, 0708 Kerckhoff-Clovis-Sanger #1-115kV (tier 2/3) relayed, did not test, auto reclosing c/out for wildfire risk; MOM Clovis #1-115/12kV xfmr (CEMO=7,263); lightning; FIA R4, full line patrol required; C-G evolving to B-C-G fault near C1/8 or 15/1, +/-2 mi; 0959 Woodward Jct-Clovis Jct cleared to replace 14 down poles due to high winds & lightning between 13/5 & 15/7 w/ steel poles; ET-WD (all 3-715 Al phases hit ground & all 3 broke, reconductored multiple phases on PM 31606829); 1302 Clovis-Sanger manually tested OK following full patrol w/ no other trouble found; 1318 Kerckhoff-Shepherd manually tested OK following full patrol w/ no other trouble found; grass fire (40 acres) no 3rd party damage at pole 15/2; 06/23/22, 0700 Kerckhoff-Clovis-Sanger #1 returned to service; CAP 123900762 | 123900762 | CENTRAL VALLEY | INT-16024 | 7263 | 0 | 0 | 0 | 0 | 0 | 5675418 | B-C-G | 015/001 | AUTO | Single Mode | non-HFTD | Fresno | Fresno |  |  | Kerckhoff-Clovis-Sanger #1 15/2 | Winds, lightning | 715.5-37,AAC |  | YES | 631 SN (N); 742 SE (A); 972 WN (B); 1039 WE ( C)
22 | 22 | Tier 2 | CENTRAL VALLEY | CENTRAL | 69 | 60 | ETL.8350 | 60236 | WEST POINT-VALLEY SPRINGS | 2022 | 2022-07-04 18:39 | 44746.7771 | No | YES | No | 1900-01-04 00:22 | 7222 | 2022-07-09 19:01 | 44751.7924 | C | Disaster | Disaster-fire | STRU | Forced - 07/04/22, 1839 West Pt-Valley Springs open ended at VS, reports of multiple Electra fire-damaged poles; on trouble West Pt PH island created; 1842 West Pt PH manually tripped terminating West Pt island & de-energizing WP-VS; SUS Electra, Pine Grove & West Pt; 07/05/22, 2209 West Pt PH island established; 07/07/22, 0943 Electra Jct-Valley Springs cleared to replace pole 10/127 & ET-WD; 0943 Valley Springs to Valley Springs SW-27 energized per CAL FIRE approval after full line patrol, no trouble found; 0944 West Pt-Electra Jct cleared to replace burnt poles 10/120, 9/112, 9/116, 9/117; 1737 Valley Springs to Valley Springs SW-27 de-energized to operate line switches dead; 1829 after CAL FIRE approval Valley Springs-Electra manually tested OK restoring Electra after pole 10/127 & ET-WD replaced; 07/09/22, 1851 Electra Jct to West Pt returned restoring Pine Grove; 1901 West Pt island synched terminating island | NONE | CENTRAL VALLEY | T22-012463 | 2838 | 2838 | 2282222 | 0.00050005 | 0.40212 | 804.1656 | 5675418 | NA | NA | EFO | Emergency Forced Outage | Tier 2 | Calaveras | Stockton |  |  | West Point-Valley Springs 10/127 | Fire (Electra) | 266.8-26/7,ACAR |  |  |  | SN (N) 384; SE (A) 438; WN (B) 551; WE (C) 585
23 | 23 | Non-HFTD | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.6740 | 60067 | DIXON-VACA #2 | 2022 | 2022-08-11 11:01 | 44784.459 | No | YES | No | 0.40486 | 583 | 2022-08-11 20:44 | 44784.8639 | F | Equipment Failure | Equip Fail-conductor | COND | Forced - 08/11/22, 1101 to 2044 Dixon-Vaca #2-60kV (Dixon JCT to Dixon Canning) forced out to replace one phase of ET-WD between poles 16/353-354; conductor down on under build Dixon 1107 at light duty steel pole 16/354; no customers interrupted | NONE | NORTH VALLEY AND SIERRA | T22-014359 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | NA | NA | EFO | Emergency Forced Outage | Non-HFTD | Solano | Sacramento |  |  | Dixon-Vaca #2 pole 16/353 | Clear | 2/0-7,CU |  |  |  | SN (N) 631; SE (A) 742; WN (B) 972; WE (C) 1039
24 | 24 | Non-HFTD | CENTRAL VALLEY | SOUTH | 69 | 70 | ETL.8550 | 70113 | CARUTHERS-LEMOORE NAS-CAMDEN | 2022 | 2022-08-26 01:59 | 44799.0826 | No | YES | No | 0.39167 | 564 | 2022-08-26 11:23 | 44799.4743 | F | Equipment Failure | Equip Fail-conductor | COND | Forced - 08/26/22, 0159 Caruthers-Lemoore NAS-Camden 70kV forced out due to single phasing condition; no customers interrupted; 1123 Line returned to service after 1 phase ET-WD (1/0 solid Cu) on ground & broke at the shoe that also got into Henrietta-1110 (CESO=312) under build at pole :053/015 & ignited small fire was repaired; crew installed vibration dampeners on LC 124374095; CAP 124385959 | 124385959 | CENTRAL VALLEY | T22-014943 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | NA | NA | EFO | Emergency Forced Outage | Non-HFTD | Kings | Fresno |  |  | Caruthers-Lemoore NAS-Camden :053/015 | Clear | 1/0-7,CU |  |  |  | SN (N) 243; SE (A) 282; WN (B) 358; WE (C) 382
25 | 25 | Tier 3 | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.7560 | 60152 | WEIMAR #1 | 2022 | 2022-08-26 07:25 | 44799.309 | No | YES | YES | 1900-01-01 07:29 | 3329 | 2022-08-28 14:54 | 44801.6208 | F | Equipment Failure | Equip Fail-conductor | COND | Relayed - 08/26/22, 0725 Middle Fork #1 & Weimar #1-60kV relayed, did not test during routine switching; automatic reclosing c/out for wildfire risk mitigation; SUS Forrest Hill (CESO=2,699; CMIN=1,113,268) & Oxbow PH; weather clear; A-C fault 7 mi from Weimar toward Forrest Hill near 007/108, +/-2 mi; <1 acre fire extinguished & repairs to 1 phase ET-WD & damage to other 2 phases between 007/105-106 to be completed under original clearance; patrol completed on Weimar #1 (Forrest Hill to Oxbow PH Jct) & Middle Fork #1, no further trouble found; waiting on NCPA to check CB status at Middle Fork & test the line; 1214 Weimar #1 (Forrest Hill Jct- Oxbow PH Jct) & Middle Fork #1 tested OK restoring Oxbow PH & ET to Forrest Hill; scheduled return of Weimar-Forrest Hill Jct=08/28; 08/28/22, 1454 Weimar #1 returned to service after crew inserted shunt splices & replaced 3 phases of conductor between poles 007/105-106 | NONE | NORTH VALLEY AND SIERRA | INT-16177 | 2699 | 2699 | 1113268 | 0.00047556 | 0.19616 | 412.4742 | 5675418 | A-C | 007/108 | AUTO | Dependent Mode-initiating | Tier 3 | Placer | Sierra |  |  | Weimar #1 between 007/105-106 | Clear | 2-7/1,ACSR |  |  |  | SN (N) 157; SE (A) 176; WN (B) 220; WE (C) 232
26 | 26 | Non-HFTD | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.6930 | 60088 | GLENN #2 | 2022 | 2022-09-18 05:09 | 44822.2146 | No | YES | No | 0.98264 | 1415 | 2022-09-19 04:44 | 44823.1972 | F | Equipment Failure | Equip Fail-structure-line | STRU | Relayed - 09/18/22, 0509 Glenn #2-60kV relayed, tested NG; SUS Hamilton "A" (CESO=1,149; CMIN=543,216), Jacinto (952; 421,077) & Rice (1,274; 400,036); rain; B-G fault 7.7 mi from Glenn near 007/136, +/-2 mi; field report structure 7/148 on fire; shared structure for both Glenn #2 & #3; Fire Dept on site 1013 Rice restored via alt source; 1229 Jacinto to Rice manually tested OK restoring Jacinto; 1332 Hamilton "A" to Jacinto manually tested OK restoring Hamilton A; 09/19/22 0444 Glenn #2 (Glenn to Hamilton A) returned to service after crew replaced pole 7/148 | NONE | NORTH VALLEY AND SIERRA | INT-16231 | 3375 | 3375 | 1364329 | 0.00059467 | 0.24039 | 404.2456 | 5675418 | B-G | 007/136 | AUTO | Single Mode | Non-HFTD | Glenn | North Valley |  |  | Glenn #2 pole 007/148 | Rain | TBD
27 | 27 | Non-HFTD | SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | ETL.8010 | 60201 | SOLEDAD #1 | 2022 | 2022-09-27 22:39 | 44831.9437 | No | YES | No | 0.82361 | 1186 | 2022-09-28 18:25 | 44832.7674 | F | External Contact | Ext Cont-car pole | STRU | Relayed - 09/27/22, 2239 Soledad #1-60kV relayed, tested NG; SUS Gonzales (CESO=2,702; CMIN=54,903); weather clear; 2246 Gonzales transferred to alt source restoring all customers; A-B-C fault 15.4 mi from Soledad near 014/278, +/-3 mi; 09/28/22, 0006 Soledad #1 energized restoring Gonzales back to normal power source; 09/28/22, 0550 to 1825 9th Street JCT to Spence JCT cleared for crew to replace pole 11/218 & 3 spans of ET wire down damaged by car | NONE | SOUTH BAY AND CENTRAL COAST | INT-16258 | 2702 | 2702 | 54903 | 0.00047609 | 0.0096738 | 20.3194 | 5675418 | A-B-C | 014/278 | AUTO | Single Mode | Non-HFTD | Monterey | Central Coast |  |  | Soledad #1 011/218 | Clear | 397.5-19,AAC |  |  |  | SN (N) 488; SE (A) 554; WN (B) 666; WE (C) 711
28 | 28 | Tier 2 | NORTH COAST | NORTH | 69 | 60 | ETL.2060 | 60389 | FORT BRAGG-ELK | 2022 | 2022-11-01 08:18 | 44866.3458 | No | YES | YES | 1899-12-31 06:24 | 384 | 2022-11-02 14:42 | 44867.6125 | F | Weather | Weather-rain | COND | Relayed – 11/01/22, 0818 Fort Bragg-Elk 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. On the trouble. Big River 60kV SVC tripped. SUS Big River (CESO=2,624; CMIN=39,360). Weather rain. Line is in tier 2/3 HFTD. Protection reports B-G fault near structure 005/001. 0829 Fort Bragg to Big River section manually tested OK restoring Big River. 1241 Elk to Big River section cleared for crew to repair one phase of downed conductor between structures 005/001 and 005/002. Estimated return 11/02/22. INT-16321. 11/02/22, 1442 Fort Bragg-Elk 60kV line (Elk to Big River section) returned to service after crew repaired downed conductor between structures 5/1 and 5/2. Line Patrol found no other trouble. From trouble on 11/01/22 at 0818. | NONE | NORTH COAST | INT-16321 | 2624 | 2624 | 39360 | 0.00046234 | 0.0069352 | 15 | 5675418 | B-G | 005/001 | AUTO | Single Mode | Tier 2 | Mendocino | Humboldt |  |  | Conductor between 005/001 & 005/002 | Rain | 397.5 AAC |  |  |  | SN (N) 488; SE (A) 554; WN (B) 666; WE (C) 711
29 | 29 | Tier 2 | NORTH COAST | NORTH | 115 | 115 | ETL.1820 | 10104 | HUMBOLDT-TRINITY | 2022 | 2022-11-01 10:24 | 44866.4333 | No | YES | YES | 0.69306 | 998 | 2022-11-02 03:02 | 44867.1264 | F | Weather | Weather-rain | COND | Relayed – 11/01/22, 1024 Humboldt-Trinity 115kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. No customer interruption. Weather rain. Line is in tier 2/3 HFTD. Protection reports C-G fault near structure 073/006. 1646 Line cleared for crew to repair one phase of downed conductor between towers 73/3 and 73/2AA. Estimated return 11/02/22. INT-16322. 11/02/22, 0302 Humboldt-Trinity 115kV line returned to servicer after crew repaired one phase of downed conductor between towers 73/3 and 73/2AA. From trouble on 11/01/22 at 1024. | NONE | NORTH COAST | INT-16322 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | C-G | 073/006 | AUTO | Single Mode | Tier 2 | Trinity | Humboldt |  |  | Conductor between 073/003 & 073/002AA | Rain | 336.4 ACSR |  |  |  | SN (N) 490; SE (A) 547; WN (B) 647; WE (C) 687
30 | 30 | Non-HFTD | CENTRAL VALLEY | CENTRAL | 69 | 70 | ETL.8700 | 70029 | GATES-TULARE LAKE | 2022 | 2022-11-07 12:33 | 44872.5229 | No | YES | No | 0.81736 | 1177 | 2022-11-08 08:10 | 44873.3403 | F | Contamination | Cntmn-animal waste | STRU | Relayed – 11/07/22, 1233 Gates-Tulare Lake 70kV line relayed and tested NG. On the trouble, Sand Drag, Sun City and Avenal Park separated. SUS Kettleman Hills, Cheveron Kettleman and Avenal. Weather rain. Line is not in a tier 2/3 HFTD. Protection reports ABCG fault near structure 007/001. 1638 Avenal 70kV tap isolated for crew to repair three phases of downed conductor and replace NG pole 1/9 due to pole fire. T-man went ot the hazard and found pole 1/9 burnt off at the 12kV level with birds nest. 1705 Gates to Tulare Lake 70kV line manually tested OK restoring transmission service to Kettleman Hills and Chevron Kettleman. Estimated return 11/08/22. INT-16338. 11/08/22, 0810 Avenal 70kV tap returned to service, restoring transmission service to Avenal, Avenal Park (offline), Sun City (offline) and Sand Drag (offline) after crew replaced NG pole 1/9 and repaired downed conductors. From trouble on 11/07/22 at 1233. | 124846355 | CENTRAL VALLEY | INT-16338 | 3141 | 3141 | 1054042 | 0.00055344 | 0.18572 | 335.5753 | 5675418 | A-B-C-G | 007/001 | AUTO | Single Mode | Non-HFTD | Fresno | Fresno |  |  | Gates-Tulare Lake STR 001/009 (12kV level) | Rain | 4/0 AAC |  |  |  | SN (N) 297; SE (A) 345; WN (B) 443; WE (C) 473
31 | 31 | Non-HFTD | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.6590 | 60051 | CORTINA #2 | 2022 | 2022-11-14 05:34 | 44879.2319 | No | YES | No | 0.4625 | 666 | 2022-11-14 16:40 | 44879.6944 | F | Equipment Failure | Equip Fail-conductor | NONE | Relayed – 11/14/22, 0534 Cortina #2-60kV line relayed and tested NG. SUS Wilkins Slough, El Dorado Pumping STA and Rough & Ready Pumping STA. Weather clear. Line is not in a tier 2/3 HFTD. Protection initially provided a fault location estimate of an AG fault near structure 25/453. This area was patrolled with no trouble found. 0853 Line manually tested NG. Then protection provided a revised fault estimate of an AG fault near structure 25/453, 000/012 (3 terminal line). 1047 District 2047 to Wilkins Slough line section manually tested OK, restoring El Dorado Pumping STA, Rough & Ready Pumping STA and Wilkins Slough. 1321 Arbuckle JCT to Wilkins Slough JCT section cleared to repair 1 phase of down conductor between pole 016/285 and 016/286. According to t-line supervisor, no evidence of animal/vegetation was found. The wire had a few strands that were broken for a while, the last melted and fell. 1640 Line returned to service. INT-16353 | NONE | NORTH VALLEY AND SIERRA | INT-16353 | 653 | 653 | 120190 | 0.00011506 | 0.021177 | 184.0582 | 5675418 | A-G | 25/453, 000/012 (3 terminal line) | AUTO | Single Mode | Non-HFTD | Colusa | Sacramento |  |  | Cortina #2 Between STR 016/285 and 016/286 | Clear | 2 STR CU |  |  |  | SN (N) 183; SE (A) 211; WN (B) 266; WE (C) 284
32 | 32 | Non-HFTD | CENTRAL VALLEY | CENTRAL | 69 | 70 | ETL.8540 | 70110 | CARNERAS-TAFT | 2022 | 2022-12-11 05:36 | 44906.2333 | No | YES | No | 0.42639 | 614 | 2022-12-11 15:50 | 44906.6597 | F | Equipment Failure | Equip Fail-structure-line | STRU | Relayed – 12/11/22, 0536 Carneras-Taft 70kV line relayed and tested NG. SUS Celeron (1), McKittrick (CESO=154;CMIN=53,592) and Midway Pipeline South (1). Weather rain. Line is not in a tier 2/3 HFTD. Protection reports A-B-C fault near structure 020/324. 1127 Carneras to Temblor JCT section energized, restoring Celeron. 1128 Taft to CRI JCT section energized, restoring McKittrick and Midway Pipeline South. 1104 Temblor JCT to CRI JCT section cleared to replace pole 020/315. 1550 Line returned to service normal. INT-16433 | 125011678 | CENTRAL VALLEY | INT-16433 | 154 | 154 | 53592 | 2.7135e-05 | 0.0094428 | 348 | 5675418 | A-B-C | 020/324 | AUTO | Single Mode | Non-HFTD | Kern | Kern |  |  | Carneras-Taft STR 020/315 | Storm | 3/0 AAC |  |  |  | SN (N) 257; SE (A) 298; WN (B) 381; WE (C) 407
33 | 33 | Non-HFTD | CENTRAL VALLEY | CENTRAL | 69 | 70 | ETL.8460 | 70004 | ARCO-TULARE LAKE | 2022 | 2022-12-18 14:43 | 44913.6132 | No | YES | No | 0.40347 | 581 | 2022-12-19 00:24 | 44914.0167 | F | Weather | Weather-rain | COND | Relayed – 12/18/22, 1443 Arco-Tulare Lake 70kV line relayed and tested NG. SUS Lost Hills, Badger Hill and Las Perillas. Weather clear. Line is not in a tier 2/3 HFTD. Protection reports C-G fault near structure 008/125. 1642 Arco to Las Perillas JCT section manually tested OK, restoring Lost Hills, Badger Hill and Las Perillas after line patrol found no trouble. 1807 Tulare Lake to Las Perillas JCT section cleared for crew to repair two phases of conductors (only one phase on ground) between towers 008/125 and 008/126. Unknown cause. Estimated return 12/19/22. INT-16450 12/19/22, 0024 Arco-Tulare Lake 70kV line (Tulare Lake to Las Perillas JCT section) returned to service after crew repaired one phase of downed conductor between towers 008/125 and 008/126. From trouble on 12/18/22 at 1443. | 125109380 | CENTRAL VALLEY | INT-16450 | 2 | 0 | 0 | 0 | 0 | 0 | 5675418 | C-G | 008/125 | AUTO | Single Mode | Non-HFTD | Kings | Fresno |  |  | Arco-Tulare Lake STR 008/125 | Clear | 3/0 AAC |  |  |  | SN (N) 257; SE (A) 298; WN (B) 381; WE (C) 407
34 | 34 | Tier 2 | NORTH COAST | NORTH | 69 | 60 | ETL.2060 | 60389 | FORT BRAGG-ELK | 2022 | 2022-12-26 22:41 | 44921.9451 | No | YES | No | 0.78472 | 1130 | 2022-12-27 17:31 | 44922.7299 | F | Tree | Tree-failure | COND | Relayed – 12/26/22, 2241 Fort Bragg-Elk 60kV line relayed and tested NG. SUS Big River(CESO=1,923;CMIN=271,143). Weather storm. Line is in tier 2/3 HFTD. 2259 Elk to Big River section manually tested OK restoring Big River. Protection reports A-C fault near STR 019/012. INT-16471. 12/27/22, 1731 Fort Bragg-Elk 60kV line (Fort Bragg to Big River JCT section) returned to service after crew repaired two phased of downed conductor between poles 20/16 and 21/1. Caused by tree falling into line From trouble on 12/26/22 at 2241. | NONE | NORTH COAST | INT-16471 | 1923 | 1923 | 271143 | 2.9449 | 415.2266 | 141 | 5675418 | A-C | 019/012 | AUTO | Single Mode | Tier 2 | Mendocino | Humboldt |  |  | Fort Bragg-Elk STR 020/016 | Storm | 397.5 AAC |  |  |  | SN (N) 488; SE (A) 554; WN (B) 666; WE (C) 711
35 | 35 | Non-HFTD | NORTH VALLEY AND SIERRA | NORTH | 115 | 115 | ETL.1140 | 10021 | BRIGHTON-DAVIS | 2022 | 2022-12-31 21:15 | 44926.8854 | YES | YES | No | 0.29375 | 423 | 2023-01-01 04:18 | 44927.1792 | F | Tree | Tree-failure | COND | Forced – 12/31/22, 2115 Brighton-Davis 115kV Line forced out of service due to single phasing condition. Estimated return 01/01/23. 1/1/23, 0418 Brighton-Davis 115kV line returned to service after crew repaired NG cross arm at structure 7/60 and NG cage top at structure 8/61. Caused by tree falling into line. T22-018515 | NONE | NORTH VALLEY AND SIERRA | T22-018515 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | A-G | 006/053 | AUTO | Single Mode | Non-HFTD | Sacramento | Sacramento |  |  | Brighton-Davis STR 007/059 | Storm | 715 AAC |  |  |  | SN (N) 631; SE (A) 742; WN (B) 972; WE (C) 1039
*Note: data puled from the Transmission Outage Database on July 16, 2025
Formulas:
Durn (hr:min) = [Date In]-[Date Out]

## 3.4 WD non-MED HFTD
kV Cls | kV | SAP FL | LINE NO | FACILITY NAME | YEAR | Date Out | Time Out | MED | ET Wire Down | Auto Reclose Disabled | Durn (hr:min) | Durn (mins) | Date In | Time In | Out Cls | Cause Category | Cause Detail | Secondary Cause | Comments | CAP | REGION | TOTL | Customers Affected | CESO Event | CMIN Event | SAIFI Contr | SAIDI Contr | CAIDI | System Customer Count | Fault Type | Fault Estimate | AUTO EFO SCHD | Outage Mode | HFTD | County | Division | LAT | LONG | Actual Location | Weather | Conductor | ETGIS Location | BS GS SD
69 | 60 | ETL.8060 | 60206 | SPAULDING-SUMMIT | 2025 | 2025-02-04 11:26 | 45692.4764 | No | YES | No | 0.21736 | 313 | 2025-02-04 16:39 | 45692.6937 | F | Weather | Weather-snow/ ice | COND | Relayed - 2/4/2025, 1126 Spaulding-Summit 60kV line relayed and tested NG. Sustained interruption to Cisco Grove, Tamarack, Summit and Summit Metering STA. Weather storm. 1129 Spaulding to Summit section tested NG. Crew found one phase of downed conductor between poles 000/007 and 000/008 on the Cisco Grove 60kV Tap. Restoration switching in progress to restore the Spaulding-Summit 60kV line. | NONE | NORTH VALLEY AND SIERRA | INT-18939 | 2008 | 2008 | 659034 | 0.00034646 | 0.11371 | 652 | 5795693 | B-C | 000/007 | AUTO | Single Mode | Tier 2 | Nevada | Sierra | Data Available upon request | Data Available upon request | Cisco Grove 60kV Tap STR 000/007 | Storm | 2 ACSR | Data Available upon request | SD
69 | 60 | ETL.6760 | 60070 | DRUM-GRASS VALLEY-WEIMAR | 2025 | 2025-02-06 23:02 | 45694.9597 | No | YES | No | 0.79653 | 1147 | 2025-02-07 18:09 | 45695.7562 | F | Tree | Tree-failure | COND | Relayed - 2/6/2025, 2302 Drum-Grass Valley-Weimar 60kV line relayed and tested NG. On the trouble, Weimar #1-60kV line momentarily de-energized. Rollins PH separated. Momentary interruption to Weimar, Forest Hill and Oxbow PH (offline). Sustained interruption to Bonnie Nook, Cape Horn and Shady Glen. Weather rain. 2321 Drum to Shady Glen section manually tested OK, restoring Bonnie Nook, Cape Horn and Shady Glen. Estimated return 02/07/24. Line patrol found a tree in the line and single phase of wire down between structures B022/492 and B022/493, line will be cleared for repairs. 2/7/24, 1809 Grass Valley to Rollins JCT section returned to service after crew removed tree and repaired one phase of wire down between structures B022/492 and B022/493. From trouble on 02/06/25 at 2302. | NONE | NORTH VALLEY AND SIERRA | INT-18950-1 | 3609 | 3609 | 68571 | 0.0006227 | 0.011831 | 38 | 5795693 |  | B023/521 | AUTO | Dependent Mode Initiating | Tier 3 | Nevada | Sierra |  |  | Drum-Grass Valley-Weimar 60kV line STR B022/492 | Rain | 2/0 CU |  | SD
69 | 60 | ETL.2060 | 60389 | FORT BRAGG-ELK | 2025 | 2025-02-13 13:39 | 45701.5687 | No | YES | No | 1899-12-31 02:07 | 1567 | 2025-02-14 15:46 | 45702.6569 | F | Tree | Tree-failure | COND | Relayed - 2/13/2025, 1339 Fort Bragg-Elk 60kV line relayed and tested NG. Fort Bragg to Big River sectionalized and tested OK. Momentary interruption to Big River. Weather storm. 1647 Line cleared to repair 3 phases of wire down and remove tree between structures 007/000 and 007/001. Estimated return 02/14/25. 2/14/25, 1546 Fort Bragg-Elk 60kV line (Elk to Big River section) returned to service after crew removed tree and repaired 3 phases of wire down between structures 007/000 and 007/001. From trouble on 02/13/25 at 1339. | NONE | NORTH COAST | INT-18969 | 2605 | 0 | 0 | 0 | 0 | 0 | 5795693 | C-A-G | 006/007 | AUTO | Single Mode | Tier 2 | Mendocino | Humboldt |  |  | Fort Bragg-Elk 60kV line STR 007/000 | Storm | 397.5 AAC |  | SD
69 | 60 | ETL.6380 | 60420 | KONOCTI-MIDDLETOWN | 2025 | 2025-03-06 17:56 | 45722.7472 | No | YES | No | 0.79444 | 1144 | 2025-03-07 13:00 | 45723.5417 | F | Tree | Tree-3rd party | COND | Relayed - 3/6/2025, 1756 Konocti-Middletown 60kV line relayed and tested NG. Momentary interruption to Middletown #2-60/12kV transformer. Weather clear. 2140 Line cleared to repair one phase of wire down caused by tree contact between structures 027/003 and 027/004. Estimated return 03/07/25. Tree contact found between 27/3-27/4, single phase down. Bill Stanton reported in the 3/7/25 T&D call that the tree was cut by a third party at a homeless encampment. 3/7/25, 1300 Konocti-Middletown 60kV line returned to service after crew repaired one phase of downed conductor between structures 027/003 and 027/004. From trouble on 03/06/25 at 1756. | NONE | NORTH COAST | INT-19037 | 2581 | 0 | 0 | 0 | 0 | 0 | 5795693 | B-C | 027/004 | AUTO | Single Mode | Tier 2 | Lake | Humboldt |  |  | Konocti-Middletown 60kV line STR 027/003 | Clear | 4/0 AAC |  | GS
69 | 60 | ETL.7820 | 60181 | POTTER VALLEY-WILLITS | 2025 | 2025-03-14 05:52 | 45730.2444 | No | YES | No | 0.47292 | 681 | 2025-03-14 17:13 | 45730.7174 | F | Tree | Tree-failure | COND | Relayed - 3/14/2025, 0552 Potter Valley-Willits 60kV line relayed and tested NG. No customer interruption. Weather storm. 1713 Line returned to service after crews repaired three phases of downed conductor between poles 009/004 and 009/005 and re-sagged three phases of conductor between poles 009/002 and 009/003.Crew repairing 3 phases of wire down between 9/4-9/5 due to tree contact ETOR 15:00hrs today. Notification # 130977381 | NONE | NORTH COAST | INT-19067 | 0 | 0 | 0 | 0 | 0 | 0 | 5795693 | B-C | 008/009 | AUTO | Single Mode | Tier 3 | Mendocino | Humboldt |  |  | Potter Valley-Willits 60kV line STR 009/002 | Storm | 1/0 ACSR |  | SD
69 | 60 | ETL.8270 | 60227 | VIEJO-MONTEREY | 2025 | 2025-03-17 14:25 | 45733.6007 | No | YES | No | 1899-12-31 00:39 | 1479 | 2025-03-18 15:04 | 45734.6278 | F | Tree | Tree-failure | COND | Relayed - 3/17/2025, 1425 Del Monte-Monterey 60kV line relayed and tested NG. Sustained interruption to Navy School. Weather storm. 2146 Del Monte-Monterey 60kV line (Del Monte to Navy school section) manually tested OK restoring transmission to Navy School. 2251 Navy School to Veijo section cleared to repair downed conductor between 000/010 and 000/013. Estimated return 03/18/25. 3/18/25, 1309 Del Monte-Monterey 60kV line de-energized for crew to re-establish clearance to close open jumpers at pole 2/50. Sustained interruption to Navy School. 1504 Del Monte-Monterey 60kV line returned to service restoring Navy School after crews replaced NG pole 0/11, re-framed pole 0/12 and repaired three phases of downed conductor between the poles. Caused by tree contact. Monterey substation is bypassed via t-line shoo-fly creating Del Monte – Monterey – Viejo 60kV line. Fault location is on the Viejo – Monterey 60kV line. | NONE | SOUTH BAY AND CENTRAL COAST | INT-19077 | 0 | 0 | 0 | 0 | 0 | 0 | 5795693 | A-B-C | 000/013 | AUTO | Single Mode | Tier 2 | Monterey | Central Coast |  |  | Viejo-Monterey 60kV line STR 000/011 | Storm | 715.5 AAC |  | SD
69 | 70 | ETL.8440 | 70002 | ARCO-CHOLAME | 2025 | 2025-05-02 03:39 | 45779.1521 | No | YES | YES | 0.54514 | 785 | 2025-05-02 16:44 | 45779.6972 | F | Equipment Failure | Equip Fail-conductor | COND | Relayed - 5/2/2025, 0339 Arco-Cholame 70kV line (EPSS) relayed and did not test as directed by Operations. Sustained interruption to Devils Den, Berrenda "A", Berrenda "C", Antelope and Cholame. Weather clear. 0503 Arco Cholame 70kV line (Arco to Berrenda JCT section) manually tested NG. Cholame JCT to Cholame section cleared for crew to repair one phase of downed conductor between structures 16/161 and 16/162. xxxx Arco to Cholame JCT section returned to service restoring transmission service to Berrenda A, Berrenda C and Antelope. | NONE | CENTRAL VALLEY | INT-19162 | 1795 | 1795 | 921489 | 0.00030971 | 0.159 | 1783 | 5795693 | B-G | 014/140 | AUTO | Single Mode | Tier 2 | Kern | Kern |  |  | Arco-Cholame 70kV line (EPSS) STR 16/161 | Clear | 3/0 AAC |  | BS
SOMs 3.4 | 1.3017 |  |  | 2025 HFTD Miles | 5377.4

## 2022 3.4 WD non-MED HFTD
HFTD | REGION | TL Area | kV Cls | kV | SAP FL | LINE NO | FACILITY | YEAR | Date Out | Time Out | MED | ET Wire Down | Auto Reclose Disabled | Durn (hr:min) | Durn (mins) | Date In | Time In | Out Cls | Cause Category | Cause Detail | Secondary Cause | Comments | CAP | REGION | TOTL | Customers Affected | CESO/ Event | CMIN/ Event | SAIFI Contr | SAIDI Contr | CAIDI | System Customer Count | Fault Type | Fault Estimate | AUTO / EFO / SCHD | Outage Mode | HFTD | County | Division | LAT | LONG | Actual Location | Weaher | Conductor | ET-GIS Location | ET-GIS Location | ET-GIS Location | Conductor Rating
Tier 3 | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.6760 | 60070 | DRUM-GRASS VALLEY-WEIMAR | 2022 | 2022-01-02 21:41 | 44563.9035 | No | YES | No | 1899-12-31 15:49 | 2389 | 2022-01-04 13:30 | 44565.5625 | F | Tree | Tree-failure | COND | Relayed - 01/02/22, 2141 Drum-GV-Weimar 60kV (tier 2/3) relayed, tested NG; Weimar #1 momentarily de-energized & Alta & Ox Bow PHs separated; 2145 Drum to Alta PH tested OK via autos restoring Bonnie Nook & Alta PH; MOM Forest Hill (CEMO=1,358), Bonnie Nook (1,044) & Weimar (2,286); SUS Shady Glen (CESO=1,462; CMIN=71,708), Cape Horn & Rollins PH; weather clear; 2145 Drum to Alta PH tested OK via autos restoring Alta PH; 2214 Rollins to Weimar tested OK restoring Cape Horn, Shady Glen & Rollins PH; A-G fault 0.7 mi from Shady Glen toward Rollins PH near B16/372 or 3.0 mi from Shady Glen toward Weimar near 018/421, w/in 3 mi; 01/03/22 patrol finds ET-WD between poles 11/264-265 (Bonnie Nook to Cape Horn); 01/03/22, 1652 Grass Valley-Rollins PH returned to service after tree removed at 23/521, 23/522 & B21/482, ET-WD repaired at B21/466 & B21/469 between B21/468 & B21/469, B21/469 & B21/470, broken xarm replaced at B20/454 & poles B21/468, B21/469 replaced; 01/04/22, 1330 Bonnie Nook-Cape Horn returned to service | NONE | NORTH VALLEY AND SIERRA | INT-15591-1 | 8669 | 1462 | 71708 | 0.0004718 | 0.059249 | 125.58 | 5631636 | A-G | B016/372 | AUTO | Dependent Mode-initiating | Tier 3 | Nevada | Sierra | Data available upon request | Data available upon request | Drum-GV-Weimar, B21/469 | Clear | 2/0-7,CU | Data available upon request | YES | 441 WN (B)
Tier 3 | SOUTH BAY AND CENTRAL COAST | SOUTH | 69 | 60 | ETL.7380 | 60133 | LAURELES-OTTER | 2022 | 2022-01-21 19:54 | 44582.8292 | No | YES | No | 1900-01-08 19:53 | 14153 | 2022-01-31 15:47 | 44592.6576 | C | Disaster | Disaster-fire | STRU | Relayed - 01/21/22, 1954 Laureles-Otter 60kV (tier 2/3) relayed, did not test; SUS Otter (CESO=1,110; CMIN=2,044,884); weather clear; A-G fault 3 mi from Otter near 12/7, +/-3 mi; 'Colorado' fire is north of Otter & burning towards sub; Public Safety Specialist on scene coordinating w/ CAL FIRE which is restricting PG&E access due to fire-fighting efforts; 01/31/22, 1547 Laureles-Otter returned to service after replacing burnt poles 14/5, 14/7, 15/1-15/6 & repairing ET-WD at 14/6, restoring ET to Otter | NONE | SOUTH BAY AND CENTRAL COAST | INT-15624-2 | 1110 | 1110 | 2044884 | 0.0001971 | 0.36311 | 1842.2378 | 5631636 | A-G | 012/007 | AUTO | Single Mode | Tier 3 | Monterey | Central Coast |  |  | Laureles-Otter, 12/7 | Clear | 4/0-7,AAC |  | No | 432 WN (B)
Tier 2 | CENTRAL VALLEY | SOUTH | 69 | 70 | ETL.8440 | 70002 | ARCO-CHOLAME | 2022 | 2022-03-28 07:19 | 44648.3049 | No | YES | No | 0.33264 | 479 | 2022-03-28 15:18 | 44648.6375 | F | External Contact | Ext Cont-vandalism | COND | Relayed - 03/28/22, 0719 Arco-Cholame 70kV (tier 2/3) relayed, tested NG; SUS Devils Den (CESO=52; CMIN=624), Cholame (1,569; 398,376), Berrenda A (1; 12), Berrenda C & Antelope (170; 2,040); high winds, rain; 0731 Arco to Antelope manually tested OK restoring ET to Devils Den, Berrenda A, Berrenda C & Antelope; multi-terminal line, B-G fault near 011/116 or near 002/028 on Antelope Tap, +/-2 mi; 1315 ET restored to Cholame from alt source; 1518 Arco-Cholame normal after 1 span ET-WD replaced between poles 13/126-127; CAP 123204599 | 123204599 | CENTRAL VALLEY | INT-15748 | 1792 | 1792 | 401052 | 0.00031575 | 0.070665 | 223.8013 | 5675418 | B-G | 011/116 | AUTO | Single Mode | Tier 2 | Kern | Kern |  |  | Arco-Cholame 13/126 | Wind, rain | 3/0-7,AAC |  | No | 381 WN (B)
Tier 3 | NORTH COAST | NORTH | 115 | 115 | ETL.4392 | 10445 | EAGLE ROCK-FULTON-SILVERADO | 2022 | 2022-06-16 05:24 | 44728.225 | No | YES | YES | 0.59306 | 854 | 2022-06-16 19:38 | 44728.8181 | F | Equipment Failure | Equip Fail-conductor | COND | Relayed - 06/16/22, 0524 Eagle Rock-Fulton-Silverado 115kV (tier 2/3) relayed, did not test, auto reclosing c/out for wildfire risk; on the trouble Silverado-Fulton Jct 115kV de-energized (tier 2/3, EPSS line); MOM Rincon (CEMO=14,656) & Silverado (8,421); SUS to Monticello (CESO=1,442; CMIN=172,697) & Monticello PH (offline); weather clear; B-G fault 2.75 mi from Eagle Rock near 003/017, +/-2 mi; 0656 Silverado-Fulton Jct returned to service restoring Monticello & Monticello PH (offline); 1105 to 1938 ER-Fulton-Silverado cleared to repair 1 phase ET-WD between towers 3/16-16B | NONE | NORTH COAST | INT-16006 | 24520 | 1442 | 172697 | 0.00025408 | 0.030429 | 119.7621 | 5675418 | B-G | 003/017 | AUTO | Dependent Mode-initiating | Tier 3 | Sonoma | Humboldt |  |  | Eagle Rock-Fulton-Silverado 3/16 | Clear | 1113-61,AAC |  | No | 825 SN (N); 975 SE (A); 1287 WN (B); 1378 WE ( C)
Tier 2 | CENTRAL VALLEY | CENTRAL | 69 | 60 | ETL.8350 | 60236 | WEST POINT-VALLEY SPRINGS | 2022 | 2022-07-04 18:39 | 44746.7771 | No | YES | No | 1900-01-04 00:22 | 7222 | 2022-07-09 19:01 | 44751.7924 | C | Disaster | Disaster-fire | STRU | Forced - 07/04/22, 1839 West Pt-Valley Springs open ended at VS, reports of multiple Electra fire-damaged poles; on trouble West Pt PH island created; 1842 West Pt PH manually tripped terminating West Pt island & de-energizing WP-VS; SUS Electra, Pine Grove & West Pt; 07/05/22, 2209 West Pt PH island established; 07/07/22, 0943 Electra Jct-Valley Springs cleared to replace pole 10/127 & ET-WD; 0943 Valley Springs to Valley Springs SW-27 energized per CAL FIRE approval after full line patrol, no trouble found; 0944 West Pt-Electra Jct cleared to replace burnt poles 10/120, 9/112, 9/116, 9/117; 1737 Valley Springs to Valley Springs SW-27 de-energized to operate line switches dead; 1829 after CAL FIRE approval Valley Springs-Electra manually tested OK restoring Electra after pole 10/127 & ET-WD replaced; 07/09/22, 1851 Electra Jct to West Pt returned restoring Pine Grove; 1901 West Pt island synched terminating island | NONE | CENTRAL VALLEY | T22-012463 | 2838 | 2838 | 2282222 | 0.00050005 | 0.40212 | 804.1656 | 5675418 | NA | NA | EFO | Emergency Forced Outage | Tier 2 | Calaveras | Stockton |  |  | West Point-Valley Springs 10/127 | Fire (Electra) | 266.8-26/7,ACAR |  |  |  | SN (N) 384; SE (A) 438; WN (B) 551; WE (C) 585
Tier 3 | NORTH VALLEY AND SIERRA | NORTH | 69 | 60 | ETL.7560 | 60152 | WEIMAR #1 | 2022 | 2022-08-26 07:25 | 44799.309 | No | YES | YES | 1900-01-01 07:29 | 3329 | 2022-08-28 14:54 | 44801.6208 | F | Equipment Failure | Equip Fail-conductor | COND | Relayed - 08/26/22, 0725 Middle Fork #1 & Weimar #1-60kV relayed, did not test during routine switching; automatic reclosing c/out for wildfire risk mitigation; SUS Forrest Hill (CESO=2,699; CMIN=1,113,268) & Oxbow PH; weather clear; A-C fault 7 mi from Weimar toward Forrest Hill near 007/108, +/-2 mi; <1 acre fire extinguished & repairs to 1 phase ET-WD & damage to other 2 phases between 007/105-106 to be completed under original clearance; patrol completed on Weimar #1 (Forrest Hill to Oxbow PH Jct) & Middle Fork #1, no further trouble found; waiting on NCPA to check CB status at Middle Fork & test the line; 1214 Weimar #1 (Forrest Hill Jct- Oxbow PH Jct) & Middle Fork #1 tested OK restoring Oxbow PH & ET to Forrest Hill; scheduled return of Weimar-Forrest Hill Jct=08/28; 08/28/22, 1454 Weimar #1 returned to service after crew inserted shunt splices & replaced 3 phases of conductor between poles 007/105-106 | NONE | NORTH VALLEY AND SIERRA | INT-16177 | 2699 | 2699 | 1113268 | 0.00047556 | 0.19616 | 412.4742 | 5675418 | A-C | 007/108 | AUTO | Dependent Mode-initiating | Tier 3 | Placer | Sierra |  |  | Weimar #1 between 007/105-106 | Clear | 2-7/1,ACSR |  |  |  | SN (N) 157; SE (A) 176; WN (B) 220; WE (C) 232
Tier 2 | NORTH COAST | NORTH | 69 | 60 | ETL.2060 | 60389 | FORT BRAGG-ELK | 2022 | 2022-11-01 08:18 | 44866.3458 | No | YES | YES | 1899-12-31 06:24 | 384 | 2022-11-02 14:42 | 44867.6125 | F | Weather | Weather-rain | COND | Relayed – 11/01/22, 0818 Fort Bragg-Elk 60kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. On the trouble. Big River 60kV SVC tripped. SUS Big River (CESO=2,624; CMIN=39,360). Weather rain. Line is in tier 2/3 HFTD. Protection reports B-G fault near structure 005/001. 0829 Fort Bragg to Big River section manually tested OK restoring Big River. 1241 Elk to Big River section cleared for crew to repair one phase of downed conductor between structures 005/001 and 005/002. Estimated return 11/02/22. INT-16321. 11/02/22, 1442 Fort Bragg-Elk 60kV line (Elk to Big River section) returned to service after crew repaired downed conductor between structures 5/1 and 5/2. Line Patrol found no other trouble. From trouble on 11/01/22 at 0818. | NONE | NORTH COAST | INT-16321 | 2624 | 2624 | 39360 | 0.00046234 | 0.0069352 | 15 | 5675418 | B-G | 005/001 | AUTO | Single Mode | Tier 2 | Mendocino | Humboldt |  |  | Conductor between 005/001 & 005/002 | Rain | 397.5 AAC |  |  |  | SN (N) 488; SE (A) 554; WN (B) 666; WE (C) 711
Tier 2 | NORTH COAST | NORTH | 115 | 115 | ETL.1820 | 10104 | HUMBOLDT-TRINITY | 2022 | 2022-11-01 10:24 | 44866.4333 | No | YES | YES | 0.69306 | 998 | 2022-11-02 03:02 | 44867.1264 | F | Weather | Weather-rain | COND | Relayed – 11/01/22, 1024 Humboldt-Trinity 115kV line relayed and did not test due to automatic reclosing disabled for wildfire mitigation. No customer interruption. Weather rain. Line is in tier 2/3 HFTD. Protection reports C-G fault near structure 073/006. 1646 Line cleared for crew to repair one phase of downed conductor between towers 73/3 and 73/2AA. Estimated return 11/02/22. INT-16322. 11/02/22, 0302 Humboldt-Trinity 115kV line returned to servicer after crew repaired one phase of downed conductor between towers 73/3 and 73/2AA. From trouble on 11/01/22 at 1024. | NONE | NORTH COAST | INT-16322 | 0 | 0 | 0 | 0 | 0 | 0 | 5675418 | C-G | 073/006 | AUTO | Single Mode | Tier 2 | Trinity | Humboldt |  |  | Conductor between 073/003 & 073/002AA | Rain | 336.4 ACSR |  |  |  | SN (N) 490; SE (A) 547; WN (B) 647; WE (C) 687
Tier 2 | NORTH COAST | NORTH | 69 | 60 | ETL.2060 | 60389 | FORT BRAGG-ELK | 2022 | 2022-12-26 22:41 | 44921.9451 | No | YES | No | 0.78472 | 1130 | 2022-12-27 17:31 | 44922.7299 | F | Tree | Tree-failure | COND | Relayed – 12/26/22, 2241 Fort Bragg-Elk 60kV line relayed and tested NG. SUS Big River(CESO=1,923;CMIN=271,143). Weather storm. Line is in tier 2/3 HFTD. 2259 Elk to Big River section manually tested OK restoring Big River. Protection reports A-C fault near STR 019/012. INT-16471. 12/27/22, 1731 Fort Bragg-Elk 60kV line (Fort Bragg to Big River JCT section) returned to service after crew repaired two phased of downed conductor between poles 20/16 and 21/1. Caused by tree falling into line From trouble on 12/26/22 at 2241. | NONE | NORTH COAST | INT-16471 | 1923 | 1923 | 271143 | 0.00033883 | 0.047775 | 141 | 5675418 | A-C | 019/012 | AUTO | Single Mode | Tier 2 | Mendocino | Humboldt |  |  | Fort Bragg-Elk STR 020/016 | Storm | 397.5 AAC |  |  |  | SN (N) 488; SE (A) 554; WN (B) 666; WE (C) 711
| SOMs 3.4 | 1.6287 |  |  |  |  | 2022 HFTD Miles | 5525.9
*Note: Outage T22-012463 was incorrectly reported as non-HFTD in the 2023 filing, the WD location is Tier 2
Formulas:
Durn (hr:min) = [Date In]-[Date Out]

## 3.4 Control Chart
Original | Corrected

## List of MEDs from Reliability
IEEE-1366 TMED Days
No Planned Outage Classification | [7 empty] | Planned Outage Classification Available
[8 empty] | MED Threshold | 5.747 | MED Threshold
1988 | 1989 | 1990 | 1991 | 1992 | 1993 | 1994 | 1995 |  | 2025
227 | 302 | 216 | 302 | 105 | 101 | 216 | 104 |  | 619
228 | 406 | 217 | 303 | 215 | 113 | 217 | 106
717 | 808 | 218 | 304 | 1029 | 114 | 815 | 107
1113 | 916 | 422 | 325 | 1121 | 121 | 928 | 108
1214 | 1017 | 423 | 1020 | 1206 | 219 | 1004 | 109
1215 | 1018 | 520 | 1025 | 1228 | 1111 | 1015 | 110
1220 | 1023 | 922 | 1026 | 1231 | 1114 | 1109 | 308
1222 |  | 1125 | 1129 |  | 1211 | 1214 | 309
1224 |  |  | 1227 |  |  |  | 310
311
314
322
323
716
717
1004
1210
1211
1212
1213
1214
1220
9 | 7 | 8 | 9 | 7 | 8 | 8 | 22
1

## Target Calculation
METRIC 3.4
2013-2022 Performance
2013 | 2.353
2014 | 1.81
2015 | 2.534
2016 | 3.438
2017 | 3.438
2018 | 1.991
2019 | 2.534
2020 | 1.448
2021 | 1.991
2022 | 1.629
10 Year Average | 2.3166
STDEV | 0.69177
STDEV x 3 | 2.0753
UCL (2025 Target) | 4.3919
10 year average + (STDEV × 3) = UCL
2.317 + 2.075 = 4.392

## Cause Translation
PG&E Outage Cause Category-Details | ISO Outage Primary Cause Code | ISO Outage Primary Cause Code Description | PG&E and ISO Outage Secondary Cause Code | ISO Outage Secondary Cause Code Description |  | Cause Category (10 categories) | Cause Details | Outage Mode
Animal-bird | ANIM | Animal Contact | ARRS | Arrestor | 1 | Animal | Animal-bird | Common Mode
Animal-ground | ANIM | Animal Contact | AUX | Station auxiliary equip (e.g., CT, PT, CCVT) | 2 | Contamination | Animal-ground | Common Mode-initiating
Contamination-agriculture | CNTM | Contamination | BATT | Battery system | 3 | Disaster | Cntmn-agriculture | Dependent Mode
Contamination-animal waste | CNTM | Contamination | BUSH | Bushing | 4 | Equipment Failure | Cntmn-animal waste | Dependent Mode-initiating
Contamination-environmental | CNTM | Contamination | CB | Circuit breaker/Circuit switch | 5 | External Contact | Cntmn-environmental | Emergency Forced Outage
Contamination-industrial waste | CNTM | Contamination | COMM | Communication facility (no relay) | 6 | Other | Cntmn-industrial waste | Scheduled Outage
Disaster-earthquake | ND | Natural Disaster | COND | Conductor/shield wire/splice | 7 | Tree | Disaster-earthquake | Single Mode
Disaster-fire | FIRE | Fire | DISC | Disconnect | 8 | Unknown | Disaster-fire
Disaster-flood | ND | Natural Disaster | ENCR | Encroachment | 9 | Weather | Disaster-flood
Disaster-other | ND | Natural Disaster | GUYS | Guy/anchor | 10 | Work Procedure Error | Disaster-other
Equipment Failure-arrestor | SEQP | Substation Equipment Problem | HDWR | Hardware, fittings, accessories |  |  | Equip Fail-arrestor
Equipment Failure-bus | SEQP | Substation Equipment Problem | INSL | Insulator (station/line) |  |  | Equip Fail-bus
Equipment Failure-bushing | SEQP | Substation Equipment Problem | LS | Line switch |  |  | Equip Fail-bushing
Equipment Failure-ccvt | SEQP | Substation Equipment Problem | NONE | None |  |  | Equip Fail-ccvt
Equipment Failure-circuit breaker | CB | Circuit Breaker Trouble | REAC | Reactive device (e.g., capacitors, condenser) |  |  | Equip Fail-circuit breaker
Equipment Failure-conductor | LEQP | Line Equipment Problem | REG | Regulator |  |  | Equip Fail-conductor
Equipment Failure-connector/hardware | LEQP | Line Equipment Problem | RELY | Relay/communicatons for relay |  |  | Equip Fail-connector/ hardware
Equipment Failure-CT | SEQP | Substation Equipment Problem | STRU | Structure/foundation |  |  | Equip Fail-CT
Equipment Failure-insulator-line | LEQP | Line Equipment Problem | XFRM | dre56] |  |  | Equip Fail-insulator-line
Equipment Failure-insulator-station | SEQP | Substation Equipment Problem | UG | Underground transmission component |  |  | Equip Fail-insulator-station
Equipment Failure-other-line | LEQP | Line Equipment Problem | PROC | Work Procedure/Human Error |  |  | Equip Fail-other-line
Equipment Failure-other-station | SEQP | Substation Equipment Problem | PSPS | Public Safety Power Shutoff |  |  | Equip Fail-other-station
Equipment Failure-PT | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-PT
Equipment Failure-reactive equipment | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-reactive equipment
Equipment Failure-regulator/LTC | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-regulator/ LTC
Equipment Failure-relay | PROT | Protection |  |  |  |  | Equip Fail-relay
Equipment Failure-structure-line | LEQP | Line Equipment Problem |  |  |  |  | Equip Fail-structure-line
Equipment Failure-structure-station | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-structure-station
Equipment Failure-switch-line | LEQP | Line Equipment Problem |  |  |  |  | Equip Fail-switch-line
Equipment Failure-switch-station | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-switch-station
Equipment Failure-transformer | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-transformer
External Contact-aircraft | AIR | Aircraft |  |  |  |  | Ext Cont-aircraft
External Contact-car pole | VEH | Vehicle Contact |  |  |  |  | Ext Cont-car pole
External Contact-foreign object | OTHR | Other |  |  |  |  | Ext Cont-foreign object
External Contact-system disturbance | DIST | System Disturbance |  |  |  |  | Ext Cont-system disturbance
External Contact-vandalism | OTHR | Other |  |  |  |  | Ext Cont-vandalism
Other-customer/IPP caused | OTHR | Other |  |  |  |  | Other-customer/ IPP caused
Other-distribution caused | UC | Utility Contact |  |  |  |  | Other-distribution caused
Other-generation caused | GEN | Generation Trouble |  |  |  |  | Other-generation caused
Other-overload situation | DIST | System Disturbance |  |  |  |  | Other-load control
Other-safety clearance | OTHR | Other |  |  |  |  | Other-safety clearance
Scheduled-approved | SCHD | Scheduled Outage |  |  |  |  | Other-scheduled-approved
Scheduled-disapproved | LATE | Late Notification |  |  |  |  | Other-scheduled-disapproved
Scheduled-extended | LATE | Late Notification |  |  |  |  | Other-scheduled-extended
Tree-3rd party | OTHR | Other |  |  |  |  | Tree-3rd party
Tree-failure | VEGA | Vegetation |  |  |  |  | Tree-failure
Tree-tree contact | VEGA | Vegetation |  |  |  |  | Tree-tree contact
Unknown-no patrol conducted | UNKN | Unknown |  |  |  |  | Unk-no patrol conducted
Unknown-patrol found nothing | UNKN | Unknown |  |  |  |  | Unk-patrol found nothing
Weather-lightning | LIGT | Lightning |  |  |  |  | Weather-lightning
Weather-rain | WEAT | Weather |  |  |  |  | Weather-rain
Weather-snow/ice | WEAT | Weather |  |  |  |  | Weather-snow/ ice
Weather-wind | WEAT | Weather |  |  |  |  | Weather-wind
Work Procedure-design error | OPER | Operating error |  |  |  |  | Work Procedure-design error
Work Procedure-equipment incorrectly set | OPER | Operating error |  |  |  |  | Work Procedure-equip incorrectly set
Work Procedure-inattention or carelessness | OPER | Operating error |  |  |  |  | Work Procedure-inattention or carelessness
Work Procedure-miscommunications or unclear expectations | OPER | Operating error |  |  |  |  | Work Procedure-miscommunications or unclear expectations
Work Procedure-not following prescribed procedures | OPER | Operating error |  |  |  |  | Work Procedure-not following prescribed procedures
SGS CAUSE CODE CATEGORIES
Description | SGS Category No | Examples
Equipment | 1 | Terminal equipment: breakers, switches, transformers, cap bks, busses, etc. ("inside the fence")
System Protection | 2 | Relay equipment failure, misoperation, incorrect settings or scheme, "over-reaching", communications
Lines | 3 | Failed hardware "outside the fence"; structures, conductors, cable cable hardware, insulators, static wire
Weather, other than lightning | 4 | Severe weather conditions, usually beyond design capabilities of facilities, exclusive of lightning
Lightning Only | 5 | Verified or suspected outages resulting from lightning
Unknown | 6 | Diligent attempts to verify cause were unsuccessful
Vegetation | 7 | Vegetation and trees which directly cause an outage
External | 8 | Causes outside control of ET system (e.g., foreign utilities, customer equip, generation, UF, instability)
Other | 9 | Operating errors, contractors, dig-ins, loggers, birds, animals, public damage, contamination, autos
Excludable Outage, Natural Causes Only | 10 | Major events (extreme), system disturbances associated w/ cascading
Excludable Outage, System Causes Only | 11 | Operational Outage for safety, voltage control or stability, System Disturbances, Unusual Configurations
Human Factors | 12 | WPE/ HPE

## ILIS Causes
Basic Cause Field | Supplemental Cause Field | [13 empty] | Equipment Condition
3rd Party* 00 | Aircraft | Aircraft-Crop Dusting | Contact with High Voltage, 3rd Party | Customer Equipment | Dig In, 3rd Party | Fire, house or bldg | Gun Shot | Kite | Metallic Balloon | Thrown Object | Vandalism | Vehicle | Other | tree - cutting 3rd party | Annealed
Animal* 02 | Bird Found | Other | Squirrel | [11 empty] | Arcing
Company Initiated* 05 | Construction Activity/equip, company | Contact with High Voltage, company | Coordination Failure | Dig in, company | Improper Construction | Insulator washing | Operating error | Other Circuits | Personnel, company | Planned, capital | Planned, customer | Planned, maintenance | Rotating Outage | Return circuit normal | Bent or Twisted
Equipment Failure/Involved* 03 | Electrical Overload | Fire, pole | overhead | Substation | underground | [9 empty] | Blown / exploded
Vegatation* 01 | Other Ground Vegetation | Tree - bark fell into line | Tree - branch fell on line | Tree - cutting PG&E contractor | Tree - fell into line | Tree - grew into line | Tree - palm frond fell into line | [7 empty] | Broken
Unknown 04 | Patrol - Found Nothing | Patrol - Not Conducted | [12 empty] | Broken, wire on ground
(Environmental)External influence * 06 | Earthquake | Fire, forest/grass | Flood/ errosion | Ice or snow | Lightning | water | [8 empty] | Burned Open
Burned / flashed
* These type outages require "Equipment Involved" & "Equipment Condition" field be populated. See available selection below | [14 empty] | Contaminated
Deteriorated
Equipment Involved | Anchor or Guy | Booster | Bus | Bushing | PT/CCVT | CT/PT | Capacitor | Circuit Breaker | Conductor, Overhead | Conductor, Underground | Connector or Splice (OH) | Connector or Splice (UG) | Crossarm, Steel |  | Leaking
See also next tabs | Crossarm, Wood | Customer Equipment | Cutout, Fused, Distribution | Cutout fuse holder | Elbow | Footings, Tower or Pole | Fuse | Insulator | Interrupter | Jumper | Lightning Arrestor | Manhole, primary box | Metering Equipment |  | Malfunctioning
| Other | PGs, Kearneys | Pole - Tower, steel | Pole - Wood | Pothead or Cable Termination | Reactive Equipment | Recloser | Regulator | Regulator, LTC substation | Relay, substation | Riser | Secondary | Sectionalizer |  | Normal
| Service Conductor | Splice Box | Stepdown | Street Light Equipment | Switch | Transformer | Transformer, Station Bank, Power | Woodpin | Generator | SCADA |  |  |  |  | Together
Equipment Condition | Annealed | Arcing | Bent or Twisted | Blown / exploded | Broken | Broken, wire on ground | Burned Open | Burned / flashed | Contaminated | Deteriorated | Leaking | Malfunctioning | Normal
see also next tabs | On Ground | Together |  |  |  | Broken, wire on object
Outage Level | Distribution Circuit | Substation Distribution | Substation Transmission | Transmission Line | Transformer Only | Generation | secondary | service
[7 empty] | FAS only | FAS only

## 2025 HFTD Miles
TLINE_NAME | RATEDKV | SAP_FL | OWNER_STATUS | STATUS | TLINEMILES | T3MILES | T2MILES | Z1MILES | T1MILES | Exclude Reason |  | 2025 ALL | 2025 Exclude | 2025 Remainder
230KV CAP BANK TIE LINE | 230 | 0 |  | ACT | 0.27 |  |  |  | 0.27 |  | HFTD Miles | 5421.63 | 44.24 | 5377.39
7TH STANDARD-KERN | 115 | ETL.1981 |  | ACT | 6.77 |  |  |  | 6.77
ADOBE SW STA #1 TAP | 115 | ETL.1145 |  | ACT | 14.25 |  |  |  | 14.25
AEC SITE #1 TAP | 115 | ETL.3982 |  | ACT | 1.6 |  |  |  | 1.6
AEC SITE #2 TAP | 115 | ETL.3983 |  | ACT | 2.16 |  |  |  | 2.16
AERA ENERGY TAP | 70 | ETL.7727 |  | ACT | 0.35 |  |  |  | 0.35
AIR PRODUCTS TAP | 115 | ETL.2314 |  | ACT | 0.29 |  |  |  | 0.29
ALMADEN-LOS GATOS | 60 | ETL.6825 |  | ACT | 6.35 |  |  |  | 6.35
ALMENDRA JCT-NICOLAUS | 60 | ETL.6150 |  | ACT | 24.9 |  |  |  | 24.9
AMERIGAS TAP | 115 | ETL.1591 |  | ACT | 0.49 |  |  |  | 0.49
AMES DISTRIBUTION-AMES | 115 | ETL.2482 |  | ACT | 0.1 |  |  |  | 0.1
AMES-MOUNTAIN VIEW | 115 | ETL.1174 |  | ACT | 2.57 |  |  |  | 2.57
AMES-WHISMAN | 115 | ETL.4150 |  | ACT | 0.97 |  |  |  | 0.97
AMFOR TAP | 60 | ETL.8241 |  | ACT | 1.04 |  |  |  | 1.04
ANTELOPE TAP | 70 | ETL.8442 |  | ACT | 4.28 |  |  |  | 4.28
APPLE HILL #1 TAP | 115 | ETL.1531 |  | ACT | 1.42 |  | 1.42 |  | 0
APPLE HILL #2 TAP | 115 | ETL.1541 |  | ACT | 1.43 |  | 1.43 |  | 0
APPLIED MATERIALS-BRITTON | 115 | ETL.4300 |  | ACT | 0.47 |  |  |  | 0.47
ARBUCKLE TAP | 60 | ETL.6591 |  | ACT | 0.82 |  |  |  | 0.82
ARBURUA TAP | 70 | ETL.8932 |  | ACT | 3.57 |  |  |  | 3.57
ARCATA-HUMBOLDT | 60 | ETL.7110 |  | ACT | 7.28 |  |  |  | 7.28
ARCO-AZALEA PV | 70 | ETL.1472 |  | ACT | 0.07 |  |  |  | 0.07
ARCO-CARNERAS | 70 | ETL.8430 |  | ACT | 18.02 |  |  |  | 18.02
ARCO-CHOLAME | 70 | ETL.8440 |  | ACT | 26.74 |  | 4.8 |  | 21.94
ARCO-MIDWAY | 230 | ETL.4320 |  | ACT | 43.36 |  |  |  | 43.36
ARCO-POLONIO PASS PP | 70 | ETL.8450 |  | ACT | 21.26 |  | 7.26 |  | 14
ARCO-TULARE LAKE | 70 | ETL.8460 |  | ACT | 16.11 |  |  |  | 16.11
ARCO-TWISSELMAN | 70 | ETL.8470 |  | ACT | 6.46 |  |  |  | 6.46
ARMSTRONG TAP | 70 | ETL.8722 |  | ACT | 0.44 |  |  |  | 0.44
ARVIN EDISON TAP | 115 | ETL.4141 |  | ACT | 1.06 |  |  |  | 1.06
ATASCADERO-CAYUCOS | 70 | ETL.8480 |  | ACT | 11.79 | 5.36 | 3.59 |  | 2.84
ATASCADERO-SAN LUIS OBISPO | 70 | ETL.8490 |  | ACT | 15.52 | 3.3 | 7.86 |  | 4.36
ATLANTIC-GOLD HILL | 230 | ETL.4330 |  | ACT | 11.11 |  |  | 0.01 | 11.1
ATLANTIC-PLEASANT GROVE #1 | 115 | ETL.6190 |  | ACT | 5.33 |  |  |  | 5.33
ATLANTIC-PLEASANT GROVE #2 | 115 | ETL.9420 |  | ACT | 5.36 |  |  |  | 5.36
ATWATER-CRESSEY | 115 | ETL.1033 |  | ACT | 5.91 |  |  |  | 5.91
ATWATER-EL CAPITAN | 115 | ETL.1020 |  | ACT | 7.31 |  |  |  | 7.31
ATWATER-LIVINGSTON-MERCED | 115 | ETL.1030 |  | ACT | 24.26 |  |  |  | 24.26
AUBERRY TAP | 70 | ETL.9331 |  | ACT | 2.28 |  | 2.28 |  | 0
AUBURN TAP | 60 | ETL.6992 |  | ACT | 0.75 |  |  |  | 0.75
AVENAL TAP | 70 | ETL.8702 |  | ACT | 5.4 |  |  |  | 5.4
BADGER CREEK (PSE) TAP | 115 | ETL.1932 |  | ACT | 1.07 |  |  |  | 1.07
BADGER HILL TAP | 70 | ETL.8452 |  | ACT | 1.56 |  |  |  | 1.56
BAHIA-MORAGA | 230 | ETL.4340 |  | ACT | 26.92 | 4.3 | 12.25 |  | 10.37
BAIR-BELMONT | 115 | ETL.1040 |  | ACT | 3.64 |  |  |  | 3.64
BAIR-COOLEY LANDING #1 | 60 | ETL.6200 |  | ACT | 5.56 |  |  |  | 5.56
BAIR-COOLEY LANDING #2 | 60 | ETL.6210 |  | ACT | 5.6 |  |  |  | 5.6
BAKERSFIELD #2 TAP | 230 | ETL.5171 |  | ACT | 6.97 |  |  |  | 6.97
BALCH-MCCALL | 230 | ETL.4350 |  | ACT | 39.76 |  | 20.2 | 0.27 | 19.29
BALCH-SANGER | 115 | ETL.1050 |  | ACT | 35.63 |  | 19.85 | 0.12 | 15.66
BARKER SLOUGH TAP | 115 | ETL.1141 |  | ACT | 1.63 |  |  |  | 1.63
BARTON-AIRWAYS-SANGER | 115 | ETL.1060 |  | ACT | 11.57 |  |  |  | 11.57
BASALT #1 TAP | 60 | ETL.8181 |  | ACT | 1.18 |  |  |  | 1.18
BEALE AFB (WAPA) #1 TAP | 60 | ETL.8001 |  | ACT | 0.11 |  | 0.11 |  | 0
BEALE AFB (WAPA) #2 TAP | 60 | ETL.7971 |  | ACT | 0.14 |  | 0.14 |  | 0
BEAR CANYON TAP | 230 | ETL.1182 |  | ACT | 0.02 | 0.02 |  |  | 0
BEAR MTN TAP | 115 | ETL.4131 |  | ACT | 1.27 |  |  |  | 1.27
BEARDSLEY TAP | 115 | ETL.1401 |  | ACT | 2.2 | 2.15 | 0.02 |  | 0.03
BELDEN TAP | 230 | ETL.4441 |  | ACT | 0.02 |  | 0.02 |  | 0
BELL-PLACER | 115 | ETL.4395 |  | ACT | 7.94 |  | 2.86 |  | 5.08
BELLE HAVEN #1 TAP | 60 | ETL.6201 |  | ACT | 0.42 |  |  |  | 0.42
BELLE HAVEN #2 TAP | 60 | ETL.6211 |  | ACT | 0.41 |  |  |  | 0.41
BELLOTA-COTTLE | 230 | ETL.4360 |  | ACT | 19.84 |  |  |  | 19.84
BELLOTA-RIVERBANK | 115 | ETL.3480 |  | ACT | 18.87 |  |  |  | 18.87
BELLOTA-RIVERBANK-MELONES SW STA | 115 | ETL.1070 |  | ACT | 44.65 |  | 11.19 |  | 33.46
BELLOTA-TESLA #2 | 230 | ETL.4370 |  | ACT | 37.94 |  |  |  | 37.94
BELLOTA-WARNERVILLE | 230 | ETL.4380 |  | ACT | 22.47 |  |  |  | 22.47
BELLOTA-WEBER | 230 | ETL.4390 |  | ACT | 14.26 |  |  |  | 14.26
BELRIDGE TAP | 115 | ETL.2631 |  | ACT | 6.94 |  |  |  | 6.94
BERRENDA A TAP | 70 | ETL.8441 |  | ACT | 2.31 |  |  |  | 2.31
BERRENDA C TAP | 70 | ETL.8443 |  | ACT | 1.87 |  |  |  | 1.87
BIOLA-GLASS-MADERA | 70 | ETL.9350 |  | ACT | 18.8 |  |  |  | 18.8
BIRDS LANDING SW STA-CONTRA COSTA PP | 230 | ETL.5830 |  | ACT | 10.2 |  |  |  | 10.2
BIRDS LANDING SW STA-CONTRA COSTA SUB | 230 | ETL.6161 |  | ACT | 9.46 |  |  |  | 9.46
BIRDS LANDING SW STA-RUSSELL | 230 | ETL.6602 |  | ACT | 0.11 |  |  |  | 0.11
BIRDS LANDING SW STA-SHILOH | 230 | ETL.1413 |  | ACT | 0.11 |  |  |  | 0.11
BITTERWATER SW STA-WHEELER RIDGE #2 | 230 | ETL.5200 |  | ACT | 27.35 |  |  |  | 27.35
BIXLER TAP | 60 | ETL.7056 |  | ACT | 0.55 |  |  |  | 0.55
BLACK TAP | 230 | ETL.5431 | POWERGEN | ACT | 0.51 |  | 0.51 |  | 0
BLUE CHIP MILLING TAP | 60 | ETL.6802 |  | ACT | 0.42 |  |  |  | 0.42
BLUE LAKE TAP | 60 | ETL.6801 |  | ACT | 3.7 |  |  |  | 3.7
BOGUE-RIO OSO | 115 | ETL.1100 |  | ACT | 21.24 |  |  |  | 21.24
BOLLMAN #1 TAP | 115 | ETL.3321 |  | ACT | 2.14 |  |  |  | 2.14
BOLLMAN #2 TAP | 115 | ETL.3331 |  | ACT | 2.19 |  |  |  | 2.19
BOLTHOUSE FARMS TAP | 115 | ETL.4132 |  | ACT | 0.11 |  |  |  | 0.11
BONITA TAP | 70 | ETL.9352 |  | ACT | 3.03 |  |  |  | 3.03
BORDEN-COPPERMINE | 70 | ETL.8500 |  | ACT | 19.92 |  |  |  | 19.92
BORDEN-GLASS | 70 | ETL.8510 |  | ACT | 6.64 |  |  |  | 6.64
BORDEN-GREGG #1 | 230 | ETL.1082 |  | ACT | 6.21 |  |  |  | 6.21
BORDEN-GREGG #2 | 230 | ETL.4400 |  | ACT | 6.21 |  |  |  | 6.21
BORDEN-LOTUS PV | 70 | ETL.1122 |  | ACT | 0.16 |  |  |  | 0.16
BORDEN-MADERA #1 | 70 | ETL.8710 |  | ACT | 4.92 |  |  |  | 4.92
BORDEN-MADERA #2 | 70 | ETL.8520 |  | ACT | 5.8 |  |  |  | 5.8
BOTTLE ROCK TAP D.W.R. | 230 | ETL.4771 |  | ACT | 1.07 | 1.07 |  |  | 0
BRENTWOOD-KELSO | 230 | ETL.4410 |  | ACT | 16.41 |  | 5.2 |  | 11.21
BRICEBURG JCT-MARIPOSA TAP | 70 | ETL.8651 |  | ACT | 7.78 |  | 7.78 |  | 0
BRIDGEVILLE-COTTONWOOD | 115 | ETL.1110 |  | ACT | 86.08 | 1 | 79.04 |  | 6.04
BRIDGEVILLE-GARBERVILLE | 60 | ETL.6220 |  | ACT | 36.15 | 9.8 | 7.13 |  | 19.22
BRIGHTON-BELLOTA | 230 | ETL.4420 |  | ACT | 42.51 |  |  |  | 42.51
BRIGHTON-DAVIS | 115 | ETL.1140 |  | ACT | 42.72 |  |  |  | 42.72
BRIGHTON-DAVIS | 115 | ETL.1140 |  | IDL | 3.59 |  |  |  | 3.59
BRIGHTON-GRAND ISLAND #1 | 115 | ETL.1150 |  | ACT | 24.99 |  |  |  | 24.99
BRIGHTON-GRAND ISLAND #2 | 115 | ETL.1160 |  | ACT | 25.04 |  |  |  | 25.04
BRIGHTON-OLEUM JCT | 0 | ETL.1162 |  | IDL | 0.3 |  |  |  | 0.3
BRIONES TAP | 60 | ETL.7055 |  | ACT | 6.99 | 0.22 | 4.28 |  | 2.49
BRITTON-MONTA VISTA | 115 | ETL.1170 |  | ACT | 7.23 |  |  |  | 7.23
BRUNSWICK #1 TAP | 115 | ETL.1422 |  | ACT | 6.98 | 5.95 | 0.61 | 0.03 | 0.39
BRUNSWICK #2 TAP | 115 | ETL.1431 |  | ACT | 7 | 5.97 | 0.63 | 0 | 0.4
BUCKS CREEK-ROCK CREEK-CRESTA | 230 | ETL.4430 |  | ACT | 9.37 | 0.07 | 9.3 |  | 0
BUELLTON TAP | 115 | ETL.1201 |  | ACT | 1.75 |  | 1.39 |  | 0.36
BUENA VISTA BIOMASS POWER TAP | 60 | ETL.8252 |  | ACT | 1.01 |  | 0.32 |  | 0.69
BUENA VISTA PUMPING PLANT #1 TAP | 230 | ETL.5191 |  | ACT | 1.18 |  |  |  | 1.18
BUENA VISTA PUMPING PLANT #2 TAP | 230 | ETL.5201 |  | ACT | 1.21 |  |  |  | 1.21
BURNEY FOREST PRODUCTS TAP | 230 | ETL.5391 |  | ACT | 0.04 |  |  |  | 0.04
BURNEY TAP | 60 | ETL.7041 |  | ACT | 1.07 |  |  |  | 1.07
BURNS-LONE STAR #1 | 60 | ETL.6230 |  | ACT | 5.44 | 3.23 | 2.21 |  | 0
BURNS-LONE STAR #2 | 60 | ETL.6240 |  | ACT | 6.31 | 4.9 | 1.4 |  | 0.01
BUTT VALLEY-CARIBOU | 115 | ETL.1180 | POWERGEN | ACT | 7.44 |  | 7.09 |  | 0.35
BUTTE-CHICO #1 | 60 | ETL.6250 |  | ACT | 0.79 |  |  |  | 0.79
BUTTE-CHICO #2 | 60 | ETL.6260 |  | ACT | 0.74 |  |  |  | 0.74
BUTTE-ESQUON | 60 | ETL.6270 |  | ACT | 9.87 |  |  |  | 9.87
BUTTE-SYCAMORE CREEK | 115 | ETL.1190 |  | ACT | 18.14 |  |  |  | 18.14
Bellota-North Central Valley | 115 | ETL.1374 |  | ACT | 0.03 |  |  |  | 0.03
CABRILLO-SANTA YNEZ SW STA | 115 | ETL.1200 |  | ACT | 14.59 |  | 13.18 |  | 1.41
CACHE SLOUGH TAP | 60 | ETL.6741 |  | ACT | 6.82 |  |  |  | 6.82
CADET TAP | 70 | ETL.9232 |  | ACT | 0.06 |  |  |  | 0.06
CAL PEAK-VACA | 115 | ETL.4230 |  | ACT | 0.11 |  |  |  | 0.11
CAL WATER TAP | 115 | ETL.3951 |  | ACT | 2.15 |  |  |  | 2.15
CALIENTE SW STA-MIDWAY #1 | 230 | ETL.5216 |  | ACT | 27.17 |  |  |  | 27.17
CALIENTE SW STA-MIDWAY #2 | 230 | ETL.5226 |  | ACT | 27.16 |  |  |  | 27.16
CALIFORNIA AVE-MCCALL | 115 | ETL.2360 |  | ACT | 23.66 |  |  |  | 23.66
CALIFORNIA FLATS SW STA-GATES | 230 | ETL.5281 |  | ACT | 22.57 |  | 1.5 |  | 21.07
CALLENDER SW STA-MESA | 115 | ETL.1210 |  | ACT | 13.76 |  | 5.61 | 0.22 | 7.93
CALPINE-WEST FORD FLAT | 230 | ETL.1183 |  | ACT | 0.05 | 0.05 |  |  | 0
CALVO TAP | 60 | ETL.7251 |  | ACT | 0.54 |  |  |  | 0.54
CAMANCHE PUMPING PLANT TAP | 230 | ETL.1230 |  | ACT | 0.45 |  |  |  | 0.45
CAMANCHE TAP | 115 | ETL.1691 |  | ACT | 6.71 |  |  |  | 6.71
CAMDEN-KINGSBURG | 70 | ETL.8653 |  | ACT | 14.93 |  |  |  | 14.93
CAMP EVERS-PAUL SWEET | 115 | ETL.1220 |  | ACT | 5.22 | 4.59 |  |  | 0.63
CANANDAIGUA WINERY TAP | 70 | ETL.9351 |  | ACT | 0.29 |  |  |  | 0.29
CANTUA TAP | 115 | ETL.3251 |  | ACT | 1.83 |  |  |  | 1.83
CAPE HORN TAP | 60 | ETL.6761 |  | ACT | 0.31 |  | 0.31 |  | 0
CARBERRY SW STA-ROUND MTN | 230 | ETL.5410 |  | ACT | 12.61 | 0.25 | 12.36 |  | 0
CARBONA #2 TAP | 60 | ETL.7233 |  | ACT | 5.6 |  |  |  | 5.6
CARIBOU #2 | 60 | ETL.6280 |  | ACT | 30.62 |  | 27.77 |  | 2.85
CARIBOU-PALERMO | 115 | ETL.3190 |  | IDL | 0.02 |  | 0.02 |  | 0 | Idle Section
CARIBOU-PLUMAS JCT | 60 | ETL.6290 |  | ACT | 21.26 |  | 16.4 |  | 4.86
CARIBOU-TABLE MTN | 230 | ETL.4440 |  | ACT | 54.34 | 9.09 | 39.35 |  | 5.9
CARIBOU-WESTWOOD | 60 | ETL.6300 |  | ACT | 20.99 |  | 20.01 |  | 0.98
CARIBOU-WESTWOOD | 60 | ETL.6300 |  | IDL | 0.06 |  |  |  | 0.06
CARNATION TAP | 70 | ETL.8901 |  | ACT | 0.54 |  |  |  | 0.54
CARNERAS-TAFT | 70 | ETL.8540 |  | ACT | 34.8 |  |  |  | 34.8
CARQUINEZ #1 TAP | 115 | ETL.1831 |  | ACT | 0.51 |  |  |  | 0.51
CARQUINEZ #2 TAP | 115 | ETL.1841 |  | ACT | 0.52 |  |  |  | 0.52
CARRIZO PLAINS TAP | 115 | ETL.3961 |  | ACT | 0.04 |  |  |  | 0.04
CARUTHERS-LEMOORE NAS-CAMDEN | 70 | ETL.8550 |  | ACT | 25.1 |  |  |  | 25.1
CASCADE-BENTON-DESCHUTES | 60 | ETL.6310 |  | ACT | 15.97 |  | 9.56 |  | 6.41
CASCADE-COTTONWOOD | 115 | ETL.1240 |  | ACT | 19.47 |  | 12.18 |  | 7.29
CASTAIC TAP | 70 | ETL.9253 |  | ACT | 0.02 |  | 0.02 |  | 0
CASTRO VALLEY-NEWARK | 230 | ETL.4450 |  | ACT | 22.71 | 5.6 | 5.96 | 0.48 | 10.67
CAWELO B TAP | 70 | ETL.8871 |  | ACT | 0.4 |  |  |  | 0.4
CAWELO C TAP | 115 | ETL.2122 |  | ACT | 1.33 |  |  |  | 1.33
CAYUCOS-CAMBRIA | 70 | ETL.8560 |  | ACT | 17.73 |  | 7.69 |  | 10.04
CELERON TAP | 70 | ETL.8541 |  | ACT | 0.04 |  |  |  | 0.04
CENTERVILLE-TABLE MTN | 60 | ETL.6320 |  | ACT | 21.51 | 4.1 | 3.81 |  | 13.6
CENTERVILLE-TABLE MTN-OROVILLE | 60 | ETL.6330 |  | ACT | 26.1 | 3.84 | 6.34 |  | 15.92
CERTAINTEED TAP | 115 | ETL.2111 |  | ACT | 2.52 |  |  |  | 2.52
CHARCA-FAMOSO | 115 | ETL.2621 |  | ACT | 7.15 |  |  |  | 7.15
CHCF TAP | 115 | ETL.7011 |  | ACT | 3 |  |  |  | 3
CHENEY #1 TAP | 115 | ETL.3231 |  | ACT | 3.99 |  |  |  | 3.99
CHENEY #2 TAP | 115 | ETL.3261 |  | ACT | 1.84 |  |  |  | 1.84
CHEVRON (LOST HILLS) TAP | 70 | ETL.8472 |  | ACT | 14.75 |  |  |  | 14.75
CHEVRON PIPELINE KETTLEMAN TAP | 70 | ETL.8703 |  | ACT | 1.17 |  |  |  | 1.17
CHINESE CAMP (ULTRA POWER) TAP | 115 | ETL.2392 |  | ACT | 2.1 |  | 1.54 |  | 0.56
CHOWCHILLA #1 TAP | 115 | ETL.2112 |  | ACT | 1.24 |  |  |  | 1.24
CHOWCHILLA-KERCKHOFF | 115 | ETL.1250 |  | ACT | 42.52 |  | 9.5 |  | 33.02
CHRISTIE-FRANKLIN #1 | 60 | ETL.6350 |  | ACT | 3.44 |  | 1.85 |  | 1.59
CHRISTIE-FRANKLIN #1 | 60 | ETL.6350 |  | IDL | 1.57 |  |  |  | 1.57
CHRISTIE-FRANKLIN #2 | 60 | ETL.6360 |  | ACT | 3.45 |  | 1.84 |  | 1.61
CHRISTIE-FRANKLIN #2 (12KV) | 60 | ETL.6360 |  | IDL | 1.62 |  |  |  | 1.62
CHRISTIE-SOBRANTE | 115 | ETL.1260 |  | ACT | 7.84 |  | 7.74 |  | 0.1
CHRISTIE-WILLOW PASS | 60 | ETL.6370 |  | ACT | 15.93 |  | 3.83 |  | 12.1
CISCO GROVE TAP | 60 | ETL.8061 |  | ACT | 0.34 |  |  | 0.16 | 0.18
CITY #1 TAP | 115 | ETL.1382 |  | ACT | 0.07 |  |  |  | 0.07
CITY #2 TAP | 115 | ETL.1371 |  | ACT | 1.37 |  |  |  | 1.37
CLAY-MARTEL | 60 | ETL.8250 |  | ACT | 16.98 |  | 14.52 |  | 2.46
CLAYTON-MEADOW LANE | 115 | ETL.1270 |  | ACT | 7.06 |  |  |  | 7.06
CLEAR LAKE-HOPLAND | 60 | ETL.6390 |  | ACT | 11.53 |  | 7.33 |  | 4.2
CLEAR LAKE-KONOCTI | 60 | ETL.6852 |  | ACT | 10.99 |  | 4.94 |  | 6.05
CLOVER CREEK TAP | 60 | ETL.7291 |  | ACT | 0.02 | 0.02 |  |  | 0
COALINGA #1-COALINGA #2 | 70 | ETL.8570 |  | ACT | 8.61 |  |  |  | 8.61
COALINGA #1-SAN MIGUEL | 70 | ETL.8580 |  | ACT | 38.01 |  | 17.45 | 0.44 | 20.12
COALINGA COGEN TAP | 70 | ETL.8571 |  | ACT | 4.91 |  |  |  | 4.91
COBURN-BASIC ENERGY | 60 | ETL.6400 |  | ACT | 3.39 |  |  |  | 3.39
COBURN-LAS AGUILAS SW STA | 230 | ETL.4460 |  | ACT | 63.97 |  | 41.16 | 0.01 | 22.8
COBURN-OIL FIELDS #1 | 60 | ETL.6410 |  | ACT | 29.46 |  |  | 0 | 29.46
COBURN-OIL FIELDS #2 | 60 | ETL.6420 |  | ACT | 31.05 |  |  |  | 31.05
COGENERATION NATIONAL TAP | 60 | ETL.8323 |  | ACT | 0.56 |  |  |  | 0.56
COLEMAN HATCHERY TAP | 60 | ETL.8428 |  | ACT | 0.56 |  |  |  | 0.56
COLEMAN-COTTONWOOD | 60 | ETL.6430 |  | ACT | 8.58 |  | 1.11 | 0.17 | 7.3
COLEMAN-RED BLUFF | 60 | ETL.6440 |  | ACT | 48.31 |  | 20.25 |  | 28.06
COLEMAN-SOUTH | 60 | ETL.6450 |  | ACT | 13.39 |  | 13.39 |  | 0
COLES LEVEE TAP | 115 | ETL.2593 |  | ACT | 0.22 |  |  |  | 0.22
COLGATE PH-COLGATE SW STA | 60 | ETL.6460 |  | ACT | 0.19 |  | 0.19 |  | 0
COLGATE-ALLEGHANY | 60 | ETL.6470 |  | ACT | 24.53 | 19.92 | 4.61 |  | 0
COLGATE-CHALLENGE | 60 | ETL.6480 |  | ACT | 13.04 | 11.62 | 1.43 |  | -0.01
COLGATE-GRASS VALLEY | 60 | ETL.6490 |  | ACT | 13.17 | 1.87 | 10.03 |  | 1.27
COLGATE-PALERMO | 60 | ETL.6500 |  | ACT | 22.65 |  | 21.72 |  | 0.93
COLGATE-RIO OSO | 230 | ETL.5900 |  | ACT | 40.89 |  | 11.86 |  | 29.03
COLGATE-SMARTVILLE #1 | 60 | ETL.6510 |  | ACT | 11.26 |  | 11.26 |  | 0
COLGATE-SMARTVILLE #2 | 60 | ETL.6520 |  | ACT | 11.19 |  | 11.19 |  | 0
COLLINS PINE TAP | 60 | ETL.7001 |  | ACT | 1 |  | 0.08 |  | 0.92
COLUMBIA SOLAR 115kV TAP | 115 | ETL.3301 |  | ACT | 0.51 |  |  |  | 0.51
COLUMBUS-MAGUNDEN | 115 | ETL.1233 |  | ACT | 3.69 |  |  |  | 3.69
COLUSA JCT #1 | 60 | ETL.8390 |  | ACT | 16.98 |  |  |  | 16.98
CONTRA COSTA #1 | 115 | ETL.1280 |  | ACT | 11.15 |  |  |  | 11.15
CONTRA COSTA #2 | 115 | ETL.1290 |  | ACT | 1.43 |  |  |  | 1.43
CONTRA COSTA PP-CONTRA COSTA SUB | 230 | ETL.4470 |  | ACT | 1.89 |  |  |  | 1.89
CONTRA COSTA-BALFOUR | 60 | ETL.8420 |  | ACT | 11.54 |  |  |  | 11.54
CONTRA COSTA-BRENTWOOD | 230 | ETL.4480 |  | ACT | 10.06 |  |  |  | 10.06
CONTRA COSTA-DELTA SWITCHYARD | 230 | ETL.4490 |  | ACT | 18.46 |  | 5.19 |  | 13.27
CONTRA COSTA-DU PONT | 60 | ETL.6530 |  | ACT | 2.14 |  |  |  | 2.14
CONTRA COSTA-LAS POSITAS | 230 | ETL.4510 |  | ACT | 23.83 | 0.88 | 10.98 |  | 11.97
CONTRA COSTA-LONE TREE | 230 | ETL.4535 |  | ACT | 5.61 |  |  |  | 5.61
CONTRA COSTA-MORAGA #1 | 230 | ETL.5452 |  | ACT | 26.76 | 4.3 | 11.36 |  | 11.1
CONTRA COSTA-MORAGA #2 | 230 | ETL.5453 |  | ACT | 26.84 | 4.38 | 11.33 |  | 11.13
CONTRA COSTA-PITTSBURG | 60 | ETL.6540 |  | ACT | 6.28 |  |  |  | 6.28
CONTRA COSTA-SHELL CHEMICAL#1(21KV) | 60 | ETL.6550 |  | IDL | 9.9 |  |  |  | 9.9
COOLEY LANDING-LOS ALTOS | 60 | ETL.6560 |  | ACT | 14.94 |  |  |  | 14.94
COOLEY LANDING-LOS ALTOS (I2KV) | 60 | ETL.6560 |  | IDL | 1.4 |  |  |  | 1.4
COOLEY LANDING-PALO ALTO | 115 | ETL.1300 |  | ACT | 2.72 |  |  |  | 2.72
COOLEY LANDING-STANFORD | 60 | ETL.6570 |  | ACT | 6.02 |  |  |  | 6.02
COPPERMINE-TIVY VALLEY | 70 | ETL.8590 |  | ACT | 24 |  | 0.89 | 0.02 | 23.09
COPUS-OLD RIVER | 70 | ETL.8970 |  | ACT | 19.62 |  |  |  | 19.62
CORCORAN-ANGIOLA | 70 | ETL.8600 |  | ACT | 8.95 |  |  |  | 8.95
CORCORAN-GUERNSEY | 70 | ETL.9360 |  | ACT | 13.49 |  |  |  | 13.49
CORCORAN-OLIVE SW STA | 115 | ETL.1310 |  | ACT | 18.43 |  |  |  | 18.43
CORCORAN-OLIVE SW STA | 115 | ETL.1310 |  | IDL | 0.02 |  |  |  | 0.02
CORDELIA #1 TAP | 60 | ETL.8182 |  | ACT | 7.69 |  | 4.56 |  | 3.13
CORDELIA #2 TAP | 60 | ETL.8184 |  | ACT | 6.87 |  | 2.99 |  | 3.88
CORONA-LAKEVILLE | 115 | ETL.4311 |  | ACT | 5.79 |  |  |  | 5.79
CORTINA #1 | 60 | ETL.6580 |  | ACT | 26.28 |  |  |  | 26.28
CORTINA #2 | 60 | ETL.6590 |  | ACT | 40.66 |  |  |  | 40.66
CORTINA #3 | 60 | ETL.6600 |  | ACT | 24.8 |  |  |  | 24.8
CORTINA #4 | 60 | ETL.6610 |  | ACT | 45.24 |  |  | 0.15 | 45.09
CORTINA-MENDOCINO #1 | 115 | ETL.1330 |  | ACT | 60.95 | 4.56 | 48.77 |  | 7.62
CORTINA-VACA | 230 | ETL.4540 |  | ACT | 53.22 |  | 2.25 |  | 50.97
COTTLE-MELONES | 230 | ETL.4530 |  | ACT | 25.92 |  | 5.29 |  | 20.63
COTTONWOOD #1 | 60 | ETL.6620 |  | ACT | 48.17 |  | 9.72 |  | 38.45
COTTONWOOD #2 | 60 | ETL.6630 |  | ACT | 23.63 |  | 9.72 |  | 13.91
COTTONWOOD-BENTON #1 | 60 | ETL.6640 |  | ACT | 15.53 |  | 5.53 |  | 10
COTTONWOOD-BENTON #2 | 60 | ETL.6650 |  | ACT | 14.67 | 2.99 | 9.6 |  | 2.08
COTTONWOOD-DELEVAN #1 | 230 | ETL.4550 |  | ACT | 71.55 |  | 9.71 |  | 61.84
COTTONWOOD-DELEVAN #2 | 230 | ETL.4580 |  | ACT | 71.54 |  | 9.71 |  | 61.83
COTTONWOOD-GLENN | 230 | ETL.4560 |  | ACT | 48.33 |  | 9.71 |  | 38.62
COTTONWOOD-LOGAN CREEK | 230 | ETL.4570 |  | ACT | 59.28 |  | 9.71 |  | 49.57
COTTONWOOD-PANORAMA | 115 | ETL.1340 |  | ACT | 2.95 |  | 2.08 |  | 0.87
COTTONWOOD-RED BLUFF | 60 | ETL.6660 |  | ACT | 16.78 |  | 10.54 |  | 6.24
COVE ROAD TAP | 230 | ETL.5421 |  | ACT | 0.11 |  | 0.11 |  | 0
COYOTE SW STA-METCALF | 230 | ETL.5092 |  | ACT | 0.88 |  |  |  | 0.88
CRAG VIEW-CASCADE | 115 | ETL.1350 |  | ACT | 21.61 | 2.41 | 17.96 |  | 1.24
CRAZY HORSE CANYON-HOLLISTER | 115 | ETL.2153 |  | ACT | 17.18 |  | 2.7 |  | 14.48
CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | 115 | ETL.2900 |  | ACT | 35.34 |  | 15.82 | 0.01 | 19.51
CRAZY HORSE CANYON-SALINAS-SOLEDAD #2 | 115 | ETL.2910 |  | ACT | 35.42 |  | 15.84 |  | 19.58
CRAZY HORSE CANYON-SAN BENITO | 115 | ETL.2152 |  | ACT | 8.94 |  | 2.64 |  | 6.3
CRESCENT SW STA-SCHINDLER | 70 | ETL.9180 |  | ACT | 10.8 |  |  |  | 10.8
CRESCENT SW STA-SCULPIN PV | 70 | ETL.1038 |  | ACT | 0.04 |  |  |  | 0.04
CRESCENT SW STA-STROUD | 70 | ETL.9190 |  | ACT | 3.62 |  |  |  | 3.62
CRESTA-RIO OSO | 230 | ETL.4590 |  | ACT | 64.79 | 8.93 | 18.2 |  | 37.66
CROW CREEK SW STA-FRONTIER SOLAR PV | 60 | ETL.7859 |  | ACT | 0.02 |  |  |  | 0.02
CROW CREEK SW STA-NEWMAN | 60 | ETL.7860 |  | ACT | 11.14 |  |  |  | 11.14
CROW CREEK SW STA-PAULSELL PV | 60 | ETL.1462 |  | ACT | 0.04 |  |  |  | 0.04
CROWS LANDING TAP | 60 | ETL.7871 |  | ACT | 5.28 |  |  |  | 5.28
CRUSHER TAP | 60 | ETL.6241 |  | ACT | 1.94 |  | 1.94 |  | 0
CRYSTAL SPRINGS TAP | 60 | ETL.7211 |  | ACT | 0.28 |  | 0.28 |  | 0
CYMRIC TAP | 115 | ETL.2582 |  | ACT | 0.18 |  |  |  | 0.18
DAIRYLAND-MENDOTA | 115 | ETL.1360 |  | ACT | 28.69 |  |  |  | 28.69
DANISH CREAMERY TAP | 115 | ETL.2362 |  | ACT | 1.2 |  |  |  | 1.2
DE FRANCESCO TAP | 115 | ETL.3245 |  | ACT | 1.03 |  |  |  | 1.03
DEEPWATER #1 TAP | 115 | ETL.4121 |  | ACT | 2.29 |  |  |  | 2.29
DEEPWATER #2 TAP | 115 | ETL.4111 |  | ACT | 2.45 |  |  |  | 2.45
DEER CREEK-DRUM | 60 | ETL.6690 | PGE | ACT | 6.27 | 6.27 |  |  | 0
DEL MAR-ATLANTIC #1 | 60 | ETL.1410 |  | ACT | 2.78 |  |  |  | 2.78
DEL MAR-ATLANTIC #2 | 60 | ETL.6170 |  | ACT | 4.39 |  |  |  | 4.39
DEL MONTE-FORT ORD #1 | 60 | ETL.8400 |  | ACT | 6.13 |  | 0.25 |  | 5.88
DEL MONTE-FORT ORD #2 | 60 | ETL.8422 |  | ACT | 5.6 |  | 0.06 |  | 5.54
DEL MONTE-MONTEREY | 60 | ETL.6700 |  | ACT | 2.53 |  |  |  | 2.53
DEL MONTE-VIEJO | 60 | ETL.6710 |  | ACT | 8.67 |  | 5.29 |  | 3.38
DELEVAN-CORTINA | 230 | ETL.4384 |  | ACT | 17.89 |  |  |  | 17.89
DELEVAN-VACA #1 | 230 | ETL.5010 |  | ACT | 71.04 |  | 2.06 |  | 68.98
DELEVAN-VACA #2 | 230 | ETL.4231 |  | ACT | 71.07 |  | 1.67 |  | 69.4
DELEVAN-VACA #3 | 230 | ETL.4790 |  | ACT | 71.09 |  | 1.49 |  | 69.6
DELTA SWITCHING YARD-TESLA | 230 | ETL.4600 |  | ACT | 7.7 |  |  |  | 7.7
DELTA-MTN GATE JCT | 60 | ETL.6750 |  | ACT | 15.11 | 2.18 | 11.65 |  | 1.28
DERRICK TAP | 70 | ETL.8573 |  | ACT | 0.85 |  |  |  | 0.85
DESABLA-CENTERVILLE | 60 | ETL.6720 |  | ACT | 5.89 | 5.89 |  |  | 0
DIABLO PP STANDBY SUPPLY | 230 | ETL.4610 |  | ACT | 0.48 | 0.48 |  |  | 0
DIABLO UNIT #1 | 500 | ETL.5940 |  | ACT | 0.54 | 0.54 |  |  | 0
DIABLO UNIT #2 | 500 | ETL.5950 |  | ACT | 0.57 | 0.57 |  |  | 0
DIABLO-GATES #1 | 500 | ETL.5960 |  | ACT | 79.23 | 10.56 | 16.5 | 0.08 | 52.09
DIABLO-MESA | 230 | ETL.4620 |  | ACT | 40.34 | 7.65 | 27.83 |  | 4.86
DIABLO-MIDWAY #2 | 500 | ETL.5970 |  | ACT | 84.09 | 15.47 | 29.47 |  | 39.15
DIABLO-MIDWAY #3 | 500 | ETL.5980 |  | ACT | 84.67 | 15.56 | 29.34 |  | 39.77
DINOSAUR POINT TAP | 70 | ETL.8961 |  | ACT | 2 |  | 0.51 |  | 1.49
DINUBA ENERGY TAP | 70 | ETL.9051 |  | ACT | 3.16 |  |  |  | 3.16
DINUBA-OROSI | 70 | ETL.8610 |  | ACT | 9.83 |  |  |  | 9.83
DISCOVERY TAP | 115 | ETL.1921 |  | ACT | 2.1 |  |  |  | 2.1
DISTRICT 1001 TAP | 60 | ETL.7701 |  | ACT | 1.45 |  |  |  | 1.45
DISTRICT 1500 TAP | 60 | ETL.7711 |  | ACT | 3.61 |  |  |  | 3.61
DIVIDE-CABRILLO #1 | 115 | ETL.1380 |  | ACT | 14.6 |  | 6.29 |  | 8.31
DIVIDE-CABRILLO #2 | 115 | ETL.1370 |  | ACT | 11.55 |  | 6.05 |  | 5.5
DIVIDE-VANDENBERG #1 | 70 | ETL.8620 |  | ACT | 6.64 |  | 5.51 |  | 1.13
DIVIDE-VANDENBERG #2 | 70 | ETL.8630 |  | ACT | 6.57 |  | 5.45 |  | 1.12
DIXON LANDING-MCKEE | 115 | ETL.1390 |  | ACT | 8.3 |  |  |  | 8.3
DIXON-VACA #1 | 60 | ETL.6730 |  | ACT | 18.35 |  |  |  | 18.35
DIXON-VACA #2 | 60 | ETL.6740 |  | ACT | 26.77 |  |  |  | 26.77
DOLAN RD #1 TAP | 115 | ETL.2881 |  | ACT | 0.32 |  |  |  | 0.32
DOLAN RD #2 TAP | 115 | ETL.2891 |  | ACT | 0.33 |  |  |  | 0.33
DONNELLS-MI-WUK | 115 | ETL.1400 |  | ACT | 18.46 | 18.46 |  |  | 0
DOS AMIGOS PUMPING PLANT-PANOCHE | 230 | ETL.4630 |  | ACT | 23.67 |  |  |  | 23.67
DOUBLE C (PSE) TAP | 115 | ETL.1931 |  | ACT | 0.06 |  |  |  | 0.06
DRUM PH #2 TAP | 115 | ETL.6375 | POWERGEN | ACT | 0.09 | 0.09 |  |  | 0
DRUM-GRASS VALLEY-WEIMAR | 60 | ETL.6760 |  | ACT | 31.17 | 17.2 | 12.72 |  | 1.25
DRUM-HIGGINS | 115 | ETL.4393 |  | ACT | 43.53 | 19.01 | 23.87 |  | 0.65
DRUM-RIO OSO #1 | 115 | ETL.1420 |  | ACT | 44.64 | 14.06 | 17.9 |  | 12.68
DRUM-RIO OSO #2 | 115 | ETL.1430 |  | ACT | 44.65 | 14.08 | 17.87 |  | 12.7
DRUM-SPAULDING | 60 | ETL.6770 |  | ACT | 9.36 | 6.88 | 2.48 |  | 0
DRUM-SUMMIT #1 | 115 | ETL.1440 |  | ACT | 27.38 | 6.51 | 15.1 | 1.54 | 4.23
DRUM-SUMMIT #2 | 115 | ETL.1450 |  | ACT | 28.36 | 6.49 | 16.36 | 1.49 | 4.02
DUMBARTON-NEWARK | 115 | ETL.1460 |  | ACT | 7.14 |  |  |  | 7.14
DUNLAP TAP | 70 | ETL.9061 |  | ACT | 16.21 |  | 13.79 |  | 2.42
DUTCH FLAT #2 TAP | 115 | ETL.1421 |  | ACT | 0.43 | 0.43 |  |  | 0
EAGLE ROCK-CORTINA | 115 | ETL.1470 |  | ACT | 43.39 | 14.63 | 23 |  | 5.76
EAGLE ROCK-FULTON-SILVERADO | 115 | ETL.4392 |  | ACT | 46.62 | 41.49 | 2.45 |  | 2.68
EAGLE ROCK-FULTON-SILVERADO | 115 | ETL.4392 |  | IDL | 0.33 | 0.33 |  |  | 0 | Idle Section
EAGLE ROCK-REDBUD | 115 | ETL.1480 |  | ACT | 23.31 | 9.94 | 13.05 |  | 0.32
EAST DUBLIN (BART) TAP | 60 | ETL.7962 |  | ACT | 0.04 |  |  |  | 0.04
EAST GRAND - SOUTH SAN FRANSICO TRACTION POWER #1 | 115 | ETL.1302 |  | ACT | 0.09 |  |  |  | 0.09
EAST GRAND - SOUTH SAN FRANSICO TRACTION POWER #2 | 115 | ETL.1304 |  | ACT | 0.05 |  |  |  | 0.05
EAST GRAND-SAN MATEO | 115 | ETL.1490 |  | ACT | 7.89 |  |  |  | 7.89
EASTSHORE-CERBERUS | 115 | ETL.7252 |  | ACT | 0.48 |  |  |  | 0.48
EASTSHORE-CLAWITER #1 | 230 | ETL.1335 |  | ACT | 0.67 |  |  |  | 0.67
EASTSHORE-CLAWITER #2 | 230 | ETL.1333 |  | ACT | 0.62 |  |  |  | 0.62
EASTSHORE-DUMBARTON | 115 | ETL.1495 |  | ACT | 12.38 |  |  |  | 12.38
EASTSHORE-MT EDEN #1 | 115 | ETL.1500 |  | ACT | 1.04 |  |  |  | 1.04
EASTSHORE-MT EDEN #2 | 115 | ETL.1501 |  | ACT | 1 |  |  |  | 1
EASTSHORE-SAN MATEO | 230 | ETL.4650 |  | ACT | 12.43 |  |  |  | 12.43
EBMUD TAP | 115 | ETL.2081 |  | ACT | 0.02 |  |  |  | 0.02
EDES #1 TAP | 115 | ETL.3521 |  | ACT | 0.04 |  |  |  | 0.04
EDES #2 TAP | 115 | ETL.3142 |  | ACT | 0.04 |  |  |  | 0.04
EEL RIVER TAP | 60 | ETL.7101 |  | ACT | 2.31 |  |  |  | 2.31
EIGHT MILE ROAD-STAGG | 230 | ETL.5002 |  | ACT | 7.2 |  |  |  | 7.2
EIGHT MILE ROAD-TESLA | 230 | ETL.4660 |  | ACT | 26.64 |  |  |  | 26.64
EISEN TAP | 70 | ETL.8883 |  | ACT | 1.86 |  |  |  | 1.86
EL CAPITAN-WILSON | 115 | ETL.1510 |  | ACT | 8.12 |  |  |  | 8.12
EL DORADO-MISSOURI FLAT #1 | 115 | ETL.1530 |  | ACT | 14.43 | 3.84 | 8.91 | 0.22 | 1.46
EL DORADO-MISSOURI FLAT #2 | 115 | ETL.1540 |  | ACT | 14.4 | 3.84 | 8.85 | 0.23 | 1.48
EL PATIO-SAN JOSE A | 115 | ETL.1520 |  | ACT | 7.08 |  |  |  | 7.08
EL PECO TAP | 70 | ETL.9353 |  | ACT | 3.02 |  |  |  | 3.02
ELECTRA-BELLOTA | 230 | ETL.4670 |  | ACT | 29.23 |  | 12.78 |  | 16.45
ELK CREEK TAP | 60 | ETL.6921 |  | ACT | 20.44 |  | 3.58 |  | 16.86
ELK-GUALALA | 60 | ETL.8410 |  | ACT | 29.02 |  | 22.59 | 0.13 | 6.3
ELLIS TAP | 115 | ETL.4021 |  | ACT | 0.16 |  |  |  | 0.16
EMIDIO TAP | 70 | ETL.9291 |  | ACT | 3.07 |  |  |  | 3.07
ENCINAL TAP | 60 | ETL.7751 |  | ACT | 1.43 |  |  |  | 1.43
ESSEX JCT-ARCATA-FAIRHAVEN | 60 | ETL.6800 |  | ACT | 16.06 |  |  |  | 16.06
ESSEX JCT-ORICK | 60 | ETL.6810 |  | ACT | 31.28 |  |  | 1.57 | 29.71
EUREKA-STA A | 60 | ETL.6820 |  | ACT | 0.22 |  |  |  | 0.22
EVERGREEN-ALMADEN | 60 | ETL.6830 |  | ACT | 4.96 |  |  | 0.03 | 4.93
EVERGREEN-MABURY | 60 | ETL.6840 |  | ACT | 5.48 |  |  |  | 5.48
EXCELSIOR SW STA-CRE FIVE POINTS PV | 115 | ETL.3247 | PGE | ACT | 0.03 |  |  |  | 0.03
EXCELSIOR SW STA-SCHINDLER #1 | 115 | ETL.3248 |  | ACT | 5.24 |  |  |  | 5.24
EXCELSIOR SW STA-SCHINDLER #2 | 115 | ETL.3249 |  | ACT | 5.23 |  |  |  | 5.23
EXCHEQUER-INDIAN FLAT | 70 | ETL.8650 | PGE | ACT | 29.89 | 4 | 25.17 | 0.01 | 0.71
EXCHEQUER-LE GRAND | 115 | ETL.1560 |  | ACT | 29.75 |  |  |  | 29.75
EXCHEQUER-MARIPOSA | 70 | ETL.8640 |  | ACT | 19.48 |  | 10.62 |  | 8.86
FAIRHAVEN #1 | 60 | ETL.6850 |  | ACT | 0.47 |  |  |  | 0.47
FAIRHAVEN POWER CO TAP | 60 | ETL.6853 |  | ACT | 0.5 |  |  |  | 0.5
FAIRHAVEN-HUMBOLDT | 60 | ETL.6860 |  | ACT | 15.44 |  |  |  | 15.44
FAIRVIEW-MARTINEZ SW STA | 115 | ETL.2275 |  | ACT | 0.1 |  |  |  | 0.1
FAIRWAY #1 TAP | 115 | ETL.2451 |  | ACT | 2.83 |  |  |  | 2.83
FAIRWAY #2 TAP | 115 | ETL.3611 |  | ACT | 1.52 |  |  |  | 1.52
FELLOWS-MIDSUN | 115 | ETL.1570 |  | ACT | 4.93 |  |  |  | 4.93
FELLOWS-TAFT | 115 | ETL.1580 |  | ACT | 7.93 |  |  |  | 7.93
FIBREBOARD STANDARD TAP | 115 | ETL.1404 |  | ACT | 0.02 |  | 0.02 |  | 0
FIBREBOARD TAP | 115 | ETL.1291 |  | ACT | 0.19 |  |  |  | 0.19
FINK SW STA-PROXIMA SOLAR | 230 | ETL.1386 |  | PRP | 0.05 |  |  |  | 0.05
FINK SW STA-WESTLEY | 230 | ETL.1384 |  | ACT | 15.87 |  | 6.81 |  | 9.06
FITCH MTN #1 TAP | 60 | ETL.6891 |  | ACT | 0.85 |  | 0.15 |  | 0.7
FITCH MTN #2 TAP | 60 | ETL.6901 |  | ACT | 0.06 |  |  |  | 0.06
FIVE POINTS SW STA-HURON-GATES | 70 | ETL.9160 |  | ACT | 19.78 |  |  |  | 19.78
FIVE POINTS SW-WHITNEY POINT PV | 70 | ETL.1053 |  | ACT | 0.05 |  |  |  | 0.05
FLINT TAP | 115 | ETL.3341 |  | ACT | 1.96 |  | 1.48 |  | 0.48
FMC - SAN JOSE TRACTION POWER #1 | 115 | ETL.1344 |  | ACT | 0.21 |  |  |  | 0.21
FMC - SAN JOSE TRACTION POWER #2 | 115 | ETL.1346 |  | ACT | 0.19 |  |  |  | 0.19
FMC-SAN JOSE B | 115 | ETL.2021 |  | ACT | 1.59 |  |  |  | 1.59
FORBESTOWN TAP | 115 | ETL.4222 |  | ACT | 0.2 | 0.2 |  |  | 0
FORKS OF THE BUTTE TAP | 60 | ETL.6722 |  | ACT | 0.25 | 0.25 |  |  | 0
FORT BRAGG-ELK | 60 | ETL.2060 |  | ACT | 24.03 |  | 21.59 | 0.06 | 2.38
FORT ROSS-GUALALA | 60 | ETL.6980 |  | ACT | 29.76 |  | 29.61 |  | 0.15
FORT SEWARD TAP | 60 | ETL.6222 |  | ACT | 7.69 |  | 2.9 | 0.03 | 4.76
FRENCH MEADOWS-MIDDLE FORK | 60 | ETL.6870 |  | ACT | 13.15 | 13.15 |  |  | 0
FRESH EXPRESS TAP | 60 | ETL.7901 |  | ACT | 0.56 |  |  |  | 0.56
FRESNO COGEN (AGRICO) TAP | 70 | ETL.8741 |  | ACT | 3.17 |  |  |  | 3.17
FRIANT-COPPERMINE | 70 | ETL.8660 |  | ACT | 8.3 |  |  |  | 8.3
FRITO LAY TAP | 115 | ETL.2602 |  | ACT | 0.51 |  |  |  | 0.51
FROGTOWN #1 TAP | 115 | ETL.3831 |  | ACT | 0.12 |  | 0.12 |  | 0
FROGTOWN #2 TAP | 115 | ETL.3843 |  | ACT | 0.11 |  | 0.11 |  | 0
FRUITLAND TAP | 60 | ETL.6221 |  | ACT | 4.26 |  | 3.85 |  | 0.41
FRUITVALE TAP | 70 | ETL.8881 |  | ACT | 0.12 |  |  |  | 0.12
FULTON JCT-VACA | 115 | ETL.1590 |  | ACT | 11.93 |  | 2.83 | 0.13 | 8.97
FULTON-CALISTOGA | 60 | ETL.6880 |  | ACT | 50.35 | 41.39 | 2.9 |  | 6.06
FULTON-HOPLAND | 60 | ETL.6890 |  | ACT | 49.29 | 7.51 | 26.29 |  | 15.49
FULTON-IGNACIO #1 | 230 | ETL.4680 |  | ACT | 40.73 | 14.88 | 7.55 |  | 18.3
FULTON-LAKEVILLE | 230 | ETL.4950 |  | ACT | 25.51 | 15.24 | 6.43 |  | 3.84
FULTON-LAKEVILLE-IGNACIO | 230 | ETL.2823 |  | IDL | 1.59 | 0.44 | 0.54 |  | 0.61 | Idle Section
FULTON-MOLINO-COTATI | 60 | ETL.6910 |  | ACT | 20.52 |  | 1.77 |  | 18.75
FULTON-PUEBLO | 115 | ETL.1600 |  | ACT | 59.95 | 18.66 | 18.92 | 0.05 | 22.32
FULTON-SANTA ROSA #1 | 115 | ETL.1620 |  | ACT | 6.69 |  |  |  | 6.69
FULTON-SANTA ROSA #2 | 115 | ETL.1630 |  | ACT | 6.29 |  |  |  | 6.29
FULTON-WINDSOR | 60 | ETL.1024 |  | ACT | 6.59 |  |  |  | 6.59
GALLO-CRESSEY | 115 | ETL.1036 |  | ACT | 14.42 |  |  |  | 14.42
GALLO-LIVINGSTON | 115 | ETL.1032 |  | ACT | 4.2 |  |  |  | 4.2
GARBERVILLE-LAYTONVILLE | 60 | ETL.8365 |  | ACT | 39.98 |  | 10.28 |  | 29.7
GARCIA TAP | 60 | ETL.8411 |  | ACT | 3.04 |  | 3.04 |  | 0
GARDNER TAP | 70 | ETL.8971 |  | ACT | 3.77 |  |  |  | 3.77
GATES BK-12 | 230 | ETL.1222 |  | ACT | 0.29 |  |  |  | 0.29
GATES-ARCO | 230 | ETL.4690 |  | ACT | 35.02 |  |  |  | 35.02
GATES-CASTANEA | 230 | ETL.1223 |  | ACT | 0.42 |  |  |  | 0.42
GATES-COALINGA #2 | 70 | ETL.8680 |  | ACT | 17.33 |  |  |  | 17.33
GATES-FIFTH STANDARD SOLAR PV | 230 | ETL.1313 | PGE | ACT | 0.3 |  |  |  | 0.3
GATES-HURON | 70 | ETL.8690 |  | ACT | 4.5 |  |  |  | 4.5
GATES-JAYNE SW STA | 70 | ETL.8652 |  | ACT | 0.68 |  |  |  | 0.68
GATES-MIDWAY | 230 | ETL.4891 |  | ACT | 63.68 |  |  |  | 63.68
GATES-MIDWAY | 500 | ETL.5990 |  | ACT | 63.78 |  |  |  | 63.78
GATES-MUSTANG SW STA #1 | 230 | ETL.2604 |  | ACT | 12.96 |  |  |  | 12.96
GATES-MUSTANG SW STA #2 | 230 | ETL.2605 |  | ACT | 12.99 |  |  |  | 12.99
GATES-PANOCHE #1 | 230 | ETL.4720 |  | ACT | 43.59 |  |  |  | 43.59
GATES-PANOCHE #2 | 230 | ETL.4730 |  | ACT | 43.57 |  |  |  | 43.57
GATES-TULARE LAKE | 70 | ETL.8700 |  | ACT | 18.34 |  |  |  | 18.34
GEYSERS #11-EAGLE ROCK | 115 | ETL.4391 |  | ACT | 0.64 | 0.64 |  |  | 0
GEYSERS #12-FULTON | 230 | ETL.4750 |  | ACT | 24.09 | 18.9 | 3.57 |  | 1.62
GEYSERS #13 TAP | 230 | ETL.4781 |  | ACT | 2.06 | 2.06 |  |  | 0
GEYSERS #16 TAP | 230 | ETL.4760 |  | ACT | 1.29 | 1.29 |  |  | 0
GEYSERS #17-FULTON | 230 | ETL.4770 |  | ACT | 25.8 | 20.68 | 3.56 |  | 1.56
GEYSERS #17-FULTON | 230 | ETL.4770 |  | IDL | 0.33 | 0.33 |  |  | 0 | Idle Section
GEYSERS #18 TAP | 230 | ETL.4784 |  | ACT | 0.74 | 0.74 |  |  | 0
GEYSERS #20 TAP | 230 | ETL.4783 |  | ACT | 0.03 | 0.03 |  |  | 0
GEYSERS #3-CLOVERDALE | 115 | ETL.1650 |  | ACT | 12.06 | 10.88 | 0.02 |  | 1.16
GEYSERS #3-EAGLE ROCK | 115 | ETL.1660 |  | ACT | 1.77 | 1.77 |  |  | 0
GEYSERS #5-GEYSERS #3 | 115 | ETL.1670 |  | ACT | 0.49 | 0.49 |  |  | 0
GEYSERS #7-EAGLE ROCK | 115 | ETL.1680 | PGE | ACT | 1.16 | 1.16 |  |  | 0
GEYSERS #9-LAKEVILLE | 230 | ETL.4780 |  | ACT | 41.08 | 31.96 | 7.03 |  | 2.09
GIFFEN TAP | 70 | ETL.8985 |  | ACT | 4.95 |  |  |  | 4.95
GIFFEN-BURFORD | 70 | ETL.1352 |  | ACT | 0.04 |  |  |  | 0.04
GILL RANCH TAP | 115 | ETL.1742 |  | ACT | 9.15 |  |  |  | 9.15
GILROY ENERGY TAP | 115 | ETL.2151 |  | ACT | 0.28 |  |  |  | 0.28
GISH TAP | 115 | ETL.4031 |  | IDL | 0.96 |  |  |  | 0.96
GLENN #1 | 60 | ETL.6920 |  | ACT | 33.38 |  |  |  | 33.38
GLENN #2 | 60 | ETL.6930 |  | ACT | 34.68 |  |  | 0.26 | 34.42
GLENN #3 | 60 | ETL.6940 |  | ACT | 28.56 |  |  |  | 28.56
GLENN #4 | 60 | ETL.8424 |  | ACT | 12.48 |  |  |  | 12.48
GLENN #5 | 60 | ETL.8427 |  | ACT | 7.41 |  |  |  | 7.41
GLENN-DELEVAN | 230 | ETL.7042 |  | ACT | 37.44 |  |  |  | 37.44
GOLD HILL #1 | 60 | ETL.6950 |  | ACT | 32.36 | 8.54 | 13.08 |  | 10.74
GOLD HILL-BELLOTA-LOCKEFORD | 115 | ETL.1690 |  | ACT | 86.17 |  |  |  | 86.17
GOLD HILL-BELLOTA-LOCKEFORD | 115 | ETL.1690 |  | IDL | 1.1 |  |  |  | 1.1
GOLD HILL-CLARKSVILLE | 115 | ETL.9430 |  | ACT | 5.77 |  |  |  | 5.77
GOLD HILL-EIGHT MILE ROAD | 230 | ETL.4800 |  | ACT | 48.8 |  |  |  | 48.8
GOLD HILL-LODI STIG | 230 | ETL.4810 |  | ACT | 46.67 |  |  |  | 46.67
GOLDEN VALLEY TAP | 115 | ETL.2603 |  | ACT | 1.59 |  |  |  | 1.59
GOLDTREE TAP | 115 | ETL.2821 |  | ACT | 2.3 |  | 1.05 |  | 1.25
GONZALES #1 TAP | 60 | ETL.8011 |  | ACT | 0.19 |  |  |  | 0.19
GONZALES #2 TAP | 60 | ETL.8021 |  | ACT | 0.3 |  |  |  | 0.3
GRANITE ROCK TAP | 60 | ETL.8311 |  | ACT | 2.39 |  | 2.35 |  | 0.04
GRANT-EASTSHORE #1 | 115 | ETL.1700 |  | ACT | 4.34 |  |  |  | 4.34
GRANT-EASTSHORE #2 | 115 | ETL.1701 |  | ACT | 4.21 |  |  |  | 4.21
GRAPEVINE TAP | 70 | ETL.9252 |  | ACT | 0.14 |  | 0.14 |  | 0
GREEN VALLEY-CAMP EVERS | 115 | ETL.1710 |  | ACT | 18.56 | 10.39 | 3.03 |  | 5.14
GREEN VALLEY-LLAGAS | 115 | ETL.1720 |  | ACT | 24.74 | 6.14 | 8.41 |  | 10.19
GREEN VALLEY-PAUL SWEET | 115 | ETL.1730 |  | ACT | 15.82 | 7.14 | 4.24 |  | 4.44
GREEN VALLEY-WATSONVILLE | 60 | ETL.6970 |  | ACT | 4.79 |  |  |  | 4.79
GREENLEAF #1 TAP | 115 | ETL.1101 |  | ACT | 4.85 |  |  |  | 4.85
GREENLEAF #2 TAP | 60 | ETL.7761 |  | ACT | 0.62 |  |  |  | 0.62
GREGG-ASHLAN | 230 | ETL.4820 |  | ACT | 7 |  |  |  | 7
GREGG-HERNDON #1 | 230 | ETL.4830 |  | ACT | 0.6 |  |  |  | 0.6
GREGG-HERNDON #2 | 230 | ETL.4840 |  | ACT | 0.63 |  |  |  | 0.63
GRONEMEYER TAP | 60 | ETL.7471 |  | ACT | 0.83 |  |  |  | 0.83
GUARDIAN #1 TAP | 115 | ETL.2301 |  | ACT | 0.75 |  |  |  | 0.75
GUARDIAN #2 TAP | 115 | ETL.2292 |  | ACT | 0.13 |  |  |  | 0.13
GUERNSEY-HENRIETTA | 70 | ETL.8720 |  | ACT | 18.44 |  |  |  | 18.44
GUSTINE #1 TAP | 60 | ETL.7862 |  | ACT | 7.51 |  |  |  | 7.51
GUSTINE #2 TAP | 60 | ETL.7872 |  | ACT | 4.44 |  |  |  | 4.44
GWF HANFORD COGEN TAP | 70 | ETL.8723 |  | IDL | 0.31 |  |  |  | 0.31
GWF-HENRIETTA | 70 | ETL.8774 |  | ACT | 0.12 |  |  |  | 0.12
GWF-KINGSBURG | 115 | ETL.1743 |  | ACT | 21.64 |  |  |  | 21.64
H-P #3 | 115 | ETL.1555 |  | ACT | 0.17 |  |  |  | 0.17
HAAS-MCCALL | 230 | ETL.4850 |  | ACT | 44.21 |  | 24.67 | 0.27 | 19.27
HAAS-WOODCHUCK | 0 | ETL.8730 |  | IDL | 6.79 |  | 3.79 | 0.94 | 2.06 | Idle Section
HALSEY-PLACER | 60 | ETL.6990 |  | ACT | 4.94 |  | 1.58 | 0.25 | 3.11
HAMILTON BRANCH-CHESTER | 60 | ETL.7000 |  | ACT | 12.27 |  | 10.09 |  | 2.18
HAMMER-COUNTRY CLUB | 60 | ETL.7010 |  | ACT | 8.82 |  |  |  | 8.82
HARDWICK TAP | 70 | ETL.8911 |  | ACT | 2.74 |  |  |  | 2.74
HARRINGTON TAP | 60 | ETL.6581 |  | ACT | 0.53 |  |  |  | 0.53
HARTLEY-CLEARLAKE | 60 | ETL.7515 |  | ACT | 6.62 |  | 3.14 |  | 3.48
HAT CREEK #1-PIT #1 | 60 | ETL.7020 |  | ACT | 6.06 |  | 6.06 |  | 0
HAT CREEK #1-WESTWOOD | 60 | ETL.7030 |  | ACT | 55.63 |  | 46.54 | 1.82 | 7.27
HEADGATE TAP | 60 | ETL.6941 |  | ACT | 0.97 |  |  |  | 0.97
HEALDSBURG #1 TAP | 60 | ETL.6892 |  | ACT | 0.25 |  |  |  | 0.25
HEALDSBURG #2 TAP | 60 | ETL.6902 |  | ACT | 0.16 |  |  |  | 0.16
HEINZ TAP (12KV) | 115 | ETL.2193 |  | IDL | 0.78 |  |  |  | 0.78
HELM-CRESCENT SW STA | 70 | ETL.8750 |  | ACT | 4.92 |  |  |  | 4.92
HELM-KERMAN | 70 | ETL.8740 |  | ACT | 13.25 |  |  |  | 13.25
HELM-MCCALL | 230 | ETL.4860 |  | ACT | 30.84 |  |  |  | 30.84
HELM-STROUD | 70 | ETL.8760 |  | ACT | 7.43 |  |  |  | 7.43
HELMS-GREGG #1 | 230 | ETL.4870 | POWERGEN | ACT | 60.67 |  | 25.11 | 5.05 | 30.51
HELMS-GREGG #2 | 230 | ETL.4880 | POWERGEN | ACT | 60.68 |  | 25.12 | 5.25 | 30.31
HENRIETTA-AMERICAN KINGS | 70 | ETL.1243 | PGE | ACT | 0.21 |  |  |  | 0.21
HENRIETTA-KENT SW STA | 70 | ETL.8791 |  | ACT | 1.47 |  |  |  | 1.47
HENRIETTA-LEMOORE | 70 | ETL.8770 |  | ACT | 9.36 |  |  |  | 9.36
HENRIETTA-LEMOORE NAS | 70 | ETL.8780 |  | ACT | 1.75 |  |  |  | 1.75
HENRIETTA-LEPRINO SW STA | 115 | ETL.1737 |  | ACT | 6.03 |  |  |  | 6.03
HERDLYN-BALFOUR | 60 | ETL.7050 |  | ACT | 16.33 |  |  |  | 16.33
HERDLYN-BALFOUR | 60 | ETL.7050 |  | IDL | 4.17 |  |  |  | 4.17
HERDLYN-TRACY | 70 | ETL.8800 |  | ACT | 2.06 |  |  |  | 2.06
HERNDON-ASHLAN | 230 | ETL.4890 |  | ACT | 6.39 |  |  |  | 6.39
HERNDON-BARTON | 115 | ETL.1750 |  | ACT | 12.69 |  |  |  | 12.69
HERNDON-BULLARD #1 | 115 | ETL.1760 |  | ACT | 11.44 |  |  |  | 11.44
HERNDON-BULLARD #2 | 115 | ETL.1770 |  | ACT | 11.43 |  |  |  | 11.43
HERNDON-KEARNEY | 230 | ETL.4900 |  | ACT | 10.83 |  |  |  | 10.83
HERNDON-MANCHESTER | 115 | ETL.1780 |  | ACT | 9.29 |  |  |  | 9.29
HERNDON-WOODWARD | 115 | ETL.1790 |  | ACT | 13.04 |  |  |  | 13.04
HICKS-METCALF | 230 | ETL.4910 |  | ACT | 9.07 |  | 3.38 | 0 | 5.69
HIGGINS-BELL | 115 | ETL.1412 |  | ACT | 18.77 |  | 15.04 | 1 | 2.73
HILLSDALE JCT-HALF MOON BAY | 60 | ETL.7060 |  | ACT | 6.81 | 1.42 | 3.25 |  | 2.14
HONCUT TAP | 115 | ETL.3201 |  | ACT | 1.65 |  |  |  | 1.65
HOWLAND ROAD TAP | 115 | ETL.2191 |  | ACT | 0.9 |  |  |  | 0.9
HUMBOLDT #1 | 60 | ETL.7113 |  | ACT | 11.08 |  |  | 0.03 | 11.05
HUMBOLDT BAY-EUREKA | 60 | ETL.7070 |  | ACT | 5.61 |  |  |  | 5.61
HUMBOLDT BAY-HUMBOLDT #1 | 60 | ETL.7080 |  | ACT | 8.41 |  |  |  | 8.41
HUMBOLDT BAY-HUMBOLDT #1 | 115 | ETL.1800 |  | ACT | 6.31 |  | 2.47 | 0.1 | 3.74
HUMBOLDT BAY-HUMBOLDT #2 | 60 | ETL.7090 |  | ACT | 6.5 |  | 2.46 | 0.11 | 3.93
HUMBOLDT BAY-RIO DELL JCT | 60 | ETL.7100 |  | ACT | 18.41 |  | 1.99 |  | 16.42
HUMBOLDT-BRIDGEVILLE | 115 | ETL.1810 |  | ACT | 30.28 |  | 7.15 | 0.32 | 22.81
HUMBOLDT-EUREKA | 60 | ETL.7120 |  | ACT | 4.74 |  |  |  | 4.74
HUMBOLDT-MAPLE CREEK | 60 | ETL.7130 |  | ACT | 14.09 |  | 8 |  | 6.09
HUMBOLDT-TRINITY | 115 | ETL.1820 |  | ACT | 68.57 |  | 63.09 |  | 5.48
IBM BAILEY AVE TAP | 115 | ETL.2491 |  | ACT | 2 |  |  |  | 2
IBM HARRY RD #1 TAP | 115 | ETL.2501 |  | ACT | 0.58 |  | 0.58 |  | 0
IBM HARRY RD #2 TAP | 115 | ETL.2481 |  | ACT | 0.58 |  | 0.58 |  | 0
IGNACIO-ALTO | 60 | ETL.7150 |  | ACT | 17.79 | 1.01 | 3.06 |  | 13.72
IGNACIO-ALTO-SAUSALITO #1 | 60 | ETL.7160 |  | ACT | 17.95 |  | 4.85 | 0 | 13.1
IGNACIO-ALTO-SAUSALITO #2 | 60 | ETL.7170 |  | ACT | 17.95 |  | 4.82 |  | 13.13
IGNACIO-BOLINAS #1 | 60 | ETL.7140 |  | ACT | 15.02 | 10.25 | 4.65 |  | 0.12
IGNACIO-BOLINAS #2 | 60 | ETL.7180 |  | ACT | 28.21 | 12.46 | 13.66 |  | 2.09
IGNACIO-LAS GALLINAS | 115 | ETL.1860 |  | ACT | 4.16 |  | 0.08 |  | 4.08
IGNACIO-MARE ISLAND #1 | 115 | ETL.1830 |  | ACT | 39.46 |  |  |  | 39.46
IGNACIO-MARE ISLAND #2 | 115 | ETL.1840 |  | ACT | 43.08 |  |  |  | 43.08
IGNACIO-SAN RAFAEL #1 | 115 | ETL.1850 |  | ACT | 11.54 | 0.62 | 2.45 |  | 8.47
IGNACIO-SOBRANTE | 230 | ETL.4920 |  | ACT | 42.49 |  | 11.94 |  | 30.55
IGNACIO-STAFFORD | 60 | ETL.1042 |  | ACT | 6.13 |  | 0.6 |  | 5.53
IMHOFF TAP | 115 | ETL.3322 |  | ACT | 1.43 |  |  |  | 1.43
INDIAN FLAT-YOSEMITE | 70 | ETL.1112 |  | ACT | 4.87 |  | 4.87 |  | 0
INDUSTRIAL TAP | 60 | ETL.7441 |  | ACT | 0.97 |  |  |  | 0.97
INGRAM CREEK TAP | 115 | ETL.4001 |  | ACT | 0.5 |  |  |  | 0.5
IONE TAP | 60 | ETL.8253 |  | ACT | 4.09 |  | 3 |  | 1.09
IUKA TAP | 60 | ETL.8281 |  | ACT | 0.49 |  |  |  | 0.49
JAMESON CANYON PUMPING PLANT TAP | 115 | ETL.1833 |  | ACT | 0.19 |  |  |  | 0.19
JANES CREEK TAP | 60 | ETL.6805 |  | ACT | 1.78 |  |  | 0.04 | 1.74
JARVIS-CRYOGENICS | 115 | ETL.1870 |  | IDL | 0.03 |  |  |  | 0.03
JAYNE SW STA-COALINGA | 70 | ETL.8670 |  | ACT | 12.25 |  |  |  | 12.25
JEFFERSON #1 | 60 | ETL.6831 |  | ACT | 8.97 |  | 2.31 |  | 6.66
JEFFERSON-HILLSDALE JCT | 60 | ETL.7190 |  | ACT | 14.78 |  | 2.3 |  | 12.48
JEFFERSON-LAS PULGAS | 60 | ETL.7200 |  | ACT | 5.99 |  | 0.11 |  | 5.88
JEFFERSON-MARTIN | 230 | ETL.5710 |  | ACT | 3.3 |  | 1.04 |  | 2.26
JEFFERSON-STANFORD | 60 | ETL.7220 |  | ACT | 7.57 |  | 2.53 |  | 5.04
JESSUP TAP | 115 | ETL.4041 |  | ACT | 0.86 |  | 0.33 |  | 0.53
JOLON TAP | 60 | ETL.7321 |  | ACT | 15.87 |  | 15.42 |  | 0.45
KAMM TAP | 115 | ETL.3253 |  | ACT | 0.51 |  |  |  | 0.51
KANAKA TAP | 115 | ETL.4223 |  | ACT | 2.59 | 0.71 | 1.87 |  | 0.01
KANSAS PV-LEPRINO SW STA | 115 | ETL.1739 |  | ACT | 0.17 |  |  |  | 0.17
KASSON #1 | 60 | ETL.7230 |  | ACT | 0.19 |  |  |  | 0.19
KASSON-BANTA #1 | 60 | ETL.7240 |  | ACT | 1.05 |  |  |  | 1.05
KASSON-CARBONA | 60 | ETL.7231 |  | ACT | 7.32 |  |  |  | 7.32
KASSON-LOUISE | 60 | ETL.7250 |  | ACT | 9.12 |  |  |  | 9.12
KEARNEY ALTERNATE TIE | 70 | ETL.9380 |  | ACT | 0.3 |  |  |  | 0.3
KEARNEY TIE | 70 | ETL.9370 |  | ACT | 0.15 |  |  |  | 0.15
KEARNEY-BIOLA | 70 | ETL.8810 |  | ACT | 19.15 |  |  |  | 19.15
KEARNEY-BOWLES | 70 | ETL.8820 |  | ACT | 9.29 |  |  |  | 9.29
KEARNEY-CARUTHERS | 70 | ETL.8830 |  | ACT | 12.05 |  |  |  | 12.05
KEARNEY-KERMAN | 70 | ETL.8840 |  | ACT | 10.98 |  |  |  | 10.98
KELLEY TAP | 70 | ETL.9293 |  | ACT | 2.79 |  |  |  | 2.79
KELSO-TESLA | 230 | ETL.4930 |  | ACT | 7.95 |  |  |  | 7.95
KENT SW STA-ALMOND PV | 70 | ETL.1485 |  | ACT | 0.48 |  |  |  | 0.48
KENT SW STA-TULARE LAKE | 70 | ETL.8790 |  | ACT | 15.93 |  |  |  | 15.93
KERCKHOFF #1-KERCKHOFF #2 | 115 | ETL.1880 |  | ACT | 1.58 |  | 1.58 |  | 0
KERCKHOFF-CLOVIS-SANGER #1 | 115 | ETL.1890 |  | ACT | 36.93 |  | 7.85 |  | 29.08
KERCKHOFF-CLOVIS-SANGER #2 | 115 | ETL.1900 |  | ACT | 32.08 |  | 7.85 |  | 24.23
KERN CANYON-MAGUNDEN-WEEDPATCH | 70 | ETL.8850 |  | ACT | 20.68 |  |  |  | 20.68
KERN OIL-DEXZEL | 115 | ETL.1910 |  | ACT | 0.44 |  |  |  | 0.44
KERN OIL-MT POSO | 70 | ETL.1212 |  | IDL | 1.08 |  |  |  | 1.08
KERN OIL-WITCO | 115 | ETL.1920 |  | ACT | 4.2 |  |  |  | 4.2
KERN-BAKERSFIELD | 230 | ETL.5151 |  | ACT | 7.04 |  |  |  | 7.04
KERN-FRUITVALE | 70 | ETL.8860 |  | ACT | 0.16 |  |  |  | 0.16
KERN-KERN FRONT | 115 | ETL.1930 |  | ACT | 12.47 |  |  |  | 12.47
KERN-KERN OIL-FAMOSO | 70 | ETL.8870 |  | ACT | 19.67 |  |  |  | 19.67
KERN-KERN OIL-FAMOSO | 70 | ETL.8870 |  | IDL | 6.53 |  |  |  | 6.53
KERN-LIVE OAK | 115 | ETL.1960 |  | ACT | 10.83 |  |  |  | 10.83
KERN-MAGUNDEN | 70 | ETL.8880 |  | ACT | 17.34 |  |  |  | 17.34
KERN-MAGUNDEN-WITCO | 115 | ETL.1970 |  | ACT | 19.57 |  |  |  | 19.57
KERN-OLD RIVER #1 | 70 | ETL.8890 |  | ACT | 11.97 |  |  |  | 11.97
KERN-OLD RIVER #2 | 70 | ETL.8900 |  | ACT | 26.33 |  |  |  | 26.33
KERN-ROSEDALE | 115 | ETL.1980 |  | ACT | 1.77 |  |  |  | 1.77
KERN-STOCKDALE #1 | 230 | ETL.5152 |  | ACT | 6.35 |  |  |  | 6.35
KERN-STOCKDALE #2 | 230 | ETL.5161 |  | ACT | 6.32 |  |  |  | 6.32
KERN-STOCKDALE-LAMONT #1 | 115 | ETL.1990 |  | ACT | 19.66 |  |  |  | 19.66
KERN-STOCKDALE-LAMONT #1 (21KV) | 115 | ETL.1990 |  | IDL | 3.71 |  |  |  | 3.71
KERN-STOCKDALE-LAMONT #2 | 115 | ETL.1940 |  | ACT | 18.23 |  |  |  | 18.23
KERN-WESTPARK #1 | 115 | ETL.2000 |  | ACT | 3.83 |  |  |  | 3.83
KERN-WESTPARK #2 | 115 | ETL.2010 |  | ACT | 3.81 |  |  |  | 3.81
KERNWATER TAP | 115 | ETL.1971 |  | ACT | 0.67 |  |  |  | 0.67
KESWICK-CASCADE | 60 | ETL.7260 |  | ACT | 9.35 | 0.56 | 8.46 |  | 0.33
KESWICK-TRINITY | 60 | ETL.7270 |  | ACT | 30.4 | 5.47 | 23.62 |  | 1.31
KETTLEMAN HILLS TAP | 70 | ETL.8701 |  | ACT | 1.02 |  |  |  | 1.02
KIFER-FMC | 115 | ETL.2020 |  | ACT | 6.07 |  |  |  | 6.07
KILARC-CEDAR CREEK | 60 | ETL.7290 |  | ACT | 13.33 | 13.33 |  |  | 0
KILARC-DESCHUTES | 60 | ETL.7300 |  | ACT | 23.41 | 0.67 | 19.94 |  | 2.8
KILARC-VOLTA TIE | 60 | ETL.7310 |  | ACT | 1.93 |  | 0.66 |  | 1.27
KING CITY-COBURN #1 | 60 | ETL.7320 |  | ACT | 21.75 |  |  |  | 21.75
KING CITY-COBURN #2 | 60 | ETL.7330 |  | ACT | 15.76 |  |  |  | 15.76
KINGS RIVER-SANGER-REEDLEY | 115 | ETL.2030 |  | ACT | 43.37 |  | 14.48 | 0.12 | 28.77
KINGSBURG COGEN TAP | 115 | ETL.2291 |  | ACT | 1.22 |  |  |  | 1.22
KINGSBURG-CORCORAN #1 | 115 | ETL.2040 |  | ACT | 27.46 |  |  |  | 27.46
KINGSBURG-LEMOORE | 70 | ETL.8910 |  | ACT | 27.57 |  |  |  | 27.57
KINGSBURG-WAUKENA SW STA | 115 | ETL.2050 |  | ACT | 25.24 |  |  |  | 25.24
KM GREEN TAP | 115 | ETL.3505 |  | ACT | 1.6 |  | 1.6 |  | 0
KONOCTI-EAGLE ROCK | 60 | ETL.6861 |  | ACT | 9.66 | 7.53 | 0.23 |  | 1.9
KONOCTI-MIDDLETOWN | 60 | ETL.6380 |  | ACT | 19.87 | 0.87 | 15.42 | 0.06 | 3.52
KYOHO TAP | 115 | ETL.3891 |  | ACT | 2.2 |  |  |  | 2.2
LAGUNA TAP | 60 | ETL.6912 |  | ACT | 1.68 |  |  |  | 1.68
LAGUNITAS TAP | 60 | ETL.8312 |  | ACT | 0.56 |  |  |  | 0.56
LAKEVILLE #1 | 60 | ETL.7360 |  | ACT | 11.15 | 1.16 | 7.42 |  | 2.57
LAKEVILLE #2 | 60 | ETL.7340 |  | ACT | 21.62 |  | 6.2 |  | 15.42
LAKEVILLE-IGNACIO #1 | 230 | ETL.4940 |  | ACT | 15.49 |  | 0.89 |  | 14.6
LAKEVILLE-IGNACIO #2 | 230 | ETL.3745 |  | ACT | 14.54 |  | 0.71 |  | 13.83
LAKEVILLE-PETALUMA C | 60 | ETL.7350 |  | ACT | 5.36 |  |  |  | 5.36
LAKEVILLE-SOBRANTE #2 | 230 | ETL.4960 |  | ACT | 47.89 |  | 11.02 |  | 36.87
LAKEVILLE-SONOMA #1 | 115 | ETL.2063 |  | ACT | 6.68 |  | 2.54 |  | 4.14
LAKEVILLE-SONOMA #2 | 115 | ETL.2070 |  | ACT | 7.18 |  | 2.54 |  | 4.64
LAKEVILLE-TULUCAY | 230 | ETL.4970 |  | ACT | 17.22 |  | 1.8 |  | 15.42
LAKEWOOD-CLAYTON | 115 | ETL.2082 |  | ACT | 5.52 |  | 1.13 |  | 4.39
LAKEWOOD-MEADOW LANE-CLAYTON | 115 | ETL.2080 |  | ACT | 9.55 |  | 1.13 |  | 8.42
LAKEWOOD-MEADOW LANE-CLAYTON | 115 | ETL.2080 |  | IDL | 0.06 |  |  |  | 0.06
LAMBIE SW STA-BIRDS LANDING SW STA | 230 | ETL.5820 |  | ACT | 7.04 |  |  |  | 7.04
LAMMERS-KASSON | 115 | ETL.3972 |  | ACT | 8.23 |  |  |  | 8.23
LAMONT-GRIMMWAY MALAGA | 115 | ETL.1942 |  | ACT | 3.55 |  |  |  | 3.55
LAS AGUILAS SW STA-PANOCHE #1 | 230 | ETL.1003 |  | ACT | 17.44 |  |  |  | 17.44
LAS AGUILAS SW STA-PANOCHE #2 | 230 | ETL.1002 |  | ACT | 17.44 |  |  |  | 17.44
LAS GALLINAS-SAN RAFAEL | 115 | ETL.1103 |  | ACT | 4.46 |  |  |  | 4.46
LAS PALMAS TAP | 115 | ETL.2181 |  | ACT | 0.85 |  |  |  | 0.85
LAS PERILLAS TAP | 70 | ETL.8463 |  | ACT | 0.39 |  |  |  | 0.39
LAS PLUMAS TAP | 115 | ETL.2653 |  | ACT | 0.48 |  |  |  | 0.48
LAS POSITAS-NEWARK | 230 | ETL.4980 |  | ACT | 20.93 |  | 4.34 | 0.51 | 16.08
LAS POSITAS-VASCO | 60 | ETL.7370 |  | ACT | 1.5 |  |  |  | 1.5
LAURELES-OTTER | 60 | ETL.7380 |  | ACT | 15.56 | 12.23 | 3.12 |  | 0.21
LAWRENCE-MONTA VISTA | 115 | ETL.2090 |  | ACT | 8.86 |  |  |  | 8.86
LAYTONVILLE-COVELO | 60 | ETL.7390 |  | ACT | 16.09 |  | 6.59 | 0.34 | 9.16
LAYTONVILLE-WILLITS | 60 | ETL.8360 |  | ACT | 22.95 |  | 15.23 |  | 7.72
LE GRAND-CHOWCHILLA | 115 | ETL.2110 |  | ACT | 10.94 |  |  |  | 10.94
LE GRAND-DAIRYLAND | 115 | ETL.2100 |  | ACT | 11.4 |  |  |  | 11.4
LEE TAP | 60 | ETL.7461 |  | IDL | 2.47 |  |  |  | 2.47
LEPRINO FOODS (TRACY) TAP | 115 | ETL.1283 |  | ACT | 0.02 |  |  |  | 0.02
LEPRINO FOODS-LEPRINO SW STA | 115 | ETL.1741 |  | ACT | 6.41 |  |  |  | 6.41
LEPRINO SW STA-GWF HANFORD SW STA | 115 | ETL.1740 |  | ACT | 12.4 |  |  |  | 12.4
LEPRINO SW STA-HENRIETTA PV | 115 | ETL.1738 |  | ACT | 0.06 |  |  |  | 0.06
LEPRINO TAP | 70 | ETL.8771 |  | ACT | 0.47 |  |  |  | 0.47
LERDO-FAMOSO | 115 | ETL.2120 |  | ACT | 13.46 |  |  |  | 13.46
LERDO-KERN OIL-7TH STANDARD | 115 | ETL.1950 |  | ACT | 16.36 |  |  |  | 16.36
LINCOLN-PLEASANT GROVE | 115 | ETL.7400 |  | ACT | 7.39 |  |  |  | 7.39
LINDE TAP | 115 | ETL.3302 |  | ACT | 0.62 |  |  |  | 0.62
LIVE OAK TAP | 115 | ETL.2130 |  | ACT | 3.97 |  |  |  | 3.97
LIVE OAK-KERN OIL | 115 | ETL.2140 |  | ACT | 4.4 |  |  |  | 4.4
LIVERMORE-LAS POSITAS | 60 | ETL.7410 |  | ACT | 3.63 |  |  |  | 3.63
LIVINGSTON-LIVINGSTON JCT | 70 | ETL.8920 |  | ACT | 23.36 |  |  |  | 23.36
LLAGAS-GILROY FOODS | 115 | ETL.2150 |  | ACT | 1.98 |  |  |  | 1.98
LLAGAS-HOLLISTER | 115 | ETL.2911 |  | ACT | 19.85 |  |  |  | 19.85
LLAGAS-HOLLISTER | 115 | ETL.2911 |  | IDL | 1.71 |  |  |  | 1.71
LOCKEFORD #1 | 60 | ETL.9461 |  | ACT | 12.91 |  |  |  | 12.91
LOCKEFORD-BELLOTA | 230 | ETL.4990 |  | ACT | 12.32 |  |  |  | 12.32
LOCKEFORD-INDUSTRIAL | 60 | ETL.7420 |  | ACT | 6.03 |  |  |  | 6.03
LOCKEFORD-LODI #2 | 60 | ETL.7440 |  | ACT | 9.49 |  |  |  | 9.49
LOCKEFORD-LODI #3 | 60 | ETL.7450 |  | ACT | 15.36 |  |  |  | 15.36
LOCKHEED #1 TAP | 115 | ETL.3051 |  | ACT | 1.71 |  |  |  | 1.71
LOCKHEED #2 TAP | 115 | ETL.2981 |  | ACT | 1.3 |  |  |  | 1.3
LODI STIG-EIGHT MILE ROAD | 230 | ETL.5001 |  | ACT | 2.18 |  |  |  | 2.18
LODI-INDUSTRIAL | 60 | ETL.6755 |  | ACT | 0.98 |  |  |  | 0.98
LOGAN CREEK-DELEVAN | 230 | ETL.6331 |  | ACT | 12.35 |  |  |  | 12.35
LONE STAR TAP | 60 | ETL.6231 |  | ACT | 1.18 |  | 0.76 |  | 0.42
LONE TREE-CAYETANO | 230 | ETL.6160 |  | ACT | 15.4 | 0.86 | 10.68 |  | 3.86
LOS BANOS-DOS AMIGOS | 230 | ETL.5020 |  | ACT | 14.31 |  |  |  | 14.31
LOS BANOS-GATES #1 | 500 | ETL.6000 |  | ACT | 80.85 |  |  |  | 80.85
LOS BANOS-LIVINGSTON JCT-CANAL | 70 | ETL.8940 |  | ACT | 14.34 |  |  |  | 14.34
LOS BANOS-MERCY SPRINGS SW STA | 70 | ETL.8929 |  | ACT | 14.7 |  |  |  | 14.7
LOS BANOS-MIDWAY #2 | 500 | ETL.6010 |  | ACT | 144.6 |  |  |  | 144.6
LOS BANOS-O'NEILL PGP | 70 | ETL.8950 |  | ACT | 3.87 |  |  |  | 3.87
LOS BANOS-PACHECO | 70 | ETL.8960 |  | ACT | 16.31 |  |  |  | 16.31
LOS BANOS-PACHECO | 70 | ETL.8960 |  | IDL | 4.46 |  |  |  | 4.46
LOS BANOS-PADRE FLAT SW STA | 230 | ETL.1092 |  | ACT | 3.67 |  |  |  | 3.67
LOS BANOS-PANOCHE #2 | 230 | ETL.5040 |  | ACT | 37.13 |  |  |  | 37.13
LOS BANOS-QUINTO SW STA | 230 | ETL.5071 |  | ACT | 12.06 |  |  |  | 12.06
LOS BANOS-SAN LUIS PUMPS #1 | 230 | ETL.5050 |  | ACT | 3.43 |  |  |  | 3.43
LOS BANOS-SAN LUIS PUMPS #2 | 230 | ETL.5060 |  | ACT | 3.43 |  |  |  | 3.43
LOS COCHES TAP | 60 | ETL.7331 |  | ACT | 1.32 |  |  |  | 1.32
LOS ESTEROS-AGNEW | 115 | ETL.2690 |  | ACT | 1.37 |  |  |  | 1.37
LOS ESTEROS-METCALF | 230 | ETL.5353 |  | ACT | 63.25 |  | 51.47 | 0.48 | 11.3
LOS ESTEROS-MONTAGUE | 115 | ETL.2380 |  | ACT | 4.64 |  |  |  | 4.64
LOS ESTEROS-NORTECH | 115 | ETL.4032 |  | ACT | 2 |  |  |  | 2
LOS ESTEROS-TRIMBLE | 115 | ETL.2550 |  | ACT | 3.73 |  |  |  | 3.73
LOST HILLS TAP | 70 | ETL.8451 |  | ACT | 2.89 |  |  |  | 2.89
LOUISIANA PACIFIC (OROVILLE) TAP | 60 | ETL.7732 |  | ACT | 0.16 |  |  |  | 0.16
LOWER LAKE-HOMESTAKE | 115 | ETL.1481 |  | ACT | 16.08 |  | 15.36 |  | 0.72
LP FLAKEBOARD TAP | 60 | ETL.7111 |  | ACT | 0.51 |  |  |  | 0.51
LUCERNE #1 TAP | 115 | ETL.1331 |  | ACT | 0.23 |  | 0.23 |  | 0
LUCERNE #2 TAP | 115 | ETL.2411 |  | ACT | 0.23 |  | 0.23 |  | 0
LYOTH TAP | 60 | ETL.7232 |  | ACT | 1.34 |  |  |  | 1.34
MABURY TAP | 115 | ETL.2651 |  | ACT | 2.81 |  |  |  | 2.81
MADISON-VACA | 115 | ETL.2170 |  | ACT | 22.99 |  | 2.84 | 0.13 | 20.02
MALACHA TAP | 230 | ETL.5910 |  | ACT | 0.12 |  | 0.12 |  | 0
MALAGA-KRCD | 115 | ETL.2294 |  | ACT | 0.99 |  |  |  | 0.99
MALIN-ROUND MTN #2 | 500 | ETL.6020 |  | ACT | 46.9 |  | 46.9 |  | 0
MANCHESTER-AIRWAYS-SANGER | 115 | ETL.2180 |  | ACT | 15.02 |  |  |  | 15.02
MANTECA #1 | 60 | ETL.7460 |  | ACT | 34.52 |  |  |  | 34.52
MANTECA-LOUISE | 60 | ETL.7470 |  | ACT | 12.53 |  |  |  | 12.53
MANTECA-VIERRA | 115 | ETL.2190 |  | ACT | 3.97 |  |  |  | 3.97
MANVILLE TAP | 115 | ETL.1372 |  | ACT | 5.53 |  | 2.73 |  | 2.8
MAPLE CREEK-HOOPA | 60 | ETL.7490 |  | ACT | 29.13 | 13.53 | 11.39 |  | 4.21
MARICOPA-COPUS | 70 | ETL.8851 |  | ACT | 7.86 |  |  |  | 7.86
MARSH TAP | 60 | ETL.7054 |  | ACT | 3.97 |  |  |  | 3.97
MARTIN-DALY CITY #1 | 115 | ETL.2200 |  | ACT | 3.93 |  |  |  | 3.93
MARTIN-DALY CITY #2 | 115 | ETL.2210 |  | ACT | 3.93 |  |  |  | 3.93
MARTIN-EAST GRAND | 115 | ETL.2220 |  | ACT | 3.96 |  |  |  | 3.96
MARTIN-MILLBRAE #1 | 115 | ETL.2230 |  | ACT | 7.28 |  |  |  | 7.28
MARTIN-SF AIRPORT | 115 | ETL.2240 |  | ACT | 5.43 |  |  |  | 5.43
MARTIN-SNEATH LANE | 60 | ETL.7210 |  | ACT | 7.23 |  | 0.79 |  | 6.44
MARTINEZ-SOBRANTE | 115 | ETL.2270 |  | ACT | 16.4 |  | 13.61 |  | 2.79
MCCALL-KINGSBURG #1 | 115 | ETL.2290 |  | ACT | 11.65 |  |  |  | 11.65
MCCALL-KINGSBURG #2 | 115 | ETL.2300 |  | ACT | 11.57 |  |  |  | 11.57
MCCALL-MALAGA | 115 | ETL.2310 |  | ACT | 10.96 |  |  |  | 10.96
MCCALL-REEDLEY | 115 | ETL.2320 |  | ACT | 15.19 |  |  |  | 15.19
MCCALL-SANGER #1 | 115 | ETL.2330 |  | ACT | 9.22 |  |  |  | 9.22
MCCALL-SANGER #2 | 115 | ETL.2340 |  | ACT | 9.21 |  |  |  | 9.21
MCCALL-SANGER #3 | 115 | ETL.2350 |  | ACT | 8.58 |  |  |  | 8.58
MCCALL-WEST FRESNO #2 | 115 | ETL.2370 |  | ACT | 19.61 |  |  |  | 19.61
MCDONALD TAP | 60 | ETL.7053 |  | ACT | 5.88 |  |  |  | 5.88
MCFARLAND TAP | 70 | ETL.9171 |  | ACT | 6 |  |  |  | 6
MCKEE-PIERCY | 115 | ETL.2379 |  | ACT | 7.75 |  |  |  | 7.75
MCSWAIN TAP | 70 | ETL.8991 |  | ACT | 1.38 |  | 0.57 |  | 0.81
MELONES-CURTIS | 115 | ETL.2390 |  | ACT | 14.8 |  | 14.07 |  | 0.73
MELONES-RACETRACK | 115 | ETL.2400 |  | ACT | 10.2 |  | 10.2 |  | 0
MELONES-WILSON | 230 | ETL.5080 |  | ACT | 61.61 |  | 5.23 |  | 56.38
MENDOCINO #1 | 60 | ETL.7530 |  | IDL | 3.99 |  | 3.3 |  | 0.69 | Idle Section
MENDOCINO-HARTLEY | 60 | ETL.7510 |  | ACT | 23.18 |  | 21.78 |  | 1.4
MENDOCINO-PHILO JCT-HOPLAND | 60 | ETL.7520 |  | ACT | 21.87 |  | 16.15 |  | 5.72
MENDOCINO-REDBUD | 115 | ETL.2410 |  | ACT | 34.83 |  | 32.61 |  | 2.22
MENDOCINO-UKIAH | 115 | ETL.2420 |  | ACT | 9.83 |  | 7.49 |  | 2.34
MENDOCINO-WILLITS | 60 | ETL.7540 |  | ACT | 14.52 | 3.77 | 8.33 |  | 2.42
MENDOCINO-WILLITS-FORT BRAGG | 60 | ETL.7550 |  | ACT | 43.81 | 3.78 | 36.76 |  | 3.27
MENDOTA BIOMASS TAP | 70 | ETL.8981 |  | ACT | 3.84 |  |  |  | 3.84
MENDOTA-LITTLE BEAR | 115 | ETL.1494 |  | ACT | 0.04 |  |  |  | 0.04
MENDOTA-NORTH STAR SOLAR | 115 | ETL.2113 |  | ACT | 0.03 |  |  |  | 0.03
MENDOTA-SAN JOAQUIN-HELM | 70 | ETL.8980 |  | ACT | 26.94 |  |  |  | 26.94
MENLO TAP | 60 | ETL.6571 |  | ACT | 0.37 |  |  |  | 0.37
MERCED #1 | 70 | ETL.9000 |  | ACT | 39.89 |  |  |  | 39.89
MERCED FALLS-EXCHEQUER | 70 | ETL.8990 | PGE | ACT | 6.51 |  | 4.34 |  | 2.17
MERCED-MERCED FALLS | 70 | ETL.9010 |  | ACT | 20.92 |  |  |  | 20.92
MERCY SPRINGS SW STA-CANAL-ORO LOMA | 70 | ETL.8930 |  | ACT | 23.31 |  |  |  | 23.31
MESA-CABALLERO STORAGE | 230 | ETL.1433 |  | ACT | 0.2 |  |  |  | 0.2
MESA-DIVIDE #1 | 115 | ETL.2430 |  | ACT | 14.71 |  |  |  | 14.71
MESA-DIVIDE #2 | 115 | ETL.2440 |  | ACT | 14.72 |  |  |  | 14.72
MESA-SANTA MARIA | 115 | ETL.2450 |  | ACT | 4.36 |  | 0.07 |  | 4.29
MESA-SISQUOC | 115 | ETL.2460 |  | ACT | 17.6 |  | 1.05 |  | 16.55
METCALF SUB INTER-TIE 230KV | 230 | 0.1 |  | ACT | 0.21 |  |  |  | 0.21
METCALF SUB INTER-TIE 230KV | 230 | 0.2 |  | ACT | 0.11 |  |  |  | 0.11
METCALF SUB INTER-TIE 230KV | 230 | 0.3 |  | ACT | 0.15 |  |  |  | 0.15
METCALF-COYOTE PUMPING PLANT | 115 | ETL.2470 |  | ACT | 7.86 |  |  |  | 7.86
METCALF-EDENVALE #2 | 115 | ETL.2490 |  | ACT | 5.6 |  | 1.3 |  | 4.3
METCALF-EL PATIO #1 | 115 | ETL.2500 |  | ACT | 14.38 |  | 3.38 |  | 11
METCALF-EL PATIO #2 | 115 | ETL.2510 |  | ACT | 14.41 |  | 3.38 |  | 11.03
METCALF-EVERGREEN #1 | 115 | ETL.2520 |  | ACT | 10.63 |  |  |  | 10.63
METCALF-EVERGREEN #2 | 115 | ETL.2530 |  | ACT | 10.57 |  |  |  | 10.57
METCALF-GREEN VALLEY | 115 | ETL.2540 |  | ACT | 25.27 | 5.75 | 4.59 |  | 14.93
METCALF-HICKS 1 & 2 | 115 | ETL.4317 |  | IDL | 6.47 |  | 2.83 |  | 3.64 | Idle Section
METCALF-MONTA VISTA #3 | 230 | ETL.5091 |  | ACT | 28.59 | 13.12 | 9.59 | 0.01 | 5.87
METCALF-MORGAN HILL | 115 | ETL.2570 |  | ACT | 9.72 |  | 1.2 |  | 8.52
METCALF-MOSS LANDING #1 | 230 | ETL.5100 |  | ACT | 35.76 | 7.17 | 9.86 |  | 18.73
METCALF-MOSS LANDING #2 | 230 | ETL.5110 |  | ACT | 35.76 | 7.17 | 9.87 |  | 18.72
METCALF-SALINAS #2 (12KV) | 115 | ETL.1731 |  | IDL | 5.55 |  |  |  | 5.55
METCALF-SANTA TERESA | 115 | ETL.2480 |  | ACT | 5.4 |  | 1.29 |  | 4.11
MI-WUK-CURTIS | 115 | ETL.1073 |  | ACT | 8.4 | 4.62 | 3.69 |  | 0.09
MIDDLE FORK #1 | 60 | ETL.8405 |  | ACT | 9.45 | 9.45 |  |  | 0
MIDDLE FORK-GOLD HILL | 230 | ETL.5140 |  | ACT | 44.08 | 25.41 | 12.02 |  | 6.65
MIDDLE RIVER TAP | 60 | ETL.7052 |  | ACT | 7.02 |  |  |  | 7.02
MIDSET TAP | 115 | ETL.1581 |  | ACT | 0.72 |  |  |  | 0.72
MIDSUN-MIDWAY | 115 | ETL.2580 |  | ACT | 19.05 |  |  |  | 19.05
MIDWAY-BITTERWATER SW STA #2 | 230 | ETL.1442 |  | ACT | 25.34 |  |  |  | 25.34
MIDWAY-KERN #1 | 230 | ETL.5150 |  | ACT | 41.07 |  |  |  | 41.07
MIDWAY-KERN #3 | 230 | ETL.5160 |  | ACT | 20.74 |  |  |  | 20.74
MIDWAY-KERN #4 | 230 | ETL.5170 |  | ACT | 20.78 |  |  |  | 20.78
MIDWAY-RENFRO-TUPMAN | 115 | ETL.2590 |  | ACT | 22.6 |  |  |  | 22.6
MIDWAY-SANTA MARIA (12KV) | 115 | ETL.9240 |  | IDL | 31.58 | 16.68 | 1.9 |  | 13 | Distribution Transferred
MIDWAY-SANTA MARIA (21KV) | 115 | ETL.9240 |  | IDL | 14.65 |  |  |  | 14.65
MIDWAY-SHAFTER | 115 | ETL.2610 |  | ACT | 13.63 |  |  |  | 13.63
MIDWAY-SUNSET | 230 | ETL.5194 |  | ACT | 0.57 |  |  |  | 0.57
MIDWAY-TAFT | 115 | ETL.2620 |  | ACT | 19.33 |  |  |  | 19.33
MIDWAY-TEMBLOR | 115 | ETL.2630 |  | ACT | 14.7 |  |  |  | 14.7
MIDWAY-TUPMAN-RIO BRAVO-RENFRO | 115 | ETL.2600 |  | ACT | 26.6 |  |  |  | 26.6
MIDWAY-WHEELER RIDGE #1 | 230 | ETL.5190 |  | ACT | 52.68 |  |  |  | 52.68
MIDWAY-WHIRLWIND | 500 | ETL.6030 |  | ACT | 52.77 |  | 8.6 |  | 44.17
MILLBRAE-SAN MATEO #1 | 115 | ETL.2640 |  | ACT | 4.71 |  |  |  | 4.71
MILLBRAE-SNEATH LANE | 60 | ETL.7570 |  | ACT | 6.72 |  | 2.15 |  | 4.57
MILLER #1 TAP | 115 | ETL.3992 |  | ACT | 21.28 |  |  |  | 21.28
MILLER #2 TAP | 115 | ETL.4002 |  | ACT | 12.32 |  |  |  | 12.32
MILPITAS-SWIFT | 115 | ETL.2650 |  | ACT | 8.86 |  |  |  | 8.86
MISSION POWER TAP | 115 | ETL.1651 |  | ACT | 1.93 | 1.93 |  |  | 0
MISSOURI FLAT-GOLD HILL #1 | 115 | ETL.2660 |  | ACT | 19.7 | 5.95 | 4.73 |  | 9.02
MISSOURI FLAT-GOLD HILL #2 | 115 | ETL.2670 |  | ACT | 19.69 | 5.91 | 4.76 |  | 9.02
MOCO TAP | 70 | ETL.9233 |  | ACT | 1.64 |  |  |  | 1.64
MOFFETT FIELD TAP | 115 | ETL.3052 |  | ACT | 0.16 |  |  |  | 0.16
MONTA VISTA-BURNS | 60 | ETL.7590 |  | ACT | 18.07 | 12.46 | 4.53 |  | 1.08
MONTA VISTA-COYOTE SW STA | 230 | ETL.5090 |  | ACT | 27.83 | 13.13 | 9.6 | 0.01 | 5.09
MONTA VISTA-HICKS | 230 | ETL.5210 |  | ACT | 13.21 |  | 0.38 |  | 12.83
MONTA VISTA-JEFFERSON #1 | 230 | ETL.5220 |  | ACT | 19.72 | 6.35 | 10.5 | 0.84 | 2.03
MONTA VISTA-JEFFERSON #2 | 230 | ETL.5230 |  | ACT | 19.73 | 6.36 | 10.5 | 0.82 | 2.05
MONTA VISTA-LOS ALTOS | 60 | ETL.7600 |  | ACT | 7.11 |  |  |  | 7.11
MONTA VISTA-LOS GATOS | 60 | ETL.7610 |  | ACT | 10.88 |  | 1.97 |  | 8.91
MONTA VISTA-PERMANENTE | 60 | ETL.7620 |  | ACT | 1.19 |  | 0.11 |  | 1.08
MONTA VISTA-SARATOGA | 230 | ETL.5240 |  | ACT | 5.49 |  | 0.37 |  | 5.12
MONTA VISTA-WOLFE | 115 | ETL.3870 |  | ACT | 2.72 |  |  |  | 2.72
MONTAGUE-TRIMBLE | 115 | ETL.2560 |  | ACT | 2.07 |  |  |  | 2.07
MONTE RIO-FORT ROSS | 60 | ETL.6979 |  | ACT | 14.3 | 7.21 | 4.73 |  | 2.36
MONTE RIO-FULTON | 60 | ETL.7630 |  | ACT | 22.56 | 7.11 | 0.13 |  | 15.32
MONTEZUMA SW STA-BIRDS LANDING SW STA | 230 | ETL.7973 |  | ACT | 0.54 |  |  |  | 0.54
MONTICELLO PH TAP | 115 | ETL.1602 |  | ACT | 0.62 |  | 0.61 |  | 0.01
MORAGA-CASTRO VALLEY | 230 | ETL.5250 |  | ACT | 14.92 | 7.96 | 3.16 |  | 3.8
MORAGA-CLAREMONT #1 | 115 | ETL.2700 |  | ACT | 5.28 | 5.09 | 0.2 |  | -0.01
MORAGA-CLAREMONT #2 | 115 | ETL.2710 |  | ACT | 5.3 | 5.11 | 0.2 |  | -0.01
MORAGA-LAKEWOOD | 115 | ETL.3741 |  | ACT | 15.02 | 1.2 | 5.44 | 0.08 | 8.3
MORAGA-OAKLAND #1 | 115 | ETL.2720 |  | ACT | 5.04 | 3.28 | 0.79 |  | 0.97
MORAGA-OAKLAND #2 | 115 | ETL.2730 |  | ACT | 5.04 | 3.28 | 0.79 |  | 0.97
MORAGA-OAKLAND #3 | 115 | ETL.2740 |  | ACT | 5.05 | 3.28 | 0.8 |  | 0.97
MORAGA-OAKLAND #4 | 115 | ETL.2750 |  | ACT | 5.05 | 3.28 | 0.8 |  | 0.97
MORAGA-OAKLAND J | 115 | ETL.2760 |  | ACT | 17.67 | 7.71 | 1.85 |  | 8.11
MORAGA-SAN LEANDRO #1 | 115 | ETL.2770 |  | ACT | 11.14 | 7.73 | 1.85 |  | 1.56
MORAGA-SAN LEANDRO #2 | 115 | ETL.2780 |  | ACT | 11.01 | 7.73 | 1.85 |  | 1.43
MORAGA-SAN LEANDRO #3 | 115 | ETL.2790 |  | ACT | 11 | 7.71 | 1.85 |  | 1.44
MORGAN HILL-LLAGAS | 115 | ETL.2800 |  | ACT | 10.84 |  | 4.04 |  | 6.8
MORRO BAY-CALIFORNIA FLATS SW STA | 230 | ETL.5280 |  | ACT | 46.19 | 5.45 | 9.75 |  | 30.99
MORRO BAY-CALIFORNIA FLATS SW STA | 230 | ETL.5280 |  | IDL | 0.03 |  |  |  | 0.03
MORRO BAY-DIABLO | 230 | ETL.5260 |  | ACT | 15.78 | 5.18 | 7.25 |  | 3.35
MORRO BAY-MESA | 230 | ETL.5290 |  | ACT | 35.25 | 2.47 | 26.6 |  | 6.18
MORRO BAY-SAN LUIS OBISPO #1 | 115 | ETL.2810 |  | ACT | 16.01 |  | 11.32 |  | 4.69
MORRO BAY-SAN LUIS OBISPO #2 | 115 | ETL.2820 |  | ACT | 16.02 |  | 11.33 |  | 4.69
MORRO BAY-SOLAR SW STA #1 | 230 | ETL.5300 |  | ACT | 45.55 | 11.87 | 24.37 |  | 9.31
MORRO BAY-SOLAR SW STA #2 | 230 | ETL.5310 |  | ACT | 45.56 | 11.76 | 24.47 |  | 9.33
MORRO BAY-TEMPLETON | 230 | ETL.5933 |  | ACT | 16.43 | 5.45 | 4.31 |  | 6.67
MOSS LANDING - DALLAS | 500 | ETL.1272 |  | ACT | 0.07 |  |  |  | 0.07
MOSS LANDING-COBURN | 230 | ETL.5330 |  | ACT | 64.03 |  | 35.17 | 0.06 | 28.8
MOSS LANDING-CRAZY HORSE CANYON #1 | 115 | ETL.2930 |  | ACT | 10.52 |  |  |  | 10.52
MOSS LANDING-CRAZY HORSE CANYON #2 | 115 | ETL.2983 |  | ACT | 10.59 |  |  |  | 10.59
MOSS LANDING-DEL MONTE #1 | 115 | ETL.2830 |  | ACT | 23.25 |  | 5.73 |  | 17.52
MOSS LANDING-DEL MONTE #2 | 115 | ETL.2840 |  | ACT | 23.29 |  | 5.73 |  | 17.56
MOSS LANDING-GREEN VALLEY #1 | 115 | ETL.2850 |  | ACT | 14.22 |  |  |  | 14.22
MOSS LANDING-GREEN VALLEY #2 | 115 | ETL.2860 |  | ACT | 14.22 |  |  |  | 14.22
MOSS LANDING-LAS AGUILAS SW STA | 230 | ETL.5340 |  | ACT | 51.9 |  | 28.03 | 0.03 | 23.84
MOSS LANDING-LOS BANOS | 500 | ETL.6040 |  | ACT | 51.33 |  | 11.64 | 0.2 | 39.49
MOSS LANDING-METCALF | 500 | ETL.6050 |  | ACT | 34.98 | 7.17 | 14.28 |  | 13.53
MOSS LANDING-MOSS LANDING PP #1 | 230 | ETL.1282 | NON PGE | ACT | 0.05 |  |  |  | 0.05 | Non-PG&E
MOSS LANDING-MOSS LANDING PP #2 | 230 | ETL.1296 | NON PGE | ACT | 0.05 |  |  |  | 0.05 | Non-PG&E
MOSS LANDING-SALINAS #1 | 115 | ETL.2880 |  | ACT | 11.99 |  |  |  | 11.99
MOSS LANDING-SALINAS #2 | 115 | ETL.2890 |  | ACT | 12.03 |  |  |  | 12.03
MTN GATE JCT-CASCADE | 60 | ETL.7640 |  | ACT | 6.58 |  | 6.58 |  | 0
MTN GATE TAP | 60 | ETL.7641 |  | ACT | 0.7 |  | 0.7 |  | 0
MTN QUARRIES TAP | 60 | ETL.6991 |  | ACT | 2.63 |  | 1.98 |  | 0.65
MTN VIEW-MONTA VISTA | 115 | ETL.2920 |  | ACT | 4.8 |  |  |  | 4.8
MULE CREEK TAP | 60 | ETL.8254 |  | ACT | 0.01 |  |  |  | 0.01
MUSTANG SW STA-CABALLO-SLATE | 230 | ETL.1172 |  | ACT | 0.07 |  |  |  | 0.07
MUSTANG SW STA-GREGG | 230 | ETL.4700 |  | ACT | 45.47 |  |  |  | 45.47
MUSTANG SW STA-MCCALL | 230 | ETL.4710 |  | ACT | 42.11 |  |  |  | 42.11
MUSTANG TAP | 70 | ETL.9091 |  | ACT | 0.71 |  | 0.71 |  | 0
NARROWS #1 TAP | 60 | ETL.6511 |  | ACT | 2.65 |  | 2.65 |  | 0
NARROWS #2 TAP | 60 | ETL.6521 |  | ACT | 3.09 |  | 3.09 |  | 0
NAVY LAB TAP | 60 | ETL.6711 |  | ACT | 0.19 |  |  |  | 0.19
NEW HOGAN TAP | 60 | ETL.8211 |  | ACT | 0.06 |  |  |  | 0.06
NEWARK E-F BUS TIE | 230 | ETL.4640 |  | ACT | 0.22 |  |  |  | 0.22
NEWARK-AMES #1 | 115 | ETL.2940 |  | ACT | 8.3 |  |  |  | 8.3
NEWARK-AMES #2 | 115 | ETL.2950 |  | ACT | 8.28 |  |  |  | 8.28
NEWARK-AMES #3 | 115 | ETL.2960 |  | ACT | 8.28 |  |  |  | 8.28
NEWARK-AMES DISTRIBUTION | 115 | ETL.4313 |  | ACT | 8.25 |  |  |  | 8.25
NEWARK-APPLIED MATERIALS | 115 | ETL.2980 |  | ACT | 11.37 |  |  |  | 11.37
NEWARK-DIXON LANDING | 115 | ETL.2990 |  | ACT | 4.69 |  |  |  | 4.69
NEWARK-FREMONT #1 | 115 | ETL.3000 |  | ACT | 3.67 |  |  |  | 3.67
NEWARK-FREMONT #2 | 115 | ETL.3010 |  | ACT | 3.74 |  |  |  | 3.74
NEWARK-JARVIS #1 | 115 | ETL.3020 |  | ACT | 14.25 |  |  | 0.69 | 13.56
NEWARK-JARVIS #2 | 115 | ETL.3030 |  | ACT | 14.48 |  |  | 0.69 | 13.79
NEWARK-KIFER | 115 | ETL.3040 |  | ACT | 10.61 |  |  |  | 10.61
NEWARK-LAWRENCE | 115 | ETL.3050 |  | ACT | 10.25 |  |  |  | 10.25
NEWARK-LIVERMORE | 60 | ETL.7660 |  | ACT | 19.05 |  | 3.93 | 0.48 | 14.64
NEWARK-LOS ESTEROS | 230 | ETL.2970 |  | ACT | 5.65 |  |  |  | 5.65
NEWARK-MILPITAS #1 | 115 | ETL.3070 |  | ACT | 8.48 |  |  |  | 8.48
NEWARK-MILPITAS #2 | 115 | ETL.3080 |  | ACT | 10.3 |  |  |  | 10.3
NEWARK-NORTHERN RECEIVING STATION #1 | 115 | ETL.3100 |  | ACT | 8.76 |  |  |  | 8.76
NEWARK-NORTHERN RECEIVING STATION #2 | 115 | ETL.3110 |  | ACT | 8.67 |  |  |  | 8.67
NEWARK-NUMMI | 115 | ETL.3090 |  | ACT | 4.94 |  |  |  | 4.94
NEWARK-RAVENSWOOD | 230 | ETL.5936 |  | ACT | 8.91 |  |  |  | 8.91
NEWARK-TRIMBLE | 115 | ETL.3120 |  | ACT | 12.36 |  |  |  | 12.36
NEWARK-VALLECITOS | 60 | ETL.7670 |  | ACT | 12.38 |  | 2.23 |  | 10.15
NICOLAUS-CATLETT JCT | 60 | ETL.7680 |  | ACT | 20.15 |  |  |  | 20.15
NICOLAUS-CATLETT JCT | 60 | ETL.7680 |  | IDL | 4.45 |  |  |  | 4.45
NICOLAUS-CATLETT JCT (12KV) | 60 | ETL.7680 |  | IDL | 14.18 |  |  |  | 14.18
NICOLAUS-MARYSVILLE | 60 | ETL.7690 |  | ACT | 18.73 |  |  |  | 18.73
NICOLAUS-PLAINFIELD | 60 | ETL.7700 |  | ACT | 30.63 |  |  |  | 30.63
NICOLAUS-WILKINS SLOUGH | 60 | ETL.7710 |  | ACT | 28.69 |  |  |  | 28.69
NORTECH-NORTHERN RECEIVING STATION | 115 | ETL.1551 |  | ACT | 2.21 |  |  |  | 2.21
NORTH DUBLIN-CAYETANO | 230 | ETL.4500 |  | ACT | 3.02 |  | 3.02 |  | 0
NORTH DUBLIN-VINEYARD | 230 | ETL.4501 |  | ACT | 12.46 |  | 4.9 |  | 7.56
NORTH TOWER-MARTINEZ JCT #1 (21KV) | 115 | ETL.3130 |  | IDL | 2.61 |  | 1.75 |  | 0.86 | Idle Section
NORTHERN RECEIVING STATION-SCOTT #1 | 115 | ETL.3101 |  | ACT | 2.08 |  |  |  | 2.08
NORTHERN RECEIVING STATION-SCOTT #2 | 115 | ETL.3111 |  | ACT | 1.98 |  |  |  | 1.98
NOTRE DAME-BUTTE | 115 | ETL.4312 |  | ACT | 2.02 |  |  |  | 2.02
OAK PARK TAP | 60 | ETL.8142 |  | ACT | 0.87 |  |  |  | 0.87
OAKHURST TAP | 115 | ETL.1252 |  | ACT | 18.16 | 0.89 | 16.58 |  | 0.69
OAKLAND C-MARITIME | 115 | ETL.3135 |  | ACT | 2.36 |  |  |  | 2.36
OAKLAND C-TURBINES | 115 | ETL.3137 |  | ACT | 0.19 |  |  |  | 0.19
OAKLAND J-GRANT | 115 | ETL.3140 |  | ACT | 14.83 |  |  |  | 14.83
OCEANO-CALLENDER SW STA | 115 | ETL.2394 |  | ACT | 4.22 |  | 3 |  | 1.22
OIL CITY TAP | 70 | ETL.8574 |  | ACT | 0.05 |  |  |  | 0.05
OILFIELDS-SALINAS RIVER | 60 | ETL.7728 |  | ACT | 1.46 |  |  |  | 1.46
OILFIELDS-SARGENT CANYON | 60 | ETL.7725 |  | ACT | 2.02 |  |  |  | 2.02
OLEUM-G #1 | 115 | ETL.3150 |  | ACT | 11.29 | 2.06 | 6.95 |  | 2.28
OLEUM-G #2 | 115 | ETL.3160 |  | ACT | 11.3 | 2.06 | 6.95 |  | 2.29
OLEUM-MARTINEZ | 115 | ETL.3170 |  | ACT | 10.5 |  | 7.03 |  | 3.47
OLEUM-NORTH TOWER-CHRISTIE | 115 | ETL.3180 |  | ACT | 8.33 |  | 6.55 |  | 1.78
OLEUM-UNOCAL #1 | 115 | ETL.4260 |  | ACT | 0.01 |  |  |  | 0.01
OLEUM-UNOCAL #2 | 115 | ETL.4270 |  | ACT | 0.05 |  |  |  | 0.05
OLIVE SW STA-SMYRNA | 115 | ETL.1923 |  | ACT | 11.07 |  |  |  | 11.07
ORO FINO TAP | 60 | ETL.6721 |  | ACT | 1.3 | 1.3 |  |  | 0
ORO LOMA-CANAL #1 | 70 | ETL.9020 |  | ACT | 24.55 |  |  |  | 24.55
ORO LOMA-MENDOTA | 70 | ETL.9030 |  | ACT | 29.41 |  |  |  | 29.41
OROVILLE-TABLE MTN #2 (CDWR) | 230 | ETL.6623 | NON PGE | ACT | 10.09 |  | 3.67 |  | 6.42 | Non-PG&E
OROVILLE-THERMALITO-TABLE MTN #1 (CDWR) | 230 | ETL.6621 | NON PGE | ACT | 12.44 |  | 5.06 |  | 7.38 | Non-PG&E
OROVILLE-THERMALITO-TABLE MTN #3 (CDWR) | 230 | ETL.6622 | NON PGE | ACT | 12.4 |  | 3.6 |  | 8.8 | Non-PG&E
OWENS ILLINOIS TAP | 115 | ETL.3971 |  | ACT | 0.68 |  |  |  | 0.68
OXBOW TAP | 60 | ETL.7561 |  | ACT | 0.15 | 0.15 |  |  | 0
OXFORD TAP | 115 | ETL.3241 |  | ACT | 3.87 |  |  |  | 3.87
P-X #2 | 115 | ETL.3125 |  | ACT | 0.28 |  |  |  | 0.28
PACIFIC ETHANOL TAP | 60 | ETL.8325 |  | ACT | 0.68 |  |  |  | 0.68
PACIFIC LUMBER (SCOTIA) TAP | 60 | ETL.7852 |  | ACT | 0.52 |  |  |  | 0.52
PACIFIC OROVILLE POWER TAP | 60 | ETL.7731 |  | IDL | 0.78 |  |  |  | 0.78
PADRE FLAT SW STA-PANOCHE | 230 | ETL.5030 |  | ACT | 33.58 |  |  |  | 33.58
PAIGE SOLAR TAP | 70 | ETL.1262 | PGE | ACT | 1.04 |  |  |  | 1.04
PALERMO-BOGUE | 115 | ETL.3200 |  | ACT | 35.73 |  | 1.24 |  | 34.49
PALERMO-COLGATE | 230 | ETL.5360 |  | ACT | 29.61 |  | 16.87 |  | 12.74
PALERMO-NICOLAUS | 115 | ETL.3210 |  | ACT | 41.18 |  | 1.19 |  | 39.99
PALERMO-OROVILLE #1 | 60 | ETL.7730 |  | ACT | 6.94 |  | 1.18 |  | 5.76
PALERMO-OROVILLE #2 | 60 | ETL.7740 |  | ACT | 10.13 |  | 2.86 |  | 7.27
PALERMO-PEASE | 115 | ETL.3220 |  | ACT | 26.53 |  | 1.08 |  | 25.45
PALERMO-WYANDOTTE | 115 | ETL.4315 |  | ACT | 3.44 |  | 1.26 |  | 2.18
PANOCHE-CAL PEAK-STARWOOD | 115 | ETL.1051 |  | ACT | 0.09 |  |  |  | 0.09
PANOCHE-EXCELSIOR SW STA #1 | 115 | ETL.3250 |  | ACT | 28.5 |  |  |  | 28.5
PANOCHE-EXCELSIOR SW STA #2 | 115 | ETL.3260 |  | ACT | 28.5 |  |  |  | 28.5
PANOCHE-MENDOTA | 115 | ETL.3230 |  | ACT | 10.08 |  |  |  | 10.08
PANOCHE-ORO LOMA | 115 | ETL.3240 |  | ACT | 18.93 |  |  |  | 18.93
PANOCHE-PANOCHE ENERGY CENTER | 230 | ETL.2293 |  | ACT | 0.09 |  |  |  | 0.09
PANOCHE-TRANQUILLITY SW STA #1 | 230 | ETL.5000 |  | ACT | 12.14 |  |  |  | 12.14
PANOCHE-TRANQUILLITY SW STA #2 | 230 | ETL.5481 |  | ACT | 12.14 |  |  |  | 12.14
PARADISE-BUTTE | 115 | ETL.4396 |  | ACT | 13.58 | 0.62 | 7.59 |  | 5.37
PARADISE-TABLE MTN | 115 | ETL.4316 |  | ACT | 35.6 | 6.69 | 19.93 |  | 8.98
PARAMOUNT FARMS TAP | 115 | ETL.1744 |  | ACT | 0.57 |  |  |  | 0.57
PARDEE #1 TAP | 60 | ETL.8231 |  | ACT | 4.33 |  | 4.33 |  | 0
PARDEE #2 TAP | 60 | ETL.8251 |  | ACT | 0.11 |  | 0.1 |  | 0.01
PARKWAY-MORAGA | 230 | ETL.5930 |  | ACT | 23.64 | 4.31 | 12.24 |  | 7.09
PASO ROBLES-TEMPLETON | 70 | ETL.9400 |  | ACT | 4.9 |  |  |  | 4.9
PEABODY-BIRDS LANDING SW STA | 230 | ETL.6171 |  | ACT | 19.85 |  |  |  | 19.85
PEACHTON-PEASE | 60 | ETL.8426 |  | ACT | 16.35 |  |  |  | 16.35
PEASE-HARTER | 60 | ETL.7760 |  | ACT | 15.91 |  |  |  | 15.91
PEASE-MARYSVILLE-HARTER | 60 | ETL.7770 |  | ACT | 10.35 |  |  |  | 10.35
PEASE-RIO OSO | 115 | ETL.3270 |  | ACT | 27.61 |  |  |  | 27.61
PENN ZIER TAP | 70 | ETL.8575 |  | ACT | 3 |  |  |  | 3
PENNGROVE SUB TAP | 115 | ETL.2061 |  | ACT | 0.81 |  |  |  | 0.81
PENTLAND TAP | 70 | ETL.8973 |  | ACT | 0.55 |  |  |  | 0.55
PEORIA TAP | 115 | ETL.2391 |  | ACT | 0.86 |  | 0.86 |  | 0
PERMANENTE #1 TAP | 60 | ETL.7621 |  | ACT | 0.31 |  | 0.13 |  | 0.18
PERMANENTE #2 TAP | 60 | ETL.7622 |  | ACT | 0.51 |  | 0.34 |  | 0.17
PHILO JCT-ELK | 60 | ETL.7780 |  | ACT | 37.24 |  | 32.94 | 0.03 | 4.27
PIERCY-METCALF | 115 | ETL.4318 |  | ACT | 4.72 |  |  |  | 4.72
PINE GROVE TAP | 60 | ETL.8351 |  | ACT | 2.67 | 0.48 | 2.19 |  | 0
PIT #1-COTTONWOOD | 230 | ETL.5390 |  | ACT | 59.75 | 7.62 | 42.04 | 0.04 | 10.05
PIT #1-HAT CREEK #2-BURNEY | 60 | ETL.7040 |  | ACT | 12.92 |  | 10.58 |  | 2.34
PIT #1-MCARTHUR | 60 | ETL.7790 |  | ACT | 7.32 |  | 3.08 |  | 4.24
PIT #3-CARBERRY SW STA | 230 | ETL.5450 |  | ACT | 10.91 |  | 9.18 | 0.03 | 1.7
PIT #3-PIT #1 | 230 | ETL.5400 |  | ACT | 22.64 |  | 19.28 | 0.03 | 3.33
PIT #4 TAP | 230 | ETL.5432 | POWERGEN | ACT | 7.03 |  | 7.03 |  | 0
PIT #5-ROUND MTN #1 | 230 | ETL.5420 |  | ACT | 13.12 |  | 13.12 |  | 0
PIT #5-ROUND MTN #2 | 230 | ETL.5430 |  | ACT | 13.11 |  | 13.11 |  | 0
PIT #6 JCT-ROUND MTN | 230 | ETL.5440 |  | ACT | 8.15 |  | 8.15 |  | 0
PIT #6 TAP | 230 | ETL.5441 | POWERGEN | ACT | 3.43 |  | 3.43 |  | 0
PIT #7 TAP | 230 | ETL.5442 | POWERGEN | ACT | 3.59 |  | 3.59 |  | 0
PITTSBURG #2 TAP | 60 | ETL.8371 |  | ACT | 1.17 |  |  |  | 1.17
PITTSBURG-BLACK DIAMOND ENERGY STORAGE | 230 | ETL.1192 |  | ACT | 0.06 |  |  |  | 0.06
PITTSBURG-CLAYTON #1 | 115 | ETL.3280 |  | ACT | 16.82 |  | 6.01 |  | 10.81
PITTSBURG-CLAYTON #3 | 115 | ETL.3290 |  | ACT | 8.41 |  | 2.91 |  | 5.5
PITTSBURG-CLAYTON #4 | 115 | ETL.3291 |  | ACT | 8.32 |  | 2.91 |  | 5.41
PITTSBURG-COLUMBIA STEEL | 115 | ETL.3300 |  | ACT | 9.23 |  | 1.21 |  | 8.02
PITTSBURG-DELTA ENERGY CENTER #1 | 230 | ETL.1254 | NON PGE | ACT | 0.01 |  |  |  | 0.01 | Non-PG&E
PITTSBURG-DELTA ENERGY CENTER #2 | 230 | ETL.3315 | NON PGE | ACT | 0.01 |  |  |  | 0.01 | Non-PG&E
PITTSBURG-EASTSHORE | 230 | ETL.5462 |  | ACT | 34.96 | 11.9 | 7.78 |  | 15.28
PITTSBURG-KIRKER-COLUMBIA STEEL | 115 | ETL.3310 |  | ACT | 9.26 |  | 1.13 |  | 8.13
PITTSBURG-LOS MEDANOS #1 | 115 | ETL.3304 |  | ACT | 0.5 |  |  |  | 0.5
PITTSBURG-LOS MEDANOS #2 | 115 | ETL.3305 |  | ACT | 0.5 |  |  |  | 0.5
PITTSBURG-MARTINEZ #1 | 115 | ETL.3320 |  | ACT | 17.23 |  | 0.34 |  | 16.89
PITTSBURG-MARTINEZ #2 | 115 | ETL.3330 |  | ACT | 15.83 |  | 0.38 |  | 15.45
PITTSBURG-SAN MATEO | 230 | ETL.5463 |  | ACT | 47.4 | 11.89 | 7.78 |  | 27.73
PITTSBURG-SAN RAMON | 230 | ETL.5490 |  | ACT | 21.66 | 6.1 | 7.7 |  | 7.86
PITTSBURG-TASSAJARA | 230 | ETL.5470 |  | ACT | 17.36 | 6.11 | 6.65 |  | 4.6
PITTSBURG-TESLA #1 | 230 | ETL.5510 |  | ACT | 31.35 |  | 18 | 0.05 | 13.3
PITTSBURG-TESLA #2 | 230 | ETL.5520 |  | ACT | 31.32 |  | 18.03 | 0.04 | 13.25
PITTSBURG-TESORO | 230 | ETL.5500 |  | ACT | 11.27 |  |  |  | 11.27
PITTSBURG-TIDEWATER | 230 | ETL.5530 |  | ACT | 11.27 |  |  |  | 11.27
PLACER-DEL MAR | 60 | ETL.7800 |  | ACT | 10.8 |  | 4.52 |  | 6.28
PLACER-GOLD HILL #1 | 115 | ETL.3340 |  | ACT | 20.73 |  | 9.92 |  | 10.81
PLACER-GOLD HILL #2 | 115 | ETL.4290 |  | ACT | 20.67 |  | 9.92 |  | 10.75
PLUMAS-SIERRA TAP | 60 | ETL.6291 |  | ACT | 0.75 | 0.01 | 0.06 |  | 0.68
POE-RIO OSO | 230 | ETL.5540 |  | ACT | 56.09 | 4.41 | 14.01 |  | 37.67
POINT PINOLE TAP | 115 | ETL.3792 |  | ACT | 1.29 |  |  |  | 1.29
POINT PINOLE TAP | 115 | ETL.3792 |  | IDL | 0.01 |  |  |  | 0.01
POST OFFICE TAP | 115 | ETL.4122 |  | ACT | 0.75 |  |  |  | 0.75
POTTER VALLEY-MENDOCINO | 60 | ETL.7810 |  | ACT | 10.94 |  | 8.38 |  | 2.56
POTTER VALLEY-WILLITS | 60 | ETL.7820 |  | ACT | 13.16 | 5.51 | 6.35 |  | 1.3
PSE MCKITTRICK TAP | 115 | ETL.2632 |  | ACT | 5.21 |  |  |  | 5.21
Padre Flat SW STA – Freeman Wright | 230 | ETL.1492 |  | ACT | 0.04 |  |  |  | 0.04
QUEBEC TAP | 115 | ETL.1311 |  | ACT | 4.38 |  |  |  | 4.38
QUINTO SW STA-FINK SW STA | 230 | ETL.5070 |  | ACT | 41.57 |  |  |  | 41.57
RACETRACK TAP | 115 | ETL.2393 |  | ACT | 3.54 |  | 3.54 |  | 0
RADUM-LIVERMORE | 60 | ETL.7830 |  | ACT | 4.65 |  |  |  | 4.65
RADUM-VALLECITOS | 60 | ETL.8280 |  | ACT | 10.6 |  |  |  | 10.6
RAINBOW TAP | 115 | ETL.2031 |  | ACT | 2.59 |  |  |  | 2.59
RALPH TAP | 230 | ETL.4931 |  | ACT | 0.06 |  |  |  | 0.06
RANCHERS COTTON TAP | 115 | ETL.2311 |  | ACT | 2.1 |  |  |  | 2.1
RANCHO SECO-BELLOTA #1 | 230 | ETL.5550 |  | ACT | 27.39 |  |  |  | 27.39
RANCHO SECO-BELLOTA #2 | 230 | ETL.5560 |  | ACT | 27.36 |  |  |  | 27.36
RAVENSWOOD-AMES #1 | 115 | ETL.3360 |  | ACT | 7.07 |  |  |  | 7.07
RAVENSWOOD-AMES #2 | 115 | ETL.3370 |  | ACT | 7.09 |  |  |  | 7.09
RAVENSWOOD-BAIR #1 | 115 | ETL.3380 |  | ACT | 7.43 |  |  |  | 7.43
RAVENSWOOD-BAIR #2 | 115 | ETL.3385 |  | ACT | 11.29 |  |  |  | 11.29
RAVENSWOOD-COOLEY LANDING #1 | 115 | ETL.3390 |  | ACT | 1.62 |  |  |  | 1.62
RAVENSWOOD-COOLEY LANDING #2 | 115 | ETL.3400 |  | ACT | 1.62 |  |  |  | 1.62
RAVENSWOOD-PALO ALTO #1 | 115 | ETL.3410 |  | ACT | 4.27 |  |  |  | 4.27
RAVENSWOOD-PALO ALTO #2 | 115 | ETL.3420 |  | ACT | 4.26 |  |  |  | 4.26
RAVENSWOOD-SAN MATEO | 115 | ETL.3430 |  | ACT | 12.04 |  |  |  | 12.04
RAVENSWOOD-SAN MATEO #1 | 230 | ETL.5580 |  | ACT | 11.89 |  |  |  | 11.89
RAVENSWOOD-SAN MATEO #2 | 230 | ETL.5351 |  | ACT | 11.88 |  |  |  | 11.88
RED BANK TAP | 60 | ETL.6631 |  | ACT | 0.68 |  |  |  | 0.68
REEDLEY-DINUBA #1 | 70 | ETL.9050 |  | ACT | 7.7 |  |  |  | 7.7
REEDLEY-OROSI | 70 | ETL.9060 |  | ACT | 10.89 |  |  |  | 10.89
RESERVE OIL TAP | 70 | ETL.8721 |  | ACT | 0.58 |  |  |  | 0.58
RINCON #1 TAP | 115 | ETL.1601 |  | ACT | 0.57 | 0.08 | 0.49 |  | 0
RINCON #2 TAP | 115 | ETL.1611 |  | ACT | 0.55 | 0.07 | 0.48 |  | 0
RIO BRAVO (FRESNO) TAP | 115 | ETL.2312 |  | ACT | 0.32 |  |  |  | 0.32
RIO BRAVO (ROCKLIN) TAP | 115 | ETL.7974 |  | ACT | 0.4 |  |  |  | 0.4
RIO BRAVO HYDRO | 70 | ETL.9070 |  | ACT | 0.24 |  |  |  | 0.24
RIO BRAVO TOMATO TAP | 115 | ETL.8328 |  | ACT | 0.43 |  |  |  | 0.43
RIO BRAVO-KERN OIL | 115 | ETL.1922 |  | IDL | 3.72 |  |  |  | 3.72
RIO DELL JCT-BRIDGEVILLE | 60 | ETL.7850 |  | ACT | 21.22 |  | 15.05 |  | 6.17
RIO DELL TAP | 60 | ETL.7851 |  | ACT | 5.35 |  | 0.79 |  | 4.56
RIO OSO-ATLANTIC | 230 | ETL.5590 |  | ACT | 17.68 |  |  |  | 17.68
RIO OSO-BRIGHTON | 230 | ETL.5600 |  | ACT | 27.17 |  |  |  | 27.17
RIO OSO-GOLD HILL | 230 | ETL.5610 |  | ACT | 28.63 |  |  | 0.02 | 28.61
RIO OSO-LINCOLN | 115 | ETL.1320 |  | ACT | 11.04 |  |  |  | 11.04
RIO OSO-LOCKEFORD | 230 | ETL.5620 |  | ACT | 65.13 |  |  |  | 65.13
RIO OSO-NICOLAUS | 115 | ETL.3440 |  | ACT | 5.39 |  |  |  | 5.39
RIO OSO-WEST SACRAMENTO | 115 | ETL.3450 |  | ACT | 43.55 |  |  |  | 43.55
RIO OSO-WOODLAND #1 | 115 | ETL.3460 |  | ACT | 45.25 |  |  |  | 45.25
RIO OSO-WOODLAND #2 | 115 | ETL.3470 |  | ACT | 53.37 |  |  |  | 53.37
RIPON-MANTECA | 115 | ETL.1062 |  | ACT | 9.16 |  |  |  | 9.16
RIVERBANK JCT SW STA-RIPON | 115 | ETL.3841 |  | ACT | 18.02 |  |  |  | 18.02
ROBERTSON TAP | 60 | ETL.8322 |  | ACT | 0.82 |  |  |  | 0.82
ROCK CREEK-POE | 230 | ETL.5630 |  | ACT | 26.98 | 6.85 | 20.13 |  | 0
ROLLINS TAP | 60 | ETL.6762 |  | ACT | 0.73 | 0.34 | 0.39 |  | 0
ROSE TAP | 70 | ETL.9251 |  | ACT | 0.31 |  |  |  | 0.31
ROSSMOOR #1 TAP | 230 | ETL.5451 |  | ACT | 0.69 | 0.48 |  |  | 0.21
ROSSMOOR #2 TAP | 230 | ETL.5461 |  | ACT | 0.66 | 0.46 |  |  | 0.2
ROUGH & READY TAP | 60 | ETL.8324 |  | ACT | 0.95 |  |  |  | 0.95
ROUND MTN-COTTONWOOD #2 | 230 | ETL.5640 |  | ACT | 33.67 | 3.73 | 22.05 |  | 7.89
ROUND MTN-COTTONWOOD #3 | 230 | ETL.5650 |  | ACT | 33.36 | 7.17 | 19.17 | 0.03 | 6.99
ROUND MTN-TABLE MTN #1 | 500 | ETL.6060 |  | ACT | 89.03 | 11.74 | 64.63 |  | 12.66
ROUND MTN-TABLE MTN #2 | 500 | ETL.6070 |  | ACT | 89.02 | 11.77 | 67.19 |  | 10.06
RUSSELL CITY ENERGY CENTER-EASTSHORE #1 | 230 | ETL.6155 |  | ACT | 1.19 |  |  |  | 1.19
RUSSELL CITY ENERGY CENTER-EASTSHORE #2 | 230 | ETL.6157 |  | ACT | 1.2 |  |  |  | 1.2
SAFEWAY TAP | 115 | ETL.3984 |  | ACT | 0.68 |  |  |  | 0.68
SALADO-CROW CREEK SW STA | 60 | ETL.7858 |  | ACT | 3.77 |  |  |  | 3.77
SALADO-NEWMAN #2 | 60 | ETL.7870 |  | ACT | 21.58 |  |  |  | 21.58
SALINAS-FIRESTONE #1 | 60 | ETL.7900 |  | ACT | 6.15 |  |  |  | 6.15
SALINAS-FORT ORD #1 | 60 | ETL.7890 |  | ACT | 10.22 |  | 3.02 |  | 7.2
SALINAS-FORT ORD #2 | 60 | ETL.8423 |  | ACT | 10.15 |  | 3 |  | 7.15
SALINAS-LAGUNITAS | 60 | ETL.7920 |  | ACT | 5.84 |  |  |  | 5.84
SALINAS-LAURELES | 60 | ETL.7930 |  | ACT | 27.44 |  | 18.24 | 0.37 | 8.83
SALINAS-SPENCE | 60 | ETL.7910 |  | ACT | 11.61 |  |  |  | 11.61
SALMON CREEK TAP | 60 | ETL.6981 |  | ACT | 10.51 | 1.04 | 5.4 |  | 4.07
SALT SPRINGS-TIGER CREEK | 115 | ETL.3500 |  | ACT | 16.48 | 1.66 | 14.82 |  | 0
SAN ANDREAS (CCSF) TAP | 60 | ETL.7571 |  | ACT | 0.39 |  |  |  | 0.39
SAN ARDO TAP | 60 | ETL.6421 |  | ACT | 0.34 |  |  |  | 0.34
SAN BENITO-HOLLISTER | 115 | ETL.2901 |  | ACT | 8.29 |  |  |  | 8.29
SAN BERNARD-TEJON | 70 | ETL.9080 |  | ACT | 6.96 |  |  |  | 6.96
SAN BRUNO TAP | 60 | ETL.7572 |  | ACT | 1.12 |  | 0.52 |  | 0.6
SAN FRANCISCO #2 | 115 | ETL.3279 |  | IDL | 3.15 |  |  |  | 3.15
SAN JOSE A-SAN JOSE B | 115 | ETL.3510 |  | ACT | 1.15 |  |  |  | 1.15
SAN JOSE B-STONE-EVERGREEN | 115 | ETL.1550 |  | ACT | 8.56 |  |  |  | 8.56
SAN LEANDRO-OAKLAND J #1 | 115 | ETL.3520 |  | ACT | 6.7 |  |  |  | 6.7
SAN LUIS #3 TAP | 115 | ETL.3244 |  | ACT | 16.11 |  |  |  | 16.11
SAN LUIS #5 TAP | 115 | ETL.3243 |  | ACT | 1.88 |  |  |  | 1.88
SAN LUIS OBISPO-CAYUCOS | 70 | ETL.9090 |  | ACT | 23.39 |  | 13.39 |  | 10
SAN LUIS OBISPO-OCEANO | 115 | ETL.3530 |  | ACT | 19.9 | 2.15 | 9.72 |  | 8.03
SAN LUIS OBISPO-SANTA MARIA | 115 | ETL.3540 |  | ACT | 25.96 | 2.16 | 11.12 |  | 12.68
SAN MATEO-BAIR | 60 | ETL.7940 |  | ACT | 13.97 |  |  |  | 13.97
SAN MATEO-BAY MEADOWS #1 | 115 | ETL.3550 |  | ACT | 4.3 |  |  |  | 4.3
SAN MATEO-BAY MEADOWS #2 | 115 | ETL.3560 |  | ACT | 4.26 |  |  |  | 4.26
SAN MATEO-BELMONT | 115 | ETL.3570 |  | ACT | 7.2 |  |  |  | 7.2
SAN MATEO-HILLSDALE JCT | 60 | ETL.7950 |  | ACT | 6.85 |  | 1.15 |  | 5.7
SAN MATEO-MARTIN #3 | 115 | ETL.3580 |  | ACT | 11.55 |  |  |  | 11.55
SAN MATEO-MARTIN #4 | 115 | ETL.7500 |  | ACT | 11.62 |  |  |  | 11.62
SAN MATEO-MARTIN #6 | 115 | ETL.3590 |  | ACT | 11.69 |  |  |  | 11.69
SAN MIGUEL-PASO ROBLES | 70 | ETL.9390 |  | ACT | 9.92 |  |  |  | 9.92
SAN PABLO #1 TAP | 115 | ETL.3801 |  | ACT | 0.44 |  |  |  | 0.44
SAN PABLO #2 TAP | 115 | ETL.3791 |  | ACT | 0.45 |  |  |  | 0.45
SAN RAMON RESEARCH CENTER TAP | 230 | ETL.5921 |  | ACT | 3.27 |  |  |  | 3.27
SAN RAMON-MORAGA | 230 | ETL.5660 |  | ACT | 22.24 | 13.67 | 3.24 |  | 5.33
SAN RAMON-RADUM | 60 | ETL.7960 |  | ACT | 7.06 |  |  |  | 7.06
SANDBAR TAP | 115 | ETL.1403 |  | ACT | 0.1 | 0.1 |  |  | 0
SANGER COGEN TAP | 115 | ETL.9141 |  | ACT | 0.83 |  |  |  | 0.83
SANGER-CALIFORNIA AVE | 115 | ETL.9130 |  | ACT | 9.15 |  |  |  | 9.15
SANGER-CALIFORNIA AVE #1 | 70 | ETL.9120 |  | IDL | 2.08 |  |  |  | 2.08
SANGER-MALAGA | 115 | ETL.3600 |  | ACT | 8.69 |  |  |  | 8.69
SANGER-REEDLEY | 115 | ETL.9140 |  | ACT | 20.61 |  |  |  | 20.61
SANTA FE GEOTHERMAL TAP | 230 | ETL.4782 |  | ACT | 1.04 | 1.04 |  |  | 0
SANTA MARIA-SISQUOC | 115 | ETL.3610 |  | ACT | 10.57 |  |  |  | 10.57
SANTA PAULA-MILLBRAE | 115 | ETL.7580 |  | ACT | 0.09 |  |  |  | 0.09
SANTA ROSA-CORONA | 115 | ETL.4309 |  | ACT | 14.34 |  | 1.09 |  | 13.25
SANTA TERESA-EDENVALE | 115 | ETL.1132 |  | ACT | 0.68 |  |  |  | 0.68
SANTA YNEZ TAP | 115 | ETL.3701 |  | ACT | 4.06 |  | 3.49 |  | 0.57
SARATOGA-VASONA | 230 | ETL.5931 |  | ACT | 3.41 |  |  |  | 3.41
SCHINDLER-COALINGA #2 | 70 | ETL.9150 |  | ACT | 17.19 |  |  |  | 17.19
SCHINDLER-FIVE POINTS SW STA | 70 | ETL.9161 |  | ACT | 1.7 |  |  |  | 1.7
SCHULTE SW STA-KASSON-MANTECA | 115 | ETL.7472 |  | ACT | 16.58 |  |  |  | 16.58
SCHULTE SW STA-LAMMERS | 115 | ETL.3993 |  | ACT | 0.69 |  |  |  | 0.69
SEBASTIANI TAP | 60 | ETL.8072 |  | ACT | 0.01 |  |  |  | 0.01
SEMITROPIC-CHARCA | 115 | ETL.3620 |  | ACT | 6.91 |  |  |  | 6.91
SEMITROPIC-MIDWAY #1 | 115 | ETL.3630 |  | ACT | 14.1 |  |  |  | 14.1
SEMITROPIC-MIDWAY #2 | 115 | ETL.3640 |  | ACT | 10.53 |  |  |  | 10.53
SEMITROPIC-MIDWAY #2 | 115 | ETL.3640 |  | IDL | 9.58 |  |  |  | 9.58
SEMITROPIC-WASCO | 70 | ETL.9170 |  | ACT | 6.32 |  |  |  | 6.32
SERRAMONTE TAP | 115 | ETL.2211 |  | ACT | 2.55 |  |  |  | 2.55
SF AIRPORT-SAN MATEO | 115 | ETL.3650 |  | ACT | 6.09 |  |  |  | 6.09
SHAFTER-RIO BRAVO | 115 | ETL.3660 |  | ACT | 8.31 |  |  |  | 8.31
SHARON PRISON TAP | 115 | ETL.1251 |  | ACT | 2.57 |  |  |  | 2.57
SHILOH II-BIRDS LANDING SW STA | 230 | ETL.4240 |  | ACT | 3.56 |  |  |  | 3.56
SHREDDER TAP | 115 | ETL.3381 |  | ACT | 1.38 |  |  |  | 1.38
SIERRA #1 | 115 | ETL.3670 |  | IDL | 5.47 |  |  |  | 5.47
SIERRA #2 | 115 | ETL.3680 |  | IDL | 4.86 |  |  |  | 4.86
SIERRA (PSE) TAP | 115 | ETL.1933 |  | ACT | 1.81 |  |  |  | 1.81
SIERRA PAC IND (QUINCY) TAP | 60 | ETL.6292 |  | ACT | 0.02 |  |  |  | 0.02
SIERRA PACIFIC IND TAP | 115 | ETL.7401 |  | ACT | 0.06 |  |  |  | 0.06
SILVERADO-FULTON JCT | 115 | ETL.1610 |  | ACT | 26.16 | 5.02 | 16.85 |  | 4.29
SIMPSON-KORBEL TAP | 60 | ETL.6804 |  | ACT | 0.39 |  |  |  | 0.39
SISQUOC-GAREY | 115 | ETL.3690 |  | ACT | 5.02 | 0.23 | 0.13 |  | 4.66
SISQUOC-SANTA YNEZ SW STA | 115 | ETL.3700 |  | ACT | 22.11 |  | 16.1 |  | 6.01
SKAGGS ISLAND #1 TAP | 115 | ETL.1832 |  | ACT | 0.59 |  |  |  | 0.59
SKAGGS ISLAND #2 TAP | 115 | ETL.1842 |  | ACT | 0.6 |  |  |  | 0.6
SLAC TAP | 60 | ETL.7221 |  | ACT | 1.41 |  |  |  | 1.41
SLY CREEK TAP | 115 | ETL.4221 |  | ACT | 5.34 | 5.34 |  |  | 0
SMARTVILLE TAP | 60 | ETL.6522 |  | ACT | 0.09 |  | 0.09 |  | 0
SMARTVILLE-CAMP FAR WEST | 60 | ETL.7970 |  | ACT | 17.81 |  | 9.28 |  | 8.53
SMARTVILLE-MARYSVILLE | 60 | ETL.7980 |  | ACT | 20.14 |  | 4.86 |  | 15.28
SMARTVILLE-NICOLAUS #1 | 60 | ETL.7990 |  | ACT | 29.6 |  | 4.75 |  | 24.85
SMARTVILLE-NICOLAUS #2 | 60 | ETL.8000 |  | ACT | 30.16 |  | 4.83 |  | 25.33
SMUD TAP | 230 | ETL.1184 |  | ACT | 0.12 | 0.12 |  |  | 0
SMYRNA-SEMITROPIC-MIDWAY | 115 | ETL.3710 |  | ACT | 22.39 |  |  |  | 22.39
SNEATH LANE-HALF MOON BAY | 60 | ETL.7212 |  | ACT | 15.41 | 11.17 | 2.36 |  | 1.88
SNEATH LANE-PACIFICA | 60 | ETL.7575 |  | ACT | 3.26 | 1.36 | 1.32 |  | 0.58
SOBRANTE-G #1 | 115 | ETL.3720 |  | ACT | 5.34 | 3.86 | 1.35 |  | 0.13
SOBRANTE-G #2 | 115 | ETL.3730 |  | ACT | 5.39 | 3.86 | 1.44 |  | 0.09
SOBRANTE-GRIZZLY-CLAREMONT #1 | 115 | ETL.3740 |  | ACT | 19.57 | 12.29 | 5.05 |  | 2.23
SOBRANTE-GRIZZLY-CLAREMONT #2 | 115 | ETL.3750 |  | ACT | 19.3 | 12.15 | 4.62 |  | 2.53
SOBRANTE-MORAGA | 115 | ETL.3742 |  | ACT | 10.36 | 0.21 | 5.38 |  | 4.77
SOBRANTE-R #1 | 115 | ETL.3770 |  | ACT | 5.54 | 3.86 | 1.4 |  | 0.28
SOBRANTE-R #2 | 115 | ETL.3780 |  | ACT | 5.53 | 3.86 | 1.4 |  | 0.27
SOBRANTE-STANDARD OIL SW STA #1 | 115 | ETL.3800 |  | ACT | 18.89 |  | 8.56 |  | 10.33
SOBRANTE-STANDARD OIL SW STA #2 | 115 | ETL.3790 |  | ACT | 18.89 |  | 8.54 |  | 10.35
SOLAR SW STA-CALIENTE SW STA #1 | 230 | ETL.5215 |  | ACT | 8.22 |  |  |  | 8.22
SOLAR SW STA-CALIENTE SW STA #2 | 230 | ETL.5225 |  | ACT | 8.22 |  |  |  | 8.22
SOLAR TANNEHILL TAP | 70 | ETL.9231 |  | ACT | 2.67 |  |  |  | 2.67
SOLEDAD #1 | 60 | ETL.8010 |  | ACT | 19.37 |  |  |  | 19.37
SOLEDAD #2 | 60 | ETL.8020 |  | ACT | 18.86 |  |  |  | 18.86
SOLEDAD #3 | 60 | ETL.8030 |  | ACT | 1.62 |  |  |  | 1.62
SOLEDAD #4 | 60 | ETL.8040 |  | ACT | 6.1 |  |  |  | 6.1
SONOMA-PUEBLO | 115 | ETL.3810 |  | ACT | 18.48 |  | 2.59 | 0.05 | 15.84
SPAULDING #3-SPAULDING #1 | 60 | ETL.8050 | POWERGEN | ACT | 1.08 |  | 0.95 |  | 0.13
SPAULDING-SUMMIT | 60 | ETL.8060 |  | ACT | 19.64 |  | 14.71 | 1.06 | 3.87
SPENCE-FIRESTONE | 60 | ETL.1152 |  | ACT | 1.66 |  |  |  | 1.66
SPI (BURNEY) TAP | 230 | ETL.5392 |  | ACT | 0.04 |  | 0.04 |  | 0
SPRING GAP TAP | 115 | ETL.1402 |  | ACT | 1.64 | 1.64 |  |  | 0
STAGG-COUNTRY CLUB #1 | 60 | ETL.8080 |  | ACT | 2.43 |  |  |  | 2.43
STAGG-COUNTRY CLUB #2 | 60 | ETL.8090 |  | ACT | 2.46 |  |  |  | 2.46
STAGG-HAMMER | 60 | ETL.8100 |  | ACT | 4.25 |  |  |  | 4.25
STAGG-TESLA | 230 | ETL.5680 |  | ACT | 23.64 |  |  |  | 23.64
STANDARD #1 & #2 (12KV) | 60 | ETL.9490 |  | IDL | 4.2 |  |  |  | 4.2
STANISLAUS RECOVERY TAP | 60 | ETL.7861 |  | ACT | 0.11 |  |  |  | 0.11
STANISLAUS-MANTECA #2 | 115 | ETL.3820 |  | ACT | 53.95 |  | 24.97 |  | 28.98
STANISLAUS-MELONES SW STA-MANTECA #1 | 115 | ETL.3830 |  | ACT | 61.15 |  | 32.13 |  | 29.02
STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | 115 | ETL.3840 |  | ACT | 43.8 |  | 32.09 |  | 11.71
STAUFFER TAP | 60 | ETL.6372 |  | ACT | 0.58 |  |  |  | 0.58
STELLING-MONTA VISTA | 115 | ETL.1000 |  | ACT | 1.61 |  |  |  | 1.61
STELLING-WOLFE | 115 | ETL.2680 |  | ACT | 1.46 |  |  |  | 1.46
STOCKTON A #1 | 60 | ETL.8110 |  | ACT | 5.58 |  |  |  | 5.58
STOCKTON A-LOCKEFORD-BELLOTA #1 | 115 | ETL.3880 |  | ACT | 42.8 |  |  |  | 42.8
STOCKTON A-LOCKEFORD-BELLOTA #2 | 115 | ETL.3890 |  | ACT | 34.49 |  |  |  | 34.49
STOCKTON A-WEBER #1 | 60 | ETL.8120 |  | ACT | 13.2 |  |  |  | 13.2
STOCKTON A-WEBER #2 | 60 | ETL.8130 |  | ACT | 9.86 |  |  |  | 9.86
STOCKTON A-WEBER #3 | 60 | ETL.8140 |  | ACT | 9.79 |  |  |  | 9.79
STOCKTON-NEWARK (12KV) | 60 | ETL.8150 |  | IDL | 0.62 |  |  |  | 0.62
STONE CORRAL TAP | 70 | ETL.8611 |  | ACT | 7.56 |  |  |  | 7.56
STONE-EVERGREEN | 115 | ETL.1424 |  | ACT | 2.23 |  |  |  | 2.23
STONY POINT TAP | 115 | ETL.2062 |  | ACT | 3.08 |  |  |  | 3.08
SUMIDEN WIRE PRODUCTS TAP | 60 | ETL.8141 |  | ACT | 0.19 |  |  |  | 0.19
SUNOL TAP | 60 | ETL.7671 |  | ACT | 0.08 |  |  |  | 0.08
SURF TAP | 115 | ETL.1381 |  | ACT | 11.37 |  | 2.08 |  | 9.29
SUTTER HOME SW STA-LOCKEFORD-LODI | 60 | ETL.8068 |  | ACT | 29.76 |  |  |  | 29.76
SUTTER HOME SW STA-STAGG | 60 | ETL.8070 |  | ACT | 17.13 |  |  |  | 17.13
SUTTER HOME-SUTTER HOME SW STA | 60 | ETL.8069 |  | ACT | 0.03 |  |  |  | 0.03
SWIFT-METCALF | 115 | ETL.3900 |  | ACT | 8.93 |  |  |  | 8.93
SYCAMORE CREEK-NOTRE DAME-TABLE MTN | 115 | ETL.4314 |  | ACT | 20.34 |  |  |  | 20.34
SYCAMORE TAP | 70 | ETL.9281 |  | ACT | 2.04 |  |  |  | 2.04
TABLE MTN-BUTTE #1 | 115 | ETL.3910 |  | ACT | 19.54 |  |  |  | 19.54
TABLE MTN-BUTTE #2 | 115 | ETL.3920 |  | ACT | 15.82 |  |  |  | 15.82
TABLE MTN-PALERMO | 230 | ETL.5690 |  | ACT | 14.57 |  | 7.85 |  | 6.72
TABLE MTN-PEACHTON | 60 | ETL.8425 |  | ACT | 14.84 |  |  |  | 14.84
TABLE MTN-RIO OSO | 230 | ETL.5700 |  | ACT | 50.18 |  | 12.38 |  | 37.8
TABLE MTN-TESLA | 500 | ETL.6080 |  | ACT | 135 |  |  |  | 135
TABLE MTN-VACA | 500 | ETL.6090 |  | ACT | 83.3 |  |  |  | 83.3
TAFT-CHALK CLIFF | 115 | ETL.3940 |  | ACT | 7.18 |  |  |  | 7.18
TAFT-CUYAMA #1 | 70 | ETL.9200 |  | ACT | 19.25 |  |  |  | 19.25
TAFT-CUYAMA #2 | 70 | ETL.9210 |  | ACT | 18.74 |  |  |  | 18.74
TAFT-ELK HILLS | 70 | ETL.9220 |  | ACT | 12.39 |  |  |  | 12.39
TAFT-MARICOPA | 70 | ETL.9230 |  | ACT | 5.98 |  |  |  | 5.98
TASSAJARA-NEWARK | 230 | ETL.5920 |  | ACT | 31.8 | 11.36 | 7 | 0.48 | 12.96
TECUYA TAP | 70 | ETL.9311 |  | ACT | 1.92 |  |  |  | 1.92
TEICHERT TAP | 115 | ETL.1266 |  | ACT | 2.11 |  |  |  | 2.11
TEJON-LEBEC | 70 | ETL.9250 |  | ACT | 12.95 |  | 5.8 |  | 7.15
TEMBLOR-KERNRIDGE | 115 | ETL.3950 |  | ACT | 4.78 |  |  |  | 4.78
TEMBLOR-SAN LUIS OBISPO | 115 | ETL.3960 |  | ACT | 57.78 | 11.43 | 19.59 |  | 26.76
TEMPLETON-ATASCADERO | 70 | ETL.9410 |  | ACT | 8.82 |  | 5.1 |  | 3.72
TEMPLETON-GATES | 230 | ETL.5934 |  | ACT | 52.18 |  | 6.97 |  | 45.21
TERMINOUS TAP | 60 | ETL.8071 |  | ACT | 3.01 |  |  |  | 3.01
TES TAP | 230 | ETL.4531 |  | ACT | 3.28 |  |  |  | 3.28
TESLA-LAWRENCE LAB | 115 | ETL.4250 |  | ACT | 9.02 |  |  |  | 9.02
TESLA-LOS BANOS #1 | 500 | ETL.6100 |  | ACT | 57.14 |  | 3.68 |  | 53.46
TESLA-METCALF | 500 | ETL.6110 |  | ACT | 35.31 |  | 27.79 |  | 7.52
TESLA-NEWARK #1 | 230 | ETL.5720 |  | ACT | 28.19 |  | 4.78 | 0.48 | 22.93
TESLA-NEWARK #2 | 230 | ETL.5354 |  | ACT | 40.82 |  | 8.14 | 0.48 | 32.2
TESLA-RAVENSWOOD | 230 | ETL.5730 |  | ACT | 37.14 |  | 4.93 | 0.48 | 31.73
TESLA-SALADO #1 | 115 | ETL.3990 |  | ACT | 32.08 |  | 3.46 |  | 28.62
TESLA-SALADO-MANTECA | 115 | ETL.4000 |  | ACT | 53.97 |  | 3.97 |  | 50
TESLA-SCHULTE SW STA #1 | 115 | ETL.3980 |  | ACT | 7.37 |  |  |  | 7.37
TESLA-SCHULTE SW STA #2 | 115 | ETL.3970 |  | ACT | 7.34 |  |  |  | 7.34
TESLA-STOCKTON COGEN JCT | 115 | ETL.4010 |  | ACT | 25.08 |  |  |  | 25.08
TESLA-TRACY #1 | 230 | ETL.5740 |  | ACT | 5.68 |  |  |  | 5.68
TESLA-TRACY #2 | 230 | ETL.5750 |  | ACT | 5.68 |  |  |  | 5.68
TESLA-TRACY(115KV) | 115 | ETL.4020 |  | ACT | 27.85 |  |  |  | 27.85
TESLA-TRACY(115KV) | 115 | ETL.4020 |  | IDL | 1.15 |  |  |  | 1.15
TESLA-TRACY(500KV) | 500 | ETL.6120 |  | ACT | 1.13 |  |  |  | 1.13
TESLA-WESTLEY | 230 | ETL.5760 |  | ACT | 45.06 |  |  |  | 45.06
TESORO-SOBRANTE | 230 | ETL.5670 |  | ACT | 12.32 | 0.56 | 5.8 |  | 5.96
TEVIS #1 TAP | 115 | ETL.1144 |  | ACT | 3.25 |  |  |  | 3.25
TEVIS #2 TAP | 115 | ETL.1143 |  | ACT | 3.29 |  |  |  | 3.29
TEXACO BASIC SCHOOL TAP | 70 | ETL.8972 |  | ACT | 0.75 |  |  |  | 0.75
TEXACO TAP | 60 | ETL.6411 |  | ACT | 0.72 |  |  |  | 0.72
THERMAL ENERGY TAP | 115 | ETL.4011 |  | IDL | 0.71 |  |  |  | 0.71
TIDEWATER-SOBRANTE | 230 | ETL.5770 |  | ACT | 12.32 | 0.56 | 5.78 |  | 5.98
TIGER CREEK-ELECTRA | 230 | ETL.5780 |  | ACT | 13.68 | 8.58 | 5.1 |  | 0
TIGER CREEK-VALLEY SPRINGS | 230 | ETL.5790 |  | ACT | 24.22 | 8.72 | 12.21 |  | 3.29
TIVY VALLEY-REEDLEY | 70 | ETL.9260 |  | ACT | 12.3 |  |  |  | 12.3
TOCALOMA TAP | 60 | ETL.7721 |  | ACT | 1.03 |  | 1.03 |  | 0
TORNADO TAP | 70 | ETL.8572 |  | ACT | 0.06 |  |  |  | 0.06
TRACY-LOS BANOS | 500 | ETL.6130 |  | ACT | 56.23 |  | 3.57 |  | 52.66
TRANQUILITY SW STA-SCARLET PV | 230 | ETL.1392 |  | ACT | 0.28 |  |  |  | 0.28
TRANQUILLITY SW STA-HELM | 230 | ETL.5370 |  | ACT | 12.68 |  |  |  | 12.68
TRANQUILLITY SW STA-KEARNEY | 230 | ETL.5380 |  | ACT | 36.9 |  |  |  | 36.9
TRANQUILLITY SW STA-OCHO SW STA | 230 | ETL.1452 |  | ACT | 0.03 |  |  |  | 0.03
TRANQUILLITY SW STA-TRANQUILLITY PV | 230 | ETL.1454 |  | ACT | 0.03 |  |  |  | 0.03
TRAVIS TAP | 60 | ETL.6731 |  | ACT | 2.88 |  |  |  | 2.88
TRIMBLE-SAN JOSE B | 115 | ETL.4030 |  | ACT | 2.54 |  |  |  | 2.54
TRINIDAD TAP | 60 | ETL.6811 |  | ACT | 1.34 |  |  |  | 1.34
TRINITY-COTTONWOOD | 115 | ETL.4040 |  | ACT | 45.97 | 10.89 | 31.92 |  | 3.16
TRINITY-MAPLE CREEK | 60 | ETL.8170 |  | ACT | 55.48 |  | 54.97 |  | 0.51
TULLOCH TAP | 115 | ETL.1071 |  | ACT | 0.31 |  | 0.28 |  | 0.03
TULUCAY-NAPA #1 | 60 | ETL.8180 |  | ACT | 9.72 |  | 4.99 |  | 4.73
TULUCAY-NAPA #2 | 60 | ETL.8190 |  | ACT | 3.93 |  |  |  | 3.93
TULUCAY-VACA | 230 | ETL.5800 |  | ACT | 23.63 |  | 16.68 |  | 6.95
TUPMAN-NORCO TAP | 115 | ETL.2592 |  | ACT | 6.67 |  |  |  | 6.67
UC DAVIS #1 TAP | 115 | ETL.6670 |  | ACT | 1.59 |  |  |  | 1.59
UC DAVIS #2 TAP | 115 | ETL.6680 |  | ACT | 1.61 |  |  |  | 1.61
UKIAH-HOPLAND-CLOVERDALE | 115 | ETL.4050 |  | ACT | 31.19 | 7.15 | 17.12 |  | 6.92
ULTRA POWER TAP | 60 | ETL.6803 |  | ACT | 1.17 |  |  |  | 1.17
ULTRAPOWER (OGLE) TAP | 115 | ETL.2121 |  | ACT | 2.45 |  |  |  | 2.45
UNION CHEMICAL TAP | 60 | ETL.6351 |  | ACT | 1.04 |  | 0.57 |  | 0.47
UNION OIL TAP | 115 | ETL.4280 |  | ACT | 0.5 |  |  |  | 0.5
UNITED COGEN INC TAP | 115 | ETL.2241 |  | ACT | 0.09 |  |  |  | 0.09
UNITED COGEN INC TAP | 115 | ETL.2241 |  | IDL | 0.59 |  |  |  | 0.59
UNIVERSITY COGEN TAP | 115 | ETL.3941 |  | ACT | 0.22 |  |  |  | 0.22
URICH TAP | 60 | ETL.6373 |  | ACT | 0.21 |  |  |  | 0.21
US WINDPOWER #3 TAP | 230 | ETL.4521 |  | ACT | 0.06 | 0.06 |  |  | 0
US WINDPOWER TAP | 60 | ETL.8261 |  | ACT | 1.52 |  |  |  | 1.52
VACA DIXON-MORAGA #1 | 230 | ETL.5935 |  | IDL | 3.08 |  |  |  | 3.08
VACA-BAHIA | 230 | ETL.5810 |  | ACT | 33.9 |  | 13.53 |  | 20.37
VACA-LAKEVILLE #1 | 230 | ETL.5840 |  | ACT | 40.93 |  | 18.48 |  | 22.45
VACA-LAMBIE SW STA | 230 | ETL.5845 |  | ACT | 13.95 |  |  |  | 13.95
VACA-PARKWAY | 230 | ETL.5850 |  | ACT | 27.76 |  | 13.55 |  | 14.21
VACA-PEABODY | 230 | ETL.5821 |  | ACT | 9.69 |  |  |  | 9.69
VACA-PLAINFIELD | 60 | ETL.8200 |  | ACT | 29.83 |  |  |  | 29.83
VACA-SUISUN | 115 | ETL.4070 |  | ACT | 22.92 |  | 8.05 |  | 14.87
VACA-SUISUN | 115 | ETL.4070 |  | IDL | 0.19 |  |  |  | 0.19
VACA-SUISUN-JAMESON | 115 | ETL.4080 |  | ACT | 25.46 |  | 8.05 |  | 17.41
VACA-TESLA | 500 | ETL.6140 |  | ACT | 57 |  |  |  | 57
VACA-VACAVILLE-CORDELIA | 115 | ETL.4090 |  | ACT | 22.04 |  | 8.06 |  | 13.98
VACA-VACAVILLE-JAMESON-NORTH TOWER | 115 | ETL.4100 |  | ACT | 36.2 |  | 8.05 |  | 28.15
VALLEY CHILDRENS HOSPITAL TAP | 115 | ETL.2142 |  | ACT | 0.03 |  |  |  | 0.03
VALLEY SPRINGS #1 | 60 | ETL.8210 |  | ACT | 27.27 |  | 10.37 |  | 16.9
VALLEY SPRINGS #2 | 60 | ETL.9460 |  | ACT | 25.65 |  | 9.31 |  | 16.34
VALLEY SPRINGS-BELLOTA | 230 | ETL.5860 |  | ACT | 20.67 |  | 5.41 |  | 15.26
VALLEY SPRINGS-CALAVERAS CEMENT | 60 | ETL.8220 |  | ACT | 7.91 |  | 7.6 |  | 0.31
VALLEY SPRINGS-CLAY | 60 | ETL.8264 |  | ACT | 17.31 |  | 10.9 | 0 | 6.41
VALLEY SPRINGS-MARTELL #1 | 60 | ETL.8240 |  | ACT | 12.75 |  | 7.33 |  | 5.42
VALLEY VIEW #1 TAP | 115 | ETL.3151 |  | ACT | 0.96 |  | 0.01 |  | 0.95
VALLEY VIEW #2 TAP | 115 | ETL.3161 |  | ACT | 0.97 |  | 0.01 |  | 0.96
VASCO-HERDLYN | 60 | ETL.8260 |  | ACT | 10.91 |  |  |  | 10.91
VASONA-METCALF | 230 | ETL.5932 |  | ACT | 13.29 |  | 3.38 | 0.01 | 9.9
VEDDER TAP | 115 | ETL.2141 |  | ACT | 11.09 |  | 4.84 |  | 6.25
VICTOR TAP | 60 | ETL.7442 |  | ACT | 0.04 |  |  |  | 0.04
VIEJO-MONTEREY | 60 | ETL.8270 |  | ACT | 2.28 |  | 0.63 |  | 1.65
VIERRA-TRACY-KASSON | 115 | ETL.4310 |  | ACT | 10.49 |  |  |  | 10.49
VINEYARD-NEWARK | 230 | ETL.4536 |  | ACT | 14.36 |  | 2.79 | 0.5 | 11.07
VOLTA-DESCHUTES | 60 | ETL.8290 |  | ACT | 20.85 | 7.58 | 12.52 |  | 0.75
VOLTA-SOUTH | 60 | ETL.8300 |  | ACT | 4.86 | 0.98 | 3.88 |  | 0
WADHAM TAP | 60 | ETL.6601 |  | ACT | 1.68 |  |  |  | 1.68
WARNERVILLE-WILSON | 230 | ETL.5870 |  | ACT | 38.41 |  |  |  | 38.41
WASCO PRISON TAP | 115 | ETL.3641 |  | ACT | 0.54 |  |  |  | 0.54
WASCO-FAMOSO | 70 | ETL.9241 |  | ACT | 7.13 |  |  |  | 7.13
WASHOE TAP | 60 | ETL.6911 |  | ACT | 1.04 |  | 1.04 |  | 0
WATERSHED TAP | 60 | ETL.7191 |  | ACT | 0.28 |  |  |  | 0.28
WATSONVILLE-SALINAS | 60 | ETL.8310 |  | ACT | 28.39 |  | 8.23 |  | 20.16
WAUKENA SW STA-CORCORAN | 115 | ETL.8773 |  | ACT | 2.39 |  |  |  | 2.39
WEBER-CASCADE ENERGY STORAGE | 60 | ETL.1363 |  | ACT | 0.04 |  |  |  | 0.04
WEBER-FRENCH CAMP #1 | 60 | ETL.8320 |  | ACT | 6.05 |  |  |  | 6.05
WEBER-FRENCH CAMP #2 | 60 | ETL.8321 |  | ACT | 10.89 |  |  |  | 10.89
WEBER-MORMON JCT | 60 | ETL.8330 |  | ACT | 17.67 |  |  |  | 17.67
WEBER-TESLA | 230 | ETL.5880 |  | ACT | 23.71 |  |  |  | 23.71
WEEDPATCH-SAN BERNARD | 70 | ETL.9270 |  | ACT | 9.26 |  |  |  | 9.26
WEEDPATCH-WELLFIELD | 70 | ETL.9280 |  | ACT | 5.88 |  |  |  | 5.88
WEIMAR #1 | 60 | ETL.7560 |  | ACT | 13.99 | 9.89 | 4.09 |  | 0.01
WEIMAR-HALSEY | 60 | ETL.8340 |  | ACT | 6.28 |  | 6.28 |  | 0
WESIX TAP | 70 | ETL.8984 |  | ACT | 2.49 |  |  |  | 2.49
WEST FRESNO-CALIFORNIA AVE | 115 | ETL.2361 |  | ACT | 4.85 |  |  |  | 4.85
WEST POINT-VALLEY SPRINGS | 60 | ETL.8350 |  | ACT | 21.66 | 5.44 | 12.12 |  | 4.1
WEST SAC COM TOWERS | 60 | ETL.5570 |  | ACT | 0.02 |  |  |  | 0.02
WEST SACRAMENTO-BRIGHTON | 115 | ETL.4110 |  | ACT | 13.97 |  |  |  | 13.97
WEST SACRAMENTO-DAVIS | 115 | ETL.4120 |  | ACT | 12.14 |  |  |  | 12.14
WESTINGHOUSE TAP | 60 | ETL.6561 |  | ACT | 8.01 |  |  |  | 8.01
WESTINGHOUSE TAP | 60 | ETL.6561 |  | IDL | 0.07 |  |  |  | 0.07
WESTLANDS #1 RA PUMPING PLANT TAP | 115 | ETL.3242 |  | ACT | 1.05 |  |  |  | 1.05
WESTLANDS #18 RA TAP | 115 | ETL.3252 |  | ACT | 3.52 |  |  |  | 3.52
WESTLANDS TAP | 70 | ETL.8983 |  | ACT | 1.07 |  |  |  | 1.07
WESTPARK-COLUMBUS | 115 | ETL.4130 |  | ACT | 8.59 |  |  |  | 8.59
WHEELER RIDGE - SANDRINI PV | 230 | ETL.1407 |  | ACT | 0.35 |  |  |  | 0.35
WHEELER RIDGE PUMPING PLANT #1 TAP | 230 | ETL.5192 |  | ACT | 0.25 |  |  |  | 0.25
WHEELER RIDGE PUMPING PLANT #2 TAP | 230 | ETL.5202 |  | ACT | 0.23 |  |  |  | 0.23
WHEELER RIDGE-ADOBE SW STA | 115 | ETL.1982 |  | ACT | 1.34 |  |  |  | 1.34
WHEELER RIDGE-LAKEVIEW | 70 | ETL.9290 |  | ACT | 7.51 |  |  |  | 7.51
WHEELER RIDGE-SAN BERNARD | 70 | ETL.9300 |  | ACT | 5.88 |  |  |  | 5.88
WHEELER RIDGE-TEJON | 70 | ETL.9310 |  | ACT | 5.01 |  |  |  | 5.01
WHEELER RIDGE-WEEDPATCH | 70 | ETL.9320 |  | ACT | 22.44 |  |  |  | 22.44
WHISMAN-MONTA VISTA | 115 | ETL.1010 |  | ACT | 5.97 |  |  |  | 5.97
WILLOW PASS-CONTRA COSTA | 60 | ETL.8370 |  | ACT | 10.83 |  |  |  | 10.83
WILSON-ATWATER #2 | 115 | ETL.4160 |  | ACT | 15.41 |  |  |  | 15.41
WILSON-BORDEN #1 | 230 | ETL.5890 |  | ACT | 35.31 |  |  |  | 35.31
WILSON-BORDEN #2 | 230 | ETL.9001 |  | ACT | 35.37 |  |  |  | 35.37
WILSON-DAIRYLAND (12KV) | 115 | ETL.1284 |  | IDL | 5.12 |  |  |  | 5.12
WILSON-LE GRAND | 115 | ETL.4170 |  | ACT | 14.11 |  |  |  | 14.11
WILSON-MERCED #1 | 115 | ETL.4180 |  | ACT | 5.58 |  |  |  | 5.58
WILSON-MERCED #2 | 115 | ETL.4190 |  | ACT | 6.2 |  |  |  | 6.2
WILSON-ORO LOMA | 115 | ETL.4200 |  | ACT | 40.73 |  |  |  | 40.73
WIND FARMS | 60 | ETL.8380 |  | ACT | 3.75 |  |  |  | 3.75
WIND GAP PUMPING PLANT #1 TAP | 230 | ETL.5193 |  | ACT | 1.64 |  |  |  | 1.64
WIND GAP PUMPING PLANT #2 TAP | 230 | ETL.5203 |  | ACT | 1.63 |  |  |  | 1.63
WINDMASTER TAP | 230 | ETL.4491 |  | ACT | 0.11 |  |  |  | 0.11
WINDSOR-FITCH MOUNTAIN | 60 | ETL.6900 |  | ACT | 13.11 |  | 2.49 |  | 10.62
WINTU TAP | 60 | ETL.6311 |  | ACT | 1.85 |  | 0.45 |  | 1.4
WISHON-COPPERMINE | 70 | ETL.9330 |  | ACT | 19.99 | 0.11 | 14 |  | 5.88
WISHON-SAN JOAQUIN #3 | 70 | ETL.9340 |  | ACT | 7.67 | 4.89 | 2.78 |  | 0
WITCO (REFINERY) TAP | 115 | ETL.1972 |  | ACT | 0.03 |  |  |  | 0.03
WOHLER TAP | 60 | ETL.7631 |  | ACT | 1.44 |  |  |  | 1.44
WOODBRIDGE TAP | 60 | ETL.7443 |  | ACT | 0.53 |  |  |  | 0.53
WOODLAND BIOMASS TAP | 115 | ETL.4211 |  | ACT | 0.87 |  |  |  | 0.87
WOODLAND-DAVIS | 115 | ETL.4210 |  | ACT | 11.75 |  |  |  | 11.75
WOODLEAF-PALERMO | 115 | ETL.4220 |  | ACT | 19.62 | 6.53 | 11.1 |  | 1.99
WOODWARD-SHEPHERD | 115 | ETL.1895 |  | ACT | 4.84 |  |  |  | 4.84
WRIGHT TAP | 70 | ETL.8931 |  | ACT | 1.18 |  |  |  | 1.18
YUBA CITY COGEN TAP | 60 | ETL.7729 |  | ACT | 0.8 |  |  |  | 0.8
ZAMORA TAP | 115 | ETL.3471 |  | ACT | 1.92 |  |  |  | 1.92
ZANKER #1 TAP | 115 | ETL.3121 |  | ACT | 0.59 |  |  |  | 0.59
ZANKER #2 TAP | 115 | ETL.3041 |  | ACT | 0.73 |  |  |  | 0.73
ZOND WIND TAP | 60 | ETL.8381 |  | ACT | 1.19 |  |  |  | 1.19
ZAMORA TAP | 115 | ETL.3471 |  | ACT | 1.92 |  |  |  | 1.92
ZANKER #1 TAP | 115 | ETL.3121 |  | ACT | 0.59 |  |  |  | 0.59
ZANKER #2 TAP | 115 | ETL.3041 |  | ACT | 0.73 |  |  |  | 0.73
ZOND WIND TAP | 60 | ETL.8381 |  | ACT | 1.19 |  |  |  | 1.19