## ET-WD Details
kV Cls | kV | SAP FL | LINE NO | FACILITY NAME | YEAR | Date Out | Time Out | MED | ET Wire Down | Auto Reclose Disabled | Durn (hr:min) | Durn (mins) | Date In | Time In | Out Cls | Cause Category | Cause Detail | Secondary Cause | Comments | CAP | REGION | TOTL | Customers Affected | CESO Event | CMIN Event | SAIFI Contr | SAIDI Contr | CAIDI | System Customer Count | Fault Type | Fault Estimate | AUTO EFO SCHD | Outage Mode | HFTD | County | Division | LAT | LONG | Actual Location | Weather | Conductor | ETGIS Location | BS GS SD
69 | 70 | ETL.9360 | 70096 | CORCORAN-GUERNSEY | 2025 | 2025-01-07 02:31 | 45664.1049 | No | YES | No | 0.88472 | 1274 | 2025-01-07 23:45 | 45664.9896 | F | External Contact | Ext Cont-car pole | STRU |  | NONE | CENTRAL VALLEY | INT-18892 | 0 | 0 | 0 | 0 | 0 | 0 | 5795693 | B-C-G | 008/012 | AUTO | Single Mode | Non-HFTD | Kings | Fresno | 36.166 | -119.6458 | Corcoran-Guernsey 70kV line STR 008/014 | Clear | 266.8 AAC | Lat: 36.165963, Long: -119.64584 | SD
69 | 60 | ETL.7860 | 60434 | CROW CREEK SW STA-NEWMAN | 2025 | 2025-01-10 23:42 | 45667.9875 | No | YES | No | 0.53611 | 772 | 2025-01-11 12:34 | 45668.5236 | F | External Contact | Ext Cont-car pole | STRU |  | NONE | CENTRAL VALLEY | INT-18895-4 | 4739 | 4739 | 145240 | 0.00081768 | 0.02506 | 31 | 5795693 | C-A | 013/006 | AUTO | Dependent Mode Initiating | Non-HFTD | Stanislaus | Yosemite | 37.3331 | -121.0288 | Crow Creek SW STA-Newman 60kV line STR 12/15 | Clear | 266.8 AAC | Lat: 37.333068, Long: -121.028771 | BS
69 | 70 | ETL.8970 | 70115 | COPUS-OLD RIVER | 2025 | 2025-01-16 12:44 | 45673.5306 | No | YES | No | 0.15486 | 223 | 2025-01-16 16:27 | 45673.6854 | F | Equipment Failure | Equip Fail-conductor | COND |  | 130749646 | CENTRAL VALLEY | INT-18904 | 220 | 220 | 16564 | 3.7959e-05 | 0.002858 | 75 | 5795693 | A-G | 018/303 | AUTO | Single Mode | Non-HFTD | Kern | Kern | 35.1101 | -119.1095 | Copus-Old River 70kV line STR 018/298 | Clear | 3/0 AAC | Lat: 35.110108, Long: -119.109513 | BS
69 | 60 | ETL.6560 | 60048 | COOLEY LANDING-LOS ALTOS | 2025 | 2025-01-18 18:07 | 45675.7549 | No | YES | No | 1900-01-02 18:27 | 5427 | 2025-01-22 12:34 | 45679.5236 | C | Equipment Failure | Equip Fail-conductor | COND |  | 130774864 | SOUTH BAY AND CENTRAL COAST | INT-18910 | 0 | 0 | 0 | 0 | 0 | 0 | 5795693 | A-B | 004/033 | AUTO | Single Mode | Non-HFTD | Santa Clara | De Anza | 37.4417 | -122.0731 | Cooley Landing-Los Altos 60kV line STR 004/032 | Clear | 4/0 CU | Lat: 37.441718, Long: -122.073088 | BS
69 | 70 | ETL.8670 | 70122 | JAYNE SW STA-COALINGA #1 | 2025 | 2025-01-22 05:30 | 45679.2292 | No | YES | No | 0.62083 | 894 | 2025-01-22 20:24 | 45679.85 | F | External Contact | Ext Cont-car pole | STRU |  | NONE | CENTRAL VALLEY | INT-18912 | 0 | 0 | 0 | 0 | 0 | 0 | 5795693 | C-A-G | 007/004 | AUTO | Single Mode | Non-HFTD | Fresno | Fresno | 36.137 | -120.2517 | Jayne SW STA-Coalinga #1-70kV line STR 007/001 | Clear | 336.4 AAC | Lat: 36.137005, Long: -120.251658 | GS
69 | 70 | ETL.9260 | 70086 | TIVY VALLEY-REEDLEY | 2025 | 2025-01-25 00:55 | 45682.0382 | No | YES | No | 0.30625 | 441 | 2025-01-25 08:16 | 45682.3444 | F | Equipment Failure | Equip Fail-conductor | COND |  | NONE | CENTRAL VALLEY | INT-18917 | 0 | 0 | 0 | 0 | 0 | 0 | 5795693 | C-G | 035/005 | AUTO | Single Mode | Non-HFTD | Fresno | Fresno | 36.6239 | -119.3765 | Tivy Valley-Reedley 70kV STR 035/003 | Clear | 397.5 AAC | Lat: 36.623947, Long: -119.376526 | GS
69 | 60 | ETL.6310 | 60019 | CASCADE-BENTON-DESCHUTES | 2025 | 2025-01-25 10:27 | 45682.4354 | No | YES | No | 0.34792 | 501 | 2025-01-25 18:48 | 45682.7833 | F | Equipment Failure | Equip Fail-conductor | COND |  | NONE | NORTH VALLEY AND SIERRA | INT-18919 | 276 | 876 | 104754 | 0.00015115 | 0.018074 | 120 | 5795693 | C | Could not determine | AUTO | Single Mode | Non-HFTD | Shasta | North Valey | 40.5636 | -122.353 | Cascade-Benton-Deschutes 60kV line STR 009/195 | Clear | 4/0 AAC | Lat: 40.563605, Long: -122.352997 | GS
69 | 60 | ETL.8060 | 60206 | SPAULDING-SUMMIT | 2025 | 2025-02-04 11:26 | 45692.4764 | No | YES | No | 0.21736 | 313 | 2025-02-04 16:39 | 45692.6937 | F | Weather | Weather-snow/ ice | COND |  | NONE | NORTH VALLEY AND SIERRA | INT-18939 | 2008 | 2008 | 659034 | 0.00034646 | 0.11371 | 652 | 5795693 | B-C | 000/007 | AUTO | Single Mode | Tier 2 | Nevada | Sierra | 39.3247 | -120.642 | Cisco Grove 60kV Tap STR 000/007 | Storm | 2 ACSR | Lat: 39.324652, Long: -120.64203 | SD
69 | 60 | ETL.6760 | 60070 | DRUM-GRASS VALLEY-WEIMAR | 2025 | 2025-02-06 23:02 | 45694.9597 | No | YES | No | 0.79653 | 1147 | 2025-02-07 18:09 | 45695.7562 | F | Tree | Tree-failure | COND |  | NONE | NORTH VALLEY AND SIERRA | INT-18950-1 | 3609 | 3609 | 68571 | 0.0006227 | 0.011831 | 38 | 5795693 |  | B023/521 | AUTO | Dependent Mode Initiating | Tier 3 | Nevada | Sierra | 39.1912 | -121.0121 | Drum-Grass Valley-Weimar 60kV line STR B022/492 | Rain | 2/0 CU | Lat: 39.191189, Long: -121.012128 | SD
69 | 70 | ETL.8500 | 70008 | BORDEN-COPPERMINE | 2025 | 2025-02-08 01:41 | 45696.0701 | No | YES | No | 0.22639 | 326 | 2025-02-08 07:07 | 45696.2965 | F | Equipment Failure | Equip Fail-conductor | COND |  | 130834460 | CENTRAL VALLEY | T25-004757 | 6003 | 6003 | 258129 | 0.0010358 | 0.044538 | 43 | 5795693 | A-G | 016/007 | AUTO | Single Mode | Non-HFTD | Madera | Yosemite | 36.923 | -119.9581 | Borden-Coppermine 70kV line STR :018/004 | Clear | 397.5 AAC | Lat: 36.923008, Long: -119.95806 | BS
69 | 60 | ETL.7460 | 60141 | MANTECA #1 | 2025 | 2025-02-12 21:55 | 45700.9132 | No | YES | No | 0.56806 | 818 | 2025-02-13 11:33 | 45701.4812 | F | Equipment Failure | Equip Fail-conductor | COND |  | NONE | CENTRAL VALLEY | INT-18957-1 | 1736 | 1736 | 31248 | 0.00029953 | 0.0053916 | 18 | 5795693 | B-C | 006/098 | AUTO | Single Mode | Non-HFTD | San Joaquin | Stockton | 37.7523 | -121.2913 | Manteca #1-60kV line STR 6/108 | Rain | 1/0 AAC | Lat: 37.75235, Long: -121.291274 | GS
69 | 60 | ETL.2060 | 60389 | FORT BRAGG-ELK | 2025 | 2025-02-13 13:39 | 45701.5687 | No | YES | No | 1899-12-31 02:07 | 1567 | 2025-02-14 15:46 | 45702.6569 | F | Tree | Tree-failure | COND |  | NONE | NORTH COAST | INT-18969 | 2605 | 0 | 0 | 0 | 0 | 0 | 5795693 | C-A-G | 006/007 | AUTO | Single Mode | Tier 2 | Mendocino | Humboldt | 39.2162 | -123.7565 | Fort Bragg-Elk 60kV line STR 007/000 | Storm | 397.5 AAC | Lat: 39.216188, Long: -123.756478 | SD
69 | 60 | ETL.6380 | 60420 | KONOCTI-MIDDLETOWN | 2025 | 2025-03-06 17:56 | 45722.7472 | No | YES | No | 0.79444 | 1144 | 2025-03-07 13:00 | 45723.5417 | F | Tree | Tree-3rd party | COND |  | NONE | NORTH COAST | INT-19037 | 2581 | 0 | 0 | 0 | 0 | 0 | 5795693 | B-C | 027/004 | AUTO | Single Mode | Tier 2 | Lake | Humboldt | 38.9063 | -122.6609 | Konocti-Middletown 60kV line STR 027/003 | Clear | 4/0 AAC | Lat: 38.906296, Long: -122.660853 | GS
69 | 60 | ETL.7820 | 60181 | POTTER VALLEY-WILLITS | 2025 | 2025-03-14 05:52 | 45730.2444 | No | YES | No | 0.47292 | 681 | 2025-03-14 17:13 | 45730.7174 | F | Tree | Tree-failure | COND |  | NONE | NORTH COAST | INT-19067 | 0 | 0 | 0 | 0 | 0 | 0 | 5795693 | B-C | 008/009 | AUTO | Single Mode | Tier 3 | Mendocino | Humboldt | 39.3737 | -123.2767 | Potter Valley-Willits 60kV line STR 009/002 | Storm | 1/0 ACSR | Lat: 39.373653, Long: -123.276743 | SD
69 | 60 | ETL.8270 | 60227 | VIEJO-MONTEREY | 2025 | 2025-03-17 14:25 | 45733.6007 | No | YES | No | 1899-12-31 00:39 | 1479 | 2025-03-18 15:04 | 45734.6278 | F | Tree | Tree-failure | COND |  | NONE | SOUTH BAY AND CENTRAL COAST | INT-19077 | 0 | 0 | 0 | 0 | 0 | 0 | 5795693 | A-B-C | 000/013 | AUTO | Single Mode | Tier 2 | Monterey | Central Coast | 36.5806 | -121.9017 | Viejo-Monterey 60kV line STR 000/011 | Storm | 715.5 AAC | Lat: 36.58055, Long: -121.901742 | SD
69 | 60 | ETL.6150 | 60001 | ALMENDRA JCT-NICOLAUS | 2025 | 2025-03-31 19:02 | 45747.7931 | No | YES | No | 0.36319 | 523 | 2025-04-01 03:45 | 45748.1562 | F | Equipment Failure | Equip Fail-conductor | COND |  | NONE | NORTH VALLEY AND SIERRA | T25-007614 | 1728 | 1444 | 264419 | 0.00024915 | 0.045623 | 363 | 5795693 | N/A | N/A | EFO | Emergency Forced Outage | Non-HFTD | Sutter | Sierra | 38.9313 | -121.6064 | Almendra JCT-Nicolaus 60kV line STR 19/404 | Rain | 2/0 CU | Lat: 38.931337, Long: -121.606432 | GS
230 | 230 | ETL.9001 | 20203 | WILSON-BORDEN | 2025 | 2025-04-02 06:01 | 45749.2507 | No | YES | No | 0.45 | 648 | 2025-04-02 16:49 | 45749.7007 | F | External Contact | Ext Cont-vandalism | COND |  | NONE | CENTRAL VALLEY | T25-007668 | 2952 | 2952 | 185976 | 0.00050934 | 0.032089 | 63 | 5795693 | B-G | 093/609 | AUTO | Dependent Mode Initiating | Non-HFTD | Madera | Yosemite | 36.9583 | -120.0124 | Wilson-Borden #2-230kV line STR 93/612 | Clear | 500 HOLO-CU | Lat: 36.958305, Long: -120.012413 | GS
69 | 70 | ETL.8670 | 70122 | JAYNE SW STA-COALINGA #1 | 2025 | 2025-05-01 16:06 | 45778.6708 | No | YES | No | 0.89792 | 1293 | 2025-05-02 13:39 | 45779.5687 | F | External Contact | Ext Cont-car pole | STRU |  | NONE | CENTRAL VALLEY | INT-19159 | 0 | 0 | 0 | 0 | 0 | 0 | 5795693 | A-B-C | 001/014 | AUTO | Single Mode | Non-HFTD | Fresno | Fresno | 36.1354 | -120.1573 | Jayne SW STA Coalinga #1-70kV line STR 001/015 | Clear | 336.4 AAC | Lat: 36.135447, Long: -120.157263 | BS
69 | 70 | ETL.8440 | 70002 | ARCO-CHOLAME | 2025 | 2025-05-02 03:39 | 45779.1521 | No | YES | YES | 0.54514 | 785 | 2025-05-02 16:44 | 45779.6972 | F | Equipment Failure | Equip Fail-conductor | COND |  | NONE | CENTRAL VALLEY | INT-19162 | 1795 | 1795 | 921489 | 0.00030971 | 0.159 | 1783 | 5795693 | B-G | 014/140 | AUTO | Single Mode | Tier 2 | Kern | Kern | 35.7084 | -120.164 | Arco-Cholame 70kV line (EPSS) STR 16/161 | Clear | 3/0 AAC | Lat: 35.708367, Long: -120.163965 | BS
69 | 60 | ETL.7920 | 60191 | SALINAS-LAGUNITAS | 2025 | 2025-05-07 15:08 | 45784.6306 | No | YES | YES | 1900-01-14 23:22 | 23002 | 2025-05-23 14:30 | 45800.6042 | C | External Contact | Ext Cont-car pole | STRU |  | NONE | SOUTH BAY AND CENTRAL COAST | INT-19175-1 | 14809 | 14809 | 3110331 | 0.0025552 | 0.53666 | 210 | 5795693 | B-G | 001/044 | AUTO | Dependent Mode Initiating | Non-HFTD | Monterey | Central Coast | 36.7069 | -121.6278 | Salinas-Lagunitas 60kV line STR 2/49 | Clear | 1/0 CU | Lat: 36.70694, Long: -121.627817 | BS
69 | 60 | ETL.7000 | 60095 | HAMILTON BRANCH-CHESTER | 2025 | 2025-05-11 13:56 | 45788.5806 | No | YES | YES | 0.71736 | 1033 | 2025-05-12 07:09 | 45789.2979 | F | Tree | Tree-failure | STRU |  | NONE | NORTH VALLEY AND SIERRA | INT-19181 | 1669 | 1669 | 1803193 | 0.00028797 | 0.31113 | 1080 | 5795693 | C-A | 009/195 | AUTO | Single Mode | Non-HFTD | Plumas | North Valley | 40.3039 | -121.2233 | Hamilton Branch-Chester 60kV line (EPSS) (HFRA) STR 011/245 | Clear | 397.5 ACSR | Lat: 40.303877, Long: -121.223338 | BS
115 | 115 | ETL.temp | 10550 | TESLA-VIERRA | 2025 | 2025-05-22 14:40 | 45799.6111 | No | YES | No | 1900-01-01 20:49 | 4129 | 2025-05-25 11:29 | 45802.4785 | F | Equipment Failure | Equip Fail-structure-line | STRU |  | NONE | CENTRAL VALLEY | INT-19197-1 | 0 | 0 | 0 | 0 | 0 | 0 | 5795693 | B-G | 000/001 | AUTO | Dependent Mode Initiating | Non-HFTD | Alameda | Mission | 37.7166 | -121.567 | Tesla-Vierra 115kV line relayed and tested NG. On the trouble Vierra-Tesla Motors 115kV line and Vierra 115kV Bus #1 de-energized | Clear | 1113 AAC | Lat: 37.71662, Long: -121.56699 | GS
115 | 115 | ETL.2170 | 10143 | MADISON-VACA | 2025 | 2025-06-14 17:10 | 45822.7153 | No | YES | YES | 0.27153 | 391 | 2025-06-14 23:41 | 45822.9868 | F | External Contact | Ext Cont-car pole | STRU |  | None | NORTH VALLEY AND SIERRA | INT-19243 | 4110 | 4110 | 622362 | 0.00070915 | 0.10738 | 151 | 5795693 | C-G | 038/238 | AUTO | Common Mode | Non-HFTD | Yolo | Sacramento | 38.6059 | -121.9791 | Madison-Vaca 115kV line (HFRA) STR 005/062 | Clear | 3/0 CU | Lat: 38.605935, Long: -121.979146 | BS
115 | 115 | ETL.3470 | 10281 | RIO OSO-WOODLAND #2 | 2025 | 2025-06-14 17:10 | 45822.7153 | No | YES | YES | 1899-12-31 05:49 | 1789 | 2025-06-15 22:59 | 45823.9576 | F | External Contact | Ext Cont-car pole | STRU |  | None | NORTH VALLEY AND SIERRA | INT-19244 | 1328 | 1328 | 164672 | 0.00022914 | 0.028413 | 124 | 5795693 | A-G | 003/052 | AUTO | Common Mode | Non-HFTD | Yolo | Sacramento | 38.6059 | -121.9791 | Rio Oso-Woodland #2-115kv line STR 005/062 | Clear | 715.5 AAC | Lat: 38.605935, Long: -121.979146 | BS
*Note: data puled from the Transmission Outage Database on July 16, 2025

## 3.6 WD RFW HFTD
County | inRFW | datetime | NWS_FireZone | RFW_ISSUED_local | RFW_EXPIRED_local
Tehama | 1 | 2017-10-08 13:11 | CAZ215 | 2017-10-08 11:00 | 2017-10-09 17:00
Sonoma | 1 | 2017-10-08 23:15 | CAZ507 | 2017-10-08 11:00 | 2017-10-10 05:00
Sonoma | 1 | 2017-10-09 02:01 | CAZ506 | 2017-10-08 11:00 | 2017-10-10 05:00
Marin | 1 | 2020-08-17 09:56 | CAZ505 | 2020-08-15 23:00 | 2020-08-17 11:00
Metric 3.6
Wire Down Events in HFTD on Red Flag Warning Days
[6 empty] | Year | WD Events | RFW OH CKT Mile-Days | WD / CKT Mile-Days
[6 empty] | 2013 | 0 | 24219.8893 | 0
[6 empty] | 2014 | 0 | 22115.1095 | 0
[6 empty] | 2015 | 0 | 8576.4054 | 0
[6 empty] | 2016 | 0 | 17315.6816 | 0
[6 empty] | 2017 | 3 | 55361.8287 | 5.4189e-05
[6 empty] | 2018 | 0 | 44290.6168 | 0
[6 empty] | 2019 | 0 | 36237.9327 | 0
[6 empty] | 2020 | 1 | 60675.43 | 1.6481e-05
[6 empty] | 2021 | 0 | 27334.9208 | 0
[6 empty] | 2022 | 0 | 13337 | 0
[6 empty] | 2023 | 0 | 9979.98 | 0
[6 empty] | 2024 | 0 | 22686 | 0
[6 empty] | 2025 | 0 | 2821.36 | 0
¹ 2022 RFW OH CKT Mile-Days was corrected from 16,578 in our March filing to 13,337 in our September 2023 filing. This correction only impacted the data file. It did not impact the narrative. The performance result was not impacted with this correction. It remains zero.
SOMs 3.6 | 0
¹

## RFW OH CKT Mile-Days
| 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025
| OH Tx | OH Tx | OH Tx | OH Tx | OH Tx | OH Tx | OH Tx | OH Tx | OH Tx | OH Tx | OH Tx | OH Tx | OH Tx
Tier2 | 16860.5621 | 16274.942 | 6818.5806 | 13218.3469 | 38017.0768 | 32991.4315 | 26812.6387 | 44686.1 | 22903.3895 | 11071.1 | 7435.97 | 16757 | 2576.35
Tier3 | 7359.3272 | 5840.1675 | 1757.8248 | 4097.3346 | 17344.7519 | 11299.1853 | 9425.294 | 15989.33 | 4431.5313 | 2265.9 | 2544.01 | 5929 | 245.01
TOTAL | 24219.8893 | 22115.1095 | 8576.4054 | 17315.6816 | 55361.8287 | 44290.6168 | 36237.9327 | 60675.43 | 27334.9208 | 13337 | 9979.98 | 22686 | 2821.36

## Cause Translation
PG&E Outage Cause Category-Details | ISO Outage Primary Cause Code | ISO Outage Primary Cause Code Description | PG&E and ISO Outage Secondary Cause Code | ISO Outage Secondary Cause Code Description |  | Cause Category (10 categories) | Cause Details | Outage Mode
Animal-bird | ANIM | Animal Contact | ARRS | Arrestor | 1 | Animal | Animal-bird | Common Mode
Animal-ground | ANIM | Animal Contact | AUX | Station auxiliary equip (e.g., CT, PT, CCVT) | 2 | Contamination | Animal-ground | Common Mode-initiating
Contamination-agriculture | CNTM | Contamination | BATT | Battery system | 3 | Disaster | Cntmn-agriculture | Dependent Mode
Contamination-animal waste | CNTM | Contamination | BUSH | Bushing | 4 | Equipment Failure | Cntmn-animal waste | Dependent Mode-initiating
Contamination-environmental | CNTM | Contamination | CB | Circuit breaker/Circuit switch | 5 | External Contact | Cntmn-environmental | Emergency Forced Outage
Contamination-industrial waste | CNTM | Contamination | COMM | Communication facility (no relay) | 6 | Other | Cntmn-industrial waste | Scheduled Outage
Disaster-earthquake | ND | Natural Disaster | COND | Conductor/shield wire/splice | 7 | Tree | Disaster-earthquake | Single Mode
Disaster-fire | FIRE | Fire | DISC | Disconnect | 8 | Unknown | Disaster-fire
Disaster-flood | ND | Natural Disaster | ENCR | Encroachment | 9 | Weather | Disaster-flood
Disaster-other | ND | Natural Disaster | GUYS | Guy/anchor | 10 | Work Procedure Error | Disaster-other
Equipment Failure-arrestor | SEQP | Substation Equipment Problem | HDWR | Hardware, fittings, accessories |  |  | Equip Fail-arrestor
Equipment Failure-bus | SEQP | Substation Equipment Problem | INSL | Insulator (station/line) |  |  | Equip Fail-bus
Equipment Failure-bushing | SEQP | Substation Equipment Problem | LS | Line switch |  |  | Equip Fail-bushing
Equipment Failure-ccvt | SEQP | Substation Equipment Problem | NONE | None |  |  | Equip Fail-ccvt
Equipment Failure-circuit breaker | CB | Circuit Breaker Trouble | REAC | Reactive device (e.g., capacitors, condenser) |  |  | Equip Fail-circuit breaker
Equipment Failure-conductor | LEQP | Line Equipment Problem | REG | Regulator |  |  | Equip Fail-conductor
Equipment Failure-connector/hardware | LEQP | Line Equipment Problem | RELY | Relay/communicatons for relay |  |  | Equip Fail-connector/ hardware
Equipment Failure-CT | SEQP | Substation Equipment Problem | STRU | Structure/foundation |  |  | Equip Fail-CT
Equipment Failure-insulator-line | LEQP | Line Equipment Problem | XFRM | dre56] |  |  | Equip Fail-insulator-line
Equipment Failure-insulator-station | SEQP | Substation Equipment Problem | UG | Underground transmission component |  |  | Equip Fail-insulator-station
Equipment Failure-other-line | LEQP | Line Equipment Problem | PROC | Work Procedure/Human Error |  |  | Equip Fail-other-line
Equipment Failure-other-station | SEQP | Substation Equipment Problem | PSPS | Public Safety Power Shutoff |  |  | Equip Fail-other-station
Equipment Failure-PT | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-PT
Equipment Failure-reactive equipment | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-reactive equipment
Equipment Failure-regulator/LTC | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-regulator/ LTC
Equipment Failure-relay | PROT | Protection |  |  |  |  | Equip Fail-relay
Equipment Failure-structure-line | LEQP | Line Equipment Problem |  |  |  |  | Equip Fail-structure-line
Equipment Failure-structure-station | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-structure-station
Equipment Failure-switch-line | LEQP | Line Equipment Problem |  |  |  |  | Equip Fail-switch-line
Equipment Failure-switch-station | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-switch-station
Equipment Failure-transformer | SEQP | Substation Equipment Problem |  |  |  |  | Equip Fail-transformer
External Contact-aircraft | AIR | Aircraft |  |  |  |  | Ext Cont-aircraft
External Contact-car pole | VEH | Vehicle Contact |  |  |  |  | Ext Cont-car pole
External Contact-foreign object | OTHR | Other |  |  |  |  | Ext Cont-foreign object
External Contact-system disturbance | DIST | System Disturbance |  |  |  |  | Ext Cont-system disturbance
External Contact-vandalism | OTHR | Other |  |  |  |  | Ext Cont-vandalism
Other-customer/IPP caused | OTHR | Other |  |  |  |  | Other-customer/ IPP caused
Other-distribution caused | UC | Utility Contact |  |  |  |  | Other-distribution caused
Other-generation caused | GEN | Generation Trouble |  |  |  |  | Other-generation caused
Other-overload situation | DIST | System Disturbance |  |  |  |  | Other-load control
Other-safety clearance | OTHR | Other |  |  |  |  | Other-safety clearance
Scheduled-approved | SCHD | Scheduled Outage |  |  |  |  | Other-scheduled-approved
Scheduled-disapproved | LATE | Late Notification |  |  |  |  | Other-scheduled-disapproved
Scheduled-extended | LATE | Late Notification |  |  |  |  | Other-scheduled-extended
Tree-3rd party | OTHR | Other |  |  |  |  | Tree-3rd party
Tree-failure | VEGA | Vegetation |  |  |  |  | Tree-failure
Tree-tree contact | VEGA | Vegetation |  |  |  |  | Tree-tree contact
Unknown-no patrol conducted | UNKN | Unknown |  |  |  |  | Unk-no patrol conducted
Unknown-patrol found nothing | UNKN | Unknown |  |  |  |  | Unk-patrol found nothing
Weather-lightning | LIGT | Lightning |  |  |  |  | Weather-lightning
Weather-rain | WEAT | Weather |  |  |  |  | Weather-rain
Weather-snow/ice | WEAT | Weather |  |  |  |  | Weather-snow/ ice
Weather-wind | WEAT | Weather |  |  |  |  | Weather-wind
Work Procedure-design error | OPER | Operating error |  |  |  |  | Work Procedure-design error
Work Procedure-equipment incorrectly set | OPER | Operating error |  |  |  |  | Work Procedure-equip incorrectly set
Work Procedure-inattention or carelessness | OPER | Operating error |  |  |  |  | Work Procedure-inattention or carelessness
Work Procedure-miscommunications or unclear expectations | OPER | Operating error |  |  |  |  | Work Procedure-miscommunications or unclear expectations
Work Procedure-not following prescribed procedures | OPER | Operating error |  |  |  |  | Work Procedure-not following prescribed procedures
SGS CAUSE CODE CATEGORIES
Description | SGS Category No | Examples
Equipment | 1 | Terminal equipment: breakers, switches, transformers, cap bks, busses, etc. ("inside the fence")
System Protection | 2 | Relay equipment failure, misoperation, incorrect settings or scheme, "over-reaching", communications
Lines | 3 | Failed hardware "outside the fence"; structures, conductors, cable cable hardware, insulators, static wire
Weather, other than lightning | 4 | Severe weather conditions, usually beyond design capabilities of facilities, exclusive of lightning
Lightning Only | 5 | Verified or suspected outages resulting from lightning
Unknown | 6 | Diligent attempts to verify cause were unsuccessful
Vegetation | 7 | Vegetation and trees which directly cause an outage
External | 8 | Causes outside control of ET system (e.g., foreign utilities, customer equip, generation, UF, instability)
Other | 9 | Operating errors, contractors, dig-ins, loggers, birds, animals, public damage, contamination, autos
Excludable Outage, Natural Causes Only | 10 | Major events (extreme), system disturbances associated w/ cascading
Excludable Outage, System Causes Only | 11 | Operational Outage for safety, voltage control or stability, System Disturbances, Unusual Configurations
Human Factors | 12 | WPE/ HPE

## ILIS Causes
Basic Cause Field | Supplemental Cause Field | [13 empty] | Equipment Condition
3rd Party* 00 | Aircraft | Aircraft-Crop Dusting | Contact with High Voltage, 3rd Party | Customer Equipment | Dig In, 3rd Party | Fire, house or bldg | Gun Shot | Kite | Metallic Balloon | Thrown Object | Vandalism | Vehicle | Other | tree - cutting 3rd party | Annealed
Animal* 02 | Bird Found | Other | Squirrel | [11 empty] | Arcing
Company Initiated* 05 | Construction Activity/equip, company | Contact with High Voltage, company | Coordination Failure | Dig in, company | Improper Construction | Insulator washing | Operating error | Other Circuits | Personnel, company | Planned, capital | Planned, customer | Planned, maintenance | Rotating Outage | Return circuit normal | Bent or Twisted
Equipment Failure/Involved* 03 | Electrical Overload | Fire, pole | overhead | Substation | underground | [9 empty] | Blown / exploded
Vegatation* 01 | Other Ground Vegetation | Tree - bark fell into line | Tree - branch fell on line | Tree - cutting PG&E contractor | Tree - fell into line | Tree - grew into line | Tree - palm frond fell into line | [7 empty] | Broken
Unknown 04 | Patrol - Found Nothing | Patrol - Not Conducted | [12 empty] | Broken, wire on ground
(Environmental)External influence * 06 | Earthquake | Fire, forest/grass | Flood/ errosion | Ice or snow | Lightning | water | [8 empty] | Burned Open
Burned / flashed
* These type outages require "Equipment Involved" & "Equipment Condition" field be populated. See available selection below | [14 empty] | Contaminated
Deteriorated
Equipment Involved | Anchor or Guy | Booster | Bus | Bushing | PT/CCVT | CT/PT | Capacitor | Circuit Breaker | Conductor, Overhead | Conductor, Underground | Connector or Splice (OH) | Connector or Splice (UG) | Crossarm, Steel |  | Leaking
See also next tabs | Crossarm, Wood | Customer Equipment | Cutout, Fused, Distribution | Cutout fuse holder | Elbow | Footings, Tower or Pole | Fuse | Insulator | Interrupter | Jumper | Lightning Arrestor | Manhole, primary box | Metering Equipment |  | Malfunctioning
| Other | PGs, Kearneys | Pole - Tower, steel | Pole - Wood | Pothead or Cable Termination | Reactive Equipment | Recloser | Regulator | Regulator, LTC substation | Relay, substation | Riser | Secondary | Sectionalizer |  | Normal
| Service Conductor | Splice Box | Stepdown | Street Light Equipment | Switch | Transformer | Transformer, Station Bank, Power | Woodpin | Generator | SCADA |  |  |  |  | Together
Equipment Condition | Annealed | Arcing | Bent or Twisted | Blown / exploded | Broken | Broken, wire on ground | Burned Open | Burned / flashed | Contaminated | Deteriorated | Leaking | Malfunctioning | Normal
see also next tabs | On Ground | Together |  |  |  | Broken, wire on object
Outage Level | Distribution Circuit | Substation Distribution | Substation Transmission | Transmission Line | Transformer Only | Generation | secondary | service
[7 empty] | FAS only | FAS only

## 2025 HFTD Miles
TLINE_NAME | RATEDKV | SAP_FL | OWNER_STATUS | STATUS | TLINEMILES | T3MILES | T2MILES | Z1MILES | T1MILES | Exclude Reason |  | 2025 ALL | 2025 Exclude | 2025 Remainder
230KV CAP BANK TIE LINE | 230 | 0 |  | ACT | 0.27 |  |  |  | 0.27 |  | HFTD Miles | 5421.63 | 44.24 | 5377.39
7TH STANDARD-KERN | 115 | ETL.1981 |  | ACT | 6.77 |  |  |  | 6.77
ADOBE SW STA #1 TAP | 115 | ETL.1145 |  | ACT | 14.25 |  |  |  | 14.25
AEC SITE #1 TAP | 115 | ETL.3982 |  | ACT | 1.6 |  |  |  | 1.6
AEC SITE #2 TAP | 115 | ETL.3983 |  | ACT | 2.16 |  |  |  | 2.16
AERA ENERGY TAP | 70 | ETL.7727 |  | ACT | 0.35 |  |  |  | 0.35
AIR PRODUCTS TAP | 115 | ETL.2314 |  | ACT | 0.29 |  |  |  | 0.29
ALMADEN-LOS GATOS | 60 | ETL.6825 |  | ACT | 6.35 |  |  |  | 6.35
ALMENDRA JCT-NICOLAUS | 60 | ETL.6150 |  | ACT | 24.9 |  |  |  | 24.9
AMERIGAS TAP | 115 | ETL.1591 |  | ACT | 0.49 |  |  |  | 0.49
AMES DISTRIBUTION-AMES | 115 | ETL.2482 |  | ACT | 0.1 |  |  |  | 0.1
AMES-MOUNTAIN VIEW | 115 | ETL.1174 |  | ACT | 2.57 |  |  |  | 2.57
AMES-WHISMAN | 115 | ETL.4150 |  | ACT | 0.97 |  |  |  | 0.97
AMFOR TAP | 60 | ETL.8241 |  | ACT | 1.04 |  |  |  | 1.04
ANTELOPE TAP | 70 | ETL.8442 |  | ACT | 4.28 |  |  |  | 4.28
APPLE HILL #1 TAP | 115 | ETL.1531 |  | ACT | 1.42 |  | 1.42 |  | 0
APPLE HILL #2 TAP | 115 | ETL.1541 |  | ACT | 1.43 |  | 1.43 |  | 0
APPLIED MATERIALS-BRITTON | 115 | ETL.4300 |  | ACT | 0.47 |  |  |  | 0.47
ARBUCKLE TAP | 60 | ETL.6591 |  | ACT | 0.82 |  |  |  | 0.82
ARBURUA TAP | 70 | ETL.8932 |  | ACT | 3.57 |  |  |  | 3.57
ARCATA-HUMBOLDT | 60 | ETL.7110 |  | ACT | 7.28 |  |  |  | 7.28
ARCO-AZALEA PV | 70 | ETL.1472 |  | ACT | 0.07 |  |  |  | 0.07
ARCO-CARNERAS | 70 | ETL.8430 |  | ACT | 18.02 |  |  |  | 18.02
ARCO-CHOLAME | 70 | ETL.8440 |  | ACT | 26.74 |  | 4.8 |  | 21.94
ARCO-MIDWAY | 230 | ETL.4320 |  | ACT | 43.36 |  |  |  | 43.36
ARCO-POLONIO PASS PP | 70 | ETL.8450 |  | ACT | 21.26 |  | 7.26 |  | 14
ARCO-TULARE LAKE | 70 | ETL.8460 |  | ACT | 16.11 |  |  |  | 16.11
ARCO-TWISSELMAN | 70 | ETL.8470 |  | ACT | 6.46 |  |  |  | 6.46
ARMSTRONG TAP | 70 | ETL.8722 |  | ACT | 0.44 |  |  |  | 0.44
ARVIN EDISON TAP | 115 | ETL.4141 |  | ACT | 1.06 |  |  |  | 1.06
ATASCADERO-CAYUCOS | 70 | ETL.8480 |  | ACT | 11.79 | 5.36 | 3.59 |  | 2.84
ATASCADERO-SAN LUIS OBISPO | 70 | ETL.8490 |  | ACT | 15.52 | 3.3 | 7.86 |  | 4.36
ATLANTIC-GOLD HILL | 230 | ETL.4330 |  | ACT | 11.11 |  |  | 0.01 | 11.1
ATLANTIC-PLEASANT GROVE #1 | 115 | ETL.6190 |  | ACT | 5.33 |  |  |  | 5.33
ATLANTIC-PLEASANT GROVE #2 | 115 | ETL.9420 |  | ACT | 5.36 |  |  |  | 5.36
ATWATER-CRESSEY | 115 | ETL.1033 |  | ACT | 5.91 |  |  |  | 5.91
ATWATER-EL CAPITAN | 115 | ETL.1020 |  | ACT | 7.31 |  |  |  | 7.31
ATWATER-LIVINGSTON-MERCED | 115 | ETL.1030 |  | ACT | 24.26 |  |  |  | 24.26
AUBERRY TAP | 70 | ETL.9331 |  | ACT | 2.28 |  | 2.28 |  | 0
AUBURN TAP | 60 | ETL.6992 |  | ACT | 0.75 |  |  |  | 0.75
AVENAL TAP | 70 | ETL.8702 |  | ACT | 5.4 |  |  |  | 5.4
BADGER CREEK (PSE) TAP | 115 | ETL.1932 |  | ACT | 1.07 |  |  |  | 1.07
BADGER HILL TAP | 70 | ETL.8452 |  | ACT | 1.56 |  |  |  | 1.56
BAHIA-MORAGA | 230 | ETL.4340 |  | ACT | 26.92 | 4.3 | 12.25 |  | 10.37
BAIR-BELMONT | 115 | ETL.1040 |  | ACT | 3.64 |  |  |  | 3.64
BAIR-COOLEY LANDING #1 | 60 | ETL.6200 |  | ACT | 5.56 |  |  |  | 5.56
BAIR-COOLEY LANDING #2 | 60 | ETL.6210 |  | ACT | 5.6 |  |  |  | 5.6
BAKERSFIELD #2 TAP | 230 | ETL.5171 |  | ACT | 6.97 |  |  |  | 6.97
BALCH-MCCALL | 230 | ETL.4350 |  | ACT | 39.76 |  | 20.2 | 0.27 | 19.29
BALCH-SANGER | 115 | ETL.1050 |  | ACT | 35.63 |  | 19.85 | 0.12 | 15.66
BARKER SLOUGH TAP | 115 | ETL.1141 |  | ACT | 1.63 |  |  |  | 1.63
BARTON-AIRWAYS-SANGER | 115 | ETL.1060 |  | ACT | 11.57 |  |  |  | 11.57
BASALT #1 TAP | 60 | ETL.8181 |  | ACT | 1.18 |  |  |  | 1.18
BEALE AFB (WAPA) #1 TAP | 60 | ETL.8001 |  | ACT | 0.11 |  | 0.11 |  | 0
BEALE AFB (WAPA) #2 TAP | 60 | ETL.7971 |  | ACT | 0.14 |  | 0.14 |  | 0
BEAR CANYON TAP | 230 | ETL.1182 |  | ACT | 0.02 | 0.02 |  |  | 0
BEAR MTN TAP | 115 | ETL.4131 |  | ACT | 1.27 |  |  |  | 1.27
BEARDSLEY TAP | 115 | ETL.1401 |  | ACT | 2.2 | 2.15 | 0.02 |  | 0.03
BELDEN TAP | 230 | ETL.4441 |  | ACT | 0.02 |  | 0.02 |  | 0
BELL-PLACER | 115 | ETL.4395 |  | ACT | 7.94 |  | 2.86 |  | 5.08
BELLE HAVEN #1 TAP | 60 | ETL.6201 |  | ACT | 0.42 |  |  |  | 0.42
BELLE HAVEN #2 TAP | 60 | ETL.6211 |  | ACT | 0.41 |  |  |  | 0.41
BELLOTA-COTTLE | 230 | ETL.4360 |  | ACT | 19.84 |  |  |  | 19.84
BELLOTA-RIVERBANK | 115 | ETL.3480 |  | ACT | 18.87 |  |  |  | 18.87
BELLOTA-RIVERBANK-MELONES SW STA | 115 | ETL.1070 |  | ACT | 44.65 |  | 11.19 |  | 33.46
BELLOTA-TESLA #2 | 230 | ETL.4370 |  | ACT | 37.94 |  |  |  | 37.94
BELLOTA-WARNERVILLE | 230 | ETL.4380 |  | ACT | 22.47 |  |  |  | 22.47
BELLOTA-WEBER | 230 | ETL.4390 |  | ACT | 14.26 |  |  |  | 14.26
BELRIDGE TAP | 115 | ETL.2631 |  | ACT | 6.94 |  |  |  | 6.94
BERRENDA A TAP | 70 | ETL.8441 |  | ACT | 2.31 |  |  |  | 2.31
BERRENDA C TAP | 70 | ETL.8443 |  | ACT | 1.87 |  |  |  | 1.87
BIOLA-GLASS-MADERA | 70 | ETL.9350 |  | ACT | 18.8 |  |  |  | 18.8
BIRDS LANDING SW STA-CONTRA COSTA PP | 230 | ETL.5830 |  | ACT | 10.2 |  |  |  | 10.2
BIRDS LANDING SW STA-CONTRA COSTA SUB | 230 | ETL.6161 |  | ACT | 9.46 |  |  |  | 9.46
BIRDS LANDING SW STA-RUSSELL | 230 | ETL.6602 |  | ACT | 0.11 |  |  |  | 0.11
BIRDS LANDING SW STA-SHILOH | 230 | ETL.1413 |  | ACT | 0.11 |  |  |  | 0.11
BITTERWATER SW STA-WHEELER RIDGE #2 | 230 | ETL.5200 |  | ACT | 27.35 |  |  |  | 27.35
BIXLER TAP | 60 | ETL.7056 |  | ACT | 0.55 |  |  |  | 0.55
BLACK TAP | 230 | ETL.5431 | POWERGEN | ACT | 0.51 |  | 0.51 |  | 0
BLUE CHIP MILLING TAP | 60 | ETL.6802 |  | ACT | 0.42 |  |  |  | 0.42
BLUE LAKE TAP | 60 | ETL.6801 |  | ACT | 3.7 |  |  |  | 3.7
BOGUE-RIO OSO | 115 | ETL.1100 |  | ACT | 21.24 |  |  |  | 21.24
BOLLMAN #1 TAP | 115 | ETL.3321 |  | ACT | 2.14 |  |  |  | 2.14
BOLLMAN #2 TAP | 115 | ETL.3331 |  | ACT | 2.19 |  |  |  | 2.19
BOLTHOUSE FARMS TAP | 115 | ETL.4132 |  | ACT | 0.11 |  |  |  | 0.11
BONITA TAP | 70 | ETL.9352 |  | ACT | 3.03 |  |  |  | 3.03
BORDEN-COPPERMINE | 70 | ETL.8500 |  | ACT | 19.92 |  |  |  | 19.92
BORDEN-GLASS | 70 | ETL.8510 |  | ACT | 6.64 |  |  |  | 6.64
BORDEN-GREGG #1 | 230 | ETL.1082 |  | ACT | 6.21 |  |  |  | 6.21
BORDEN-GREGG #2 | 230 | ETL.4400 |  | ACT | 6.21 |  |  |  | 6.21
BORDEN-LOTUS PV | 70 | ETL.1122 |  | ACT | 0.16 |  |  |  | 0.16
BORDEN-MADERA #1 | 70 | ETL.8710 |  | ACT | 4.92 |  |  |  | 4.92
BORDEN-MADERA #2 | 70 | ETL.8520 |  | ACT | 5.8 |  |  |  | 5.8
BOTTLE ROCK TAP D.W.R. | 230 | ETL.4771 |  | ACT | 1.07 | 1.07 |  |  | 0
BRENTWOOD-KELSO | 230 | ETL.4410 |  | ACT | 16.41 |  | 5.2 |  | 11.21
BRICEBURG JCT-MARIPOSA TAP | 70 | ETL.8651 |  | ACT | 7.78 |  | 7.78 |  | 0
BRIDGEVILLE-COTTONWOOD | 115 | ETL.1110 |  | ACT | 86.08 | 1 | 79.04 |  | 6.04
BRIDGEVILLE-GARBERVILLE | 60 | ETL.6220 |  | ACT | 36.15 | 9.8 | 7.13 |  | 19.22
BRIGHTON-BELLOTA | 230 | ETL.4420 |  | ACT | 42.51 |  |  |  | 42.51
BRIGHTON-DAVIS | 115 | ETL.1140 |  | ACT | 42.72 |  |  |  | 42.72
BRIGHTON-DAVIS | 115 | ETL.1140 |  | IDL | 3.59 |  |  |  | 3.59
BRIGHTON-GRAND ISLAND #1 | 115 | ETL.1150 |  | ACT | 24.99 |  |  |  | 24.99
BRIGHTON-GRAND ISLAND #2 | 115 | ETL.1160 |  | ACT | 25.04 |  |  |  | 25.04
BRIGHTON-OLEUM JCT | 0 | ETL.1162 |  | IDL | 0.3 |  |  |  | 0.3
BRIONES TAP | 60 | ETL.7055 |  | ACT | 6.99 | 0.22 | 4.28 |  | 2.49
BRITTON-MONTA VISTA | 115 | ETL.1170 |  | ACT | 7.23 |  |  |  | 7.23
BRUNSWICK #1 TAP | 115 | ETL.1422 |  | ACT | 6.98 | 5.95 | 0.61 | 0.03 | 0.39
BRUNSWICK #2 TAP | 115 | ETL.1431 |  | ACT | 7 | 5.97 | 0.63 | 0 | 0.4
BUCKS CREEK-ROCK CREEK-CRESTA | 230 | ETL.4430 |  | ACT | 9.37 | 0.07 | 9.3 |  | 0
BUELLTON TAP | 115 | ETL.1201 |  | ACT | 1.75 |  | 1.39 |  | 0.36
BUENA VISTA BIOMASS POWER TAP | 60 | ETL.8252 |  | ACT | 1.01 |  | 0.32 |  | 0.69
BUENA VISTA PUMPING PLANT #1 TAP | 230 | ETL.5191 |  | ACT | 1.18 |  |  |  | 1.18
BUENA VISTA PUMPING PLANT #2 TAP | 230 | ETL.5201 |  | ACT | 1.21 |  |  |  | 1.21
BURNEY FOREST PRODUCTS TAP | 230 | ETL.5391 |  | ACT | 0.04 |  |  |  | 0.04
BURNEY TAP | 60 | ETL.7041 |  | ACT | 1.07 |  |  |  | 1.07
BURNS-LONE STAR #1 | 60 | ETL.6230 |  | ACT | 5.44 | 3.23 | 2.21 |  | 0
BURNS-LONE STAR #2 | 60 | ETL.6240 |  | ACT | 6.31 | 4.9 | 1.4 |  | 0.01
BUTT VALLEY-CARIBOU | 115 | ETL.1180 | POWERGEN | ACT | 7.44 |  | 7.09 |  | 0.35
BUTTE-CHICO #1 | 60 | ETL.6250 |  | ACT | 0.79 |  |  |  | 0.79
BUTTE-CHICO #2 | 60 | ETL.6260 |  | ACT | 0.74 |  |  |  | 0.74
BUTTE-ESQUON | 60 | ETL.6270 |  | ACT | 9.87 |  |  |  | 9.87
BUTTE-SYCAMORE CREEK | 115 | ETL.1190 |  | ACT | 18.14 |  |  |  | 18.14
Bellota-North Central Valley | 115 | ETL.1374 |  | ACT | 0.03 |  |  |  | 0.03
CABRILLO-SANTA YNEZ SW STA | 115 | ETL.1200 |  | ACT | 14.59 |  | 13.18 |  | 1.41
CACHE SLOUGH TAP | 60 | ETL.6741 |  | ACT | 6.82 |  |  |  | 6.82
CADET TAP | 70 | ETL.9232 |  | ACT | 0.06 |  |  |  | 0.06
CAL PEAK-VACA | 115 | ETL.4230 |  | ACT | 0.11 |  |  |  | 0.11
CAL WATER TAP | 115 | ETL.3951 |  | ACT | 2.15 |  |  |  | 2.15
CALIENTE SW STA-MIDWAY #1 | 230 | ETL.5216 |  | ACT | 27.17 |  |  |  | 27.17
CALIENTE SW STA-MIDWAY #2 | 230 | ETL.5226 |  | ACT | 27.16 |  |  |  | 27.16
CALIFORNIA AVE-MCCALL | 115 | ETL.2360 |  | ACT | 23.66 |  |  |  | 23.66
CALIFORNIA FLATS SW STA-GATES | 230 | ETL.5281 |  | ACT | 22.57 |  | 1.5 |  | 21.07
CALLENDER SW STA-MESA | 115 | ETL.1210 |  | ACT | 13.76 |  | 5.61 | 0.22 | 7.93
CALPINE-WEST FORD FLAT | 230 | ETL.1183 |  | ACT | 0.05 | 0.05 |  |  | 0
CALVO TAP | 60 | ETL.7251 |  | ACT | 0.54 |  |  |  | 0.54
CAMANCHE PUMPING PLANT TAP | 230 | ETL.1230 |  | ACT | 0.45 |  |  |  | 0.45
CAMANCHE TAP | 115 | ETL.1691 |  | ACT | 6.71 |  |  |  | 6.71
CAMDEN-KINGSBURG | 70 | ETL.8653 |  | ACT | 14.93 |  |  |  | 14.93
CAMP EVERS-PAUL SWEET | 115 | ETL.1220 |  | ACT | 5.22 | 4.59 |  |  | 0.63
CANANDAIGUA WINERY TAP | 70 | ETL.9351 |  | ACT | 0.29 |  |  |  | 0.29
CANTUA TAP | 115 | ETL.3251 |  | ACT | 1.83 |  |  |  | 1.83
CAPE HORN TAP | 60 | ETL.6761 |  | ACT | 0.31 |  | 0.31 |  | 0
CARBERRY SW STA-ROUND MTN | 230 | ETL.5410 |  | ACT | 12.61 | 0.25 | 12.36 |  | 0
CARBONA #2 TAP | 60 | ETL.7233 |  | ACT | 5.6 |  |  |  | 5.6
CARIBOU #2 | 60 | ETL.6280 |  | ACT | 30.62 |  | 27.77 |  | 2.85
CARIBOU-PALERMO | 115 | ETL.3190 |  | IDL | 0.02 |  | 0.02 |  | 0 | Idle Section
CARIBOU-PLUMAS JCT | 60 | ETL.6290 |  | ACT | 21.26 |  | 16.4 |  | 4.86
CARIBOU-TABLE MTN | 230 | ETL.4440 |  | ACT | 54.34 | 9.09 | 39.35 |  | 5.9
CARIBOU-WESTWOOD | 60 | ETL.6300 |  | ACT | 20.99 |  | 20.01 |  | 0.98
CARIBOU-WESTWOOD | 60 | ETL.6300 |  | IDL | 0.06 |  |  |  | 0.06
CARNATION TAP | 70 | ETL.8901 |  | ACT | 0.54 |  |  |  | 0.54
CARNERAS-TAFT | 70 | ETL.8540 |  | ACT | 34.8 |  |  |  | 34.8
CARQUINEZ #1 TAP | 115 | ETL.1831 |  | ACT | 0.51 |  |  |  | 0.51
CARQUINEZ #2 TAP | 115 | ETL.1841 |  | ACT | 0.52 |  |  |  | 0.52
CARRIZO PLAINS TAP | 115 | ETL.3961 |  | ACT | 0.04 |  |  |  | 0.04
CARUTHERS-LEMOORE NAS-CAMDEN | 70 | ETL.8550 |  | ACT | 25.1 |  |  |  | 25.1
CASCADE-BENTON-DESCHUTES | 60 | ETL.6310 |  | ACT | 15.97 |  | 9.56 |  | 6.41
CASCADE-COTTONWOOD | 115 | ETL.1240 |  | ACT | 19.47 |  | 12.18 |  | 7.29
CASTAIC TAP | 70 | ETL.9253 |  | ACT | 0.02 |  | 0.02 |  | 0
CASTRO VALLEY-NEWARK | 230 | ETL.4450 |  | ACT | 22.71 | 5.6 | 5.96 | 0.48 | 10.67
CAWELO B TAP | 70 | ETL.8871 |  | ACT | 0.4 |  |  |  | 0.4
CAWELO C TAP | 115 | ETL.2122 |  | ACT | 1.33 |  |  |  | 1.33
CAYUCOS-CAMBRIA | 70 | ETL.8560 |  | ACT | 17.73 |  | 7.69 |  | 10.04
CELERON TAP | 70 | ETL.8541 |  | ACT | 0.04 |  |  |  | 0.04
CENTERVILLE-TABLE MTN | 60 | ETL.6320 |  | ACT | 21.51 | 4.1 | 3.81 |  | 13.6
CENTERVILLE-TABLE MTN-OROVILLE | 60 | ETL.6330 |  | ACT | 26.1 | 3.84 | 6.34 |  | 15.92
CERTAINTEED TAP | 115 | ETL.2111 |  | ACT | 2.52 |  |  |  | 2.52
CHARCA-FAMOSO | 115 | ETL.2621 |  | ACT | 7.15 |  |  |  | 7.15
CHCF TAP | 115 | ETL.7011 |  | ACT | 3 |  |  |  | 3
CHENEY #1 TAP | 115 | ETL.3231 |  | ACT | 3.99 |  |  |  | 3.99
CHENEY #2 TAP | 115 | ETL.3261 |  | ACT | 1.84 |  |  |  | 1.84
CHEVRON (LOST HILLS) TAP | 70 | ETL.8472 |  | ACT | 14.75 |  |  |  | 14.75
CHEVRON PIPELINE KETTLEMAN TAP | 70 | ETL.8703 |  | ACT | 1.17 |  |  |  | 1.17
CHINESE CAMP (ULTRA POWER) TAP | 115 | ETL.2392 |  | ACT | 2.1 |  | 1.54 |  | 0.56
CHOWCHILLA #1 TAP | 115 | ETL.2112 |  | ACT | 1.24 |  |  |  | 1.24
CHOWCHILLA-KERCKHOFF | 115 | ETL.1250 |  | ACT | 42.52 |  | 9.5 |  | 33.02
CHRISTIE-FRANKLIN #1 | 60 | ETL.6350 |  | ACT | 3.44 |  | 1.85 |  | 1.59
CHRISTIE-FRANKLIN #1 | 60 | ETL.6350 |  | IDL | 1.57 |  |  |  | 1.57
CHRISTIE-FRANKLIN #2 | 60 | ETL.6360 |  | ACT | 3.45 |  | 1.84 |  | 1.61
CHRISTIE-FRANKLIN #2 (12KV) | 60 | ETL.6360 |  | IDL | 1.62 |  |  |  | 1.62
CHRISTIE-SOBRANTE | 115 | ETL.1260 |  | ACT | 7.84 |  | 7.74 |  | 0.1
CHRISTIE-WILLOW PASS | 60 | ETL.6370 |  | ACT | 15.93 |  | 3.83 |  | 12.1
CISCO GROVE TAP | 60 | ETL.8061 |  | ACT | 0.34 |  |  | 0.16 | 0.18
CITY #1 TAP | 115 | ETL.1382 |  | ACT | 0.07 |  |  |  | 0.07
CITY #2 TAP | 115 | ETL.1371 |  | ACT | 1.37 |  |  |  | 1.37
CLAY-MARTEL | 60 | ETL.8250 |  | ACT | 16.98 |  | 14.52 |  | 2.46
CLAYTON-MEADOW LANE | 115 | ETL.1270 |  | ACT | 7.06 |  |  |  | 7.06
CLEAR LAKE-HOPLAND | 60 | ETL.6390 |  | ACT | 11.53 |  | 7.33 |  | 4.2
CLEAR LAKE-KONOCTI | 60 | ETL.6852 |  | ACT | 10.99 |  | 4.94 |  | 6.05
CLOVER CREEK TAP | 60 | ETL.7291 |  | ACT | 0.02 | 0.02 |  |  | 0
COALINGA #1-COALINGA #2 | 70 | ETL.8570 |  | ACT | 8.61 |  |  |  | 8.61
COALINGA #1-SAN MIGUEL | 70 | ETL.8580 |  | ACT | 38.01 |  | 17.45 | 0.44 | 20.12
COALINGA COGEN TAP | 70 | ETL.8571 |  | ACT | 4.91 |  |  |  | 4.91
COBURN-BASIC ENERGY | 60 | ETL.6400 |  | ACT | 3.39 |  |  |  | 3.39
COBURN-LAS AGUILAS SW STA | 230 | ETL.4460 |  | ACT | 63.97 |  | 41.16 | 0.01 | 22.8
COBURN-OIL FIELDS #1 | 60 | ETL.6410 |  | ACT | 29.46 |  |  | 0 | 29.46
COBURN-OIL FIELDS #2 | 60 | ETL.6420 |  | ACT | 31.05 |  |  |  | 31.05
COGENERATION NATIONAL TAP | 60 | ETL.8323 |  | ACT | 0.56 |  |  |  | 0.56
COLEMAN HATCHERY TAP | 60 | ETL.8428 |  | ACT | 0.56 |  |  |  | 0.56
COLEMAN-COTTONWOOD | 60 | ETL.6430 |  | ACT | 8.58 |  | 1.11 | 0.17 | 7.3
COLEMAN-RED BLUFF | 60 | ETL.6440 |  | ACT | 48.31 |  | 20.25 |  | 28.06
COLEMAN-SOUTH | 60 | ETL.6450 |  | ACT | 13.39 |  | 13.39 |  | 0
COLES LEVEE TAP | 115 | ETL.2593 |  | ACT | 0.22 |  |  |  | 0.22
COLGATE PH-COLGATE SW STA | 60 | ETL.6460 |  | ACT | 0.19 |  | 0.19 |  | 0
COLGATE-ALLEGHANY | 60 | ETL.6470 |  | ACT | 24.53 | 19.92 | 4.61 |  | 0
COLGATE-CHALLENGE | 60 | ETL.6480 |  | ACT | 13.04 | 11.62 | 1.43 |  | -0.01
COLGATE-GRASS VALLEY | 60 | ETL.6490 |  | ACT | 13.17 | 1.87 | 10.03 |  | 1.27
COLGATE-PALERMO | 60 | ETL.6500 |  | ACT | 22.65 |  | 21.72 |  | 0.93
COLGATE-RIO OSO | 230 | ETL.5900 |  | ACT | 40.89 |  | 11.86 |  | 29.03
COLGATE-SMARTVILLE #1 | 60 | ETL.6510 |  | ACT | 11.26 |  | 11.26 |  | 0
COLGATE-SMARTVILLE #2 | 60 | ETL.6520 |  | ACT | 11.19 |  | 11.19 |  | 0
COLLINS PINE TAP | 60 | ETL.7001 |  | ACT | 1 |  | 0.08 |  | 0.92
COLUMBIA SOLAR 115kV TAP | 115 | ETL.3301 |  | ACT | 0.51 |  |  |  | 0.51
COLUMBUS-MAGUNDEN | 115 | ETL.1233 |  | ACT | 3.69 |  |  |  | 3.69
COLUSA JCT #1 | 60 | ETL.8390 |  | ACT | 16.98 |  |  |  | 16.98
CONTRA COSTA #1 | 115 | ETL.1280 |  | ACT | 11.15 |  |  |  | 11.15
CONTRA COSTA #2 | 115 | ETL.1290 |  | ACT | 1.43 |  |  |  | 1.43
CONTRA COSTA PP-CONTRA COSTA SUB | 230 | ETL.4470 |  | ACT | 1.89 |  |  |  | 1.89
CONTRA COSTA-BALFOUR | 60 | ETL.8420 |  | ACT | 11.54 |  |  |  | 11.54
CONTRA COSTA-BRENTWOOD | 230 | ETL.4480 |  | ACT | 10.06 |  |  |  | 10.06
CONTRA COSTA-DELTA SWITCHYARD | 230 | ETL.4490 |  | ACT | 18.46 |  | 5.19 |  | 13.27
CONTRA COSTA-DU PONT | 60 | ETL.6530 |  | ACT | 2.14 |  |  |  | 2.14
CONTRA COSTA-LAS POSITAS | 230 | ETL.4510 |  | ACT | 23.83 | 0.88 | 10.98 |  | 11.97
CONTRA COSTA-LONE TREE | 230 | ETL.4535 |  | ACT | 5.61 |  |  |  | 5.61
CONTRA COSTA-MORAGA #1 | 230 | ETL.5452 |  | ACT | 26.76 | 4.3 | 11.36 |  | 11.1
CONTRA COSTA-MORAGA #2 | 230 | ETL.5453 |  | ACT | 26.84 | 4.38 | 11.33 |  | 11.13
CONTRA COSTA-PITTSBURG | 60 | ETL.6540 |  | ACT | 6.28 |  |  |  | 6.28
CONTRA COSTA-SHELL CHEMICAL#1(21KV) | 60 | ETL.6550 |  | IDL | 9.9 |  |  |  | 9.9
COOLEY LANDING-LOS ALTOS | 60 | ETL.6560 |  | ACT | 14.94 |  |  |  | 14.94
COOLEY LANDING-LOS ALTOS (I2KV) | 60 | ETL.6560 |  | IDL | 1.4 |  |  |  | 1.4
COOLEY LANDING-PALO ALTO | 115 | ETL.1300 |  | ACT | 2.72 |  |  |  | 2.72
COOLEY LANDING-STANFORD | 60 | ETL.6570 |  | ACT | 6.02 |  |  |  | 6.02
COPPERMINE-TIVY VALLEY | 70 | ETL.8590 |  | ACT | 24 |  | 0.89 | 0.02 | 23.09
COPUS-OLD RIVER | 70 | ETL.8970 |  | ACT | 19.62 |  |  |  | 19.62
CORCORAN-ANGIOLA | 70 | ETL.8600 |  | ACT | 8.95 |  |  |  | 8.95
CORCORAN-GUERNSEY | 70 | ETL.9360 |  | ACT | 13.49 |  |  |  | 13.49
CORCORAN-OLIVE SW STA | 115 | ETL.1310 |  | ACT | 18.43 |  |  |  | 18.43
CORCORAN-OLIVE SW STA | 115 | ETL.1310 |  | IDL | 0.02 |  |  |  | 0.02
CORDELIA #1 TAP | 60 | ETL.8182 |  | ACT | 7.69 |  | 4.56 |  | 3.13
CORDELIA #2 TAP | 60 | ETL.8184 |  | ACT | 6.87 |  | 2.99 |  | 3.88
CORONA-LAKEVILLE | 115 | ETL.4311 |  | ACT | 5.79 |  |  |  | 5.79
CORTINA #1 | 60 | ETL.6580 |  | ACT | 26.28 |  |  |  | 26.28
CORTINA #2 | 60 | ETL.6590 |  | ACT | 40.66 |  |  |  | 40.66
CORTINA #3 | 60 | ETL.6600 |  | ACT | 24.8 |  |  |  | 24.8
CORTINA #4 | 60 | ETL.6610 |  | ACT | 45.24 |  |  | 0.15 | 45.09
CORTINA-MENDOCINO #1 | 115 | ETL.1330 |  | ACT | 60.95 | 4.56 | 48.77 |  | 7.62
CORTINA-VACA | 230 | ETL.4540 |  | ACT | 53.22 |  | 2.25 |  | 50.97
COTTLE-MELONES | 230 | ETL.4530 |  | ACT | 25.92 |  | 5.29 |  | 20.63
COTTONWOOD #1 | 60 | ETL.6620 |  | ACT | 48.17 |  | 9.72 |  | 38.45
COTTONWOOD #2 | 60 | ETL.6630 |  | ACT | 23.63 |  | 9.72 |  | 13.91
COTTONWOOD-BENTON #1 | 60 | ETL.6640 |  | ACT | 15.53 |  | 5.53 |  | 10
COTTONWOOD-BENTON #2 | 60 | ETL.6650 |  | ACT | 14.67 | 2.99 | 9.6 |  | 2.08
COTTONWOOD-DELEVAN #1 | 230 | ETL.4550 |  | ACT | 71.55 |  | 9.71 |  | 61.84
COTTONWOOD-DELEVAN #2 | 230 | ETL.4580 |  | ACT | 71.54 |  | 9.71 |  | 61.83
COTTONWOOD-GLENN | 230 | ETL.4560 |  | ACT | 48.33 |  | 9.71 |  | 38.62
COTTONWOOD-LOGAN CREEK | 230 | ETL.4570 |  | ACT | 59.28 |  | 9.71 |  | 49.57
COTTONWOOD-PANORAMA | 115 | ETL.1340 |  | ACT | 2.95 |  | 2.08 |  | 0.87
COTTONWOOD-RED BLUFF | 60 | ETL.6660 |  | ACT | 16.78 |  | 10.54 |  | 6.24
COVE ROAD TAP | 230 | ETL.5421 |  | ACT | 0.11 |  | 0.11 |  | 0
COYOTE SW STA-METCALF | 230 | ETL.5092 |  | ACT | 0.88 |  |  |  | 0.88
CRAG VIEW-CASCADE | 115 | ETL.1350 |  | ACT | 21.61 | 2.41 | 17.96 |  | 1.24
CRAZY HORSE CANYON-HOLLISTER | 115 | ETL.2153 |  | ACT | 17.18 |  | 2.7 |  | 14.48
CRAZY HORSE CANYON-SALINAS-SOLEDAD #1 | 115 | ETL.2900 |  | ACT | 35.34 |  | 15.82 | 0.01 | 19.51
CRAZY HORSE CANYON-SALINAS-SOLEDAD #2 | 115 | ETL.2910 |  | ACT | 35.42 |  | 15.84 |  | 19.58
CRAZY HORSE CANYON-SAN BENITO | 115 | ETL.2152 |  | ACT | 8.94 |  | 2.64 |  | 6.3
CRESCENT SW STA-SCHINDLER | 70 | ETL.9180 |  | ACT | 10.8 |  |  |  | 10.8
CRESCENT SW STA-SCULPIN PV | 70 | ETL.1038 |  | ACT | 0.04 |  |  |  | 0.04
CRESCENT SW STA-STROUD | 70 | ETL.9190 |  | ACT | 3.62 |  |  |  | 3.62
CRESTA-RIO OSO | 230 | ETL.4590 |  | ACT | 64.79 | 8.93 | 18.2 |  | 37.66
CROW CREEK SW STA-FRONTIER SOLAR PV | 60 | ETL.7859 |  | ACT | 0.02 |  |  |  | 0.02
CROW CREEK SW STA-NEWMAN | 60 | ETL.7860 |  | ACT | 11.14 |  |  |  | 11.14
CROW CREEK SW STA-PAULSELL PV | 60 | ETL.1462 |  | ACT | 0.04 |  |  |  | 0.04
CROWS LANDING TAP | 60 | ETL.7871 |  | ACT | 5.28 |  |  |  | 5.28
CRUSHER TAP | 60 | ETL.6241 |  | ACT | 1.94 |  | 1.94 |  | 0
CRYSTAL SPRINGS TAP | 60 | ETL.7211 |  | ACT | 0.28 |  | 0.28 |  | 0
CYMRIC TAP | 115 | ETL.2582 |  | ACT | 0.18 |  |  |  | 0.18
DAIRYLAND-MENDOTA | 115 | ETL.1360 |  | ACT | 28.69 |  |  |  | 28.69
DANISH CREAMERY TAP | 115 | ETL.2362 |  | ACT | 1.2 |  |  |  | 1.2
DE FRANCESCO TAP | 115 | ETL.3245 |  | ACT | 1.03 |  |  |  | 1.03
DEEPWATER #1 TAP | 115 | ETL.4121 |  | ACT | 2.29 |  |  |  | 2.29
DEEPWATER #2 TAP | 115 | ETL.4111 |  | ACT | 2.45 |  |  |  | 2.45
DEER CREEK-DRUM | 60 | ETL.6690 | PGE | ACT | 6.27 | 6.27 |  |  | 0
DEL MAR-ATLANTIC #1 | 60 | ETL.1410 |  | ACT | 2.78 |  |  |  | 2.78
DEL MAR-ATLANTIC #2 | 60 | ETL.6170 |  | ACT | 4.39 |  |  |  | 4.39
DEL MONTE-FORT ORD #1 | 60 | ETL.8400 |  | ACT | 6.13 |  | 0.25 |  | 5.88
DEL MONTE-FORT ORD #2 | 60 | ETL.8422 |  | ACT | 5.6 |  | 0.06 |  | 5.54
DEL MONTE-MONTEREY | 60 | ETL.6700 |  | ACT | 2.53 |  |  |  | 2.53
DEL MONTE-VIEJO | 60 | ETL.6710 |  | ACT | 8.67 |  | 5.29 |  | 3.38
DELEVAN-CORTINA | 230 | ETL.4384 |  | ACT | 17.89 |  |  |  | 17.89
DELEVAN-VACA #1 | 230 | ETL.5010 |  | ACT | 71.04 |  | 2.06 |  | 68.98
DELEVAN-VACA #2 | 230 | ETL.4231 |  | ACT | 71.07 |  | 1.67 |  | 69.4
DELEVAN-VACA #3 | 230 | ETL.4790 |  | ACT | 71.09 |  | 1.49 |  | 69.6
DELTA SWITCHING YARD-TESLA | 230 | ETL.4600 |  | ACT | 7.7 |  |  |  | 7.7
DELTA-MTN GATE JCT | 60 | ETL.6750 |  | ACT | 15.11 | 2.18 | 11.65 |  | 1.28
DERRICK TAP | 70 | ETL.8573 |  | ACT | 0.85 |  |  |  | 0.85
DESABLA-CENTERVILLE | 60 | ETL.6720 |  | ACT | 5.89 | 5.89 |  |  | 0
DIABLO PP STANDBY SUPPLY | 230 | ETL.4610 |  | ACT | 0.48 | 0.48 |  |  | 0
DIABLO UNIT #1 | 500 | ETL.5940 |  | ACT | 0.54 | 0.54 |  |  | 0
DIABLO UNIT #2 | 500 | ETL.5950 |  | ACT | 0.57 | 0.57 |  |  | 0
DIABLO-GATES #1 | 500 | ETL.5960 |  | ACT | 79.23 | 10.56 | 16.5 | 0.08 | 52.09
DIABLO-MESA | 230 | ETL.4620 |  | ACT | 40.34 | 7.65 | 27.83 |  | 4.86
DIABLO-MIDWAY #2 | 500 | ETL.5970 |  | ACT | 84.09 | 15.47 | 29.47 |  | 39.15
DIABLO-MIDWAY #3 | 500 | ETL.5980 |  | ACT | 84.67 | 15.56 | 29.34 |  | 39.77
DINOSAUR POINT TAP | 70 | ETL.8961 |  | ACT | 2 |  | 0.51 |  | 1.49
DINUBA ENERGY TAP | 70 | ETL.9051 |  | ACT | 3.16 |  |  |  | 3.16
DINUBA-OROSI | 70 | ETL.8610 |  | ACT | 9.83 |  |  |  | 9.83
DISCOVERY TAP | 115 | ETL.1921 |  | ACT | 2.1 |  |  |  | 2.1
DISTRICT 1001 TAP | 60 | ETL.7701 |  | ACT | 1.45 |  |  |  | 1.45
DISTRICT 1500 TAP | 60 | ETL.7711 |  | ACT | 3.61 |  |  |  | 3.61
DIVIDE-CABRILLO #1 | 115 | ETL.1380 |  | ACT | 14.6 |  | 6.29 |  | 8.31
DIVIDE-CABRILLO #2 | 115 | ETL.1370 |  | ACT | 11.55 |  | 6.05 |  | 5.5
DIVIDE-VANDENBERG #1 | 70 | ETL.8620 |  | ACT | 6.64 |  | 5.51 |  | 1.13
DIVIDE-VANDENBERG #2 | 70 | ETL.8630 |  | ACT | 6.57 |  | 5.45 |  | 1.12
DIXON LANDING-MCKEE | 115 | ETL.1390 |  | ACT | 8.3 |  |  |  | 8.3
DIXON-VACA #1 | 60 | ETL.6730 |  | ACT | 18.35 |  |  |  | 18.35
DIXON-VACA #2 | 60 | ETL.6740 |  | ACT | 26.77 |  |  |  | 26.77
DOLAN RD #1 TAP | 115 | ETL.2881 |  | ACT | 0.32 |  |  |  | 0.32
DOLAN RD #2 TAP | 115 | ETL.2891 |  | ACT | 0.33 |  |  |  | 0.33
DONNELLS-MI-WUK | 115 | ETL.1400 |  | ACT | 18.46 | 18.46 |  |  | 0
DOS AMIGOS PUMPING PLANT-PANOCHE | 230 | ETL.4630 |  | ACT | 23.67 |  |  |  | 23.67
DOUBLE C (PSE) TAP | 115 | ETL.1931 |  | ACT | 0.06 |  |  |  | 0.06
DRUM PH #2 TAP | 115 | ETL.6375 | POWERGEN | ACT | 0.09 | 0.09 |  |  | 0
DRUM-GRASS VALLEY-WEIMAR | 60 | ETL.6760 |  | ACT | 31.17 | 17.2 | 12.72 |  | 1.25
DRUM-HIGGINS | 115 | ETL.4393 |  | ACT | 43.53 | 19.01 | 23.87 |  | 0.65
DRUM-RIO OSO #1 | 115 | ETL.1420 |  | ACT | 44.64 | 14.06 | 17.9 |  | 12.68
DRUM-RIO OSO #2 | 115 | ETL.1430 |  | ACT | 44.65 | 14.08 | 17.87 |  | 12.7
DRUM-SPAULDING | 60 | ETL.6770 |  | ACT | 9.36 | 6.88 | 2.48 |  | 0
DRUM-SUMMIT #1 | 115 | ETL.1440 |  | ACT | 27.38 | 6.51 | 15.1 | 1.54 | 4.23
DRUM-SUMMIT #2 | 115 | ETL.1450 |  | ACT | 28.36 | 6.49 | 16.36 | 1.49 | 4.02
DUMBARTON-NEWARK | 115 | ETL.1460 |  | ACT | 7.14 |  |  |  | 7.14
DUNLAP TAP | 70 | ETL.9061 |  | ACT | 16.21 |  | 13.79 |  | 2.42
DUTCH FLAT #2 TAP | 115 | ETL.1421 |  | ACT | 0.43 | 0.43 |  |  | 0
EAGLE ROCK-CORTINA | 115 | ETL.1470 |  | ACT | 43.39 | 14.63 | 23 |  | 5.76
EAGLE ROCK-FULTON-SILVERADO | 115 | ETL.4392 |  | ACT | 46.62 | 41.49 | 2.45 |  | 2.68
EAGLE ROCK-FULTON-SILVERADO | 115 | ETL.4392 |  | IDL | 0.33 | 0.33 |  |  | 0 | Idle Section
EAGLE ROCK-REDBUD | 115 | ETL.1480 |  | ACT | 23.31 | 9.94 | 13.05 |  | 0.32
EAST DUBLIN (BART) TAP | 60 | ETL.7962 |  | ACT | 0.04 |  |  |  | 0.04
EAST GRAND - SOUTH SAN FRANSICO TRACTION POWER #1 | 115 | ETL.1302 |  | ACT | 0.09 |  |  |  | 0.09
EAST GRAND - SOUTH SAN FRANSICO TRACTION POWER #2 | 115 | ETL.1304 |  | ACT | 0.05 |  |  |  | 0.05
EAST GRAND-SAN MATEO | 115 | ETL.1490 |  | ACT | 7.89 |  |  |  | 7.89
EASTSHORE-CERBERUS | 115 | ETL.7252 |  | ACT | 0.48 |  |  |  | 0.48
EASTSHORE-CLAWITER #1 | 230 | ETL.1335 |  | ACT | 0.67 |  |  |  | 0.67
EASTSHORE-CLAWITER #2 | 230 | ETL.1333 |  | ACT | 0.62 |  |  |  | 0.62
EASTSHORE-DUMBARTON | 115 | ETL.1495 |  | ACT | 12.38 |  |  |  | 12.38
EASTSHORE-MT EDEN #1 | 115 | ETL.1500 |  | ACT | 1.04 |  |  |  | 1.04
EASTSHORE-MT EDEN #2 | 115 | ETL.1501 |  | ACT | 1 |  |  |  | 1
EASTSHORE-SAN MATEO | 230 | ETL.4650 |  | ACT | 12.43 |  |  |  | 12.43
EBMUD TAP | 115 | ETL.2081 |  | ACT | 0.02 |  |  |  | 0.02
EDES #1 TAP | 115 | ETL.3521 |  | ACT | 0.04 |  |  |  | 0.04
EDES #2 TAP | 115 | ETL.3142 |  | ACT | 0.04 |  |  |  | 0.04
EEL RIVER TAP | 60 | ETL.7101 |  | ACT | 2.31 |  |  |  | 2.31
EIGHT MILE ROAD-STAGG | 230 | ETL.5002 |  | ACT | 7.2 |  |  |  | 7.2
EIGHT MILE ROAD-TESLA | 230 | ETL.4660 |  | ACT | 26.64 |  |  |  | 26.64
EISEN TAP | 70 | ETL.8883 |  | ACT | 1.86 |  |  |  | 1.86
EL CAPITAN-WILSON | 115 | ETL.1510 |  | ACT | 8.12 |  |  |  | 8.12
EL DORADO-MISSOURI FLAT #1 | 115 | ETL.1530 |  | ACT | 14.43 | 3.84 | 8.91 | 0.22 | 1.46
EL DORADO-MISSOURI FLAT #2 | 115 | ETL.1540 |  | ACT | 14.4 | 3.84 | 8.85 | 0.23 | 1.48
EL PATIO-SAN JOSE A | 115 | ETL.1520 |  | ACT | 7.08 |  |  |  | 7.08
EL PECO TAP | 70 | ETL.9353 |  | ACT | 3.02 |  |  |  | 3.02
ELECTRA-BELLOTA | 230 | ETL.4670 |  | ACT | 29.23 |  | 12.78 |  | 16.45
ELK CREEK TAP | 60 | ETL.6921 |  | ACT | 20.44 |  | 3.58 |  | 16.86
ELK-GUALALA | 60 | ETL.8410 |  | ACT | 29.02 |  | 22.59 | 0.13 | 6.3
ELLIS TAP | 115 | ETL.4021 |  | ACT | 0.16 |  |  |  | 0.16
EMIDIO TAP | 70 | ETL.9291 |  | ACT | 3.07 |  |  |  | 3.07
ENCINAL TAP | 60 | ETL.7751 |  | ACT | 1.43 |  |  |  | 1.43
ESSEX JCT-ARCATA-FAIRHAVEN | 60 | ETL.6800 |  | ACT | 16.06 |  |  |  | 16.06
ESSEX JCT-ORICK | 60 | ETL.6810 |  | ACT | 31.28 |  |  | 1.57 | 29.71
EUREKA-STA A | 60 | ETL.6820 |  | ACT | 0.22 |  |  |  | 0.22
EVERGREEN-ALMADEN | 60 | ETL.6830 |  | ACT | 4.96 |  |  | 0.03 | 4.93
EVERGREEN-MABURY | 60 | ETL.6840 |  | ACT | 5.48 |  |  |  | 5.48
EXCELSIOR SW STA-CRE FIVE POINTS PV | 115 | ETL.3247 | PGE | ACT | 0.03 |  |  |  | 0.03
EXCELSIOR SW STA-SCHINDLER #1 | 115 | ETL.3248 |  | ACT | 5.24 |  |  |  | 5.24
EXCELSIOR SW STA-SCHINDLER #2 | 115 | ETL.3249 |  | ACT | 5.23 |  |  |  | 5.23
EXCHEQUER-INDIAN FLAT | 70 | ETL.8650 | PGE | ACT | 29.89 | 4 | 25.17 | 0.01 | 0.71
EXCHEQUER-LE GRAND | 115 | ETL.1560 |  | ACT | 29.75 |  |  |  | 29.75
EXCHEQUER-MARIPOSA | 70 | ETL.8640 |  | ACT | 19.48 |  | 10.62 |  | 8.86
FAIRHAVEN #1 | 60 | ETL.6850 |  | ACT | 0.47 |  |  |  | 0.47
FAIRHAVEN POWER CO TAP | 60 | ETL.6853 |  | ACT | 0.5 |  |  |  | 0.5
FAIRHAVEN-HUMBOLDT | 60 | ETL.6860 |  | ACT | 15.44 |  |  |  | 15.44
FAIRVIEW-MARTINEZ SW STA | 115 | ETL.2275 |  | ACT | 0.1 |  |  |  | 0.1
FAIRWAY #1 TAP | 115 | ETL.2451 |  | ACT | 2.83 |  |  |  | 2.83
FAIRWAY #2 TAP | 115 | ETL.3611 |  | ACT | 1.52 |  |  |  | 1.52
FELLOWS-MIDSUN | 115 | ETL.1570 |  | ACT | 4.93 |  |  |  | 4.93
FELLOWS-TAFT | 115 | ETL.1580 |  | ACT | 7.93 |  |  |  | 7.93
FIBREBOARD STANDARD TAP | 115 | ETL.1404 |  | ACT | 0.02 |  | 0.02 |  | 0
FIBREBOARD TAP | 115 | ETL.1291 |  | ACT | 0.19 |  |  |  | 0.19
FINK SW STA-PROXIMA SOLAR | 230 | ETL.1386 |  | PRP | 0.05 |  |  |  | 0.05
FINK SW STA-WESTLEY | 230 | ETL.1384 |  | ACT | 15.87 |  | 6.81 |  | 9.06
FITCH MTN #1 TAP | 60 | ETL.6891 |  | ACT | 0.85 |  | 0.15 |  | 0.7
FITCH MTN #2 TAP | 60 | ETL.6901 |  | ACT | 0.06 |  |  |  | 0.06
FIVE POINTS SW STA-HURON-GATES | 70 | ETL.9160 |  | ACT | 19.78 |  |  |  | 19.78
FIVE POINTS SW-WHITNEY POINT PV | 70 | ETL.1053 |  | ACT | 0.05 |  |  |  | 0.05
FLINT TAP | 115 | ETL.3341 |  | ACT | 1.96 |  | 1.48 |  | 0.48
FMC - SAN JOSE TRACTION POWER #1 | 115 | ETL.1344 |  | ACT | 0.21 |  |  |  | 0.21
FMC - SAN JOSE TRACTION POWER #2 | 115 | ETL.1346 |  | ACT | 0.19 |  |  |  | 0.19
FMC-SAN JOSE B | 115 | ETL.2021 |  | ACT | 1.59 |  |  |  | 1.59
FORBESTOWN TAP | 115 | ETL.4222 |  | ACT | 0.2 | 0.2 |  |  | 0
FORKS OF THE BUTTE TAP | 60 | ETL.6722 |  | ACT | 0.25 | 0.25 |  |  | 0
FORT BRAGG-ELK | 60 | ETL.2060 |  | ACT | 24.03 |  | 21.59 | 0.06 | 2.38
FORT ROSS-GUALALA | 60 | ETL.6980 |  | ACT | 29.76 |  | 29.61 |  | 0.15
FORT SEWARD TAP | 60 | ETL.6222 |  | ACT | 7.69 |  | 2.9 | 0.03 | 4.76
FRENCH MEADOWS-MIDDLE FORK | 60 | ETL.6870 |  | ACT | 13.15 | 13.15 |  |  | 0
FRESH EXPRESS TAP | 60 | ETL.7901 |  | ACT | 0.56 |  |  |  | 0.56
FRESNO COGEN (AGRICO) TAP | 70 | ETL.8741 |  | ACT | 3.17 |  |  |  | 3.17
FRIANT-COPPERMINE | 70 | ETL.8660 |  | ACT | 8.3 |  |  |  | 8.3
FRITO LAY TAP | 115 | ETL.2602 |  | ACT | 0.51 |  |  |  | 0.51
FROGTOWN #1 TAP | 115 | ETL.3831 |  | ACT | 0.12 |  | 0.12 |  | 0
FROGTOWN #2 TAP | 115 | ETL.3843 |  | ACT | 0.11 |  | 0.11 |  | 0
FRUITLAND TAP | 60 | ETL.6221 |  | ACT | 4.26 |  | 3.85 |  | 0.41
FRUITVALE TAP | 70 | ETL.8881 |  | ACT | 0.12 |  |  |  | 0.12
FULTON JCT-VACA | 115 | ETL.1590 |  | ACT | 11.93 |  | 2.83 | 0.13 | 8.97
FULTON-CALISTOGA | 60 | ETL.6880 |  | ACT | 50.35 | 41.39 | 2.9 |  | 6.06
FULTON-HOPLAND | 60 | ETL.6890 |  | ACT | 49.29 | 7.51 | 26.29 |  | 15.49
FULTON-IGNACIO #1 | 230 | ETL.4680 |  | ACT | 40.73 | 14.88 | 7.55 |  | 18.3
FULTON-LAKEVILLE | 230 | ETL.4950 |  | ACT | 25.51 | 15.24 | 6.43 |  | 3.84
FULTON-LAKEVILLE-IGNACIO | 230 | ETL.2823 |  | IDL | 1.59 | 0.44 | 0.54 |  | 0.61 | Idle Section
FULTON-MOLINO-COTATI | 60 | ETL.6910 |  | ACT | 20.52 |  | 1.77 |  | 18.75
FULTON-PUEBLO | 115 | ETL.1600 |  | ACT | 59.95 | 18.66 | 18.92 | 0.05 | 22.32
FULTON-SANTA ROSA #1 | 115 | ETL.1620 |  | ACT | 6.69 |  |  |  | 6.69
FULTON-SANTA ROSA #2 | 115 | ETL.1630 |  | ACT | 6.29 |  |  |  | 6.29
FULTON-WINDSOR | 60 | ETL.1024 |  | ACT | 6.59 |  |  |  | 6.59
GALLO-CRESSEY | 115 | ETL.1036 |  | ACT | 14.42 |  |  |  | 14.42
GALLO-LIVINGSTON | 115 | ETL.1032 |  | ACT | 4.2 |  |  |  | 4.2
GARBERVILLE-LAYTONVILLE | 60 | ETL.8365 |  | ACT | 39.98 |  | 10.28 |  | 29.7
GARCIA TAP | 60 | ETL.8411 |  | ACT | 3.04 |  | 3.04 |  | 0
GARDNER TAP | 70 | ETL.8971 |  | ACT | 3.77 |  |  |  | 3.77
GATES BK-12 | 230 | ETL.1222 |  | ACT | 0.29 |  |  |  | 0.29
GATES-ARCO | 230 | ETL.4690 |  | ACT | 35.02 |  |  |  | 35.02
GATES-CASTANEA | 230 | ETL.1223 |  | ACT | 0.42 |  |  |  | 0.42
GATES-COALINGA #2 | 70 | ETL.8680 |  | ACT | 17.33 |  |  |  | 17.33
GATES-FIFTH STANDARD SOLAR PV | 230 | ETL.1313 | PGE | ACT | 0.3 |  |  |  | 0.3
GATES-HURON | 70 | ETL.8690 |  | ACT | 4.5 |  |  |  | 4.5
GATES-JAYNE SW STA | 70 | ETL.8652 |  | ACT | 0.68 |  |  |  | 0.68
GATES-MIDWAY | 230 | ETL.4891 |  | ACT | 63.68 |  |  |  | 63.68
GATES-MIDWAY | 500 | ETL.5990 |  | ACT | 63.78 |  |  |  | 63.78
GATES-MUSTANG SW STA #1 | 230 | ETL.2604 |  | ACT | 12.96 |  |  |  | 12.96
GATES-MUSTANG SW STA #2 | 230 | ETL.2605 |  | ACT | 12.99 |  |  |  | 12.99
GATES-PANOCHE #1 | 230 | ETL.4720 |  | ACT | 43.59 |  |  |  | 43.59
GATES-PANOCHE #2 | 230 | ETL.4730 |  | ACT | 43.57 |  |  |  | 43.57
GATES-TULARE LAKE | 70 | ETL.8700 |  | ACT | 18.34 |  |  |  | 18.34
GEYSERS #11-EAGLE ROCK | 115 | ETL.4391 |  | ACT | 0.64 | 0.64 |  |  | 0
GEYSERS #12-FULTON | 230 | ETL.4750 |  | ACT | 24.09 | 18.9 | 3.57 |  | 1.62
GEYSERS #13 TAP | 230 | ETL.4781 |  | ACT | 2.06 | 2.06 |  |  | 0
GEYSERS #16 TAP | 230 | ETL.4760 |  | ACT | 1.29 | 1.29 |  |  | 0
GEYSERS #17-FULTON | 230 | ETL.4770 |  | ACT | 25.8 | 20.68 | 3.56 |  | 1.56
GEYSERS #17-FULTON | 230 | ETL.4770 |  | IDL | 0.33 | 0.33 |  |  | 0 | Idle Section
GEYSERS #18 TAP | 230 | ETL.4784 |  | ACT | 0.74 | 0.74 |  |  | 0
GEYSERS #20 TAP | 230 | ETL.4783 |  | ACT | 0.03 | 0.03 |  |  | 0
GEYSERS #3-CLOVERDALE | 115 | ETL.1650 |  | ACT | 12.06 | 10.88 | 0.02 |  | 1.16
GEYSERS #3-EAGLE ROCK | 115 | ETL.1660 |  | ACT | 1.77 | 1.77 |  |  | 0
GEYSERS #5-GEYSERS #3 | 115 | ETL.1670 |  | ACT | 0.49 | 0.49 |  |  | 0
GEYSERS #7-EAGLE ROCK | 115 | ETL.1680 | PGE | ACT | 1.16 | 1.16 |  |  | 0
GEYSERS #9-LAKEVILLE | 230 | ETL.4780 |  | ACT | 41.08 | 31.96 | 7.03 |  | 2.09
GIFFEN TAP | 70 | ETL.8985 |  | ACT | 4.95 |  |  |  | 4.95
GIFFEN-BURFORD | 70 | ETL.1352 |  | ACT | 0.04 |  |  |  | 0.04
GILL RANCH TAP | 115 | ETL.1742 |  | ACT | 9.15 |  |  |  | 9.15
GILROY ENERGY TAP | 115 | ETL.2151 |  | ACT | 0.28 |  |  |  | 0.28
GISH TAP | 115 | ETL.4031 |  | IDL | 0.96 |  |  |  | 0.96
GLENN #1 | 60 | ETL.6920 |  | ACT | 33.38 |  |  |  | 33.38
GLENN #2 | 60 | ETL.6930 |  | ACT | 34.68 |  |  | 0.26 | 34.42
GLENN #3 | 60 | ETL.6940 |  | ACT | 28.56 |  |  |  | 28.56
GLENN #4 | 60 | ETL.8424 |  | ACT | 12.48 |  |  |  | 12.48
GLENN #5 | 60 | ETL.8427 |  | ACT | 7.41 |  |  |  | 7.41
GLENN-DELEVAN | 230 | ETL.7042 |  | ACT | 37.44 |  |  |  | 37.44
GOLD HILL #1 | 60 | ETL.6950 |  | ACT | 32.36 | 8.54 | 13.08 |  | 10.74
GOLD HILL-BELLOTA-LOCKEFORD | 115 | ETL.1690 |  | ACT | 86.17 |  |  |  | 86.17
GOLD HILL-BELLOTA-LOCKEFORD | 115 | ETL.1690 |  | IDL | 1.1 |  |  |  | 1.1
GOLD HILL-CLARKSVILLE | 115 | ETL.9430 |  | ACT | 5.77 |  |  |  | 5.77
GOLD HILL-EIGHT MILE ROAD | 230 | ETL.4800 |  | ACT | 48.8 |  |  |  | 48.8
GOLD HILL-LODI STIG | 230 | ETL.4810 |  | ACT | 46.67 |  |  |  | 46.67
GOLDEN VALLEY TAP | 115 | ETL.2603 |  | ACT | 1.59 |  |  |  | 1.59
GOLDTREE TAP | 115 | ETL.2821 |  | ACT | 2.3 |  | 1.05 |  | 1.25
GONZALES #1 TAP | 60 | ETL.8011 |  | ACT | 0.19 |  |  |  | 0.19
GONZALES #2 TAP | 60 | ETL.8021 |  | ACT | 0.3 |  |  |  | 0.3
GRANITE ROCK TAP | 60 | ETL.8311 |  | ACT | 2.39 |  | 2.35 |  | 0.04
GRANT-EASTSHORE #1 | 115 | ETL.1700 |  | ACT | 4.34 |  |  |  | 4.34
GRANT-EASTSHORE #2 | 115 | ETL.1701 |  | ACT | 4.21 |  |  |  | 4.21
GRAPEVINE TAP | 70 | ETL.9252 |  | ACT | 0.14 |  | 0.14 |  | 0
GREEN VALLEY-CAMP EVERS | 115 | ETL.1710 |  | ACT | 18.56 | 10.39 | 3.03 |  | 5.14
GREEN VALLEY-LLAGAS | 115 | ETL.1720 |  | ACT | 24.74 | 6.14 | 8.41 |  | 10.19
GREEN VALLEY-PAUL SWEET | 115 | ETL.1730 |  | ACT | 15.82 | 7.14 | 4.24 |  | 4.44
GREEN VALLEY-WATSONVILLE | 60 | ETL.6970 |  | ACT | 4.79 |  |  |  | 4.79
GREENLEAF #1 TAP | 115 | ETL.1101 |  | ACT | 4.85 |  |  |  | 4.85
GREENLEAF #2 TAP | 60 | ETL.7761 |  | ACT | 0.62 |  |  |  | 0.62
GREGG-ASHLAN | 230 | ETL.4820 |  | ACT | 7 |  |  |  | 7
GREGG-HERNDON #1 | 230 | ETL.4830 |  | ACT | 0.6 |  |  |  | 0.6
GREGG-HERNDON #2 | 230 | ETL.4840 |  | ACT | 0.63 |  |  |  | 0.63
GRONEMEYER TAP | 60 | ETL.7471 |  | ACT | 0.83 |  |  |  | 0.83
GUARDIAN #1 TAP | 115 | ETL.2301 |  | ACT | 0.75 |  |  |  | 0.75
GUARDIAN #2 TAP | 115 | ETL.2292 |  | ACT | 0.13 |  |  |  | 0.13
GUERNSEY-HENRIETTA | 70 | ETL.8720 |  | ACT | 18.44 |  |  |  | 18.44
GUSTINE #1 TAP | 60 | ETL.7862 |  | ACT | 7.51 |  |  |  | 7.51
GUSTINE #2 TAP | 60 | ETL.7872 |  | ACT | 4.44 |  |  |  | 4.44
GWF HANFORD COGEN TAP | 70 | ETL.8723 |  | IDL | 0.31 |  |  |  | 0.31
GWF-HENRIETTA | 70 | ETL.8774 |  | ACT | 0.12 |  |  |  | 0.12
GWF-KINGSBURG | 115 | ETL.1743 |  | ACT | 21.64 |  |  |  | 21.64
H-P #3 | 115 | ETL.1555 |  | ACT | 0.17 |  |  |  | 0.17
HAAS-MCCALL | 230 | ETL.4850 |  | ACT | 44.21 |  | 24.67 | 0.27 | 19.27
HAAS-WOODCHUCK | 0 | ETL.8730 |  | IDL | 6.79 |  | 3.79 | 0.94 | 2.06 | Idle Section
HALSEY-PLACER | 60 | ETL.6990 |  | ACT | 4.94 |  | 1.58 | 0.25 | 3.11
HAMILTON BRANCH-CHESTER | 60 | ETL.7000 |  | ACT | 12.27 |  | 10.09 |  | 2.18
HAMMER-COUNTRY CLUB | 60 | ETL.7010 |  | ACT | 8.82 |  |  |  | 8.82
HARDWICK TAP | 70 | ETL.8911 |  | ACT | 2.74 |  |  |  | 2.74
HARRINGTON TAP | 60 | ETL.6581 |  | ACT | 0.53 |  |  |  | 0.53
HARTLEY-CLEARLAKE | 60 | ETL.7515 |  | ACT | 6.62 |  | 3.14 |  | 3.48
HAT CREEK #1-PIT #1 | 60 | ETL.7020 |  | ACT | 6.06 |  | 6.06 |  | 0
HAT CREEK #1-WESTWOOD | 60 | ETL.7030 |  | ACT | 55.63 |  | 46.54 | 1.82 | 7.27
HEADGATE TAP | 60 | ETL.6941 |  | ACT | 0.97 |  |  |  | 0.97
HEALDSBURG #1 TAP | 60 | ETL.6892 |  | ACT | 0.25 |  |  |  | 0.25
HEALDSBURG #2 TAP | 60 | ETL.6902 |  | ACT | 0.16 |  |  |  | 0.16
HEINZ TAP (12KV) | 115 | ETL.2193 |  | IDL | 0.78 |  |  |  | 0.78
HELM-CRESCENT SW STA | 70 | ETL.8750 |  | ACT | 4.92 |  |  |  | 4.92
HELM-KERMAN | 70 | ETL.8740 |  | ACT | 13.25 |  |  |  | 13.25
HELM-MCCALL | 230 | ETL.4860 |  | ACT | 30.84 |  |  |  | 30.84
HELM-STROUD | 70 | ETL.8760 |  | ACT | 7.43 |  |  |  | 7.43
HELMS-GREGG #1 | 230 | ETL.4870 | POWERGEN | ACT | 60.67 |  | 25.11 | 5.05 | 30.51
HELMS-GREGG #2 | 230 | ETL.4880 | POWERGEN | ACT | 60.68 |  | 25.12 | 5.25 | 30.31
HENRIETTA-AMERICAN KINGS | 70 | ETL.1243 | PGE | ACT | 0.21 |  |  |  | 0.21
HENRIETTA-KENT SW STA | 70 | ETL.8791 |  | ACT | 1.47 |  |  |  | 1.47
HENRIETTA-LEMOORE | 70 | ETL.8770 |  | ACT | 9.36 |  |  |  | 9.36
HENRIETTA-LEMOORE NAS | 70 | ETL.8780 |  | ACT | 1.75 |  |  |  | 1.75
HENRIETTA-LEPRINO SW STA | 115 | ETL.1737 |  | ACT | 6.03 |  |  |  | 6.03
HERDLYN-BALFOUR | 60 | ETL.7050 |  | ACT | 16.33 |  |  |  | 16.33
HERDLYN-BALFOUR | 60 | ETL.7050 |  | IDL | 4.17 |  |  |  | 4.17
HERDLYN-TRACY | 70 | ETL.8800 |  | ACT | 2.06 |  |  |  | 2.06
HERNDON-ASHLAN | 230 | ETL.4890 |  | ACT | 6.39 |  |  |  | 6.39
HERNDON-BARTON | 115 | ETL.1750 |  | ACT | 12.69 |  |  |  | 12.69
HERNDON-BULLARD #1 | 115 | ETL.1760 |  | ACT | 11.44 |  |  |  | 11.44
HERNDON-BULLARD #2 | 115 | ETL.1770 |  | ACT | 11.43 |  |  |  | 11.43
HERNDON-KEARNEY | 230 | ETL.4900 |  | ACT | 10.83 |  |  |  | 10.83
HERNDON-MANCHESTER | 115 | ETL.1780 |  | ACT | 9.29 |  |  |  | 9.29
HERNDON-WOODWARD | 115 | ETL.1790 |  | ACT | 13.04 |  |  |  | 13.04
HICKS-METCALF | 230 | ETL.4910 |  | ACT | 9.07 |  | 3.38 | 0 | 5.69
HIGGINS-BELL | 115 | ETL.1412 |  | ACT | 18.77 |  | 15.04 | 1 | 2.73
HILLSDALE JCT-HALF MOON BAY | 60 | ETL.7060 |  | ACT | 6.81 | 1.42 | 3.25 |  | 2.14
HONCUT TAP | 115 | ETL.3201 |  | ACT | 1.65 |  |  |  | 1.65
HOWLAND ROAD TAP | 115 | ETL.2191 |  | ACT | 0.9 |  |  |  | 0.9
HUMBOLDT #1 | 60 | ETL.7113 |  | ACT | 11.08 |  |  | 0.03 | 11.05
HUMBOLDT BAY-EUREKA | 60 | ETL.7070 |  | ACT | 5.61 |  |  |  | 5.61
HUMBOLDT BAY-HUMBOLDT #1 | 60 | ETL.7080 |  | ACT | 8.41 |  |  |  | 8.41
HUMBOLDT BAY-HUMBOLDT #1 | 115 | ETL.1800 |  | ACT | 6.31 |  | 2.47 | 0.1 | 3.74
HUMBOLDT BAY-HUMBOLDT #2 | 60 | ETL.7090 |  | ACT | 6.5 |  | 2.46 | 0.11 | 3.93
HUMBOLDT BAY-RIO DELL JCT | 60 | ETL.7100 |  | ACT | 18.41 |  | 1.99 |  | 16.42
HUMBOLDT-BRIDGEVILLE | 115 | ETL.1810 |  | ACT | 30.28 |  | 7.15 | 0.32 | 22.81
HUMBOLDT-EUREKA | 60 | ETL.7120 |  | ACT | 4.74 |  |  |  | 4.74
HUMBOLDT-MAPLE CREEK | 60 | ETL.7130 |  | ACT | 14.09 |  | 8 |  | 6.09
HUMBOLDT-TRINITY | 115 | ETL.1820 |  | ACT | 68.57 |  | 63.09 |  | 5.48
IBM BAILEY AVE TAP | 115 | ETL.2491 |  | ACT | 2 |  |  |  | 2
IBM HARRY RD #1 TAP | 115 | ETL.2501 |  | ACT | 0.58 |  | 0.58 |  | 0
IBM HARRY RD #2 TAP | 115 | ETL.2481 |  | ACT | 0.58 |  | 0.58 |  | 0
IGNACIO-ALTO | 60 | ETL.7150 |  | ACT | 17.79 | 1.01 | 3.06 |  | 13.72
IGNACIO-ALTO-SAUSALITO #1 | 60 | ETL.7160 |  | ACT | 17.95 |  | 4.85 | 0 | 13.1
IGNACIO-ALTO-SAUSALITO #2 | 60 | ETL.7170 |  | ACT | 17.95 |  | 4.82 |  | 13.13
IGNACIO-BOLINAS #1 | 60 | ETL.7140 |  | ACT | 15.02 | 10.25 | 4.65 |  | 0.12
IGNACIO-BOLINAS #2 | 60 | ETL.7180 |  | ACT | 28.21 | 12.46 | 13.66 |  | 2.09
IGNACIO-LAS GALLINAS | 115 | ETL.1860 |  | ACT | 4.16 |  | 0.08 |  | 4.08
IGNACIO-MARE ISLAND #1 | 115 | ETL.1830 |  | ACT | 39.46 |  |  |  | 39.46
IGNACIO-MARE ISLAND #2 | 115 | ETL.1840 |  | ACT | 43.08 |  |  |  | 43.08
IGNACIO-SAN RAFAEL #1 | 115 | ETL.1850 |  | ACT | 11.54 | 0.62 | 2.45 |  | 8.47
IGNACIO-SOBRANTE | 230 | ETL.4920 |  | ACT | 42.49 |  | 11.94 |  | 30.55
IGNACIO-STAFFORD | 60 | ETL.1042 |  | ACT | 6.13 |  | 0.6 |  | 5.53
IMHOFF TAP | 115 | ETL.3322 |  | ACT | 1.43 |  |  |  | 1.43
INDIAN FLAT-YOSEMITE | 70 | ETL.1112 |  | ACT | 4.87 |  | 4.87 |  | 0
INDUSTRIAL TAP | 60 | ETL.7441 |  | ACT | 0.97 |  |  |  | 0.97
INGRAM CREEK TAP | 115 | ETL.4001 |  | ACT | 0.5 |  |  |  | 0.5
IONE TAP | 60 | ETL.8253 |  | ACT | 4.09 |  | 3 |  | 1.09
IUKA TAP | 60 | ETL.8281 |  | ACT | 0.49 |  |  |  | 0.49
JAMESON CANYON PUMPING PLANT TAP | 115 | ETL.1833 |  | ACT | 0.19 |  |  |  | 0.19
JANES CREEK TAP | 60 | ETL.6805 |  | ACT | 1.78 |  |  | 0.04 | 1.74
JARVIS-CRYOGENICS | 115 | ETL.1870 |  | IDL | 0.03 |  |  |  | 0.03
JAYNE SW STA-COALINGA | 70 | ETL.8670 |  | ACT | 12.25 |  |  |  | 12.25
JEFFERSON #1 | 60 | ETL.6831 |  | ACT | 8.97 |  | 2.31 |  | 6.66
JEFFERSON-HILLSDALE JCT | 60 | ETL.7190 |  | ACT | 14.78 |  | 2.3 |  | 12.48
JEFFERSON-LAS PULGAS | 60 | ETL.7200 |  | ACT | 5.99 |  | 0.11 |  | 5.88
JEFFERSON-MARTIN | 230 | ETL.5710 |  | ACT | 3.3 |  | 1.04 |  | 2.26
JEFFERSON-STANFORD | 60 | ETL.7220 |  | ACT | 7.57 |  | 2.53 |  | 5.04
JESSUP TAP | 115 | ETL.4041 |  | ACT | 0.86 |  | 0.33 |  | 0.53
JOLON TAP | 60 | ETL.7321 |  | ACT | 15.87 |  | 15.42 |  | 0.45
KAMM TAP | 115 | ETL.3253 |  | ACT | 0.51 |  |  |  | 0.51
KANAKA TAP | 115 | ETL.4223 |  | ACT | 2.59 | 0.71 | 1.87 |  | 0.01
KANSAS PV-LEPRINO SW STA | 115 | ETL.1739 |  | ACT | 0.17 |  |  |  | 0.17
KASSON #1 | 60 | ETL.7230 |  | ACT | 0.19 |  |  |  | 0.19
KASSON-BANTA #1 | 60 | ETL.7240 |  | ACT | 1.05 |  |  |  | 1.05
KASSON-CARBONA | 60 | ETL.7231 |  | ACT | 7.32 |  |  |  | 7.32
KASSON-LOUISE | 60 | ETL.7250 |  | ACT | 9.12 |  |  |  | 9.12
KEARNEY ALTERNATE TIE | 70 | ETL.9380 |  | ACT | 0.3 |  |  |  | 0.3
KEARNEY TIE | 70 | ETL.9370 |  | ACT | 0.15 |  |  |  | 0.15
KEARNEY-BIOLA | 70 | ETL.8810 |  | ACT | 19.15 |  |  |  | 19.15
KEARNEY-BOWLES | 70 | ETL.8820 |  | ACT | 9.29 |  |  |  | 9.29
KEARNEY-CARUTHERS | 70 | ETL.8830 |  | ACT | 12.05 |  |  |  | 12.05
KEARNEY-KERMAN | 70 | ETL.8840 |  | ACT | 10.98 |  |  |  | 10.98
KELLEY TAP | 70 | ETL.9293 |  | ACT | 2.79 |  |  |  | 2.79
KELSO-TESLA | 230 | ETL.4930 |  | ACT | 7.95 |  |  |  | 7.95
KENT SW STA-ALMOND PV | 70 | ETL.1485 |  | ACT | 0.48 |  |  |  | 0.48
KENT SW STA-TULARE LAKE | 70 | ETL.8790 |  | ACT | 15.93 |  |  |  | 15.93
KERCKHOFF #1-KERCKHOFF #2 | 115 | ETL.1880 |  | ACT | 1.58 |  | 1.58 |  | 0
KERCKHOFF-CLOVIS-SANGER #1 | 115 | ETL.1890 |  | ACT | 36.93 |  | 7.85 |  | 29.08
KERCKHOFF-CLOVIS-SANGER #2 | 115 | ETL.1900 |  | ACT | 32.08 |  | 7.85 |  | 24.23
KERN CANYON-MAGUNDEN-WEEDPATCH | 70 | ETL.8850 |  | ACT | 20.68 |  |  |  | 20.68
KERN OIL-DEXZEL | 115 | ETL.1910 |  | ACT | 0.44 |  |  |  | 0.44
KERN OIL-MT POSO | 70 | ETL.1212 |  | IDL | 1.08 |  |  |  | 1.08
KERN OIL-WITCO | 115 | ETL.1920 |  | ACT | 4.2 |  |  |  | 4.2
KERN-BAKERSFIELD | 230 | ETL.5151 |  | ACT | 7.04 |  |  |  | 7.04
KERN-FRUITVALE | 70 | ETL.8860 |  | ACT | 0.16 |  |  |  | 0.16
KERN-KERN FRONT | 115 | ETL.1930 |  | ACT | 12.47 |  |  |  | 12.47
KERN-KERN OIL-FAMOSO | 70 | ETL.8870 |  | ACT | 19.67 |  |  |  | 19.67
KERN-KERN OIL-FAMOSO | 70 | ETL.8870 |  | IDL | 6.53 |  |  |  | 6.53
KERN-LIVE OAK | 115 | ETL.1960 |  | ACT | 10.83 |  |  |  | 10.83
KERN-MAGUNDEN | 70 | ETL.8880 |  | ACT | 17.34 |  |  |  | 17.34
KERN-MAGUNDEN-WITCO | 115 | ETL.1970 |  | ACT | 19.57 |  |  |  | 19.57
KERN-OLD RIVER #1 | 70 | ETL.8890 |  | ACT | 11.97 |  |  |  | 11.97
KERN-OLD RIVER #2 | 70 | ETL.8900 |  | ACT | 26.33 |  |  |  | 26.33
KERN-ROSEDALE | 115 | ETL.1980 |  | ACT | 1.77 |  |  |  | 1.77
KERN-STOCKDALE #1 | 230 | ETL.5152 |  | ACT | 6.35 |  |  |  | 6.35
KERN-STOCKDALE #2 | 230 | ETL.5161 |  | ACT | 6.32 |  |  |  | 6.32
KERN-STOCKDALE-LAMONT #1 | 115 | ETL.1990 |  | ACT | 19.66 |  |  |  | 19.66
KERN-STOCKDALE-LAMONT #1 (21KV) | 115 | ETL.1990 |  | IDL | 3.71 |  |  |  | 3.71
KERN-STOCKDALE-LAMONT #2 | 115 | ETL.1940 |  | ACT | 18.23 |  |  |  | 18.23
KERN-WESTPARK #1 | 115 | ETL.2000 |  | ACT | 3.83 |  |  |  | 3.83
KERN-WESTPARK #2 | 115 | ETL.2010 |  | ACT | 3.81 |  |  |  | 3.81
KERNWATER TAP | 115 | ETL.1971 |  | ACT | 0.67 |  |  |  | 0.67
KESWICK-CASCADE | 60 | ETL.7260 |  | ACT | 9.35 | 0.56 | 8.46 |  | 0.33
KESWICK-TRINITY | 60 | ETL.7270 |  | ACT | 30.4 | 5.47 | 23.62 |  | 1.31
KETTLEMAN HILLS TAP | 70 | ETL.8701 |  | ACT | 1.02 |  |  |  | 1.02
KIFER-FMC | 115 | ETL.2020 |  | ACT | 6.07 |  |  |  | 6.07
KILARC-CEDAR CREEK | 60 | ETL.7290 |  | ACT | 13.33 | 13.33 |  |  | 0
KILARC-DESCHUTES | 60 | ETL.7300 |  | ACT | 23.41 | 0.67 | 19.94 |  | 2.8
KILARC-VOLTA TIE | 60 | ETL.7310 |  | ACT | 1.93 |  | 0.66 |  | 1.27
KING CITY-COBURN #1 | 60 | ETL.7320 |  | ACT | 21.75 |  |  |  | 21.75
KING CITY-COBURN #2 | 60 | ETL.7330 |  | ACT | 15.76 |  |  |  | 15.76
KINGS RIVER-SANGER-REEDLEY | 115 | ETL.2030 |  | ACT | 43.37 |  | 14.48 | 0.12 | 28.77
KINGSBURG COGEN TAP | 115 | ETL.2291 |  | ACT | 1.22 |  |  |  | 1.22
KINGSBURG-CORCORAN #1 | 115 | ETL.2040 |  | ACT | 27.46 |  |  |  | 27.46
KINGSBURG-LEMOORE | 70 | ETL.8910 |  | ACT | 27.57 |  |  |  | 27.57
KINGSBURG-WAUKENA SW STA | 115 | ETL.2050 |  | ACT | 25.24 |  |  |  | 25.24
KM GREEN TAP | 115 | ETL.3505 |  | ACT | 1.6 |  | 1.6 |  | 0
KONOCTI-EAGLE ROCK | 60 | ETL.6861 |  | ACT | 9.66 | 7.53 | 0.23 |  | 1.9
KONOCTI-MIDDLETOWN | 60 | ETL.6380 |  | ACT | 19.87 | 0.87 | 15.42 | 0.06 | 3.52
KYOHO TAP | 115 | ETL.3891 |  | ACT | 2.2 |  |  |  | 2.2
LAGUNA TAP | 60 | ETL.6912 |  | ACT | 1.68 |  |  |  | 1.68
LAGUNITAS TAP | 60 | ETL.8312 |  | ACT | 0.56 |  |  |  | 0.56
LAKEVILLE #1 | 60 | ETL.7360 |  | ACT | 11.15 | 1.16 | 7.42 |  | 2.57
LAKEVILLE #2 | 60 | ETL.7340 |  | ACT | 21.62 |  | 6.2 |  | 15.42
LAKEVILLE-IGNACIO #1 | 230 | ETL.4940 |  | ACT | 15.49 |  | 0.89 |  | 14.6
LAKEVILLE-IGNACIO #2 | 230 | ETL.3745 |  | ACT | 14.54 |  | 0.71 |  | 13.83
LAKEVILLE-PETALUMA C | 60 | ETL.7350 |  | ACT | 5.36 |  |  |  | 5.36
LAKEVILLE-SOBRANTE #2 | 230 | ETL.4960 |  | ACT | 47.89 |  | 11.02 |  | 36.87
LAKEVILLE-SONOMA #1 | 115 | ETL.2063 |  | ACT | 6.68 |  | 2.54 |  | 4.14
LAKEVILLE-SONOMA #2 | 115 | ETL.2070 |  | ACT | 7.18 |  | 2.54 |  | 4.64
LAKEVILLE-TULUCAY | 230 | ETL.4970 |  | ACT | 17.22 |  | 1.8 |  | 15.42
LAKEWOOD-CLAYTON | 115 | ETL.2082 |  | ACT | 5.52 |  | 1.13 |  | 4.39
LAKEWOOD-MEADOW LANE-CLAYTON | 115 | ETL.2080 |  | ACT | 9.55 |  | 1.13 |  | 8.42
LAKEWOOD-MEADOW LANE-CLAYTON | 115 | ETL.2080 |  | IDL | 0.06 |  |  |  | 0.06
LAMBIE SW STA-BIRDS LANDING SW STA | 230 | ETL.5820 |  | ACT | 7.04 |  |  |  | 7.04
LAMMERS-KASSON | 115 | ETL.3972 |  | ACT | 8.23 |  |  |  | 8.23
LAMONT-GRIMMWAY MALAGA | 115 | ETL.1942 |  | ACT | 3.55 |  |  |  | 3.55
LAS AGUILAS SW STA-PANOCHE #1 | 230 | ETL.1003 |  | ACT | 17.44 |  |  |  | 17.44
LAS AGUILAS SW STA-PANOCHE #2 | 230 | ETL.1002 |  | ACT | 17.44 |  |  |  | 17.44
LAS GALLINAS-SAN RAFAEL | 115 | ETL.1103 |  | ACT | 4.46 |  |  |  | 4.46
LAS PALMAS TAP | 115 | ETL.2181 |  | ACT | 0.85 |  |  |  | 0.85
LAS PERILLAS TAP | 70 | ETL.8463 |  | ACT | 0.39 |  |  |  | 0.39
LAS PLUMAS TAP | 115 | ETL.2653 |  | ACT | 0.48 |  |  |  | 0.48
LAS POSITAS-NEWARK | 230 | ETL.4980 |  | ACT | 20.93 |  | 4.34 | 0.51 | 16.08
LAS POSITAS-VASCO | 60 | ETL.7370 |  | ACT | 1.5 |  |  |  | 1.5
LAURELES-OTTER | 60 | ETL.7380 |  | ACT | 15.56 | 12.23 | 3.12 |  | 0.21
LAWRENCE-MONTA VISTA | 115 | ETL.2090 |  | ACT | 8.86 |  |  |  | 8.86
LAYTONVILLE-COVELO | 60 | ETL.7390 |  | ACT | 16.09 |  | 6.59 | 0.34 | 9.16
LAYTONVILLE-WILLITS | 60 | ETL.8360 |  | ACT | 22.95 |  | 15.23 |  | 7.72
LE GRAND-CHOWCHILLA | 115 | ETL.2110 |  | ACT | 10.94 |  |  |  | 10.94
LE GRAND-DAIRYLAND | 115 | ETL.2100 |  | ACT | 11.4 |  |  |  | 11.4
LEE TAP | 60 | ETL.7461 |  | IDL | 2.47 |  |  |  | 2.47
LEPRINO FOODS (TRACY) TAP | 115 | ETL.1283 |  | ACT | 0.02 |  |  |  | 0.02
LEPRINO FOODS-LEPRINO SW STA | 115 | ETL.1741 |  | ACT | 6.41 |  |  |  | 6.41
LEPRINO SW STA-GWF HANFORD SW STA | 115 | ETL.1740 |  | ACT | 12.4 |  |  |  | 12.4
LEPRINO SW STA-HENRIETTA PV | 115 | ETL.1738 |  | ACT | 0.06 |  |  |  | 0.06
LEPRINO TAP | 70 | ETL.8771 |  | ACT | 0.47 |  |  |  | 0.47
LERDO-FAMOSO | 115 | ETL.2120 |  | ACT | 13.46 |  |  |  | 13.46
LERDO-KERN OIL-7TH STANDARD | 115 | ETL.1950 |  | ACT | 16.36 |  |  |  | 16.36
LINCOLN-PLEASANT GROVE | 115 | ETL.7400 |  | ACT | 7.39 |  |  |  | 7.39
LINDE TAP | 115 | ETL.3302 |  | ACT | 0.62 |  |  |  | 0.62
LIVE OAK TAP | 115 | ETL.2130 |  | ACT | 3.97 |  |  |  | 3.97
LIVE OAK-KERN OIL | 115 | ETL.2140 |  | ACT | 4.4 |  |  |  | 4.4
LIVERMORE-LAS POSITAS | 60 | ETL.7410 |  | ACT | 3.63 |  |  |  | 3.63
LIVINGSTON-LIVINGSTON JCT | 70 | ETL.8920 |  | ACT | 23.36 |  |  |  | 23.36
LLAGAS-GILROY FOODS | 115 | ETL.2150 |  | ACT | 1.98 |  |  |  | 1.98
LLAGAS-HOLLISTER | 115 | ETL.2911 |  | ACT | 19.85 |  |  |  | 19.85
LLAGAS-HOLLISTER | 115 | ETL.2911 |  | IDL | 1.71 |  |  |  | 1.71
LOCKEFORD #1 | 60 | ETL.9461 |  | ACT | 12.91 |  |  |  | 12.91
LOCKEFORD-BELLOTA | 230 | ETL.4990 |  | ACT | 12.32 |  |  |  | 12.32
LOCKEFORD-INDUSTRIAL | 60 | ETL.7420 |  | ACT | 6.03 |  |  |  | 6.03
LOCKEFORD-LODI #2 | 60 | ETL.7440 |  | ACT | 9.49 |  |  |  | 9.49
LOCKEFORD-LODI #3 | 60 | ETL.7450 |  | ACT | 15.36 |  |  |  | 15.36
LOCKHEED #1 TAP | 115 | ETL.3051 |  | ACT | 1.71 |  |  |  | 1.71
LOCKHEED #2 TAP | 115 | ETL.2981 |  | ACT | 1.3 |  |  |  | 1.3
LODI STIG-EIGHT MILE ROAD | 230 | ETL.5001 |  | ACT | 2.18 |  |  |  | 2.18
LODI-INDUSTRIAL | 60 | ETL.6755 |  | ACT | 0.98 |  |  |  | 0.98
LOGAN CREEK-DELEVAN | 230 | ETL.6331 |  | ACT | 12.35 |  |  |  | 12.35
LONE STAR TAP | 60 | ETL.6231 |  | ACT | 1.18 |  | 0.76 |  | 0.42
LONE TREE-CAYETANO | 230 | ETL.6160 |  | ACT | 15.4 | 0.86 | 10.68 |  | 3.86
LOS BANOS-DOS AMIGOS | 230 | ETL.5020 |  | ACT | 14.31 |  |  |  | 14.31
LOS BANOS-GATES #1 | 500 | ETL.6000 |  | ACT | 80.85 |  |  |  | 80.85
LOS BANOS-LIVINGSTON JCT-CANAL | 70 | ETL.8940 |  | ACT | 14.34 |  |  |  | 14.34
LOS BANOS-MERCY SPRINGS SW STA | 70 | ETL.8929 |  | ACT | 14.7 |  |  |  | 14.7
LOS BANOS-MIDWAY #2 | 500 | ETL.6010 |  | ACT | 144.6 |  |  |  | 144.6
LOS BANOS-O'NEILL PGP | 70 | ETL.8950 |  | ACT | 3.87 |  |  |  | 3.87
LOS BANOS-PACHECO | 70 | ETL.8960 |  | ACT | 16.31 |  |  |  | 16.31
LOS BANOS-PACHECO | 70 | ETL.8960 |  | IDL | 4.46 |  |  |  | 4.46
LOS BANOS-PADRE FLAT SW STA | 230 | ETL.1092 |  | ACT | 3.67 |  |  |  | 3.67
LOS BANOS-PANOCHE #2 | 230 | ETL.5040 |  | ACT | 37.13 |  |  |  | 37.13
LOS BANOS-QUINTO SW STA | 230 | ETL.5071 |  | ACT | 12.06 |  |  |  | 12.06
LOS BANOS-SAN LUIS PUMPS #1 | 230 | ETL.5050 |  | ACT | 3.43 |  |  |  | 3.43
LOS BANOS-SAN LUIS PUMPS #2 | 230 | ETL.5060 |  | ACT | 3.43 |  |  |  | 3.43
LOS COCHES TAP | 60 | ETL.7331 |  | ACT | 1.32 |  |  |  | 1.32
LOS ESTEROS-AGNEW | 115 | ETL.2690 |  | ACT | 1.37 |  |  |  | 1.37
LOS ESTEROS-METCALF | 230 | ETL.5353 |  | ACT | 63.25 |  | 51.47 | 0.48 | 11.3
LOS ESTEROS-MONTAGUE | 115 | ETL.2380 |  | ACT | 4.64 |  |  |  | 4.64
LOS ESTEROS-NORTECH | 115 | ETL.4032 |  | ACT | 2 |  |  |  | 2
LOS ESTEROS-TRIMBLE | 115 | ETL.2550 |  | ACT | 3.73 |  |  |  | 3.73
LOST HILLS TAP | 70 | ETL.8451 |  | ACT | 2.89 |  |  |  | 2.89
LOUISIANA PACIFIC (OROVILLE) TAP | 60 | ETL.7732 |  | ACT | 0.16 |  |  |  | 0.16
LOWER LAKE-HOMESTAKE | 115 | ETL.1481 |  | ACT | 16.08 |  | 15.36 |  | 0.72
LP FLAKEBOARD TAP | 60 | ETL.7111 |  | ACT | 0.51 |  |  |  | 0.51
LUCERNE #1 TAP | 115 | ETL.1331 |  | ACT | 0.23 |  | 0.23 |  | 0
LUCERNE #2 TAP | 115 | ETL.2411 |  | ACT | 0.23 |  | 0.23 |  | 0
LYOTH TAP | 60 | ETL.7232 |  | ACT | 1.34 |  |  |  | 1.34
MABURY TAP | 115 | ETL.2651 |  | ACT | 2.81 |  |  |  | 2.81
MADISON-VACA | 115 | ETL.2170 |  | ACT | 22.99 |  | 2.84 | 0.13 | 20.02
MALACHA TAP | 230 | ETL.5910 |  | ACT | 0.12 |  | 0.12 |  | 0
MALAGA-KRCD | 115 | ETL.2294 |  | ACT | 0.99 |  |  |  | 0.99
MALIN-ROUND MTN #2 | 500 | ETL.6020 |  | ACT | 46.9 |  | 46.9 |  | 0
MANCHESTER-AIRWAYS-SANGER | 115 | ETL.2180 |  | ACT | 15.02 |  |  |  | 15.02
MANTECA #1 | 60 | ETL.7460 |  | ACT | 34.52 |  |  |  | 34.52
MANTECA-LOUISE | 60 | ETL.7470 |  | ACT | 12.53 |  |  |  | 12.53
MANTECA-VIERRA | 115 | ETL.2190 |  | ACT | 3.97 |  |  |  | 3.97
MANVILLE TAP | 115 | ETL.1372 |  | ACT | 5.53 |  | 2.73 |  | 2.8
MAPLE CREEK-HOOPA | 60 | ETL.7490 |  | ACT | 29.13 | 13.53 | 11.39 |  | 4.21
MARICOPA-COPUS | 70 | ETL.8851 |  | ACT | 7.86 |  |  |  | 7.86
MARSH TAP | 60 | ETL.7054 |  | ACT | 3.97 |  |  |  | 3.97
MARTIN-DALY CITY #1 | 115 | ETL.2200 |  | ACT | 3.93 |  |  |  | 3.93
MARTIN-DALY CITY #2 | 115 | ETL.2210 |  | ACT | 3.93 |  |  |  | 3.93
MARTIN-EAST GRAND | 115 | ETL.2220 |  | ACT | 3.96 |  |  |  | 3.96
MARTIN-MILLBRAE #1 | 115 | ETL.2230 |  | ACT | 7.28 |  |  |  | 7.28
MARTIN-SF AIRPORT | 115 | ETL.2240 |  | ACT | 5.43 |  |  |  | 5.43
MARTIN-SNEATH LANE | 60 | ETL.7210 |  | ACT | 7.23 |  | 0.79 |  | 6.44
MARTINEZ-SOBRANTE | 115 | ETL.2270 |  | ACT | 16.4 |  | 13.61 |  | 2.79
MCCALL-KINGSBURG #1 | 115 | ETL.2290 |  | ACT | 11.65 |  |  |  | 11.65
MCCALL-KINGSBURG #2 | 115 | ETL.2300 |  | ACT | 11.57 |  |  |  | 11.57
MCCALL-MALAGA | 115 | ETL.2310 |  | ACT | 10.96 |  |  |  | 10.96
MCCALL-REEDLEY | 115 | ETL.2320 |  | ACT | 15.19 |  |  |  | 15.19
MCCALL-SANGER #1 | 115 | ETL.2330 |  | ACT | 9.22 |  |  |  | 9.22
MCCALL-SANGER #2 | 115 | ETL.2340 |  | ACT | 9.21 |  |  |  | 9.21
MCCALL-SANGER #3 | 115 | ETL.2350 |  | ACT | 8.58 |  |  |  | 8.58
MCCALL-WEST FRESNO #2 | 115 | ETL.2370 |  | ACT | 19.61 |  |  |  | 19.61
MCDONALD TAP | 60 | ETL.7053 |  | ACT | 5.88 |  |  |  | 5.88
MCFARLAND TAP | 70 | ETL.9171 |  | ACT | 6 |  |  |  | 6
MCKEE-PIERCY | 115 | ETL.2379 |  | ACT | 7.75 |  |  |  | 7.75
MCSWAIN TAP | 70 | ETL.8991 |  | ACT | 1.38 |  | 0.57 |  | 0.81
MELONES-CURTIS | 115 | ETL.2390 |  | ACT | 14.8 |  | 14.07 |  | 0.73
MELONES-RACETRACK | 115 | ETL.2400 |  | ACT | 10.2 |  | 10.2 |  | 0
MELONES-WILSON | 230 | ETL.5080 |  | ACT | 61.61 |  | 5.23 |  | 56.38
MENDOCINO #1 | 60 | ETL.7530 |  | IDL | 3.99 |  | 3.3 |  | 0.69 | Idle Section
MENDOCINO-HARTLEY | 60 | ETL.7510 |  | ACT | 23.18 |  | 21.78 |  | 1.4
MENDOCINO-PHILO JCT-HOPLAND | 60 | ETL.7520 |  | ACT | 21.87 |  | 16.15 |  | 5.72
MENDOCINO-REDBUD | 115 | ETL.2410 |  | ACT | 34.83 |  | 32.61 |  | 2.22
MENDOCINO-UKIAH | 115 | ETL.2420 |  | ACT | 9.83 |  | 7.49 |  | 2.34
MENDOCINO-WILLITS | 60 | ETL.7540 |  | ACT | 14.52 | 3.77 | 8.33 |  | 2.42
MENDOCINO-WILLITS-FORT BRAGG | 60 | ETL.7550 |  | ACT | 43.81 | 3.78 | 36.76 |  | 3.27
MENDOTA BIOMASS TAP | 70 | ETL.8981 |  | ACT | 3.84 |  |  |  | 3.84
MENDOTA-LITTLE BEAR | 115 | ETL.1494 |  | ACT | 0.04 |  |  |  | 0.04
MENDOTA-NORTH STAR SOLAR | 115 | ETL.2113 |  | ACT | 0.03 |  |  |  | 0.03
MENDOTA-SAN JOAQUIN-HELM | 70 | ETL.8980 |  | ACT | 26.94 |  |  |  | 26.94
MENLO TAP | 60 | ETL.6571 |  | ACT | 0.37 |  |  |  | 0.37
MERCED #1 | 70 | ETL.9000 |  | ACT | 39.89 |  |  |  | 39.89
MERCED FALLS-EXCHEQUER | 70 | ETL.8990 | PGE | ACT | 6.51 |  | 4.34 |  | 2.17
MERCED-MERCED FALLS | 70 | ETL.9010 |  | ACT | 20.92 |  |  |  | 20.92
MERCY SPRINGS SW STA-CANAL-ORO LOMA | 70 | ETL.8930 |  | ACT | 23.31 |  |  |  | 23.31
MESA-CABALLERO STORAGE | 230 | ETL.1433 |  | ACT | 0.2 |  |  |  | 0.2
MESA-DIVIDE #1 | 115 | ETL.2430 |  | ACT | 14.71 |  |  |  | 14.71
MESA-DIVIDE #2 | 115 | ETL.2440 |  | ACT | 14.72 |  |  |  | 14.72
MESA-SANTA MARIA | 115 | ETL.2450 |  | ACT | 4.36 |  | 0.07 |  | 4.29
MESA-SISQUOC | 115 | ETL.2460 |  | ACT | 17.6 |  | 1.05 |  | 16.55
METCALF SUB INTER-TIE 230KV | 230 | 0.1 |  | ACT | 0.21 |  |  |  | 0.21
METCALF SUB INTER-TIE 230KV | 230 | 0.2 |  | ACT | 0.11 |  |  |  | 0.11
METCALF SUB INTER-TIE 230KV | 230 | 0.3 |  | ACT | 0.15 |  |  |  | 0.15
METCALF-COYOTE PUMPING PLANT | 115 | ETL.2470 |  | ACT | 7.86 |  |  |  | 7.86
METCALF-EDENVALE #2 | 115 | ETL.2490 |  | ACT | 5.6 |  | 1.3 |  | 4.3
METCALF-EL PATIO #1 | 115 | ETL.2500 |  | ACT | 14.38 |  | 3.38 |  | 11
METCALF-EL PATIO #2 | 115 | ETL.2510 |  | ACT | 14.41 |  | 3.38 |  | 11.03
METCALF-EVERGREEN #1 | 115 | ETL.2520 |  | ACT | 10.63 |  |  |  | 10.63
METCALF-EVERGREEN #2 | 115 | ETL.2530 |  | ACT | 10.57 |  |  |  | 10.57
METCALF-GREEN VALLEY | 115 | ETL.2540 |  | ACT | 25.27 | 5.75 | 4.59 |  | 14.93
METCALF-HICKS 1 & 2 | 115 | ETL.4317 |  | IDL | 6.47 |  | 2.83 |  | 3.64 | Idle Section
METCALF-MONTA VISTA #3 | 230 | ETL.5091 |  | ACT | 28.59 | 13.12 | 9.59 | 0.01 | 5.87
METCALF-MORGAN HILL | 115 | ETL.2570 |  | ACT | 9.72 |  | 1.2 |  | 8.52
METCALF-MOSS LANDING #1 | 230 | ETL.5100 |  | ACT | 35.76 | 7.17 | 9.86 |  | 18.73
METCALF-MOSS LANDING #2 | 230 | ETL.5110 |  | ACT | 35.76 | 7.17 | 9.87 |  | 18.72
METCALF-SALINAS #2 (12KV) | 115 | ETL.1731 |  | IDL | 5.55 |  |  |  | 5.55
METCALF-SANTA TERESA | 115 | ETL.2480 |  | ACT | 5.4 |  | 1.29 |  | 4.11
MI-WUK-CURTIS | 115 | ETL.1073 |  | ACT | 8.4 | 4.62 | 3.69 |  | 0.09
MIDDLE FORK #1 | 60 | ETL.8405 |  | ACT | 9.45 | 9.45 |  |  | 0
MIDDLE FORK-GOLD HILL | 230 | ETL.5140 |  | ACT | 44.08 | 25.41 | 12.02 |  | 6.65
MIDDLE RIVER TAP | 60 | ETL.7052 |  | ACT | 7.02 |  |  |  | 7.02
MIDSET TAP | 115 | ETL.1581 |  | ACT | 0.72 |  |  |  | 0.72
MIDSUN-MIDWAY | 115 | ETL.2580 |  | ACT | 19.05 |  |  |  | 19.05
MIDWAY-BITTERWATER SW STA #2 | 230 | ETL.1442 |  | ACT | 25.34 |  |  |  | 25.34
MIDWAY-KERN #1 | 230 | ETL.5150 |  | ACT | 41.07 |  |  |  | 41.07
MIDWAY-KERN #3 | 230 | ETL.5160 |  | ACT | 20.74 |  |  |  | 20.74
MIDWAY-KERN #4 | 230 | ETL.5170 |  | ACT | 20.78 |  |  |  | 20.78
MIDWAY-RENFRO-TUPMAN | 115 | ETL.2590 |  | ACT | 22.6 |  |  |  | 22.6
MIDWAY-SANTA MARIA (12KV) | 115 | ETL.9240 |  | IDL | 31.58 | 16.68 | 1.9 |  | 13 | Distribution Transferred
MIDWAY-SANTA MARIA (21KV) | 115 | ETL.9240 |  | IDL | 14.65 |  |  |  | 14.65
MIDWAY-SHAFTER | 115 | ETL.2610 |  | ACT | 13.63 |  |  |  | 13.63
MIDWAY-SUNSET | 230 | ETL.5194 |  | ACT | 0.57 |  |  |  | 0.57
MIDWAY-TAFT | 115 | ETL.2620 |  | ACT | 19.33 |  |  |  | 19.33
MIDWAY-TEMBLOR | 115 | ETL.2630 |  | ACT | 14.7 |  |  |  | 14.7
MIDWAY-TUPMAN-RIO BRAVO-RENFRO | 115 | ETL.2600 |  | ACT | 26.6 |  |  |  | 26.6
MIDWAY-WHEELER RIDGE #1 | 230 | ETL.5190 |  | ACT | 52.68 |  |  |  | 52.68
MIDWAY-WHIRLWIND | 500 | ETL.6030 |  | ACT | 52.77 |  | 8.6 |  | 44.17
MILLBRAE-SAN MATEO #1 | 115 | ETL.2640 |  | ACT | 4.71 |  |  |  | 4.71
MILLBRAE-SNEATH LANE | 60 | ETL.7570 |  | ACT | 6.72 |  | 2.15 |  | 4.57
MILLER #1 TAP | 115 | ETL.3992 |  | ACT | 21.28 |  |  |  | 21.28
MILLER #2 TAP | 115 | ETL.4002 |  | ACT | 12.32 |  |  |  | 12.32
MILPITAS-SWIFT | 115 | ETL.2650 |  | ACT | 8.86 |  |  |  | 8.86
MISSION POWER TAP | 115 | ETL.1651 |  | ACT | 1.93 | 1.93 |  |  | 0
MISSOURI FLAT-GOLD HILL #1 | 115 | ETL.2660 |  | ACT | 19.7 | 5.95 | 4.73 |  | 9.02
MISSOURI FLAT-GOLD HILL #2 | 115 | ETL.2670 |  | ACT | 19.69 | 5.91 | 4.76 |  | 9.02
MOCO TAP | 70 | ETL.9233 |  | ACT | 1.64 |  |  |  | 1.64
MOFFETT FIELD TAP | 115 | ETL.3052 |  | ACT | 0.16 |  |  |  | 0.16
MONTA VISTA-BURNS | 60 | ETL.7590 |  | ACT | 18.07 | 12.46 | 4.53 |  | 1.08
MONTA VISTA-COYOTE SW STA | 230 | ETL.5090 |  | ACT | 27.83 | 13.13 | 9.6 | 0.01 | 5.09
MONTA VISTA-HICKS | 230 | ETL.5210 |  | ACT | 13.21 |  | 0.38 |  | 12.83
MONTA VISTA-JEFFERSON #1 | 230 | ETL.5220 |  | ACT | 19.72 | 6.35 | 10.5 | 0.84 | 2.03
MONTA VISTA-JEFFERSON #2 | 230 | ETL.5230 |  | ACT | 19.73 | 6.36 | 10.5 | 0.82 | 2.05
MONTA VISTA-LOS ALTOS | 60 | ETL.7600 |  | ACT | 7.11 |  |  |  | 7.11
MONTA VISTA-LOS GATOS | 60 | ETL.7610 |  | ACT | 10.88 |  | 1.97 |  | 8.91
MONTA VISTA-PERMANENTE | 60 | ETL.7620 |  | ACT | 1.19 |  | 0.11 |  | 1.08
MONTA VISTA-SARATOGA | 230 | ETL.5240 |  | ACT | 5.49 |  | 0.37 |  | 5.12
MONTA VISTA-WOLFE | 115 | ETL.3870 |  | ACT | 2.72 |  |  |  | 2.72
MONTAGUE-TRIMBLE | 115 | ETL.2560 |  | ACT | 2.07 |  |  |  | 2.07
MONTE RIO-FORT ROSS | 60 | ETL.6979 |  | ACT | 14.3 | 7.21 | 4.73 |  | 2.36
MONTE RIO-FULTON | 60 | ETL.7630 |  | ACT | 22.56 | 7.11 | 0.13 |  | 15.32
MONTEZUMA SW STA-BIRDS LANDING SW STA | 230 | ETL.7973 |  | ACT | 0.54 |  |  |  | 0.54
MONTICELLO PH TAP | 115 | ETL.1602 |  | ACT | 0.62 |  | 0.61 |  | 0.01
MORAGA-CASTRO VALLEY | 230 | ETL.5250 |  | ACT | 14.92 | 7.96 | 3.16 |  | 3.8
MORAGA-CLAREMONT #1 | 115 | ETL.2700 |  | ACT | 5.28 | 5.09 | 0.2 |  | -0.01
MORAGA-CLAREMONT #2 | 115 | ETL.2710 |  | ACT | 5.3 | 5.11 | 0.2 |  | -0.01
MORAGA-LAKEWOOD | 115 | ETL.3741 |  | ACT | 15.02 | 1.2 | 5.44 | 0.08 | 8.3
MORAGA-OAKLAND #1 | 115 | ETL.2720 |  | ACT | 5.04 | 3.28 | 0.79 |  | 0.97
MORAGA-OAKLAND #2 | 115 | ETL.2730 |  | ACT | 5.04 | 3.28 | 0.79 |  | 0.97
MORAGA-OAKLAND #3 | 115 | ETL.2740 |  | ACT | 5.05 | 3.28 | 0.8 |  | 0.97
MORAGA-OAKLAND #4 | 115 | ETL.2750 |  | ACT | 5.05 | 3.28 | 0.8 |  | 0.97
MORAGA-OAKLAND J | 115 | ETL.2760 |  | ACT | 17.67 | 7.71 | 1.85 |  | 8.11
MORAGA-SAN LEANDRO #1 | 115 | ETL.2770 |  | ACT | 11.14 | 7.73 | 1.85 |  | 1.56
MORAGA-SAN LEANDRO #2 | 115 | ETL.2780 |  | ACT | 11.01 | 7.73 | 1.85 |  | 1.43
MORAGA-SAN LEANDRO #3 | 115 | ETL.2790 |  | ACT | 11 | 7.71 | 1.85 |  | 1.44
MORGAN HILL-LLAGAS | 115 | ETL.2800 |  | ACT | 10.84 |  | 4.04 |  | 6.8
MORRO BAY-CALIFORNIA FLATS SW STA | 230 | ETL.5280 |  | ACT | 46.19 | 5.45 | 9.75 |  | 30.99
MORRO BAY-CALIFORNIA FLATS SW STA | 230 | ETL.5280 |  | IDL | 0.03 |  |  |  | 0.03
MORRO BAY-DIABLO | 230 | ETL.5260 |  | ACT | 15.78 | 5.18 | 7.25 |  | 3.35
MORRO BAY-MESA | 230 | ETL.5290 |  | ACT | 35.25 | 2.47 | 26.6 |  | 6.18
MORRO BAY-SAN LUIS OBISPO #1 | 115 | ETL.2810 |  | ACT | 16.01 |  | 11.32 |  | 4.69
MORRO BAY-SAN LUIS OBISPO #2 | 115 | ETL.2820 |  | ACT | 16.02 |  | 11.33 |  | 4.69
MORRO BAY-SOLAR SW STA #1 | 230 | ETL.5300 |  | ACT | 45.55 | 11.87 | 24.37 |  | 9.31
MORRO BAY-SOLAR SW STA #2 | 230 | ETL.5310 |  | ACT | 45.56 | 11.76 | 24.47 |  | 9.33
MORRO BAY-TEMPLETON | 230 | ETL.5933 |  | ACT | 16.43 | 5.45 | 4.31 |  | 6.67
MOSS LANDING - DALLAS | 500 | ETL.1272 |  | ACT | 0.07 |  |  |  | 0.07
MOSS LANDING-COBURN | 230 | ETL.5330 |  | ACT | 64.03 |  | 35.17 | 0.06 | 28.8
MOSS LANDING-CRAZY HORSE CANYON #1 | 115 | ETL.2930 |  | ACT | 10.52 |  |  |  | 10.52
MOSS LANDING-CRAZY HORSE CANYON #2 | 115 | ETL.2983 |  | ACT | 10.59 |  |  |  | 10.59
MOSS LANDING-DEL MONTE #1 | 115 | ETL.2830 |  | ACT | 23.25 |  | 5.73 |  | 17.52
MOSS LANDING-DEL MONTE #2 | 115 | ETL.2840 |  | ACT | 23.29 |  | 5.73 |  | 17.56
MOSS LANDING-GREEN VALLEY #1 | 115 | ETL.2850 |  | ACT | 14.22 |  |  |  | 14.22
MOSS LANDING-GREEN VALLEY #2 | 115 | ETL.2860 |  | ACT | 14.22 |  |  |  | 14.22
MOSS LANDING-LAS AGUILAS SW STA | 230 | ETL.5340 |  | ACT | 51.9 |  | 28.03 | 0.03 | 23.84
MOSS LANDING-LOS BANOS | 500 | ETL.6040 |  | ACT | 51.33 |  | 11.64 | 0.2 | 39.49
MOSS LANDING-METCALF | 500 | ETL.6050 |  | ACT | 34.98 | 7.17 | 14.28 |  | 13.53
MOSS LANDING-MOSS LANDING PP #1 | 230 | ETL.1282 | NON PGE | ACT | 0.05 |  |  |  | 0.05 | Non-PG&E
MOSS LANDING-MOSS LANDING PP #2 | 230 | ETL.1296 | NON PGE | ACT | 0.05 |  |  |  | 0.05 | Non-PG&E
MOSS LANDING-SALINAS #1 | 115 | ETL.2880 |  | ACT | 11.99 |  |  |  | 11.99
MOSS LANDING-SALINAS #2 | 115 | ETL.2890 |  | ACT | 12.03 |  |  |  | 12.03
MTN GATE JCT-CASCADE | 60 | ETL.7640 |  | ACT | 6.58 |  | 6.58 |  | 0
MTN GATE TAP | 60 | ETL.7641 |  | ACT | 0.7 |  | 0.7 |  | 0
MTN QUARRIES TAP | 60 | ETL.6991 |  | ACT | 2.63 |  | 1.98 |  | 0.65
MTN VIEW-MONTA VISTA | 115 | ETL.2920 |  | ACT | 4.8 |  |  |  | 4.8
MULE CREEK TAP | 60 | ETL.8254 |  | ACT | 0.01 |  |  |  | 0.01
MUSTANG SW STA-CABALLO-SLATE | 230 | ETL.1172 |  | ACT | 0.07 |  |  |  | 0.07
MUSTANG SW STA-GREGG | 230 | ETL.4700 |  | ACT | 45.47 |  |  |  | 45.47
MUSTANG SW STA-MCCALL | 230 | ETL.4710 |  | ACT | 42.11 |  |  |  | 42.11
MUSTANG TAP | 70 | ETL.9091 |  | ACT | 0.71 |  | 0.71 |  | 0
NARROWS #1 TAP | 60 | ETL.6511 |  | ACT | 2.65 |  | 2.65 |  | 0
NARROWS #2 TAP | 60 | ETL.6521 |  | ACT | 3.09 |  | 3.09 |  | 0
NAVY LAB TAP | 60 | ETL.6711 |  | ACT | 0.19 |  |  |  | 0.19
NEW HOGAN TAP | 60 | ETL.8211 |  | ACT | 0.06 |  |  |  | 0.06
NEWARK E-F BUS TIE | 230 | ETL.4640 |  | ACT | 0.22 |  |  |  | 0.22
NEWARK-AMES #1 | 115 | ETL.2940 |  | ACT | 8.3 |  |  |  | 8.3
NEWARK-AMES #2 | 115 | ETL.2950 |  | ACT | 8.28 |  |  |  | 8.28
NEWARK-AMES #3 | 115 | ETL.2960 |  | ACT | 8.28 |  |  |  | 8.28
NEWARK-AMES DISTRIBUTION | 115 | ETL.4313 |  | ACT | 8.25 |  |  |  | 8.25
NEWARK-APPLIED MATERIALS | 115 | ETL.2980 |  | ACT | 11.37 |  |  |  | 11.37
NEWARK-DIXON LANDING | 115 | ETL.2990 |  | ACT | 4.69 |  |  |  | 4.69
NEWARK-FREMONT #1 | 115 | ETL.3000 |  | ACT | 3.67 |  |  |  | 3.67
NEWARK-FREMONT #2 | 115 | ETL.3010 |  | ACT | 3.74 |  |  |  | 3.74
NEWARK-JARVIS #1 | 115 | ETL.3020 |  | ACT | 14.25 |  |  | 0.69 | 13.56
NEWARK-JARVIS #2 | 115 | ETL.3030 |  | ACT | 14.48 |  |  | 0.69 | 13.79
NEWARK-KIFER | 115 | ETL.3040 |  | ACT | 10.61 |  |  |  | 10.61
NEWARK-LAWRENCE | 115 | ETL.3050 |  | ACT | 10.25 |  |  |  | 10.25
NEWARK-LIVERMORE | 60 | ETL.7660 |  | ACT | 19.05 |  | 3.93 | 0.48 | 14.64
NEWARK-LOS ESTEROS | 230 | ETL.2970 |  | ACT | 5.65 |  |  |  | 5.65
NEWARK-MILPITAS #1 | 115 | ETL.3070 |  | ACT | 8.48 |  |  |  | 8.48
NEWARK-MILPITAS #2 | 115 | ETL.3080 |  | ACT | 10.3 |  |  |  | 10.3
NEWARK-NORTHERN RECEIVING STATION #1 | 115 | ETL.3100 |  | ACT | 8.76 |  |  |  | 8.76
NEWARK-NORTHERN RECEIVING STATION #2 | 115 | ETL.3110 |  | ACT | 8.67 |  |  |  | 8.67
NEWARK-NUMMI | 115 | ETL.3090 |  | ACT | 4.94 |  |  |  | 4.94
NEWARK-RAVENSWOOD | 230 | ETL.5936 |  | ACT | 8.91 |  |  |  | 8.91
NEWARK-TRIMBLE | 115 | ETL.3120 |  | ACT | 12.36 |  |  |  | 12.36
NEWARK-VALLECITOS | 60 | ETL.7670 |  | ACT | 12.38 |  | 2.23 |  | 10.15
NICOLAUS-CATLETT JCT | 60 | ETL.7680 |  | ACT | 20.15 |  |  |  | 20.15
NICOLAUS-CATLETT JCT | 60 | ETL.7680 |  | IDL | 4.45 |  |  |  | 4.45
NICOLAUS-CATLETT JCT (12KV) | 60 | ETL.7680 |  | IDL | 14.18 |  |  |  | 14.18
NICOLAUS-MARYSVILLE | 60 | ETL.7690 |  | ACT | 18.73 |  |  |  | 18.73
NICOLAUS-PLAINFIELD | 60 | ETL.7700 |  | ACT | 30.63 |  |  |  | 30.63
NICOLAUS-WILKINS SLOUGH | 60 | ETL.7710 |  | ACT | 28.69 |  |  |  | 28.69
NORTECH-NORTHERN RECEIVING STATION | 115 | ETL.1551 |  | ACT | 2.21 |  |  |  | 2.21
NORTH DUBLIN-CAYETANO | 230 | ETL.4500 |  | ACT | 3.02 |  | 3.02 |  | 0
NORTH DUBLIN-VINEYARD | 230 | ETL.4501 |  | ACT | 12.46 |  | 4.9 |  | 7.56
NORTH TOWER-MARTINEZ JCT #1 (21KV) | 115 | ETL.3130 |  | IDL | 2.61 |  | 1.75 |  | 0.86 | Idle Section
NORTHERN RECEIVING STATION-SCOTT #1 | 115 | ETL.3101 |  | ACT | 2.08 |  |  |  | 2.08
NORTHERN RECEIVING STATION-SCOTT #2 | 115 | ETL.3111 |  | ACT | 1.98 |  |  |  | 1.98
NOTRE DAME-BUTTE | 115 | ETL.4312 |  | ACT | 2.02 |  |  |  | 2.02
OAK PARK TAP | 60 | ETL.8142 |  | ACT | 0.87 |  |  |  | 0.87
OAKHURST TAP | 115 | ETL.1252 |  | ACT | 18.16 | 0.89 | 16.58 |  | 0.69
OAKLAND C-MARITIME | 115 | ETL.3135 |  | ACT | 2.36 |  |  |  | 2.36
OAKLAND C-TURBINES | 115 | ETL.3137 |  | ACT | 0.19 |  |  |  | 0.19
OAKLAND J-GRANT | 115 | ETL.3140 |  | ACT | 14.83 |  |  |  | 14.83
OCEANO-CALLENDER SW STA | 115 | ETL.2394 |  | ACT | 4.22 |  | 3 |  | 1.22
OIL CITY TAP | 70 | ETL.8574 |  | ACT | 0.05 |  |  |  | 0.05
OILFIELDS-SALINAS RIVER | 60 | ETL.7728 |  | ACT | 1.46 |  |  |  | 1.46
OILFIELDS-SARGENT CANYON | 60 | ETL.7725 |  | ACT | 2.02 |  |  |  | 2.02
OLEUM-G #1 | 115 | ETL.3150 |  | ACT | 11.29 | 2.06 | 6.95 |  | 2.28
OLEUM-G #2 | 115 | ETL.3160 |  | ACT | 11.3 | 2.06 | 6.95 |  | 2.29
OLEUM-MARTINEZ | 115 | ETL.3170 |  | ACT | 10.5 |  | 7.03 |  | 3.47
OLEUM-NORTH TOWER-CHRISTIE | 115 | ETL.3180 |  | ACT | 8.33 |  | 6.55 |  | 1.78
OLEUM-UNOCAL #1 | 115 | ETL.4260 |  | ACT | 0.01 |  |  |  | 0.01
OLEUM-UNOCAL #2 | 115 | ETL.4270 |  | ACT | 0.05 |  |  |  | 0.05
OLIVE SW STA-SMYRNA | 115 | ETL.1923 |  | ACT | 11.07 |  |  |  | 11.07
ORO FINO TAP | 60 | ETL.6721 |  | ACT | 1.3 | 1.3 |  |  | 0
ORO LOMA-CANAL #1 | 70 | ETL.9020 |  | ACT | 24.55 |  |  |  | 24.55
ORO LOMA-MENDOTA | 70 | ETL.9030 |  | ACT | 29.41 |  |  |  | 29.41
OROVILLE-TABLE MTN #2 (CDWR) | 230 | ETL.6623 | NON PGE | ACT | 10.09 |  | 3.67 |  | 6.42 | Non-PG&E
OROVILLE-THERMALITO-TABLE MTN #1 (CDWR) | 230 | ETL.6621 | NON PGE | ACT | 12.44 |  | 5.06 |  | 7.38 | Non-PG&E
OROVILLE-THERMALITO-TABLE MTN #3 (CDWR) | 230 | ETL.6622 | NON PGE | ACT | 12.4 |  | 3.6 |  | 8.8 | Non-PG&E
OWENS ILLINOIS TAP | 115 | ETL.3971 |  | ACT | 0.68 |  |  |  | 0.68
OXBOW TAP | 60 | ETL.7561 |  | ACT | 0.15 | 0.15 |  |  | 0
OXFORD TAP | 115 | ETL.3241 |  | ACT | 3.87 |  |  |  | 3.87
P-X #2 | 115 | ETL.3125 |  | ACT | 0.28 |  |  |  | 0.28
PACIFIC ETHANOL TAP | 60 | ETL.8325 |  | ACT | 0.68 |  |  |  | 0.68
PACIFIC LUMBER (SCOTIA) TAP | 60 | ETL.7852 |  | ACT | 0.52 |  |  |  | 0.52
PACIFIC OROVILLE POWER TAP | 60 | ETL.7731 |  | IDL | 0.78 |  |  |  | 0.78
PADRE FLAT SW STA-PANOCHE | 230 | ETL.5030 |  | ACT | 33.58 |  |  |  | 33.58
PAIGE SOLAR TAP | 70 | ETL.1262 | PGE | ACT | 1.04 |  |  |  | 1.04
PALERMO-BOGUE | 115 | ETL.3200 |  | ACT | 35.73 |  | 1.24 |  | 34.49
PALERMO-COLGATE | 230 | ETL.5360 |  | ACT | 29.61 |  | 16.87 |  | 12.74
PALERMO-NICOLAUS | 115 | ETL.3210 |  | ACT | 41.18 |  | 1.19 |  | 39.99
PALERMO-OROVILLE #1 | 60 | ETL.7730 |  | ACT | 6.94 |  | 1.18 |  | 5.76
PALERMO-OROVILLE #2 | 60 | ETL.7740 |  | ACT | 10.13 |  | 2.86 |  | 7.27
PALERMO-PEASE | 115 | ETL.3220 |  | ACT | 26.53 |  | 1.08 |  | 25.45
PALERMO-WYANDOTTE | 115 | ETL.4315 |  | ACT | 3.44 |  | 1.26 |  | 2.18
PANOCHE-CAL PEAK-STARWOOD | 115 | ETL.1051 |  | ACT | 0.09 |  |  |  | 0.09
PANOCHE-EXCELSIOR SW STA #1 | 115 | ETL.3250 |  | ACT | 28.5 |  |  |  | 28.5
PANOCHE-EXCELSIOR SW STA #2 | 115 | ETL.3260 |  | ACT | 28.5 |  |  |  | 28.5
PANOCHE-MENDOTA | 115 | ETL.3230 |  | ACT | 10.08 |  |  |  | 10.08
PANOCHE-ORO LOMA | 115 | ETL.3240 |  | ACT | 18.93 |  |  |  | 18.93
PANOCHE-PANOCHE ENERGY CENTER | 230 | ETL.2293 |  | ACT | 0.09 |  |  |  | 0.09
PANOCHE-TRANQUILLITY SW STA #1 | 230 | ETL.5000 |  | ACT | 12.14 |  |  |  | 12.14
PANOCHE-TRANQUILLITY SW STA #2 | 230 | ETL.5481 |  | ACT | 12.14 |  |  |  | 12.14
PARADISE-BUTTE | 115 | ETL.4396 |  | ACT | 13.58 | 0.62 | 7.59 |  | 5.37
PARADISE-TABLE MTN | 115 | ETL.4316 |  | ACT | 35.6 | 6.69 | 19.93 |  | 8.98
PARAMOUNT FARMS TAP | 115 | ETL.1744 |  | ACT | 0.57 |  |  |  | 0.57
PARDEE #1 TAP | 60 | ETL.8231 |  | ACT | 4.33 |  | 4.33 |  | 0
PARDEE #2 TAP | 60 | ETL.8251 |  | ACT | 0.11 |  | 0.1 |  | 0.01
PARKWAY-MORAGA | 230 | ETL.5930 |  | ACT | 23.64 | 4.31 | 12.24 |  | 7.09
PASO ROBLES-TEMPLETON | 70 | ETL.9400 |  | ACT | 4.9 |  |  |  | 4.9
PEABODY-BIRDS LANDING SW STA | 230 | ETL.6171 |  | ACT | 19.85 |  |  |  | 19.85
PEACHTON-PEASE | 60 | ETL.8426 |  | ACT | 16.35 |  |  |  | 16.35
PEASE-HARTER | 60 | ETL.7760 |  | ACT | 15.91 |  |  |  | 15.91
PEASE-MARYSVILLE-HARTER | 60 | ETL.7770 |  | ACT | 10.35 |  |  |  | 10.35
PEASE-RIO OSO | 115 | ETL.3270 |  | ACT | 27.61 |  |  |  | 27.61
PENN ZIER TAP | 70 | ETL.8575 |  | ACT | 3 |  |  |  | 3
PENNGROVE SUB TAP | 115 | ETL.2061 |  | ACT | 0.81 |  |  |  | 0.81
PENTLAND TAP | 70 | ETL.8973 |  | ACT | 0.55 |  |  |  | 0.55
PEORIA TAP | 115 | ETL.2391 |  | ACT | 0.86 |  | 0.86 |  | 0
PERMANENTE #1 TAP | 60 | ETL.7621 |  | ACT | 0.31 |  | 0.13 |  | 0.18
PERMANENTE #2 TAP | 60 | ETL.7622 |  | ACT | 0.51 |  | 0.34 |  | 0.17
PHILO JCT-ELK | 60 | ETL.7780 |  | ACT | 37.24 |  | 32.94 | 0.03 | 4.27
PIERCY-METCALF | 115 | ETL.4318 |  | ACT | 4.72 |  |  |  | 4.72
PINE GROVE TAP | 60 | ETL.8351 |  | ACT | 2.67 | 0.48 | 2.19 |  | 0
PIT #1-COTTONWOOD | 230 | ETL.5390 |  | ACT | 59.75 | 7.62 | 42.04 | 0.04 | 10.05
PIT #1-HAT CREEK #2-BURNEY | 60 | ETL.7040 |  | ACT | 12.92 |  | 10.58 |  | 2.34
PIT #1-MCARTHUR | 60 | ETL.7790 |  | ACT | 7.32 |  | 3.08 |  | 4.24
PIT #3-CARBERRY SW STA | 230 | ETL.5450 |  | ACT | 10.91 |  | 9.18 | 0.03 | 1.7
PIT #3-PIT #1 | 230 | ETL.5400 |  | ACT | 22.64 |  | 19.28 | 0.03 | 3.33
PIT #4 TAP | 230 | ETL.5432 | POWERGEN | ACT | 7.03 |  | 7.03 |  | 0
PIT #5-ROUND MTN #1 | 230 | ETL.5420 |  | ACT | 13.12 |  | 13.12 |  | 0
PIT #5-ROUND MTN #2 | 230 | ETL.5430 |  | ACT | 13.11 |  | 13.11 |  | 0
PIT #6 JCT-ROUND MTN | 230 | ETL.5440 |  | ACT | 8.15 |  | 8.15 |  | 0
PIT #6 TAP | 230 | ETL.5441 | POWERGEN | ACT | 3.43 |  | 3.43 |  | 0
PIT #7 TAP | 230 | ETL.5442 | POWERGEN | ACT | 3.59 |  | 3.59 |  | 0
PITTSBURG #2 TAP | 60 | ETL.8371 |  | ACT | 1.17 |  |  |  | 1.17
PITTSBURG-BLACK DIAMOND ENERGY STORAGE | 230 | ETL.1192 |  | ACT | 0.06 |  |  |  | 0.06
PITTSBURG-CLAYTON #1 | 115 | ETL.3280 |  | ACT | 16.82 |  | 6.01 |  | 10.81
PITTSBURG-CLAYTON #3 | 115 | ETL.3290 |  | ACT | 8.41 |  | 2.91 |  | 5.5
PITTSBURG-CLAYTON #4 | 115 | ETL.3291 |  | ACT | 8.32 |  | 2.91 |  | 5.41
PITTSBURG-COLUMBIA STEEL | 115 | ETL.3300 |  | ACT | 9.23 |  | 1.21 |  | 8.02
PITTSBURG-DELTA ENERGY CENTER #1 | 230 | ETL.1254 | NON PGE | ACT | 0.01 |  |  |  | 0.01 | Non-PG&E
PITTSBURG-DELTA ENERGY CENTER #2 | 230 | ETL.3315 | NON PGE | ACT | 0.01 |  |  |  | 0.01 | Non-PG&E
PITTSBURG-EASTSHORE | 230 | ETL.5462 |  | ACT | 34.96 | 11.9 | 7.78 |  | 15.28
PITTSBURG-KIRKER-COLUMBIA STEEL | 115 | ETL.3310 |  | ACT | 9.26 |  | 1.13 |  | 8.13
PITTSBURG-LOS MEDANOS #1 | 115 | ETL.3304 |  | ACT | 0.5 |  |  |  | 0.5
PITTSBURG-LOS MEDANOS #2 | 115 | ETL.3305 |  | ACT | 0.5 |  |  |  | 0.5
PITTSBURG-MARTINEZ #1 | 115 | ETL.3320 |  | ACT | 17.23 |  | 0.34 |  | 16.89
PITTSBURG-MARTINEZ #2 | 115 | ETL.3330 |  | ACT | 15.83 |  | 0.38 |  | 15.45
PITTSBURG-SAN MATEO | 230 | ETL.5463 |  | ACT | 47.4 | 11.89 | 7.78 |  | 27.73
PITTSBURG-SAN RAMON | 230 | ETL.5490 |  | ACT | 21.66 | 6.1 | 7.7 |  | 7.86
PITTSBURG-TASSAJARA | 230 | ETL.5470 |  | ACT | 17.36 | 6.11 | 6.65 |  | 4.6
PITTSBURG-TESLA #1 | 230 | ETL.5510 |  | ACT | 31.35 |  | 18 | 0.05 | 13.3
PITTSBURG-TESLA #2 | 230 | ETL.5520 |  | ACT | 31.32 |  | 18.03 | 0.04 | 13.25
PITTSBURG-TESORO | 230 | ETL.5500 |  | ACT | 11.27 |  |  |  | 11.27
PITTSBURG-TIDEWATER | 230 | ETL.5530 |  | ACT | 11.27 |  |  |  | 11.27
PLACER-DEL MAR | 60 | ETL.7800 |  | ACT | 10.8 |  | 4.52 |  | 6.28
PLACER-GOLD HILL #1 | 115 | ETL.3340 |  | ACT | 20.73 |  | 9.92 |  | 10.81
PLACER-GOLD HILL #2 | 115 | ETL.4290 |  | ACT | 20.67 |  | 9.92 |  | 10.75
PLUMAS-SIERRA TAP | 60 | ETL.6291 |  | ACT | 0.75 | 0.01 | 0.06 |  | 0.68
POE-RIO OSO | 230 | ETL.5540 |  | ACT | 56.09 | 4.41 | 14.01 |  | 37.67
POINT PINOLE TAP | 115 | ETL.3792 |  | ACT | 1.29 |  |  |  | 1.29
POINT PINOLE TAP | 115 | ETL.3792 |  | IDL | 0.01 |  |  |  | 0.01
POST OFFICE TAP | 115 | ETL.4122 |  | ACT | 0.75 |  |  |  | 0.75
POTTER VALLEY-MENDOCINO | 60 | ETL.7810 |  | ACT | 10.94 |  | 8.38 |  | 2.56
POTTER VALLEY-WILLITS | 60 | ETL.7820 |  | ACT | 13.16 | 5.51 | 6.35 |  | 1.3
PSE MCKITTRICK TAP | 115 | ETL.2632 |  | ACT | 5.21 |  |  |  | 5.21
Padre Flat SW STA – Freeman Wright | 230 | ETL.1492 |  | ACT | 0.04 |  |  |  | 0.04
QUEBEC TAP | 115 | ETL.1311 |  | ACT | 4.38 |  |  |  | 4.38
QUINTO SW STA-FINK SW STA | 230 | ETL.5070 |  | ACT | 41.57 |  |  |  | 41.57
RACETRACK TAP | 115 | ETL.2393 |  | ACT | 3.54 |  | 3.54 |  | 0
RADUM-LIVERMORE | 60 | ETL.7830 |  | ACT | 4.65 |  |  |  | 4.65
RADUM-VALLECITOS | 60 | ETL.8280 |  | ACT | 10.6 |  |  |  | 10.6
RAINBOW TAP | 115 | ETL.2031 |  | ACT | 2.59 |  |  |  | 2.59
RALPH TAP | 230 | ETL.4931 |  | ACT | 0.06 |  |  |  | 0.06
RANCHERS COTTON TAP | 115 | ETL.2311 |  | ACT | 2.1 |  |  |  | 2.1
RANCHO SECO-BELLOTA #1 | 230 | ETL.5550 |  | ACT | 27.39 |  |  |  | 27.39
RANCHO SECO-BELLOTA #2 | 230 | ETL.5560 |  | ACT | 27.36 |  |  |  | 27.36
RAVENSWOOD-AMES #1 | 115 | ETL.3360 |  | ACT | 7.07 |  |  |  | 7.07
RAVENSWOOD-AMES #2 | 115 | ETL.3370 |  | ACT | 7.09 |  |  |  | 7.09
RAVENSWOOD-BAIR #1 | 115 | ETL.3380 |  | ACT | 7.43 |  |  |  | 7.43
RAVENSWOOD-BAIR #2 | 115 | ETL.3385 |  | ACT | 11.29 |  |  |  | 11.29
RAVENSWOOD-COOLEY LANDING #1 | 115 | ETL.3390 |  | ACT | 1.62 |  |  |  | 1.62
RAVENSWOOD-COOLEY LANDING #2 | 115 | ETL.3400 |  | ACT | 1.62 |  |  |  | 1.62
RAVENSWOOD-PALO ALTO #1 | 115 | ETL.3410 |  | ACT | 4.27 |  |  |  | 4.27
RAVENSWOOD-PALO ALTO #2 | 115 | ETL.3420 |  | ACT | 4.26 |  |  |  | 4.26
RAVENSWOOD-SAN MATEO | 115 | ETL.3430 |  | ACT | 12.04 |  |  |  | 12.04
RAVENSWOOD-SAN MATEO #1 | 230 | ETL.5580 |  | ACT | 11.89 |  |  |  | 11.89
RAVENSWOOD-SAN MATEO #2 | 230 | ETL.5351 |  | ACT | 11.88 |  |  |  | 11.88
RED BANK TAP | 60 | ETL.6631 |  | ACT | 0.68 |  |  |  | 0.68
REEDLEY-DINUBA #1 | 70 | ETL.9050 |  | ACT | 7.7 |  |  |  | 7.7
REEDLEY-OROSI | 70 | ETL.9060 |  | ACT | 10.89 |  |  |  | 10.89
RESERVE OIL TAP | 70 | ETL.8721 |  | ACT | 0.58 |  |  |  | 0.58
RINCON #1 TAP | 115 | ETL.1601 |  | ACT | 0.57 | 0.08 | 0.49 |  | 0
RINCON #2 TAP | 115 | ETL.1611 |  | ACT | 0.55 | 0.07 | 0.48 |  | 0
RIO BRAVO (FRESNO) TAP | 115 | ETL.2312 |  | ACT | 0.32 |  |  |  | 0.32
RIO BRAVO (ROCKLIN) TAP | 115 | ETL.7974 |  | ACT | 0.4 |  |  |  | 0.4
RIO BRAVO HYDRO | 70 | ETL.9070 |  | ACT | 0.24 |  |  |  | 0.24
RIO BRAVO TOMATO TAP | 115 | ETL.8328 |  | ACT | 0.43 |  |  |  | 0.43
RIO BRAVO-KERN OIL | 115 | ETL.1922 |  | IDL | 3.72 |  |  |  | 3.72
RIO DELL JCT-BRIDGEVILLE | 60 | ETL.7850 |  | ACT | 21.22 |  | 15.05 |  | 6.17
RIO DELL TAP | 60 | ETL.7851 |  | ACT | 5.35 |  | 0.79 |  | 4.56
RIO OSO-ATLANTIC | 230 | ETL.5590 |  | ACT | 17.68 |  |  |  | 17.68
RIO OSO-BRIGHTON | 230 | ETL.5600 |  | ACT | 27.17 |  |  |  | 27.17
RIO OSO-GOLD HILL | 230 | ETL.5610 |  | ACT | 28.63 |  |  | 0.02 | 28.61
RIO OSO-LINCOLN | 115 | ETL.1320 |  | ACT | 11.04 |  |  |  | 11.04
RIO OSO-LOCKEFORD | 230 | ETL.5620 |  | ACT | 65.13 |  |  |  | 65.13
RIO OSO-NICOLAUS | 115 | ETL.3440 |  | ACT | 5.39 |  |  |  | 5.39
RIO OSO-WEST SACRAMENTO | 115 | ETL.3450 |  | ACT | 43.55 |  |  |  | 43.55
RIO OSO-WOODLAND #1 | 115 | ETL.3460 |  | ACT | 45.25 |  |  |  | 45.25
RIO OSO-WOODLAND #2 | 115 | ETL.3470 |  | ACT | 53.37 |  |  |  | 53.37
RIPON-MANTECA | 115 | ETL.1062 |  | ACT | 9.16 |  |  |  | 9.16
RIVERBANK JCT SW STA-RIPON | 115 | ETL.3841 |  | ACT | 18.02 |  |  |  | 18.02
ROBERTSON TAP | 60 | ETL.8322 |  | ACT | 0.82 |  |  |  | 0.82
ROCK CREEK-POE | 230 | ETL.5630 |  | ACT | 26.98 | 6.85 | 20.13 |  | 0
ROLLINS TAP | 60 | ETL.6762 |  | ACT | 0.73 | 0.34 | 0.39 |  | 0
ROSE TAP | 70 | ETL.9251 |  | ACT | 0.31 |  |  |  | 0.31
ROSSMOOR #1 TAP | 230 | ETL.5451 |  | ACT | 0.69 | 0.48 |  |  | 0.21
ROSSMOOR #2 TAP | 230 | ETL.5461 |  | ACT | 0.66 | 0.46 |  |  | 0.2
ROUGH & READY TAP | 60 | ETL.8324 |  | ACT | 0.95 |  |  |  | 0.95
ROUND MTN-COTTONWOOD #2 | 230 | ETL.5640 |  | ACT | 33.67 | 3.73 | 22.05 |  | 7.89
ROUND MTN-COTTONWOOD #3 | 230 | ETL.5650 |  | ACT | 33.36 | 7.17 | 19.17 | 0.03 | 6.99
ROUND MTN-TABLE MTN #1 | 500 | ETL.6060 |  | ACT | 89.03 | 11.74 | 64.63 |  | 12.66
ROUND MTN-TABLE MTN #2 | 500 | ETL.6070 |  | ACT | 89.02 | 11.77 | 67.19 |  | 10.06
RUSSELL CITY ENERGY CENTER-EASTSHORE #1 | 230 | ETL.6155 |  | ACT | 1.19 |  |  |  | 1.19
RUSSELL CITY ENERGY CENTER-EASTSHORE #2 | 230 | ETL.6157 |  | ACT | 1.2 |  |  |  | 1.2
SAFEWAY TAP | 115 | ETL.3984 |  | ACT | 0.68 |  |  |  | 0.68
SALADO-CROW CREEK SW STA | 60 | ETL.7858 |  | ACT | 3.77 |  |  |  | 3.77
SALADO-NEWMAN #2 | 60 | ETL.7870 |  | ACT | 21.58 |  |  |  | 21.58
SALINAS-FIRESTONE #1 | 60 | ETL.7900 |  | ACT | 6.15 |  |  |  | 6.15
SALINAS-FORT ORD #1 | 60 | ETL.7890 |  | ACT | 10.22 |  | 3.02 |  | 7.2
SALINAS-FORT ORD #2 | 60 | ETL.8423 |  | ACT | 10.15 |  | 3 |  | 7.15
SALINAS-LAGUNITAS | 60 | ETL.7920 |  | ACT | 5.84 |  |  |  | 5.84
SALINAS-LAURELES | 60 | ETL.7930 |  | ACT | 27.44 |  | 18.24 | 0.37 | 8.83
SALINAS-SPENCE | 60 | ETL.7910 |  | ACT | 11.61 |  |  |  | 11.61
SALMON CREEK TAP | 60 | ETL.6981 |  | ACT | 10.51 | 1.04 | 5.4 |  | 4.07
SALT SPRINGS-TIGER CREEK | 115 | ETL.3500 |  | ACT | 16.48 | 1.66 | 14.82 |  | 0
SAN ANDREAS (CCSF) TAP | 60 | ETL.7571 |  | ACT | 0.39 |  |  |  | 0.39
SAN ARDO TAP | 60 | ETL.6421 |  | ACT | 0.34 |  |  |  | 0.34
SAN BENITO-HOLLISTER | 115 | ETL.2901 |  | ACT | 8.29 |  |  |  | 8.29
SAN BERNARD-TEJON | 70 | ETL.9080 |  | ACT | 6.96 |  |  |  | 6.96
SAN BRUNO TAP | 60 | ETL.7572 |  | ACT | 1.12 |  | 0.52 |  | 0.6
SAN FRANCISCO #2 | 115 | ETL.3279 |  | IDL | 3.15 |  |  |  | 3.15
SAN JOSE A-SAN JOSE B | 115 | ETL.3510 |  | ACT | 1.15 |  |  |  | 1.15
SAN JOSE B-STONE-EVERGREEN | 115 | ETL.1550 |  | ACT | 8.56 |  |  |  | 8.56
SAN LEANDRO-OAKLAND J #1 | 115 | ETL.3520 |  | ACT | 6.7 |  |  |  | 6.7
SAN LUIS #3 TAP | 115 | ETL.3244 |  | ACT | 16.11 |  |  |  | 16.11
SAN LUIS #5 TAP | 115 | ETL.3243 |  | ACT | 1.88 |  |  |  | 1.88
SAN LUIS OBISPO-CAYUCOS | 70 | ETL.9090 |  | ACT | 23.39 |  | 13.39 |  | 10
SAN LUIS OBISPO-OCEANO | 115 | ETL.3530 |  | ACT | 19.9 | 2.15 | 9.72 |  | 8.03
SAN LUIS OBISPO-SANTA MARIA | 115 | ETL.3540 |  | ACT | 25.96 | 2.16 | 11.12 |  | 12.68
SAN MATEO-BAIR | 60 | ETL.7940 |  | ACT | 13.97 |  |  |  | 13.97
SAN MATEO-BAY MEADOWS #1 | 115 | ETL.3550 |  | ACT | 4.3 |  |  |  | 4.3
SAN MATEO-BAY MEADOWS #2 | 115 | ETL.3560 |  | ACT | 4.26 |  |  |  | 4.26
SAN MATEO-BELMONT | 115 | ETL.3570 |  | ACT | 7.2 |  |  |  | 7.2
SAN MATEO-HILLSDALE JCT | 60 | ETL.7950 |  | ACT | 6.85 |  | 1.15 |  | 5.7
SAN MATEO-MARTIN #3 | 115 | ETL.3580 |  | ACT | 11.55 |  |  |  | 11.55
SAN MATEO-MARTIN #4 | 115 | ETL.7500 |  | ACT | 11.62 |  |  |  | 11.62
SAN MATEO-MARTIN #6 | 115 | ETL.3590 |  | ACT | 11.69 |  |  |  | 11.69
SAN MIGUEL-PASO ROBLES | 70 | ETL.9390 |  | ACT | 9.92 |  |  |  | 9.92
SAN PABLO #1 TAP | 115 | ETL.3801 |  | ACT | 0.44 |  |  |  | 0.44
SAN PABLO #2 TAP | 115 | ETL.3791 |  | ACT | 0.45 |  |  |  | 0.45
SAN RAMON RESEARCH CENTER TAP | 230 | ETL.5921 |  | ACT | 3.27 |  |  |  | 3.27
SAN RAMON-MORAGA | 230 | ETL.5660 |  | ACT | 22.24 | 13.67 | 3.24 |  | 5.33
SAN RAMON-RADUM | 60 | ETL.7960 |  | ACT | 7.06 |  |  |  | 7.06
SANDBAR TAP | 115 | ETL.1403 |  | ACT | 0.1 | 0.1 |  |  | 0
SANGER COGEN TAP | 115 | ETL.9141 |  | ACT | 0.83 |  |  |  | 0.83
SANGER-CALIFORNIA AVE | 115 | ETL.9130 |  | ACT | 9.15 |  |  |  | 9.15
SANGER-CALIFORNIA AVE #1 | 70 | ETL.9120 |  | IDL | 2.08 |  |  |  | 2.08
SANGER-MALAGA | 115 | ETL.3600 |  | ACT | 8.69 |  |  |  | 8.69
SANGER-REEDLEY | 115 | ETL.9140 |  | ACT | 20.61 |  |  |  | 20.61
SANTA FE GEOTHERMAL TAP | 230 | ETL.4782 |  | ACT | 1.04 | 1.04 |  |  | 0
SANTA MARIA-SISQUOC | 115 | ETL.3610 |  | ACT | 10.57 |  |  |  | 10.57
SANTA PAULA-MILLBRAE | 115 | ETL.7580 |  | ACT | 0.09 |  |  |  | 0.09
SANTA ROSA-CORONA | 115 | ETL.4309 |  | ACT | 14.34 |  | 1.09 |  | 13.25
SANTA TERESA-EDENVALE | 115 | ETL.1132 |  | ACT | 0.68 |  |  |  | 0.68
SANTA YNEZ TAP | 115 | ETL.3701 |  | ACT | 4.06 |  | 3.49 |  | 0.57
SARATOGA-VASONA | 230 | ETL.5931 |  | ACT | 3.41 |  |  |  | 3.41
SCHINDLER-COALINGA #2 | 70 | ETL.9150 |  | ACT | 17.19 |  |  |  | 17.19
SCHINDLER-FIVE POINTS SW STA | 70 | ETL.9161 |  | ACT | 1.7 |  |  |  | 1.7
SCHULTE SW STA-KASSON-MANTECA | 115 | ETL.7472 |  | ACT | 16.58 |  |  |  | 16.58
SCHULTE SW STA-LAMMERS | 115 | ETL.3993 |  | ACT | 0.69 |  |  |  | 0.69
SEBASTIANI TAP | 60 | ETL.8072 |  | ACT | 0.01 |  |  |  | 0.01
SEMITROPIC-CHARCA | 115 | ETL.3620 |  | ACT | 6.91 |  |  |  | 6.91
SEMITROPIC-MIDWAY #1 | 115 | ETL.3630 |  | ACT | 14.1 |  |  |  | 14.1
SEMITROPIC-MIDWAY #2 | 115 | ETL.3640 |  | ACT | 10.53 |  |  |  | 10.53
SEMITROPIC-MIDWAY #2 | 115 | ETL.3640 |  | IDL | 9.58 |  |  |  | 9.58
SEMITROPIC-WASCO | 70 | ETL.9170 |  | ACT | 6.32 |  |  |  | 6.32
SERRAMONTE TAP | 115 | ETL.2211 |  | ACT | 2.55 |  |  |  | 2.55
SF AIRPORT-SAN MATEO | 115 | ETL.3650 |  | ACT | 6.09 |  |  |  | 6.09
SHAFTER-RIO BRAVO | 115 | ETL.3660 |  | ACT | 8.31 |  |  |  | 8.31
SHARON PRISON TAP | 115 | ETL.1251 |  | ACT | 2.57 |  |  |  | 2.57
SHILOH II-BIRDS LANDING SW STA | 230 | ETL.4240 |  | ACT | 3.56 |  |  |  | 3.56
SHREDDER TAP | 115 | ETL.3381 |  | ACT | 1.38 |  |  |  | 1.38
SIERRA #1 | 115 | ETL.3670 |  | IDL | 5.47 |  |  |  | 5.47
SIERRA #2 | 115 | ETL.3680 |  | IDL | 4.86 |  |  |  | 4.86
SIERRA (PSE) TAP | 115 | ETL.1933 |  | ACT | 1.81 |  |  |  | 1.81
SIERRA PAC IND (QUINCY) TAP | 60 | ETL.6292 |  | ACT | 0.02 |  |  |  | 0.02
SIERRA PACIFIC IND TAP | 115 | ETL.7401 |  | ACT | 0.06 |  |  |  | 0.06
SILVERADO-FULTON JCT | 115 | ETL.1610 |  | ACT | 26.16 | 5.02 | 16.85 |  | 4.29
SIMPSON-KORBEL TAP | 60 | ETL.6804 |  | ACT | 0.39 |  |  |  | 0.39
SISQUOC-GAREY | 115 | ETL.3690 |  | ACT | 5.02 | 0.23 | 0.13 |  | 4.66
SISQUOC-SANTA YNEZ SW STA | 115 | ETL.3700 |  | ACT | 22.11 |  | 16.1 |  | 6.01
SKAGGS ISLAND #1 TAP | 115 | ETL.1832 |  | ACT | 0.59 |  |  |  | 0.59
SKAGGS ISLAND #2 TAP | 115 | ETL.1842 |  | ACT | 0.6 |  |  |  | 0.6
SLAC TAP | 60 | ETL.7221 |  | ACT | 1.41 |  |  |  | 1.41
SLY CREEK TAP | 115 | ETL.4221 |  | ACT | 5.34 | 5.34 |  |  | 0
SMARTVILLE TAP | 60 | ETL.6522 |  | ACT | 0.09 |  | 0.09 |  | 0
SMARTVILLE-CAMP FAR WEST | 60 | ETL.7970 |  | ACT | 17.81 |  | 9.28 |  | 8.53
SMARTVILLE-MARYSVILLE | 60 | ETL.7980 |  | ACT | 20.14 |  | 4.86 |  | 15.28
SMARTVILLE-NICOLAUS #1 | 60 | ETL.7990 |  | ACT | 29.6 |  | 4.75 |  | 24.85
SMARTVILLE-NICOLAUS #2 | 60 | ETL.8000 |  | ACT | 30.16 |  | 4.83 |  | 25.33
SMUD TAP | 230 | ETL.1184 |  | ACT | 0.12 | 0.12 |  |  | 0
SMYRNA-SEMITROPIC-MIDWAY | 115 | ETL.3710 |  | ACT | 22.39 |  |  |  | 22.39
SNEATH LANE-HALF MOON BAY | 60 | ETL.7212 |  | ACT | 15.41 | 11.17 | 2.36 |  | 1.88
SNEATH LANE-PACIFICA | 60 | ETL.7575 |  | ACT | 3.26 | 1.36 | 1.32 |  | 0.58
SOBRANTE-G #1 | 115 | ETL.3720 |  | ACT | 5.34 | 3.86 | 1.35 |  | 0.13
SOBRANTE-G #2 | 115 | ETL.3730 |  | ACT | 5.39 | 3.86 | 1.44 |  | 0.09
SOBRANTE-GRIZZLY-CLAREMONT #1 | 115 | ETL.3740 |  | ACT | 19.57 | 12.29 | 5.05 |  | 2.23
SOBRANTE-GRIZZLY-CLAREMONT #2 | 115 | ETL.3750 |  | ACT | 19.3 | 12.15 | 4.62 |  | 2.53
SOBRANTE-MORAGA | 115 | ETL.3742 |  | ACT | 10.36 | 0.21 | 5.38 |  | 4.77
SOBRANTE-R #1 | 115 | ETL.3770 |  | ACT | 5.54 | 3.86 | 1.4 |  | 0.28
SOBRANTE-R #2 | 115 | ETL.3780 |  | ACT | 5.53 | 3.86 | 1.4 |  | 0.27
SOBRANTE-STANDARD OIL SW STA #1 | 115 | ETL.3800 |  | ACT | 18.89 |  | 8.56 |  | 10.33
SOBRANTE-STANDARD OIL SW STA #2 | 115 | ETL.3790 |  | ACT | 18.89 |  | 8.54 |  | 10.35
SOLAR SW STA-CALIENTE SW STA #1 | 230 | ETL.5215 |  | ACT | 8.22 |  |  |  | 8.22
SOLAR SW STA-CALIENTE SW STA #2 | 230 | ETL.5225 |  | ACT | 8.22 |  |  |  | 8.22
SOLAR TANNEHILL TAP | 70 | ETL.9231 |  | ACT | 2.67 |  |  |  | 2.67
SOLEDAD #1 | 60 | ETL.8010 |  | ACT | 19.37 |  |  |  | 19.37
SOLEDAD #2 | 60 | ETL.8020 |  | ACT | 18.86 |  |  |  | 18.86
SOLEDAD #3 | 60 | ETL.8030 |  | ACT | 1.62 |  |  |  | 1.62
SOLEDAD #4 | 60 | ETL.8040 |  | ACT | 6.1 |  |  |  | 6.1
SONOMA-PUEBLO | 115 | ETL.3810 |  | ACT | 18.48 |  | 2.59 | 0.05 | 15.84
SPAULDING #3-SPAULDING #1 | 60 | ETL.8050 | POWERGEN | ACT | 1.08 |  | 0.95 |  | 0.13
SPAULDING-SUMMIT | 60 | ETL.8060 |  | ACT | 19.64 |  | 14.71 | 1.06 | 3.87
SPENCE-FIRESTONE | 60 | ETL.1152 |  | ACT | 1.66 |  |  |  | 1.66
SPI (BURNEY) TAP | 230 | ETL.5392 |  | ACT | 0.04 |  | 0.04 |  | 0
SPRING GAP TAP | 115 | ETL.1402 |  | ACT | 1.64 | 1.64 |  |  | 0
STAGG-COUNTRY CLUB #1 | 60 | ETL.8080 |  | ACT | 2.43 |  |  |  | 2.43
STAGG-COUNTRY CLUB #2 | 60 | ETL.8090 |  | ACT | 2.46 |  |  |  | 2.46
STAGG-HAMMER | 60 | ETL.8100 |  | ACT | 4.25 |  |  |  | 4.25
STAGG-TESLA | 230 | ETL.5680 |  | ACT | 23.64 |  |  |  | 23.64
STANDARD #1 & #2 (12KV) | 60 | ETL.9490 |  | IDL | 4.2 |  |  |  | 4.2
STANISLAUS RECOVERY TAP | 60 | ETL.7861 |  | ACT | 0.11 |  |  |  | 0.11
STANISLAUS-MANTECA #2 | 115 | ETL.3820 |  | ACT | 53.95 |  | 24.97 |  | 28.98
STANISLAUS-MELONES SW STA-MANTECA #1 | 115 | ETL.3830 |  | ACT | 61.15 |  | 32.13 |  | 29.02
STANISLAUS-MELONES SW STA-RIVERBANK JCT SW STA | 115 | ETL.3840 |  | ACT | 43.8 |  | 32.09 |  | 11.71
STAUFFER TAP | 60 | ETL.6372 |  | ACT | 0.58 |  |  |  | 0.58
STELLING-MONTA VISTA | 115 | ETL.1000 |  | ACT | 1.61 |  |  |  | 1.61
STELLING-WOLFE | 115 | ETL.2680 |  | ACT | 1.46 |  |  |  | 1.46
STOCKTON A #1 | 60 | ETL.8110 |  | ACT | 5.58 |  |  |  | 5.58
STOCKTON A-LOCKEFORD-BELLOTA #1 | 115 | ETL.3880 |  | ACT | 42.8 |  |  |  | 42.8
STOCKTON A-LOCKEFORD-BELLOTA #2 | 115 | ETL.3890 |  | ACT | 34.49 |  |  |  | 34.49
STOCKTON A-WEBER #1 | 60 | ETL.8120 |  | ACT | 13.2 |  |  |  | 13.2
STOCKTON A-WEBER #2 | 60 | ETL.8130 |  | ACT | 9.86 |  |  |  | 9.86
STOCKTON A-WEBER #3 | 60 | ETL.8140 |  | ACT | 9.79 |  |  |  | 9.79
STOCKTON-NEWARK (12KV) | 60 | ETL.8150 |  | IDL | 0.62 |  |  |  | 0.62
STONE CORRAL TAP | 70 | ETL.8611 |  | ACT | 7.56 |  |  |  | 7.56
STONE-EVERGREEN | 115 | ETL.1424 |  | ACT | 2.23 |  |  |  | 2.23
STONY POINT TAP | 115 | ETL.2062 |  | ACT | 3.08 |  |  |  | 3.08
SUMIDEN WIRE PRODUCTS TAP | 60 | ETL.8141 |  | ACT | 0.19 |  |  |  | 0.19
SUNOL TAP | 60 | ETL.7671 |  | ACT | 0.08 |  |  |  | 0.08
SURF TAP | 115 | ETL.1381 |  | ACT | 11.37 |  | 2.08 |  | 9.29
SUTTER HOME SW STA-LOCKEFORD-LODI | 60 | ETL.8068 |  | ACT | 29.76 |  |  |  | 29.76
SUTTER HOME SW STA-STAGG | 60 | ETL.8070 |  | ACT | 17.13 |  |  |  | 17.13
SUTTER HOME-SUTTER HOME SW STA | 60 | ETL.8069 |  | ACT | 0.03 |  |  |  | 0.03
SWIFT-METCALF | 115 | ETL.3900 |  | ACT | 8.93 |  |  |  | 8.93
SYCAMORE CREEK-NOTRE DAME-TABLE MTN | 115 | ETL.4314 |  | ACT | 20.34 |  |  |  | 20.34
SYCAMORE TAP | 70 | ETL.9281 |  | ACT | 2.04 |  |  |  | 2.04
TABLE MTN-BUTTE #1 | 115 | ETL.3910 |  | ACT | 19.54 |  |  |  | 19.54
TABLE MTN-BUTTE #2 | 115 | ETL.3920 |  | ACT | 15.82 |  |  |  | 15.82
TABLE MTN-PALERMO | 230 | ETL.5690 |  | ACT | 14.57 |  | 7.85 |  | 6.72
TABLE MTN-PEACHTON | 60 | ETL.8425 |  | ACT | 14.84 |  |  |  | 14.84
TABLE MTN-RIO OSO | 230 | ETL.5700 |  | ACT | 50.18 |  | 12.38 |  | 37.8
TABLE MTN-TESLA | 500 | ETL.6080 |  | ACT | 135 |  |  |  | 135
TABLE MTN-VACA | 500 | ETL.6090 |  | ACT | 83.3 |  |  |  | 83.3
TAFT-CHALK CLIFF | 115 | ETL.3940 |  | ACT | 7.18 |  |  |  | 7.18
TAFT-CUYAMA #1 | 70 | ETL.9200 |  | ACT | 19.25 |  |  |  | 19.25
TAFT-CUYAMA #2 | 70 | ETL.9210 |  | ACT | 18.74 |  |  |  | 18.74
TAFT-ELK HILLS | 70 | ETL.9220 |  | ACT | 12.39 |  |  |  | 12.39
TAFT-MARICOPA | 70 | ETL.9230 |  | ACT | 5.98 |  |  |  | 5.98
TASSAJARA-NEWARK | 230 | ETL.5920 |  | ACT | 31.8 | 11.36 | 7 | 0.48 | 12.96
TECUYA TAP | 70 | ETL.9311 |  | ACT | 1.92 |  |  |  | 1.92
TEICHERT TAP | 115 | ETL.1266 |  | ACT | 2.11 |  |  |  | 2.11
TEJON-LEBEC | 70 | ETL.9250 |  | ACT | 12.95 |  | 5.8 |  | 7.15
TEMBLOR-KERNRIDGE | 115 | ETL.3950 |  | ACT | 4.78 |  |  |  | 4.78
TEMBLOR-SAN LUIS OBISPO | 115 | ETL.3960 |  | ACT | 57.78 | 11.43 | 19.59 |  | 26.76
TEMPLETON-ATASCADERO | 70 | ETL.9410 |  | ACT | 8.82 |  | 5.1 |  | 3.72
TEMPLETON-GATES | 230 | ETL.5934 |  | ACT | 52.18 |  | 6.97 |  | 45.21
TERMINOUS TAP | 60 | ETL.8071 |  | ACT | 3.01 |  |  |  | 3.01
TES TAP | 230 | ETL.4531 |  | ACT | 3.28 |  |  |  | 3.28
TESLA-LAWRENCE LAB | 115 | ETL.4250 |  | ACT | 9.02 |  |  |  | 9.02
TESLA-LOS BANOS #1 | 500 | ETL.6100 |  | ACT | 57.14 |  | 3.68 |  | 53.46
TESLA-METCALF | 500 | ETL.6110 |  | ACT | 35.31 |  | 27.79 |  | 7.52
TESLA-NEWARK #1 | 230 | ETL.5720 |  | ACT | 28.19 |  | 4.78 | 0.48 | 22.93
TESLA-NEWARK #2 | 230 | ETL.5354 |  | ACT | 40.82 |  | 8.14 | 0.48 | 32.2
TESLA-RAVENSWOOD | 230 | ETL.5730 |  | ACT | 37.14 |  | 4.93 | 0.48 | 31.73
TESLA-SALADO #1 | 115 | ETL.3990 |  | ACT | 32.08 |  | 3.46 |  | 28.62
TESLA-SALADO-MANTECA | 115 | ETL.4000 |  | ACT | 53.97 |  | 3.97 |  | 50
TESLA-SCHULTE SW STA #1 | 115 | ETL.3980 |  | ACT | 7.37 |  |  |  | 7.37
TESLA-SCHULTE SW STA #2 | 115 | ETL.3970 |  | ACT | 7.34 |  |  |  | 7.34
TESLA-STOCKTON COGEN JCT | 115 | ETL.4010 |  | ACT | 25.08 |  |  |  | 25.08
TESLA-TRACY #1 | 230 | ETL.5740 |  | ACT | 5.68 |  |  |  | 5.68
TESLA-TRACY #2 | 230 | ETL.5750 |  | ACT | 5.68 |  |  |  | 5.68
TESLA-TRACY(115KV) | 115 | ETL.4020 |  | ACT | 27.85 |  |  |  | 27.85
TESLA-TRACY(115KV) | 115 | ETL.4020 |  | IDL | 1.15 |  |  |  | 1.15
TESLA-TRACY(500KV) | 500 | ETL.6120 |  | ACT | 1.13 |  |  |  | 1.13
TESLA-WESTLEY | 230 | ETL.5760 |  | ACT | 45.06 |  |  |  | 45.06
TESORO-SOBRANTE | 230 | ETL.5670 |  | ACT | 12.32 | 0.56 | 5.8 |  | 5.96
TEVIS #1 TAP | 115 | ETL.1144 |  | ACT | 3.25 |  |  |  | 3.25
TEVIS #2 TAP | 115 | ETL.1143 |  | ACT | 3.29 |  |  |  | 3.29
TEXACO BASIC SCHOOL TAP | 70 | ETL.8972 |  | ACT | 0.75 |  |  |  | 0.75
TEXACO TAP | 60 | ETL.6411 |  | ACT | 0.72 |  |  |  | 0.72
THERMAL ENERGY TAP | 115 | ETL.4011 |  | IDL | 0.71 |  |  |  | 0.71
TIDEWATER-SOBRANTE | 230 | ETL.5770 |  | ACT | 12.32 | 0.56 | 5.78 |  | 5.98
TIGER CREEK-ELECTRA | 230 | ETL.5780 |  | ACT | 13.68 | 8.58 | 5.1 |  | 0
TIGER CREEK-VALLEY SPRINGS | 230 | ETL.5790 |  | ACT | 24.22 | 8.72 | 12.21 |  | 3.29
TIVY VALLEY-REEDLEY | 70 | ETL.9260 |  | ACT | 12.3 |  |  |  | 12.3
TOCALOMA TAP | 60 | ETL.7721 |  | ACT | 1.03 |  | 1.03 |  | 0
TORNADO TAP | 70 | ETL.8572 |  | ACT | 0.06 |  |  |  | 0.06
TRACY-LOS BANOS | 500 | ETL.6130 |  | ACT | 56.23 |  | 3.57 |  | 52.66
TRANQUILITY SW STA-SCARLET PV | 230 | ETL.1392 |  | ACT | 0.28 |  |  |  | 0.28
TRANQUILLITY SW STA-HELM | 230 | ETL.5370 |  | ACT | 12.68 |  |  |  | 12.68
TRANQUILLITY SW STA-KEARNEY | 230 | ETL.5380 |  | ACT | 36.9 |  |  |  | 36.9
TRANQUILLITY SW STA-OCHO SW STA | 230 | ETL.1452 |  | ACT | 0.03 |  |  |  | 0.03
TRANQUILLITY SW STA-TRANQUILLITY PV | 230 | ETL.1454 |  | ACT | 0.03 |  |  |  | 0.03
TRAVIS TAP | 60 | ETL.6731 |  | ACT | 2.88 |  |  |  | 2.88
TRIMBLE-SAN JOSE B | 115 | ETL.4030 |  | ACT | 2.54 |  |  |  | 2.54
TRINIDAD TAP | 60 | ETL.6811 |  | ACT | 1.34 |  |  |  | 1.34
TRINITY-COTTONWOOD | 115 | ETL.4040 |  | ACT | 45.97 | 10.89 | 31.92 |  | 3.16
TRINITY-MAPLE CREEK | 60 | ETL.8170 |  | ACT | 55.48 |  | 54.97 |  | 0.51
TULLOCH TAP | 115 | ETL.1071 |  | ACT | 0.31 |  | 0.28 |  | 0.03
TULUCAY-NAPA #1 | 60 | ETL.8180 |  | ACT | 9.72 |  | 4.99 |  | 4.73
TULUCAY-NAPA #2 | 60 | ETL.8190 |  | ACT | 3.93 |  |  |  | 3.93
TULUCAY-VACA | 230 | ETL.5800 |  | ACT | 23.63 |  | 16.68 |  | 6.95
TUPMAN-NORCO TAP | 115 | ETL.2592 |  | ACT | 6.67 |  |  |  | 6.67
UC DAVIS #1 TAP | 115 | ETL.6670 |  | ACT | 1.59 |  |  |  | 1.59
UC DAVIS #2 TAP | 115 | ETL.6680 |  | ACT | 1.61 |  |  |  | 1.61
UKIAH-HOPLAND-CLOVERDALE | 115 | ETL.4050 |  | ACT | 31.19 | 7.15 | 17.12 |  | 6.92
ULTRA POWER TAP | 60 | ETL.6803 |  | ACT | 1.17 |  |  |  | 1.17
ULTRAPOWER (OGLE) TAP | 115 | ETL.2121 |  | ACT | 2.45 |  |  |  | 2.45
UNION CHEMICAL TAP | 60 | ETL.6351 |  | ACT | 1.04 |  | 0.57 |  | 0.47
UNION OIL TAP | 115 | ETL.4280 |  | ACT | 0.5 |  |  |  | 0.5
UNITED COGEN INC TAP | 115 | ETL.2241 |  | ACT | 0.09 |  |  |  | 0.09
UNITED COGEN INC TAP | 115 | ETL.2241 |  | IDL | 0.59 |  |  |  | 0.59
UNIVERSITY COGEN TAP | 115 | ETL.3941 |  | ACT | 0.22 |  |  |  | 0.22
URICH TAP | 60 | ETL.6373 |  | ACT | 0.21 |  |  |  | 0.21
US WINDPOWER #3 TAP | 230 | ETL.4521 |  | ACT | 0.06 | 0.06 |  |  | 0
US WINDPOWER TAP | 60 | ETL.8261 |  | ACT | 1.52 |  |  |  | 1.52
VACA DIXON-MORAGA #1 | 230 | ETL.5935 |  | IDL | 3.08 |  |  |  | 3.08
VACA-BAHIA | 230 | ETL.5810 |  | ACT | 33.9 |  | 13.53 |  | 20.37
VACA-LAKEVILLE #1 | 230 | ETL.5840 |  | ACT | 40.93 |  | 18.48 |  | 22.45
VACA-LAMBIE SW STA | 230 | ETL.5845 |  | ACT | 13.95 |  |  |  | 13.95
VACA-PARKWAY | 230 | ETL.5850 |  | ACT | 27.76 |  | 13.55 |  | 14.21
VACA-PEABODY | 230 | ETL.5821 |  | ACT | 9.69 |  |  |  | 9.69
VACA-PLAINFIELD | 60 | ETL.8200 |  | ACT | 29.83 |  |  |  | 29.83
VACA-SUISUN | 115 | ETL.4070 |  | ACT | 22.92 |  | 8.05 |  | 14.87
VACA-SUISUN | 115 | ETL.4070 |  | IDL | 0.19 |  |  |  | 0.19
VACA-SUISUN-JAMESON | 115 | ETL.4080 |  | ACT | 25.46 |  | 8.05 |  | 17.41
VACA-TESLA | 500 | ETL.6140 |  | ACT | 57 |  |  |  | 57
VACA-VACAVILLE-CORDELIA | 115 | ETL.4090 |  | ACT | 22.04 |  | 8.06 |  | 13.98
VACA-VACAVILLE-JAMESON-NORTH TOWER | 115 | ETL.4100 |  | ACT | 36.2 |  | 8.05 |  | 28.15
VALLEY CHILDRENS HOSPITAL TAP | 115 | ETL.2142 |  | ACT | 0.03 |  |  |  | 0.03
VALLEY SPRINGS #1 | 60 | ETL.8210 |  | ACT | 27.27 |  | 10.37 |  | 16.9
VALLEY SPRINGS #2 | 60 | ETL.9460 |  | ACT | 25.65 |  | 9.31 |  | 16.34
VALLEY SPRINGS-BELLOTA | 230 | ETL.5860 |  | ACT | 20.67 |  | 5.41 |  | 15.26
VALLEY SPRINGS-CALAVERAS CEMENT | 60 | ETL.8220 |  | ACT | 7.91 |  | 7.6 |  | 0.31
VALLEY SPRINGS-CLAY | 60 | ETL.8264 |  | ACT | 17.31 |  | 10.9 | 0 | 6.41
VALLEY SPRINGS-MARTELL #1 | 60 | ETL.8240 |  | ACT | 12.75 |  | 7.33 |  | 5.42
VALLEY VIEW #1 TAP | 115 | ETL.3151 |  | ACT | 0.96 |  | 0.01 |  | 0.95
VALLEY VIEW #2 TAP | 115 | ETL.3161 |  | ACT | 0.97 |  | 0.01 |  | 0.96
VASCO-HERDLYN | 60 | ETL.8260 |  | ACT | 10.91 |  |  |  | 10.91
VASONA-METCALF | 230 | ETL.5932 |  | ACT | 13.29 |  | 3.38 | 0.01 | 9.9
VEDDER TAP | 115 | ETL.2141 |  | ACT | 11.09 |  | 4.84 |  | 6.25
VICTOR TAP | 60 | ETL.7442 |  | ACT | 0.04 |  |  |  | 0.04
VIEJO-MONTEREY | 60 | ETL.8270 |  | ACT | 2.28 |  | 0.63 |  | 1.65
VIERRA-TRACY-KASSON | 115 | ETL.4310 |  | ACT | 10.49 |  |  |  | 10.49
VINEYARD-NEWARK | 230 | ETL.4536 |  | ACT | 14.36 |  | 2.79 | 0.5 | 11.07
VOLTA-DESCHUTES | 60 | ETL.8290 |  | ACT | 20.85 | 7.58 | 12.52 |  | 0.75
VOLTA-SOUTH | 60 | ETL.8300 |  | ACT | 4.86 | 0.98 | 3.88 |  | 0
WADHAM TAP | 60 | ETL.6601 |  | ACT | 1.68 |  |  |  | 1.68
WARNERVILLE-WILSON | 230 | ETL.5870 |  | ACT | 38.41 |  |  |  | 38.41
WASCO PRISON TAP | 115 | ETL.3641 |  | ACT | 0.54 |  |  |  | 0.54
WASCO-FAMOSO | 70 | ETL.9241 |  | ACT | 7.13 |  |  |  | 7.13
WASHOE TAP | 60 | ETL.6911 |  | ACT | 1.04 |  | 1.04 |  | 0
WATERSHED TAP | 60 | ETL.7191 |  | ACT | 0.28 |  |  |  | 0.28
WATSONVILLE-SALINAS | 60 | ETL.8310 |  | ACT | 28.39 |  | 8.23 |  | 20.16
WAUKENA SW STA-CORCORAN | 115 | ETL.8773 |  | ACT | 2.39 |  |  |  | 2.39
WEBER-CASCADE ENERGY STORAGE | 60 | ETL.1363 |  | ACT | 0.04 |  |  |  | 0.04
WEBER-FRENCH CAMP #1 | 60 | ETL.8320 |  | ACT | 6.05 |  |  |  | 6.05
WEBER-FRENCH CAMP #2 | 60 | ETL.8321 |  | ACT | 10.89 |  |  |  | 10.89
WEBER-MORMON JCT | 60 | ETL.8330 |  | ACT | 17.67 |  |  |  | 17.67
WEBER-TESLA | 230 | ETL.5880 |  | ACT | 23.71 |  |  |  | 23.71
WEEDPATCH-SAN BERNARD | 70 | ETL.9270 |  | ACT | 9.26 |  |  |  | 9.26
WEEDPATCH-WELLFIELD | 70 | ETL.9280 |  | ACT | 5.88 |  |  |  | 5.88
WEIMAR #1 | 60 | ETL.7560 |  | ACT | 13.99 | 9.89 | 4.09 |  | 0.01
WEIMAR-HALSEY | 60 | ETL.8340 |  | ACT | 6.28 |  | 6.28 |  | 0
WESIX TAP | 70 | ETL.8984 |  | ACT | 2.49 |  |  |  | 2.49
WEST FRESNO-CALIFORNIA AVE | 115 | ETL.2361 |  | ACT | 4.85 |  |  |  | 4.85
WEST POINT-VALLEY SPRINGS | 60 | ETL.8350 |  | ACT | 21.66 | 5.44 | 12.12 |  | 4.1
WEST SAC COM TOWERS | 60 | ETL.5570 |  | ACT | 0.02 |  |  |  | 0.02
WEST SACRAMENTO-BRIGHTON | 115 | ETL.4110 |  | ACT | 13.97 |  |  |  | 13.97
WEST SACRAMENTO-DAVIS | 115 | ETL.4120 |  | ACT | 12.14 |  |  |  | 12.14
WESTINGHOUSE TAP | 60 | ETL.6561 |  | ACT | 8.01 |  |  |  | 8.01
WESTINGHOUSE TAP | 60 | ETL.6561 |  | IDL | 0.07 |  |  |  | 0.07
WESTLANDS #1 RA PUMPING PLANT TAP | 115 | ETL.3242 |  | ACT | 1.05 |  |  |  | 1.05
WESTLANDS #18 RA TAP | 115 | ETL.3252 |  | ACT | 3.52 |  |  |  | 3.52
WESTLANDS TAP | 70 | ETL.8983 |  | ACT | 1.07 |  |  |  | 1.07
WESTPARK-COLUMBUS | 115 | ETL.4130 |  | ACT | 8.59 |  |  |  | 8.59
WHEELER RIDGE - SANDRINI PV | 230 | ETL.1407 |  | ACT | 0.35 |  |  |  | 0.35
WHEELER RIDGE PUMPING PLANT #1 TAP | 230 | ETL.5192 |  | ACT | 0.25 |  |  |  | 0.25
WHEELER RIDGE PUMPING PLANT #2 TAP | 230 | ETL.5202 |  | ACT | 0.23 |  |  |  | 0.23
WHEELER RIDGE-ADOBE SW STA | 115 | ETL.1982 |  | ACT | 1.34 |  |  |  | 1.34
WHEELER RIDGE-LAKEVIEW | 70 | ETL.9290 |  | ACT | 7.51 |  |  |  | 7.51
WHEELER RIDGE-SAN BERNARD | 70 | ETL.9300 |  | ACT | 5.88 |  |  |  | 5.88
WHEELER RIDGE-TEJON | 70 | ETL.9310 |  | ACT | 5.01 |  |  |  | 5.01
WHEELER RIDGE-WEEDPATCH | 70 | ETL.9320 |  | ACT | 22.44 |  |  |  | 22.44
WHISMAN-MONTA VISTA | 115 | ETL.1010 |  | ACT | 5.97 |  |  |  | 5.97
WILLOW PASS-CONTRA COSTA | 60 | ETL.8370 |  | ACT | 10.83 |  |  |  | 10.83
WILSON-ATWATER #2 | 115 | ETL.4160 |  | ACT | 15.41 |  |  |  | 15.41
WILSON-BORDEN #1 | 230 | ETL.5890 |  | ACT | 35.31 |  |  |  | 35.31
WILSON-BORDEN #2 | 230 | ETL.9001 |  | ACT | 35.37 |  |  |  | 35.37
WILSON-DAIRYLAND (12KV) | 115 | ETL.1284 |  | IDL | 5.12 |  |  |  | 5.12
WILSON-LE GRAND | 115 | ETL.4170 |  | ACT | 14.11 |  |  |  | 14.11
WILSON-MERCED #1 | 115 | ETL.4180 |  | ACT | 5.58 |  |  |  | 5.58
WILSON-MERCED #2 | 115 | ETL.4190 |  | ACT | 6.2 |  |  |  | 6.2
WILSON-ORO LOMA | 115 | ETL.4200 |  | ACT | 40.73 |  |  |  | 40.73
WIND FARMS | 60 | ETL.8380 |  | ACT | 3.75 |  |  |  | 3.75
WIND GAP PUMPING PLANT #1 TAP | 230 | ETL.5193 |  | ACT | 1.64 |  |  |  | 1.64
WIND GAP PUMPING PLANT #2 TAP | 230 | ETL.5203 |  | ACT | 1.63 |  |  |  | 1.63
WINDMASTER TAP | 230 | ETL.4491 |  | ACT | 0.11 |  |  |  | 0.11
WINDSOR-FITCH MOUNTAIN | 60 | ETL.6900 |  | ACT | 13.11 |  | 2.49 |  | 10.62
WINTU TAP | 60 | ETL.6311 |  | ACT | 1.85 |  | 0.45 |  | 1.4
WISHON-COPPERMINE | 70 | ETL.9330 |  | ACT | 19.99 | 0.11 | 14 |  | 5.88
WISHON-SAN JOAQUIN #3 | 70 | ETL.9340 |  | ACT | 7.67 | 4.89 | 2.78 |  | 0
WITCO (REFINERY) TAP | 115 | ETL.1972 |  | ACT | 0.03 |  |  |  | 0.03
WOHLER TAP | 60 | ETL.7631 |  | ACT | 1.44 |  |  |  | 1.44
WOODBRIDGE TAP | 60 | ETL.7443 |  | ACT | 0.53 |  |  |  | 0.53
WOODLAND BIOMASS TAP | 115 | ETL.4211 |  | ACT | 0.87 |  |  |  | 0.87
WOODLAND-DAVIS | 115 | ETL.4210 |  | ACT | 11.75 |  |  |  | 11.75
WOODLEAF-PALERMO | 115 | ETL.4220 |  | ACT | 19.62 | 6.53 | 11.1 |  | 1.99
WOODWARD-SHEPHERD | 115 | ETL.1895 |  | ACT | 4.84 |  |  |  | 4.84
WRIGHT TAP | 70 | ETL.8931 |  | ACT | 1.18 |  |  |  | 1.18
YUBA CITY COGEN TAP | 60 | ETL.7729 |  | ACT | 0.8 |  |  |  | 0.8
ZAMORA TAP | 115 | ETL.3471 |  | ACT | 1.92 |  |  |  | 1.92
ZANKER #1 TAP | 115 | ETL.3121 |  | ACT | 0.59 |  |  |  | 0.59
ZANKER #2 TAP | 115 | ETL.3041 |  | ACT | 0.73 |  |  |  | 0.73
ZOND WIND TAP | 60 | ETL.8381 |  | ACT | 1.19 |  |  |  | 1.19
ZAMORA TAP | 115 | ETL.3471 |  | ACT | 1.92 |  |  |  | 1.92
ZANKER #1 TAP | 115 | ETL.3121 |  | ACT | 0.59 |  |  |  | 0.59
ZANKER #2 TAP | 115 | ETL.3041 |  | ACT | 0.73 |  |  |  | 0.73
ZOND WIND TAP | 60 | ETL.8381 |  | ACT | 1.19 |  |  |  | 1.19