## All Outage Details
HFTD WIRE-DOWN OUTAGE DETAILS (2013 - 2023) |  |  |  |  | Source: Extracted from Outage Database on 1/8/2024.
DISTRIBUTION CIRCUIT & TRANSFORMER-ONLY OUTAGES
(Excluding 2.5b ME Days)
Division | Field Ops Center | Tier | Feeder Name | Feeder # | Device | Oper # | Date | FNL | OIS # | Duration | Outage Level | Basic Cause | Supplemental Cause | CESO | C Min | Open Point Latitude | Open Point Longitude | Fault Location | Weather | Failed/Involved Equipment | Equipment Condition | ILIS # | Const Type | Sus/Mom | PM # | Weather Day | Year | Month | Wire Down | Outage Fault Type | Misc | EquipTypeID | OH/UG | MEDay | Conductor Energized
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | RECLOSER | 432 | 20130103 | 51 | 724756 | 797 | Distribution Circuit | Vegetation | Tree - fell into line | 329 | 174086 | 36.3978 | -121.6492 | KINCANON RD LD SIDE 6625- NARROW DIRT RD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0001801 | OH | Sus | 41833888 | No | 2013 | JAN | Yes | Line to Ground | 99306031 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5485 | 20130106 | 705 | 726116 | 523 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 5231 | 37.1322 | -122.109 | JUST SS OF MTR 1007345500 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0002344 | OH | Sus | 41834609 | No | 2013 | JAN | Yes | Open Circuit | 99305670 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7619 | 20130106 | 937 | 726176 | 353 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2471 | 37.1129 | -121.9863 | MATTSON-2818/ 682-1913: 4546 Glenwood Dr Scotts Valley | Rain-32 - 90 F | Conductor, Overhead | On Ground | 13-0002355 | OH | Sus | 41834617 | No | 2013 | JAN | Yes | Open Circuit | 99305658 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 1445 | 20130106 | 823 | 726139 | 202 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 9696 | 36.5734 | -121.9108 | 490 AQUAJITO RD | Rain-32 - 90 F | Conductor, Overhead | On Ground | 13-0002347 | OH | Sus | 0 | No | 2013 | JAN | Yes | Three Phase Fault | 99305666 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | OTHER |  | 20130107 | 1942 | 726881 | 525 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 10641 | 37.0366 | -122.0744 | 6 SPANS LD SIDE OF 5209 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0002660 | OH | Sus | 41835222 | No | 2013 | JAN | Yes | Open Circuit | 99305459 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2104 | 83252104 | FUSE | 5023 | 20130125 | 2301 | 734669 | 924 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 40656 | 37.0135 | -121.9634 | FIRST TRANSF LD SIDE OF 5023 | Fog-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0006278 | OH | Sus | 30973389 | No | 2013 | JAN | Yes | Line to Ground | 99303275 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | OCB | OCB | 20130202 | 2342 | 737829 | 87 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 2346 | 134450 | 37.1308 | -122.1723 | 4 SPANS SOURCE SIDE OF SW 5433 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0007741 | OH | Sus | 0 | No | 2013 | FEB | Yes | Line to Line | 99302330 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 6409 | 20130219 | 1917 | 744414 | 734 | Distribution Circuit | Equipment Failure/Involved | Other | 108 | 19822 | 36.5899 | -121.9113 | 577 MAR VISTA & 2 spans SS (E/OF) 6409 | Drizzle-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 13-0011043 | OH | Sus | 30978315 | yes | 2013 | FEB | Yes | Line to Ground | 99300212 | CAW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5439 | 20130225 | 1757 | 747444 | 965 | Distribution Circuit | Vegetation | Tree - fell into line | 228 | 86875 | 37.1126 | -122.1142 | at 9305 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0012382 | OH | Sus | 30979479 | No | 2013 | FEB | Yes | Line to Line | 99299166 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 8033 | 20130226 | 1613 | 747916 | 762 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5334 | 37.1036 | -122.2768 | 1ST SP LD SIDE 8033 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0012703 | OH | Sus | 41859219 | No | 2013 | FEB | Yes |  | 99299009 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | OTHER |  | 20130305 | 2032 | 751956 | 451 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 31885 | 36.393 | -121.8772 | BANTA/5801/ 682-1736: 4 SPANS LD SD OF C/O 637 | Rain-32 - 90 F | Conductor, Overhead | On Ground | 13-0014374 | OH | Sus | 41862075 | yes | 2013 | MAR | Yes | Open Circuit | 99297894 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8427 | 20130306 | 401 | 752475 | 707 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 24975 | 37.0768 | -121.9812 | 400 CHARLES HILL RD | Rain-32 - 90 F | Conductor, Overhead | On Ground | 13-0014489 | OH | Sus | 0 | yes | 2013 | MAR | Yes | Line to Ground | 99297843 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 5076 | 20130306 | 214 | 752226 | 713 | Distribution Circuit | Vegetation | Tree - fell into line | 117 | 65151 | 37.0316 | -122.1891 | Alvarez 2814/ 535-9251: 328 Swanton Rd- Davenport | Rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0014423 | OH | Sus | 30981211 | yes | 2013 | MAR | Yes |  | 99297883 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | BIG TREES-0402 | 83050402 | OTHER |  | 20130309 | 2023 | 754742 | 332 | Distribution Circuit | Equipment Failure/Involved | Other | 838 | 231634 | 37.046 | -122.0735 | Just LD side of 8737 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0015454 | OH | Sus | 41863800 | No | 2013 | MAR | Yes | Line to Ground | 99297193 | CSO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | OTHER |  | 20130309 | 1606 | 754733 | 1165 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 11471 | 37.0699 | -122.2256 | 390 Big Creek- Davenport | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0015450 | OH | Sus | 41863751 | No | 2013 | MAR | Yes |  | 99297150 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 5989 | 20130323 | 1613 | 760855 | 427 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 3421 | 37.0574 | -121.9424 | 720 OLSON RD. | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 13-0018689 | OH | Sus | 41872903 | No | 2013 | MAR | Yes | Line to Ground | 99295010 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8331 | 20130409 | 1637 | 771926 | 1245 | Distribution Circuit | Equipment Failure/Involved | Other | 5 | 6225 | 37.0576 | -121.9737 | CAPWELL- DAVID: 305 MOUNTAIN VIEW RD | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0023199 | OH | Sus | 41878888 | yes | 2013 | APR | Yes |  | 99291414 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | OTHER |  | 20130409 | 904 | 771458 | 399 | Distribution Circuit | Equipment Failure/Involved | Other | 15 | 5453 | 37.0096 | -121.9357 | 18 SPANS LOAD SIDE OF 8095 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022953 | OH | Sus | 41878625 | yes | 2013 | APR | Yes | None | 99291692 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | OTHER |  | 20130418 | 1505 | 777855 | 779 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 11410 | 36.9946 | -122.0282 | 1ST SPAN LD SIDE OF 5365 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0025690 | OH | Sus | 41885800 | No | 2013 | APR | Yes |  | 99289665 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2104 | 83252104 | SWITCH | 62153 | 20130421 | 154 | 778794 | 69 | Distribution Circuit | Equipment Failure/Involved | Other | 10 | 529 | 37.0447 | -121.9652 | 6 spans S/OF 2613 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on object | 13-0026043 | OH | Sus | 0 | No | 2013 | APR | Yes | Line to Ground | 99289387 | CSO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | RECLOSER | 2762 | 20130429 | 2212 | 783883 | 688 | Distribution Circuit | 3rd Party | Vehicle | 1182 | 74070 | 36.558 | -121.7505 | 89 ROBLEY | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0028122 | OH | Sus | 0 | No | 2013 | APR | Yes | Open Circuit | 99287841 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | OTHER |  | 20130429 | 312 | 783166 | 743 | Distribution Circuit | 3rd Party | Vehicle | 96 | 70898 | 37.0162 | -121.937 | CRIVELLO- 2808/ 682-1912: 6362 GLEN HAVEN RD | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0027839 | OH | Sus | 30992942 | No | 2013 | APR | Yes | Open Circuit | 99288016 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | OTHER |  | 20130430 | 2109 | 784506 | 455 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 14805 | 37.0306 | -122.07 | GLEN GARY RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0028458 | OH | Sus | 41891117 | yes | 2013 | APR | Yes | None | 99287620 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6577 | 20130505 | 1345 | 787772 | 725 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 34075 | 37.0487 | -121.8084 | Alvarez 2814/ 535-9251: 2026 Eureka Canyon Rd- Watsonville | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0029656 | OH | Sus | 0 | yes | 2013 | MAY | Yes | Line to Ground | 99286645 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 9309 | 20130513 | 1451 | 792189 | 1344 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 37477 | 37.1186 | -122.1154 | 966 ELSIE MAE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0031613 | OH | Sus | 41897423 | yes | 2013 | MAY | Yes |  | 99285172 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | RECLOSER | 10714 | 20130513 | 512 | 791858 | 638 | Distribution Circuit | Vegetation | Tree - bark fell into line | 453 | 84407 | 36.9779 | -121.8666 | LARKIN VALLEY RD. | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0031388 | OH | Sus | 30996103 | yes | 2013 | MAY | Yes | Line to Line | 99285350 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 7687 | 20130516 | 1135 | 793745 | 220 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 2860 | 36.5818 | -121.863 | 1 SPAN LOAD SIDE OF 7687 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0032332 | OH | Sus | 41899964 | No | 2013 | MAY | Yes | Line to Ground | 99284746 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 4567 | 20130521 | 1801 | 796193 | 455 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2730 | 37.0329 | -121.9868 | 192 FAST LANE- SC | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0033463 | OH | Sus | 41902037 | yes | 2013 | MAY | Yes | Line to Ground | 99284002 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 5213 | 20130525 | 1510 | 798303 | 522 | Distribution Circuit | Vegetation | Tree - branch fell on line | 51 | 23850 | 37.0323 | -122.0769 | FLUITT- 3755 / 831-682-1793: 1258 fern ave | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0034389 | OH | Sus | 41903858 | No | 2013 | MAY | Yes | Line to Ground | 99283364 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 2567 | 20130527 | 247 | 798934 | 356 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 47 | 16732 | 36.6018 | -121.9374 | BANTA/5801/ 682-1736: 2567 C/O POLE TOP BURNED OFF-CUT OUT AND BELLS FLOATING AT PHONE LEVEL | Fog-32 - 90 F | Cutout, fuse holder | Broken, wire on object | 13-0034512 | OH | Sus | 41903986 | yes | 2013 | MAY | Yes | Line to Ground | 99283197 | CFH | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | OCB | OCB | 20130602 | 139 | 802385 | 621 | Distribution Circuit | 3rd Party | Metallic Balloon | 3576 | 319991 | 36.9792 | -121.867 | APWELL - 3915 / 831-206-1280: BEHIND 401 CORROLITOS RD- WATS | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0035895 | OH | Sus | 41906342 | No | 2013 | JUN | Yes | Line to Ground | 99282292 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2102 | 83252102 | FUSE | 11105 | 20130607 | 348 | 805184 | 410 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 2460 | 37.0112 | -122.075 | BRANDT- 4179 / 831-212-2088: 2519 Empire Grade ucc branch broke wire 40Ft worth | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0037306 | OH | Sus | 31001204 | yes | 2013 | JUN | Yes | Line to Ground | 99281462 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | OTHER |  | 20130612 | 1610 | 809547 | 756 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 34308 | 37.0182 | -121.7878 | FLUITT- 3755 / 831-682-1793: 733 browns vly. and 3 spans past has 2 of 3 conductors broke. | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0039168 | OH | Sus | 31002476 | No | 2013 | JUN | Yes | Line to Ground | 99280135 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7593 | 20130618 | 1749 | 812771 | 453 | Distribution Circuit | Vegetation | Tree - branch fell on line | 85 | 29513 | 37.1057 | -121.9723 | BRANDT- 4179 / 831-212-2088: laruel rd assist M Crivello | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0040762 | OH | Sus | 41915919 | No | 2013 | JUN | Yes | Line to Ground | 99279190 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | LOMPICO-0401 | 88880401 | OTHER |  | 20130620 | 1542 | 813842 | 1369 | Distribution Circuit | Vegetation | Tree - fell into line | 487 | 250138 | 37.1051 | -122.0515 | STORMENT- 4178 / 831-682-1809: 10775 Lompico Rd.- Felton | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0041295 | OH | Sus | 31004148 | No | 2013 | JUN | Yes |  | 99278767 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | FUSE | 7791 | 20130621 | 250 | 814107 | 505 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 6750 | 36.264 | -121.7982 | HARRIS- STEVE: SSD 641 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0041390 | OH | Sus | 0 | No | 2013 | JUN | Yes | Line to Ground | 99278733 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | JOLON-1102 | 182981102 | SWITCH | 7531 | 20130622 | 2006 | 814791 | 336 | Distribution Circuit | Equipment Failure/Involved | Other | 17 | 1071 | 36.0476 | -121.1827 | TUCKER/ 7867/ 682-1744: sulpher springs road off jolon road | Clear-32 - 90 F | Insulator | Broken, wire on ground | 13-0041775 | OH | Sus | 41917591 | No | 2013 | JUN | Yes | Line to Ground | 99277873 | INS | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2105 | 83252105 | FUSE | 4471 | 20130625 | 1812 | 817362 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 201 | 73122 | 37.001 | -122.0141 | CRIVELLO- 4176 / 831-682-1912: 315 isbel | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0042694 | OH | Sus | 31005254 | yes | 2013 | JUN | Yes | Line to Line | 99277920 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 7017 | 20130628 | 1509 | 819476 | 961 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 6434 | 37.1755 | -122.1388 | at MTR #1007591087 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0043505 | OH | Sus | 31005993 | yes | 2013 | JUN | Yes | Line to Ground | 99277229 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 5217 | 20130629 | 1713 | 820711 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 2350 | 37.0371 | -122.0662 | FLUITT- 3755 / 831-682-1793: 244 mckee and 2 spans affected | Clear-Above 90 F | Conductor, Overhead | Broken, wire on ground | 13-0043781 | OH | Sus | 41920058 | yes | 2013 | JUN | Yes |  | 99277068 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9435 | 20130629 | 601 | 820088 | 417 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 3028 | 37.074 | -122.0803 | at MTR #1007591459 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0043630 | OH | Sus | 41919911 | yes | 2013 | JUN | Yes |  | 99277191 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 6597 | 20130630 | 1326 | 821634 | 427 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1524 | 36.9969 | -121.7163 | 6 spans LD side of 12155 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0043994 | OH | Sus | 41920109 | yes | 2013 | JUN | Yes | Line to Ground | 99276810 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2104 | 83252104 | FUSE | 7713 | 20130707 | 1420 | 827194 | 817 | Distribution Circuit | 3rd Party | Vehicle | 227 | 185459 | 37.0012 | -121.9756 | 5006 THURBER LN | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0045622 | OH | Sus | 31007188 | No | 2013 | JUL | Yes | Line to Ground | 99275469 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OILFIELDS-1103 | 182391103 | OTHER |  | 20130708 | 41 | 827327 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 6602 | 35.8923 | -120.99 | 5 SPANS SS OF MTR 1008096613 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0045650 | OH | Sus | 41922330 | No | 2013 | JUL | Yes | Open Circuit | 99275422 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | RESERVATION ROAD-1101 | 182731101 | FUSE | 5021 | 20130710 | 1849 | 829420 | 421 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 12074 | 36.5548 | -121.6955 | MTR 1009262673 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0046537 | OH | Sus | 41924872 | No | 2013 | JUL | Yes | Line to Ground | 99274866 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 6037 | 20130715 | 1835 | 831908 | 580 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 12760 | 37.0731 | -122.0156 | 125 MCKENZIE CREEK RD | Clear-32 - 90 F | Bushing | Broken, wire on ground | 13-0047563 | OH | Sus | 31008905 | No | 2013 | JUL | Yes | Line to Ground | 99274143 | BU | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 9309 | 20130720 | 326 | 835234 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 24865 | 37.1186 | -122.1154 | STORMENT- 4178 / 831-682-1809: 1025 Nina Ct.- B.C. | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0048805 | OH | Sus | 41930309 | No | 2013 | JUL | Yes | Line to Ground | 99273308 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5501 | 20130726 | 1427 | 839042 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 22978 | 37.1431 | -122.1317 | 1 span SS of 12499 on main line | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0050469 | OH | Sus | 41933652 | No | 2013 | JUL | Yes | Line to Ground | 99272143 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5487 | 20130731 | 2216 | 841494 | 419 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 23045 | 37.1375 | -122.1006 | FLUITT- 3755 / 831-682-1793: hopkins gulch rd at dorrance | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0051602 | OH | Sus | 41935718 | No | 2013 | JUL | Yes | Line to Line | 99271442 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | OTHER |  | 20130731 | 2257 | 841507 | 688 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 40149 | 37.0226 | -121.7837 | SS OF FU-6651- BROWNS VALLEY RD. | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0051606 | OH | Sus | 41936177 | No | 2013 | JUL | Yes |  | 99271415 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 3413 | 20130804 | 43 | 842824 | 526 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1688 | 37.0301 | -121.858 | 2 SPANS SS OF 6001 APTOS VIEW RD MTR#1009756305 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0052241 | OH | Sus | 41937840 | No | 2013 | AUG | Yes | Line to Ground | 99271027 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 7123 | 20130810 | 2137 | 846289 | 468 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 5148 | 37.0653 | -122.0578 | EL ALAMEIN RD. | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0053820 | OH | Sus | 0 | No | 2013 | AUG | Yes |  | 99269990 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20130812 | 1513 | 847126 | 636 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 60412 | 37.0666 | -122.0336 | 2 SP LD SIDE OF 6087 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0054077 | OH | Sus | 31014391 | No | 2013 | AUG | Yes | Open Circuit | 99269750 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | RESERVATION ROAD-1102 | 182731102 | OCB | OCB | 20130816 | 1108 | 849652 | 250 | Distribution Circuit | Equipment Failure/Involved | Other | 2103 | 88950 | 36.6245 | -121.6884 | HWY 68 E/OF C/OUTS 24211 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0055150 | OH | Sus | 41944601 | No | 2013 | AUG | Yes | Line to Ground | 99268961 | CSO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 9125 | 20130821 | 1542 | 853592 | 733 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 8466 | 37.1006 | -122.086 | 8 SPANS LD SIDE OF FUSE 5151 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0056503 | OH | Sus | 41946343 | No | 2013 | AUG | Yes | Line to Ground | 99267813 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 11847 | 20130825 | 120 | 855240 | 670 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 48936 | 37.0397 | -122.0766 | 473 GOLD AVE. | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0057297 | OH | Sus | 41947260 | No | 2013 | AUG | Yes | Line to Ground | 99267267 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 11905 | 20130827 | 724 | 856198 | 346 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 346 | 37.0558 | -121.9248 | 5 SPANS LOAD SIDE OF 11905 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0057705 | OH | Sus | 41948144 | No | 2013 | AUG | Yes |  | 99266960 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 12840 | 20130904 | 1715 | 860725 | 660 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 21155 | 37.0538 | -121.9548 | CAPWELL - 3915 / 831-206-1280: 1450 LAUREL GLEN RD- SOQUEL | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0059771 | OH | Sus | 41950803 | No | 2013 | SEP | Yes | Line to Ground | 99265577 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | FUSE | 88973 | 20130906 | 1322 | 861732 | 128 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 128 | 36.2198 | -121.7535 | 48657 HWY 1 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0060295 | OH | Sus | 41951936 | No | 2013 | SEP | Yes | Line to Ground | 99265265 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7457 | 20130916 | 1718 | 866965 | 652 | Distribution Circuit | 3rd Party | Vehicle | 328 | 213856 | 37.0369 | -122.042 | CRIVELLO- 4176 / 831-682-1912: LOCKWOOD LANE and wispering pines | Clear-32 - 90 F | Pole-Wood | Broken, wire on object | 13-0062392 | OH | Sus | 31021858 | No | 2013 | SEP | Yes | Line to Line | 99263685 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | OCB | OCB | 20130918 | 111 | 867795 | 508 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 9948 | 37.0491 | -122.0646 | 6744 HWY. 9- FELTON | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0062711 | OH | Sus | 41960867 | No | 2013 | SEP | Yes | Line to Ground | 99263463 | CSO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 6713 | 20130919 | 1443 | 868761 | 769 | Distribution Circuit | Vegetation | Tree - branch fell on line | 93 | 36166 | 36.4701 | -121.7241 | Sissom/ 5808/ 206-2617: 79 Hitchcock cyn | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0063197 | OH | Sus | 31022761 | No | 2013 | SEP | Yes | Line to Ground | 99263118 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 12760 | 20130921 | 1223 | 870206 | 547 | Distribution Circuit | Equipment Failure/Involved | Other | 490 | 73550 | 37.0674 | -121.9964 | 4555 BRANCIFORTE DR | Drizzle-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0063685 | OH | Sus | 41962659 | yes | 2013 | SEP | Yes | Line to Ground | 99262809 | CSO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 6045 | 20130921 | 1343 | 870966 | 1302 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 72912 | 37.097 | -121.975 | MTR # 1009700851 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0063874 | OH | Sus | 0 | yes | 2013 | SEP | Yes | Line to Ground | 99262601 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 11737 | 20130925 | 104 | 872729 | 626 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 11196 | 37.0697 | -122.1302 | BETWEEN 24 GRAINGER LN (MTR#B34416) & 49 GRAINGER LN | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0064611 | OH | Sus | 41963909 | No | 2013 | SEP | Yes | Line to Ground | 99261990 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | OTHER |  | 20131003 | 1107 | ODB-9925 | 466 | Distribution Circuit | 3rd Party | Vehicle | 327 | 62839 | 36.5383 | -121.7252 | MAINLINE at FU-20461 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0066813 | OH | Sus | 31025881 | yes | 2013 | OCT | Yes |  | 99257816 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6577 | 20131004 | 434 | 878069 | 868 | Distribution Circuit | Equipment Failure/Involved | Other | 47 | 28885 | 37.0487 | -121.8084 | at MTR 1007591875 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0067178 | OH | Sus | 41967826 | yes | 2013 | OCT | Yes |  | 99260269 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 7601 | 20131008 | 1703 | 881443 | 24 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 24 | 36.4489 | -121.6833 | 3 SP SS OF MTR 1009300264 | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 13-0068205 | OH | Sus | 41969192 | No | 2013 | OCT | Yes | Multi-Fault | 99259498 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | LOMPICO-0401 | 88880401 | RECLOSER | 10294 | 20131008 | 427 | 881013 | 706 | Distribution Circuit | Equipment Failure/Involved | Other | 430 | 130032 | 37.0991 | -122.053 | 10837 LOMPICO RD | Clear-32 - 90 F | Insulator | Broken, wire on ground | 13-0067945 | OH | Sus | 31026755 | No | 2013 | OCT | Yes | None | 99259623 | INS | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 3459 | 20131008 | 1448 | 881420 | 768 | Distribution Circuit | Equipment Failure/Involved | Other | 63 | 17591 | 37.0246 | -121.8835 | 5 SP LS of 12675 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0068196 | OH | Sus | 31027029 | No | 2013 | OCT | Yes | Line to Ground | 99259500 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9443 | 20131027 | 1028 | 890835 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 37521 | 37.0817 | -122.0731 | 3 SPANS LOAD SIDE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0072387 | OH | Sus | 31031567 | yes | 2013 | OCT | Yes |  | 99256471 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 7773 | 20131029 | 1133 | 893407 | 948 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 32232 | 37.1881 | -122.1584 | MTR 1007587836 | Drizzle-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 13-0073108 | OH | Sus | 31032181 | No | 2013 | OCT | Yes | Line to Ground | 99255829 | CAW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 3029 | 20131120 | 214 | 905236 | 663 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 29835 | 36.9643 | -121.8171 | 733 CALABASA RD & ACROSS FROM 700 CALABASAS RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0077227 | OH | Sus | 31037239 | yes | 2013 | NOV | Yes | Open Circuit | 99252614 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER |  | 20131206 | 2357 | 921537 | 649 | Distribution Circuit | Equipment Failure/Involved | Other | 23 | 14033 | 37.0532 | -122.0773 | BLAIR ST- FELTON | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081134 | OH | Sus | 31041165 | yes | 2013 | DEC | Yes | Open Circuit | 99249055 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 5215 | 20131207 | 1121 | 922750 | 416 | Distribution Circuit | Vegetation | Tree - branch fell on line | 60 | 24960 | 37.0323 | -122.0765 | 1260 SCENIC DR | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081322 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99248901 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 1445 | 20131210 | 1317 | 925099 | 633 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 21031 | 36.5734 | -121.9108 | 3 SPANS LS OF 1445 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081800 | OH | Sus | 42044588 | No | 2013 | DEC | Yes | Line to Ground | 99248393 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | FUSE | 205 | 20131217 | 1155 | 929065 | 11518 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 3 | 18762 | 36.251 | -121.7871 | LOAD SIDE OF FUSES 205 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0082644 | OH | Sus | 0 | No | 2013 | DEC | Yes | Three Phase Fault | 99246506 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5503 | 20131219 | 1326 | 930223 | 655 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 24890 | 37.1461 | -122.129 | CRIVELLO- 4176 / 831-682-1912: 15050 fern | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0082926 | OH | Sus | 42048939 | yes | 2013 | DEC | Yes | Line to Ground | 99246962 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8243 | 20131228 | 1343 | 934835 | 1252 | Distribution Circuit | Equipment Failure/Involved | Other | 12 | 15024 | 37.1168 | -121.9668 | FLUITT- 3755 / 831-682-1793: red tail ridge | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0083570 | OH | Sus | 42051336 | No | 2013 | DEC | Yes | Open Circuit | 99245960 | CSO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 4741 | 20140117 | 1708 | 943500 | 612 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 13053 | 37.0907 | -122.1052 | 805 FANNING GRAD | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0004973 | OH | Sus | 42062219 | No | 2014 | JAN | Yes | Multi-Fault | 99243839 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 5491 | 20140121 | 2127 | 945083 | 484 | Distribution Circuit | 3rd Party | Vehicle | 194 | 22804 | 37.0442 | -121.9842 | 5491 FUSES | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0005480 | OH | Sus | 31050951 | No | 2014 | JAN | Yes | Line to Line | 99243459 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5183 | 20140131 | 1558 | 955868 | 670 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 11452 | 37.1078 | -122.1098 | 14 HUCKLEBERRY ISLE- BROOKDALE | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0008007 | OH | Sus | 42068734 | No | 2014 | JAN | Yes | Line to Ground | 99241886 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | SWITCH | 12521 | 20140202 | 1918 | 958699 | 612 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 3740 | 37.0946 | -122.0121 | SOURCE SIDE TO 1374 WESTON RIDGE | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0008209 | OH | Sus | 31053961 | yes | 2014 | FEB | Yes | None | 99241697 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 6813 | 20140206 | 529 | 960481 | 367 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 4771 | 36.5713 | -121.8905 | 5 SPANS SS OF 7779 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0009128 | OH | Sus | 42071586 | yes | 2014 | FEB | Yes | Line to Line | 99241197 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2105 | 83692105 | OTHER |  | 20140206 | 2206 | 961124 | 769 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 54959 | 36.9723 | -121.881 | 2 SPANS S/OF 5805 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0009462 | OH | Sus | 31055235 | yes | 2014 | FEB | Yes | Open Circuit | 99241055 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9373 | 20140207 | 1519 | 961536 | 581 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 16735 | 37.1261 | -122.1218 | 13181 MIDDLETON AVE | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0009687 | OH | Sus | 31055408 | yes | 2014 | FEB | Yes | Line to Ground | 99240954 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 7307 | 20140208 | 716 | 962562 | 395 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2370 | 37.0383 | -122.0698 | 1 SPAN LOAD SIDE OF 7307 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0009854 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Ground | 99240766 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10786 | 20140209 | 1352 | 964322 | 707 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 30785 | 37.0925 | -122.0969 | ALBA & WESTERN | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0010155 | OH | Sus | 31055653 | yes | 2014 | FEB | Yes |  | 99240471 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER |  | 20140210 | 1430 | 965284 | 400 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 400 | 37.1835 | -122.2088 | 815 BIG BASIN PARK | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0010467 | OH | Sus | 42075566 | yes | 2014 | FEB | Yes | None | 99240241 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 9755 | 20140210 | 1958 | 965493 | 477 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 5247 | 37.1665 | -122.1874 | 20604 LITTLE BASIN RD. MTR 0J4445 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0010545 | OH | Sus | 42075703 | yes | 2014 | FEB | Yes | Line to Ground | 99240196 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 11301 | 20140210 | 208 | 964697 | 832 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 832 | 37.0299 | -121.7839 | 1 SPAN LOAD SIDE | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0010304 | OH | Sus | 42075196 | yes | 2014 | FEB | Yes | None | 99240319 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 6103 | 20140211 | 6 | 965573 | 704 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 5739 | 37.0116 | -122.012 | ON UNFUSED TAP 100 YARDS PAST 401 REDWOOD- MTR 1006216514 DEAD LINE | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0010547 | OH | Sus | 42075601 | No | 2014 | FEB | Yes | Open Circuit | 99240170 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 7993 | 20140211 | 1044 | 965841 | 282 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 13957 | 37.0283 | -121.7407 | STA SIDE OF 5645 | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0010668 | OH | Sus | 0 | No | 2014 | FEB | Yes | None | 99240056 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER |  | 20140216 | 1400 | 968202 | 165 | Distribution Circuit | Equipment Failure/Involved | Other | 3 | 495 | 37.1388 | -122.0909 | LOAD SIDE OF TXR 315365523654 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0011583 | OH | Sus | 42079345 | No | 2014 | FEB | Yes |  | 99239421 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 8033 | 20140218 | 657 | 968794 | 504 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3528 | 37.1036 | -122.2768 | ALVAREZ- 3463 / 831-535-9251: 3642 Hwy 1- Davenport. Rancho Del Oso State Park. | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0011731 | OH | Sus | 31057341 | No | 2014 | FEB | Yes | Line to Ground | 99239281 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | OCB | OCB | 20140226 | 2110 | 973372 | 553 | Distribution Circuit | Vegetation | Tree - fell into line | 753 | 180595 | 37.0921 | -122.0965 | AT SS OF FU-7233 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0013683 | OH | Sus | 0 | yes | 2014 | FEB | Yes |  | 99238006 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10912 | 20140226 | 1955 | 972914 | 2649 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 74310 | 37.0911 | -122.0961 | at DDE POLE 4SP E/OF 11043 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0013607 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Ground | 99237733 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7315 | 20140226 | 2035 | 973144 | 850 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 25710 | 37.0406 | -122.0817 | SS OF FUCO1625 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0013698 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Ground | 99238001 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 1519 | 20140226 | 2337 | 973419 | 773 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 30504 | 37.0234 | -121.9323 | UNFUSED TAP LD SIDE OF 8399 GLE HAVEN | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0013723 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Ground | 99237992 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 711 | 20140226 | 1609 | 972857 | 1082 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 22722 | 37.0528 | -122.1604 | CARTER RD & COUNTRY ESTATES- BONNY DOON | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0013563 | OH | Sus | 42083725 | yes | 2014 | FEB | Yes | Line to Ground | 99238019 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 8033 | 20140226 | 1520 | 972803 | 457 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3199 | 37.1036 | -122.2768 | HOOVER RANCH/ LAST CHANCE | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0013578 | OH | Sus | 0 | yes | 2014 | FEB | Yes |  | 99238017 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 7279 | 20140227 | 243 | 973430 | 840 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 5040 | 37.0995 | -122.101 | TRUMBO/7732: 415 pike | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0013742 | OH | Sus | 31058669 | yes | 2014 | FEB | Yes | Line to Line | 99237984 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | BIG BASIN-1102 | 82841102 | FUSE | 8503 | 20140227 | 854 | 973609 | 866 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1732 | 37.1697 | -122.2198 | 4 SP LD SIDE OF 77767 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0013820 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Line | 99237730 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | LOMPICO-0401 | 88880401 | OTHER |  | 20140227 | 323 | 973445 | 581 | Distribution Circuit | Equipment Failure/Involved | Other | 66 | 34615 | 37.1077 | -122.0566 | 511 PORTOLA- FELTON. 3 SP LD SIDE OF 1927 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0013737 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Ground | 99237987 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 8033 | 20140227 | 800 | 973552 | 205 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 1435 | 37.1036 | -122.2768 | 8033 RIGHT ON THE SOURCE SIDE | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0013785 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Three Phase Fault | 99237957 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5421 | 20140228 | 503 | 974421 | 530 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 60420 | 37.1253 | -122.1278 | CAPWELL - 3915 / 831-206-1280: HWY 236 LOAD SIDE C/O 5421 | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0014210 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Three Phase Fault | 99237683 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 5066 | 20140228 | 704 | 974526 | 3321 | Distribution Circuit | Vegetation | Tree - branch fell on line | 108 | 79489 | 37.1705 | -122.1654 | MTR 1007591511 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0014229 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Line | 99236855 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2002 | 20140228 | 356 | 974315 | 948 | Distribution Circuit | Equipment Failure/Involved | Other | 123 | 108612 | 36.2248 | -121.7589 | 2 SP S/OF MTR 1008663252 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0014164 | OH | Sus | 31058675 | yes | 2014 | FEB | Yes | Line to Line | 99237334 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 1489 | 20140228 | 747 | 974604 | 291 | Distribution Circuit | Equipment Failure/Involved | Other | 11 | 3201 | 36.5665 | -121.9355 | 2SP LD SIDE | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0014287 | OH | Sus | 31058675 | yes | 2014 | FEB | Yes | Line to Ground | 99237623 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9597 | 20140301 | 521 | 976035 | 492 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2460 | 37.1441 | -122.0894 | 13 SPANS LD SIDE OF 9597 CLOSE TO 401 SHADOW MTN RD | Drizzle-32 - 90 F | Conductor, Overhead | On Ground | 14-0014721 | OH | Sus | 0 | yes | 2014 | MAR | Yes | Line to Line | 99237303 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 98036 | 20140301 | 1435 | 976545 | 29 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 1437 | 36.1796 | -121.6956 |  | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0014824 | OH | Sus | 0 | yes | 2014 | MAR | Yes | None | 99237113 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 815 | 20140301 | 1212 | 976415 | 419 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 419 | 37.0476 | -122.1564 | 4664 BONNY DOON RD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0014811 | OH | Sus | 0 | yes | 2014 | MAR | Yes | Line to Line | 99237227 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | SWITCH | 12103 | 20140301 | 1355 | 976484 | 515 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1179 | 37.0035 | -121.8296 | 2000 PLEASANT VALLEY | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0014807 | OH | Sus | 0 | yes | 2014 | MAR | Yes |  | 99237232 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | BIG BASIN-1102 | 82841102 | FUSE | 8505 | 20140303 | 848 | 977683 | 412 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1648 | 37.1753 | -122.2213 | 10 SPANS LOAD SIDE OF 8505 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0015110 | OH | Sus | 42085439 | No | 2014 | MAR | Yes | Line to Line | 99236924 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | SECTIONALIZER | 11029 | 20140305 | 127 | 978675 | 749 | Distribution Circuit | Vegetation | Tree - fell into line | 591 | 156483 | 37.193 | -122.1458 | 1 spans SS 2285 but on the Main line | Overcast-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0015503 | OH | Sus | 31060751 | yes | 2014 | MAR | Yes | Three Phase Fault | 99236692 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | RECLOSER | 5096 | 20140305 | 507 | 978693 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 526 | 151014 | 37.0509 | -122.0369 | MTR# 1007587232 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0015508 | OH | Sus | 42086770 | yes | 2014 | MAR | Yes | Multi-Fault | 99236688 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 12155 | 20140306 | 1640 | 980125 | 149 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 447 | 37.0043 | -121.7043 | Moyano/4819: 3 poles e/o lco 12155 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0016290 | OH | Sus | 31061447 | yes | 2014 | MAR | Yes | Line to Ground | 99236144 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN BENITO-2102 | 182742102 | FUSE | 4351 | 20140309 | 703 | 981093 | 467 | Distribution Circuit | Equipment Failure/Involved | Other | 59 | 14133 | 36.87 | -121.591 | MTR 1007987713 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0016740 | OH | Sus | 42088889 | No | 2014 | MAR | Yes | Line to Ground | 99235851 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 8353 | 20140311 | 542 | 981999 | 445 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4005 | 37.058 | -121.9417 | 15 SP LOAD SIDE 8353 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0017110 | OH | Sus | 42090675 | yes | 2014 | MAR | Yes | Line to Ground | 99235599 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | FUSE | 7343 | 20140312 | 2151 | 983828 | 2665 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 9987 | 36.1231 | -121.6345 | FUSES 6133 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0017723 | OH | Sus | 0 | yes | 2014 | MAR | Yes |  | 99234941 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9699 | 20140318 | 1943 | 986567 | 962 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1924 | 37.0969 | -122.1242 | at FU-9699- | Clear-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0019006 | OH | Sus | 31063949 | No | 2014 | MAR | Yes | Line to Ground | 99234249 | CAW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 12613 | 20140320 | 233 | 987108 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2328 | 37.097 | -121.992 | 3333 GLENNWOOD DR.- at FU-12613- SCOTTS VALLEY | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0019271 | OH | Sus | 42095801 | No | 2014 | MAR | Yes | Line to Ground | 99234087 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | FUSE | 2181 | 20140324 | 2318 | 989078 | 1022 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 47845 | 36.4893 | -121.9362 | METER 1009551936 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0020192 | OH | Sus | 31065056 | No | 2014 | MAR | Yes | Three Phase Fault | 99233396 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 9309 | 20140325 | 2316 | 989752 | 390 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 21029 | 37.1186 | -122.1154 | 1121 HIGHLAND DR CGC# 315301123110 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0020488 | OH | Sus | 42098068 | No | 2014 | MAR | Yes |  | 99233207 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 169 | 20140326 | 936 | 989916 | 575 | Distribution Circuit | 3rd Party | Vehicle | 5 | 1523 | 37.0539 | -122.042 | 1600 MOUNT HERMON RD | Rain-32 - 90 F | Pole-Wood | Broken, wire on object | 14-0020602 | OH | Sus | 31065450 | yes | 2014 | MAR | Yes | Line to Ground | 99233149 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 9949 | 20140326 | 1018 | 989933 | 372 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 14522 | 37.0159 | -121.8209 | SAME | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0020646 | OH | Sus | 42098392 | yes | 2014 | MAR | Yes | Line to Ground | 99233133 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER |  | 20140329 | 1520 | 991442 | 678 | Distribution Circuit | Vegetation | Tree - fell into line | 295 | 36577 | 37.1498 | -122.1674 | STORMENT- 4178 / 831-278-0287: 16587 Jamison Creek Rd.- B.C. | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0021416 | OH | Sus | 31066085 | yes | 2014 | MAR | Yes | Line to Line | 99232561 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 8929 | 20140330 | 1223 | 991971 | 262 | Distribution Circuit | Equipment Failure/Involved | Other | 57 | 14934 | 37.0661 | -122.0844 | ON MAIN LINE LS OF TAP FUSE 11405 | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0021561 | OH | Sus | 42099726 | yes | 2014 | MAR | Yes | None | 99232479 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 8353 | 20140331 | 1438 | 992569 | 725 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 6525 | 37.058 | -121.9417 | OLD SAN JOSE RD PAST HOOVER | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0021880 | OH | Sus | 42100383 | yes | 2014 | MAR | Yes | Line to Ground | 99232279 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER |  | 20140401 | 929 | 993211 | 474 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 47325 | 37.1732 | -122.1758 | 19100 BIG BASIN WAY | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0022071 | OH | Sus | 42100678 | yes | 2014 | APR | Yes |  | 99232097 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8365 | 20140401 | 2101 | 993797 | 548 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 15892 | 37.1667 | -122.2006 | FLUITT- 3755 / 831-682-1793: 8 spans load side of 8365 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0022314 | OH | Sus | 42100865 | yes | 2014 | APR | Yes | Three Phase Fault | 99231946 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER |  | 20140402 | 750 | 994210 | 510 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1020 | 37.2143 | -122.1475 | MTR#1007347607 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0022464 | OH | Sus | 0 | yes | 2014 | APR | Yes | Open Circuit | 99231835 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 6673 | 20140402 | 134 | 993924 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 57846 | 36.9913 | -121.8281 | 3 SPANS LOAD SIDE OF C/O 6673 | Fog-32 - 90 F | Conductor, Overhead | On Ground | 14-0022336 | OH | Sus | 42100971 | yes | 2014 | APR | Yes |  | 99231938 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5263 | 20140406 | 1818 | 995862 | 1122 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1122 | 37.117 | -121.9682 | 16750 Laurel | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0023294 | OH | Sus | 31067696 | No | 2014 | APR | Yes | Line to Ground | 99231299 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | SWITCH | 5607 | 20140408 | 1657 | 996929 | 831 | Distribution Circuit | 3rd Party | Vehicle | 191 | 79433 | 37.0926 | -122.0429 | CAPWELL - 3915 / 831-206-1280: 10333 ZAYANTE RD | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0023836 | OH | Sus | 31068258 | No | 2014 | APR | Yes | None | 99230955 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | OTHER |  | 20140410 | 1631 | 997989 | 834 | Distribution Circuit | Equipment Failure/Involved | Other | 787 | 91979 | 37.0295 | -122.0192 | MAIN LINE AT FUSE TAP 5035 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0024377 | OH | Sus | 31068743 | No | 2014 | APR | Yes | None | 99230619 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | OTHER |  | 20140411 | 1735 | 998471 | 388 | Distribution Circuit | Equipment Failure/Involved | Other | 91 | 30444 | 37.0375 | -121.8186 | MTR 1008452543 | Partly cloudy-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0024639 | OH | Sus | 42106867 | No | 2014 | APR | Yes | Open Circuit | 99230501 | CSO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6851 | 20140411 | 1735 | 998514 | 670 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 11390 | 37.042 | -121.8167 | MTR 1008452543 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0024639 | OH | Sus | 42106867 | No | 2014 | APR | Yes | Line to Ground | 99230024 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5477 | 20140413 | 1937 | 999052 | 379 | Distribution Circuit | Equipment Failure/Involved | Other | 53 | 20087 | 37.1291 | -122.1143 | 1 SPAN LOAD SIDE OF 5477 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on object | 14-0024803 | OH | Sus | 42107046 | No | 2014 | APR | Yes | Line to Ground | 99230332 | CSO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6577 | 20140414 | 2247 | 999560 | 989 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 46483 | 37.0487 | -121.8084 | 2044 HIGHLAND | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0025062 | OH | Sus | 42107625 | No | 2014 | APR | Yes | Line to Line | 99230174 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 6091 | 20140418 | 2126 | 1001451 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 236 | 152572 | 36.3916 | -121.6192 | FUCO 6625 | Partly cloudy-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0025978 | OH | Sus | 31070370 | No | 2014 | APR | Yes | Line to Ground | 99229620 | CAW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | RECLOSER | 5096 | 20140419 | 1713 | 1001663 | 547 | Distribution Circuit | Equipment Failure/Involved | Other | 745 | 84842 | 37.0509 | -122.0369 | SOURCE SIDE OF LR 5906 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0026037 | OH | Sus | 42110940 | No | 2014 | APR | Yes | Line to Ground | 99229566 | CSO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2012 | 20140419 | 244 | 1001472 | 606 | Distribution Circuit | Equipment Failure/Involved | Other | 506 | 306636 | 36.3311 | -121.8829 | 1SP SS OF B104 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0025988 | OH | Sus | 31070285 | No | 2014 | APR | Yes | Line to Ground | 99229615 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 2949 | 20140426 | 712 | 1004990 | 538 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 33356 | 36.445 | -121.6735 | CORI- MARK: 33790 carmel valley rd | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0027527 | OH | Sus | 31071866 | yes | 2014 | APR | Yes | Line to Ground | 99228531 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 2835 | 20140506 | 1649 | 1011198 | 110 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 3630 | 36.586 | -121.875 | 1 & 2 SPAN LOAD SIDE OF 2775 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0029808 | OH | Sus | 42118080 | yes | 2014 | MAY | Yes | Line to Ground | 99226996 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 709 | 20140510 | 1619 | 1013186 | 700 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1400 | 37.0516 | -122.1606 | 2ND SP LD SIDE OF 709 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0030846 | OH | Sus | 42120991 | yes | 2014 | MAY | Yes | Line to Line | 99226359 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER |  | 20140511 | 1102 | 1013535 | 418 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2090 | 37.1017 | -121.9823 | 1 P SS/OF TRANSF MTR 1006223586 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0030952 | OH | Sus | 42121054 | No | 2014 | MAY | Yes | Open Circuit | 99226254 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER |  | 20140515 | 1310 | 1016345 | 730 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 20804 | 37.1725 | -122.202 | 9 SP LD SIDE OF FUCO 8365 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0032222 | OH | Sus | 42124811 | yes | 2014 | MAY | Yes | Open Circuit | 99225474 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 6753 | 20140515 | 856 | 1016037 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 2747 | 36.5661 | -121.8873 | 502 AUGAJITO RD. | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0032027 | OH | Sus | 42124533 | yes | 2014 | MAY | Yes | Line to Ground | 99225547 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5509 | 20140519 | 449 | 1020495 | 531 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 10089 | 37.153 | -122.1291 | 1ST POLE LD SIDE OF 5509 | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0032731 | OH | Sus | 42125945 | yes | 2014 | MAY | Yes | Open Circuit | 99225010 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2105 | 83252105 | FUSE | 10031 | 20140519 | 1314 | 1020873 | 380 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 760 | 37.006 | -121.9841 | 10031 CUT OUT SPAN | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0032953 | OH | Sus | 31077257 | yes | 2014 | MAY | Yes | Open Circuit | 99224877 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 1445 | 20140520 | 209 | 1021241 | 340 | Distribution Circuit | Equipment Failure/Involved | Other | 49 | 22774 | 36.5734 | -121.9108 | 490 AQUAJITO RD | Partly cloudy-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0033046 | OH | Sus | 0 | No | 2014 | MAY | Yes | Line to Ground | 99224779 | CSO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 8163 | 20140526 | 1715 | 1024279 | 349 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 4961 | 36.5989 | -121.9389 | ARROWHEAD RD. | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0034315 | OH | Sus | 42129842 | No | 2014 | MAY | Yes | Line to Ground | 99223918 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9597 | 20140602 | 1912 | 1027672 | 636 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3180 | 37.1441 | -122.0894 | 401 HARMON GLUCH | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0035717 | OH | Sus | 42132877 | No | 2014 | JUN | Yes | Line to Line | 99222935 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 1445 | 20140602 | 423 | 1027234 | 477 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 23373 | 36.5734 | -121.9108 | 3 SPANS LOAD SIDE OF 1445 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0035460 | OH | Sus | 31079767 | No | 2014 | JUN | Yes |  | 99223054 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 3729 | 20140604 | 1005 | 1028390 | 935 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2805 | 37.1986 | -122.1546 | MTR 1007330146 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0036109 | OH | Sus | 42133942 | No | 2014 | JUN | Yes | Line to Line | 99222660 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 7805 | 20140608 | 258 | 1030235 | 732 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1464 | 37.2145 | -122.1491 | 2 SP LS OF 7805 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0036861 | OH | Sus | 42135261 | yes | 2014 | JUN | Yes |  | 99222181 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | RECLOSER | 5404 | 20140616 | 1754 | 1035445 | 2514 | Distribution Circuit | 3rd Party | Customer Equipment | 737 | 172538 | 37.0156 | -122.0253 | STA SIDE FUSE TAP 87057 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0038731 | OH | Sus | 31082991 | No | 2014 | JUN | Yes |  | 99220599 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | SWITCH | 11009 | 20140618 | 1506 | 1036281 | 10 | Distribution Circuit | 3rd Party | Customer Equipment | 580 | 5800 | 36.9993 | -122.0207 | STA SIDE OF FUCO 87057 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0038731 | OH | Sus | 31082991 | No | 2014 | JUN | Yes | Multi-Fault | 99220501 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5503 | 20140619 | 1729 | 1036830 | 412 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 15656 | 37.1461 | -122.129 | FERN & TWO BAR RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0039466 | OH | Sus | 42142064 | No | 2014 | JUN | Yes | Three Phase Fault | 99220322 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 5143 | 20140624 | 1848 | ODB-9921 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 15002 | 37.0994 | -122.0868 | 460 ROBERTS RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0040329 | OH | Sus | 0 | No | 2014 | JUN | Yes |  | 99219640 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5995 | 20140624 | 2306 | 1039199 | 770 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5390 | 37.078 | -122.244 | 460 MILL RD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0040351 | OH | Sus | 42144626 | No | 2014 | JUN | Yes | Line to Ground | 99219604 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 8095 | 20140627 | 1750 | 1040816 | 507 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 7605 | 37.0023 | -121.9416 | FLUITT- 3755 / 831-682-1793: 4801 prescott rd. soquel | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0041134 | OH | Sus | 0 | No | 2014 | JUN | Yes | Line to Ground | 99219114 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12758 | 20140630 | 2144 | 1042381 | 846 | Distribution Circuit | Vegetation | Tree - fell into line | 295 | 57067 | 37.1485 | -122.1745 | PARK AVE at C/OUTS 5457 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0041592 | OH | Sus | 31086154 | No | 2014 | JUN | Yes | Line to Line | 99218681 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | OCB | OCB | 20140701 | 2311 | 1043176 | 1185 | Distribution Circuit | 3rd Party | Vehicle | 453 | 0 | 36.9792 | -121.867 | FREEDOM BLVD & SANTA FE RIDGE (NEAR FUCO 3529) | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0041910 | OH | Sus | 31086382 | yes | 2014 | JUL | Yes |  | 99218467 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | RESERVATION ROAD-1102 | 182731102 | OCB | OCB | 20140704 | 156 | 1044236 | 364 | Distribution Circuit | 3rd Party | Vehicle | 2106 | 205617 | 36.6245 | -121.6884 | HILLTOWN ON MAIN LINE NEAR C/OUTS 46759 | Partly cloudy-32 - 90 F | Anchor or Guy | Broken, wire on ground | 14-0042514 | OH | Sus | 31086891 | No | 2014 | JUL | Yes | None | 99218143 | ANC | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | RECLOSER | 2020 | 20140708 | 1234 | 1046367 | 308 | Distribution Circuit | Vegetation | Tree - fell into line | 846 | 119733 | 36.4634 | -121.7122 | 5 SPANS BEYOND FU-9383 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0043182 | OH | Sus | 0 | No | 2014 | JUL | Yes | Line to Line | 99217586 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER | 5206 | 20140709 | 116 | 1046645 | 724 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 56446 | 37.0956 | -122.0857 | LOVE CREEK RD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0043335 | OH | Sus | 42150539 | No | 2014 | JUL | Yes | Multi-Fault | 99217507 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | BXD7 | 20140712 | 2113 | 1048413 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1515 | 37.0265 | -121.8382 | 5 POLES LOAD SIDE OF CGC#316105219390 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0044106 | OH | Sus | 42153521 | No | 2014 | JUL | Yes | Line to Ground | 99216953 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | BXD7 | 20140720 | 1825 | 1052536 | 792 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 792 | 37.1179 | -121.9863 | 24650 GLENWOOD DR | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0045701 | OH | Sus | 31089911 | yes | 2014 | JUL | Yes | Open Circuit | 99215812 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | OTHER |  | 20140724 | 104 | 1054294 | 654 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 2868 | 37.0806 | -122.1427 | 1 SP SS OF MTR 1008516620 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0046538 | OH | Sus | 42158631 | yes | 2014 | JUL | Yes | Open Circuit | 99215290 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 4743 | 20140727 | 1631 | 1056276 | 404 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 404 | 37.093 | -122.1073 | CAPWELL - 3915 / 831-206-1280: 500 HUBBARD GULCH RD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0047312 | OH | Sus | 42159931 | No | 2014 | JUL | Yes | Line to Ground | 99214732 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | BIG BASIN-1102 | 82841102 | FUSE | 8505 | 20140801 | 1118 | 1059438 | 952 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3808 | 37.1753 | -122.2213 | 12 POLES LOAD SIDE OF 8505 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0048622 | OH | Sus | 31092588 | yes | 2014 | AUG | Yes | Line to Line | 99213842 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5569 | 20140802 | 1420 | 1060039 | 680 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 10120 | 37.0502 | -122.0672 | 500 BLOCK OF RIVER RD | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0048751 | OH | Sus | 31092612 | No | 2014 | AUG | Yes | Line to Ground | 99213728 | CSO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 9307 | 20140806 | 2132 | 1062399 | 548 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2192 | 37.1165 | -122.1142 | FLUITT- 3755 / 831-682-1793: 6 spans load side of SSD 9307 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0049585 | OH | Sus | 42165075 | No | 2014 | AUG | Yes | Line to Ground | 99213116 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 5459 | 20140816 | 834 | 1067253 | 581 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 10933 | 37.1386 | -122.1433 | 1480 HILLSIDE | Clear-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0051341 | OH | Sus | 31095257 | No | 2014 | AUG | Yes |  | 99211854 | CAW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 3147 | 20140901 | 1558 | 1075738 | 506 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4048 | 37.0584 | -122.1599 | At FUCO 2541 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0054422 | OH | Sus | 31098268 | No | 2014 | SEP | Yes | Line to Ground | 99209652 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 7613 | 20140903 | 746 | 1076510 | 349 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2552 | 37.0486 | -122.0885 | 1901 FELTON EMPIRE RD | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0054760 | OH | Sus | 31098653 | No | 2014 | SEP | Yes | Line to Ground | 99209413 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | RESERVATION ROAD-1102 | 182731102 | FUSE | 24517 | 20140910 | 842 | 1079357 | 328 | Distribution Circuit | Equipment Failure/Involved | Other | 9 | 2952 | 36.6589 | -121.7378 | 2 SPANS LOAD SIDE OF 24517 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0056080 | OH | Sus | 42188070 | No | 2014 | SEP | Yes | Line to Line | 99208543 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 3575 | 20140912 | 1800 | 1080540 | 1260 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 9727 | 37.1751 | -122.1536 | 3 SP SS OF MTR 5000074549 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0056697 | OH | Sus | 31100974 | No | 2014 | SEP | Yes | Line to Ground | 99208175 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 5405 | 20140914 | 1806 | 1081264 | 1149 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 13788 | 37.0671 | -122.141 | at MTR 1008518171 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0056888 | OH | Sus | 31101114 | No | 2014 | SEP | Yes |  | 99207980 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | RECLOSER | 5300 | 20140916 | 1334 | 1082747 | 841 | Distribution Circuit | Vegetation | Tree - fell into line | 368 | 248183 | 37.0382 | -122.0705 | 2 SPANS LS OF FUSE-5211 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0057294 | OH | Sus | 0 | No | 2014 | SEP | Yes |  | 99207746 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN BENITO-2101 | 182742101 | FUSE | 4801 | 20140917 | 836 | 1083005 | 324 | Distribution Circuit | Equipment Failure/Involved | Other | 11 | 3564 | 36.8354 | -121.5577 | MTR # 1009306141- 1980 SALINAS RD.- SAN JUAN BATISTA. | Fog-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0057442 | OH | Sus | 31101608 | No | 2014 | SEP | Yes | Line to Ground | 99207637 | CSO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 1859 | 20140919 | 723 | 1084392 | 516 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2580 | 37.0939 | -122.1443 | 2 SPANS LD SIDE FUCO 1859 | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0057967 | OH | Sus | 31102133 | No | 2014 | SEP | Yes | Line to Ground | 99207296 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 7295 | 20140924 | 1150 | 1086767 | 315 | Distribution Circuit | Vegetation | Tree - branch fell on line | 57 | 7830 | 37.0326 | -122.0879 | CORI- MARK: 1555 mclellan MTR 1006215651 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0058948 | OH | Sus | 42196412 | No | 2014 | SEP | Yes | Line to Ground | 99206583 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 3459 | 20140925 | 743 | 1087497 | 569 | Distribution Circuit | Equipment Failure/Involved | Other | 63 | 13666 | 37.0246 | -121.8835 | 4 SP SS OF 12677 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0059299 | OH | Sus | 0 | yes | 2014 | SEP | Yes | Line to Ground | 99206342 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 5146 | 20140929 | 1850 | 1090452 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 1101 | 85425 | 37.0579 | -122.0596 | STORMENT- 4178 / 831-278-0287: 8266 W. Zayante Rd.- Felton | Partly cloudy-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0060337 | OH | Sus | 31104281 | No | 2014 | SEP | Yes |  | 99199475 | CAW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5225 | 20140930 | 2008 | 1090967 | 526 | Distribution Circuit | 3rd Party | Vehicle | 10 | 5260 | 37.0495 | -122.0855 | CAPWELL - 3915 / 831-206-1280: 1ST POLE LOAD SIDE OF C/O 5225 ON FELTON EMPIRE GRADE | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0060568 | OH | Sus | 31104491 | No | 2014 | SEP | Yes | None | 99205482 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | RIO DEL MAR-0402 | 83260402 | FUSE | 6137 | 20141004 | 1805 | 1092779 | 809 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 30742 | 36.9728 | -121.9031 | 2 SP TREE WIRE ON GRD LS 6137 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0061429 | OH | Sus | 31105506 | No | 2014 | OCT | Yes | None | 99204903 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | RECLOSER | 2020 | 20141011 | 310 | 1095914 | 551 | Distribution Circuit | Vegetation | Tree - branch fell on line | 849 | 282941 | 36.4634 | -121.7122 | at MTR #1009546364 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0062933 | OH | Sus | 42205787 | No | 2014 | OCT | Yes | Line to Line | 99204018 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5511 | 20141012 | 133 | 1096206 | 569 | Distribution Circuit | 3rd Party | Vehicle | 41 | 23329 | 37.1499 | -122.1364 | at 5511 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0062998 | OH | Sus | 31106882 | No | 2014 | OCT | Yes | Line to Ground | 99203928 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12758 | 20141012 | 1254 | 1096323 | 1004 | Distribution Circuit | Vegetation | Tree - fell into line | 295 | 137138 | 37.1485 | -122.1745 | 16580 JAMISON CREEK | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0063036 | OH | Sus | 31106899 | No | 2014 | OCT | Yes | Line to Line | 99203862 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 4477 | 20141014 | 1302 | 1097042 | 903 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 27090 | 37.1336 | -122.0195 | CAPWELL - 3915 / 831-206-1280: 13485 LOWER ELLEN RD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0063575 | OH | Sus | 31107409 | No | 2014 | OCT | Yes | Line to Ground | 99203617 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 5725 | 20141014 | 1718 | 1097295 | 644 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 9016 | 36.99 | -121.7367 | BRANDT- 4179 / 831-212-2088: 97 Gaffey Rd tree broke a xarm and brought two spans down | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0063654 | OH | Sus | 0 | No | 2014 | OCT | Yes | Line to Ground | 99203565 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | GABILAN-1101 | 182331101 | FUSE | 25027 | 20141024 | 815 | 1101572 | 152 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 152 | 36.7982 | -121.5697 | 1ST SP LS OF 25027 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0065648 | OH | Sus | 0 | No | 2014 | OCT | Yes | Line to Ground | 99202326 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 6151 | 20141025 | 2003 | 1102937 | 612 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4284 | 36.9653 | -121.8293 | FLUITT- 3755 / 831-682-1793: 420 ranco laguna x st calabasas | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0066137 | OH | Sus | 42215941 | yes | 2014 | OCT | Yes | Line to Ground | 99201944 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 11865 | 20141026 | 1209 | 1103161 | 866 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 19993 | 37.001 | -121.7393 | (MTR1009698835) 662 & 668 HAZEL DELL RD MTR5000038089 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0066203 | OH | Sus | 0 | No | 2014 | OCT | Yes | Line to Line | 99201829 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 5151 | 20141101 | 842 | 1107591 | 778 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 4668 | 37.1106 | -122.0897 | 5 SP LS 5151- WIRE DOWN | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0067719 | OH | Sus | 0 | yes | 2014 | NOV | Yes | Line to Ground | 99200866 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 12455 | 20141106 | 1159 | 1109917 | 403 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 4600 | 37.0964 | -121.9923 | 365 NORTHRIDGE- SANTA CRUZ | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0068762 | OH | Sus | 42224733 | No | 2014 | NOV | Yes | Line to Line | 99200137 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 5219 | 20141107 | 1613 | 1110451 | 708 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 14868 | 37.037 | -122.0657 | 101 N BIG TREES PARK RD- FELTON | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0069058 | OH | Sus | 42243797 | No | 2014 | NOV | Yes | None | 99199965 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20141109 | 403 | 1110776 | 1317 | Distribution Circuit | 3rd Party | Vehicle | 390 | 90649 | 36.9803 | -121.8921 | 1 SP N/O FUCO 9629 ON MAIN LINE | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0069144 | OH | Sus | 31114010 | No | 2014 | NOV | Yes | Line to Line | 99199866 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 10705 | 20141115 | 2100 | 1113390 | 420 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1740 | 36.3915 | -121.6294 | 2 SP FROM EOL TRANSF TWD THE WEST | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0070261 | OH | Sus | 0 | No | 2014 | NOV | Yes | Line to Line | 99199116 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | CAMP EVERS-2106 | 83622106 | RECLOSER | 5302 | 20141118 | 1416 | 1114684 | 912 | Distribution Circuit | Vegetation | Tree - fell into line | 578 | 42048 | 37.0438 | -122.0755 | LOAD SIDE OF 9285 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0070715 | OH | Sus | 31116022 | No | 2014 | NOV | Yes |  | 99198771 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2166 | 20141120 | 1909 | 1115897 | 461 | Distribution Circuit | Vegetation | Tree - branch fell on line | 480 | 221280 | 36.2768 | -121.8263 | 15 SPANS LOAD SIDE OF 2166 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0071275 | OH | Sus | 0 | No | 2014 | NOV | Yes | Line to Ground | 99198502 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 7219 | 20141121 | 907 | 1116146 | 1048 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 8062 | 37.1413 | -122.091 | 708 RALSTON RIDGE | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0071388 | OH | Sus | 31117106 | No | 2014 | NOV | Yes |  | 99198362 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 3233 | 20141121 | 1128 | 1116148 | 298 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 11026 | 37.0325 | -122.0627 | 220 TOLLHOUSE GULCH RD | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0071407 | OH | Sus | 42279951 | No | 2014 | NOV | Yes | Line to Ground | 99198357 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | OCB | OCB | 20141124 | 1137 | 1117555 | 1031 | Distribution Circuit | Equipment Failure/Involved | Other | 2395 | 529706 | 37.1308 | -122.1723 | 3 SPAN S/OF SW-8831 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0071823 | OH | Sus | 31117524 | No | 2014 | NOV | Yes | Line to Ground | 99197934 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 12019 | 20141129 | 1230 | 1119326 | 145 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 725 | 37.0104 | -121.9345 | 1 SP LS OF 12019 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0072424 | OH | Sus | 42282010 | No | 2014 | NOV | Yes | Line to Ground | 99197561 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | LOMPICO-0401 | 88880401 | RECLOSER | 10294 | 20141130 | 1623 | 1119743 | 647 | Distribution Circuit | Vegetation | Tree - branch fell on line | 429 | 84437 | 37.0991 | -122.053 | 12639 LOMPICO RD | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0072526 | OH | Sus | 0 | No | 2014 | NOV | Yes |  | 99197452 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 5217 | 20141202 | 1247 | 1121001 | 713 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 10695 | 37.0371 | -122.0662 | 3 SPANS LD SIDE OF 5217 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0072968 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99197149 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 11943 | 20141202 | 511 | 1120455 | 469 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 37051 | 37.0112 | -122.0442 | at MTR #1009748597 448 YORK | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0072773 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99197254 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | RECLOSER | 2010 | 20141202 | 1312 | 1121064 | 786 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 16712 | 36.5059 | -121.9358 | 78 FERN CYN RD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0072950 | OH | Sus | 31117940 | yes | 2014 | DEC | Yes |  | 99197158 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2012 | 20141202 | 1130 | 1121020 | 414 | Distribution Circuit | Equipment Failure/Involved | Other | 506 | 209484 | 36.3311 | -121.8829 | 2 SPANS SS/OF 40555 MTR 1009655779 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0072955 | OH | Sus | 31117940 | yes | 2014 | DEC | Yes |  | 99197155 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | FUSE | 1295 | 20141205 | 1812 | 1125499 | 1108 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 13296 | 36.3795 | -121.861 | CORI- MARK: rocky creek rd palo colorado | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074099 | OH | Sus | 31119751 | No | 2014 | DEC | Yes | Line to Ground | 99196148 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | OTHER |  | 20141206 | 1709 | 1126158 | 501 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1503 | 37.1181 | -122.086 | CRIVELLO- 4176 / 831-682-1912: 2101 LOVE CREEK | Fog-32 - 90 F | Conductor, Overhead | On Ground | 14-0074194 | OH | Sus | 0 | No | 2014 | DEC | Yes | Line to Ground | 99196037 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER |  | 20141206 | 726 | 1125793 | 816 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 12748 | 37.1352 | -122.0167 | 14040 MIDDLE ELLEN RD | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074152 | OH | Sus | 0 | No | 2014 | DEC | Yes | Line to Ground | 99196085 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8985 | 20141206 | 906 | 1125894 | 434 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 8246 | 37.0236 | -122.1323 | BOYNTON- 3459 / 831-331-6620: 2801 smith grade | Overcast-32 - 90 F | Conductor, Overhead | On Ground | 14-0074163 | OH | Sus | 0 | No | 2014 | DEC | Yes |  | 99196071 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5617 | 20141207 | 237 | 1126242 | 718 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 6462 | 37.0985 | -122.0531 | 10274 LOMITA- FELTON. | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074208 | OH | Sus | 31119880 | No | 2014 | DEC | Yes | Line to Ground | 99196006 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER |  | 20141210 | 2305 | 1128701 | 1078 | Distribution Circuit | Vegetation | Tree - branch fell on line | 769 | 425878 | 37.1517 | -122.1359 | 1 POLE NE/OF 5519- GOING TWD 5513. | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074774 | OH | Sus | 0 | yes | 2014 | DEC | Yes | None | 99194420 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | OTHER |  | 20141213 | 1554 | 1140025 | 126 | Distribution Circuit | Equipment Failure/Involved | Other | 3 | 378 | 37.0406 | -122.0657 | 1 SP SS OF MTR 5000122580 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076789 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Open Circuit | 99193308 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 12155 | 20141213 | 720 | 1139474 | 310 | Distribution Circuit | Equipment Failure/Involved | Other | 3 | 930 | 37.0043 | -121.7043 | 4 SP LD SIDE OF 12155 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076675 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193406 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HOLLISTER-2105 | 182492105 | FUSE | 4257 | 20141213 | 1045 | 1139719 | 218 | Distribution Circuit | Equipment Failure/Involved | Other | 42 | 9156 | 36.5174 | -121.1341 | PATTERSON- MICHAEL: Airline Hwy at 4257 | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0076722 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99193366 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | FUSE | 2867 | 20141213 | 950 | 1139646 | 276 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 828 | 36.2678 | -121.8048 | 6 SP LD SIDE OF FUCO | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076710 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99193378 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | OTHER |  | 20141213 | 819 | 1139636 | 571 | Distribution Circuit | Equipment Failure/Involved | Other | 59 | 32471 | 36.1805 | -121.6963 | 51400 PARTINGTON RIDGE at MTR 1008505164 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076731 | OH | Sus | 0 | yes | 2014 | DEC | Yes | None | 99193357 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5617 | 20141215 | 827 | 1140964 | 518 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4662 | 37.0985 | -122.0531 | MTR 1008736264 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076991 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Open Circuit | 99193008 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 9167 | 20141215 | 811 | 1140946 | 289 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 289 | 36.5722 | -121.8852 | 2 SPANS LD SIDE OF FUSES | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076970 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Open Circuit | 99193020 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | OCB | OCB | 20141215 | 1421 | 1141410 | 943 | Distribution Circuit | Vegetation | Tree - fell into line | 1676 | 245653 | 36.5782 | -121.9083 | FONDA RD BET SW 40017- 9114 & 9893 | Rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0077061 | OH | Sus | 31120494 | yes | 2014 | DEC | Yes | Multi-Fault | 99192860 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5157 | 20141216 | 1845 | 1142491 | 610 | Distribution Circuit | Vegetation | Tree - fell into line | 171 | 104310 | 37.0841 | -122.0885 | CRIVELLO- 4176 / 831-682-1912: past 260 SCENIC WAY | Rain-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0077326 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99192643 | CAW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 6737 | 20141217 | 713 | 1142708 | 1002 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 15994 | 36.5711 | -121.8864 | 2 SP LD SIDE OF 6737 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077373 | OH | Sus | 31121625 | No | 2014 | DEC | Yes | Three Phase Fault | 99192460 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | RECLOSER | 2762 | 20141217 | 1549 | 1143151 | 694 | Distribution Circuit | Vegetation | Tree - fell into line | 1187 | 41138 | 36.558 | -121.7505 | MTR 1008264051 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077473 | OH | Sus | 31121831 | No | 2014 | DEC | Yes | Line to Ground | 99192456 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 1421 | 20141217 | 2323 | 1143357 | 1212 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 24240 | 36.5742 | -121.9483 | 2 SPANS LOAD SIDE OF 1421 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077505 | OH | Sus | 31121904 | No | 2014 | DEC | Yes | Line to Line | 99192453 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | OTHER |  | 20141217 | 1237 | 1143016 | 166 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 544 | 36.5712 | -121.9027 | 1ST SP LD SIDE OF FUSES 7537 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077430 | OH | Sus | 42299668 | No | 2014 | DEC | Yes | None | 99192553 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 2615 | 20141219 | 1821 | 1144737 | 1339 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4017 | 37.0346 | -121.9967 | 200 BACHELDER | Overcast-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0077767 | OH | Sus | 31122388 | No | 2014 | DEC | Yes | Line to Ground | 99192136 | CAW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 6605 | 20141219 | 2034 | 1144792 | 1136 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 7966 | 37.0131 | -121.7518 | 1 SPAN LOAD SIDE OF 6605 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077773 | OH | Sus | 42301460 | No | 2014 | DEC | Yes | Line to Ground | 99192134 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 7159 | 20141219 | 1350 | 1144508 | 656 | Distribution Circuit | 3rd Party | Vehicle | 23 | 15088 | 36.578 | -121.9067 | at FUSES 7567 | Drizzle-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0077734 | OH | Sus | 31122318 | No | 2014 | DEC | Yes | Line to Ground | 99192187 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 7309 | 20141220 | 815 | 1144905 | 665 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 11305 | 37.0328 | -122.0755 | 2 SPANS LOAD SIDE | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077800 | OH | Sus | 31122400 | No | 2014 | DEC | Yes | Line to Ground | 99192098 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER | 92792 | 20141220 | 544 | 1144864 | 399 | Distribution Circuit | Vegetation | Tree - branch fell on line | 141 | 30799 | 36.5898 | -121.9457 | at MTR#1008350801 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077781 | OH | Sus | 42301472 | No | 2014 | DEC | Yes | Line to Ground | 99192128 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 9307 | 20141222 | 307 | 1145785 | 578 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2312 | 37.1165 | -122.1142 | NEAR 12470 IRWIN WAY- 3 POLES LS OF 9307 | Overcast-32 - 90 F | Conductor, Overhead | On Ground | 14-0077935 | OH | Sus | 31122501 | No | 2014 | DEC | Yes | Line to Ground | 99191931 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 1117 | 20141224 | 2047 | 1147997 | 1799 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 35980 | 37.1155 | -121.9709 | BET 1117 & 8161 TREE WENT THRU LINE | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078384 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99191263 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 8405 | 20141224 | 1609 | 1147748 | 1216 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 22004 | 36.579 | -121.8688 | MTER 1009295156 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078343 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99191388 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 6713 | 20141224 | 1954 | 1147974 | 356 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 22903 | 36.4701 | -121.7241 | METER 1008373463 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078374 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99191447 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 7257 | 20141224 | 2102 | 1148008 | 1578 | Distribution Circuit | Vegetation | Tree - branch fell on line | 83 | 42389 | 36.5768 | -121.9392 | RHONDA & VISCAINO- PEBBLE BEACH | Overcast-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0078395 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99191378 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 4355 | 20141225 | 1214 | 1148264 | 1542 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 33924 | 37.0602 | -122.0641 | FLUITT- 3755 / 831-682-1793: 7125 mcadams ln. | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078482 | OH | Sus | 0 | No | 2014 | DEC | Yes | Line to Ground | 99191259 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8497 | 20141225 | 1345 | 1148373 | 828 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 2321 | 37.0581 | -122.1235 | LS METER 50000510192 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078481 | OH | Sus | 0 | No | 2014 | DEC | Yes | Line to Ground | 99191326 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | FUSE | 7079 | 20141225 | 306 | 1148120 | 879 | Distribution Circuit | Equipment Failure/Involved | Other | 4 | 3516 | 36.3994 | -121.8771 | LS OF 7079 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078421 | OH | Sus | 0 | No | 2014 | DEC | Yes | Line to Ground | 99191372 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | RECLOSER | 2052 | 20141225 | 1050 | 1148236 | 275 | Distribution Circuit | Vegetation | Tree - branch fell on line | 137 | 35931 | 36.3999 | -121.9019 | Washington/1811/ 206-8370: approx 40 poles load side lr | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078453 | OH | Sus | 0 | No | 2014 | DEC | Yes | None | 99191353 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8525 | 20141225 | 1022 | 1148268 | 1477 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 18250 | 37.0585 | -122.1474 | 1 SP LS OF 1575 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078459 | OH | Sus | 0 | No | 2014 | DEC | Yes | Line to Line | 99191260 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HOLLISTER-2105 | 182492105 | OTHER |  | 20141227 | 1137 | 1149165 | 271 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 813 | 36.4976 | -121.1282 | OJ TO TAP WITH CGC 413749343062 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078646 | OH | Sus | 0 | No | 2014 | DEC | Yes | Line to Ground | 99191104 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2105 | 83252105 | FUSE | 2455 | 20141229 | 1159 | 1149967 | 646 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 15504 | 37.011 | -121.9874 | 1 SP SS OF MTR#1006265017 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078838 | OH | Sus | 31123891 | No | 2014 | DEC | Yes | None | 99190846 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 1071 | 20141231 | 1926 | 1157559 | 675 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 3096 | 37.1667 | -122.1353 | MTR 1009701915 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079786 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99189692 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | SWITCH | 9285 | 20141231 | 113 | 1155996 | 1677 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 10062 | 37.0353 | -122.0866 | 3 SPANS LD SIDE OF 9285 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0079568 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190103 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 2311 | 20141231 | 1214 | 1157015 | 1366 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5464 | 36.9496 | -121.8279 | MTR#1009922973 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079742 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99189701 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 11297 | 20141231 | 134 | 1156007 | 1980 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 21780 | 37.0137 | -121.7907 | 2 SPANS LOAD SIDE OF MTR 1009716705 & 3 SPANS LD SIDE OF 11297 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079778 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99189695 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 4427 | 20141231 | 623 | 1156605 | 1728 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6912 | 36.9667 | -121.8472 | white rd. and halten ln. | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079809 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99189686 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 8643 | 20141231 | 608 | 1156173 | 1387 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 38142 | 37.0099 | -121.8858 | 2 SP SS OF MTR#1009804772 ON MAIN LINE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079643 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99189709 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 1847 | 20150102 | 1021 | 1158298 | 294 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 294 | 37.0634 | -122.0697 | 2 SP LD SIDE OF FUCO 1847 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0002187 | OH | Sus | 0 | No | 2015 | JAN | Yes | Line to Ground | 99189508 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2105 | 83692105 | OTHER |  | 20150107 | 1652 | 1160773 | 698 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5584 | 36.9701 | -121.8785 | 625 ENCINO DR | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0003183 | OH | Sus | 31126260 | No | 2015 | JAN | Yes | None | 99188865 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | RECLOSER | 9114 | 20150108 | 1728 | 1161291 | 270 | Distribution Circuit | Equipment Failure/Involved | Other | 5671 | 215143 | 36.5784 | -121.9279 | 4 SPANS LOAD SIDE OF 9114 AT SW 2127 | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 15-0003442 | OH | Sus | 42310913 | No | 2015 | JAN | Yes | Line to Ground | 99188733 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 5217 | 20150109 | 1644 | 1161758 | 1119 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 16785 | 37.0371 | -122.0662 | 300 ANDREA | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0003680 | OH | Sus | 42312146 | No | 2015 | JAN | Yes | Line to Ground | 99188583 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 10641 | 20150113 | 37 | 1163005 | 673 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 673 | 37.1766 | -122.1192 | 2 SPANS LD SIDE OF 10641 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0004118 | OH | Sus | 42314069 | No | 2015 | JAN | Yes | Line to Ground | 99188305 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8985 | 20150113 | 901 | 1163147 | 1017 | Distribution Circuit | Equipment Failure/Involved | Other | 19 | 10647 | 37.0236 | -122.1323 | MTR 1008449108- 2801 SMITH GRADE RD | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0004201 | OH | Sus | 31127935 | No | 2015 | JAN | Yes | Line to Ground | 99188258 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | SWITCH | 12675 | 20150113 | 943 | 1163137 | 402 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4020 | 37.0377 | -121.8596 | 13 SP LS OF 12673 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0004286 | OH | Sus | 42314507 | No | 2015 | JAN | Yes | Line to Ground | 99188226 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 81217 | 20150121 | 1557 | 1166954 | 403 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3224 | 37.0572 | -122.0588 | JUST LOAD SIDE 81217 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0006136 | OH | Sus | 42319500 | No | 2015 | JAN | Yes | Line to Ground | 99187270 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 8929 | 20150122 | 1612 | 1167407 | 418 | Distribution Circuit | Equipment Failure/Involved | Other | 57 | 23826 | 37.0661 | -122.0844 | 550 EL SOYO HEIGHTS DR- FELTON | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0006444 | OH | Sus | 42320169 | No | 2015 | JAN | Yes | Line to Ground | 99187139 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 711 | 20150126 | 351 | 1168347 | 362 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 7602 | 37.0528 | -122.1603 | CRIVELLO- 4176 / 831-682-1912: COUNTRY ESTATES DR and carter | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0007000 | OH | Sus | 31130629 | No | 2015 | JAN | Yes | Line to Ground | 99186870 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | JOLON-1102 | 182981102 | RECLOSER | 7040 | 20150129 | 944 | 1169781 | 77 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 116 | 6644 | 36.0451 | -121.1754 | LOAD SIDE OF C50 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0007955 | OH | Sus | 42324210 | No | 2015 | JAN | Yes | Line to Ground | 99186368 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 9181 | 20150209 | 404 | 1185595 | 1466 | Distribution Circuit | Environmental/External | Flood/Erosion | 15 | 8295 | 37.2286 | -122.1483 | 6 SPANS PAST C/OUTS 3483 ON MAIN LINE | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011995 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183239 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 6597 | 20150209 | 1450 | 1186789 | 1490 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8940 | 36.9969 | -121.7163 | MTR 1008724132 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012255 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182763 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER |  | 20150210 | 838 | 1187602 | 1112 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2224 | 37.0688 | -122.0938 | 1245 EL SOLYO HEIGHTS | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012489 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182645 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | LOMPICO-0401 | 88880401 | FUSE | 5621 | 20150213 | 1143 | 1189735 | 757 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 10106 | 37.1014 | -122.0525 | 10366 REDWOOD DR- FELTON | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0013200 | OH | Sus | 31134578 | No | 2015 | FEB | Yes | Line to Ground | 99182107 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10912 | 20150214 | 421 | 1189990 | 511 | Distribution Circuit | Equipment Failure/Involved | Other | 66 | 8546 | 37.0911 | -122.0961 | at FUCO 4749 | Overcast-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0013313 | OH | Sus | 42333850 | No | 2015 | FEB | Yes | Line to Ground | 99182044 | CSO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9775 | 20150215 | 1640 | 1190566 | 1569 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 36881 | 37.1408 | -122.0899 | 15530 FOREST HILL- BOULDER CREEK- MTR 1007590749 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0013473 | OH | Sus | 31134924 | No | 2015 | FEB | Yes | Line to Line | 99181886 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | SECTIONALIZER | 11029 | 20150215 | 1943 | 1190718 | 1026 | Distribution Circuit | Equipment Failure/Involved | Other | 594 | 218850 | 37.193 | -122.1458 | at FUCO 9579 | Overcast-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0013478 | OH | Sus | 31134928 | No | 2015 | FEB | Yes | Line to Ground | 99181884 | CSO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 9309 | 20150221 | 604 | 1193386 | 556 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 22891 | 37.1186 | -122.1154 | 10 SP LD SIDE OF DISCS 991341 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0014729 | OH | Sus | 42337030 | No | 2015 | FEB | Yes | Line to Ground | 99181102 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 6093 | 20150225 | 1345 | 1195846 | 670 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 5844 | 37.0267 | -122.0253 | 3556 LA MADRONA RD | Rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0015729 | OH | Sus | 31137008 | No | 2015 | FEB | Yes | Line to Ground | 99180449 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1102 | 182941102 | OCB | OCB | 20150227 | 1311 | 1196550 | 371 | Distribution Circuit | Equipment Failure/Involved | Other | 533 | 190356 | 36.3799 | -121.8987 | 10 SPANS LOAD SIDE OF LR 2012 | Clear-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 15-0016215 | OH | Sus | 31137638 | No | 2015 | FEB | Yes | Line to Ground | 99180137 | CAW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER |  | 20150308 | 1511 | 1200773 | 634 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 3 | 1902 | 37.1233 | -122.1197 | 13110 IRWIN WAY- BOULDER CREEK | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0018087 | OH | Sus | 31139412 | No | 2015 | MAR | Yes | Line to Ground | 99178957 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 6091 | 20150309 | 1550 | 1201238 | 640 | Distribution Circuit | Vegetation | Tree - fell into line | 238 | 56194 | 36.3916 | -121.6192 | 1 SPAN SS METER 96R847 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0018394 | OH | Sus | 31139832 | No | 2015 | MAR | Yes | Line to Ground | 99178814 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER |  | 20150320 | 831 | 1205871 | 654 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1962 | 37.194 | -122.1574 | 1 SPAN SS 805 VIA RATON | Clear-32 - 90 F | Other | Broken, wire on ground | 15-0020978 | OH | Sus | 31142560 | No | 2015 | MAR | Yes | Line to Ground | 99177376 | NON | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | RECLOSER | 2020 | 20150320 | 1029 | 1205968 | 321 | Distribution Circuit | Vegetation | Tree - branch fell on line | 851 | 232425 | 36.4634 | -121.7122 | WIRE DOWN 1 SPAN LOAD SIDE OF C-400 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0020949 | OH | Sus | 42354215 | No | 2015 | MAR | Yes | Line to Line | 99177387 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5443 | 20150323 | 507 | 1206749 | 339 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 2034 | 37.1106 | -122.1144 | MTR 1008858468 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0021284 | OH | Sus | 42355483 | No | 2015 | MAR | Yes | Line to Line | 99177181 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 2913 | 20150323 | 1345 | 1207027 | 774 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3608 | 37.1752 | -122.1447 | 720 DRY WELL | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0021525 | OH | Sus | 31143055 | No | 2015 | MAR | Yes | Line to Line | 99177094 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | RECLOSER | 2052 | 20150324 | 1431 | 1207529 | 854 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 111586 | 36.3999 | -121.9019 | 19 SPANS LOAD SIDE OF LR 2052 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0021836 | OH | Sus | 31143237 | No | 2015 | MAR | Yes | Multi-Fault | 99176941 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | SWITCH | 8759 | 20150326 | 2142 | 1208588 | 471 | Distribution Circuit | 3rd Party | Vehicle | 294 | 18246 | 37.0474 | -122.1606 | BROKEN POLE 2 SP N/OF FUCO 8577 | Clear-32 - 90 F | Pole-Wood | Broken, wire on object | 15-0022418 | OH | Sus | 31143989 | No | 2015 | MAR | Yes | None | 99176616 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 6029 | 20150331 | 1753 | 1210873 | 578 | Distribution Circuit | Vegetation | Tree - branch fell on line | 132 | 16167 | 36.6088 | -121.9305 | 1 SP LD SIDE OF FUCO 6029 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0023388 | OH | Sus | 42360422 | No | 2015 | MAR | Yes | Line to Ground | 99176016 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | FUSE | 1291 | 20150401 | 714 | 1211202 | 461 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1383 | 36.4002 | -121.8693 | END OF LINE ON GARAPATA CYN RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0023498 | OH | Sus | 0 | No | 2015 | APR | Yes | Line to Ground | 99175849 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5617 | 20150407 | 1046 | 1214818 | 383 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3447 | 37.0985 | -122.0531 | 10274 LOMITA AVE | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0024864 | OH | Sus | 0 | yes | 2015 | APR | Yes | Line to Ground | 99174984 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9071 | 20150414 | 2234 | 1219606 | 985 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 41954 | 37.0596 | -122.0589 | at MTR# 1009694319 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0026736 | OH | Sus | 31148340 | No | 2015 | APR | Yes | Line to Line | 99173542 | PW | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | FUSE | 6087 | 20150414 | 1906 | 1219550 | 1209 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 3627 | 36.248 | -121.7819 | Rodriguez- Lou 5809/ 233-0361: end of line of 6087 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0026719 | OH | Sus | 31148336 | No | 2015 | APR | Yes | Line to Line | 99173581 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6651 | 20150414 | 1059 | 1219263 | 526 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2630 | 37.0218 | -121.7847 | KELLY- 4017 / 831-682-1802: Half mile in form C/O 6651 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0026627 | OH | Sus | 42368636 | No | 2015 | APR | Yes | Line to Ground | 99173621 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 12155 | 20150501 | 1915 | 1228164 | 108 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 375 | 37.0043 | -121.7043 | 9 SPANS LS OF 12155 at COUNTY CAMPGROUND. | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0031196 | OH | Sus | 42380398 | No | 2015 | MAY | Yes | None | 99170775 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER |  | 20150509 | 433 | 1231893 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3616 | 37.0679 | -121.9803 | 1 SPAN LOAD SIDE OF MTR 1007586799 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0033046 | OH | Sus | 31153863 | No | 2015 | MAY | Yes | Open Circuit | 99169478 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 7219 | 20150519 | 1026 | 1236892 | 944 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 19 | 11708 | 37.1413 | -122.091 | 498 RALSTON RIDGE (MTR#1007590881) | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0035205 | OH | Sus | 42391692 | No | 2015 | MAY | Yes | Line to Ground | 99167840 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SOLEDAD-2102 | 182052102 | OTHER |  | 20150522 | 1044 | 1238397 | 237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 118 | 7707 | 36.3884 | -121.3635 | 3 SP SS OF SBCO 8813 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0035994 | OH | Sus | 42394358 | No | 2015 | MAY | Yes | Open Circuit | 99167348 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 5335 | 20150525 | 2128 | 1239353 | 487 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 36038 | 37.0281 | -121.9871 | 701 HAPPY VALLEY RD. | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0036330 | OH | Sus | 42394753 | No | 2015 | MAY | Yes | Line to Ground | 99167087 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5163 | 20150527 | 1322 | 1240222 | 94 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 2350 | 37.0754 | -122.0802 | 1 SPAN LD SIDE OF 5163 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0036758 | OH | Sus | 31157394 | No | 2015 | MAY | Yes | Line to Ground | 99166084 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2705 | 20150601 | 42 | 1241911 | 749 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 17976 | 37.0005 | -121.74 | FUCO 3455 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0037526 | OH | Sus | 31158290 | No | 2015 | JUN | Yes | Line to Ground | 99166247 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | BIG BASIN-1102 | 82841102 | OTHER |  | 20150604 | 1624 | 1243768 | 696 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1392 | 37.249 | -122.1554 | 1SP SS OF MTR 1007591049 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0038584 | OH | Sus | 42401069 | No | 2015 | JUN | Yes | Open Circuit | 99165573 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 8351 | 20150604 | 1445 | 1243634 | 316 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 2844 | 37.0537 | -121.9393 | BRANDT- 4179 / 831-212-2088: 5452 Old San Jose Rd neutral brought down at DE pole in E. direction! | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0038511 | OH | Sus | 31159078 | No | 2015 | JUN | Yes | Force Out | 99165609 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6083 | 20150605 | 2207 | 1244604 | 1163 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 68429 | 37.0584 | -122.0333 | 365 NELSON RD- MTR#1007587441 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0038962 | OH | Sus | 31159455 | yes | 2015 | JUN | Yes | Line to Ground | 99165289 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER | 5206 | 20150610 | 708 | 1248223 | 472 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 50826 | 37.0956 | -122.0857 | 10225 LOVE CRK RD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0039927 | OH | Sus | 42404404 | yes | 2015 | JUN | Yes | Line to Ground | 99164470 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 2989 | 20150611 | 1414 | 1249354 | 811 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3244 | 37.1639 | -122.0767 | ALVAREZ- 3463 / 831-535-9251: 17729 Bear Creek Rd- Boulder Creek | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0040489 | OH | Sus | 31160805 | No | 2015 | JUN | Yes | Line to Ground | 99164098 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 9793 | 20150611 | 1952 | 1249527 | 426 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 22418 | 37.1963 | -122.1452 | 375 SYLVAN | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0040530 | OH | Sus | 31160880 | No | 2015 | JUN | Yes | Line to Ground | 99164080 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 6623 | 20150618 | 1641 | 1252943 | 574 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 35014 | 36.3781 | -121.5904 | 38590 OAK RD MTR#1006239467 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0041999 | OH | Sus | 31162160 | No | 2015 | JUN | Yes | Line to Ground | 99163000 | CO | OH | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | FUSE | 88973 | 20150630 | 1818 | 1259782 | 158 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 158 | 36.2198 | -121.7536 | Sissom/ 5808/ 206-2617: 1 span loadside of 88973 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 15-0044405 | OH | Sus | 42417942 | yes | 2015 | JUN | Yes | Line to Ground | 99161118 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | FUSE | 88973 | 20150701 | 1012 | 1260299 | 113 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 113 | 36.2198 | -121.7536 | 48603 CA-1 NEAR HENRY MILLER MEMORIAL LIBRARY | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0044541 | OH | Sus | 0 | yes | 2015 | JUL | Yes | Line to Ground | 1143206 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 5331 | 20150702 | 218 | 1261450 | 752 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 14288 | 37.0245 | -121.9877 | 333 CASTLE DR | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0044836 | OH | Sus | 31165546 | yes | 2015 | JUL | Yes | Line to Ground | 1143386 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 7989 | 20150706 | 515 | 1263422 | 667 | Distribution Circuit | Vegetation | Tree - fell into line | 261 | 41029 | 36.9817 | -121.8645 | 3 SP LS OF 12051 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0045620 | OH | Sus | 41875599 | No | 2015 | JUL | Yes | Line to Ground | 1143961 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2667 | 20150707 | 1529 | 1264463 | 956 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3136 | 37.0263 | -121.7749 | MTR#5000038076 | Clear-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0046114 | OH | Sus | 31166856 | yes | 2015 | JUL | Yes | Line to Ground | 1144238 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 12601 | 20150713 | 2040 | 1267549 | 566 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 7448 | 37.1578 | -122.1658 | 337 HILTON DR- BOULDER CREEK | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0047250 | OH | Sus | 31168429 | No | 2015 | JUL | Yes | Line to Line | 1145100 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | CAMP EVERS-2105 | 83622105 | FUSE | 2955 | 20150715 | 427 | 1268290 | 708 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 11328 | 37.0555 | -122.0771 | 6621 COOPER ST- FELTON | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0047521 | OH | Sus | 0 | No | 2015 | JUL | Yes | None | 1145295 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2161 | 20150715 | 900 | 1268417 | 950 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3800 | 36.997 | -121.7381 | Tree down- 6 spans in load side OF 2161 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0047650 | OH | Sus | 0 | No | 2015 | JUL | Yes | Line to Line | 1145401 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6083 | 20150717 | 16 | 1269374 | 667 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 52026 | 37.0584 | -122.0333 | LOAD SIDE FUSE 6083 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0048083 | OH | Sus | 42429709 | No | 2015 | JUL | Yes | Line to Ground | 1145644 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 1593 | 20150717 | 1225 | 1269601 | 314 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 668 | 37.0006 | -121.8334 | 2 SPAN LD SIDE OF 12103 | Overcast-32-90 F | Conductor, Overhead | On Ground | 15-0048222 | OH | Sus | 31169633 | No | 2015 | JUL | Yes | Line to Ground | 1145747 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 5209 | 20150723 | 44 | 1275825 | 399 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 8379 | 37.0373 | -122.0722 | 559 BROOKSIDE WAY | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0049965 | OH | Sus | 42434066 | No | 2015 | JUL | Yes | Line to Line | 1147179 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 8033 | 20150725 | 1831 | 1277261 | 1009 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 7063 | 37.1036 | -122.2768 | 1P LOAD SIDE 8033 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0050515 | OH | Sus | 42435042 | No | 2015 | JUL | Yes | Line to Line | 1147563 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5995 | 20150801 | 2216 | 1281390 | 789 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5523 | 37.0781 | -122.244 | 456 SWANTON RD.- DAVENPORT | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0052133 | OH | Sus | 42441380 | No | 2015 | AUG | Yes | Line to Line | 1148641 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER | 92792 | 20150801 | 23 | 1281099 | 770 | Distribution Circuit | Vegetation | Tree - branch fell on line | 142 | 17813 | 36.5898 | -121.9457 | 3125 MIDDLE RANCH RD.- PEBBLE BEACH | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0052036 | OH | Sus | 0 | No | 2015 | AUG | Yes | Line to Line | 1148540 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 6813 | 20150806 | 1816 | 1283761 | 687 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 9618 | 36.5715 | -121.8904 | 6 SP LS OF 6813 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0053345 | OH | Sus | 42444010 | yes | 2015 | AUG | Yes | Line to Line | 1149365 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1112 | 182371112 | OTHER | WIRE DOWN 4 SPANS N/OF 977477 TAP | 20150808 | 1427 | 1285294 | 456 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 4072 | 36.5165 | -121.7386 | 4 SPANS N/OF 977477 TAP | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0053852 | OH | Sus | 0 | yes | 2015 | AUG | Yes | Open Circuit | 1149862 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5237 | 20150819 | 549 | 1291289 | 609 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 15225 | 37.0655 | -122.0795 | LAST SPAN ON TAP LS OF 5237 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0055985 | OH | Sus | 31177096 | No | 2015 | AUG | Yes | Line to Ground | 1151427 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9597 | 20150821 | 1116 | 1292532 | 276 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1380 | 37.1439 | -122.0899 | 401 HARMON GULCH RD | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0056598 | OH | Sus | 42455580 | No | 2015 | AUG | Yes | Line to Ground | 1151802 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 1827 | 20150821 | 1654 | 1292726 | 1317 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 14487 | 37.2132 | -122.1553 | 4 SP LD SIDE OF 1827 AND 6P LD SODE OF 1827 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0056657 | OH | Sus | 31178165 | No | 2015 | AUG | Yes | Line to Line | 1151826 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SOLEDAD-2102 | 182052102 | JUMPER | WIRE DOWN 1 SP LD SIDE OF 9527 | 20150826 | 2309 | 1295224 | 395 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 8445 | 36.3899 | -121.3658 | 1 SPAN LD SIDE OF 9527 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0057613 | OH | Sus | 42458126 | No | 2015 | AUG | Yes | Line to Ground | 1152483 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9737 | 20150827 | 12 | 1295234 | 342 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 6964 | 37.1533 | -122.1302 | 450 BLUE RIDGE DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0057614 | OH | Sus | 42458127 | No | 2015 | AUG | Yes | Line to Ground | 1152484 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5501 | 20150828 | 2026 | 1296412 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 46451 | 37.1432 | -122.1317 | 15275 TWO BAR RD. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0058110 | OH | Sus | 42459959 | No | 2015 | AUG | Yes | Three Phase Fault | 1152811 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HOLLISTER-2105 | 182492105 | FUSE | 4519 | 20150831 | 1428 | 1297820 | 372 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 25668 | 36.5612 | -121.1744 | 1 SP SS CGC: 413697444375 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0058455 | OH | Sus | 42461209 | No | 2015 | AUG | Yes | Line to Ground | 1153131 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 10457 | 20150904 | 1727 | 1300348 | 1228 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 10513 | 37.1087 | -122.046 | 1 SPAN SS/OF MTR#1006215046 (12265 MADRONE) | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0059453 | OH | Sus | 0 | No | 2015 | SEP | Yes | Line to Ground | 1153826 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 1011 | 20150904 | 1915 | 1300397 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 22374 | 37 | -121.8566 | 1 SPAN LOAD SIDE OF 365 RANCHITOS DEL SOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0059455 | OH | Sus | 0 | No | 2015 | SEP | Yes | Line to Ground | 1153831 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 1911 | 20150908 | 1917 | 1301948 | 357 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 6426 | 37.1142 | -121.984 | NYSTROM - 1058/ 408-799-8799: IFO 18500 Main Blvd / xst Circle | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0059925 | OH | Sus | 42466389 | yes | 2015 | SEP | Yes | Line to Ground | 1154215 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5453 | 20150912 | 2240 | 1304825 | 617 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 12957 | 37.1361 | -122.1393 | METER 1007592182 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0061050 | OH | Sus | 42470140 | No | 2015 | SEP | Yes | Line to Ground | 1154935 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND SUB | 8304 | RECLOSER | B1101 | 20150915 | 247 | 1305903 | 911 | Distribution Circuit | 3rd Party | Vehicle | 290 | 91570 | 37.0926 | -122.0966 | FUCO 5175 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on object | 15-0061370 | OH | Sus | 0 | yes | 2015 | SEP | Yes | Three Phase Fault | 1155194 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9597 | 20150915 | 1545 | 1306367 | 655 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2649 | 37.1439 | -122.0899 | 15 SPANS LOAD SIDE OF 9597 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0061560 | OH | Sus | 42473087 | yes | 2015 | SEP | Yes | Line to Line | 1155341 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2107 | 83252107 | OTHER | WIRE DOWN SS MTR 1009798849 | 20150915 | 55 | 1305885 | 1168 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 2324 | 37.0076 | -122.1175 | 997 SMITH GRADE- SANTA CRUZ | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0061408 | OH | Sus | 0 | yes | 2015 | SEP | Yes | None | 1155224 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 6597 | 20150919 | 2005 | 1308771 | 160 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 480 | 36.9969 | -121.7159 | 2 SPANS LOAD SIDE OF 12155 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 15-0062332 | OH | Sus | 0 | No | 2015 | SEP | Yes | Line to Ground | 1155944 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | GREEN VALLEY-2101 | 83192101 | FUSE | 6775 | 20150928 | 902 | 1312984 | 489 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 75 | 26595 | 36.8812 | -121.6414 | 18825 REA AVE | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0066072 | OH | Sus | 31187233 | No | 2015 | SEP | Yes | Line to Line | 1159306 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5179 | 20151002 | 1357 | 1315532 | 511 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 11451 | 37.1076 | -122.1077 | 1 SPAN NOF 5179 ON SINGLE PHASE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0067496 | OH | Sus | 31188317 | No | 2015 | OCT | Yes | Line to Line | 1160253 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 3017 | 20151003 | 1750 | 1316071 | 613 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1226 | 37.1424 | -122.1538 | 1 SP LS OF 3017 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0067617 | OH | Sus | 42489046 | yes | 2015 | OCT | Yes | Line to Ground | 1160376 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | RESERVATION ROAD-1102 | 182731102 | OCB | 1102/2 | 20151003 | 1555 | 1315945 | 845 | Distribution Circuit | 3rd Party | Vehicle | 2093 | 143822 | 36.6242 | -121.6886 | Washington/1811/ 206-8370: off foster rd | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 15-0067604 | OH | Sus | 0 | yes | 2015 | OCT | Yes | Line to Line | 1160363 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 5781 | 20151004 | 442 | 1316494 | 631 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6310 | 37.0448 | -121.8145 | NYSTROM - 1058/ 408-799-8799: Lower Highland Way- 3 spans of wire down | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0067753 | OH | Sus | 0 | yes | 2015 | OCT | Yes | Line to Ground | 1160524 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 7757 | 20151013 | 1405 | 1321237 | 774 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3870 | 37.013 | -121.937 | MTR 1009701921 | Clear-32-90 F | Conductor, Overhead | On Ground | 15-0070014 | OH | Sus | 0 | No | 2015 | OCT | Yes | Line to Ground | 1162045 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 3147 | 20151014 | 1640 | 1321991 | 725 | Distribution Circuit | 3rd Party | Other | 8 | 5800 | 37.0584 | -122.1596 | WELSH: 335 SHAKE MILL RD BONNY DOON | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0070370 | OH | Sus | 0 | yes | 2015 | OCT | Yes | Multi-Fault | 1162270 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | HATTON-1102 | 182291102 | JUMPER | WIRE DOWN 2 SP SS MTR#1008499329 | 20151028 | 138 | 1330147 | 399 | Distribution Circuit | Vegetation | Tree - branch fell on line | 137 | 52703 | 36.3968 | -121.8827 | 2 SP SS MTR#1008499329 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0073742 | OH | Sus | 0 | No | 2015 | OCT | Yes | None | 1164888 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 7595 | 20151029 | 1514 | 1331198 | 693 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4158 | 37.1021 | -121.9819 | 1 SP LD SIDE OF 7595 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0074125 | OH | Sus | 31196176 | No | 2015 | OCT | Yes | Line to Ground | 1165234 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 11865 | 20151102 | 513 | 1333070 | 462 | Distribution Circuit | Vegetation | Tree - branch fell on line | 73 | 33726 | 37.001 | -121.7398 | 1 P SS OF 2029 MAIN LINE | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0074807 | OH | Sus | 31196762 | yes | 2015 | NOV | Yes | Line to Line | 1165859 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6577 | 20151102 | 446 | 1332844 | 645 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 30315 | 37.048 | -121.8081 | MTR#5000044642 | Overcast-Fog-Heavy Rain-32-90 F | Insulator | Broken, wire on object | 15-0074684 | OH | Sus | 0 | yes | 2015 | NOV | Yes | Line to Ground | 1165769 | INS | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | GREEN VALLEY-2101 | 83192101 | SWITCH | 139 | 20151105 | 1421 | 1336140 | 635 | Distribution Circuit | 3rd Party | Vehicle | 8 | 4463 | 36.9098 | -121.6203 | 3 P E/O 139 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 15-0075878 | OH | Sus | 0 | No | 2015 | NOV | Yes | Force Out | 1166695 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | FUSE | 40419 | 20151112 | 519 | 1339790 | 366 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 20496 | 36.4908 | -121.9357 | 204 UPPER WALDEN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0077310 | OH | Sus | 42566982 | No | 2015 | NOV | Yes | Line to Ground | 1167829 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5619 | 20151115 | 1815 | 1342524 | 1815 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 179685 | 37.1095 | -122.0496 | BETWEEN 5627 & 7199 | Strong Winds-Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 15-0078014 | OH | Sus | 0 | yes | 2015 | NOV | Yes | Multi-Fault | 1168500 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 3753 | 20151115 | 1550 | s1169129 | 627 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 8151 | 37.0539 | -121.9527 | LOAD SIDE | Partly Cloudy-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0077968 | OH | Sus | 0 | yes | 2015 | NOV | Yes | Line to Ground | 1169129 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 1491 | 20151115 | 2137 | 1342680 | 734 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 29166 | 36.5058 | -121.9351 | at MTR#1008576636 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0078058 | OH | Sus | 0 | yes | 2015 | NOV | Yes | Line to Ground | 1168544 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | RECLOSER | 2010 | 20151115 | 2333 | 1342723 | 161 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 12962 | 36.5061 | -121.9358 | 1 SP SS OF FUCO 8047 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0078068 | OH | Sus | 0 | yes | 2015 | NOV | Yes | Three Phase Fault | 1168554 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | JUMPER | OJ 2 SP SS OF MTR#1009764386 | 20151116 | 1421 | 1343504 | 309 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 309 | 37.0409 | -121.9353 | at MTR#1009764386 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0078454 | OH | Sus | 0 | yes | 2015 | NOV | Yes | None | 1168886 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 5213 | 20151119 | 2238 | 1345654 | 423 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 10023 | 37.0324 | -122.0768 | 1255 QUARRY RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0079406 | OH | Sus | 42573671 | No | 2015 | NOV | Yes | Line to Line | 1169572 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7593 | 20151121 | 1133 | 1346486 | 647 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 13687 | 37.1058 | -121.9724 | 1 SPAN LOAD SIDE OF 5263 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0079878 | OH | Sus | 42575268 | No | 2015 | NOV | Yes | Line to Ground | 1169996 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 10721 | 20151125 | 1306 | 1348659 | 1412 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 11296 | 37.0855 | -122.1043 | 2/W/O 10721 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0081114 | OH | Sus | 42577427 | No | 2015 | NOV | Yes | Line to Ground | 1170942 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | FUSE | 1293 | 20151203 | 1307 | 1352890 | 833 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4165 | 36.3876 | -121.8719 | 37751 PALO COLORADO RD BY FIRE STATION | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082552 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1172231 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 7347 | 20151203 | 1242 | 1352847 | 833 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 3160 | 37.0411 | -121.9424 | 1 SPAN LD SIDE OF OJS | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082520 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1172208 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE | 6523 | 20151203 | 2121 | 1353515 | 425 | Distribution Circuit | Vegetation | Tree - fell into line | 164 | 20472 | 36.8749 | -121.6417 | LOAD SIDE 6523 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | On Ground | 15-0082660 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1172320 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | RECLOSER | 10954 | 20151204 | 715 | 1353603 | 319 | Distribution Circuit | Equipment Failure/Involved | Overhead | 428 | 58377 | 36.9873 | -121.86 | MARKARIAN-FRED / 559-289-4068: 4 spans on L/S OF SW 1289 | Overcast-Fog-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0082681 | OH | Sus | 42583054 | No | 2015 | DEC | Yes | Line to Ground | 1172344 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER | 5206 | 20151205 | 1253 | 1354339 | 673 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 80760 | 37.0955 | -122.0857 | ON MAIN LINE AT 557 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082942 | OH | Sus | 42583647 | No | 2015 | DEC | Yes | Multi-Fault | 1172540 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 9791 | 20151205 | 824 | 1354199 | 1850 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 101750 | 37.185 | -122.1414 | 294 Fern Dr.- B.C. | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082925 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Line | 1172515 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 9271 | 20151209 | 1301 | 1356306 | 904 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 9251 | 37.0359 | -121.8594 | FLUITT- 3755 / 831-682-1793: 6600 fern flat rd. and 4 spans past | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083632 | OH | Sus | 31205214 | yes | 2015 | DEC | Yes | Line to Ground | 1173273 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | RECLOSER | 39126 | 20151210 | 351 | 1356999 | 448 | Distribution Circuit | Vegetation | Tree - branch fell on line | 136 | 51488 | 37.0778 | -122.1326 | ALVAREZ- 3463 / 831-535-9251: 556 Sunlit Ln- Santa Cruz | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083776 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1173415 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HOLLISTER-2106 | 182492106 | FUSE | 4353 | 20151211 | 947 | 1358748 | 337 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2696 | 36.7697 | -121.4137 | 3 POLES SS/OF MTR#1008640686 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084250 | OH | Sus | 31205662 | yes | 2015 | DEC | Yes | Line to Line | 1173888 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2104 | 83252104 | FUSE | 7603 | 20151215 | 1345 | 1364337 | 789 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 18147 | 37.0844 | -122.0048 | CORI- MARK: 400 sand hill | Clear-32-90 F | Conductor, Overhead | On Ground | 15-0085539 | OH | Sus | 31206634 | No | 2015 | DEC | Yes | Line to Line | 1175258 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 6295 | 20151217 | 2225 | 1365912 | 344 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 10320 | 37.0992 | -122.0867 | AT MTR#1007591422 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086027 | OH | Sus | 42594640 | No | 2015 | DEC | Yes | Line to Ground | 1175907 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 5215 | 20151221 | 1358 | 1367942 | 811 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 32940 | 37.0325 | -122.0765 | MTR 1008735122 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086478 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Multi-Fault | 1176470 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | CAMP EVERS-2105 | 83622105 | FUSE | 5235 | 20151221 | 1838 | 1368197 | 657 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 39420 | 37.0596 | -122.0793 | CAPWELL - 3915 / 831-206-1280: END OF FALL CREEK & END OF FARMER | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086506 | OH | Sus | 42595879 | yes | 2015 | DEC | Yes | Multi-Fault | 1176500 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8503 | 20151222 | 925 | 1369700 | 245 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 490 | 37.1711 | -122.2183 | LOAD SIDE 77767 WIRE DOWN | Strong Winds-Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086804 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1176834 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 12758 | 20151222 | 854 | 1369196 | 516 | Distribution Circuit | Vegetation | Tree - fell into line | 293 | 43849 | 37.1487 | -122.1748 | WEST SIDE OF METER # 279027 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086709 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1176716 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 11867 | 20151222 | 1652 | 1369846 | 732 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 19764 | 37.1248 | -122.1265 | 1007589976 AT MET | Rain-Strong Winds-Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086831 | OH | Sus | 0 | yes | 2015 | DEC | Yes | None | 1176863 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2002 | 20151222 | 322 | 1368615 | 2340 | Distribution Circuit | Equipment Failure/Involved | Overhead | 124 | 245426 | 36.2249 | -121.7589 | LD SIDE OF 56653 ON MAIN LINE | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086603 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Multi-Fault | 1176599 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8983 | 20151222 | 101 | 1368445 | 808 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 16368 | 37.0367 | -122.1496 | CAPWELL - 3915 / 831-206-1280: BTWN 4208 SMITH GRADE & 3131 SMITH GRADE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086589 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1176583 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | TRANSFORMER | 315379520157 | 20151223 | 624 | 1370113 | 474 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 474 | 37.0427 | -122.0842 | 890 LOST ACRES DR | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086928 | OH | Sus | 42596744 | No | 2015 | DEC | Yes | Line to Ground | 1176960 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 8353 | 20151223 | 837 | 1370178 | 567 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 2379 | 37.0582 | -121.9417 | 15 SPANS LD SIDE 8353 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086945 | OH | Sus | 42596882 | No | 2015 | DEC | Yes | Line to Ground | 1177007 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | FUSE | 32690 | 20151228 | 950 | 1373325 | 1030 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 14880 | 36.2411 | -121.8092 | 1 SPAN LOAD SIDE OF 32690 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 15-0087644 | OH | Sus | 31209142 | No | 2015 | DEC | Yes | Line to Line | 1177782 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1101 | 182291101 | RECLOSER | 37088 | 20160103 | 539 | 1376114 | 411 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2070 | 76224 | 36.5464 | -121.8985 | at MTR#10099549952 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0002547 | OH | Sus | 31210101 | No | 2016 | JAN | Yes | Line to Ground | 1178462 | CAW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8501 | 20160105 | 1125 | 1377274 | 590 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 11800 | 37.1653 | -122.201 | MTR 1009128583 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0003008 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1178744 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 12383 | 20160105 | 1004 | 1377358 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 10925 | 37.1649 | -122.1934 | MTR 1009128583 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0003164 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1178797 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | SWITCH | 11803 | 20160105 | 1918 | 1377811 | 458 | Distribution Circuit | Equipment Failure/Involved | Overhead | 184 | 50196 | 37.078 | -122.0318 | SW 11803 PN DOWN | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | On Ground | 16-0003205 | OH | Sus | 42600852 | yes | 2016 | JAN | Yes | Force Out | 1178822 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | PAUL SWEET-2109 | 83252109 | FUSE | 6003 | 20160105 | 305 | 1376993 | 618 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 76632 | 36.992 | -121.9269 | 1 SS OF 79279 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0002858 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1178668 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 8645 | 20160105 | 608 | 1377047 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 28904 | 37.0115 | -121.885 | CRIVELLO- 4176 / 831-682-1912: 5 poles from c/o 1195 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0002904 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1178698 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 6097 | 20160106 | 436 | 1377992 | 459 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3213 | 37.0197 | -122.0274 | 4 SP LS OF 6097 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003268 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1178889 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | RECLOSER | 2010 | 20160106 | 650 | 1378014 | 160 | Distribution Circuit | Vegetation | Tree - branch fell on line | 121 | 7430 | 36.5061 | -121.9358 | Sissom/ 5808/ 206-2617: 3 spans loadside of 2853 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003288 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1178906 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 5989 | 20160106 | 601 | 1378052 | 624 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 7637 | 37.0576 | -121.9424 | MTR 1009790861 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0003301 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1178914 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | TRANSFORMER | 314949021410 | 20160106 | 1205 | 1378576 | 755 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2701 | 37.0753 | -122.2327 | MTR#7H9282 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003520 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1179058 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9307 | 20160107 | 306 | 1379312 | 887 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3548 | 37.1165 | -122.1141 | 2 SPANS LD SIDE OF FUCO 9307 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003732 | OH | Sus | 42602587 | yes | 2016 | JAN | Yes | Line to Ground | 1179212 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2102 | 83252102 | FUSE | 11103 | 20160107 | 228 | 1379263 | 744 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 4657 | 36.9936 | -122.0698 | 2 SPANS FROM END OF 11827 TAP | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003685 | OH | Sus | 31211054 | yes | 2016 | JAN | Yes | Line to Ground | 1179182 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8511 | 20160109 | 1036 | 1380720 | 414 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5796 | 37.0618 | -122.1474 | STORMENT- 4178 / 831-278-0287: 545 Westdale Dr.- S.C. | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0004208 | OH | Sus | 42603944 | No | 2016 | JAN | Yes | Line to Line | 1179627 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 83815 | 20160113 | 625 | 1382571 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 6402 | 36.9946 | -122.0285 | 230 OLD GRAHAM HILL RD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0004967 | OH | Sus | 31212367 | yes | 2016 | JAN | Yes | Line to Ground | 1180241 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | FUSE | 78253 | 20160115 | 844 | 1384715 | 553 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 553 | 36.19 | -121.6984 | LOAD SIDE OF 78253 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0005710 | OH | Sus | 31213238 | No | 2016 | JAN | Yes | Line to Line | 1180683 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 8095 | 20160115 | 1534 | 1384702 | 906 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 14496 | 37.0022 | -121.9417 | 15 SP LD SIDE OF FUCO 8095 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0005740 | OH | Sus | 0 | No | 2016 | JAN | Yes | Line to Ground | 1180707 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 6673 | 20160117 | 1959 | 1385723 | 709 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 53080 | 36.9915 | -121.8281 | 3 SPANS PAST 1593 ON MAIN LINE | Rain-Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0005949 | OH | Sus | 31213414 | yes | 2016 | JAN | Yes | Line to Ground | 1180916 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 9507 | 20160118 | 107 | 1385829 | 823 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2469 | 37.0352 | -122.0177 | 2 SPANS LD SIDE OF FUSES 9507 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0005985 | OH | Sus | 31213416 | yes | 2016 | JAN | Yes | None | 1180952 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 8405 | 20160119 | 1502 | 1387831 | 783 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 27247 | 36.5791 | -121.8688 | 7 SP LS 8405 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006565 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1181387 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 63868 | 20160119 | 1532 | 1387830 | 522 | Distribution Circuit | Vegetation | Tree - fell into line | 418 | 218196 | 36.2641 | -121.7954 | 2 SP LS 10441 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006548 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1181374 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | SWITCH | 1279 | 20160119 | 1340 | 1387711 | 911 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 64561 | 37.0123 | -121.9368 | MTR#341920 | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0006478 | OH | Sus | 0 | yes | 2016 | JAN | Yes | None | 1181330 | CAW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 5819 | 20160119 | 1032 | 1387281 | 238 | Distribution Circuit | Equipment Failure/Involved | Overhead | 90 | 16684 | 37.0447 | -121.8131 | OJ 1/E OF 5819 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006367 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Open Circuit | 1181259 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6711 | 20160119 | 2310 | 1388220 | 1006 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 17528 | 36.998 | -121.8689 | MTR#1009255774 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006697 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1181507 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | RECLOSER | 10960 | 20160121 | 510 | 1389021 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 2420 | 108690 | 36.9866 | -121.8582 | NYSTROM - 1058/ 408-799-8799: Day Valley and Freedom Blvd | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007000 | OH | Sus | 42614744 | No | 2016 | JAN | Yes | Line to Ground | 1181714 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 8469 | 20160122 | 1433 | 1390165 | 747 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 747 | 37.1544 | -122.0824 | 2 SPANS LOAD SIDE OF 8469 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007535 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1182028 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5487 | 20160122 | 1612 | 1390218 | 428 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 23968 | 37.1371 | -122.1006 | STORMENT- 4178 / 831-278-0287: 720 Hopkins Gulch Rd.- B.C. | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007540 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1182033 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 2989 | 20160122 | 1610 | 1390211 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2300 | 37.1634 | -122.0764 | CRIVELLO- 4176 / 831-682-1912: at c/o 2989 | Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007543 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1182035 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9725 | 20160122 | 1833 | 1390317 | 677 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 8145 | 37.1522 | -122.1366 | 545 SUNSET RD | Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007567 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1182049 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER | WIRE DOWN AT 5157 | 20160122 | 1231 | 1390111 | 725 | Distribution Circuit | Vegetation | Tree - fell into line | 258 | 125646 | 37.0839 | -122.089 | AT FUSE 5157 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007485 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Open Circuit | 1182011 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 839 | 20160122 | 2259 | 1390429 | 550 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 18700 | 37.1298 | -122.0177 | 2 SPANS LOAD SIDE C/O 839 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007667 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1182156 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 1909 | 20160122 | 1443 | 1390155 | 935 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4675 | 37.0976 | -121.9772 | WITHIN FIRST SPAN LOAD SIDE OF 1909 | Rain-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007539 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1182030 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 7993 | 20160122 | 2322 | 1390434 | 719 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 21570 | 37.0284 | -121.7411 | 515 SUMMIT RD | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007670 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1182159 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 8949 | 20160122 | 2359 | 1390440 | 595 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 7140 | 36.5009 | -121.9335 | MTR#78L657 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007676 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1182165 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | TRANSFORMER | 315962019383 | 20160122 | 1549 | 1390230 | 566 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1132 | 37.0241 | -121.8851 | BRANDT- 4179 / 831-212-2088: 4400 Trout Gulch Rd tree brought wire down | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007555 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1182040 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 8021 | 20160122 | 2234 | 1390418 | 459 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 18777 | 36.5868 | -121.9096 | 4 SP LS 8021 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007662 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1182151 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5901 | 20160123 | 606 | 1390545 | 389 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 6613 | 37.0945 | -121.9715 | 1535 TUCKER | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007699 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1182190 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7351 | 20160123 | 816 | 1390603 | 451 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 902 | 37.0557 | -121.978 | 4 SPANS LOAD SIDE OF 7351 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007710 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1182203 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER | OJ MTR# 1009700849 | 20160123 | 1626 | 1390988 | 484 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 484 | 37.092 | -121.9635 | 1535 TUCKER RD | Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007796 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Open Circuit | 1182292 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | JUMPER | WIRE DOWN AT MILE MARKER 8.11 ON EUREKA CYN | 20160123 | 504 | 1390589 | 532 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 5266 | 37.0585 | -121.8219 | MILE MARKER 8.11 ON EUREKA CYN - LOAD SIDE OF MTR 10075918875 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007704 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Open Circuit | 1182194 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 3893 | 20160123 | 1600 | 1390916 | 1256 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 21352 | 36.9685 | -121.8552 | 1 SPAN LOAD SIDE OF 3893 | Rain-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007780 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1182276 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER | 315441220717 | 20160124 | 2106 | 1391385 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 3318 | 37.0585 | -122.0635 | 7090 MCADAMS LN- FELTON | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007911 | OH | Sus | 42616560 | No | 2016 | JAN | Yes | Line to Ground | 1182417 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE | 1569 | 20160124 | 9 | 1391043 | 400 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 16440 | 36.8741 | -121.6216 | 1 SP LS MTR1009549541 | Overcast-Fog-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0007828 | OH | Sus | 42616443 | No | 2016 | JAN | Yes | Line to Ground | 1182331 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER | 3729 | 20160125 | 814 | 1391497 | 1097 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3291 | 37.1979 | -122.1542 | at MTR 1007347654 | Clear-Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0008032 | OH | Sus | 42617002 | No | 2016 | JAN | Yes | None | 1182512 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 12122 | 20160126 | 2229 | 1392675 | 524 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 40872 | 37.0664 | -122.2286 | 2 SP SS OF 10559 AND GOES AT LEAST 10 SP LS OF 10559 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0008510 | OH | Sus | 31215222 | No | 2016 | JAN | Yes | Line to Ground | 1182820 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2105 | 83692105 | RECLOSER | 71630 | 20160126 | 222 | 1392097 | 917 | Distribution Circuit | Vegetation | Tree - fell into line | 626 | 126046 | 36.976 | -121.8947 | 250 APTOS SCHOOL ROAD MTR#9315R5 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0008207 | OH | Sus | 31215002 | No | 2016 | JAN | Yes | Force Out | 1182626 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | GREEN VALLEY-2101 | 83192101 | FUSE | 4373 | 20160129 | 2338 | 1394339 | 666 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1332 | 36.9725 | -121.7213 | 601 HECKER PASS RD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009252 | OH | Sus | 0 | No | 2016 | JAN | Yes | Line to Ground | 1183339 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5629 | 20160130 | 1541 | 1394568 | 889 | Distribution Circuit | 3rd Party | Other | 20 | 17780 | 37.1128 | -122.0481 | 12749 LOMPICO RD- 11 SPANS LOAD SIDE OF 5629 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0009308 | OH | Sus | 0 | No | 2016 | JAN | Yes | Line to Line | 1183395 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9779 | 20160131 | 1755 | 1395381 | 578 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4046 | 37.1545 | -122.0827 | 5 SP LS 9779 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009539 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1183620 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 4295 | 20160131 | 1436 | 1394945 | 924 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 9456 | 37.033 | -122.0109 | 1251 REDWOOD DR | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009465 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1183542 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | OCB | 401/2 | 20160131 | 1602 | s1183578 | 793 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 12906 | 37.0491 | -122.0645 | MTR 1007590377 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009469 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1183578 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | FUSE | 457 | 20160131 | 1957 | 1395570 | 2463 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 26667 | 36.4913 | -121.9325 | 212 CREST RD # A | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009640 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1183723 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 9089 | 20160131 | 1832 | 1395441 | 1854 | Distribution Circuit | Vegetation | Tree - fell into line | 147 | 272538 | 36.6057 | -121.9381 | 1 SPAN EAST OF 8175 AND 1074 MISSION RD. | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009593 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1183674 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 9127 | 20160131 | 1924 | 1395539 | 1226 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 14712 | 36.604 | -121.9361 | 2418 RACCON TRAIL | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009757 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1183820 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 1445 | 20160131 | 2246 | 1395817 | 724 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 36351 | 36.5735 | -121.9107 | E & W OF 786229 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009612 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1183694 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | WIRE DOWN 1 SPAN SS OF 1913 | 20160201 | 1437 | 1396535 | 658 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 17766 | 37.1159 | -121.9825 | 1 POLES SS OF 1913 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009898 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Open Circuit | 1183885 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 2835 | 20160201 | 1426 | 1396571 | 446 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 18732 | 36.5859 | -121.8752 | 3 SPANS SOURCE SIDE OF 10383 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009872 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Line | 1183874 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | OTHER | WIRES DOWN TWD MTR 1008580315 | 20160201 | 456 | 1395956 | 658 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 10956 | 36.4962 | -121.938 | BILBREY/523: 161 spindrift | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009643 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1183727 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | JUMPER | OJ TO TAP FEEDING MTR#1008880479 TO EOL | 20160201 | 48 | 1395871 | 1002 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3006 | 36.5829 | -121.9344 | MTR#1008880479 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009637 | OH | Sus | 0 | yes | 2016 | FEB | Yes | None | 1183720 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 42365 | 20160201 | 48 | 1395946 | 197 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 1182 | 36.5828 | -121.9343 | MTR#1008880479 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009638 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1183721 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | SECTIONALIZER | 8655 | 20160203 | 1634 | 1397952 | 574 | Distribution Circuit | Vegetation | Tree - fell into line | 179 | 34110 | 37.1402 | -122.0938 | 3/S/O 8469 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0010396 | OH | Sus | 31217035 | No | 2016 | FEB | Yes | Line to Ground | 1184242 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 4745 | 20160218 | 935 | 1408554 | 535 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 535 | 37.0939 | -122.1129 | TREE CAME DOWN 100 FT LD SIDE OF 4745 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013881 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186869 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2705 | 20160218 | 727 | 1407955 | 700 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 17500 | 37.0005 | -121.7405 | BET 3455 & 10413 ON MAINLINE | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013713 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Line | 1186766 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2105 | 83252105 | FUSE | 4471 | 20160218 | 450 | 1407739 | 778 | Distribution Circuit | Vegetation | Tree - fell into line | 200 | 58839 | 37.0009 | -122.0142 | at MTR# 1008902472 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013593 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186673 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 9949 | 20160218 | 42 | 1407656 | 860 | Distribution Circuit | Vegetation | Tree - bark fell into line | 31 | 25500 | 37.016 | -121.8207 | at MTR#540R55 TREE IN LINE WIRE ON GRD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013573 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186655 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | OTHER | WIRE DOWN 2 SPANS N/OF 7685 | 20160219 | 916 | 1409124 | 266 | Distribution Circuit | Vegetation | Tree - fell into line | 412 | 18740 | 36.583 | -121.8647 | WIRE DOWN 2 SPANS N/OF 7685 ON MAIN LIN | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 16-0014099 | OH | Sus | 42633888 | No | 2016 | FEB | Yes | Line to Ground | 1187031 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5521 | 20160221 | 213 | 1409940 | 892 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 38356 | 37.1575 | -122.1357 | 6 SPANS LD 5521 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0014527 | OH | Sus | 0 | No | 2016 | FEB | Yes | Line to Ground | 1187323 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2105 | 83252105 | OTHER | 2457 | 20160222 | 1711 | 1410672 | 521 | Distribution Circuit | Vegetation | Tree - branch fell on line | 58 | 5024 | 37.0062 | -121.9912 | AT 2481 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0014796 | OH | Sus | 42638219 | No | 2016 | FEB | Yes | Line to Ground | 1187579 | CSO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | OJ AT HARD TAP 127 LOMPCO RD | 20160225 | 2039 | 1412374 | 521 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 521 | 37.1174 | -122.0496 | 10 SPANS LOAD SIDE 5629 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0015745 | OH | Sus | 42641382 | No | 2016 | FEB | Yes | Multi-Fault | 1188196 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8505 | 20160228 | 1025 | 1413279 | 258 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1032 | 37.1759 | -122.2196 | 3 SPANS S/S OF METER # 152069 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0016092 | OH | Sus | 31221980 | No | 2016 | FEB | Yes | Line to Ground | 1188469 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 9271 | 20160229 | 2307 | 1413928 | 583 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 4029 | 37.0359 | -121.8594 | 6200 APTOS VIEW RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0016361 | OH | Sus | 42643054 | No | 2016 | FEB | Yes | Line to Ground | 1188668 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2105 | 83252105 | FUSE | 12119 | 20160304 | 2116 | 1416164 | 635 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2540 | 37.0052 | -121.9836 | STORMENT- 4178 / 831-278-0287: Past 4050 Paul Sweet Rd.- S.C. | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017363 | OH | Sus | 42647426 | No | 2016 | MAR | Yes | Line to Line | 1189265 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5479 | 20160306 | 2249 | 1422881 | 399 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5586 | 37.1292 | -122.113 | 142 NELLY LANE | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018610 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190454 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8365 | 20160306 | 1011 | 1422825 | 1372 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 39788 | 37.1667 | -122.2007 | 4 TO 5 POLES FROM 8365 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018641 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190486 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | SWITCH | 8483 | 20160306 | 5 | 1421061 | 1189 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 168838 | 37.0336 | -122.0781 | CRIVELLO- 4176 / 831-682-1912: 1084 LAKESIDE DR. | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018227 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Open Circuit | 1190094 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | RECLOSER | 12882 | 20160306 | 312 | 1421014 | 754 | Distribution Circuit | Vegetation | Tree - fell into line | 258 | 135236 | 37.0502 | -121.9813 | MONSIBAIS- MANUEL: 8345 WIRE FOUND ON GROUND BOTH SIDE OF POLE | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018189 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190058 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9125 | 20160306 | 539 | 1421137 | 1881 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 32130 | 37.1005 | -122.086 | 11059 LOVE CREEK RD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018341 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190194 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | WIRE DOWN LAST SPAN ON TAP LINE | 20160306 | 1214 | 1421851 | 548 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 548 | 37.1078 | -122.056 | WIRE DOWN LAST SPAN ON TAP LINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018435 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Open Circuit | 1190272 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 10719 | 20160306 | 1346 | 1422200 | 149 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 596 | 37.0864 | -122.1043 | NA | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018458 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Force Out | 1190295 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 11006 | 20160306 | 2228 | 1422855 | 723 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 68655 | 37.05 | -122.0657 | 1 SP LS 6191 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018603 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190445 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2667 | 20160306 | 905 | 1421612 | 445 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2225 | 37.0261 | -121.775 | LD SIDE OF 2667 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018489 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190326 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2105 | 83252105 | OTHER | 10671 | 20160306 | 554 | 1421343 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 156 | 22068 | 37.0073 | -122.0204 | 2/S/O 10671 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018302 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190165 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2107 | 83252107 | FUSE | 11829 | 20160306 | 2350 | 1422906 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1875 | 37.009 | -122.0756 | 3 SP W/O 11829 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018627 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190471 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 7259 | 20160306 | 224 | 1420964 | 860 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 37840 | 36.5752 | -121.9365 | MTR#1009441055 | Clear-32-90 F | Conductor, Overhead | On Ground | 16-0018214 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190082 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | JUMPER | WIRE DOWN FROM TREE 1 SPAN LD SIDE OF MTR#10 | 20160306 | 56 | 1420965 | 874 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1748 | 36.5746 | -121.9427 | 1 SPAN LD SIDE OF MTR#1009758307 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018239 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Open Circuit | 1190107 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 7537 | 20160306 | 235 | 1420985 | 461 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2305 | 36.572 | -121.9054 | 1 SP LS 7537 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018199 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190068 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 2989 | 20160307 | 1150 | 1423875 | 751 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3004 | 37.1634 | -122.0764 | 1 SPAN SOUTH OF 2989 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0019009 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190759 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 4857 | 20160307 | 1355 | 1424107 | 457 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 5027 | 37.0909 | -122.0948 | STORMENT- 4178 / 831-278-0287: 9670 Old County Rd.- B.L. | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018992 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190745 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1112 | 182371112 | FUSE | 2961 | 20160307 | 539 | 1423216 | 861 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 7601 | 36.486 | -121.7374 | 2 SPANS SS OF MTR 1008975139 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018726 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190566 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | PAUL SWEET-2106 | 83252106 | FUSE | 7749 | 20160307 | 2116 | 1424728 | 39 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 1911 | 36.9978 | -121.9506 | 3 SPANS SS OF 6289 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0019106 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190863 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2107 | 83252107 | FUSE | 11829 | 20160307 | 708 | 1423342 | 430 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2150 | 37.009 | -122.0756 | 2 POLES LD SIDE OF 11829 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018782 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190610 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 6445 | 20160307 | 420 | 1423141 | 1631 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 11417 | 36.5809 | -121.919 | 2 SPANS LD SIDE OF 6445 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018682 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190525 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | SECTIONALIZER | 40017 | 20160307 | 1849 | 1424632 | 229 | Distribution Circuit | Vegetation | Tree - fell into line | 912 | 80387 | 36.5786 | -121.9085 | 5 SPANS NORTH OF 9893 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0019045 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190790 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 9623 | 20160307 | 1756 | 1424412 | 1204 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 57834 | 36.5722 | -121.9058 | 1 POLE SOUTH OF 9623 & SEVERAL SPANS BEYOND 7537 DUE TO TREES | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0019038 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190784 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER | WIRE DOWN 2/W/O 2231 | 20160308 | 546 | 1425066 | 754 | Distribution Circuit | Vegetation | Tree - fell into line | 441 | 62433 | 37.1017 | -122.0589 | 2/W/O 2231 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0019187 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190965 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | SWITCH | 8235 | 20160308 | 931 | 1425065 | 236 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 15260 | 37.1143 | -121.9713 | 1117 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018413 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190964 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5515 | 20160311 | 1225 | 1427727 | 135 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 12285 | 37.1524 | -122.1342 | at 5515 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 16-0020435 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1191850 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER | WIRE DOWN MTR 1007591907 | 20160311 | 1338 | 1427941 | 279 | Distribution Circuit | Equipment Failure/Involved | Overhead | 639 | 174731 | 37.1289 | -122.1149 | MTR 1007591907 | Overcast-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0020451 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Force Out | 1191860 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5515 | 20160311 | 1446 | 1428097 | 455 | Distribution Circuit | Vegetation | Tree - branch fell on line | 91 | 41405 | 37.1524 | -122.1342 | 535 BLUE RIDGE & WIRE DOWN at 15526 KINGS CREEK RD PER T-MAN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020594 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1191964 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 12383 | 20160311 | 455 | 1427036 | 430 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 26660 | 37.1649 | -122.1934 | ON MAINLINE at 5565 TAP | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 16-0020191 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Multi-Fault | 1191715 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 2323 | 20160311 | 1927 | 1428734 | 843 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1327 | 37.1746 | -122.1383 | MTR 1007590133 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 16-0020695 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192068 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER | WIRE DOWN @ 600 MITCHELL | 20160311 | 2102 | 1428892 | 447 | Distribution Circuit | Vegetation | Tree - fell into line | 419 | 9213 | 37.1659 | -122.128 | 600 MITCHEL | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020698 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Open Circuit | 1192071 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 6753 | 20160311 | 1134 | 1427656 | 380 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 15200 | 36.5659 | -121.8877 | 6637 | Partly Cloudy-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0020449 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1191858 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 5104 | 20160311 | 1209 | 1427704 | 1781 | Distribution Circuit | Vegetation | Tree - fell into line | 256 | 137794 | 37.0302 | -122.1868 | WELSH: 297 SWANTON RD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020384 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1191820 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | JUMPER | OJ AT MTR1008746636 | 20160311 | 1415 | 1428294 | 1245 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 599 | 36.9841 | -121.8703 | MTR#1009297581 | Overcast-Drizzle-32-90 F | Conductor, Overhead | On Ground | 16-0020532 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1191915 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2105 | 83692105 | OCB | 2105/2 | 20160311 | 1052 | s1191797 | 468 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4976 | 596817 | 36.9794 | -121.8671 | at C-0328 & SS 10205 & 3 SP LOAD SIDE FUCO 6135 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020334 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1191797 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 1421 | 20160311 | 901 | 1427258 | 444 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 6678 | 36.5742 | -121.9483 | 1450 oleada | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020275 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1191767 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 2253 | 20160312 | 1507 | 1429549 | 1513 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 6062 | 37.1711 | -122.1653 | 22 SPANS LD SIDE OF FUCO 2253 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020817 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1192199 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 3537 | 20160312 | 1730 | 1429678 | 1049 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 7956 | 37.0749 | -121.9603 | 558 RICHARDSON RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020837 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192226 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 2145 | 20160312 | 1 | 1428982 | 395 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1185 | 36.5682 | -121.9289 | 3 SPANS WEST OF 2145 | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 16-0020699 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192072 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5485 | 20160313 | 600 | 1429920 | 576 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 12978 | 37.1322 | -122.1091 | 480 ORMAN RD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020890 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1192278 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 5461 | 20160313 | 147 | 1429891 | 760 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 15960 | 37.1383 | -122.1435 | at 7055 ON MAINLNIE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 16-0020873 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192263 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 5215 | 20160313 | 1959 | 1430599 | 377 | Distribution Circuit | Vegetation | Tree - branch fell on line | 60 | 22620 | 37.0325 | -122.0765 | 1190 SCENEIC DRIVE | Overcast-Rain-32-90 F | Conductor, Overhead | On Ground | 16-0021060 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1192427 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 5749 | 20160313 | 506 | 1429913 | 475 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2850 | 37.0002 | -122.0375 | 4 SP LD SIDE OF 5749 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020924 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192302 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10718 | 20160313 | 1713 | 1430411 | 500 | Distribution Circuit | Environmental/External | Flood/Erosion | 230 | 31644 | 37.0361 | -122.107 | BOYNTON- 3459 / 831-331-6620: 5550 EMPIRE GRADE RD | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021010 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Three Phase Fault | 1192386 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 11865 | 20160313 | 136 | 1429856 | 1541 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 39893 | 37.001 | -121.7398 | 6 TRANSF LD SIDE OF FUCO 11865 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020874 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Multi-Fault | 1192264 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 5955 | 20160313 | 1053 | 1430085 | 1006 | Distribution Circuit | Vegetation | Tree - bark fell into line | 169 | 101467 | 37.0021 | -121.9422 | 10 SP LS 1279 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020928 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192307 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 5401 | 20160313 | 1252 | 1430191 | 583 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 36902 | 37.0648 | -122.1233 | 3 SPANS LOAD SIDE OF 5401 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020989 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192366 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 6121 | 20160313 | 1938 | 1430584 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 52812 | 36.9836 | -121.8848 | 805 VALENCIA | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | On Ground | 16-0021048 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192416 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2105 | 83692105 | FUSE | 1181 | 20160313 | 2121 | 1430652 | 355 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 3905 | 36.9792 | -121.8923 | HAS TREE THROUGH THE LINE WIRE DOWN 2 SPANS LD SIDE OF 1181 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021064 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192431 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 12125 | 20160314 | 1125 | 1431177 | 579 | Distribution Circuit | Environmental/External | Flood/Erosion | 3 | 1737 | 37.2253 | -122.1487 | APPX 4 POLES LD SIDE OF 12125 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021234 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192575 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 63868 | 20160328 | 956 | 1439720 | 419 | Distribution Circuit | Vegetation | Tree - fell into line | 416 | 165634 | 36.2641 | -121.7954 | on mainline at FCO 9567 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0024358 | OH | Sus | 31227619 | yes | 2016 | MAR | Yes | Line to Ground | 1194916 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN JUSTO-1101 | 183181101 | FUSE | 4245 | 20160331 | 1704 | 1442457 | 526 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 13676 | 36.8938 | -121.5973 | 4 SPANS L/S OF 4245 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0025410 | OH | Sus | 0 | No | 2016 | MAR | Yes | Line to Ground | 1195608 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8505 | 20160404 | 1800 | 1444420 | 130 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 520 | 37.1759 | -122.2196 | 5 SPANS L/S OF 8505 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0026081 | OH | Sus | 0 | No | 2016 | APR | Yes | Line to Ground | 1196132 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER | 7289 | 20160410 | 2131 | 1448529 | 340 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 4760 | 37.1709 | -122.1805 | 6 SPANS L/S OF 7289 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0027654 | OH | Sus | 42675792 | No | 2016 | APR | Yes | Line to Ground | 1197245 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | RECLOSER | 5300 | 20160410 | 1526 | 1448321 | 467 | Distribution Circuit | Vegetation | Tree - fell into line | 368 | 68729 | 37.0383 | -122.0709 | 123 PINE AVE | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0027610 | OH | Sus | 42675784 | No | 2016 | APR | Yes | Line to Ground | 1197200 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | JUMPER | WIRE DOWN 4 SS OF 56893 | 20160411 | 1114 | 1448824 | 296 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2072 | 37.0607 | -121.8228 | 4 SPANS SS OF 56893 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0027774 | OH | Sus | 0 | No | 2016 | APR | Yes | Force Out | 1197335 | PW | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 11865 | 20160415 | 1735 | 1451658 | 620 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 24560 | 37.001 | -121.7398 | 2 SS OF MTR 5000040125 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0029048 | OH | Sus | 42680308 | yes | 2016 | APR | Yes | Three Phase Fault | 1198205 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 6645 | 20160415 | 1613 | 1451585 | 732 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 8784 | 37.0119 | -121.7939 | 3 LD SIDE OF 6645 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0029036 | OH | Sus | 0 | yes | 2016 | APR | Yes | Three Phase Fault | 1198196 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5185 | 20160419 | 633 | 1453456 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 8208 | 37.1075 | -122.1095 | ALTA VIA RIDGE & MOON RIDGE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0029555 | OH | Sus | 42681859 | No | 2016 | APR | Yes | Line to Ground | 1198656 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE | 3383 | 20160423 | 2221 | 1456895 | 558 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4464 | 36.8863 | -121.6338 | WELSH: 492 CARR AVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0030984 | OH | Sus | 42684584 | No | 2016 | APR | Yes | Line to Ground | 1199647 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | SECTIONALIZER | 12157 | 20160424 | 2204 | 1457731 | 868 | Distribution Circuit | Vegetation | Tree - branch fell on line | 740 | 180210 | 37.1071 | -122.1071 | CRIVELLO- 4176 / 831-682-1912: clear creek and hwy 9 | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 16-0031130 | OH | Sus | 42684746 | yes | 2016 | APR | Yes | Three Phase Fault | 1199808 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20160425 | 1634 | 1458827 | 937 | Distribution Circuit | Vegetation | Tree - fell into line | 845 | 117481 | 36.5786 | -121.9085 | MULTIPLE - EL BOSQUE & SUNRIDGE- PB | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0031403 | OH | Sus | 31234176 | yes | 2016 | APR | Yes | Line to Ground | 1200023 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 6741 | 20160427 | 2005 | 1460544 | 384 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2688 | 36.5716 | -121.8844 | 2 SPANS LD SIDE OF 6741 | Overcast-32-90 F | Conductor, Overhead | On Ground | 16-0032134 | OH | Sus | 31234923 | yes | 2016 | APR | Yes | Line to Ground | 1200570 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2105 | 83252105 | FUSE | 2457 | 20160427 | 1609 | 1460344 | 676 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 13428 | 37.0062 | -121.9912 | 1 SOUTH OF 3759 ON SINGLE PHASE TO NORTH AND 3 PHASE TO SOUTH | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0032098 | OH | Sus | 31234922 | yes | 2016 | APR | Yes | Line to Ground | 1200534 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | FUSE | 7611 | 20160428 | 539 | 1460687 | 431 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 6253 | 36.3864 | -121.8708 | 1 SP SS OF MTR#1009290285 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0032267 | OH | Sus | 42686770 | No | 2016 | APR | Yes | Line to Ground | 1200694 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 8321 | 20160430 | 1513 | 1462313 | 797 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4782 | 37.0397 | -121.9767 | 6 SPANS LOAD SIDE OF 8321 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0032899 | OH | Sus | 31235656 | yes | 2016 | APR | Yes | Line to Ground | 1201171 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 7279 | 20160501 | 1322 | 1462722 | 766 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4596 | 37.0995 | -122.1011 | 1 SPAN LOAD SIDE OF 7279 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0033052 | OH | Sus | 42687948 | No | 2016 | MAY | Yes | Line to Line | 1201331 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | JUMPER | OJ 5 SP LD SIDE OF FUCO 6079 | 20160504 | 1004 | 1464504 | 400 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 4168 | 37.0559 | -122.0305 | 146 GREEN VALLEY DR | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0033740 | OH | Sus | 0 | No | 2016 | MAY | Yes | Force Out | 1201917 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 45255 | 20160504 | 1959 | 1464750 | 295 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 11505 | 36.5864 | -121.9148 | AT MTR # 1008409207 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0033871 | OH | Sus | 31236615 | No | 2016 | MAY | Yes | Line to Ground | 1201973 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6851 | 20160507 | 1156 | 1466393 | 454 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 7718 | 37.042 | -121.8165 | STORMENT- 4178 / 831-278-0287: 1518 & 1550 Tindall Ranch Rd.- Wat. | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0034647 | OH | Sus | 42692324 | No | 2016 | MAY | Yes | Line to Ground | 1202497 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | OTHER | 8557 | 20160508 | 906 | 1466640 | 423 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2538 | 36.5665 | -121.8861 | 4 SPANS L/S OF 8557 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0034705 | OH | Sus | 42692347 | No | 2016 | MAY | Yes | Line to Ground | 1202558 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LOS OSITOS-2103 | 182082103 | RECLOSER | 7062 | 20160510 | 653 | 1467365 | 307 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 3804 | 36.2789 | -121.303 | TAP at FUSE 9353 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0035007 | OH | Sus | 31237636 | No | 2016 | MAY | Yes | Line to Ground | 1202770 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | RECLOSER | 2010 | 20160511 | 1335 | 1468169 | 257 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 14145 | 36.5061 | -121.9358 | 1 SPAN SOUTH OF 2010 TAP TO EAST | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0035375 | OH | Sus | 31237973 | No | 2016 | MAY | Yes | Line to Ground | 1203043 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 83815 | 20160604 | 511 | 1482652 | 1001 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 10693 | 36.9946 | -122.0285 | 1 SPAN S/S OF METER # 1008445794 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 16-0041023 | OH | Sus | 0 | No | 2016 | JUN | Yes | Line to Ground | 1207283 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5187 | 20160608 | 43 | 1485001 | 668 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 26052 | 37.107 | -122.1095 | 11780 CLEAR CREEK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0041802 | OH | Sus | 42714501 | No | 2016 | JUN | Yes | Line to Line | 1207926 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 7989 | 20160610 | 1654 | 1486841 | 638 | Distribution Circuit | Equipment Failure/Involved | Overhead | 261 | 83491 | 36.9817 | -121.8645 | WIRE DOWN at MTR# 29G300 ON MAINLINE- SS OF 7921 | Clear-32-90 F | Insulator | Broken, wire on ground | 16-0042514 | OH | Sus | 31246842 | No | 2016 | JUN | Yes | Line to Ground | 1208405 | INS | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6851 | 20160614 | 716 | 1488487 | 649 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 11033 | 37.042 | -121.8165 | CAPWELL - 3915 / 831-206-1280: BTWN 1518 AND 1550 TINDALL RANCH | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0043123 | OH | Sus | 42724310 | No | 2016 | JUN | Yes | Force Out | 1208972 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LOS OSITOS-2103 | 182082103 | OTHER | WIRE DOWN @ CGC 412706433621 | 20160616 | 2214 | 1491091 | 886 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 26702 | 36.2318 | -121.474 | at CGC # 412706433621 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0043869 | OH | Sus | 0 | No | 2016 | JUN | Yes | Line to Ground | 1209475 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 5825 | 20160616 | 2302 | 1491071 | 615 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 15532 | 37.0127 | -121.7936 | 1 SP S/S OF FUCO 6651 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0043867 | OH | Sus | 42726576 | No | 2016 | JUN | Yes | Line to Line | 1209473 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2105 | 83252105 | FUSE | 12119 | 20160622 | 1623 | 1494166 | 721 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2884 | 37.0052 | -121.9836 | 6 SP LS 12119 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0045152 | OH | Sus | 31249001 | No | 2016 | JUN | Yes | Line to Line | 1210416 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | OTHER | WIRE DOWN @ MTR#1009787591 | 20160623 | 1527 | 1494780 | 624 | Distribution Circuit | Vegetation | Tree - branch fell on line | 368 | 74560 | 37.0334 | -122.0879 | MTR#1009787591 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0045452 | OH | Sus | 42730803 | No | 2016 | JUN | Yes | Line to Ground | 1210606 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6577 | 20160625 | 1933 | 1495916 | 1125 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 39103 | 37.048 | -121.8081 | 4 LD SIDE OF N12493 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0045801 | OH | Sus | 0 | No | 2016 | JUN | Yes | Line to Ground | 1210872 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 9949 | 20160702 | 1310 | 1500053 | 1015 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 28485 | 37.016 | -121.8207 | STORMENT- 4178 / 831-278-0287: Ryder Rd.- Wat. | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0047580 | OH | Sus | 42735314 | No | 2016 | JUL | Yes | Line to Ground | 1212121 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 8321 | 20160704 | 13 | 1500706 | 724 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3737 | 37.0397 | -121.9767 | 2 SS OF 1008378667 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0047717 | OH | Sus | 42735462 | No | 2016 | JUL | Yes | Line to Ground | 1212264 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 7263 | 20160710 | 2043 | 1507872 | 1357 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 3917 | 37.1534 | -122.1232 | Two Bar Rd.- .9 Miles E/O Hwy 9 At Private Rd. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0048926 | OH | Sus | 31256531 | No | 2016 | JUL | Yes | Force Out | 1213169 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | JUMPER | WIRE DOWN | 20160711 | 2336 | 1508575 | 639 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 36072 | 37.0485 | -121.8086 | 1396 EUREKA CAN RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0049193 | OH | Sus | 42739795 | No | 2016 | JUL | Yes | Line to Ground | 1213358 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6711 | 20160714 | 2151 | 1510300 | 456 | Distribution Circuit | Vegetation | Tree - branch fell on line | 49 | 22344 | 36.998 | -121.8689 | 425 FLUME RD APTOS | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0050063 | OH | Sus | 42741711 | yes | 2016 | JUL | Yes | Line to Ground | 1213972 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2166 | 20160716 | 1040 | 1511113 | 218 | Distribution Circuit | Vegetation | Tree - fell into line | 476 | 103768 | 36.2769 | -121.8264 | 8 SPANS LD SIDE OF R101 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0050371 | OH | Sus | 0 | No | 2016 | JUL | Yes | Line to Ground | 1214193 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 7773 | 20160718 | 2020 | 1512185 | 573 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 16738 | 37.1882 | -122.1579 | 315 STELLAR WAY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0050752 | OH | Sus | 31258023 | No | 2016 | JUL | Yes | Line to Ground | 1214510 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | HATTON-1102 | 182291102 | FUSE | 1295 | 20160725 | 945 | 1515600 | 17754 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 132 | 216 | 36.3795 | -121.8611 | FIRE AREA BEYOND FUCO 1295 & LR2052 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0052248 | OH | Sus | 0 | yes | 2016 | JUL | Yes | Line to Ground | 1215513 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8501 | 20160728 | 1905 | 1518104 | 595 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 11900 | 37.1653 | -122.201 | 16 SPANS LOAD SIDE OF 8501 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0053437 | OH | Sus | 0 | yes | 2016 | JUL | Yes | Line to Ground | 1216288 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 9271 | 20160728 | 1805 | 1518074 | 583 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 2849 | 37.0359 | -121.8594 | 5 SPANS WEST OF LINE AND BUCK AT APTOS VIEW RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0053442 | OH | Sus | 31260223 | yes | 2016 | JUL | Yes | Line to Ground | 1216291 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 6355 | 20160811 | 2135 | 1525130 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 369 | 26375 | 37.0506 | -122.0594 | CRIVELLO- 4176 / 831-682-1912: c/o 6355 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0056779 | OH | Sus | 31262676 | No | 2016 | AUG | Yes | Line to Ground | 1218489 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN @ MTR 1007188920 | 20160814 | 1532 | 1526202 | 517 | Distribution Circuit | Vegetation | Tree - branch fell on line | 535 | 72995 | 37.0688 | -121.9953 | KELLY- 4017 / 831-682-1802: 6465 Scotts Valley Dr. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0057198 | OH | Sus | 31263246 | No | 2016 | AUG | Yes | Line to Ground | 1218813 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5569 | 20160817 | 2035 | 1528113 | 466 | Distribution Circuit | Vegetation | Tree - branch fell on line | 53 | 24698 | 37.0503 | -122.0673 | STORMENT- 4178 / 831-278-0287: 185 Sylvan Way | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0058025 | OH | Sus | 42772035 | No | 2016 | AUG | Yes | Line to Ground | 1219379 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | RECLOSER | 3088 | 20160823 | 816 | 1530685 | 309 | Distribution Circuit | Equipment Failure/Involved | Overhead | 334 | 23913 | 36.5493 | -121.7319 | VALENZUELA- JAIME: 2 SPANS S/O 4191 S/B C/O'S | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0059249 | OH | Sus | 42774824 | No | 2016 | AUG | Yes | Line to Ground | 1220163 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | RECLOSER | 8773 | 20160824 | 1211 | 1531506 | 399 | Distribution Circuit | 3rd Party | Vehicle | 814 | 232770 | 36.4633 | -121.712 | MAIN LINE BETWEEN 67399 & 43741 | Clear-32-90 F | Conductor, Overhead | On Ground | 16-0059702 | OH | Sus | 42775390 | No | 2016 | AUG | Yes | Multi-Fault | 1220463 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | CAMP EVERS-2106 | 83622106 | RECLOSER | 12760 | 20160826 | 2233 | 1532842 | 537 | Distribution Circuit | Vegetation | Tree - fell into line | 535 | 50643 | 37.0676 | -121.9966 | STORMENT- 4178 / 831-278-0287: 1595 Laurel Glen Rd.- Soquel | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0060426 | OH | Sus | 42776817 | No | 2016 | AUG | Yes | Line to Ground | 1220909 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 6101 | 20160829 | 1343 | 1533890 | 696 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 20532 | 37.0321 | -122.0174 | mtr 1007854669 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0060812 | OH | Sus | 42777777 | No | 2016 | AUG | Yes | Line to Ground | 1221274 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 8353 | 20160908 | 1514 | 1538570 | 380 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3420 | 37.0582 | -121.9417 | SS/O 8353 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0063301 | OH | Sus | 42783220 | No | 2016 | SEP | Yes | Line to Ground | 1222877 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | RECLOSER | 2052 | 20160912 | 424 | 1539878 | 959 | Distribution Circuit | Vegetation | Tree - fell into line | 138 | 130604 | 36.3999 | -121.902 | CORI- MARK: 36935 palo colorado rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0063826 | OH | Sus | 0 | No | 2016 | SEP | Yes | Line to Ground | 1223227 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER | WIRE DOWN S/O 9787 | 20160918 | 1433 | 1543564 | 684 | Distribution Circuit | Equipment Failure/Involved | Overhead | 597 | 54983 | 37.1618 | -122.1348 | STORMENT- 4178 / 831-278-0287: 16255 Hwy. 9- B.C. | Clear-Above 90 | Connector or Splice (OH) | Broken, wire on ground | 16-0065437 | OH | Sus | 42793933 | No | 2016 | SEP | Yes | Line to Ground | 1224326 | CSO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | OCB | 2104/2 | 20160922 | 1558 | 1546260 | 628 | Distribution Circuit | Vegetation | Tree - fell into line | 3147 | 351061 | 36.9794 | -121.8671 | BRANDT- 4179 / 831-212-2088: Freedom at Mc Donald Crivello has info | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0066756 | OH | Sus | 31272932 | No | 2016 | SEP | Yes | Line to Ground | 1225275 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9697 | 20160925 | 1919 | 1547456 | 499 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1497 | 37.0995 | -122.1169 | CRIVELLO- 4176 / 831-682-1912: 2 spans from c/os | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0067346 | OH | Sus | 0 | No | 2016 | SEP | Yes | Line to Ground | 1225700 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER | 5028 | 20160926 | 1659 | 1547980 | 481 | Distribution Circuit | Vegetation | Tree - branch fell on line | 635 | 29304 | 37.1284 | -122.1222 | 1ST SPAN L/SIDE OF METER # 1007328170 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 16-0067624 | OH | Sus | 42798479 | yes | 2016 | SEP | Yes | Line to Ground | 1225891 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | RESERVATION ROAD-1101 | 182731101 | FUSE | 24845 | 20160926 | 1820 | 1548060 | 573 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 5730 | 36.5567 | -121.6971 | 4 SPANS L/S OF FUCO 24845 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0067633 | OH | Sus | 42798521 | yes | 2016 | SEP | Yes | Line to Ground | 1225898 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 2061 | 20160927 | 1313 | 1548650 | 777 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 21465 | 37.0709 | -121.9639 | 1 SPAN L/S OF METER # 1008726669 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0067915 | OH | Sus | 0 | yes | 2016 | SEP | Yes | Line to Ground | 1226111 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 6045 | 20161005 | 1252 | 1553509 | 920 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 25485 | 37.097 | -121.9748 | 1/E/O 5901 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0069900 | OH | Sus | 31275365 | No | 2016 | OCT | Yes | Line to Line | 1227597 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER | WIRE DOWN IFO 322 CHARLES HILL RD | 20161006 | 1421 | 1554137 | 739 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 739 | 37.0806 | -121.9747 | WIRE DOWN IFO 322 CHARLES HILL RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0070201 | OH | Sus | 42806347 | No | 2016 | OCT | Yes | Open Circuit | 1227810 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5183 | 20161007 | 329 | 1554376 | 644 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 14244 | 37.108 | -122.1098 | #1 HUCKELBERRY ISLAND | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0070264 | OH | Sus | 42806357 | No | 2016 | OCT | Yes | Multi-Fault | 1227865 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 7301 | 20161015 | 2222 | 1562033 | 726 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 12342 | 37.0329 | -122.0745 | STORMENT- 4178 / 831-278-0287: 726 Redwood Dr.- Felton | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072720 | OH | Sus | 31277784 | yes | 2016 | OCT | Yes | Line to Ground | 1229762 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6083 | 20161015 | 2117 | 1561999 | 813 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 39886 | 37.0587 | -122.0334 | 1165 NELSON RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072693 | OH | Sus | 31277784 | yes | 2016 | OCT | Yes | Line to Ground | 1229732 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5995 | 20161015 | 954 | 1560819 | 949 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 6643 | 37.078 | -122.244 | CAPWELL - 3915 / 831-206-1280: BEYOND C/O 5995 PAST HARD TAP | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072472 | OH | Sus | 31277784 | yes | 2016 | OCT | Yes | Line to Line | 1229521 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SEACLIFF-0401 | 83500401 | FUSE | 7533 | 20161015 | 2008 | 1561901 | 268 | Distribution Circuit | Vegetation | Tree - branch fell on line | 212 | 14278 | 36.9903 | -121.9164 | 1829 CHERYL WAY | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072659 | OH | Sus | 31277784 | yes | 2016 | OCT | Yes | Line to Ground | 1229700 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5435 | 20161016 | 1234 | 1562793 | 457 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3199 | 37.1175 | -122.1214 | 2 SPANS LD SIDE 5435 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072933 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Line | 1229964 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 8257 | 20161016 | 1614 | 1563414 | 608 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 10944 | 37.1529 | -122.1322 | 355 HOOT OWL WAY | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072960 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Line | 1229991 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12992 | 20161016 | 1935 | 1563634 | 665 | Distribution Circuit | Vegetation | Tree - fell into line | 690 | 63290 | 37.1987 | -122.1536 | 1 SP LD SIDE OF FUCO 1191 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0073002 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Line | 1230032 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 5565 | 20161016 | 1602 | 1563225 | 789 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3945 | 37.1632 | -122.1982 | NEAR FUSE 11125 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0073074 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Line | 1230100 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10912 | 20161016 | 1119 | 1562617 | 466 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 13996 | 37.0913 | -122.096 | NEAR FUSE 4745 ON MAIN LINE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072835 | OH | Sus | 31277784 | yes | 2016 | OCT | Yes | Line to Ground | 1229865 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 6601 | 20161016 | 1844 | 1563326 | 1306 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 45710 | 36.9941 | -121.7172 | 184 BELLA VISTA DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0073310 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Force Out | 1230269 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | RECLOSER | 2052 | 20161016 | 304 | 1562188 | 930 | Distribution Circuit | Vegetation | Tree - fell into line | 138 | 116928 | 36.3999 | -121.902 | 23 SPAN LD SIDE OF 2052 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0072753 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Line | 1229793 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 2209 | 20161016 | 1031 | 1562499 | 491 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 982 | 37.0456 | -121.9398 | FIRST SPAN IN FROM 2209 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072887 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1229920 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2109 | 83252109 | FUSE | 6005 | 20161016 | 1341 | 1562939 | 384 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 7296 | 36.9959 | -121.9233 | 5/NE/O 6005 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072905 | OH | Sus | 31277784 | yes | 2016 | OCT | Yes | Line to Line | 1229938 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6653 | 20161016 | 1054 | 1562545 | 1625 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4875 | 37.0165 | -121.7907 | 1 SP LD SIDE OF FUCO | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072883 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Force Out | 1229916 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 1955 | 20161016 | 1448 | 1563079 | 1230 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 11215 | 36.9615 | -121.82 | 362 DUSTY TRAIL RD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072996 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1230026 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 9949 | 20161016 | 1600 | 1563220 | 928 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 28768 | 37.016 | -121.8207 | 4 SP LD SIDE | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0073058 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Line | 1230085 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 3459 | 20161016 | 538 | 1562247 | 1292 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 34067 | 37.0246 | -121.8841 | GONZALES- 4018 / 831-682-1831: MADRONE AND TAN OAK TOOK OUT PRI. AND ARE ACROSS RD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072778 | OH | Sus | 31277784 | yes | 2016 | OCT | Yes | Line to Line | 1229818 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 2323 | 20161016 | 1348 | 1562957 | 270 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 13230 | 36.5822 | -121.9214 | FIRST SPAN FROM C/OUTS 2323 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072907 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1229939 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 2631 | 20161017 | 624 | 1564019 | 454 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 908 | 37.0469 | -121.9839 | LD SIDE OF 2631 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0073178 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1230202 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | OTHER | WIRE DOWN @ MTR 1007589562 | 20161018 | 654 | 1564968 | 317 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 33824 | 37.0992 | -122.0858 | 10200 LOVE CREEK RD | Overcast-Drizzle-32-90 F | Conductor, Overhead | On Ground | 16-0073538 | OH | Sus | 31278258 | No | 2016 | OCT | Yes | Line to Ground | 1230463 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | FUSE | 7611 | 20161018 | 817 | 1565005 | 378 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 15876 | 36.3864 | -121.8708 | MTR# 030H60 | Clear-32-90 F | Conductor, Overhead | On Ground | 16-0073569 | OH | Sus | 42818860 | No | 2016 | OCT | Yes | Multi-Fault | 1230513 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER | WIRE DOWN 1 N/OF 12431 | 20161020 | 1808 | 1566767 | 435 | Distribution Circuit | Vegetation | Tree - fell into line | 295 | 16761 | 37.1398 | -122.1499 | 1/2 N/OF 12431 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0074402 | OH | Sus | 42825022 | No | 2016 | OCT | Yes | Force Out | 1231108 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | OCB | 5000BP | 20161028 | 1158 | 1571893 | 1473 | Distribution Circuit | Vegetation | Tree - fell into line | 177 | 97766 | 37.0953 | -122.1437 | 1038 EMPIRE GRADE RD | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0076392 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Multi-Fault | 1232590 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 11967 | 20161030 | 1022 | 1573057 | 692 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 21452 | 37.0289 | -122.0724 | MTR # 1008738692 & 1830 UPPER SCENIC DR | Overcast-Drizzle-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0076768 | OH | Sus | 0 | No | 2016 | OCT | Yes | Line to Ground | 1232875 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 5166 | 20161030 | 2335 | 1573492 | 913 | Distribution Circuit | Vegetation | Tree - fell into line | 269 | 189569 | 36.9818 | -121.901 | 786 CATHEDRAL | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076870 | OH | Sus | 0 | No | 2016 | OCT | Yes | Line to Ground | 1232972 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8259 | 20161031 | 229 | 1573512 | 617 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 11106 | 37.1593 | -122.1271 | 20/N/O 8259 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076879 | OH | Sus | 0 | No | 2016 | OCT | Yes | Line to Line | 1232983 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | 15 POLES LOAD SIDE OPEN JUMPERS | 20161101 | 716 | 1574337 | 459 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1446 | 37.1197 | -122.0848 | 17 POLES & 19 POLES LOAD SIDE 5151 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0077241 | OH | Sus | 31281609 | No | 2016 | NOV | Yes | None | 1233304 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | OTHER | WIRE DOWN 1 SS OF MTR 1009551630 | 20161101 | 123 | 1574300 | 668 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 6585 | 37.0187 | -121.8268 | 1 SS OF MTR 1009551630 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0077153 | OH | Sus | 31281559 | No | 2016 | NOV | Yes | Line to Line | 1233199 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | GONZALES-1101 | 182131101 | FUSE | 7605 | 20161109 | 22 | 1578544 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 1687 | 36.544 | -121.3958 | 2 SPANS ROM EOL- L/S OF 7605 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0078804 | OH | Sus | 42875250 | No | 2016 | NOV | Yes | Line to Ground | 1234445 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | OTHER | WIRE DOWN @ MTR 1008550934 | 20161109 | 1936 | 1579094 | 559 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 4618 | 36.399 | -121.8818 | MTR 1008550934 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0079084 | OH | Sus | 31283373 | No | 2016 | NOV | Yes | Line to Ground | 1234647 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER | WIRE DOWN | 20161112 | 1859 | 1580306 | 1086 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 9984 | 37.1094 | -122.045 | 2/S/O CGC 315500822581 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0079491 | OH | Sus | 42879161 | No | 2016 | NOV | Yes | Line to Ground | 1234978 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10912 | 20161113 | 1844 | 1580579 | 1557 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 45418 | 37.0913 | -122.096 | WELSH: 1400 HUBBARD GULCH RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0079544 | OH | Sus | 31283709 | No | 2016 | NOV | Yes | Three Phase Fault | 1235039 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10912 | 20161119 | 1637 | 1585273 | 1283 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 43490 | 37.0913 | -122.096 | 10723 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081155 | OH | Sus | 42882737 | yes | 2016 | NOV | Yes | Multi-Fault | 1236172 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 5329 | 20161120 | 741 | 1585536 | 976 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 64416 | 37.0179 | -121.9973 | 304 GRANITE CREEK RD | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081238 | OH | Sus | 42882775 | yes | 2016 | NOV | Yes | Line to Ground | 1236268 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5629 | 20161120 | 730 | 1585522 | 716 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 20100 | 37.1128 | -122.0481 | 8 SPANS LOAD SIDE 5629 & 13095 LOMPICO ROAD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081234 | OH | Sus | 42882769 | yes | 2016 | NOV | Yes | Line to Line | 1236262 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 6295 | 20161120 | 922 | 1585602 | 458 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 7722 | 37.0992 | -122.0867 | STORMENT- 4178 / 831-278-0287: 1125 Roberts Rd.- B.L. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081240 | OH | Sus | 0 | yes | 2016 | NOV | Yes | Line to Ground | 1236270 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 7993 | 20161120 | 912 | 1585590 | 538 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 17644 | 37.0284 | -121.7411 | 515 SUMMIT RD | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081243 | OH | Sus | 42882772 | yes | 2016 | NOV | Yes | Line to Ground | 1236272 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | WIRE 1 W/OF 12840 | 20161124 | 1331 | 1588295 | 766 | Distribution Circuit | Vegetation | Tree - branch fell on line | 135 | 25284 | 37.054 | -121.9555 | 1 SPAN W/O 12840 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0082120 | OH | Sus | 42884285 | No | 2016 | NOV | Yes | Line to Ground | 1236878 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5173 | 20161126 | 2027 | 1589488 | 934 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 57908 | 37.1011 | -122.1017 | 1838 RIVER RD | Rain | Pole-Wood | Broken, wire on ground | 16-0082362 | OH | Sus | 0 | yes | 2016 | NOV | Yes | Line to Ground | 1237118 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 83716 | 20161126 | 404 | 1588895 | 656 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 10526 | 37.0863 | -122.261 | LD SIDE OF 8033 TREE THROUGH LINE | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0082246 | OH | Sus | 42884787 | yes | 2016 | NOV | Yes | Line to Ground | 1237008 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7223 | 20161201 | 1559 | 1592991 | 248 | Distribution Circuit | 3rd Party | Vehicle | 1 | 248 | 37.0418 | -122.047 | 1 LD SIDE OF 7223 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0083485 | OH | Sus | 0 | No | 2016 | DEC | Yes | Three Phase Fault | 1238050 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | JUMPER | WIRE DOWN @ METER # 1007591875 | 20161202 | 709 | 1593377 | 501 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 13851 | 37.0574 | -121.8219 | at METER # 1007591875 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0083586 | OH | Sus | 0 | No | 2016 | DEC | Yes | Line to Ground | 1238169 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 11305 | 20161206 | 346 | 1595176 | 444 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 5772 | 37.0307 | -121.7864 | at 200 REDWOOD RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084027 | OH | Sus | 31287602 | No | 2016 | DEC | Yes | Line to Ground | 1238625 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 6043 | 20161208 | 2006 | 1597315 | 856 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 36710 | 37.0696 | -121.995 | 1 SOUTH OF AND 3 EAST OF MTR#1010194669 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084691 | OH | Sus | 31288450 | yes | 2016 | DEC | Yes | Line to Ground | 1239206 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6983 | 20161208 | 2039 | 1597370 | 1011 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 9099 | 37.0391 | -121.8072 | METER # 1008452540 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084707 | OH | Sus | 42893821 | yes | 2016 | DEC | Yes | Line to Ground | 1239227 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8015 | 20161209 | 1557 | 1597939 | 888 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 69433 | 37.1536 | -122.1616 | 216 DOUBLE BOGIE DR 4 SPANS LD SIDE OF 8015 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084831 | OH | Sus | 31288614 | No | 2016 | DEC | Yes | Multi-Fault | 1239357 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2105 | 83252105 | FUSE | 12119 | 20161209 | 2223 | 1598126 | 383 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1532 | 37.0052 | -121.9836 | 4250 PAUL SWEET RD | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084859 | OH | Sus | 42894387 | No | 2016 | DEC | Yes | Line to Ground | 1239391 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 7773 | 20161210 | 1535 | 1599122 | 880 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 24600 | 37.1882 | -122.1579 | 400 STELLAR WAY | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 16-0085010 | OH | Sus | 42897944 | yes | 2016 | DEC | Yes | Multi-Fault | 1239558 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | JOLON-1102 | 182981102 | RECLOSER | 7002 | 20161210 | 1348 | 1598983 | 477 | Distribution Circuit | Equipment Failure/Involved | Overhead | 138 | 39366 | 35.9664 | -121.1153 | BET 9199 AND MAIN LINE & BUCK WIRE DOWN | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0084975 | OH | Sus | 31288727 | yes | 2016 | DEC | Yes | Line to Ground | 1239520 | CAW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | JUMPER | OJ'S 5 SPANS FROM EOL | 20161210 | 1500 | 1599548 | 1265 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2530 | 37.0227 | -122.1304 | 3 SPANS S/S OF 3002 SMITH GRADE RD/EOL | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085053 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1239607 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | JUMPER | WIRE DWN | 20161210 | 642 | 1598504 | 508 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 7993 | 37.0601 | -121.822 | 3 SP LD SIDE OF MTR#1007591875 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084935 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Open Circuit | 1239483 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 8645 | 20161210 | 1041 | 1598549 | 912 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 46288 | 37.0115 | -121.885 | 1 SP LD SIDE OF FUCO 8645 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084953 | OH | Sus | 42897910 | yes | 2016 | DEC | Yes | Line to Line | 1239499 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE | 655 | 20161210 | 1823 | 1599385 | 1942 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 9688 | 36.8785 | -121.6417 | MTR#1006212759 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0085016 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1239566 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | OTHER | LINE DOWN SS OF 7689 | 20161213 | 1745 | 1601310 | 707 | Distribution Circuit | Equipment Failure/Involved | Overhead | 108 | 48292 | 36.9856 | -121.8127 | MAINLINE SS OF 7689 | Overcast-32-90 F | Conductor, Overhead | On Ground | 16-0085472 | OH | Sus | 42899422 | No | 2016 | DEC | Yes | Line to Ground | 1240097 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5501 | 20161215 | 1940 | 1603637 | 851 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 28444 | 37.1432 | -122.1317 | at 12499 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085880 | OH | Sus | 31289565 | yes | 2016 | DEC | Yes | Line to Ground | 1240545 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5599 | 20161215 | 1742 | 1603542 | 1267 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 25340 | 37.0795 | -122.0513 | 255 Zayante SCHOOL RD | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085851 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1240518 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | WIRE DOWN 1 NW OF 5233 | 20161215 | 1913 | 1603713 | 591 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 10962 | 37.0588 | -122.0764 | 1 NW OF 5233 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085854 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Open Circuit | 1240521 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9229 | 20161215 | 2046 | 1603744 | 929 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 5162 | 37.0694 | -122.0577 | CORNER OF WILLOW & NEWTON | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085891 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Line | 1240556 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5151 | 20161215 | 2158 | 1603819 | 1083 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6498 | 37.1109 | -122.0898 | 6 SPANS LOAD SIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085925 | OH | Sus | 0 | yes | 2016 | DEC | Yes | None | 1240591 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 6033 | 20161215 | 940 | 1602544 | 453 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 36240 | 37.081 | -122.0046 | at METER # 1007346232 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085704 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1240377 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 40423 | 20161215 | 2321 | 1603943 | 354 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 10266 | 36.5538 | -121.899 | 2 spans ld side 40423 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085928 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Line | 1240594 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6639 | 20161215 | 1643 | 1603233 | 1636 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 46700 | 37.0077 | -121.8085 | KELLY- 4017 / 831-682-1802: Up mountain some where. | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085822 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1240490 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 5825 | 20161215 | 1918 | 1603571 | 508 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 37592 | 37.0127 | -121.7936 | 733 BROWNS VALLEY RD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085843 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Line | 1240510 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | CAMP EVERS-2105 | 83622105 | FUSE | 5233 | 20161216 | 1128 | 1604562 | 197 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 4728 | 37.0577 | -122.0762 | 1 SPAN L/SIDE OF 5233 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0086042 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Force Out | 1240763 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | FUSE | 8389 | 20161216 | 1243 | 1604553 | 345 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 345 | 36.2709 | -121.7972 | 2 SPANS LOAD SIDE 8389 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0086055 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Line | 1240778 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 11305 | 20161216 | 804 | 1604342 | 1295 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 16835 | 37.0307 | -121.7864 | STORMENT- 4178 / 831-278-0287: 1500 Redwood Rd.- Wat. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0086116 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1240849 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | CAMP EVERS-2106 | 83622106 | RECLOSER | 12760 | 20161217 | 1304 | 1605603 | 461 | Distribution Circuit | Equipment Failure/Involved | Overhead | 628 | 68167 | 37.0676 | -121.9966 | connection at hard tap going tw 4690 rodeo gulch drive | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0086167 | OH | Sus | 42902123 | No | 2016 | DEC | Yes | Line to Ground | 1240933 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5173 | 20161218 | 448 | 1605939 | 517 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 32054 | 37.1011 | -122.1017 | at METER # 1007592191 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0086214 | OH | Sus | 42902144 | No | 2016 | DEC | Yes | Line to Ground | 1240994 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | JUMPER | WIRE DOWN 1 SP L/S OF METER # 1008517303 | 20161220 | 756 | 1607481 | 574 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1148 | 37.0336 | -121.7929 | METER # 1008517303 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0086511 | OH | Sus | 0 | No | 2016 | DEC | Yes | Line to Ground | 1241444 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 5335 | 20161224 | 853 | 1610181 | 379 | Distribution Circuit | Vegetation | Tree - bark fell into line | 74 | 28046 | 37.0281 | -121.9871 | 1SPAN N/O 150 HAPPYVALLEY RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0086895 | OH | Sus | 42905520 | No | 2016 | DEC | Yes | Line to Ground | 1242083 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 6217 | 20161224 | 958 | 1610229 | 1277 | Distribution Circuit | Vegetation | Tree - fell into line | 275 | 296984 | 37.078 | -122.0793 | at MTR#1007589527 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0086902 | OH | Sus | 0 | No | 2016 | DEC | Yes | Line to Line | 1242089 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 11865 | 20161226 | 356 | 1610896 | 572 | Distribution Circuit | Vegetation | Tree - branch fell on line | 73 | 24897 | 37.001 | -121.7398 | SPAN SOURCE SIDE OF FUSE 2029 | Strong Winds-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0087021 | OH | Sus | 42905585 | No | 2016 | DEC | Yes | Line to Line | 1242214 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12992 | 20170104 | 600 | 1617758 | 782 | Distribution Circuit | Vegetation | Tree - fell into line | 597 | 123467 | 37.1987 | -122.1536 | 2 SPANS LD SIDE OF 9133 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003429 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243616 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 6093 | 20170104 | 46 | 1617410 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 9623 | 37.0267 | -122.0251 | MTR # 100785458 | Overcast-Fog-Heavy Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0003384 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243566 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20170104 | 354 | 1617765 | 1176 | Distribution Circuit | Vegetation | Tree - fell into line | 185 | 92610 | 37.0669 | -122.0336 | 7 P LD SIDE OF 6087 1ST SPAN ON HARD TAP | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003526 | OH | Sus | 31292865 | yes | 2017 | JAN | Yes | Line to Ground | 1243691 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 8315 | 20170104 | 409 | 1617685 | 2161 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 51864 | 37.0997 | -122.118 | 2 SP LD SIDE OF 8315 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003420 | OH | Sus | 31292865 | yes | 2017 | JAN | Yes | Line to Ground | 1243609 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 5901 | 20170104 | 33 | 1617403 | 683 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 10155 | 37.0945 | -121.9715 | 5 SPANS LOAD SIDE FUCO 5901 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003486 | OH | Sus | 31292865 | yes | 2017 | JAN | Yes | Line to Ground | 1243654 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 565 | 20170104 | 17 | 1617327 | 1450 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 19686 | 37.0424 | -122.1064 | MTR 1008747882 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003553 | OH | Sus | 31292865 | yes | 2017 | JAN | Yes | Line to Ground | 1243706 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 2321 | 20170104 | 333 | 1617584 | 1083 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 27308 | 37.005 | -121.8623 | CGC 316041218747 | Overcast-Fog-Heavy Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0003481 | OH | Sus | 31292865 | yes | 2017 | JAN | Yes | Line to Ground | 1243652 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 9423 | 20170107 | 1346 | -1621265 | 271 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 5088 | 37.077 | -122.0861 | PARK & FLINTLOCK | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004727 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244534 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 9787 | 20170107 | 1023 | 1621430 | 762 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3810 | 37.1622 | -122.1349 | CAPWELL - 3915 / 831-206-1280: BEHIND 16255 HWY 9 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004676 | OH | Sus | 31294181 | yes | 2017 | JAN | Yes | Line to Line | 1244494 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8501 | 20170107 | 1531 | 1621937 | 197 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 3940 | 37.1653 | -122.201 | BRANDT- 4179 / 831-212-2088: 21600 Big Basin Hwy at Camp Hammer tree fell thru line | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004731 | OH | Sus | 31294181 | yes | 2017 | JAN | Yes | Line to Ground | 1244540 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12992 | 20170107 | 1623 | 1622021 | 2161 | Distribution Circuit | Vegetation | Tree - fell into line | 685 | 167379 | 37.1987 | -122.1536 | 3 SPANS S/O 9789 | Strong Winds-Overcast-Fog-Rain-32-90 F | Transformer (OH) | Broken, wire on ground | 17-0004750 | OH | Sus | 31294181 | yes | 2017 | JAN | Yes | Line to Ground | 1244556 | TXO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | FUSE | 5183 | 20170107 | 1838 | 1622161 | 35 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 1120 | 37.108 | -122.1098 | HUCKLEBERRY ISLAND | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004784 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1244584 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | FUSE | 40419 | 20170107 | 734 | 1620903 | 376 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 21056 | 36.4908 | -121.9357 | SS 8245 FUCO | Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004557 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244385 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 5076 | 20170107 | 2218 | 1622283 | 1167 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 31186 | 37.0317 | -122.1882 | MTR: 5000038041 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0004852 | OH | Sus | 31294181 | yes | 2017 | JAN | Yes | Line to Ground | 1244653 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | OTHER | WIRE DOWN 7 SPANS LD SIDE OF 5819 | 20170107 | 2252 | 1622331 | 3746 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 212598 | 37.0446 | -121.8077 | WIRE DOWN 7 SPANS LD SIDE OF 5819 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 17-0004887 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1244686 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 8645 | 20170107 | 820 | 1620977 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 26705 | 37.0115 | -121.885 | 3 LD SIDE OF 8645 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004584 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1244413 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | RECLOSER | 9490 | 20170107 | 857 | 1621054 | 1098 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 52645 | 36.566 | -121.9352 | 1/P/NE OF 2799 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004607 | OH | Sus | 31293495 | yes | 2017 | JAN | Yes | Line to Line | 1244434 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | FUSE | 7511 | 20170112 | 1400 | 1641670 | 102 | Distribution Circuit | Environmental/External | Flood/Erosion | 1 | 102 | 36.2354 | -121.7674 | CGC 411850234063 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0008470 | OH | Sus | 31293495 | yes | 2017 | JAN | Yes | Three Phase Fault | 1247842 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5995 | 20170112 | 409 | 1640940 | 846 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5922 | 37.078 | -122.244 | RANGEL- RUFINO: 466 SWANTON RD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008304 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1247734 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 47077 | 20170112 | 759 | 1641086 | 634 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 634 | 37.0744 | -122.2369 | 380 SWANTON RD- DAVENPORT | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008305 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247735 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | JUMPER | OJ 123 PAX PLACE | 20170112 | 1028 | 1641313 | 207 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 207 | 37.0393 | -121.8497 | SAME | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008384 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1247783 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | JUMPER | 3 SPANS LOAD MTR 1007185768 SIDEWIRE DOWN | 20170112 | 1225 | 1641136 | 1645 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1645 | 37.045 | -121.8073 | LOAD SIDE TAP UNKNOWN IF THERE WAS FAULT | Overcast-32-90 F | Conductor, Overhead | On Ground | 17-0008431 | OH | Sus | 0 | yes | 2017 | JAN | Yes | None | 1247816 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | SWITCH | 2327 | 20170113 | 1127 | 1642466 | 136 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 1224 | 37.014 | -121.7173 | LOAD SIDE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008737 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1248049 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | OTHER | 12155 | 20170113 | 1430 | 1642706 | 80 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 240 | 37.004 | -121.7038 | 6 SPANS LOAD SIDE OF 12155 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008810 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1248089 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 6407 | 20170113 | 1207 | 1642541 | 395 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 9480 | 36.5917 | -121.9125 | 2 SPANS LOAD SIDE 6407 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008811 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1248090 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | OTHER | WIRE DOWN @ FUCO 4235 | 20170116 | 34 | 1644277 | 950 | Distribution Circuit | Vegetation | Tree - fell into line | 430 | 200166 | 36.9921 | -121.8417 | at FUCO 4235 | Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0009347 | OH | Sus | 31296563 | No | 2017 | JAN | Yes | Open Circuit | 1248611 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 9005 | 20170127 | 345 | 1668359 | 540 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 11880 | 37.0318 | -122.1371 | RANGEL- RUFINO: WARREN DR X ST SMITH GRADE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0015555 | OH | Sus | 42933889 | No | 2017 | JAN | Yes | Line to Line | 1254064 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5487 | 20170203 | 714 | 1673509 | 415 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 23240 | 37.1371 | -122.1006 | 5 SPANS LD SIDE 5487 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017094 | OH | Sus | 31303560 | yes | 2017 | FEB | Yes | Line to Ground | 1255185 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5151 | 20170203 | 745 | 1673607 | 710 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4260 | 37.1109 | -122.0898 | CAPWELL - 3915 / 831-206-1280: 3 SPANS LOAD SIDE OF C/O 5151 ON LOVE CREEK RD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017192 | OH | Sus | 42938053 | yes | 2017 | FEB | Yes | Line to Ground | 1255249 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 12173 | 20170203 | 1829 | 1674429 | 687 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 687 | 37.1135 | -122.0927 | 6 SPANS L/S OF 12181 / EOL | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017391 | OH | Sus | 31303860 | yes | 2017 | FEB | Yes | Line to Ground | 1255351 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8355 | 20170203 | 637 | 1673570 | 487 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 46752 | 37.0459 | -122.1101 | BOYNTON- 3459 / 831-331-6620: 6009 EMPIRE GRADE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017099 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1255189 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 6605 | 20170203 | 1946 | 1674403 | 1011 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 7097 | 37.013 | -121.7519 | 5 SPANS L/S OF 6605 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017388 | OH | Sus | 42938973 | yes | 2017 | FEB | Yes | Line to Ground | 1255348 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 11305 | 20170203 | 755 | 1673611 | 430 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 5590 | 37.0307 | -121.7864 | 4 SP LD SIDE 11305 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017161 | OH | Sus | 42937887 | yes | 2017 | FEB | Yes | Line to Ground | 1255234 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | JUMPER | OJ MTR 1007591875 | 20170203 | 822 | 1674201 | 868 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 9548 | 37.0577 | -121.8218 | MTR 1007591875 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017322 | OH | Sus | 42938950 | yes | 2017 | FEB | Yes | Open Circuit | 1255293 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | RECLOSER | 2064 | 20170203 | 900 | 1673698 | 416 | Distribution Circuit | Vegetation | Tree - fell into line | 601 | 70542 | 36.5823 | -121.9204 | 4 SP LD SIDE OF 2064 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017137 | OH | Sus | 31303632 | yes | 2017 | FEB | Yes | Line to Ground | 1255215 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER | 9104 | 20170203 | 1945 | 1674406 | 288 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1320 | 94629 | 36.5869 | -121.9142 | AT MTR 1008757565 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0017365 | OH | Sus | 31303819 | yes | 2017 | FEB | Yes | Line to Ground | 1255325 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 5166 | 20170204 | 1109 | 1674780 | 955 | Distribution Circuit | Vegetation | Tree - fell into line | 269 | 216247 | 36.9818 | -121.901 | 1/2 MILE NORTH OF 5166 | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 17-0017451 | OH | Sus | 42939015 | No | 2017 | FEB | Yes | Line to Line | 1255411 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | RECLOSER | 5178 | 20170206 | 1915 | 1677048 | 424 | Distribution Circuit | Vegetation | Tree - fell into line | 268 | 113632 | 37.0326 | -121.9462 | ON MAIN LINE BET 2205 AND 2209 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | On Ground | 17-0017926 | OH | Sus | 31304284 | yes | 2017 | FEB | Yes | Multi-Fault | 1255778 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8985 | 20170206 | 2025 | 1677093 | 1235 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 27170 | 37.0291 | -122.1406 | 4 SPANS LD SIDE OF 8985 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 17-0018711 | OH | Sus | 42939797 | yes | 2017 | FEB | Yes | Multi-Fault | 1256463 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 3017 | 20170208 | 30 | 1681229 | 1047 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2094 | 37.1424 | -122.1538 | 6 LD SIDE OF 3017 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018828 | OH | Sus | 31304215 | yes | 2017 | FEB | Yes | Force Out | 1256573 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 12525 | 20170208 | 1754 | 1682435 | 334 | Distribution Circuit | Environmental/External | Flood/Erosion | 64 | 22144 | 37.094 | -122.0241 | 4 SPANS FROM 835 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019167 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1256779 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN 1 SP LD SIDE OF 8241 | 20170208 | 818 | 1681519 | 9048 | Distribution Circuit | Environmental/External | Flood/Erosion | 13 | 109536 | 37.1179 | -121.9645 | 1 SPAN LD SIDE OF 8241 POLE CAUGHT IN MUD SLIDE | Overcast-Drizzle-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018941 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Open Circuit | 1256649 | PW | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2109 | 83252109 | FUSE | 11573 | 20170208 | 1106 | 1681785 | 426 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 8520 | 37.0113 | -121.9253 | 5075 PORTER GULCH RD | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019123 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Force Out | 1256737 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 12122 | 20170208 | 528 | 1681318 | 787 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 55877 | 37.0664 | -122.2286 | 10 SPANS LD SIDE OF 12122 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | On Ground | 17-0018851 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256598 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | JUMPER | WIRE DOWN @ MTR#5000025090 | 20170208 | 652 | 1682257 | 6071 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 12242 | 37.1045 | -121.9629 | WIRE DOWN AT MTR 5000025090 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019109 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256723 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | OTHER | WIRE DOWN @ 2141 | 20170208 | 1013 | 1681807 | 3224 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 17929 | 37.0284 | -121.8627 | ON MAINLINE at 2141 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018981 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256663 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 9949 | 20170208 | 1255 | 1681939 | 416 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 12896 | 37.016 | -121.8207 | 5 SP LD SIDE OF 9949 ON RIDER RD at BUZZARD LAGOON | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019023 | OH | Sus | 31304215 | yes | 2017 | FEB | Yes | Line to Line | 1256684 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 12673 | 20170208 | 1321 | 1681993 | 1594 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 58978 | 37.0295 | -121.844 | 1 LD SIDE OF 12673 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019117 | OH | Sus | 31304215 | yes | 2017 | FEB | Yes | Three Phase Fault | 1256731 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER | WIRE DOWN @ 9759 | 20170210 | 528 | 1684562 | 532 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 12904 | 37.1661 | -122.1987 | 9759 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019837 | OH | Sus | 42939797 | yes | 2017 | FEB | Yes | Open Circuit | 1257279 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 12525 | 20170210 | 502 | 1684564 | 298 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 19072 | 37.094 | -122.0241 | 2/W/O 835 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019827 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1257273 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1112 | 182371112 | FUSE | 431 | 20170210 | 530 | 1684476 | 654 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6540 | 36.5115 | -121.7695 | AT MTR 1008367830 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019764 | OH | Sus | 42939726 | yes | 2017 | FEB | Yes | Line to Ground | 1257235 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | SWITCH | 10175 | 20170210 | 1220 | 1685068 | 302 | Distribution Circuit | Vegetation | Tree - bark fell into line | 671 | 40416 | 37.044 | -122.1539 | KELLY- 4017 / 831-682-1802: Tree down. PG&E crew onsite. | Overcast-32-90 F | Conductor, Overhead | On Ground | 17-0019862 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1257338 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6851 | 20170210 | 809 | 1684877 | 1880 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 31960 | 37.042 | -121.8165 | GONZALES- 2810 / 831-682-1831: TAN OAK TOOK OUT PRI. NEUTRAL AT THIS ADDRESS | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019909 | OH | Sus | 31304125 | yes | 2017 | FEB | Yes | Line to Ground | 1257323 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 2687 | 20170210 | 1352 | 1685246 | 719 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 3109 | 37.0224 | -121.8275 | WALKER- NICK - 1906: DOWN STREAM FROM SSD 2687. | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019995 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1257372 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2105 | 83692105 | RECLOSER | 71630 | 20170210 | 1611 | 1685473 | 1323 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 38417 | 36.976 | -121.8947 | STORMENT- 4178 / 831-278-0287: 175 Valencia Rd.- Aptos | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0020023 | OH | Sus | 42939797 | yes | 2017 | FEB | Yes | Multi-Fault | 1257388 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 5020 | 20170211 | 1139 | 1685973 | 1484 | Distribution Circuit | Vegetation | Tree - fell into line | 1009 | 148397 | 37.1024 | -121.9848 | 24650 GLENWOOD CUTOFF- LG | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0020315 | OH | Sus | 0 | No | 2017 | FEB | Yes | Multi-Fault | 1257696 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2667 | 20170211 | 1752 | 1686362 | 1210 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 7175 | 37.0261 | -121.775 | 1253 HAZEL DELL RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0020405 | OH | Sus | 0 | No | 2017 | FEB | Yes | Line to Ground | 1257780 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6639 | 20170211 | 1355 | 1686181 | 7237 | Distribution Circuit | Environmental/External | Flood/Erosion | 35 | 52963 | 37.0077 | -121.8085 | KELLY- 4017 / 831-682-1802: at D.E. pole wire on ground. | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0020374 | OH | Sus | 0 | No | 2017 | FEB | Yes | Line to Ground | 1257748 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 5166 | 20170211 | 443 | 1685797 | 629 | Distribution Circuit | Vegetation | Tree - fell into line | 262 | 127607 | 36.9818 | -121.901 | 830 CATHEDRAL | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0020262 | OH | Sus | 31304215 | No | 2017 | FEB | Yes | Line to Ground | 1257629 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 1655 | 20170216 | 1634 | 1690675 | 595 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 5950 | 37.1027 | -122.0483 | 1 SPAN LOAD SIDE1655 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021760 | OH | Sus | 42950232 | yes | 2017 | FEB | Yes | Multi-Fault | 1258874 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER | 5185 | 20170219 | 540 | 1701041 | 1892 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 39732 | 37.1075 | -122.1095 | 2 SPANS L/S OF 5185 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023346 | OH | Sus | 31306188 | yes | 2017 | FEB | Yes | Force Out | 1260334 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | JUMPER | WIRE DOWN BEFORE 3 OT BANK | 20170219 | 221 | 1701002 | 2231 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 9860 | 36.4333 | -121.6099 | LOAD SIDE | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023306 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Force Out | 1260309 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | RESERVATION ROAD-1101 | 182731101 | FUSE | 24831 | 20170219 | 1154 | 1701382 | 156 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 624 | 36.5711 | -121.7097 | 1 SPAN L/S OF 24831 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023414 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260399 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 1391 | 20170219 | 1106 | 1701318 | 1674 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6696 | 36.5761 | -121.8997 | at DEAD END POLE at EOL | Heavy Rain-Strong Winds-Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023416 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260402 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 12383 | 20170223 | 854 | 1711707 | 1575 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 21410 | 37.1649 | -122.1934 | MTR 152069 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025984 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262740 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | OJ FEEDING MTR1010000056 | 20170223 | 1125 | 1711750 | 127 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1016 | 37.1023 | -122.054 | 3 SPANS LD SIDE OF MTROJ FEEDING MTR1010000056 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0025981 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262738 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 11929 | 20170223 | 1639 | 1712349 | 1081 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 103910 | 37.0999 | -122.0343 | 7 SPAN LOAD SIDE 11929 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0026082 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1262804 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | WIRE DOWN 2 SS/OF 10445 | 20170223 | 1811 | 1712407 | 979 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1958 | 37.1066 | -122.0436 | WIRE DOWN 2 SS/OF 10445 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0026100 | OH | Sus | 42949498 | yes | 2017 | FEB | Yes | Line to Ground | 1262819 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1102 | 182941102 | FUSE | 6191 | 20170223 | 1043 | 1711892 | 183 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 732 | 36.3755 | -121.8966 | LD SIDE OF 6191 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0025952 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262728 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | RESERVATION ROAD-1101 | 182731101 | OTHER | WIRE DWN 1 S/OF 24857 | 20170223 | 1340 | 1712101 | 170 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 8595 | 36.5504 | -121.675 | WIRE DWN 1 S/OF 24857 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0026021 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1262762 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | FUSE | 8833 | 20170224 | 1923 | 1713496 | 1153 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1153 | 36.3825 | -121.8637 | FUCO WERE OPEN ON DEAD LINE LOAD SIDE IS TROUBLE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0026562 | OH | Sus | 0 | yes | 2017 | FEB | Yes | None | 1263224 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 4295 | 20170225 | 1610 | 1714013 | 1282 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 32050 | 37.033 | -122.0109 | 1 SPAN SOURCE SIDE OF 450 REDWOOD DR | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0026748 | OH | Sus | 0 | No | 2017 | FEB | Yes | Line to Line | 1263441 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 11929 | 20170227 | 409 | 1714764 | 887 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 86926 | 37.0999 | -122.0343 | 5 SPANS LOAD SIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0026940 | OH | Sus | 42954073 | No | 2017 | FEB | Yes | Multi-Fault | 1263640 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 3549 | 20170227 | 1416 | 1715315 | 568 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 880 | 37.0662 | -122.0573 | CGC 315486021105 | Clear-32-90 F | Insulator | Broken, wire on object | 17-0027158 | OH | Sus | 31308035 | No | 2017 | FEB | Yes | Line to Ground | 1263786 | INS | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | OCB | 2101/2 | 20170304 | 33 | 1719029 | 1329 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 60898 | 37.0953 | -122.1437 | 11855 ALBA RD | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0028273 | OH | Sus | 0 | No | 2017 | MAR | Yes | Line to Ground | 1264631 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 8095 | 20170304 | 1311 | 1719302 | 1031 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 17527 | 37.0022 | -121.9417 | 10 PL LD SIDE OF 8095 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 17-0028328 | OH | Sus | 0 | No | 2017 | MAR | Yes | Line to Ground | 1264685 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 12647 | 20170305 | 629 | 1719733 | 946 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2838 | 37.0527 | -121.9981 | 1 SS/OF 9281 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0028539 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Ground | 1264901 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10786 | 20170305 | 443 | 1719678 | 1057 | Distribution Circuit | Vegetation | Tree - branch fell on line | 96 | 34362 | 37.0926 | -122.097 | 12025 ALBA RD | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0028412 | OH | Sus | 31309263 | yes | 2017 | MAR | Yes | Line to Ground | 1264766 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10912 | 20170305 | 606 | 1719697 | 1861 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 59706 | 37.0913 | -122.096 | BOYNTON- 3459 / 831-331-6620: HUBBARD GULCH RD 2 SPANS LOAD SIDE C/O 10723 | Partly Cloudy-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0028417 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Three Phase Fault | 1264771 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 8353 | 20170305 | 1501 | 1720274 | 1899 | Distribution Circuit | Environmental/External | Flood/Erosion | 9 | 6740 | 37.0582 | -121.9417 | 1/N/O MTR 1008375091 & 1 S/OF 5991 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0028569 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Ground | 1264930 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9125 | 20170306 | 1451 | 1721211 | 644 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 27048 | 37.1005 | -122.086 | 1 PL LD SIDE OF 9125 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0028871 | OH | Sus | 42959987 | yes | 2017 | MAR | Yes | Line to Ground | 1265140 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 8245 | 20170308 | 1016 | 1722440 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 4108 | 36.4938 | -121.9342 | 8 SPANS LD SIDE OF 8245 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0029374 | OH | Sus | 0 | No | 2017 | MAR | Yes | Line to Line | 1265514 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | HATTON-1101 | 182291101 | FUSE | 9302 | 20170310 | 2352 | 1724429 | 804 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 77585 | 36.4377 | -121.7935 | 5 SPANS SS OF 9101 TREE IN LINE WIRE DOWN | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0030094 | OH | Sus | 0 | No | 2017 | MAR | Yes | Line to Ground | 1266011 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE | 6875 | 20170311 | 37 | 1724485 | 810 | Distribution Circuit | Equipment Failure/Involved | Overhead | 103 | 37710 | 36.8864 | -121.6326 | at MTR#1008746676 | Partly Cloudy-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 17-0030095 | OH | Sus | 0 | No | 2017 | MAR | Yes | Three Phase Fault | 1266012 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10912 | 20170315 | 706 | 1727414 | 7620 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 62081 | 37.0913 | -122.096 | CAPWELL - 3915 / 831-206-1280: END OF HUBBARD GULCH AT MTR 1008865825 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0030847 | OH | Sus | 0 | No | 2017 | MAR | Yes | Line to Line | 1266624 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 6121 | 20170315 | 115 | 1727351 | 776 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 84584 | 36.9836 | -121.8848 | 750 VALENCIA RD | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0030835 | OH | Sus | 42969691 | No | 2017 | MAR | Yes | Line to Line | 1266614 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN NE/O 7623 MAINLINE | 20170320 | 1952 | s1267604 | 569 | Distribution Circuit | Vegetation | Tree - branch fell on line | 576 | 67983 | 37.1263 | -121.9836 | 24375 GLENWOOD HWY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0032114 | OH | Sus | 42973863 | yes | 2017 | MAR | Yes | Open Circuit | 1267604 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8985 | 20170320 | 55 | 1731741 | 2229 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 48387 | 37.0291 | -122.1406 | 7 SPANS LOAD SIDE 209531 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0032244 | OH | Sus | 42973967 | yes | 2017 | MAR | Yes | Open Circuit | 1267733 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | PRUNEDALE-1110 | 182961110 | JUMPER | OJ'S @ METER # 1008376455 | 20170320 | 1633 | 1731077 | 782 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 12850 | 36.8274 | -121.6987 | at METER # 1008376455 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 17-0032088 | OH | Sus | 42973808 | yes | 2017 | MAR | Yes | Line to Ground | 1267582 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE | 6523 | 20170320 | 1608 | 1731005 | 1277 | Distribution Circuit | Vegetation | Tree - bark fell into line | 163 | 56996 | 36.8749 | -121.6417 | at 2063 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0032099 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Line | 1267589 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 6185 | 20170320 | 2209 | 1731440 | 756 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2283 | 36.5688 | -121.9289 | 5 LD SIDE OF 6185 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0032158 | OH | Sus | 42973868 | yes | 2017 | MAR | Yes | Line to Ground | 1267653 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8503 | 20170321 | 1015 | 1731904 | 812 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1624 | 37.1711 | -122.2183 | CRIVELLO- 4176 / 831-682-1912: 2 spans from end off tap | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0032333 | OH | Sus | 42973967 | yes | 2017 | MAR | Yes | Line to Ground | 1267760 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5629 | 20170321 | 552 | 1731543 | 479 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 4286 | 37.1128 | -122.0481 | AT MTR 1009872852 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0032232 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Ground | 1267713 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2105 | 83252105 | FUSE | 2457 | 20170324 | 1311 | 1734720 | 962 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 9950 | 37.0062 | -121.9912 | BRANDT- 4179 / 831-212-2088: 4552 Paul Sweet Rd tree fell 1st span LS C/O 3759- broke pole top at | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0033522 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Ground | 1268473 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6085 | 20170327 | 1739 | 1736965 | 547 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 5470 | 37.0639 | -122.0349 | CAPWELL - 3915 / 831-206-1280: BEGINNING OF RYDER ROAD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0034237 | OH | Sus | 42978233 | yes | 2017 | MAR | Yes | Line to Ground | 1269068 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 6645 | 20170329 | 211 | 1738064 | 1425 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 17100 | 37.0119 | -121.7939 | 261 AVACADO LN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0034614 | OH | Sus | 42978615 | No | 2017 | MAR | Yes | Line to Ground | 1269393 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2104 | 83252104 | FUSE | 5021 | 20170330 | 1225 | 1739182 | 454 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 18160 | 37.0104 | -121.9644 | ALVAREZ- 3463 / 831-535-9251: 530 Amigo Rd- Soquel | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0035082 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Ground | 1269780 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 7159 | 20170330 | 1852 | 1740201 | 518 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 7936 | 36.5781 | -121.9066 | 1391 | Clear-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0035285 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Multi-Fault | 1269915 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9779 | 20170331 | 1432 | 1741408 | 1123 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6738 | 37.1545 | -122.0827 | 7 SPANS LD SIDE OF FUCO 9779 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0035673 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Multi-Fault | 1270221 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7595 | 20170402 | 1655 | 1742532 | 548 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 3273 | 37.1021 | -121.9819 | WIRE DOWN 2/S OF 7595 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0035882 | OH | Sus | 31316304 | No | 2017 | APR | Yes | Open Circuit | 1270446 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 7509 | 20170408 | 22 | 1752224 | 990 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 23760 | 37.0937 | -122.0507 | 10400 WRITE BLVD | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0038203 | OH | Sus | 31316813 | yes | 2017 | APR | Yes | Line to Ground | 1272260 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 12173 | 20170408 | 705 | 1752386 | 610 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 610 | 37.1135 | -122.0927 | last span | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038278 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1272336 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 2061 | 20170408 | 1159 | 1752694 | 484 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 14850 | 37.0709 | -121.9639 | 6 SS OF MTR 1009535497 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038297 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1272354 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 2695 | 20170409 | 1754 | 1753702 | 522 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 8874 | 36.5886 | -121.9081 | GALLEGOS-HENRY: 24 Wellings Pl | Clear-32-90 F | Capacitor | Broken, wire on ground | 17-0038482 | OH | Sus | 0 | No | 2017 | APR | Yes | Line to Ground | 1272535 | ECA | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7605 | 20170412 | 2256 | 1756543 | 1054 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 43366 | 37.0863 | -122.0057 | 12523 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0039744 | OH | Sus | 0 | No | 2017 | APR | Yes | Line to Ground | 1273481 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | SWITCH | 759717 | 20170412 | 827 | 1755880 | 943 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 943 | 37.0211 | -122.1304 | 3 SP LD SIDE OF 759717 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0039474 | OH | Sus | 42993148 | No | 2017 | APR | Yes | Force Out | 1273361 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | JUMPER | WIRE DOWN 1 SPAN W/OF 2429 | 20170413 | 1359 | 1757123 | 650 | Distribution Circuit | Vegetation | Tree - fell into line | 184 | 31417 | 37.0069 | -121.8566 | RANGEL- RUFINO: 1000 COX RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0040019 | OH | Sus | 42993859 | yes | 2017 | APR | Yes | Line to Ground | 1273660 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9443 | 20170416 | 1710 | 1758970 | 1240 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 46495 | 37.0818 | -122.0734 | 415 RANCHERIA DR | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0040624 | OH | Sus | 0 | No | 2017 | APR | Yes | Line to Ground | 1274111 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8397 | 20170416 | 1729 | 1758973 | 546 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3220 | 37.0796 | -122.1395 | COMSTOCK RD & PINE FLAT | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0040630 | OH | Sus | 42996153 | No | 2017 | APR | Yes | Line to Ground | 1274115 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 2293 | 20170417 | 1150 | 1759260 | 366 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 366 | 37.0638 | -122.2268 | 2 SPANS LD SIDE OF 2293 | Overcast-Drizzle-32-90 F | Conductor, Overhead | On Ground | 17-0040827 | OH | Sus | 42996607 | No | 2017 | APR | Yes | Line to Ground | 1274283 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 660617 | 20170418 | 1535 | 1760601 | 643 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 10288 | 37.0757 | -121.9926 | MRT 1007591241 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0041249 | OH | Sus | 31320371 | yes | 2017 | APR | Yes | Line to Ground | 1274572 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN @ 1025 MORRELL MILL RD | 20170429 | 1254 | 1770436 | 1482 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 9222 | 37.1054 | -121.9599 | 1025 MORRELL MILL RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0043909 | OH | Sus | 31322661 | No | 2017 | APR | Yes | Open Circuit | 1276530 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | OTHER | PN WIRE DOWN TWD TX MTR# 1005533444 | 20170430 | 1947 | 1771134 | 490 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 3882 | 37.0633 | -121.9404 | 7 LD SIDE OF 8353 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0044031 | OH | Sus | 43004131 | No | 2017 | APR | Yes | Open Circuit | 1276664 | CSO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE | 23665 | 20170502 | 2048 | 1772895 | 402 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 2431 | 36.5367 | -121.7377 | 2 SPAN LOAD SIDE 3207 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0044730 | OH | Sus | 43005972 | yes | 2017 | MAY | Yes | Line to Ground | 1277133 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 6625 | 20170505 | 1218 | 1775464 | 887 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 5856 | 36.376 | -121.5912 | 2 SPANS LD SIDE MTR 1008672894 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0045677 | OH | Sus | 43007849 | No | 2017 | MAY | Yes | Line to Ground | 1277792 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5995 | 20170506 | 748 | 1776040 | 262 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 1834 | 37.078 | -122.244 | HARD TAP AT MTR10702J | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0045775 | OH | Sus | 31324256 | yes | 2017 | MAY | Yes | Line to Ground | 1277898 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8513 | 20170506 | 349 | 1775982 | 664 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 7459 | 37.055 | -122.1531 | MTR1008412329 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0045778 | OH | Sus | 43008037 | yes | 2017 | MAY | Yes | Line to Line | 1277901 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN BENITO-2104 | 182742104 | RECLOSER | 88772 | 20170506 | 430 | 1775986 | 599 | Distribution Circuit | 3rd Party | Vehicle | 135 | 22617 | 36.904 | -121.6087 | 3 SPANS SOUTH OF 139 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0045737 | OH | Sus | 0 | yes | 2017 | MAY | Yes | Line to Line | 1277851 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5501 | 20170512 | 1727 | 1781038 | 448 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 60070 | 37.1432 | -122.1317 | 1 SPAN L/S OF 5501 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0047657 | OH | Sus | 43016042 | No | 2017 | MAY | Yes | Line to Ground | 1279312 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER | WIRE DOWN SINGLE PHASE | 20170517 | 1701 | 1784370 | 687 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 23358 | 37.1882 | -122.1581 | 10/4 Monte Vista 60Kv at End Of Owl Ridge Rd. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0048674 | OH | Sus | 43018997 | No | 2017 | MAY | Yes | None | 1280155 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 11817 | 20170521 | 1720 | 1786857 | 1336 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 17368 | 37.1725 | -122.2143 | 2 SPANS SS OF 9361 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0049483 | OH | Sus | 43020448 | No | 2017 | MAY | Yes | Line to Line | 1280747 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 5819 | 20170527 | 1643 | 1791974 | 1204 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 71036 | 37.0447 | -121.8131 | WIRE DOWN 1 AND 4 SPANS LD SIDE OF 5819 | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 17-0051171 | OH | Sus | 43024543 | No | 2017 | MAY | Yes | Line to Ground | 1281872 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | OTHER | WIRE DOWN 1 E/OF METER # 1007589596 | 20170528 | 1151 | 1792373 | 444 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 888 | 37.1141 | -122.1102 | 1 SPAN E/OF METER # 1007589596 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0051234 | OH | Sus | 0 | No | 2017 | MAY | Yes | Line to Ground | 1281937 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | JUMPER | OJ @ MRT#1008727042 | 20170601 | 700 | 1794359 | 1095 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 4430 | 37.0302 | -122.0876 | ALVAREZ- 3463 / 831-535-9251: End of Atamont Dr- Felton | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0052034 | OH | Sus | 43026643 | No | 2017 | JUN | Yes | Line to Ground | 1282574 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN @ 4577 | 20170601 | 1703 | 1795093 | 704 | Distribution Circuit | Vegetation | Tree - fell into line | 330 | 126416 | 37.0569 | -121.9793 | at SBCO 4577 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0052140 | OH | Sus | 43026737 | No | 2017 | JUN | Yes | Line to Ground | 1282615 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER | WIRE DOWN 1 SP N/OF MTR# 1007345110 | 20170605 | 947 | 1797108 | 436 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 98 | 36005 | 37.0479 | -122.0613 | 1 SPAN NORTH OF MTR#1007345110 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0052768 | OH | Sus | 43028829 | No | 2017 | JUN | Yes | Line to Ground | 1283146 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | JUMPER | OJ 2/N/O MTR 1007591875 | 20170608 | 1106 | 1799577 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4334 | 37.0595 | -121.8219 | 3/N/O MTR 1007591875 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0053667 | OH | Sus | 43030467 | yes | 2017 | JUN | Yes | Line to Ground | 1283775 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE | 20461 | 20170611 | 1859 | 1802008 | 490 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 5390 | 36.5383 | -121.7249 | MTR#1009440655 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0054353 | OH | Sus | 31331157 | yes | 2017 | JUN | Yes | Line to Ground | 1284255 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9229 | 20170617 | 1318 | 1806791 | 1403 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 9709 | 37.0694 | -122.0577 | STORMENT- 4178 / 831-278-0287: 170 Willow Dr.- Felton | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0055944 | OH | Sus | 43041057 | yes | 2017 | JUN | Yes | Multi-Fault | 1285420 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER | WIRE DOWN @ 5511 ML | 20170619 | 2227 | 1811822 | 818 | Distribution Circuit | 3rd Party | Vehicle | 771 | 94892 | 37.15 | -122.1365 | BOYNTON- 3459 / 831-331-6620: 15244 HWY 9 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0056836 | OH | Sus | 0 | yes | 2017 | JUN | Yes | Open Circuit | 1286272 | PW | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 1911 | 20170620 | 2154 | 1813334 | 444 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 11394 | 37.1142 | -121.984 | BET 1913 AND 1911 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0057160 | OH | Sus | 43042547 | yes | 2017 | JUN | Yes | Line to Ground | 1286544 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | RESERVATION ROAD-1102 | 182731102 | FUSE | 24581 | 20170621 | 1215 | 1813843 | 172 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 688 | 36.6023 | -121.6755 | 2 SPANS FROM METER 5000122490 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0057307 | OH | Sus | 0 | yes | 2017 | JUN | Yes | Line to Ground | 1286653 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | OTHER | WIRE DWN @ MTR#1007295369 | 20170622 | 937 | 1814926 | 982 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 28082 | 37.1108 | -122.0967 | MTR#1007295369 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0057721 | OH | Sus | 0 | yes | 2017 | JUN | Yes | Line to Ground | 1286982 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 9271 | 20170622 | 2011 | 1815327 | 229 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 2977 | 37.0359 | -121.8594 | NEAR MTR 8L1818 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0057887 | OH | Sus | 43043721 | yes | 2017 | JUN | Yes | Force Out | 1287077 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | FUSE | 5209 | 20170623 | 928 | 1816046 | 634 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 13314 | 37.0372 | -122.0723 | at 711 BROOKSIDE WAY | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0058090 | OH | Sus | 31333514 | yes | 2017 | JUN | Yes | Line to Line | 1287251 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | OTHER | WIRE DOWN 101 BIG TREES | 20170626 | 1736 | 1818679 | 599 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5083 | 37.0398 | -122.0644 | 101 BIG TREES | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0058750 | OH | Sus | 43045338 | No | 2017 | JUN | Yes | Line to Ground | 1287785 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5183 | 20170627 | 2323 | 1819508 | 783 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 18815 | 37.108 | -122.1098 | 285 PACIFIC ST | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0059060 | OH | Sus | 43045988 | No | 2017 | JUN | Yes | Line to Ground | 1288043 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 5066 | 20170628 | 1031 | 1819826 | 1460 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 148202 | 37.1707 | -122.1655 | STORMENT- 4178 / 831-278-0287: Past 19515 Big Basin Way- B.C. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0059184 | OH | Sus | 43046238 | No | 2017 | JUN | Yes | Line to Line | 1288161 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | JUMPER | WIRE DOWN HOT | 20170703 | 1428 | 1822932 | 191 | Distribution Circuit | Vegetation | Tree - branch fell on line | 173 | 27567 | 37.157 | -122.1357 | 548 RIVER ROAD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0060292 | OH | Sus | 43048880 | No | 2017 | JUL | Yes | Line to Ground | 1288881 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12992 | 20170708 | 841 | 1826234 | 490 | Distribution Circuit | Vegetation | Tree - fell into line | 689 | 63045 | 37.1987 | -122.1536 | 9 SPANS LD SIDE OF 8259 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0061404 | OH | Sus | 43052327 | yes | 2017 | JUL | Yes | Line to Ground | 1289613 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | PAUL SWEET-2106 | 83252106 | JUMPER | OPEN CORNER ISOLATING IRE DOWN | 20170711 | 2123 | 1829511 | 357 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 714 | 37.0121 | -121.95 | at MTR 1008811232 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0062198 | OH | Sus | 43058074 | No | 2017 | JUL | Yes | Line to Ground | 1290242 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2705 | 20170714 | 1534 | 1831643 | 163 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 3141 | 37.0005 | -121.7405 | BET 2705 & 12349 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0063021 | OH | Sus | 43059966 | No | 2017 | JUL | Yes | Line to Ground | 1290821 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | GONZALES-1101 | 182131101 | OTHER | WIRE DOWN FEEDING 7411 | 20170715 | 729 | 1831976 | 406 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 10948 | 36.536 | -121.4027 | SS OF 7411 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0063084 | OH | Sus | 0 | No | 2017 | JUL | Yes | Line to Ground | 1290891 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9307 | 20170716 | 2007 | 1833073 | 1260 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5040 | 37.1165 | -122.1141 | 3 SPANS L/S 9307 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0063300 | OH | Sus | 0 | No | 2017 | JUL | Yes | Line to Ground | 1291097 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 11929 | 20170717 | 1904 | 1834222 | 513 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 50787 | 37.0999 | -122.0343 | 3 SPANS L/S OF 11929 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0063518 | OH | Sus | 43062046 | No | 2017 | JUL | Yes | Line to Ground | 1291291 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 4285 | 20170720 | 752 | 1836104 | 527 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 10013 | 37.135 | -122.0238 | ALVAREZ- 3463 / 831-535-9251: 14717 Upper Zayante Rd- Los Gatos | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0064137 | OH | Sus | 0 | No | 2017 | JUL | Yes | Line to Line | 1291719 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN JUSTO-1101 | 183181101 | OTHER | WIRE DWN 10 SP LD SIDE OF 4245 | 20170724 | 1418 | 1838852 | 174 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 4596 | 36.8936 | -121.603 | 10 SP LD SIDE OF 4245 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0065086 | OH | Sus | 31338894 | No | 2017 | JUL | Yes | Line to Ground | 1292389 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 7567 | 20170728 | 132 | 1841326 | 344 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 6880 | 36.5783 | -121.9039 | 1 SP LD SIDE FUCO 7567 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0066145 | OH | Sus | 31339586 | No | 2017 | JUL | Yes | Line to Ground | 1293026 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6081 | 20170729 | 1502 | 1842220 | 776 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 12416 | 37.0578 | -122.0337 | 209 GEYER RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0066470 | OH | Sus | 31339765 | No | 2017 | JUL | Yes | Line to Line | 1293247 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 9421 | 20170801 | 2234 | 1844266 | 444 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 6096 | 37.077 | -122.0861 | 1014 VALLEY VIEW | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0067199 | OH | Sus | 43072541 | No | 2017 | AUG | Yes | Line to Ground | 1293794 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 2967 | 20170802 | 1726 | 1845016 | 1284 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3852 | 37.1602 | -122.0827 | 1 SP LD SIDE OF FUCO 2967 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0067511 | OH | Sus | 0 | yes | 2017 | AUG | Yes | Line to Ground | 1293994 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2107 | 83252107 | OTHER | WIRE DWN @ 5561 | 20170802 | 1858 | 1845007 | 532 | Distribution Circuit | 3rd Party | Vehicle | 176 | 42416 | 37.011 | -122.1226 | at FUCO 5561 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0067516 | OH | Sus | 0 | yes | 2017 | AUG | Yes | Line to Ground | 1294000 | PW | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | OTHER | WIRE DOWN 2010 GOLD GULCH | 20170804 | 326 | 1846107 | 690 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 24207 | 37.0312 | -122.0915 | 2010 GOLD GULCH MTE 1010194706 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0067864 | OH | Sus | 31340788 | No | 2017 | AUG | Yes | Line to Ground | 1294266 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | RESERVATION ROAD-1101 | 182731101 | OTHER | WIRE DOWN 6/E/O R27 | 20170806 | 1138 | 1847335 | 558 | Distribution Circuit | 3rd Party | Vehicle | 3815 | 87172 | 36.5845 | -121.7127 | 6/E/O R27 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0068279 | OH | Sus | 43075586 | No | 2017 | AUG | Yes | Three Phase Fault | 1294569 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | FUSE | 40251 | 20170812 | 1039 | 1851084 | 695 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 17993 | 36.2416 | -121.7955 | 1 SPAN L/S OF 32690 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0069855 | OH | Sus | 43083243 | No | 2017 | AUG | Yes | Line to Ground | 1295679 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 287 | 20170813 | 2204 | 1851851 | 840 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 13440 | 37.0905 | -122.0855 | 9700 LIVE OAK AVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0069997 | OH | Sus | 43083353 | No | 2017 | AUG | Yes | Line to Ground | 1295814 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8017 | 20170813 | 704 | 1851414 | 959 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 72884 | 37.1565 | -122.1617 | MTR # 1007591950 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0069915 | OH | Sus | 0 | No | 2017 | AUG | Yes | Three Phase Fault | 1295736 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | OCB | 401/2 | 20170820 | 2204 | 1855865 | 416 | Distribution Circuit | Vegetation | Tree - fell into line | 755 | 167082 | 37.0923 | -122.0965 | C0092 & GLEN ARBOR AT RIVERSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0071612 | OH | Sus | 43091029 | No | 2017 | AUG | Yes | Multi-Fault | 1296938 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6851 | 20170824 | 2230 | 1858821 | 940 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 15980 | 37.042 | -121.8165 | 3 LD SIDE OF 6851 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0072708 | OH | Sus | 43093457 | No | 2017 | AUG | Yes | Line to Ground | 1297713 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 374675 | 20170830 | 1839 | 1863605 | 559 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6708 | 37.0953 | -122.0853 | AT LAST TRANSFORMER ON ARNOLD AVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0074300 | OH | Sus | 0 | No | 2017 | AUG | Yes | Line to Ground | 1298788 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 6713 | 20170830 | 521 | 1862980 | 333 | Distribution Circuit | Vegetation | Tree - branch fell on line | 85 | 13805 | 36.4701 | -121.7242 | 15 SP LD SIDE OF FUCO 6713 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0073996 | OH | Sus | 43096700 | No | 2017 | AUG | Yes | Line to Ground | 1298617 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 487 | 20170902 | 948 | 1866124 | 1040 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 17680 | 37.1053 | -122.0857 | 4 SP LD SIDE OF FUCO 487 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0075142 | OH | Sus | 0 | yes | 2017 | SEP | Yes | Line to Ground | 1299432 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5743 | 20170904 | 1809 | 1870069 | 533 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2665 | 37.105 | -122.1161 | 2 pole load side 5743 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0075892 | OH | Sus | 31349081 | yes | 2017 | SEP | Yes | Line to Line | 1300134 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 11305 | 20170904 | 2158 | 1870182 | 277 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 3601 | 37.0307 | -121.7864 | 2 SPANS LD SIDE OF 11035 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0075953 | OH | Sus | 0 | yes | 2017 | SEP | Yes | Line to Ground | 1300194 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 8047 | 20170904 | 2016 | 1870131 | 493 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 3976 | 36.5031 | -121.9334 | 3 SPAN LOAD SIDE 8047 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0075905 | OH | Sus | 31349124 | yes | 2017 | SEP | Yes | Line to Line | 1300146 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 9789 | 20170905 | 310 | 1870240 | 540 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2160 | 37.1835 | -122.1411 | 3 SPANS LD SIDE OF FUCO 9789 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0075958 | OH | Sus | 43099276 | No | 2017 | SEP | Yes | Line to Ground | 1300199 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 8259 | 20170909 | 1013 | 1873911 | 360 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 6480 | 37.1593 | -122.1271 | 10 SPAN LD SIDE OF 8259 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0077197 | OH | Sus | 0 | No | 2017 | SEP | Yes | Line to Line | 1301106 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12992 | 20170909 | 730 | 1873834 | 165 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 15345 | 37.1987 | -122.1536 | 10 LD SIDE OF 8259 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0077178 | OH | Sus | 31350024 | No | 2017 | SEP | Yes | Line to Ground | 1301076 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12124 | 20170909 | 1508 | 1874013 | 800 | Distribution Circuit | Vegetation | Tree - fell into line | 471 | 49641 | 37.1678 | -122.1661 | at FUCO 9751 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0077229 | OH | Sus | 43102551 | No | 2017 | SEP | Yes | Line to Ground | 1301126 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 1241 | 20170910 | 58 | 1874171 | 998 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3992 | 37.0499 | -122.0604 | at 1241 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0077284 | OH | Sus | 0 | No | 2017 | SEP | Yes | Line to Line | 1301185 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | JUMPER | 3 SS OF MTR 1007330018 | 20170912 | 1545 | 1877759 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1214 | 37.103 | -122.0966 | AT MTR 1007330018 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0078366 | OH | Sus | 0 | yes | 2017 | SEP | Yes | Open Circuit | 1302006 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9445 | 20170917 | 637 | 1880407 | 413 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 14138 | 37.081 | -122.073 | 381 WEBSTER DR | Clear-32-90 F | Insulator | Broken, wire on object | 17-0079536 | OH | Sus | 43112642 | No | 2017 | SEP | Yes | Line to Ground | 1302846 | INS | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | RECLOSER | 5096 | 20170918 | 2105 | 1881389 | 391 | Distribution Circuit | Vegetation | Tree - fell into line | 525 | 77239 | 37.0511 | -122.037 | STORMENT- 4178 / 831-278-0287: Across from 333 Lockhart Gulch Rd.- S.V. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0079830 | OH | Sus | 43113425 | No | 2017 | SEP | Yes | Multi-Fault | 1303072 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 3753 | 20170926 | 2019 | 1886440 | 1842 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 21440 | 37.0539 | -121.9528 | 700 twin ln | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0081950 | OH | Sus | 43117891 | No | 2017 | SEP | Yes | Line to Ground | 1304504 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 6121 | 20170926 | 1243 | 1886137 | 401 | Distribution Circuit | Vegetation | Tree - branch fell on line | 109 | 43709 | 36.9836 | -121.8848 | MTR 1010290322 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0081826 | OH | Sus | 43117822 | No | 2017 | SEP | Yes | Line to Ground | 1304439 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5487 | 20170930 | 1332 | 1888607 | 1206 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 67536 | 37.1371 | -122.1006 | CRIVELLO- 4176 / 831-682-1912: same | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0083062 | OH | Sus | 0 | No | 2017 | SEP | Yes | Line to Line | 1305140 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER | 1 SPAN LD SIDE OF 7949 | 20171004 | 1440 | 1890946 | 456 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 8208 | 37.1895 | -122.1417 | 205 STAPP RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0084246 | OH | Sus | 31354748 | No | 2017 | OCT | Yes | Open Circuit | 1305879 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN AT FUSE 11425 | 20171013 | 1001 | 1899938 | 474 | Distribution Circuit | Vegetation | Tree - grew into line | 2792 | 201996 | 37.0562 | -122.0209 | 610 BEAN CREEK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087093 | OH | Sus | 43195135 | No | 2017 | OCT | Yes | Open Circuit | 1308112 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20171016 | 1253 | 1901696 | 137 | Distribution Circuit | 3rd Party | Vehicle | 74 | 6313 | 36.5786 | -121.9085 | 2 SPANS EAST OF 7885 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0087767 | OH | Sus | 43196868 | No | 2017 | OCT | Yes | Three Phase Fault | 1308705 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8161 | 20171025 | 2052 | 1909649 | 1055 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 12660 | 37.1174 | -121.975 | RANGEL- RUFINO: 24705 HIGHWAY 17 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0090425 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1310569 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | RECLOSER | 11056 | 20171027 | 1152 | 1910821 | 659 | Distribution Circuit | Vegetation | Tree - fell into line | 451 | 52189 | 36.9937 | -122.0299 | 2/E/O 5277 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0090827 | OH | Sus | 43202434 | No | 2017 | OCT | Yes | Line to Line | 1310840 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | FUSE | 7295 | 20171029 | 429 | 1911681 | 426 | Distribution Circuit | Vegetation | Tree - branch fell on line | 58 | 15788 | 37.0326 | -122.0875 | MTR 1006215618 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0091082 | OH | Sus | 43202640 | No | 2017 | OCT | Yes | Line to Line | 1311057 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | OTHER | 833763 | 20171106 | 1736 | 1917147 | 594 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 594 | 37.0205 | -122.1297 | 2 LD SIDE OF 833763 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0093064 | OH | Sus | 43207935 | No | 2017 | NOV | Yes | Force Out | 1312503 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12124 | 20171108 | 1451 | 1918499 | 793 | Distribution Circuit | Vegetation | Tree - fell into line | 471 | 66386 | 37.1678 | -122.1661 | AT SBCO 333109 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0093616 | OH | Sus | 43209147 | yes | 2017 | NOV | Yes | Line to Ground | 1312899 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5593 | 20171109 | 451 | 1919046 | 810 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 810 | 37.0735 | -122.0569 | BOYNTON- 3459 / 831-331-6620: 8266 W ZAYANTE RD - LAST SPAN ON TAP LINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0093939 | OH | Sus | 43209491 | yes | 2017 | NOV | Yes | Line to Ground | 1313145 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER | 5206 | 20171116 | 1003 | 1923740 | 594 | Distribution Circuit | Equipment Failure/Involved | Overhead | 121 | 71874 | 37.0955 | -122.0857 | 1 NORTH OF 557 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0095503 | OH | Sus | 31365752 | yes | 2017 | NOV | Yes | Line to Line | 1314364 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 3603 | 20171116 | 1105 | 1923815 | 548 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4932 | 37.1149 | -122.1138 | 11 TINKERS TRL | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0095624 | OH | Sus | 31365537 | yes | 2017 | NOV | Yes | Line to Ground | 1314426 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12836 | 20171116 | 1127 | 1923849 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 471 | 53119 | 37.1478 | -122.1576 | ALVAREZ- 3463 / 831-535-9251: Hwy 236 S/O China Grade Rd- Boulder Creek | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0095542 | OH | Sus | 43216312 | yes | 2017 | NOV | Yes | Line to Line | 1314389 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | FUSE | 1295 | 20171116 | 1033 | 1923771 | 817 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11438 | 36.3795 | -121.8611 | MTR 1010313846 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0095562 | OH | Sus | 31365735 | yes | 2017 | NOV | Yes | Line to Line | 1314397 | CAW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | OTHER | WIRE DOWN @ MTR 1008711118 | 20171116 | 1628 | 1924227 | 1307 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 8267 | 37.0101 | -121.8544 | MTR 1008711118 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0095786 | OH | Sus | 31365537 | yes | 2017 | NOV | Yes | Open Circuit | 1314544 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 2989 | 20171122 | 1453 | 1928124 | 1272 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 1785 | 37.1638 | -122.0767 | 1 SPAN S/OF 2989 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0097201 | OH | Sus | 31366734 | No | 2017 | NOV | Yes | Line to Line | 1315497 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | GREEN VALLEY-2101 | 83192101 | JUMPER | O/J AT OD BANK DUE TO TREE WIRE DOWN | 20171124 | 332 | 1928488 | 583 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3498 | 36.9895 | -121.744 | MTR #316370518075 | Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0097358 | OH | Sus | 43220658 | No | 2017 | NOV | Yes | Open Circuit | 1315618 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | PANOCHE-1103 | 253671103 | OTHER | WIRE DOWN 1 SP SS 51075 | 20171124 | 926 | 1928595 | 144 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1 | 144 | 36.6089 | -120.9125 | WIRE DOWN 1 SP SS 51075 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0097367 | OH | Sus | 0 | No | 2017 | NOV | Yes | None | 1315624 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | RECLOSER | 10960 | 20171125 | 526 | 1928852 | 354 | Distribution Circuit | 3rd Party | Vehicle | 1202 | 70335 | 36.9866 | -121.8582 | at FUCO 587 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0097449 | OH | Sus | 0 | No | 2017 | NOV | Yes | Line to Ground | 1315696 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5173 | 20171126 | 818 | 1929177 | 531 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 32391 | 37.1011 | -122.1017 | NYSTROM-ERIK-1058/408-799-8799: 1500 River Rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0097583 | OH | Sus | 43222265 | No | 2017 | NOV | Yes | Line to Ground | 1315808 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9373 | 20171126 | 1107 | 1929315 | 447 | Distribution Circuit | Vegetation | Tree - branch fell on line | 36 | 16092 | 37.1261 | -122.1219 | 4 SP LD SIDE OF FUCO 9373 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0097589 | OH | Sus | 43222268 | No | 2017 | NOV | Yes | Line to Line | 1315814 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 11010 | 20171126 | 854 | 1929201 | 444 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 14509 | 37.1053 | -122.0518 | MTR# 1006237654 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0097572 | OH | Sus | 43222263 | No | 2017 | NOV | Yes | Line to Ground | 1315797 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | FUSE | 5209 | 20171126 | 551 | 1929152 | 447 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 9387 | 37.0372 | -122.0723 | 699 BROOKSIDE | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0097560 | OH | Sus | 31366960 | No | 2017 | NOV | Yes | Line to Ground | 1315787 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN BENITO-2104 | 182742104 | RECLOSER | 88772 | 20171126 | 2000 | 1929568 | 528 | Distribution Circuit | 3rd Party | Vehicle | 1245 | 39884 | 36.904 | -121.6087 | 1 S/O SW 139 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0097636 | OH | Sus | 0 | No | 2017 | NOV | Yes | Multi-Fault | 1315858 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | JUMPER | WIRE DOWN 1 SP LS 42365 ON TAP | 20171127 | 925 | 1930053 | 490 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1470 | 36.5828 | -121.9343 | 1 SP LS 42365 ON TAP OPEN | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0097819 | OH | Sus | 0 | yes | 2017 | NOV | Yes | Line to Ground | 1316043 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | TRIP-SAVER | 9741 | 20171207 | 702 | 1937894 | 291 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 12222 | 37.157 | -122.1289 | 340 SUNBEAM | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0100421 | OH | Sus | 31368682 | No | 2017 | DEC | Yes | Force Out | 1318087 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | FUSE | 9187 | 20171211 | 438 | 1940233 | 524 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2096 | 36.2299 | -121.757 | 3 SPANS LD SIDE OF 9187 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0101070 | OH | Sus | 0 | No | 2017 | DEC | Yes | Line to Ground | 1318767 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER | WIRE DWN 1 SP SS/OF FUCO 11929 | 20171212 | 1413 | 1941342 | 797 | Distribution Circuit | 3rd Party | Vehicle | 190 | 145788 | 37.0999 | -122.0343 | WIRE DWN 1 SP SS/OF FUCO 11929 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0101360 | OH | Sus | 31369516 | No | 2017 | DEC | Yes | Line to Ground | 1319122 | PW | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | FUSE | 7299 | 20171217 | 333 | 1946085 | 845 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 9316 | 37.031 | -122.0941 | 1 SPAN LD SIDE OF FUCO 7299 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102285 | OH | Sus | 0 | No | 2017 | DEC | Yes | Line to Ground | 1320198 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | OTHER | WIRE DOWN SS 11737 | 20171217 | 8 | 1946111 | 887 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 21288 | 37.0694 | -122.1303 | 1 SPAN SS 11737 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102321 | OH | Sus | 0 | No | 2017 | DEC | Yes | Open Circuit | 1320242 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 1003 | 20171220 | 256 | 1948126 | 672 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 34668 | 36.999 | -121.8643 | 4 SPANS L/S OF 1003 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102712 | OH | Sus | 43238621 | yes | 2017 | DEC | Yes | Line to Line | 1320949 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER | WIRE DOWN | 20171221 | 2008 | 1949893 | 967 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 18391 | 37.1909 | -122.1634 | at MTR 5000128545 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0103008 | OH | Sus | 43240431 | No | 2017 | DEC | Yes | Open Circuit | 1321540 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN 1/SS/O 6043 | 20180105 | 808 | 2485-2 | 362 | Distribution Circuit | Vegetation | Tree - fell into line | 543 | 58074 | 37.0676 | -121.9966 | 1/SS/O 6043 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0003786 | OH | Sus | 31372276 | No | 2018 | JAN | Yes | Line to Ground | 1323306 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 9751 | 20180106 | 534 | 3054 | 474 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 474 | 37.1611 | -122.1627 | LAST SPAN ON TAP LINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0003974 | OH | Sus | 43245623 | No | 2018 | JAN | Yes | Line to Line | 1323415 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | RESERVATION ROAD-1102 | 182731102 | FUSE | 5567 | 20180106 | 2152 | 3307 | 331 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 6620 | 36.5213 | -121.5213 | CHAVEZ- TOM: LIMEKILN RD. at RIVER RD. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0004071 | OH | Sus | 43245761 | No | 2018 | JAN | Yes | Line to Line | 1323486 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER | WIRE DOWN 1/NE/O 5605 | 20180108 | 2024 | 4323 | 1021 | Distribution Circuit | Vegetation | Tree - fell into line | 905 | 431418 | 37.0876 | -122.0466 | 1/NE/O 5605 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0004468 | OH | Sus | 43245387 | yes | 2018 | JAN | Yes | Open Circuit | 1323700 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 7637 | 20180108 | 1719 | 4108 | 656 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 17056 | 37.0078 | -121.9385 | 7 SPANS LOAD SIDE 7637 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0004447 | OH | Sus | 31372380 | yes | 2018 | JAN | Yes | Line to Ground | 1323679 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 9271 | 20180108 | 2228 | 4402 | 1107 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 5051 | 37.0359 | -121.8594 | 2 SPANS L/S OF METER # 1010018399 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0004516 | OH | Sus | 31372380 | yes | 2018 | JAN | Yes | Line to Ground | 1323750 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER | WIRE DOWN BET 97951 & 468365 | 20180109 | 2236 | 5546 | 872 | Distribution Circuit | Equipment Failure/Involved | Overhead | 96 | 19347 | 37.0968 | -122.107 | ZANDATE- BOBBY: 11130 Alba Rd Between LCO 97951 & SBCO 468365 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0004901 | OH | Sus | 0 | yes | 2018 | JAN | Yes | Open Circuit | 1323987 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | OTHER | WIRE DOWN @ METER # 1008067954 | 20180109 | 1721 | 5389 | 475 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 18918 | 36.6043 | -121.9443 | at METER # 1008067954 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0004868 | OH | Sus | 0 | yes | 2018 | JAN | Yes | Open Circuit | 1323954 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5439 | 20180111 | 1641 | 6862 | 804 | Distribution Circuit | Vegetation | Tree - fell into line | 228 | 64993 | 37.1128 | -122.1145 | 4 SPANS LD SIDE 5439 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0005493 | OH | Sus | 0 | No | 2018 | JAN | Yes | Line to Ground | 1324366 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | OCB | 5400 | 20180113 | 716 | 7662 | 850 | Distribution Circuit | Vegetation | Tree - fell into line | 920 | 229553 | 37.0491 | -122.0645 | AT SW 8669 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0005917 | OH | Sus | 0 | No | 2018 | JAN | Yes | Line to Ground | 1324683 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 8095 | 20180113 | 1803 | 7923 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 5394 | 37.0022 | -121.9417 | 18 SPANS LD SIDE OF 8095 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0005995 | OH | Sus | 0 | No | 2018 | JAN | Yes | Line to Ground | 1324742 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5995 | 20180113 | 1239 | 7825 | 681 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 4767 | 37.078 | -122.244 | 8 SPANS FROM EOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0005981 | OH | Sus | 43253054 | No | 2018 | JAN | Yes | Line to Ground | 1324735 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | TRIP-SAVER | 2253 | 20180114 | 2049 | 8160 | 857 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 4956 | 37.1711 | -122.1653 | at CGC 315130825018 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0006101 | OH | Sus | 43253261 | No | 2018 | JAN | Yes | Line to Line | 1324844 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 6103 | 20180117 | 1137 | 9750 | 307 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 54 | 16578 | 37.0115 | -122.0121 | at 3979 ON MAINLINE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0006767 | OH | Sus | 43255448 | No | 2018 | JAN | Yes | Line to Ground | 1325260 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9771 | 20180301 | 1011 | 34434 | 754 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 21938 | 37.1313 | -122.121 | AT METER 1007586772 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0018568 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333022 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9725 | 20180301 | 1627 | 35316 | 1383 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 37341 | 37.1522 | -122.1366 | 495 BAND RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0018790 | OH | Sus | 31381881 | yes | 2018 | MAR | Yes | Line to Line | 1333163 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8503 | 20180301 | 1030 | 34643 | 31 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 62 | 37.1711 | -122.2183 | 3 SPANS L/S OF 77767 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0018504 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1332983 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | OTHER | WIRE DOWN BET 10013 & 63323 | 20180301 | 1059 | 34628 | 468 | Distribution Circuit | Vegetation | Tree - fell into line | 347 | 71457 | 37.015 | -121.9989 | BET 10013 & 63323 at FCO 10013 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0018512 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Open Circuit | 1332987 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 6813 | 20180301 | 1241 | 34786 | 1587 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 10434 | 36.5715 | -121.8904 | 7779 | Overcast-Heavy Rain-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0018695 | OH | Sus | 31381790 | yes | 2018 | MAR | Yes | Three Phase Fault | 1333091 | CAW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 8337 | 20180301 | 1240 | 34784 | 350 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 5250 | 37.0344 | -121.9448 | 2 SP E/O 8337 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0018773 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333147 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 5819 | 20180301 | 944 | 34381 | 1976 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 58538 | 37.0447 | -121.8131 | 3 SPANS S/S OF METER # 1007591874 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0018470 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1332970 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6819 | 20180301 | 1257 | 34969 | 1378 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 26173 | 36.9961 | -121.8656 | 2/N/O MTR 1008734944 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0018725 | OH | Sus | 43286418 | yes | 2018 | MAR | Yes | Line to Line | 1333108 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 7873 | 20180301 | 1154 | 34794 | 217 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 6510 | 36.5772 | -121.9452 | CGC #411339246664 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0018563 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333018 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5995 | 20180302 | 702 | 35980 | 590 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2110 | 37.078 | -122.244 | DARBYSHIRE- 4177 /831-212-2089: 460 SWANTON ROAD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019042 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333358 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 2943 | 20180310 | 1546 | 41668 | 1570 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 64248 | 36.4759 | -121.7193 | MTR #1009012722. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0021590 | OH | Sus | 31383662 | No | 2018 | MAR | Yes | Line to Ground | 1335144 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 7289 | 20180313 | 253 | 43142 | 790 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1580 | 37.1782 | -122.1856 | 4 SPAN LD SD OF MTR# 1008988493 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0022167 | OH | Sus | 43299632 | yes | 2018 | MAR | Yes | Line to Ground | 1335592 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | OTHER | WIRE DOWN BET 40511 & 8045 | 20180313 | 1112 | 43229 | 270 | Distribution Circuit | Vegetation | Tree - branch fell on line | 122 | 8989 | 36.5046 | -121.936 | BET 40511 & 8045 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0022234 | OH | Sus | 31383913 | yes | 2018 | MAR | Yes | Open Circuit | 1335605 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5519 | 20180314 | 850 | 43846 | 733 | Distribution Circuit | Vegetation | Tree - fell into line | 172 | 106267 | 37.1515 | -122.1362 | 548 RIVER RD | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0022613 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Multi-Fault | 1335820 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | FUSE | 11967 | 20180314 | 629 | 43756 | 455 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 14105 | 37.0289 | -122.0724 | MTR#1008858359 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0022533 | OH | Sus | 43300470 | yes | 2018 | MAR | Yes | Line to Ground | 1335746 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | TRIP-SAVER | 6577 | 20180315 | 1843 | 45053 | 1102 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 52896 | 37.048 | -121.8081 | 2030 UPPER HIGHLAND WAY | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023216 | OH | Sus | 43300898 | No | 2018 | MAR | Yes | Line to Ground | 1336118 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | JOLON-1102 | 182981102 | FUSE | 9577 | 20180318 | 1731 | 47469 | 408 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 6528 | 35.9897 | -121.1346 | 65103 DAVIS CANYON RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023948 | OH | Sus | 43303160 | No | 2018 | MAR | Yes | Line to Ground | 1336732 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8983 | 20180318 | 1112 | 47315 | 168 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 8064 | 37.0309 | -122.143 | 4201 SMITH GRADE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023893 | OH | Sus | 43303122 | No | 2018 | MAR | Yes | Force Out | 1336698 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 5143 | 20180321 | 1215 | 49472 | 285 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 7410 | 37.0995 | -122.0869 | Roberts Rd 2nd span in. | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0024967 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1337323 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER | WIRE DOWN @ 208 ALTA DR | 20180321 | 1141 | 49453 | 637 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 11427 | 37.1563 | -122.1261 | CAPWELL - 3915 / 831-206-1280: 208 ALTO DR | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0024914 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Open Circuit | 1337312 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | CAMP EVERS-2105 | 83622105 | FUSE | 5233 | 20180321 | 349 | 49106 | 401 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 8822 | 37.0577 | -122.0762 | 1 SPAN LD SIDE 5233 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0024678 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1337229 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | FUSE | 5205 | 20180321 | 700 | 49177 | 763 | Distribution Circuit | Vegetation | Tree - fell into line | 235 | 155979 | 37.0417 | -122.0727 | 331 SAN LORENZO AVE | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0024713 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1337237 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 5985 | 20180321 | 213 | 49086 | 477 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 43407 | 37.045 | -121.9384 | 7 SPANS LD SIDE 5985 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0024666 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1337221 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8365 | 20180322 | 843 | 50980 | 781 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 22649 | 37.1667 | -122.2008 | 2 SP LS 8365 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025680 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1337657 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 8215 | 20180322 | 1021 | 50580 | 328 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 19352 | 37.0622 | -122.0322 | MTR#1007586383 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025456 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1337579 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | RECLOSER | 2052 | 20180322 | 840 | 50396 | 467 | Distribution Circuit | Vegetation | Tree - fell into line | 140 | 65380 | 36.3999 | -121.902 | 37200 PALO COLORADO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025346 | OH | Sus | 43303197 | yes | 2018 | MAR | Yes | Line to Ground | 1337527 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5477 | 20180330 | 1958 | 56933 | 955 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 28925 | 37.1291 | -122.1142 | MTR 1008746901 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0028077 | OH | Sus | 43312072 | No | 2018 | MAR | Yes | Line to Line | 1339584 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2012 | 20180330 | 241 | 56311 | 612 | Distribution Circuit | Equipment Failure/Involved | Overhead | 504 | 308448 | 36.3314 | -121.8829 | 1span SS of B104 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0027878 | OH | Sus | 43311782 | No | 2018 | MAR | Yes | Multi-Fault | 1339436 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5501 | 20180406 | 448 | 60559 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 32196 | 37.1432 | -122.1317 | METER # 1008735802 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0029760 | OH | Sus | 43316474 | yes | 2018 | APR | Yes | Line to Ground | 1340847 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 5151 | 20180407 | 644 | 61693 | 604 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3624 | 37.1109 | -122.0898 | BRANDT- 4179 / 831-212-2088: Love creek at fritch creek Rd 2nd span LS 5151 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0030224 | OH | Sus | 31387699 | yes | 2018 | APR | Yes | Line to Ground | 1341103 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 3649 | 20180407 | 857 | 61788 | 409 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3272 | 36.9864 | -121.8507 | 3 SP L/S OF 3649 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0030235 | OH | Sus | 43316978 | yes | 2018 | APR | Yes | Line to Ground | 1341116 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER | 5028 | 20180408 | 314 | 62477 | 570 | Distribution Circuit | Vegetation | Tree - fell into line | 178 | 28005 | 37.1284 | -122.1222 | HARD TAP 1 SPAN S/S OF 8469 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0030358 | OH | Sus | 31387900 | No | 2018 | APR | Yes | Line to Ground | 1341234 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 1159 | 20180414 | 1239 | 66872 | 445 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 15130 | 37.0409 | -122.0795 | 4 SP LD SIDE 1159 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0032263 | OH | Sus | 31388708 | No | 2018 | APR | Yes | Line to Line | 1342723 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6083 | 20180422 | 650 | 71569 | 820 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 59667 | 37.0587 | -122.0334 | MTR 1007587439 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0034403 | OH | Sus | 43329560 | No | 2018 | APR | Yes | Line to Ground | 1344222 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9267 | 20180423 | 631 | 71814 | 202 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 1414 | 37.1 | -122.0353 | FIRS SPAN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0034510 | OH | Sus | 31389603 | No | 2018 | APR | Yes | Line to Ground | 1344315 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | OTHER | WIRE DOWN 300' NE/O 520 TINKERS TRL | 20180427 | 814 | 74826 | 475 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3691 | 37.1146 | -122.1087 | 4 NE/OF MTR#1007589596 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0036120 | OH | Sus | 31390205 | No | 2018 | APR | Yes | Open Circuit | 1345336 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | OTHER | WIRE DOWN @ METER # 1008448505 | 20180509 | 2040 | s1347905 | 1047 | Distribution Circuit | Vegetation | Tree - fell into line | 945 | 45007 | 37.0003 | -122.0278 | 4 OAK RD- SANTA CRUZ | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0039738 | OH | Sus | 0 | No | 2018 | MAY | Yes | Line to Ground | 1347905 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | RESERVATION ROAD-1101 | 182731101 | RECLOSER | 3026 | 20180527 | 2047 | 94934 | 818 | Distribution Circuit | 3rd Party | Vehicle | 710 | 236788 | 36.5787 | -121.7199 | SW 725- 1 S/S POLE IS DOWN | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0044765 | OH | Sus | 0 | No | 2018 | MAY | Yes | Three Phase Fault | 1351838 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | OTHER | WIRE DOWN @ RCO 11859 | 20180601 | 1737 | 98991 | 622 | Distribution Circuit | 3rd Party | Vehicle | 5434 | 85239 | 36.9858 | -121.8609 | RCO 11859 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0046482 | OH | Sus | 31394454 | No | 2018 | JUN | Yes | Open Circuit | 1353120 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2104 | 83252104 | OTHER | WIRE DOWN @ 845 | 20180602 | 1741 | 99667 | 1163 | Distribution Circuit | Vegetation | Tree - fell into line | 296 | 34320 | 37.0322 | -121.9666 | at FU 845 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0046677 | OH | Sus | 31394333 | No | 2018 | JUN | Yes | Line to Ground | 1353307 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9071 | 20180603 | 1221 | 100036 | 882 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 72021 | 37.0594 | -122.0589 | 2 SPANS SOURCE SIDE OF FUCO 7193 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0046755 | OH | Sus | 43361549 | No | 2018 | JUN | Yes | Line to Ground | 1353412 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 9849 | 20180607 | 2302 | 104007 | 777 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4662 | 37.0263 | -121.7794 | 4 SPANS LD SIDE OF FUCO 9849 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0048742 | OH | Sus | 43365035 | No | 2018 | JUN | Yes | Line to Ground | 1354869 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20180610 | 136 | 105554 | 691 | Distribution Circuit | Vegetation | Tree - fell into line | 185 | 83330 | 37.0669 | -122.0336 | 1 SPAM S/S MTR: 1008517809 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0049361 | OH | Sus | 31395482 | No | 2018 | JUN | Yes | Line to Ground | 1355406 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 12069 | 20180614 | 1625 | 109495 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 14487 | 37.1239 | -122.1196 | 205 FAIRVIEW AVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0051237 | OH | Sus | 43373610 | No | 2018 | JUN | Yes | Line to Line | 1356716 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 6975 | 20180614 | 548 | 108836 | 358 | Distribution Circuit | Vegetation | Tree - branch fell on line | 53 | 17136 | 36.5797 | -121.9203 | CORI- MARK: 4136 sunset | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0050804 | OH | Sus | 31395917 | No | 2018 | JUN | Yes | Line to Ground | 1356505 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | RECLOSER | 3088 | 20180616 | 2018 | 111090 | 272 | Distribution Circuit | Equipment Failure/Involved | Overhead | 719 | 102993 | 36.5493 | -121.7318 | at 3241 GOING NORTH | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0051678 | OH | Sus | 43375767 | yes | 2018 | JUN | Yes | Line to Ground | 1357122 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5617 | 20180619 | 2257 | 113363 | 771 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 6939 | 37.0986 | -122.0533 | 10274 LOMITA AVE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0052543 | OH | Sus | 31396648 | No | 2018 | JUN | Yes | Line to Ground | 1357885 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 5076 | 20180621 | 738 | 114219 | 369 | Distribution Circuit | Equipment Failure/Involved | Overhead | 122 | 42516 | 37.0321 | -122.1892 | SOURCE SIDE 8199 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0053023 | OH | Sus | 43379125 | No | 2018 | JUN | Yes | Line to Ground | 1358229 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 9305 | 20180624 | 1405 | 117027 | 741 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 3168 | 37.1153 | -122.1145 | 1 SP SS CGC# 315282722743 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0054046 | OH | Sus | 43381468 | No | 2018 | JUN | Yes | Line to Ground | 1359071 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | WIER DOWN FEEDING MTR# 1009257835 | 20180701 | 1502 | 122460 | 463 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 463 | 37.053 | -121.9861 | MTR#1009257835 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0056098 | OH | Sus | 43386922 | No | 2018 | JUL | Yes | Line to Ground | 1360906 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 6091 | 20180701 | 2011 | 122613 | 1631 | Distribution Circuit | 3rd Party | Aircraft | 237 | 34103 | 36.3915 | -121.6193 | 10 SP LS MTR#1010273507 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0056126 | OH | Sus | 31398585 | No | 2018 | JUL | Yes | Force Out | 1360930 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN JUSTO-1101 | 183181101 | FUSE | 4245 | 20180705 | 242 | 124660 | 374 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 10098 | 36.8938 | -121.5973 | 5 P LS 4245 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0057027 | OH | Sus | 31398867 | No | 2018 | JUL | Yes | Line to Line | 1361551 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | OCB | 401/2 | 20180706 | 2110 | 125809 | 810 | Distribution Circuit | Vegetation | Tree - fell into line | 756 | 63448 | 37.0923 | -122.0965 | 9890 BROOKSIDE DR- METER # 1007591419 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0057593 | OH | Sus | 31399042 | No | 2018 | JUL | Yes | Line to Ground | 1361864 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | OTHER | WIRE DOWN 7 SPANS LD SIDE OF 5143 | 20180708 | 1911 | 126639 | 459 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 11619 | 37.1029 | -122.0912 | 7 SP LD SIDE 5143 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0057793 | OH | Sus | 43390992 | No | 2018 | JUL | Yes | Open Circuit | 1362091 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5495 | 20180708 | 1124 | 126514 | 866 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 16356 | 37.1384 | -122.1294 | 315 HIGH RISE DRIVE//////METER 1007345380 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0057763 | OH | Sus | 43390983 | No | 2018 | JUL | Yes | Three Phase Fault | 1362063 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | PRUNEDALE-1107 | 182961107 | FUSE | 25027 | 20180713 | 345 | 130396 | 523 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 523 | 36.798 | -121.5697 | FUSE 25027 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0059429 | OH | Sus | 43399518 | No | 2018 | JUL | Yes | Line to Ground | 1363349 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2012 | 20180714 | 2138 | 132021 | 979 | Distribution Circuit | Animal | Other | 504 | 493416 | 36.3314 | -121.8829 | 1 LD SIDE OF C312 ON MAINLINE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0059900 | OH | Sus | 43401322 | No | 2018 | JUL | Yes | Three Phase Fault | 1363846 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5569 | 20180718 | 2153 | 135169 | 1203 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 63759 | 37.0503 | -122.0673 | SYLVAN & RIVER | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0061267 | OH | Sus | 0 | yes | 2018 | JUL | Yes | Line to Ground | 1364882 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | FUSE | 7295 | 20180720 | 500 | 136052 | 495 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 28710 | 37.0326 | -122.0875 | BOYNTON- 3459 / 831-331-6620: 1701 LAKESIDE DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0061702 | OH | Sus | 31400624 | No | 2018 | JUL | Yes | Line to Ground | 1365218 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | FUSE | 9725 | 20180722 | 531 | 137465 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 13824 | 37.1522 | -122.1366 | KELLY- 4017 / 831-682-1802: 4 spans in from C/O 9725 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0062478 | OH | Sus | 31400920 | No | 2018 | JUL | Yes | Line to Ground | 1365699 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5461 | 20180722 | 2349 | 137743 | 768 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 15597 | 37.1383 | -122.1435 | 411 BROOK LANE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0062561 | OH | Sus | 43413624 | No | 2018 | JUL | Yes | Line to Ground | 1365793 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 11319 | 20180725 | 2009 | 140481 | 966 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2898 | 37.0253 | -121.8838 | 5251 BOTH WAYS | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0063782 | OH | Sus | 0 | No | 2018 | JUL | Yes | Line to Ground | 1366695 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5157 | 20180726 | 120 | 140585 | 728 | Distribution Circuit | Vegetation | Tree - fell into line | 172 | 125216 | 37.0839 | -122.089 | 3 SPANS SW OF 5157 | Clear-32-90F | Conductor, Overhead | On Ground | 18-0063810 | OH | Sus | 43418251 | No | 2018 | JUL | Yes | Line to Ground | 1366728 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | JOLON-1102 | 182981102 | FUSE | 9889 | 20180726 | 2138 | 141359 | 1111 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 14860 | 35.9806 | -121.0811 | 1 SP S/S OF MTR# 1009479825 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0064235 | OH | Sus | 43421578 | No | 2018 | JUL | Yes | Line to Line | 1367008 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | OCB | 1101/2 | 20180727 | 1027 | 141724 | 1087 | Distribution Circuit | Vegetation | Tree - fell into line | 2815 | 293958 | 37.1312 | -122.1724 | 13575 EMPIRE GRADE ALVAREZ- 3463 / 831-535-9251: Empire Grade- Bonny Doon | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0064350 | OH | Sus | 0 | No | 2018 | JUL | Yes | Multi-Fault | 1367149 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER | OJ SS OF METER 1008968330 | 20180801 | 252 | 146349 | 1088 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 2356 | 37.1777 | -122.1797 | METER 1008968330 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0065587 | OH | Sus | 0 | No | 2018 | AUG | Yes | Line to Line | 1368158 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 1913 | 20180802 | 2207 | 147961 | 535 | Distribution Circuit | Vegetation | Tree - bark fell into line | 27 | 14445 | 37.1158 | -121.9822 | 2 SPAN LD SIDE OF FUCO 1913- 18461 CIRCLE DR- LOS GATOS | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0066345 | OH | Sus | 31401951 | No | 2018 | AUG | Yes | Line to Ground | 1368742 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | JUMPER | OJS 3 SPANS LD SIDE OF MTR # 5000022231 | 20180803 | 2049 | 148596 | 879 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1758 | 37.1275 | -122.1348 | 4 SPAN LD SIDE MTR # 5000022231 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0066627 | OH | Sus | 43429761 | No | 2018 | AUG | Yes | Line to Ground | 1368958 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6087 | 20180804 | 1718 | 149012 | 687 | Distribution Circuit | Vegetation | Tree - fell into line | 185 | 29355 | 37.0669 | -122.0336 | 3175 WAKEFIELD WAY | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0066787 | OH | Sus | 43429946 | No | 2018 | AUG | Yes | Line to Ground | 1369104 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 9307 | 20180807 | 1715 | 150919 | 497 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1988 | 37.1165 | -122.1141 | 1 SPAN SOURCE SIDE OF CGC 315306522901 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0067641 | OH | Sus | 43431308 | No | 2018 | AUG | Yes | Force Out | 1369739 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12758 | 20180808 | 1253 | 151483 | 863 | Distribution Circuit | Vegetation | Tree - fell into line | 295 | 39055 | 37.1486 | -122.1748 | 16405 JAMISON CREEK RD | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0068001 | OH | Sus | 0 | No | 2018 | AUG | Yes | Multi-Fault | 1369891 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | RESERVATION ROAD-1102 | 182731102 | OCB | 1102/2 | 20180813 | 1407 | 154589 | 251 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2105 | 245876 | 36.6242 | -121.6886 | RESERVATION RD W/O HWY 68 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0069362 | OH | Sus | 31402786 | No | 2018 | AUG | Yes | Three Phase Fault | 1370623 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | RESERVATION ROAD-1102 | 182731102 | OCB | 3730 | 20180827 | 933 | 163051 | 581 | Distribution Circuit | 3rd Party | Vehicle | 2442 | 617541 | 36.6242 | -121.6886 | Broken pole 1 span SS of 23067 and WIRE Down at 80115 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0073729 | OH | Sus | 43448971 | No | 2018 | AUG | Yes | Multi-Fault | 1373720 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5443 | 20180830 | 1926 | 165995 | 499 | Distribution Circuit | Vegetation | Tree - bark fell into line | 6 | 1845 | 37.1106 | -122.1143 | 12130 ALTA VIA BROOKEDALE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0075306 | OH | Sus | 43451623 | No | 2018 | AUG | Yes | Multi-Fault | 1374882 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | OTHER | WIRE DOWN @ MTR#1010368577 | 20180831 | 1531 | 166428 | 459 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2241 | 37.0488 | -121.8165 | at MTR#1010368577 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0075718 | OH | Sus | 31404790 | No | 2018 | AUG | Yes | Line to Line | 1375111 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 1101 | 20180903 | 47 | 167309 | 979 | Distribution Circuit | Vegetation | Tree - fell into line | 448 | 124023 | 37.0926 | -122.0966 | BOYNTON- 3459 / 831-331-6620: C/O POLE # 5187 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0075937 | OH | Sus | 31404987 | No | 2018 | SEP | Yes | Line to Ground | 1375311 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 7083 | 20180907 | 1715 | 170232 | 1285 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 136210 | 37.1744 | -122.1449 | MTR#1007591328 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0077712 | OH | Sus | 31405470 | No | 2018 | SEP | Yes | Line to Line | 1376447 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | RECLOSER | 5178 | 20180910 | 342 | 171180 | 659 | Distribution Circuit | Vegetation | Tree - fell into line | 268 | 97970 | 37.0326 | -121.9462 | 3 SP SS 8091 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0078005 | OH | Sus | 43457473 | No | 2018 | SEP | Yes | Line to Ground | 1376730 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5203 | 20180913 | 28 | 173381 | 827 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 22329 | 37.0394 | -122.0817 | 876 BROOKSIDE DR | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0079202 | OH | Sus | 43463693 | No | 2018 | SEP | Yes | Line to Ground | 1377581 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5183 | 20180916 | 1954 | 175453 | 430 | Distribution Circuit | Vegetation | Tree - branch fell on line | 49 | 21070 | 37.108 | -122.1098 | CRIVELLO- 4176 / 831-682-1912: same | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0080173 | OH | Sus | 43466644 | No | 2018 | SEP | Yes | Line to Ground | 1378395 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | TRIP-SAVER | 7603 | 20180923 | 818 | 179710 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 4870 | 37.0844 | -122.0048 | 500 SAND HILL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0082521 | OH | Sus | 43487277 | No | 2018 | SEP | Yes | Line to Ground | 1380061 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 3649 | 20180923 | 638 | 179682 | 334 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2672 | 36.9864 | -121.8507 | 2 SPANS SOUTH OF 3649 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0082486 | OH | Sus | 43487270 | No | 2018 | SEP | Yes | Line to Ground | 1380056 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | OTHER | WIRE DOWN @ 37400 PALO COLORADO CYN | 20181004 | 523 | 187929 | 412 | Distribution Circuit | Equipment Failure/Involved | Overhead | 140 | 51116 | 36.3956 | -121.8802 | 37400 PALO COLORADO RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0086557 | OH | Sus | 43496343 | yes | 2018 | OCT | Yes | Line to Ground | 1382935 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12758 | 20181007 | 1232 | 190216 | 1091 | Distribution Circuit | Vegetation | Tree - fell into line | 295 | 102773 | 37.1486 | -122.1748 | 3 SP SOURCE SIDE OF 12431 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0087918 | OH | Sus | 0 | yes | 2018 | OCT | Yes | Line to Ground | 1383855 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10786 | 20181007 | 1531 | 190364 | 623 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 28781 | 37.0926 | -122.097 | NYSTROM-ERIK-1058/408-799-8799: Near 10880 Alba Rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0087967 | OH | Sus | 43498463 | yes | 2018 | OCT | Yes | Multi-Fault | 1383879 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER | WIRE DOWN 2 LD SIDE OF 11919 | 20181007 | 1125 | 190224 | 395 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 6819 | 37.0697 | -122.016 | WIRE DOWN 2 LD SIDE OF 11919 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0087920 | OH | Sus | 43498404 | yes | 2018 | OCT | Yes | Line to Ground | 1383857 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 7289 | 20181008 | 631 | 190649 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 6566 | 37.1709 | -122.1805 | 723 LODGE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0088084 | OH | Sus | 0 | No | 2018 | OCT | Yes | None | 1384010 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 2863 | 20181008 | 735 | 190597 | 573 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 12606 | 36.5229 | -121.9255 | 3 SPANS LD SIDE OF 8387 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0088140 | OH | Sus | 31411778 | No | 2018 | OCT | Yes | Line to Ground | 1384062 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | FUSE | 1295 | 20181028 | 850 | 203653 | 623 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 3046 | 36.3795 | -121.8611 | MTR#1008503468 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0094889 | OH | Sus | 43518633 | No | 2018 | OCT | Yes | Force Out | 1388741 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6711 | 20181028 | 1606 | 203885 | 874 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 18677 | 36.998 | -121.8689 | 3 SPAN SS OF 4491 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0094949 | OH | Sus | 0 | No | 2018 | OCT | Yes | Line to Ground | 1388774 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | TRIP-SAVER | 5753 | 20181101 | 1355 | 207067 | 434 | Distribution Circuit | Vegetation | Tree - branch fell on line | 344 | 55396 | 37.0019 | -122.0379 | WELSH- MARK: KNIGHT TEMPLAR WAY | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0096452 | OH | Sus | 31414719 | No | 2018 | NOV | Yes | Line to Ground | 1389882 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 2631 | 20181110 | 1331 | 213027 | 741 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1482 | 37.0469 | -121.9839 | 1 SP SS 4991 BRANCIFORTE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0098856 | OH | Sus | 31415589 | No | 2018 | NOV | Yes | Line to Ground | 1391927 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | OTHER | 8137 | 20181114 | 822 | 214937 | 1237 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 8982 | 37.0581 | -121.9803 | at METER # 1007853897 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0099642 | OH | Sus | 0 | No | 2018 | NOV | Yes | Line to Ground | 1392562 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8397 | 20181117 | 1938 | 217527 | 1108 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 11080 | 37.0796 | -122.1395 | 65 COMSTOCK | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0100730 | OH | Sus | 43560092 | No | 2018 | NOV | Yes | Line to Line | 1393291 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 7807 | 20181120 | 1833 | 219398 | 437 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 5074 | 36.9884 | -121.7395 | RANGEL-4015 / 831-682-1816: 46 VALLEY VIEW | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0101634 | OH | Sus | 43577352 | No | 2018 | NOV | Yes | Force Out | 1393917 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | TRANSFORMER | 315821519850 | 20181122 | 1433 | 222109 | 1535 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1535 | 37.0362 | -121.9322 | CRIVELLO- 4176 / 831-682-1912: same | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 18-0102371 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1394523 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | JUMPER | WIRE DWN 2 LD SIDE OF 10175 | 20181122 | 1645 | 222330 | 695 | Distribution Circuit | Vegetation | Tree - fell into line | 678 | 204989 | 37.0441 | -122.1531 | 2 LD SIDE OF 10175 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102403 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1394555 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5617 | 20181123 | 16 | 222470 | 735 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 6615 | 37.0986 | -122.0533 | 2 SP LD SIDE 5617 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102456 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1394610 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5203 | 20181123 | 1522 | 223035 | 1458 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 39366 | 37.0394 | -122.0817 | 4 SP LD SIDE 5203 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102642 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1394736 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | FUSE | 5209 | 20181123 | 2152 | 223230 | 861 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 17220 | 37.0372 | -122.0723 | 420 BROOKESIDE | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102717 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Line | 1394809 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2667 | 20181124 | 732 | 223468 | 702 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4212 | 37.0261 | -121.775 | 6 SPAN LD SIDE OF 2667///1079 HAZEL DELL RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102782 | OH | Sus | 0 | No | 2018 | NOV | Yes | Line to Ground | 1394864 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1101 | 182291101 | FUSE | 6301 | 20181124 | 749 | 223478 | 416 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 832 | 36.5434 | -121.8847 | 3 SPANS LD OF 8171 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102765 | OH | Sus | 0 | No | 2018 | NOV | Yes | Line to Line | 1394847 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | FUSE | 5217 | 20181128 | 2110 | 226966 | 1073 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 16095 | 37.0374 | -122.0662 | 3 SPANS LD SIDE OF FUCO 5217 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104641 | OH | Sus | 43586641 | yes | 2018 | NOV | Yes | Line to Ground | 1395955 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8505 | 20181130 | 1030 | 230136 | 330 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 1320 | 37.176 | -122.2197 | S SPANS LD SIDE OF 8505 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105555 | OH | Sus | 43586641 | yes | 2018 | NOV | Yes | Line to Ground | 1396576 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | JUMPER | OJ'S 1 SPAN EAST OF 2667 | 20181207 | 556 | 235444 | 434 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 2604 | 37.026 | -121.7748 | BETWEEN 6649 AND 2667 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0107793 | OH | Sus | 43607259 | No | 2018 | DEC | Yes | Line to Ground | 1398128 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN BENITO-2104 | 182742104 | FUSE | 775 | 20181209 | 519 | 236526 | 538 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2152 | 36.8875 | -121.6273 | 2ND SPAN BEYOND 775 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0108138 | OH | Sus | 31418060 | No | 2018 | DEC | Yes | Line to Ground | 1398526 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | RESERVATION ROAD-1101 | 182731101 | RECLOSER | 3026 | 20181214 | 659 | 239805 | 235 | Distribution Circuit | Animal | Bird found | 710 | 73553 | 36.5787 | -121.7199 | 1 SPAN SS/OF 24851 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0109120 | OH | Sus | 43615382 | yes | 2018 | DEC | Yes | Line to Ground | 1399567 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | FUSE | 5215 | 20181216 | 1928 | 241738 | 877 | Distribution Circuit | Vegetation | Tree - branch fell on line | 60 | 52620 | 37.0325 | -122.0765 | 950 Scenic DR | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0109585 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Line | 1400216 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 2321 | 20181216 | 1919 | 241729 | 1571 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 31610 | 37.005 | -121.8623 | MTR# 1006890686 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0109651 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Line | 1400327 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 5166 | 20181216 | 2215 | 241829 | 933 | Distribution Circuit | Vegetation | Tree - fell into line | 269 | 249654 | 36.9818 | -121.901 | 2 SPANS LD SIDE OF LR 5166 (PER T-MAN/ODT 200 CATHEDRAL DR) | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0109563 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Ground | 1400195 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 9535 | 20181217 | 2250 | 242746 | 985 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2955 | 37.0235 | -121.9894 | 2 SPANS LD OF FUSES 9535 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0109802 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Line | 1400479 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8427 | 20181217 | 155 | 241987 | 847 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 41503 | 37.0769 | -121.9812 | 3 SPAN LD SIDE OF 8427 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0109592 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Line | 1400232 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 6053 | 20181217 | 513 | 242071 | 674 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 44484 | 37.1033 | -121.9881 | CAPWELL - 3915 / 831-206-1280: 3850 GLENWOOD DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0109642 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Ground | 1400316 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 6605 | 20181221 | 724 | 244898 | 484 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3388 | 37.013 | -121.7519 | 1 SPAN BEYOND 500 HIDDEN VALLEY | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110262 | OH | Sus | 43620850 | No | 2018 | DEC | Yes | Line to Ground | 1401274 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 2815 | 20181224 | 757 | 246043 | 257 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1542 | 37.0536 | -121.9785 | 215 WILDFLOWER LANE- SCOTTS VALLEY | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110445 | OH | Sus | 43621563 | yes | 2018 | DEC | Yes | Line to Ground | 1401522 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | TRIP-SAVER | 6577 | 20181225 | 343 | 246971 | 1221 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 58608 | 37.048 | -121.8081 | 2026 UPPER HIGHLAND | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110646 | OH | Sus | 0 | No | 2018 | DEC | Yes | Line to Line | 1401728 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 3459 | 20181225 | 352 | 246974 | 708 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 30651 | 37.0246 | -121.8841 | 10 SPANS SS 9271 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110615 | OH | Sus | 0 | No | 2018 | DEC | Yes | Line to Ground | 1401696 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | RESERVATION ROAD-1102 | 182731102 | FUSE | 24517 | 20181226 | 1019 | 247409 | 221 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1977 | 36.659 | -121.7373 | at SW 3295- BLANCO RD W/O COOPER | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0110720 | OH | Sus | 43621869 | No | 2018 | DEC | Yes | Line to Ground | 1401817 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 3499 | 20181226 | 837 | 247331 | 1803 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 3606 | 37.0269 | -121.8803 | at 3499 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on object | 18-0110703 | OH | Sus | 43621867 | No | 2018 | DEC | Yes | Line to Ground | 1401790 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | JUMPER | WIRE DOWN @MTR#1008503667 | 20181227 | 1914 | 248468 | 1226 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2452 | 36.2314 | -121.7546 | WIRE DOWN at MTR#1008503667 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110878 | OH | Sus | 0 | No | 2018 | DEC | Yes | Line to Ground | 1402035 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | GREEN VALLEY-2101 | 83192101 | FUSE | 12347 | 20181228 | 1928 | 249079 | 380 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 3154 | 37.0056 | -121.7695 | PRIMARY NEUT WIRE DOWN at 6287 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110989 | OH | Sus | 43623206 | No | 2018 | DEC | Yes | Force Out | 1402190 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 9423 | 20181231 | 1323 | 250613 | 1427 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 26500 | 37.077 | -122.0861 | Medeiros- Mike / 559-580-5006: crest and flintlock | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0111316 | OH | Sus | 43624004 | yes | 2018 | DEC | Yes | Multi-Fault | 1402575 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | FUSE | 8985 | 20181231 | 1428 | 251113 | 1624 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 37352 | 37.0291 | -122.1406 | 28871 SMITH GRADE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0111311 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Line | 1402569 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 5365 | 20181231 | 1050 | 250292 | 1865 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 41030 | 36.9946 | -122.0283 | 33 HOLLINS DR | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0111253 | OH | Sus | 31420283 | yes | 2018 | DEC | Yes | Force Out | 1402507 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 1157 | 20181231 | 1025 | 250244 | 504 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1512 | 37.0181 | -121.8208 | 2 SPANS LD SIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0111223 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Line | 1402471 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 3649 | 20181231 | 1458 | 251107 | 1381 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 11048 | 36.9864 | -121.8507 | WELSH- MARK: 5803 FREEDOM BLVD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0111309 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Ground | 1402566 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 6187 | 20190101 | 949 | 251366 | 495 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 10890 | 36.5676 | -121.9288 | AT CGC 411401346264 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0003419 | OH | Sus | 0 | No | 2019 | JAN | Yes | Line to Ground | 1402620 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 11929 | 20190105 | 1430 | 254325 | 389 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 39289 | 37.0999 | -122.0343 | 2 SPANS LD SIDE OF 11929 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0004864 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Multi-Fault | 1403401 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 7805 | 20190107 | 226 | 258505 | 874 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1748 | 37.2145 | -122.1489 | 3 SPANS LD SIDE | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005602 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1404055 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | FUSE | 5215 | 20190107 | 1216 | 259376 | 389 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 23340 | 37.0325 | -122.0765 | AT MTR 1008738413 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005870 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1404230 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | RECLOSER | 5178 | 20190107 | 53 | 258437 | 1147 | Distribution Circuit | Vegetation | Tree - fell into line | 267 | 306249 | 37.0326 | -121.9462 | AT C/OUTS 7347 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0005561 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Three Phase Fault | 1404011 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 4371 | 20190107 | 503 | 258802 | 1827 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 12789 | 36.9796 | -121.8656 | 3 SPANS LD SIDE OF 4371 | Overcast-Fog-32-90 F | Conductor, Overhead | On Ground | 19-0005709 | OH | Sus | 43625150 | yes | 2019 | JAN | Yes | Multi-Fault | 1404119 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 5819 | 20190107 | 1606 | 259355 | 279 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2511 | 37.0447 | -121.8131 | PN DOWN at 1605 EUREKA CANYON RD | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005978 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Force Out | 1404285 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | JUMPER | WIRE DWN MTR#1010292732 | 20190107 | 1955 | 259903 | 1002 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 4828 | 37.0366 | -121.8031 | WIRE DWN MTR#1010292732 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0006063 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1404375 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 9423 | 20190108 | 2339 | 261107 | 566 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 15848 | 37.077 | -122.0861 | MTR#1009207148 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0006620 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1404702 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 688471 | 20190108 | 2341 | 261194 | 623 | Distribution Circuit | Vegetation | Tree - bark fell into line | 17 | 10591 | 37.1094 | -122.11 | 3 SAPNS LD SIDE OF 688471 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0006626 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1404708 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 11867 | 20190108 | 906 | 260237 | 209 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 5434 | 37.1248 | -122.1265 | CGC# 315260623119 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0006212 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1404461 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2029 | 20190108 | 831 | 260188 | 89 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 801 | 37.0154 | -121.7543 | 2 SPANS S/S OF 6606 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0006111 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1404411 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | TRIP-SAVER | 8403 | 20190109 | 30 | 261218 | 672 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 32388 | 37.1548 | -122.1333 | 22 SPANS LD SIDE OF 8259 | Overcast-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0006634 | OH | Sus | 31420594 | yes | 2019 | JAN | Yes | Line to Ground | 1404717 | CAW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | TRIP-SAVER | 2253 | 20190109 | 300 | 261214 | 625 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5138 | 37.1711 | -122.1653 | NYSTROM-ERIK-1058/408-799-8799: Private Rd last driveway on China Grade Rd | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0006673 | OH | Sus | 31420594 | yes | 2019 | JAN | Yes | Line to Line | 1404744 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8365 | 20190109 | 905 | 261516 | 875 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 20903 | 37.1824 | -122.2074 | at METER # 1009129482 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0006784 | OH | Sus | 31420594 | yes | 2019 | JAN | Yes | Line to Ground | 1404839 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2667 | 20190109 | 1323 | 261744 | 292 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1752 | 37.0261 | -121.775 | 1 SPAN LOAD SIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0007042 | OH | Sus | 43625150 | yes | 2019 | JAN | Yes | Multi-Fault | 1404901 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | 7123 | 20190111 | 607 | 262986 | 321 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 3531 | 37.0655 | -122.0579 | NYSTROM-ERIK-1058/408-799-8799: 2nd span Moonmeadow at W Zayantee | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0007810 | OH | Sus | 31421391 | No | 2019 | JAN | Yes | Open Circuit | 1405464 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | SEACLIFF-0401 | 83500401 | FUSE | 6007 | 20190113 | 1101 | 264241 | 143 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 7436 | 37.0028 | -121.9273 | 5 SPAN LD SIDE OF 6007 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0008362 | OH | Sus | 0 | No | 2019 | JAN | Yes | Force Out | 1405937 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 10457 | 20190114 | 848 | 264639 | 597 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 9552 | 37.1087 | -122.046 | NYSTROM-ERIK-1058/408-799-8799: Volver and Coleman | Overcast-Drizzle-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0008700 | OH | Sus | 43634788 | yes | 2019 | JAN | Yes | Line to Ground | 1406211 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 6465 | 20190114 | 926 | 264702 | 362 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 362 | 37.0543 | -122.1694 | 3 SPAN LD SIDE OF 6465 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0008576 | OH | Sus | 31421971 | yes | 2019 | JAN | Yes | Line to Ground | 1406115 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5901 | 20190115 | 1019 | 265525 | 463 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 4088 | 37.0945 | -121.9715 | 4 SPAN LD SIDE OF 11237 FUSES | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009117 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Multi-Fault | 1406348 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 11010 | 20190115 | 1751 | 266196 | 354 | Distribution Circuit | Equipment Failure/Involved | Overhead | 123 | 33010 | 37.1053 | -122.0518 | 11033 SEQUOIA DR | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009276 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406411 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | SWITCH | 473 | 20190115 | 1441 | 265942 | 527 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 20977 | 36.5036 | -121.9378 | 2 SPANS LOAD SIDE 473 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009254 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Force Out | 1406401 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | JUMPER | WIRE DOWN | 20190115 | 1138 | 265585 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 7803 | 36.4146 | -121.9113 | 1 SPAN LOAD SIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009175 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406377 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2166 | 20190115 | 1533 | 265790 | 1124 | Distribution Circuit | Vegetation | Tree - branch fell on line | 476 | 468584 | 36.2769 | -121.8264 | 2 SPANS LD SIDE OF 6591 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009206 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406393 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6711 | 20190115 | 1839 | 266256 | 950 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 46550 | 36.998 | -121.8689 | 2400 Valencia Rd | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009357 | OH | Sus | 31422113 | yes | 2019 | JAN | Yes | Line to Line | 1406478 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 495039 | 20190115 | 1601 | 266021 | 404 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 15756 | 36.5692 | -121.912 | 3 SPANS LD SIDE OF 495039 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009284 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1406415 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8505 | 20190118 | 1743 | 276164 | 1662 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 6648 | 37.176 | -122.2197 | 3 SP LS 8505 | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 19-0011950 | OH | Sus | 43639876 | yes | 2019 | JAN | Yes | Line to Ground | 1408287 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 8405 | 20190118 | 1658 | 276130 | 1187 | Distribution Circuit | Vegetation | Tree - branch fell on line | 44 | 52228 | 36.5791 | -121.8688 | 8/SPANS LD SIDE OF 8405 | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 19-0011949 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408286 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | OTHER | WIRE DOWN @ CGC 315436820043 | 20190118 | 924 | 275692 | 1741 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 13601 | 37.0397 | -122.0644 | CGC 315436820043 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011729 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408180 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | FUSE | 1295 | 20190118 | 1129 | 275679 | 1499 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 20986 | 36.3795 | -121.8611 | RODRIGUEZ LOU 5809/ 233-0361: meter #1010313846 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011754 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1408196 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 709 | 20190118 | 1028 | 275554 | 653 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1306 | 37.0518 | -122.1608 | 2 SPANS LD SIDE OF FUCO 709 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011864 | OH | Sus | 31422113 | yes | 2019 | JAN | Yes | Line to Line | 1408243 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 2145 | 20190118 | 1336 | 276036 | 1227 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6135 | 36.5682 | -121.9289 | 3/P/W OF 2145 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011912 | OH | Sus | 43639873 | yes | 2019 | JAN | Yes | Line to Ground | 1408259 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1101 | 182291101 | FUSE | 8171 | 20190119 | 1135 | 276663 | 360 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 720 | 36.5448 | -121.8847 | 4 SP LS 8171 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012138 | OH | Sus | 43640846 | yes | 2019 | JAN | Yes | Line to Line | 1408484 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | RECLOSER | 10912 | 20190120 | 1019 | 277199 | 733 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 16622 | 37.0913 | -122.096 | 1 SPAN S/S OF 4709 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012533 | OH | Sus | 31422651 | yes | 2019 | JAN | Yes | Line to Ground | 1408879 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 2487 | 20190129 | 1458 | 283439 | 75 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 1350 | 37.0456 | -122.1099 | 1 SPAN LD SIDE OF 2487 | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 19-0015630 | OH | Sus | 0 | No | 2019 | JAN | Yes | Force Out | 1410632 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5203 | 20190201 | 2109 | 285729 | 1378 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 37206 | 37.0394 | -122.0817 | 4 SPANS LD SIDE | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016813 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411272 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8503 | 20190203 | 1240 | 288853 | 1413 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2826 | 37.1711 | -122.2183 | 2 SP S/OF 77767 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017536 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1411944 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | RECLOSER | 11056 | 20190203 | 1458 | 289025 | 693 | Distribution Circuit | Vegetation | Tree - fell into line | 452 | 78561 | 36.9937 | -122.0299 | 1/S LD SIDE 5789 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017584 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411997 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2105 | 182222105 | FUSE | 8167 | 20190203 | 1252 | 288869 | 351 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 5616 | 36.58 | -121.9517 | at 2077 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017580 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411995 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | FELTON-0401 | 83140401 | FUSE | 11967 | 20190203 | 900 | 288631 | 300 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 9300 | 37.0289 | -122.0724 | 1949 UPPER SENIEC DR | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0017506 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1411921 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | RECLOSER | 9698 | 20190203 | 408 | 288414 | 2229 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 29661 | 36.5726 | -121.9437 | 3 POLES N/E OF 9698 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017421 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411836 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 2453 | 20190203 | 48 | 288327 | 2247 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 14721 | 36.5723 | -121.9397 | 2 SP LD SIDE MTR#1009260665 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017518 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411930 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12992 | 20190206 | 1216 | 294268 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 689 | 99263 | 37.1987 | -122.1536 | WIRE DOWN ON THE MAIN LINE ON BOTH SIDES at 9579 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0019162 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413162 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 6113 | 20190206 | 1508 | 294483 | 1327 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 5308 | 36.3825 | -121.5354 | 3 SPANS LD SIDE | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0019262 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413223 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2002 | 20190208 | 2249 | 296636 | 2466 | Distribution Circuit | Environmental/External | Lightning | 123 | 166677 | 36.2249 | -121.7589 | 4 SPANS LD SIDE OF 1375 | Partly Cloudy-Drizzle-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020168 | OH | Sus | 31425082 | yes | 2019 | FEB | Yes | Line to Ground | 1413855 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5901 | 20190218 | 1418 | 317773 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 10557 | 37.0945 | -121.9715 | 11 POLES SS 11237 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025719 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418765 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | OCB | 2203/2 | 20190218 | 709 | 317179 | 538 | Distribution Circuit | Vegetation | Tree - fell into line | 5458 | 216140 | 36.5786 | -121.9085 | CARPENTER at LOWER TRAIL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025532 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418588 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8247 | 20190221 | 1034 | 320492 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2560 | 37.1194 | -121.9775 | 23640 GLENWOOD | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0026926 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1419457 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 1939 | 20190222 | 138 | 321037 | 659 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1977 | 36.9838 | -121.8311 | 3 SPAN LD OF FUSES 1939 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0027140 | OH | Sus | 0 | No | 2019 | FEB | Yes | Line to Line | 1419561 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 9949 | 20190222 | 149 | 321050 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 25792 | 37.016 | -121.8207 | 5 SPANS FROM RYDER RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0027148 | OH | Sus | 0 | No | 2019 | FEB | Yes | Line to Ground | 1419572 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 495039 | 20190228 | 21 | 327671 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 22113 | 36.5692 | -121.912 | 4 SPANS LOAD SIDE | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029217 | OH | Sus | 43687038 | yes | 2019 | FEB | Yes | Line to Line | 1420966 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | JUMPER | OPEN JUMPERS 1 SPAN SS 8257 | 20190302 | 1402 | 329683 | 1005 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 18090 | 37.1534 | -122.1317 | 1 SPAN SS 8257 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0030101 | OH | Sus | 31427226 | yes | 2019 | MAR | Yes | Line to Ground | 1421561 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 2643 | 20190303 | 512 | 329976 | 743 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 10590 | 37.0233 | -121.8836 | MTR 10009786949 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0030226 | OH | Sus | 31427241 | No | 2019 | MAR | Yes | Multi-Fault | 1421684 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8503 | 20190306 | 948 | 332574 | 467 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 934 | 37.1711 | -122.2183 | 4 SPANS LD SIDE OF 77767 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031221 | OH | Sus | 43690325 | yes | 2019 | MAR | Yes | Line to Line | 1422279 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 97411 | 20190306 | 706 | 332410 | 679 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 14259 | 37.1824 | -122.2074 | MTR: 1009129462 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031227 | OH | Sus | 43690325 | yes | 2019 | MAR | Yes | Line to Line | 1422285 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12992 | 20190306 | 1211 | 332765 | 905 | Distribution Circuit | Vegetation | Tree - fell into line | 689 | 145553 | 37.1987 | -122.1536 | NYSTROM-ERIK-1058/408-799-8799: McGaffigan Mill at Hwy 9 | Partly Cloudy-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0031275 | OH | Sus | 31427522 | yes | 2019 | MAR | Yes | Line to Line | 1422308 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 11929 | 20190306 | 452 | 332429 | 664 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 66170 | 37.0999 | -122.0343 | 2 SPANS LD SIDE OF 6161 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031155 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1422229 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 8949 | 20190306 | 1541 | 333076 | 387 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4644 | 36.5009 | -121.9335 | CGC 411385843872 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031458 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1422395 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HOLLISTER-2105 | 182492105 | FUSE | 4893 | 20190306 | 453 | 332140 | 487 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 13636 | 36.4896 | -121.1509 | 1 SP LD SIDE OF 4893 | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031073 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1422183 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | RECLOSER | 440 | 20190306 | 53 | 332086 | 966 | Distribution Circuit | Vegetation | Tree - fell into line | 372 | 336420 | 36.4379 | -121.9198 | MULITABLE LOCATIONS N/OF C/OUT 40411 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0031050 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Multi-Fault | 1422161 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | FUSE | 1295 | 20190306 | 458 | 332181 | 536 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 7504 | 36.3795 | -121.8611 | CGC 411620939322 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031201 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Line | 1422265 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | JUMPER | WIRE DOWN 1 SPAN S/S OF 315816820041 | 20190306 | 1302 | 332832 | 501 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 1861 | 37.0409 | -121.9357 | 1 SPAN S/S OF CGC # 315816820041 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031413 | OH | Sus | 43690325 | yes | 2019 | MAR | Yes | Line to Ground | 1422366 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 7371 | 20190306 | 438 | 332166 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2510 | 37.0586 | -122.142 | 8 POLES LD OF FUSEES 7371 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031225 | OH | Sus | 43690325 | yes | 2019 | MAR | Yes | Line to Line | 1422283 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | TRIP-SAVER | 8403 | 20190308 | 424 | 334051 | 529 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 36828 | 37.1548 | -122.1333 | 18TH AND 19TH SP L/S OF 8259 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031929 | OH | Sus | 31427655 | No | 2019 | MAR | Yes | Line to Ground | 1422717 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 6295 | 20190310 | 420 | 335354 | 317 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 10144 | 37.0992 | -122.0867 | at 5143 | Partly Cloudy-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0032383 | OH | Sus | 0 | No | 2019 | MAR | Yes | Line to Ground | 1423053 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | SEACLIFF-0401 | 83500401 | OTHER | WIRE DOWN @6500 PRESCOTT RD | 20190310 | 1708 | 335652 | 516 | Distribution Circuit | Vegetation | Tree - branch fell on line | 52 | 21273 | 37.0122 | -121.927 | 6500 PRESCOTT RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0032449 | OH | Sus | 43698701 | No | 2019 | MAR | Yes | Line to Ground | 1423126 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 8021 | 20190310 | 1621 | 335608 | 516 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 42828 | 36.5868 | -121.9096 | 7 SPANS LD SIDE TREE CAUSE WIRE DOWN | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0032440 | OH | Sus | 31428214 | No | 2019 | MAR | Yes | Line to Ground | 1423119 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12758 | 20190312 | 1548 | 337517 | 885 | Distribution Circuit | Vegetation | Tree - fell into line | 295 | 119691 | 37.1486 | -122.1748 | MAIN LINE AT TAP 9353 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033128 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Line | 1423606 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | FUSE | 465 | 20190312 | 2205 | 338036 | 1120 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1120 | 36.3038 | -121.876 | 2 SPANS FROM EOL | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0033246 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1423707 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 1445 | 20190312 | 1623 | 337575 | 711 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 7110 | 36.5735 | -121.9107 | 3 SPANS L/S OF 1445 | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033244 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Line | 1423705 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 5149 | 20190313 | 1646 | 338793 | 740 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3700 | 37.1109 | -122.0899 | 2 SPANS L/S OF FUSES | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033623 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1423964 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER | WIRE DOWN 1 SP SS OF CGC 315295525380 | 20190313 | 628 | s1423966 | 867 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 867 | 37.1851 | -122.1173 | 1 SPAN S/S OF CGC# 315295525380 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033627 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1423966 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 2871 | 20190313 | 736 | 338168 | 749 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2247 | 36.5708 | -121.8886 | 3 SPANS L/S OF FUSES 2871 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033360 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1423820 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | SWITCH | 6115 | 20190318 | 710 | 341782 | 294 | Distribution Circuit | Vegetation | Tree - branch fell on line | 78 | 22932 | 37.0067 | -121.9016 | AT MTR 1009258961 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0034578 | OH | Sus | 31429508 | No | 2019 | MAR | Yes | Multi-Fault | 1424770 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8503 | 20190320 | 855 | 343681 | 275 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 550 | 37.1711 | -122.2183 | 4 SPANS LOAD SIDE | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0035299 | OH | Sus | 43711938 | yes | 2019 | MAR | Yes | Multi-Fault | 1425264 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER | WIRE DOWN @ SBCO 327 | 20190326 | 125 | 347329 | 833 | Distribution Circuit | Vegetation | Tree - fell into line | 295 | 57833 | 37.1501 | -122.1729 | 327 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0036882 | OH | Sus | 0 | No | 2019 | MAR | Yes | Force Out | 1426294 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 5781 | 20190328 | 1843 | 349829 | 724 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 6516 | 37.0448 | -121.8145 | 2 SP LS 5781 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0038120 | OH | Sus | 43721320 | yes | 2019 | MAR | Yes | Line to Ground | 1427067 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | OTHER | WIRE DOWN 7 SP LS OF 4431 | 20190328 | 2216 | 349903 | 351 | Distribution Circuit | Equipment Failure/Involved | Overhead | 99 | 34289 | 37.0227 | -121.82 | BRANDT- 4179 / 831-212-2088: 7 Spns LS 4431 pole # 120763263 line broke connection | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0038151 | OH | Sus | 43721326 | yes | 2019 | MAR | Yes | Line to Ground | 1427096 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE | 8419 | 20190409 | 238 | 356189 | 726 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 30294 | 36.5692 | -121.7915 | 2 SP LS CGC#1008545792 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0040705 | OH | Sus | 43730348 | yes | 2019 | APR | Yes | Line to Line | 1428930 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2204 | 182852204 | FUSE | 7567 | 20190409 | 1713 | 357091 | 625 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 8657 | 36.5783 | -121.9039 | MTR# 1009849447 | Clear-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0041100 | OH | Sus | 31433182 | yes | 2019 | APR | Yes | Line to Ground | 1429195 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | FUSE | 10043 | 20190411 | 1514 | 359127 | 1026 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1026 | 37.1383 | -122.1437 | 5 SPANS LD SIDE OF 10043 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0041759 | OH | Sus | 43737402 | yes | 2019 | APR | Yes | Force Out | 1429737 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | TRIP-SAVER | 8403 | 20190411 | 1841 | 359274 | 421 | Distribution Circuit | Vegetation | Tree - branch fell on line | 141 | 59361 | 37.1548 | -122.1333 | MTR#1007591022 | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0041792 | OH | Sus | 31433922 | yes | 2019 | APR | Yes | Line to Ground | 1429769 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 7681 | 20190411 | 1800 | 359185 | 342 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3420 | 36.5832 | -121.865 | 1 SP LD SIDE OF 7481 | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0041786 | OH | Sus | 43737415 | yes | 2019 | APR | Yes | Line to Ground | 1429762 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | JUMPER | WIRE DWN 1007330019 | 20190413 | 1017 | 360185 | 540 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1080 | 37.1028 | -122.0956 | WIRE DWN 1007330019 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0042208 | OH | Sus | 43738600 | No | 2019 | APR | Yes | Line to Ground | 1430074 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2166 | 20190416 | 2205 | 362143 | 838 | Distribution Circuit | Vegetation | Tree - fell into line | 477 | 358776 | 36.2769 | -121.8264 | 7 SPAN LD SIDE OF 10441 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0043066 | OH | Sus | 31434463 | No | 2019 | APR | Yes | Three Phase Fault | 1430593 | CAW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1101 | 182291101 | FUSE | 8171 | 20190417 | 942 | 362386 | 557 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1114 | 36.5448 | -121.8847 | 5 POLES LD SIDE OF 8171 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0043431 | OH | Sus | 0 | No | 2019 | APR | Yes | Force Out | 1430888 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | TRIP-SAVER | 6577 | 20190422 | 218 | 365075 | 557 | Distribution Circuit | Vegetation | Tree - branch fell on line | 49 | 27293 | 37.048 | -121.8081 | at MTR#1008514310 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0044733 | OH | Sus | 43746648 | No | 2019 | APR | Yes | Line to Ground | 1431901 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | RECLOSER | 2020 | 20190504 | 1552 | 373766 | 1333 | Distribution Circuit | 3rd Party | Vehicle | 848 | 117011 | 36.4633 | -121.712 | CGC # 412162940222 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0048900 | OH | Sus | 0 | No | 2019 | MAY | Yes | Line to Line | 1434583 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 4259 | 20190509 | 52 | 376704 | 707 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4242 | 37.1674 | -122.187 | 7 SPANS L/S OF 4259 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0050204 | OH | Sus | 31439261 | yes | 2019 | MAY | Yes | Line to Ground | 1435464 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER | 9112 | 20190514 | 659 | 379827 | 251 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3136 | 109663 | 36.6048 | -121.9339 | HIGH SIDE OF FUCO 6961 | Overcast-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0051576 | OH | Sus | 43778001 | No | 2019 | MAY | Yes | Line to Ground | 1436474 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 6209 | 20190515 | 2042 | 381466 | 1068 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3204 | 37.1791 | -122.1392 | 6 SPANS LOAD SIDE | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052453 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Multi-Fault | 1437098 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | OCB | 2101/2 | 20190515 | 1601 | 381096 | 560 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 3460 | 37.0953 | -122.1437 | BOYNTON- 3459 / 831-331-6620: 12700 ALBA RD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052267 | OH | Sus | 43782777 | yes | 2019 | MAY | Yes | Line to Ground | 1436914 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5629 | 20190516 | 1537 | 382723 | 458 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 9160 | 37.1128 | -122.0481 | 123639 LOMPICO RD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052958 | OH | Sus | 43778603 | yes | 2019 | MAY | Yes | Line to Ground | 1437363 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 11929 | 20190518 | 1949 | 384633 | 456 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 45508 | 37.0999 | -122.0343 | 5/P/LD SIDE OF 5613 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053773 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Line | 1437985 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 6053 | 20190518 | 2239 | 384644 | 744 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 40224 | 37.1033 | -121.9881 | 2/SPANS LD SIDE 12527 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053822 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Line | 1438036 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | RECLOSER | 2020 | 20190518 | 1754 | 384421 | 1792 | Distribution Circuit | Equipment Failure/Involved | Overhead | 846 | 441476 | 36.4633 | -121.712 | 2 SPANS LD SIDE OF 6421 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053701 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1437917 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 11303 | 20190518 | 1612 | 384499 | 2949 | Distribution Circuit | 3rd Party | Vehicle | 6 | 16518 | 37.0303 | -121.7845 | MTR 1010426919 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0053720 | OH | Sus | 31442680 | yes | 2019 | MAY | Yes | Line to Ground | 1437933 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 11010 | 20190519 | 1414 | 385384 | 807 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 44901 | 37.1053 | -122.0518 | RANGEL-4015 / 831-682-1816: 661 WEST DR | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053970 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1438181 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER | WIRE DOWN 11130 ALBA | 20190519 | 1440 | 385421 | 1619 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 75725 | 37.0969 | -122.1072 | 11130 ALBA | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0054042 | OH | Sus | 43788296 | yes | 2019 | MAY | Yes | Line to Ground | 1438240 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5629 | 20190519 | 1653 | 385517 | 1157 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 20368 | 37.1128 | -122.0481 | 4 SPANS FROM EOL | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0054147 | OH | Sus | 43788967 | yes | 2019 | MAY | Yes | Line to Ground | 1438343 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | HATTON-1102 | 182291102 | FUSE | 1295 | 20190519 | 1111 | 385142 | 491 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 6874 | 36.3795 | -121.8611 | LOAD SIDE 1295 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053998 | OH | Sus | 43788289 | yes | 2019 | MAY | Yes | Line to Line | 1438205 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 6511 | 20190519 | 743 | 384928 | 755 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 81540 | 36.9714 | -121.8195 | CRIVELLO- 4176 / 831-682-1912: 15 white rd | Overcast-Heavy Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053900 | OH | Sus | 31442846 | yes | 2019 | MAY | Yes | Line to Ground | 1438110 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 2239 | 20190524 | 1420 | 389602 | 389 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3890 | 36.951 | -121.8324 | MTR 1008716453 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0056977 | OH | Sus | 43797242 | No | 2019 | MAY | Yes | Line to Ground | 1440457 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5477 | 20190526 | 1502 | 390852 | 338 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 17238 | 37.1291 | -122.1142 | 1 SPAN LD SIDE OF 5477 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0057807 | OH | Sus | 43798278 | No | 2019 | MAY | Yes | Line to Ground | 1441327 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | TRIP-SAVER | 9773 | 20190526 | 1502 | 390853 | 355 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 10295 | 37.1288 | -122.1141 | KELLY- 4017 / 831-682-1802: Jumper open that feed C/O 9773 and C/O 5477 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0057809 | OH | Sus | 0 | No | 2019 | MAY | Yes | Line to Ground | 1441329 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | SECTIONALIZER | 8655 | 20190526 | 1739 | 390944 | 365 | Distribution Circuit | Vegetation | Tree - fell into line | 178 | 7015 | 37.1402 | -122.0938 | 2 SPANS L/S OF 8655 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0057821 | OH | Sus | 0 | No | 2019 | MAY | Yes | Force Out | 1441339 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 4857 | 20190528 | 1030 | 391766 | 989 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 10879 | 37.0909 | -122.0948 | 2 POLES LD SIDE OF 4857 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0058499 | OH | Sus | 0 | No | 2019 | MAY | Yes | Line to Ground | 1441998 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2705 | 20190602 | 315 | 395598 | 270 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 6750 | 37.0005 | -121.7405 | 5 SPANS LD SIDE OF 2705 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0061474 | OH | Sus | 43813902 | yes | 2019 | JUN | Yes | Three Phase Fault | 1444332 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | RECLOSER | 2020 | 20190607 | 246 | 400307 | 723 | Distribution Circuit | Vegetation | Tree - fell into line | 847 | 76226 | 36.4633 | -121.712 | 4 SPANS LD SIDE OF 2949 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0064076 | OH | Sus | 31451931 | yes | 2019 | JUN | Yes | Line to Ground | 1446333 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | TRIP-SAVER | 6601 | 20190611 | 426 | 404973 | 609 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 21315 | 36.9941 | -121.7172 | 184 BELLA VISTA LN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0065831 | OH | Sus | 43838494 | yes | 2019 | JUN | Yes | Line to Ground | 1447933 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 6741 | 20190612 | 1618 | 407961 | 631 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4417 | 36.5716 | -121.8844 | 4 POLES L/S OF 6741 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0066930 | OH | Sus | 31453526 | yes | 2019 | JUN | Yes | Line to Ground | 1448622 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | OTHER | WIRE DOWN 56 ROBLEY RD | 20190613 | 11 | 408495 | 783 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1198 | 148986 | 36.5511 | -121.7352 | AT MTR # 1006195956 56 ROBLEY RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0067072 | OH | Sus | 31453032 | No | 2019 | JUN | Yes | Line to Ground | 1448747 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 11865 | 20190613 | 1435 | 409266 | 403 | Distribution Circuit | Equipment Failure/Involved | Overhead | 73 | 24895 | 37.001 | -121.7398 | 3 SPANS WEST OF 2029 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0067443 | OH | Sus | 0 | No | 2019 | JUN | Yes | Three Phase Fault | 1448951 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 3029 | 20190615 | 1741 | 415144 | 347 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 7856 | 36.9644 | -121.8173 | REAR OF 374 DUSTY TRAIL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0068099 | OH | Sus | 0 | No | 2019 | JUN | Yes | Line to Ground | 1449501 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 7799 | 20190616 | 1855 | 417074 | 660 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 40260 | 37.0909 | -122.1397 | 2 POLLES EAST OF 160 VIC DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0068415 | OH | Sus | 0 | No | 2019 | JUN | Yes | Force Out | 1449816 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10294 | 20190617 | 439 | 417189 | 603 | Distribution Circuit | Vegetation | Tree - fell into line | 430 | 172602 | 37.0992 | -122.0531 | SBCO 10423 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0068420 | OH | Sus | 43844848 | No | 2019 | JUN | Yes | Line to Ground | 1449821 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LOS OSITOS-2103 | 182082103 | RECLOSER | 7062 | 20190619 | 604 | 420904 | 2561 | Distribution Circuit | Equipment Failure/Involved | Overhead | 49 | 10849 | 36.2789 | -121.303 | METER 1008680172 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0069542 | OH | Sus | 31454692 | No | 2019 | JUN | Yes | Multi-Fault | 1450605 | CAW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 4403 | 20190622 | 1845 | 426535 | 1325 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 7 | 9275 | 36.9719 | -121.8437 | 1 SPAN FROM EOL AT TX 316068017513 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0071075 | OH | Sus | 43854760 | No | 2019 | JUN | Yes | Line to Ground | 1451906 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | RECLOSER | 2762 | 20190623 | 1534 | 426960 | 126 | Distribution Circuit | Vegetation | Tree - fell into line | 1198 | 105368 | 36.5581 | -121.7505 | 2SPANS S/S OF 3088 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0071254 | OH | Sus | 31455265 | No | 2019 | JUN | Yes | Line to Ground | 1452081 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER | OJ1 POLE LD SIDE 1007590530 | 20190625 | 1107 | 428483 | 688 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 688 | 37.159 | -122.1549 | 1 SPOLE LD SIDE OF 1007590530 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0071847 | OH | Sus | 43856479 | No | 2019 | JUN | Yes | Open Circuit | 1452599 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER | 65444 | 20190628 | 1737 | 434773 | 2546 | Distribution Circuit | Vegetation | Tree - fell into line | 769 | 548585 | 37.1278 | -122.1229 | Moore 3755 831-206-3524: Hwy 9 btwn Spring Creek & Kings Creek | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0073243 | OH | Sus | 31455796 | No | 2019 | JUN | Yes | Line to Ground | 1453474 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5629 | 20190701 | 1631 | 439359 | 713 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 11150 | 37.1128 | -122.0481 | 13095 LOMPIC RD- 14 POLES LD SIDE OF 5629 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0073775 | OH | Sus | 43863989 | No | 2019 | JUL | Yes | Line to Ground | 1453921 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 5335 | 20190702 | 701 | 439572 | 500 | Distribution Circuit | Equipment Failure/Involved | Overhead | 74 | 37000 | 37.0281 | -121.9871 | at 7213 POLE | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0073912 | OH | Sus | 0 | No | 2019 | JUL | Yes | Line to Ground | 1454046 | CAW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 7773 | 20190709 | 826 | 443296 | 1024 | Distribution Circuit | 3rd Party | Vehicle | 34 | 34816 | 37.1882 | -122.1579 | 3 SPANS & 80 SOUTH STELLER WAY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0075577 | OH | Sus | 43870602 | No | 2019 | JUL | Yes | Line to Ground | 1455004 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 8949 | 20190709 | 1016 | 443468 | 429 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5148 | 36.5009 | -121.9335 | 4 SPANS LOAD SIDE 8949 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0075592 | OH | Sus | 31456747 | No | 2019 | JUL | Yes | Multi-Fault | 1455016 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND SUB | 8304 | OCB | 401/2 | 20190716 | 1713 | 454751 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 759 | 215579 | 37.0923 | -122.0965 | BARGAS -1496 / 831-682-1830: glen arbor and riverside at solid blades 13005 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0078088 | OH | Sus | 31457643 | No | 2019 | JUL | Yes | Line to Ground | 1456646 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9725 | 20190717 | 1944 | 456900 | 498 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 13446 | 37.1522 | -122.1366 | CGC 315228524196 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0078593 | OH | Sus | 43887973 | No | 2019 | JUL | Yes | Line to Ground | 1456967 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | OTHER | WIRE DOWN 3P/SS/ OF 8527 | 20190721 | 1234 | 465041 | 971 | Distribution Circuit | Vegetation | Tree - fell into line | 814 | 89102 | 37.0522 | -122.154 | 3P/SS/OF 8527 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0079583 | OH | Sus | 31459408 | No | 2019 | JUL | Yes | Line to Ground | 1457692 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 8895 | 20190722 | 441 | 465289 | 478 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 23472 | 36.5891 | -121.9104 | 2 SPANS LD OF 8895 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0079678 | OH | Sus | 43893056 | No | 2019 | JUL | Yes | Line to Line | 1457747 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 2745 | 20190729 | 1417 | 474803 | 988 | Distribution Circuit | 3rd Party | Vehicle | 74 | 50710 | 36.4707 | -121.7259 | CALLE DE LOS AGRIMENSORS / CAMINO DE TRAVESIA | Clear-32-90 F | Pole-Wood | Broken, wire on object | 19-0082264 | OH | Sus | 0 | No | 2019 | JUL | Yes | Force Out | 1459453 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | TRIP-SAVER | 8403 | 20190801 | 1649 | 477428 | 578 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 25745 | 37.1548 | -122.1333 | 2 POLES SOUTH OF 9109 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0083592 | OH | Sus | 31460728 | No | 2019 | AUG | Yes | Line to Line | 1460228 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | OCB | 2103/2 | 20190804 | 656 | 482308 | 398 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2558 | 271451 | 36.5851 | -121.8743 | FUCO 8557 TO 1 SPAN WEST | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0084129 | OH | Sus | 43908368 | No | 2019 | AUG | Yes | Line to Ground | 1460688 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE | 5835 | 20190806 | 1543 | 487363 | 482 | Distribution Circuit | 3rd Party | Vehicle | 61 | 6209 | 36.5695 | -121.7532 | AT METER 1008985758 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0084968 | OH | Sus | 43910430 | No | 2019 | AUG | Yes | Line to Ground | 1461176 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN JUSTO-1101 | 183181101 | FUSE | 4245 | 20190810 | 1513 | 501414 | 338 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 7227 | 36.8938 | -121.5973 | 2956 anzar | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0086572 | OH | Sus | 43918273 | yes | 2019 | AUG | Yes | Line to Ground | 1462132 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | JUMPER | WIRE DOWN SS OF CGC 315538321710 | 20190814 | 1209 | 509973 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 406 | 37.0866 | -122.0283 | 2800 LOCKHART GULCH RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0087961 | OH | Sus | 0 | yes | 2019 | AUG | Yes | Open Circuit | 1463086 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 5459 | 20190817 | 58 | 519040 | 647 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 18116 | 37.1385 | -122.1432 | 450 HAZEL BREAK | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0089024 | OH | Sus | 31462794 | No | 2019 | AUG | Yes | Line to Ground | 1463780 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 9783 | 20190820 | 1303 | 525911 | 778 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 10492 | 37.1573 | -122.1336 | MTR# 1007590196 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0090038 | OH | Sus | 0 | No | 2019 | AUG | Yes | Line to Line | 1464603 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN BENITO-2104 | 182742104 | RECLOSER | 88772 | 20190822 | 1432 | 532493 | 494 | Distribution Circuit | Vegetation | Tree - branch fell on line | 135 | 15236 | 36.904 | -121.6087 | WELSH- MARK 831-359-3166: HWY 129 X ROGGE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0091049 | OH | Sus | 31467068 | No | 2019 | AUG | Yes | Line to Line | 1465131 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 8099 | 20190824 | 427 | 535103 | 430 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 14498 | 37.1245 | -122.1246 | CGC 315271722985 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0091711 | OH | Sus | 0 | No | 2019 | AUG | Yes | Line to Ground | 1465472 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8501 | 20190905 | 2259 | 556944 | 896 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 17920 | 37.1653 | -122.201 | 4 LD SIDE OF 8501 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0095858 | OH | Sus | 31470823 | No | 2019 | SEP | Yes | Line to Ground | 1467999 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 11929 | 20190907 | 1714 | 562199 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 50702 | 37.0999 | -122.0343 | 2 PHASES LD SIDE OF 11929 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0096478 | OH | Sus | 43947582 | yes | 2019 | SEP | Yes | Line to Ground | 1468390 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7605 | 20190907 | 1546 | 562060 | 503 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 8048 | 37.0863 | -122.0057 | 10 POLES NORTH OF 7605 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0096464 | OH | Sus | 43947538 | yes | 2019 | SEP | Yes | Line to Ground | 1468375 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8501 | 20190910 | 710 | 567398 | 1175 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 23500 | 37.1653 | -122.201 | 6 POLES LOADSIDE OF 8501 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0097264 | OH | Sus | 31471283 | No | 2019 | SEP | Yes | Line to Ground | 1469010 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2166 | 20190915 | 2058 | 583481 | 949 | Distribution Circuit | 3rd Party | Vehicle | 476 | 451724 | 36.2769 | -121.8264 | 8 POLES LOADSIDE OF R101 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0099283 | OH | Sus | 31471744 | No | 2019 | SEP | Yes | Three Phase Fault | 1470170 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9769 | 20190920 | 1820 | 599848 | 510 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 16830 | 37.1292 | -122.1204 | MTR 1007590794 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0102010 | OH | Sus | 43963248 | No | 2019 | SEP | Yes | Line to Ground | 1471643 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | JOLON-1103 | 182981103 | FUSE | 8997 | 20190922 | 1114 | 603513 | 907 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2721 | 36.0225 | -121.249 | 4 SPANS LD SIDE OF 8997 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0102235 | OH | Sus | 31472905 | No | 2019 | SEP | Yes | Three Phase Fault | 1471902 | CAW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HOLLISTER-2105 | 182492105 | FUSE | 4519 | 20190927 | 1029 | 621874 | 299 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 20631 | 36.5609 | -121.1749 | 30003 HWY 25 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0104536 | OH | Sus | 31473466 | No | 2019 | SEP | Yes | Line to Ground | 1473510 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 5335 | 20190928 | 1547 | 627949 | 1157 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 85618 | 37.0281 | -121.9871 | MTR #1007958669 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0105077 | OH | Sus | 0 | yes | 2019 | SEP | Yes | Line to Ground | 1473856 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | JUMPER | WIRE DOWN 3 SPANS LD SIDE OF 8163 | 20190928 | 1647 | 628038 | 456 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 13140 | 36.5984 | -121.9385 | 3 SPANS LD SIDE OF 8163 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0105010 | OH | Sus | 0 | yes | 2019 | SEP | Yes | Line to Ground | 1473785 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 5725 | 20191001 | 557 | 633542 | 832 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11648 | 36.9902 | -121.7367 | 1 LD SIDE OF 5725 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0105769 | OH | Sus | 0 | No | 2019 | OCT | Yes | Line to Ground | 1474299 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 11737 | 20191020 | 2351 | 674982 | 619 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 6819 | 37.0697 | -122.1303 | 701 SUNLIT LN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0113890 | OH | Sus | 31475805 | No | 2019 | OCT | Yes | Line to Ground | 1481386 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | OTHER | WIRE DOWN AT MTR 1006215656 | 20191022 | 1837 | 677215 | 114 | Distribution Circuit | Vegetation | Tree - branch fell on line | 369 | 14593 | 37.0327 | -122.089 | AT MTR 1006215656 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0114840 | OH | Sus | 0 | No | 2019 | OCT | Yes | Line to Ground | 1481936 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 5985 | 20191022 | 1452 | 677086 | 645 | Distribution Circuit | Vegetation | Tree - branch fell on line | 91 | 14835 | 37.045 | -121.9384 | 199 MAKA TRAIL- SOQUEL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0114776 | OH | Sus | 31475951 | No | 2019 | OCT | Yes | Line to Ground | 1481928 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | OCB | 2201/2 | 20191024 | 1552 | 679857 | 99 | Distribution Circuit | Vegetation | Tree - fell into line | 928 | 15334 | 36.5786 | -121.9085 | SB 9893 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0115731 | OH | Sus | 0 | No | 2019 | OCT | Yes | Three Phase Fault | 1483015 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2667 | 20191028 | 1730 | 692496 | 2783 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 16698 | 37.0261 | -121.775 | MTR 1008517304 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0118112 | OH | Sus | 31476475 | yes | 2019 | OCT | Yes | Line to Ground | 1487133 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | FUSE | 2937 | 20191103 | 1810 | 698834 | 1169 | Distribution Circuit | Vegetation | Tree - fell into line | 417 | 59211 | 36.2641 | -121.7954 | SISSOM / 5808/ 831-206-2617: last spand beyond 2937 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0120570 | OH | Sus | 31477163 | No | 2019 | NOV | Yes | Line to Ground | 1488983 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 9529 | 20191104 | 1700 | 699593 | 634 | Distribution Circuit | 3rd Party | Vehicle | 2 | 1268 | 36.9997 | -122.0044 | 3 SOUTH W/OF 9529 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0121122 | OH | Sus | 31477700 | No | 2019 | NOV | Yes | Line to Ground | 1489184 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 9181 | 20191105 | 430 | 699731 | 608 | Distribution Circuit | 3rd Party | Vehicle | 15 | 9120 | 37.2286 | -122.1481 | NYSTROM-ERIK-1058/408-799-8799: Hwy 9 2 miles N/O Hwy 236 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0121166 | OH | Sus | 0 | No | 2019 | NOV | Yes | Line to Line | 1489232 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER | DDE 1 P/W OF MTR #1007591087 | 20191110 | 934 | 703904 | 918 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1836 | 37.1751 | -122.1436 | AT MTR #1007591087 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0123409 | OH | Sus | 44096566 | No | 2019 | NOV | Yes | Line to Line | 1490379 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5625 | 20191125 | 1124 | 714356 | 487 | Distribution Circuit | Vegetation | Tree - fell into line | 130 | 63310 | 37.1051 | -122.0512 | MTR 1006215690 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0128398 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Three Phase Fault | 1493928 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | OTHER | WIRE DWN @ 660 MYSTERY SPOT RD | 20191129 | 1323 | 723642 | 277 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 5299 | 37.0202 | -122.0039 | 660 MYSTERY SPOT RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0131096 | OH | Sus | 44107269 | yes | 2019 | NOV | Yes | Line to Ground | 1495799 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 6909 | 20191129 | 1551 | 723772 | 331 | Distribution Circuit | Equipment Failure/Involved | Overhead | 118 | 31266 | 36.9929 | -121.7356 | 11 SPANS LD SIDE OF 6909 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0131112 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Ground | 1495815 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | RECLOSER | 3066 | 20191201 | 1917 | 726654 | 125 | Distribution Circuit | Vegetation | Tree - fell into line | 3216 | 372936 | 36.5584 | -121.7506 | 1 SPAN SS OF 54079 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0132066 | OH | Sus | 0 | No | 2019 | DEC | Yes | Line to Ground | 1496754 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SEACLIFF-0401 | 83500401 | FUSE | 7533 | 20191201 | 2331 | 726808 | 716 | Distribution Circuit | Vegetation | Tree - fell into line | 212 | 144376 | 36.9903 | -121.9164 | S SPANS LD SIDE 7533 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0132127 | OH | Sus | 0 | No | 2019 | DEC | Yes | Line to Line | 1496813 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 11929 | 20191202 | 957 | 727345 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 45349 | 37.0999 | -122.0343 | 5SP LOAD SIDE OF 11929 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0132361 | OH | Sus | 44109722 | No | 2019 | DEC | Yes | Three Phase Fault | 1496940 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 6809 | 20191202 | 236 | 726924 | 1141 | Distribution Circuit | Vegetation | Tree - fell into line | 180 | 154550 | 36.573 | -121.9271 | 7259 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0132147 | OH | Sus | 0 | No | 2019 | DEC | Yes | Three Phase Fault | 1496833 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 5989 | 20191203 | 437 | 728173 | 778 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 17894 | 37.0576 | -121.9424 | 14 P LD SIDE OF 5989 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0132783 | OH | Sus | 44109722 | No | 2019 | DEC | Yes | Line to Ground | 1497191 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5443 | 20191204 | 713 | 729344 | 422 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 2532 | 37.1106 | -122.1143 | 2 S/OF 12182 ALTA VIA RD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0133282 | OH | Sus | 44109722 | yes | 2019 | DEC | Yes | Line to Line | 1497543 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 7311 | 20191204 | 16 | 729199 | 755 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 17641 | 37.0332 | -122.0775 | 734 WILLOW WAY | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0133116 | OH | Sus | 31479703 | yes | 2019 | DEC | Yes | Line to Line | 1497417 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 11941 | 20191204 | 2029 | 730148 | 980 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 26460 | 37.0087 | -122.0453 | 6 W/OF 11941 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0133669 | OH | Sus | 0 | yes | 2019 | DEC | Yes | Line to Ground | 1497738 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 10457 | 20191204 | 511 | 729248 | 590 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 10154 | 37.1087 | -122.046 | LD SIDE OF 10457 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0133147 | OH | Sus | 44109722 | yes | 2019 | DEC | Yes | Line to Ground | 1497449 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 8047 | 20191204 | 124 | 729205 | 869 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 21725 | 36.5029 | -121.9334 | 4 LD SIDE OF 8047 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0133160 | OH | Sus | 44108658 | yes | 2019 | DEC | Yes | Line to Ground | 1497457 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | JUMPER | WIRE DWN HOT | 20191205 | 25 | 730200 | 604 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 9478 | 37.0875 | -122.0901 | OLD COUNTRY & HILLSIDE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0133692 | OH | Sus | 0 | No | 2019 | DEC | Yes | Line to Ground | 1497763 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | OTHER | WIRE DOWN 1245/1255 COX RD | 20191206 | 642 | 731061 | 804 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 13835 | 37.0096 | -121.8549 | 2P N/OF CGC# 316046018837 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0134319 | OH | Sus | 44114703 | yes | 2019 | DEC | Yes | Line to Ground | 1498232 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 3729 | 20191207 | 805 | 732303 | 837 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2511 | 37.1979 | -122.1542 | S SPANS LD SIDE 3729 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0134755 | OH | Sus | 44113814 | yes | 2019 | DEC | Yes | Line to Line | 1498556 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER | WIRE DOWN | 20191207 | 1007 | 732482 | 420 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 3529 | 37.1356 | -122.1429 | 500 BROOK LN | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0134775 | OH | Sus | 44113814 | yes | 2019 | DEC | Yes | Line to Ground | 1498576 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 5985 | 20191207 | 230 | 732123 | 536 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 48776 | 37.045 | -121.9384 | MTR #1009441105 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | On Ground | 19-0134677 | OH | Sus | 31480135 | yes | 2019 | DEC | Yes | Line to Line | 1498429 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 5985 | 20191207 | 1947 | 733406 | 1211 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 32953 | 37.045 | -121.9384 | at MTR #1009262602 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0134940 | OH | Sus | 31480135 | yes | 2019 | DEC | Yes | Line to Ground | 1498728 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 6183 | 20191207 | 330 | 732139 | 947 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5682 | 37.008 | -121.8853 | 301 SHADY MAPLE DR | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0134752 | OH | Sus | 44113814 | yes | 2019 | DEC | Yes | Line to Line | 1498552 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 2145 | 20191207 | 1214 | 732737 | 345 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1035 | 36.5682 | -121.9289 | 2 SPANS LD SIDE OF 2145 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0134782 | OH | Sus | 0 | yes | 2019 | DEC | Yes | Force Out | 1498583 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER | 9104 | 20191207 | 2233 | 733472 | 949 | Distribution Circuit | Vegetation | Tree - branch fell on line | 700 | 410137 | 36.5869 | -121.9142 | SS AND LD SIDE OF 1337 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0134971 | OH | Sus | 31480138 | yes | 2019 | DEC | Yes | Multi-Fault | 1498761 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | FUSE | 2811 | 20191208 | 829 | 733606 | 755 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 14345 | 36.5151 | -121.8129 | 4 P/LD SIDE OF 2811 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0135019 | OH | Sus | 31480138 | No | 2019 | DEC | Yes | Line to Ground | 1498811 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 5411 | 20191210 | 726 | 735306 | 531 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 9027 | 37.0549 | -122.1609 | 150 THAYER RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0135604 | OH | Sus | 0 | No | 2019 | DEC | Yes | Line to Ground | 1499435 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | OTHER | WIRE DOWN 2206 UPPER SCENIC | 20191214 | 1904 | 739899 | 927 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 15312 | 37.0269 | -122.0738 | 2206 UPPER SCENIC DR | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0136600 | OH | Sus | 44122878 | No | 2019 | DEC | Yes | Line to Ground | 1500707 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 1445 | 20200102 | 206 | 753504 | 652 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6520 | 36.5735 | -121.9107 | 1 SPAN E OF 7347 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0004268 | OH | Sus | 44142514 | No | 2020 | JAN | Yes | Line to Ground | 1503738 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER | 10720 | 20200103 | 1158 | 754383 | 80 | Distribution Circuit | Vegetation | Tree - fell into line | 2229 | 50808 | 37.1086 | -122.1439 | FIRST 3 POLE STRUCTURE SOUTH OF 5433 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0004875 | OH | Sus | 0 | No | 2020 | JAN | Yes | Line to Line | 1503986 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | FUSE | 94581 | 20200105 | 1000 | 755058 | 2180 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1 | 2180 | 36.2976 | -121.8667 | E/OF MTR# 1010399070 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0005272 | OH | Sus | 0 | No | 2020 | JAN | Yes | Line to Ground | 1504132 | CAW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 495039 | 20200109 | 931 | 757803 | 532 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 20748 | 36.5692 | -121.912 | CGC 411467846355 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0006852 | OH | Sus | 44147712 | No | 2020 | JAN | Yes | Line to Line | 1505262 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8021 | 20200118 | 1324 | 765678 | 301 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 6131 | 37.1636 | -122.1621 | 1 POLE E/OF MTR# 1007344661 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0011095 | OH | Sus | 44159235 | No | 2020 | JAN | Yes | Line to Ground | 1507603 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12124 | 20200122 | 29 | 767637 | 761 | Distribution Circuit | Vegetation | Tree - fell into line | 473 | 141003 | 37.1678 | -122.1661 | 16537 BIG BASIN WAY- BOULDER CREEK | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0012073 | OH | Sus | 31487067 | No | 2020 | JAN | Yes | Line to Line | 1508234 | CAW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | JUMPER | WIRE DWN | 20200202 | 1322 | 776034 | 672 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 10507 | 37.0075 | -121.8763 | 4 LD SIDE OF 11587 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0016379 | OH | Sus | 44175155 | yes | 2020 | FEB | Yes | Line to Ground | 1511143 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER | 9488 | 20200202 | 1410 | 775876 | 1211 | Distribution Circuit | 3rd Party | Vehicle | 378 | 51798 | 36.5902 | -121.9442 | at SB 66237 | Clear-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 20-0016340 | OH | Sus | 31488504 | yes | 2020 | FEB | Yes | Three Phase Fault | 1511108 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 8353 | 20200211 | 1643 | 789064 | 241 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1928 | 37.0582 | -121.9417 | 5991 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0020762 | OH | Sus | 0 | yes | 2020 | FEB | Yes | Force Out | 1514358 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | OTHER | WIRE DOWN @ 4035 SYLVESTER DR | 20200212 | 916 | 789388 | 550 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 6190 | 37.0288 | -122.0971 | 4035 SYLVESTER DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0020975 | OH | Sus | 0 | No | 2020 | FEB | Yes | Open Circuit | 1514540 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN HOT | 20200213 | 2213 | 790724 | 741 | Distribution Circuit | 3rd Party | Vehicle | 15 | 10539 | 37.0722 | -121.9846 | TX MTR 1007347195 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0022087 | OH | Sus | 44192661 | No | 2020 | FEB | Yes | Line to Ground | 1515244 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | OTHER | WIRE DOWN @ 7425 | 20200215 | 15 | 791597 | 924 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3215 | 128677 | 36.5623 | -121.7913 | 7425 ON MAINLINE | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0022550 | OH | Sus | 44194663 | No | 2020 | FEB | Yes | Open Circuit | 1515546 | CSO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 2451 | 20200217 | 1027 | 792537 | 438 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3066 | 36.5723 | -121.9406 | 6 SPANS LD SIDE OF 2451 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0022783 | OH | Sus | 31491439 | No | 2020 | FEB | Yes | Line to Ground | 1515780 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 9181 | 20200222 | 417 | 800551 | 633 | Distribution Circuit | 3rd Party | Vehicle | 15 | 9495 | 37.2286 | -122.1481 | 24100 HWY 9 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0024885 | OH | Sus | 0 | No | 2020 | FEB | Yes | Line to Ground | 1517018 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 7993 | 20200313 | 2002 | 850997 | 1012 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 39468 | 37.0284 | -121.7411 | 572 SUMMIT RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0031982 | OH | Sus | 44252627 | No | 2020 | MAR | Yes | Three Phase Fault | 1521308 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20200319 | 452 | 858638 | 719 | Distribution Circuit | Vegetation | Tree - fell into line | 421 | 170042 | 36.9804 | -121.892 | 1 LD SIDE OF 6121 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0034027 | OH | Sus | 31497902 | yes | 2020 | MAR | Yes | Line to Line | 1522917 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12758 | 20200405 | 1550 | 883167 | 1205 | Distribution Circuit | Vegetation | Tree - branch fell on line | 295 | 34933 | 37.1486 | -122.1748 | at 9797 TWD 12758 | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0038603 | OH | Sus | 31498955 | yes | 2020 | APR | Yes | Line to Line | 1525415 | CAW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 764889 | 20200405 | 1104 | 882861 | 448 | Distribution Circuit | Vegetation | Tree - fell into line | 343 | 143388 | 37.0019 | -122.0379 | 4 N/OF 5279 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0038548 | OH | Sus | 31498950 | yes | 2020 | APR | Yes | Line to Line | 1525382 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | CAMP EVERS-2105 | 83622105 | OTHER | WIRE DOWN 1 SPAN LD SIDE 5233 | 20200405 | 2108 | 883368 | 457 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 10760 | 37.0582 | -122.0758 | 1 SPAN LD SIDE OF 5233 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0038667 | OH | Sus | 31499060 | yes | 2020 | APR | Yes | Line to Ground | 1525480 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8983 | 20200405 | 1236 | 882917 | 1792 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 87808 | 37.0309 | -122.143 | 3 SPANS NORTH EAST OF 8985 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 20-0038561 | OH | Sus | 31498984 | yes | 2020 | APR | Yes | Line to Ground | 1525394 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 5090 | 20200405 | 331 | 882598 | 654 | Distribution Circuit | Vegetation | Tree - branch fell on line | 430 | 207440 | 36.9804 | -121.892 | 12 SPANS LOAD SIDE OF 5090 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0038482 | OH | Sus | 44281628 | yes | 2020 | APR | Yes | Line to Ground | 1525318 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6083 | 20200406 | 1245 | 885499 | 333 | Distribution Circuit | Vegetation | Tree - branch fell on line | 80 | 6711 | 37.0587 | -122.0334 | at MTR# 1010153078 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0038962 | OH | Sus | 44282811 | yes | 2020 | APR | Yes | Line to Ground | 1525712 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2002 | 20200406 | 705 | 883737 | 772 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 96500 | 36.2249 | -121.7589 | 1SPAN SOUTH OF LR 2002 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0038732 | OH | Sus | 44282574 | yes | 2020 | APR | Yes | Three Phase Fault | 1525541 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | JUMPER | WIRE DOWN 2 SPANS N/OF MTR# 1007591866 | 20200406 | 748 | 884813 | 730 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 9424 | 37.0579 | -121.8216 | 2 N/OF MTR# 1007591866 | Partly Cloudy-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 20-0038842 | OH | Sus | 0 | yes | 2020 | APR | Yes | Open Circuit | 1525636 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 4355 | 20200409 | 342 | 892725 | 517 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 11891 | 37.0602 | -122.064 | 2P LOAD SIDE OF 4355 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0039938 | OH | Sus | 44285085 | No | 2020 | APR | Yes | Line to Ground | 1526264 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | RECLOSER | 2000 | 20200409 | 809 | 892783 | 606 | Distribution Circuit | 3rd Party | Vehicle | 769 | 117424 | 36.5851 | -121.8743 | AGUAJITO S\ OF HWY 1 (1 LD SIDE OF 2839) | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 20-0039957 | OH | Sus | 31499751 | No | 2020 | APR | Yes | Multi-Fault | 1526282 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2705 | 20200418 | 308 | 897320 | 138 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 3450 | 37.0005 | -121.7405 | TREE DWN 5 SP LD SIDE OF 2705- WIRE DOWN 3 SP LD SIDE 2705 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0042500 | OH | Sus | 0 | No | 2020 | APR | Yes | Line to Line | 1527838 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2204 | 182852204 | OCB | 2204/2 | 20200420 | 751 | 897930 | 121 | Distribution Circuit | Animal | Squirrel | 277 | 16555 | 36.5786 | -121.9084 | 9540 | Overcast-32-90 F | Recloser | Broken, wire on ground | 20-0042738 | OH | Sus | 0 | No | 2020 | APR | Yes | Line to Ground | 1528027 | RCA | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 3317 | 20200423 | 1344 | 900176 | 370 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 740 | 37.0645 | -121.9833 | 2P N/OF 3317 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0044095 | OH | Sus | 44302507 | No | 2020 | APR | Yes | Line to Ground | 1528727 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HOLLISTER-2105 | 182492105 | JUMPER | WIRE DOWN AT MTR# 1009252753 | 20200426 | 1704 | 901876 | 341 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 341 | 36.709 | -121.3339 | MTR# 1009252753 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0044678 | OH | Sus | 31501382 | No | 2020 | APR | Yes | Line to Ground | 1529154 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2103 | 182222103 | FUSE | 2871 | 20200427 | 1149 | 902220 | 172 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 516 | 36.5708 | -121.8886 | Rodriguez/ 5809/ 831-233-0361: spans loadside of 2871 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0044827 | OH | Sus | 31501355 | No | 2020 | APR | Yes | Force Out | 1529290 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2105 | 83252105 | FUSE | 6095 | 20200506 | 2248 | 908551 | 690 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 11040 | 37.021 | -122.0265 | 1 E/OF 6095 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0047975 | OH | Sus | 44312284 | No | 2020 | MAY | Yes | Line to Ground | 1531188 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5519 | 20200512 | 736 | 911881 | 523 | Distribution Circuit | Vegetation | Tree - fell into line | 172 | 75877 | 37.1515 | -122.1362 | 4 LD SIDE OF 5521 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 20-0049339 | OH | Sus | 0 | yes | 2020 | MAY | Yes | Line to Line | 1532073 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | RECLOSER | 3088 | 20200512 | 226 | 911739 | 754 | Distribution Circuit | Equipment Failure/Involved | Overhead | 337 | 53327 | 36.5493 | -121.7318 | 24147 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0049270 | OH | Sus | 44321009 | yes | 2020 | MAY | Yes | Three Phase Fault | 1532030 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 2321 | 20200512 | 1139 | 912112 | 219 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 6789 | 37.005 | -121.8623 | at CGC# 316036519020 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0049573 | OH | Sus | 0 | yes | 2020 | MAY | Yes | Line to Line | 1532151 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 6409 | 20200515 | 1223 | 914286 | 387 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 14190 | 36.59 | -121.9114 | 2 S/OF 8747 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0050639 | OH | Sus | 44325608 | No | 2020 | MAY | Yes | Three Phase Fault | 1532717 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 83765 | 20200518 | 2329 | 917263 | 1163 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 13964 | 37.1175 | -121.975 | LD SIDE OF 83765 | Clear-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 20-0051629 | OH | Sus | 0 | yes | 2020 | MAY | Yes | Line to Line | 1533282 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER | BROKEN WIRE AT 1607. | 20200519 | 1052 | 917641 | 371 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 13 | 4823 | 37.1935 | -122.1559 | 1ST SPAN LD SIDE OF 1607 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0051845 | OH | Sus | 44326909 | No | 2020 | MAY | Yes | Line to Ground | 1533407 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | OTHER | WIRE DOWN AT MTR# 1010494936 | 20200519 | 452 | 917318 | 592 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 24377 | 36.5848 | -121.9115 | MTR# 1010494936 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0051632 | OH | Sus | 31503351 | No | 2020 | MAY | Yes | Line to Ground | 1533287 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 1445 | 20200519 | 1653 | 917800 | 402 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 4020 | 36.5735 | -121.9107 | 3 SPANS LD SIDE OF 1445 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0052051 | OH | Sus | 44326991 | No | 2020 | MAY | Yes | Line to Ground | 1533443 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER | WIRE DWN 4 LD SIDE OF 6187 | 20200527 | 641 | 923103 | 445 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 2365 | 37.0767 | -122.0592 | 4 LD SIDE OF 6187 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0054622 | OH | Sus | 31504209 | yes | 2020 | MAY | Yes | Line to Ground | 1534966 | CAW | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | FUSE | 1295 | 20200529 | 733 | 924965 | 733 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 10262 | 36.3795 | -121.8611 | 5 SPANS FROM THE EOL | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0055655 | OH | Sus | 0 | yes | 2020 | MAY | Yes | Line to Line | 1535573 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER | WIRE DOWN AT MTR 1007586964 | 20200530 | 1211 | 926368 | 564 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 564 | 37.1586 | -122.1713 | MTR 1007586964 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 20-0055958 | OH | Sus | 31504455 | yes | 2020 | MAY | Yes | Line to Ground | 1535830 | PW | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | OTHER | WIRE DOWN2 SPANS LD FROM MTR# 1007590068 | 20200605 | 1528 | 932107 | 257 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 2351 | 37.166 | -122.1298 | 2 SPANS LD FROM MTR# 1007590068 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0058273 | OH | Sus | 44344342 | yes | 2020 | JUN | Yes | Line to Ground | 1537534 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | RECLOSER | 10960 | 20200605 | 2357 | 932451 | 633 | Distribution Circuit | 3rd Party | Vehicle | 2393 | 221908 | 36.9866 | -121.8582 | 3 SE OF 11227 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 20-0058365 | OH | Sus | 35180577 | yes | 2020 | JUN | Yes | Line to Line | 1537607 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | WIRE DWN | 20200606 | 515 | 932533 | 818 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1531 | 37.1003 | -122.1158 | 3 LD SIDE OF 9697 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0058388 | OH | Sus | 0 | yes | 2020 | JUN | Yes | None | 1537629 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 9005 | 20200612 | 208 | 937339 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 11968 | 37.0318 | -122.1371 | 13 N/OF 9005 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0060460 | OH | Sus | 31505518 | yes | 2020 | JUN | Yes | Line to Line | 1539158 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 1101 | 20200617 | 1322 | 941267 | 117 | Distribution Circuit | Vegetation | Tree - fell into line | 737 | 35419 | 37.0926 | -122.0966 | 240 LARKSPUR ST | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0062276 | OH | Sus | 0 | No | 2020 | JUN | Yes | Line to Ground | 1540498 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5173 | 20200623 | 1309 | 945360 | 338 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 20618 | 37.1011 | -122.1017 | 1630 RIVER RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0064054 | OH | Sus | 44363778 | yes | 2020 | JUN | Yes | Line to Ground | 1541858 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6711 | 20200624 | 822 | 945974 | 536 | Distribution Circuit | Vegetation | Tree - branch fell on line | 49 | 26264 | 36.998 | -121.8689 | LD SIDE OF MTR #100872744 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0064360 | OH | Sus | 44364369 | No | 2020 | JUN | Yes | Line to Ground | 1542120 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5535 | 20200628 | 14 | 949171 | 643 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6430 | 37.066 | -122.2284 | 425 BIG CREEK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0065776 | OH | Sus | 44368148 | No | 2020 | JUN | Yes | Line to Ground | 1542998 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | RECLOSER | 12990 | 20200703 | 2219 | 957610 | 930 | Distribution Circuit | 3rd Party | Vehicle | 795 | 56989 | 37.039 | -122.0215 | 80381 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0068316 | OH | Sus | 0 | No | 2020 | JUL | Yes | Line to Ground | 1544336 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | OTHER | WIRE DOWN HOT 1 N/OF MTR# 1007345863 | 20200710 | 219 | 961356 | 1009 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 23935 | 37.0653 | -122.0333 | 1 N/OF MTR# 1007345863 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0070337 | OH | Sus | 31508157 | No | 2020 | JUL | Yes | Line to Ground | 1545569 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9697 | 20200712 | 2138 | 963103 | 982 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1964 | 37.0995 | -122.1169 | 4 SPANS LD SIDE OF 9697 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0071064 | OH | Sus | 31508451 | yes | 2020 | JUL | Yes | Force Out | 1546098 | CAW | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7625 | 20200712 | 1055 | 962820 | 355 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1065 | 37.1221 | -121.9791 | AT 7625 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0070960 | OH | Sus | 44388124 | yes | 2020 | JUL | Yes | Force Out | 1546034 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6641 | 20200715 | 2327 | 965664 | 1178 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 42285 | 37.0161 | -121.8161 | BET FUCO 1157 & 2701 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0072470 | OH | Sus | 35186608 | yes | 2020 | JUL | Yes | Line to Line | 1546971 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | FUSE | 8245 | 20200802 | 910 | 976959 | 386 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 7334 | 36.4938 | -121.9344 | 2 SPANS N/OF 8245 | Overcast-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0078804 | OH | Sus | 44407110 | No | 2020 | AUG | Yes | Line to Ground | 1551081 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8505 | 20200805 | 1026 | 979394 | 419 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1676 | 37.176 | -122.2197 | 4 LD SIDE OF 8505 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0079990 | OH | Sus | 44410452 | yes | 2020 | AUG | Yes | Line to Line | 1551956 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8501 | 20200807 | 951 | 983013 | 599 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 11980 | 37.1653 | -122.201 | BOYNTON-3459 / 831-331-6620: 7 SPANS LOAD SIDE C/O 8501 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0080932 | OH | Sus | 44414253 | No | 2020 | AUG | Yes | Line to Line | 1552511 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 5989 | 20200818 | 621 | 1018122 | 699 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 6761 | 37.0576 | -121.9424 | 2SPANS LD SIDE OF CGC 315773220883 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0086562 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Ground | 1556611 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | SWITCH | 12649 | 20200826 | 2218 | 1033423 | 240 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 15360 | 37.0512 | -121.9995 | 1P SOURCE SIDE OF CGC# 315624720151 | Clear-32-90 F | Crossarm, Wood | Broken, wire on object | 20-0090507 | OH | Sus | 0 | No | 2020 | AUG | Yes | None | 1559177 | CAW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 3649 | 20200826 | 53 | 1030893 | 807 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 6456 | 36.9864 | -121.8507 | 5P S/OF 3649 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0090047 | OH | Sus | 31512351 | No | 2020 | AUG | Yes | Line to Ground | 1558812 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6851 | 20200826 | 445 | 1030973 | 502 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 8032 | 37.042 | -121.8165 | 6 SPANS LD SIDE OF 6851 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0090058 | OH | Sus | 31512271 | No | 2020 | AUG | Yes | Line to Ground | 1558817 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 10718 | 20200904 | 1005 | 1053520 | 355 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 61 | 8712 | 37.0361 | -122.107 | 2 SS OF 1995 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0093354 | OH | Sus | 31512968 | No | 2020 | SEP | Yes | Line to Ground | 1560873 | CAW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | JUMPER | WIRE DOWN N/OF MTR# 1007345073 | 20200906 | 1333 | 1056984 | 369 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 4942 | 37.0873 | -122.0898 | at MTR# 1007345073 | Clear-Above 90 | Connector or Splice (OH) | Broken, wire on ground | 20-0093893 | OH | Sus | 44459558 | yes | 2020 | SEP | Yes | Line to Ground | 1561158 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | TRIP-SAVER | 5401 | 20200909 | 322 | 1061739 | 456 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 31464 | 37.0648 | -122.1233 | Miller Rd and Empire Grade | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0095348 | OH | Sus | 31513301 | yes | 2020 | SEP | Yes | Line to Ground | 1562486 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2105 | 83692105 | OTHER | WIRE DOWN AT MTR # 1008734619 | 20200914 | 459 | 1067546 | 529 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1058 | 36.9694 | -121.8795 | MTR # 1008734619 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0097046 | OH | Sus | 31513624 | No | 2020 | SEP | Yes | Line to Ground | 1563420 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5519 | 20200915 | 329 | 1070672 | 412 | Distribution Circuit | Vegetation | Tree - branch fell on line | 160 | 65920 | 37.1515 | -122.1362 | CGC 315233224330 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0097506 | OH | Sus | 31513458 | No | 2020 | SEP | Yes | Line to Ground | 1563683 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 5104 | 20200916 | 1758 | 1076690 | 49 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 49 | 37.0302 | -122.1868 | JUST S/OUTH OF 5523 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0098304 | OH | Sus | 0 | No | 2020 | SEP | Yes | Force Out | 1564147 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8397 | 20200917 | 1048 | 1078202 | 165 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 8 | 1320 | 37.0796 | -122.1395 | 54 COMSTOCK LN | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0098588 | OH | Sus | 0 | No | 2020 | SEP | Yes | Line to Line | 1564324 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | OJ'S 2 POLES S/O MTR# 1007344970 | 20200918 | 913 | 1080217 | 142 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 4 | 568 | 37.1638 | -122.1592 | MTR # 1007344970 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0098888 | OH | Sus | 0 | No | 2020 | SEP | Yes | Force Out | 1564500 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 8475 | 20200918 | 1108 | 1080696 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1516 | 37.1319 | -122.1372 | James 415-517-1140/ 4176: burnt tree fell into line | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0098978 | OH | Sus | 31514147 | No | 2020 | SEP | Yes | Line to Line | 1564560 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 39126 | 20200918 | 1731 | 1081952 | 1149 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 523 | 103227 | 37.0778 | -122.1322 | 462 MOLINA DR | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0099100 | OH | Sus | 0 | No | 2020 | SEP | Yes | Line to Ground | 1564602 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 5209 | 20200922 | 1957 | 1088666 | 1177 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 23540 | 37.0372 | -122.0723 | MTR# 1008736318 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0100412 | OH | Sus | 35201814 | No | 2020 | SEP | Yes | Line to Line | 1565464 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 5066 | 20200926 | 2 | 1093682 | 931 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 57593 | 37.1706 | -122.1655 | SOURCE SIDE OF 7289 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0101780 | OH | Sus | 0 | No | 2020 | SEP | Yes | Line to Line | 1566249 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 6407 | 20200930 | 939 | 1101334 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 9720 | 36.5917 | -121.9125 | 3 SPANS LOADSIDE OF 6407 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0103357 | OH | Sus | 44483899 | No | 2020 | SEP | Yes | Line to Ground | 1567416 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 6209 | 20201002 | 1225 | 1107356 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1320 | 37.1793 | -122.1392 | 4 E/OF 6209 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0104479 | OH | Sus | 31515100 | No | 2020 | OCT | Yes | Line to Line | 1568022 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | JUMPER | WIRE DOWN @ CGC# 315436020101 | 20201004 | 819 | 1110810 | 716 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1432 | 37.0408 | -122.0646 | CGC# 315436020101 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0104934 | OH | Sus | 0 | No | 2020 | OCT | Yes | Line to Ground | 1568372 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 8047 | 20201029 | 646 | 1131214 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 11225 | 36.5029 | -121.9334 | 4 P/LD SIDE OF 8047 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0114641 | OH | Sus | 0 | No | 2020 | OCT | Yes | Line to Ground | 1575371 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | JUMPER | 2 P/LD SIDE OF CGC 315971819260 | 20201105 | 1818 | 1136992 | 1249 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 12490 | 37.019 | -121.8799 | 2 P/LD SIDE OF CGC 315971819230 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0117587 | OH | Sus | 0 | No | 2020 | NOV | Yes | Force Out | 1577355 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | JUMPER | WIRE DWN @ CGC 315232323354 | 20201108 | 544 | 1139160 | 676 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 12310 | 37.1294 | -122.1365 | CGC 315232323354 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0118391 | OH | Sus | 44517621 | No | 2020 | NOV | Yes | Line to Ground | 1578029 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 7311 | 20201110 | 1407 | 1141364 | 496 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 11904 | 37.0332 | -122.0775 | 790 WILLOW WAY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0119419 | OH | Sus | 31518226 | No | 2020 | NOV | Yes | Line to Line | 1578834 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER | WIRE DOWN NE/OF MTR# 1009773933 | 20201117 | 601 | 1146772 | 446 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 6343 | 37.1606 | -122.1555 | NE/OF MTR# 1009773933 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0121685 | OH | Sus | 44542873 | No | 2020 | NOV | Yes | Open Circuit | 1580422 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 9463 | 20201118 | 1119 | 1148552 | 458 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 27480 | 37.0697 | -122.0714 | 7900 HIHN RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0122450 | OH | Sus | 44542655 | No | 2020 | NOV | Yes | Line to Line | 1581015 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | JOLON-1102 | 182981102 | RECLOSER | 7002 | 20201128 | 1309 | 1155578 | 194 | Distribution Circuit | Equipment Failure/Involved | Overhead | 140 | 20053 | 35.9664 | -121.1153 | MTR # 1010046695 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0125604 | OH | Sus | 44571056 | No | 2020 | NOV | Yes | Line to Ground | 1582739 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 8099 | 20201129 | 810 | 1155790 | 840 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 85368 | 37.1245 | -122.1246 | PINE AN HARMON | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0125705 | OH | Sus | 44571292 | No | 2020 | NOV | Yes | Line to Line | 1582816 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5445 | 20201209 | 1224 | 1173583 | 249 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 8 | 1992 | 37.1301 | -122.1341 | 7 LOADSIDE OF 5445 | Clear-32-90 F | Insulator | Broken, wire on ground | 20-0129180 | OH | Sus | 31520033 | No | 2020 | DEC | Yes | Force Out | 1585764 | INS | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER | WIRE DOWN @ CGC# 315181625755 | 20201211 | 631 | 1178045 | 618 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 618 | 37.1955 | -122.1565 | CGC# 315181625755 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0129644 | OH | Sus | 0 | No | 2020 | DEC | Yes | Open Circuit | 1586283 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9727 | 20201223 | 1313 | 1197806 | 281 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1124 | 37.1537 | -122.1358 | 2 SPANS LOAD SIDE OF 9727 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0131608 | OH | Sus | 44595542 | No | 2020 | DEC | Yes | Line to Ground | 1589313 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | OTHER | WIRE DOWN 5 LD SIDE OF 56893 | 20201223 | 1425 | 1197921 | 539 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 12471 | 37.0614 | -121.8229 | 5 SPANS LD SIDE OF 59893 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0131617 | OH | Sus | 31522440 | No | 2020 | DEC | Yes | Line to Ground | 1589324 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 3459 | 20210104 | 1227 | 1203763 | 593 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 8972 | 37.0243 | -121.8837 | 2647 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0004776 | OH | Sus | 44609965 | No | 2021 | JAN | Yes | Line to Ground | 1590748 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 5217 | 20210105 | 725 | 1204321 | 460 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 2844 | 37.0374 | -122.0662 | 5 POLES LD SIDE OF 5217 AT HARD TAP TO NORTH | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0005092 | OH | Sus | 44610247 | No | 2021 | JAN | Yes | Line to Ground | 1590976 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER | WIRE DOWN 2/P/S/W CGC#315176424695 | 20210120 | 1415 | 1219028 | 201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 3405 | 37.1656 | -122.1566 | 2/P/S/W CGC#315176424695 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0011634 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1595167 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | TRIP-SAVER | 9031 | 20210120 | 2036 | 1219321 | 1058 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 49726 | 37.0726 | -122.0742 | THORNE-ALLAN: TREE IN LINE LOAD SIDE OF 5163 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0012138 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1595459 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 7309 | 20210121 | 2035 | 1220327 | 805 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 12880 | 37.0328 | -122.0754 | S/S Lakeside Drive At Madrona | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0012470 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1595687 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 5339 | 20210122 | 1326 | 1221099 | 50 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 650 | 37.0502 | -121.981 | 2 LD SIDE OF 5339 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0012694 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1595760 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 10457 | 20210122 | 2126 | 1221513 | 1042 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 16672 | 37.1086 | -122.0459 | 2 SPANS N/OF OF 10457 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013197 | OH | Sus | 0 | No | 2021 | JAN | Yes | Three Phase Fault | 1596181 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 10103 | 20210123 | 1245 | 1221809 | 217 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 434 | 37.1127 | -122.1513 | 4 SPANS LD SIDE OF 10103 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013274 | OH | Sus | 0 | No | 2021 | JAN | Yes | Force Out | 1596228 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 10621 | 20210124 | 909 | 1222369 | 541 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2705 | 37.0651 | -122.0174 | 1 SP LD SIDE OF 10621 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0013429 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1596396 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 2687 | 20210129 | 646 | 1241067 | 451 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 29629 | 37.0224 | -121.8276 | 3P LOAD SIDE OF 3413 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0018199 | OH | Sus | 0 | No | 2021 | JAN | Yes | Multi-Fault | 1600200 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5487 | 20210130 | 1942 | 1243572 | 1150 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 64400 | 37.1371 | -122.1003 | 1 SP N/OF FUCO 4183 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0019524 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1601394 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 3459 | 20210202 | 2206 | 1246612 | 1019 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 33686 | 37.0243 | -121.8837 | BENTLEY-STEVE: 1/P/SS of 12673 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0021138 | OH | Sus | 31529171 | No | 2021 | FEB | Yes | Line to Line | 1602579 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | RESERVATION ROAD-1102 | 182731102 | FUSE | 5567 | 20210211 | 446 | 1252915 | 721 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 14420 | 36.5213 | -121.5213 | 4 POLES LD SIDE OF CGC 412549743842 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0024415 | OH | Sus | 0 | No | 2021 | FEB | Yes | Line to Ground | 1604525 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 6343 | 20210225 | 304 | 1261839 | 976 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 18544 | 37.2222 | -122.1452 | 2 SS/OF 3857 (TREE COND DWN) & 2 SS/OF & 1 LD SIDE/OF 3483 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0029352 | OH | Sus | 0 | No | 2021 | FEB | Yes | Line to Ground | 1607687 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2933 | 20210225 | 520 | 1261841 | 548 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7124 | 37.0198 | -121.7611 | 1 SS/OF CGC 316309019155 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0029353 | OH | Sus | 0 | No | 2021 | FEB | Yes | Line to Ground | 1607689 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2161 | 20210225 | 1646 | 1262537 | 656 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2624 | 36.9969 | -121.7382 | 5 P/LD SIDE OF 2161 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0029743 | OH | Sus | 0 | No | 2021 | FEB | Yes | Line to Ground | 1607959 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2103 | 83192103 | OTHER | WIRE DOWN | 20210227 | 1100 | 1263553 | 575 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1725 | 37.0244 | -121.7773 | 2P E/OF CGC# 316270519345 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0030345 | OH | Sus | 44666141 | No | 2021 | FEB | Yes | Open Circuit | 1608382 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1102 | 182941102 | FUSE | 2877 | 20210227 | 829 | 1263454 | 356 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 356 | 36.3767 | -121.8975 | 1P LOAD SIDE OF 2877 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 21-0030265 | OH | Sus | 44666088 | No | 2021 | FEB | Yes | Line to Ground | 1608333 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | JUMPER | 1 E/OF CGC 411900347911 | 20210309 | 1224 | 1275476 | 131 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 226 | 36.6191 | -121.7581 | 1 E/OF CGC 411900347911 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0033982 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1610717 | CSO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8397 | 20210311 | 210 | 1278294 | 888 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 8880 | 37.0795 | -122.1393 | 4 SPANS LD SIDE OF 8397 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0035061 | OH | Sus | 31532932 | No | 2021 | MAR | Yes | Line to Line | 1611222 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8097 | 20210311 | 239 | 1278364 | 1161 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 19737 | 37.0785 | -122.139 | LD SIDE OF 8097 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0035099 | OH | Sus | 31532933 | No | 2021 | MAR | Yes | Line to Ground | 1611233 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 9827 | 20210311 | 210 | 1278368 | 1032 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 33024 | 37.0797 | -122.1385 | 1 P/LD SIDE OF 9827- BLOWN LIGHTNING ARRESTOR AT CGC 315216421704 | Clear-32-90 F | Lightning Arrestor | Broken, wire on ground | 21-0035107 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1611234 | LA | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 7799 | 20210311 | 427 | 1278393 | 878 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 44778 | 37.091 | -122.1396 | A CGC 315202421918 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0035171 | OH | Sus | 31532935 | No | 2021 | MAR | Yes | Force Out | 1611261 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 6187 | 20210318 | 1156 | 1287833 | 678 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 15594 | 36.5676 | -121.9288 | CGC at 411401346264 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0038135 | OH | Sus | 31533648 | No | 2021 | MAR | Yes | Line to Ground | 1613150 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5225 | 20210319 | 1121 | 1288929 | 304 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 2115 | 37.0496 | -122.0856 | 1901 FELTON EMPIRE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0038728 | OH | Sus | 31533195 | No | 2021 | MAR | Yes | Line to Ground | 1613432 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 11425 | 20210319 | 545 | 1288413 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 332 | 37.0565 | -122.0206 | .5 SPAN LD SIDE 11425 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0038405 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1613263 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 3233 | 20210320 | 1312 | 1290168 | 457 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 17366 | 37.0325 | -122.0628 | CGC# 315424119793 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0039001 | OH | Sus | 44695477 | No | 2021 | MAR | Yes | Line to Ground | 1613627 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | JUMPER | BURNED OJ 1 P SS OF CGC 315967617888 | 20210320 | 751 | 1289599 | 393 | Distribution Circuit | Equipment Failure/Involved | Overhead | 108 | 37922 | 36.9835 | -121.8848 | 1 P SS OF CGC 315967617888 | Clear-32-90 F | Jumper | Broken, wire on ground | 21-0038937 | OH | Sus | 44695085 | No | 2021 | MAR | Yes | Open Circuit | 1613583 | JMP | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 10563 | 20210402 | 1810 | 1306078 | 424 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 20297 | 37.1097 | -122.0485 | JUST LD SIDE OF 10453 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0044354 | OH | Sus | 31535203 | No | 2021 | APR | Yes | Line to Ground | 1617291 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LOS OSITOS-2103 | 182082103 | FUSE | 3027 | 20210411 | 938 | 1312995 | 706 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 41028 | 36.2495 | -121.432 | METER# 1009764336 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0047270 | OH | Sus | 31535703 | No | 2021 | APR | Yes | Line to Ground | 1619250 | CAW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2105 | 83692105 | FUSE | 1181 | 20210418 | 1257 | 1322035 | 491 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 5401 | 36.9792 | -121.8924 | SIESTA DR & VALENCIA DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0050069 | OH | Sus | 31536246 | No | 2021 | APR | Yes | Line to Ground | 1621064 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9237 | 20210420 | 2221 | 1326056 | 1224 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3672 | 37.0789 | -122.0518 | CGC 315477721416 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0051119 | OH | Sus | 0 | No | 2021 | APR | Yes | Line to Ground | 1621811 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9237 | 20210422 | 254 | 1327849 | 563 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1689 | 37.0789 | -122.0518 | 3 SP LD SIDE OF 9237 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0051632 | OH | Sus | 44757525 | No | 2021 | APR | Yes | Line to Ground | 1622149 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | RESERVATION ROAD-1102 | 182731102 | OTHER | WIRE DOWN | 20210426 | 425 | 1333841 | 666 | Distribution Circuit | Equipment Failure/Involved | Overhead | 155 | 32475 | 36.5732 | -121.5769 | WIRE DOWN HOT N/OF HARD TAP WITH CGC# 412440846151 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0052990 | OH | Sus | 44763177 | No | 2021 | APR | Yes | Open Circuit | 1623031 | CSO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 1825 | 20210429 | 1030 | 1336898 | 92 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 552 | 37.0118 | -121.8331 | 1 SOURCE SIDE CGC 316093319185 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0054827 | OH | Sus | 31537496 | No | 2021 | APR | Yes | Line to Ground | 1624256 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN BENITO-2104 | 182742104 | RECLOSER | 88772 | 20210501 | 422 | 1338394 | 716 | Distribution Circuit | 3rd Party | Vehicle | 135 | 24214 | 36.904 | -121.6087 | SW 139 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0055697 | OH | Sus | 0 | No | 2021 | MAY | Yes | Line to Line | 1624672 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | FUSE | 7537 | 20210510 | 1528 | 1345298 | 497 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 2007 | 36.572 | -121.9054 | 5P SS/OF 7625 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0059485 | OH | Sus | 44787071 | No | 2021 | MAY | Yes | Line to Ground | 1627372 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HOLLISTER-2102 | 182492102 | FUSE | 9765 | 20210513 | 708 | 1347671 | 534 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 10146 | 37.0678 | -121.2177 | 1 POLE LD SIDE OF MTR#1009290960 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0060792 | OH | Sus | 0 | No | 2021 | MAY | Yes | Line to Line | 1628195 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 5151 | 20210523 | 842 | 1356724 | 254 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 2604 | 37.111 | -122.0899 | BOYNTON-3459 / 831-331-6620: at C/O 4149 | Clear-32-90 F | Conductor, Overhead | On Ground | 21-0064842 | OH | Sus | 44815089 | No | 2021 | MAY | Yes | Line to Line | 1631333 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN BENITO-2101 | 182742101 | OTHER | 50423 | 20210612 | 1821 | 1371735 | 979 | Distribution Circuit | Equipment Failure/Involved | Overhead | 193 | 149464 | 36.8394 | -121.567 | 5 SPANS SOURCE SIDE OF 50423 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0073554 | OH | Sus | 31543320 | No | 2021 | JUN | Yes | Line to Ground | 1636770 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | FUSE | 5501 | 20210618 | 242 | 1377113 | 691 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 47725 | 37.1431 | -122.1318 | 1 S/OF CGC#315269624200 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0075960 | OH | Sus | 31543984 | No | 2021 | JUN | Yes | Line to Ground | 1638353 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5901 | 20210627 | 2209 | 1386354 | 825 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 4239 | 37.0944 | -121.9716 | 1 NE/OF CGC 315720821917 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0080653 | OH | Sus | 31544811 | No | 2021 | JUN | Yes | Line to Ground | 1642309 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 84785 | 20210630 | 809 | 1388628 | 334 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 3786 | 37.0393 | -121.9768 | 1/2 SPAN LD SIDE OF FOCU 8321 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0082163 | OH | Sus | 31544958 | No | 2021 | JUN | Yes | Line to Ground | 1643516 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER | WIRE DOWN BET 3209 & 5981 | 20210714 | 548 | 1403861 | 674 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 31904 | 37.0474 | -121.9525 | BET 3209 & 5981 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0089261 | OH | Sus | 0 | No | 2021 | JUL | Yes | Open Circuit | 1648075 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | FUSE | 3583 | 20210724 | 617 | 1412895 | 835 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 11690 | 37.1389 | -122.1011 | 6 SPANS LD SIDE OF 3583 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 21-0094362 | OH | Sus | 44919341 | No | 2021 | JUL | Yes | Line to Ground | 1651231 | CSO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | JUMPER | 9133 | 20210731 | 519 | 1424801 | 461 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 2801 | 37.1903 | -122.1251 | Sloan 408-212-1099: 18500 Kings Creek | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0097888 | OH | Sus | 44927444 | No | 2021 | JUL | Yes | Force Out | 1653507 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER | 4285 | 20210803 | 1032 | 1429672 | 392 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 4988 | 37.1346 | -122.0242 | WIRE DOWN HOT 3 NW OF CGC# 315575123938 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0099161 | OH | Sus | 44930791 | No | 2021 | AUG | Yes | Open Circuit | 1654318 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8239 | 20210803 | 317 | 1429360 | 892 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7249 | 37.1186 | -121.964 | 2 N/OF CGC# 100000042088 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0098943 | OH | Sus | 44930440 | No | 2021 | AUG | Yes | Line to Ground | 1654185 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | CAMP EVERS-2105 | 83622105 | RECLOSER | 12590 | 20210829 | 1027 | 1457510 | 392 | Distribution Circuit | Vegetation | Tree - fell into line | 348 | 61016 | 37.0633 | -122.0798 | 6807 SAN LORENZO WAY- FELTON | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0110772 | OH | Sus | 31550705 | No | 2021 | AUG | Yes | Line to Ground | 1661902 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 10728 | 20210907 | 34 | 1463338 | 580 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2992 | 1440514 | 37.0665 | -122.0797 | IFO 12415 LORENZO AVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0113972 | OH | Sus | 44970616 | No | 2021 | SEP | Yes | Line to Line | 1663741 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | RECLOSER | 439972 | 20210911 | 204 | 1468645 | 833 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 46522 | 37.0195 | -121.8841 | 1P SOURCE-SIDE OF 12673- END OF RYDER RD at C/O 12673 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0116314 | OH | Sus | 31551529 | No | 2021 | SEP | Yes | Three Phase Fault | 1664955 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER | 5206 | 20210925 | 1354 | 1480587 | 520 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 21640 | 37.0954 | -122.0857 | 6 LD SIDE OF 5149- 244 FRITCH CREEK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0122381 | OH | Sus | 44991097 | No | 2021 | SEP | Yes | Line to Ground | 1668714 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 5957 | 20211012 | 1322 | 1495960 | 190 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 3800 | 37.0051 | -121.9393 | BEHIND 520 LAGUNITA DR | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0129980 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1673648 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | RECLOSER | 5178 | 20211014 | 1204 | 1497618 | 437 | Distribution Circuit | Vegetation | Tree - fell into line | 268 | 55131 | 37.0324 | -121.9467 | 2 SPAN SS OF CGC 315805920584- 5382 SOQUEL SAN JOSE RD(FC/O'S 8351) | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0131098 | OH | Sus | 31554795 | No | 2021 | OCT | Yes | Line to Ground | 1674219 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | JUMPER | WIRE DOWN 1/2 SPAN S/S CGC315124824344 | 20211020 | 2337 | 1503880 | 1270 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2540 | 37.1563 | -122.1738 | 1/2 SPAN S/S OF CGC315124824344- 555 POND VIEW | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0134618 | OH | Sus | 45018450 | No | 2021 | OCT | Yes | Line to Ground | 1676470 | CAW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8983 | 20211021 | 705 | 1504208 | 613 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 17825 | 37.0307 | -122.1429 | 1 SPAN LOAD SIDE OF 288711- 3131 SMITH GRADE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0134481 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1676425 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 11006 | 20211022 | 1320 | 1506067 | 403 | Distribution Circuit | 3rd Party | Vehicle | 104 | 18526 | 37.05 | -122.0657 | 4 SPANS N/O 1706- E. ZAYANTE & REDWOOD CIRCLE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135179 | OH | Sus | 45019561 | No | 2021 | OCT | Yes | Line to Ground | 1676793 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 40285 | 20211028 | 2335 | 1524877 | 1157 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 29926 | 36.5854 | -121.9211 | 4025 COSTADO RD- PEBBLE BEACH | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0139593 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1680046 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 10719 | 20211101 | 2143 | 1527639 | 1315 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 10520 | 37.0863 | -122.1043 | 2 SPANS SS OF CGC 315337221760 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0141099 | OH | Sus | 45038344 | No | 2021 | NOV | Yes | Line to Ground | 1681111 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2105 | 83692105 | OTHER | WIRE DOWN 1 E/OF CGC# 315964317506 | 20211102 | 1711 | 1532568 | 1078 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 10678 | 36.9724 | -121.8817 | 1 E/OF CGC# 315964317506- 430 BONITA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0141480 | OH | Sus | 45038774 | No | 2021 | NOV | Yes | Line to Ground | 1681333 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | JOLON-1102 | 182981102 | OTHER | WIRE DOWN 3 P/W/OF MTR# 1009993361 | 20211108 | 1100 | 1537425 | 312 | Distribution Circuit | Equipment Failure/Involved | Overhead | 138 | 27745 | 35.9663 | -121.0959 | WIRE DOWN 3P W/OF MTR# 1009993361 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0143336 | OH | Sus | 0 | No | 2021 | NOV | Yes | Open Circuit | 1682694 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 1607 | 20211109 | 2250 | 1539340 | 902 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 11726 | 37.1931 | -122.156 | 4 SS/OF CGC 315163725683- 805 VIA RATON | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0144214 | OH | Sus | 45061380 | No | 2021 | NOV | Yes | Line to Ground | 1683191 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 11943 | 20211110 | 354 | 1539369 | 514 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 40606 | 37.0112 | -122.0442 | METER # 1006212609 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0144227 | OH | Sus | 0 | No | 2021 | NOV | Yes | Line to Ground | 1683195 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 7807 | 20211116 | 2157 | 1547255 | 980 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 16660 | 36.9884 | -121.7391 | JUST LOAD SIDE OF7807 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0146669 | OH | Sus | 45068785 | No | 2021 | NOV | Yes | Line to Ground | 1685290 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | GREEN VALLEY-2101 | 83192101 | FUSE | 12347 | 20211118 | 1628 | 1549489 | 987 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 8155 | 37.0056 | -121.7685 | CGC 316291518735- - 275 APPLE VALLEY LN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0148215 | OH | Sus | 31578743 | No | 2021 | NOV | Yes | Line to Ground | 1686353 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12758 | 20211120 | 1959 | 1552210 | 1039 | Distribution Circuit | Vegetation | Tree - fell into line | 271 | 81491 | 37.1486 | -122.1745 | TAP LINE C/O 10043- 15055 HWY 236 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0149081 | OH | Sus | 31578862 | No | 2021 | NOV | Yes | Three Phase Fault | 1687019 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 7295 | 20211216 | 223 | 1574192 | 705 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 40890 | 37.0325 | -122.0872 | 1485 MCLELLAN | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158857 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1695878 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 74170 | 20211216 | 241 | 1574237 | 967 | Distribution Circuit | Vegetation | Tree - fell into line | 1017 | 395572 | 37.0883 | -122.0884 | STARTING 1 LD SIDE OF CGC 315370121612- THEN 5 SP TWD 8729- BETWEEN SAP. 101675114 & SAP 101675109 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158772 | OH | Sus | 0 | No | 2021 | DEC | Yes | Three Phase Fault | 1695780 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5901 | 20211216 | 238 | 1574227 | 698 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 11866 | 37.0944 | -121.9716 | 5 LOAD SIDE OF 5901 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158891 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1695925 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | FUSE | 1491 | 20211216 | 505 | 1574325 | 781 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 31240 | 36.5057 | -121.9352 | CGC 411390644052 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0158794 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1695804 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5525 | 20211222 | 621 | 1579008 | 589 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4712 | 37.0247 | -122.2116 | 1 LD SIDE OF 3153 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0160103 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1697518 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 9799 | 20211223 | 558 | 1579809 | 533 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1066 | 37.1561 | -122.1715 | 2 SPANS LD SIDE OF 9799 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160262 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1697698 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 12435 | 20211223 | 445 | 1579551 | 322 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 5474 | 37.1378 | -122.0133 | 2 SPANS LD-SIDE OF CGC# 315587223861 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0160268 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1697708 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 5901 | 20211223 | 137 | 1579487 | 633 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 10761 | 37.0944 | -121.9716 | MID SPAN LD SIDE OF CGC 315720821917 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160219 | OH | Sus | 31588224 | No | 2021 | DEC | Yes | Line to Ground | 1697647 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 2701 | 20211223 | 1906 | 1580240 | 1354 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1354 | 37.0215 | -121.8267 | 1 SPAN LD SIDE OF 2701 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160357 | OH | Sus | 45100793 | No | 2021 | DEC | Yes | Line to Ground | 1697800 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1101 | 182941101 | FUSE | 2181 | 20220104 | 919 | 1594715 | 225 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 84 | 18900 | 36.4895 | -121.9363 | 19 MENTONE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0005943 | OH | Sus | 31588922 | No | 2022 | JAN | Yes | Line to Ground | 1700904 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER | HOT WIRE DOWN @ 700 EL SOLYO | 20220105 | 100 | 1595428 | 551 | Distribution Circuit | Vegetation | Tree - branch fell on line | 57 | 28767 | 37.0673 | -122.0867 | 700 EL SOLYO HEIGHTS RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0006257 | OH | Sus | 45107666 | No | 2022 | JAN | Yes | Open Circuit | 1701081 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG TREES-0402 | 83050402 | FUSE | 5215 | 20220106 | 2300 | 1597068 | 876 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 36468 | 37.0325 | -122.0765 | 1 N/OF CGC 315412919701- 1215 SCENIC DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0007152 | OH | Sus | 31589721 | No | 2022 | JAN | Yes | Line to Ground | 1701395 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 7295 | 20220123 | 528 | 1609758 | 825 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 13697 | 37.0325 | -122.0872 | CGC 315370019702- 1880 ALTAMONT DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0013147 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Line | 1704479 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | JUMPER | WIRE DOWN 1/2 SP N/OF FUCO 67433 | 20220203 | 1328 | 1620567 | 504 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1008 | 37.0836 | -122.2535 | 1/2 SP N/OF FUCO 67433 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0018358 | OH | Sus | 45164317 | No | 2022 | FEB | Yes | Open Circuit | 1707393 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 1181 | 20220227 | 145 | 1638530 | 950 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 10450 | 36.9798 | -121.8912 | 175 VALENCIA DR | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0027192 | OH | Sus | 0 | No | 2022 | FEB | Yes | Line to Ground | 1713113 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 6975 | 20220314 | 2149 | 1648600 | 345 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 17250 | 36.5797 | -121.9204 | 1 SPAN SE/ OF 6975- 4133 SUNRIDGE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0033806 | OH | Sus | 45211273 | No | 2022 | MAR | Yes | Line to Ground | 1717081 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 7593 | 20220327 | 1453 | 1656781 | 356 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 24524 | 37.1057 | -121.9724 | FUCO 8241- 24133 SCHULTIES RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0039038 | OH | Sus | 0 | No | 2022 | MAR | Yes | Line to Ground | 1720379 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6059 | 20220327 | 2059 | 1657330 | 8 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 160 | 37.1187 | -121.975 | 8241 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0039038 | OH | Sus | 0 | No | 2022 | MAR | Yes | Line to Ground | 1720429 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER | 12838 | 20220328 | 348 | 1657449 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 54363 | 37.1272 | -122.1236 | 2 SPANS LD SIDE OF CGC 315235923354 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0039129 | OH | Sus | 45229394 | No | 2022 | MAR | Yes | Line to Ground | 1720474 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | JUMPER | WIRE DOWN 615 WENTE ST | 20220411 | 1806 | 1669896 | 359 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4152 | 37.0836 | -122.0849 | 615 WENTE ST | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0045908 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Ground | 1724884 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | FUSE | 5173 | 20220411 | 1621 | 1669542 | 247 | Distribution Circuit | Vegetation | Tree - branch fell on line | 61 | 15067 | 37.1011 | -122.1017 | 165 FERN LN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0045822 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Ground | 1724816 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 891361 | 20220411 | 1447 | 1669811 | 561 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 10098 | 37.1892 | -122.1431 | 5 LD SIDE OF 891361 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0045643 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Ground | 1724791 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 1847 | 20220411 | 1503 | 1669340 | 336 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 336 | 37.0635 | -122.0696 | 1755 HIHN RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0045752 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Ground | 1724757 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5419 | 20220414 | 1215 | 1672650 | 530 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 24910 | 37.1244 | -122.1281 | 245 ST FRANCIS DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0048349 | OH | Sus | 45256067 | No | 2022 | APR | Yes | Line to Ground | 1726778 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9719 | 20220416 | 724 | 1674199 | 601 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 9616 | 37.1471 | -122.1341 | 233 DOUGLAS BOULDER CREEK | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0050590 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Ground | 1728695 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN 2 LD SIDE OF 5203 | 20220416 | 817 | 1674409 | 816 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 22032 | 37.0395 | -122.0825 | 2 LD SIDE OF 5203- 846 BROOKSIDE DR | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0050529 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Ground | 1728630 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 823 | 20220421 | 639 | 1678073 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 586 | 37.044 | -122.1497 | 160 PINE FLAT RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0052425 | OH | Sus | 45262533 | No | 2022 | APR | Yes | Line to Ground | 1729871 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | JUMPER | WIRE DOWN | 20220422 | 621 | 1679082 | 603 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 20937 | 36.3964 | -121.8793 | 2 SPANS LOAD SIDE OF 187705 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0053112 | OH | Sus | 45264124 | No | 2022 | APR | Yes | Line to Ground | 1730193 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1102 | 182291102 | OCB | 1102/2 | 20220424 | 554 | 1680202 | 752 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2143 | 164725 | 36.5569 | -121.8976 | 2 S/OF 6247 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0053749 | OH | Sus | 31601681 | No | 2022 | APR | Yes | Multi-Fault | 1730597 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | OTHER | WIRE DOWN | 20220425 | 1110 | 1681163 | 560 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 10188 | 37.0207 | -122.1297 | 1 SOURCE SIDE OF 209531 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0054119 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Ground | 1730952 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 5409 | 20220425 | 1647 | 1681286 | 338 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 2366 | 37.0657 | -122.152 | 1P SS OF CGC# 315182620896 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0054277 | OH | Sus | 45267137 | No | 2022 | APR | Yes | Line to Line | 1730989 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | SWITCH | 2565 | 20220427 | 42 | 1682179 | 6 | Distribution Circuit | Company Initiated | Return Circuit Normal | 165 | 990 | 36.9825 | -121.872 | at 59545 TWD 4213 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0054796 | OH | Sus | 45268700 | No | 2022 | APR | Yes | None | 1731366 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 5781 | 20220504 | 1305 | 1688379 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3250 | 37.0447 | -121.8152 | 1 P LD SIDE OF | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0057946 | OH | Sus | 31602509 | No | 2022 | MAY | Yes | Line to Ground | 1733614 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 5461 | 20220524 | 722 | 1708576 | 442 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 9724 | 37.1383 | -122.1436 | 1 N/OF CGC# 315213223482- 500 BROOK LN BOULDER CREEK | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0065626 | OH | Sus | 31604254 | No | 2022 | MAY | Yes | Line to Line | 1738920 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN | 20220529 | 1158 | 1713557 | 388 | Distribution Circuit | Vegetation | Tree - branch fell on line | 372 | 55881 | 37.0331 | -122.0878 | 1636 LAKESIDE DR- FELTON | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0067956 | OH | Sus | 31604821 | No | 2022 | MAY | Yes | Open Circuit | 1740263 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 753753 | 20220530 | 1256 | 1714026 | 596 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1192 | 37.0994 | -122.1169 | 2 SPANS LD SIDE OF 753753 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0068064 | OH | Sus | 0 | No | 2022 | MAY | Yes | Line to Ground | 1740376 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | JUMPER | WIRE DOWN 2 SPANS LD SIDE OF 6085 | 20220607 | 717 | 1721018 | 687 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 11679 | 36.2549 | -121.787 | WIRE DOWN 2 SPANS LD SIDE OF 6085 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0070940 | OH | Sus | 0 | No | 2022 | JUN | Yes | Line to Ground | 1742482 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | RESERVATION ROAD-1102 | 182731102 | OCB | 1102/2 | 20220609 | 905 | 1726310 | 474 | Distribution Circuit | 3rd Party | Aircraft | 2116 | 299647 | 36.6242 | -121.6886 | 1 LD SIDE OF 24809 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0072059 | OH | Sus | 0 | No | 2022 | JUN | Yes | Line to Ground | 1743143 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 711 | 20220611 | 705 | 1728344 | 445 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 9790 | 37.0529 | -122.1604 | BOYNTON-3459 / 831-331-6620: 156 COUNTRY ESTATES DR | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0073199 | OH | Sus | 45340016 | No | 2022 | JUN | Yes | Line to Ground | 1743765 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER | 95690 | 20220612 | 1232 | 1729428 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 2027 | 52515 | 37.1249 | -122.125 | 230 HOOT OWL WAY | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0073414 | OH | Sus | 45341021 | No | 2022 | JUN | Yes | Line to Line | 1743983 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 33542 | 20220613 | 2248 | 1730638 | 1128 | Distribution Circuit | Vegetation | Tree - fell into line | 525 | 112436 | 37.0906 | -122.0456 | 1 SPAN LD SIDE OF 10294 - 10325 LOMPICO RD at LR 10294 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0073900 | OH | Sus | 35355991 | No | 2022 | JUN | Yes | Line to Line | 1744381 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER | 944178 | 20220627 | 1038 | 1743306 | 419 | Distribution Circuit | Vegetation | Tree - branch fell on line | 752 | 86400 | 37.0926 | -122.0964 | 3 SPANS LOADSIDE OF 5149 - FRISCH CREEK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0078981 | OH | Sus | 31607190 | No | 2022 | JUN | Yes | Line to Ground | 1748309 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 95050 | 20220707 | 1731 | 1750955 | 426 | Distribution Circuit | Vegetation | Tree - fell into line | 1964 | 131640 | 37.0888 | -122.0877 | 10275 RIVERSIDE RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0082926 | OH | Sus | 31608031 | No | 2022 | JUL | Yes | Line to Line | 1750503 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | OTHER | HOT WIRE DOWN @ 290 RIDGE RD | 20220712 | 1631 | 1754725 | 498 | Distribution Circuit | Vegetation | Tree - branch fell on line | 123 | 19778 | 37.1014 | -122.087 | CGC 315374822324 - 290 RIDGE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0084510 | OH | Sus | 45378497 | No | 2022 | JUL | Yes | Open Circuit | 1751615 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | RECLOSER | 9112 | 20220715 | 1001 | 1757018 | 564 | Distribution Circuit | Vegetation | Tree - fell into line | 3093 | 181138 | 36.6047 | -121.934 | 1 N/OF CGC# 411394847620 - 2810 CONGRESS RD.- PEBBLE BEACH- CA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0085770 | OH | Sus | 31608944 | No | 2022 | JUL | Yes | Line to Ground | 1752499 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 95050 | 20220717 | 224 | 1758258 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 1966 | 256257 | 37.0883 | -122.0884 | 4 SPANS LD SIDE OF 5157 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0086234 | OH | Sus | 31609100 | No | 2022 | JUL | Yes | Line to Ground | 1752818 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 4295 | 20220727 | 1614 | 1766808 | 574 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 14350 | 37.033 | -122.0105 | 1 LD SIDE OF CGC 315598819597 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0090529 | OH | Sus | 45392567 | No | 2022 | JUL | Yes | Line to Ground | 1755562 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 5445 | 20220728 | 159 | 1766989 | 603 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5427 | 37.1301 | -122.1341 | 5 N/OF CGC 315234223265- 313 MADRONE DR | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0090595 | OH | Sus | 31610337 | No | 2022 | JUL | Yes | Line to Ground | 1755608 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 9005 | 20220730 | 346 | 1768711 | 434 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 9548 | 37.0318 | -122.1369 | CGC 315231520080 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0091597 | OH | Sus | 31611169 | No | 2022 | JUL | Yes | Line to Line | 1756151 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 11327 | 20220809 | 2029 | 1777339 | 491 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 491 | 36.9868 | -121.8846 | 1 SPAN SOURCE SIDE CGC 315962018038 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0095584 | OH | Sus | 45406019 | No | 2022 | AUG | Yes | Line to Ground | 1758905 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | RECLOSER | 11046 | 20220814 | 831 | 1780575 | 521 | Distribution Circuit | Vegetation | Tree - fell into line | 352 | 69968 | 36.9995 | -122.0078 | CGC# 315679019795 - 501 HAPPY VALLEY ROAD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0097289 | OH | Sus | 35377325 | No | 2022 | AUG | Yes | Line to Ground | 1760134 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 1301 | 20220817 | 1047 | 1783608 | 169 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 507 | 36.9967 | -121.8857 | 2225 TROUT GULCH RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0098707 | OH | Sus | 45416975 | No | 2022 | AUG | Yes | Line to Ground | 1761105 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 11384 | 20220819 | 1753 | 1785589 | 182 | Distribution Circuit | Vegetation | Tree - branch fell on line | 430 | 42362 | 37.0534 | -122.0437 | 3 MANZANITA RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0099956 | OH | Sus | 31613636 | No | 2022 | AUG | Yes | Line to Ground | 1761705 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | RECLOSER | 563516 | 20220827 | 1639 | 1793204 | 142 | Distribution Circuit | Vegetation | Tree - branch fell on line | 860 | 37856 | 36.5785 | -121.9279 | at 6809 TWD CGC 411404646421 - 3110 SPRUANCE RD.- PEBBLE BEACH- CA | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0102739 | OH | Sus | 31614668 | No | 2022 | AUG | Yes | Line to Ground | 1763787 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | JUMPER | 6445 HIGH SIDE JUMPER | 20220829 | 1331 | 1794243 | 778 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 5446 | 36.5804 | -121.9186 | 1/2 SPAN N/OF 6445 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0103218 | OH | Sus | 31614890 | No | 2022 | AUG | Yes | Line to Ground | 1764167 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2012 | 20220903 | 1204 | 1798314 | 754 | Distribution Circuit | Vegetation | Tree - fell into line | 499 | 302891 | 36.3306 | -121.8831 | MIDSPAN BETWENN FUCO 7059 AND FUCO 9567 ON MAINLINE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0105479 | OH | Sus | 31615224 | No | 2022 | SEP | Yes | Multi-Fault | 1765457 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 2101 | 20220918 | 1545 | 1814921 | 445 | Distribution Circuit | Vegetation | Tree - branch fell on line | 741 | 81315 | 37.0926 | -122.0964 | 2 SPANS LD SIDE OF 5743 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0111708 | OH | Sus | 0 | No | 2022 | SEP | Yes | Line to Ground | 1769741 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 1101 | 20220919 | 223 | 1815726 | 427 | Distribution Circuit | Vegetation | Tree - fell into line | 718 | 67226 | 37.0926 | -122.0966 | 1 SPAN SOURCE SIDE CGC 315292922407 - 11722 CLEAR CREEK | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0111862 | OH | Sus | 0 | No | 2022 | SEP | Yes | Line to Ground | 1769899 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8985 | 20220919 | 55 | 1815678 | 1346 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 30958 | 37.0288 | -122.1405 | 4 E/OF 8985 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0111924 | OH | Sus | 0 | No | 2022 | SEP | Yes | Line to Line | 1769954 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 5459 | 20220923 | 1244 | 1820147 | 257 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 5486 | 37.1385 | -122.1432 | 1 SPAN LD SIDE OF 457495 - 421 HAZEL BRAKE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0114356 | OH | Sus | 31616911 | No | 2022 | SEP | Yes | Line to Line | 1771482 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 12155 | 20221001 | 859 | 1825648 | 547 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1641 | 37.0046 | -121.7041 | 2 SPANS LOAD SIDE OF FUCO 12155 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0116922 | OH | Sus | 31617502 | No | 2022 | OCT | Yes | Line to Ground | 1773348 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 937291 | 20221008 | 939 | 1831864 | 829 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 10777 | 37.1186 | -121.964 | 23990 SHULTIES RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0119392 | OH | Sus | 35393553 | No | 2022 | OCT | Yes | Line to Ground | 1775062 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | JUMPER | OJ'S 1 NE/OF CGC 316341018960 | 20221015 | 1246 | 1837948 | 294 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 1 | 294 | 37.0141 | -121.7537 | 523 HAZEL DELL RD WATSONVILLE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0121809 | OH | Sus | 31618641 | No | 2022 | OCT | Yes | Line to Ground | 1776664 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1101 | 182291101 | FUSE | 8171 | 20221016 | 643 | 1838275 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 958 | 36.5445 | -121.8848 | 1 POLE LOAD SIDE C/O 8171 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0121867 | OH | Sus | 31618701 | No | 2022 | OCT | Yes | Line to Ground | 1776731 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | FUSE | 97951 | 20221020 | 124 | 1841139 | 1012 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1012 | 37.0965 | -122.1069 | LD SIDE OF 97951 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0123087 | OH | Sus | 35398128 | No | 2022 | OCT | Yes | Line to Ground | 1777711 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SEACLIFF-0401 | 83500401 | RECLOSER | 12946 | 20221020 | 154 | 1841140 | 797 | Distribution Circuit | Vegetation | Tree - fell into line | 213 | 162573 | 36.9875 | -121.9186 | 2 LD SIDE OF 7533 - 3350 VIENNA DRIVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0123084 | OH | Sus | 31618983 | No | 2022 | OCT | Yes | Line to Ground | 1777707 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | TRIP-SAVER | 9773 | 20221107 | 32 | 1855581 | 462 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 13398 | 37.1288 | -122.1143 | MTR 1007591533 | Clear-32-90F | Conductor, Overhead | On Ground | 22-0128392 | OH | Sus | 35402182 | No | 2022 | NOV | Yes | Line to Ground | 1781818 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | OTHER | WIRE DWN 2035 TROUT GULCH | 20221108 | 914 | 1857197 | 366 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 6242 | 37.0184 | -121.8788 | 2035 SPARROW VALLEY RD APTOS | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0128997 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Ground | 1782158 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 5146 | 20221110 | 349 | 1859672 | 686 | Distribution Circuit | Vegetation | Tree - fell into line | 177 | 45682 | 37.0578 | -122.0595 | 1 SPAN SS OF C0244 - 8049 WEST ZAYANTE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0129876 | OH | Sus | 45515911 | No | 2022 | NOV | Yes | Line to Ground | 1782736 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER | 393582 | 20221122 | 446 | 1867419 | 285 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2136 | 138559 | 37.1284 | -122.1222 | 1 SPAN SOURCE SIDE OF CGC 315360523640 - 15515 FOREST HILL | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0133287 | OH | Sus | 45568218 | No | 2022 | NOV | Yes | Line to Ground | 1785088 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SAN JUSTO-1101 | 183181101 | FUSE | 4351 | 20221201 | 809 | 1872810 | 401 | Distribution Circuit | 3rd Party | Vehicle | 61 | 17101 | 36.8704 | -121.5913 | CGC #412455056635 - HWY 101 AND 156 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0135473 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1786659 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 5151 | 20221205 | 1316 | 1876655 | 739 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 8418 | 37.1109 | -122.0899 | 2 POLES LOAD SIDE OF CGC 315363822601 - 11155 LOVE CREEK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0136830 | OH | Sus | 31629615 | No | 2022 | DEC | Yes | Line to Ground | 1787686 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | TRIP-SAVER | 5479 | 20221205 | 812 | 1876249 | 340 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 4760 | 37.1292 | -122.1131 | 160 NELLY LN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0136646 | OH | Sus | 45580773 | No | 2022 | DEC | Yes | Line to Line | 1787604 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 83815 | 20221205 | 742 | 1876225 | 388 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4268 | 36.9946 | -122.0283 | LAST SPAN AT CGC 315540618443 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0136649 | OH | Sus | 0 | No | 2022 | DEC | Yes | Force Out | 1787611 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 125 | 20221206 | 643 | 1876961 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 14934 | 37.0115 | -121.9009 | 3 SPANS LOAD SIDE FUCO 125 - 318 REDWOOD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0136900 | OH | Sus | 0 | No | 2022 | DEC | Yes | Force Out | 1787735 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12992 | 20221209 | 629 | 1879370 | 652 | Distribution Circuit | Vegetation | Tree - branch fell on line | 697 | 186358 | 37.1991 | -122.1532 | 1 SPAN LD SIDE OF 9783 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0137797 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1788605 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | RESERVATION ROAD-1102 | 182731102 | OTHER | WIRE DOWN 1 SPAN LD SIDE OF 1007758249 | 20221209 | 623 | 1879494 | 412 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 6800 | 36.5153 | -121.528 | 1 SPAN LD SIDE OF MTR 1007758249 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 22-0137829 | OH | Sus | 45583727 | No | 2022 | DEC | Yes | Line to Ground | 1788675 | CSO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | OTHER | HOT WIRE DOWN 1 N/OF 5495 | 20221211 | 2328 | 1886556 | 1152 | Distribution Circuit | Vegetation | Tree - fell into line | 770 | 489202 | 37.1385 | -122.1295 | CGC 315244523665 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 22-0139110 | OH | Sus | 0 | No | 2022 | DEC | Yes | Open Circuit | 1789923 | CAW | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5215 | 20221211 | 41 | 1884551 | 1014 | Distribution Circuit | Vegetation | Tree - branch fell on line | 60 | 60840 | 37.0325 | -122.0765 | 3 SPANS LD SIDE 5215 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138854 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1789681 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | POINT MORETTI-1101 | 82931101 | FUSE | 8983 | 20221211 | 530 | 1885116 | 772 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 25768 | 37.0307 | -122.1429 | Brunelle- Mike 831 535 8751: 2700 Smith Grade | Clear-32-90F | Conductor, Overhead | On Ground | 22-0138898 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1789726 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER | BROKEN WIRE 3 P N/OF 6165 | 20221212 | 1105 | 1887181 | 499 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 998 | 37.0852 | -121.992 | 3 P N/OF 6165 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0139239 | OH | Sus | 0 | No | 2022 | DEC | Yes | Open Circuit | 1790094 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | OTHER | 2201/2 | 20221212 | 345 | 1886647 | 561 | Distribution Circuit | Vegetation | Tree - fell into line | 7839 | 2739310 | 36.5786 | -121.9085 | SKYLINE E/O FOREST RIDGE RD- 1P N/O LR 9638- 3\ P\ E\ O CR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0139126 | OH | Sus | 0 | No | 2022 | DEC | Yes | Open Circuit | 1789941 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6641 | 20221213 | 411 | 1887943 | 541 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 26257 | 37.016 | -121.8161 | 123 BUZZARD LAGOON | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0139426 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1790248 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8333 | 20221224 | 826 | 1896739 | 509 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 509 | 37.0583 | -121.971 | 1 P LD SIDE OF 8333 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0141165 | OH | Sus | 45602609 | No | 2022 | DEC | Yes | Line to Ground | 1792840 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | TRIP-SAVER | 6219 | 20221227 | 1111 | 1899141 | 609 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 13398 | 37.1841 | -122.1409 | 2 SPANS LD SIDE OF 6219 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0141703 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793389 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | FUSE | 6093 | 20221227 | 822 | 1898752 | 530 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 5388 | 37.0267 | -122.0251 | 2 SPANS SS OF CGC 100000004548 - 3556 LA MADRONA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0141583 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793262 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 5577 | 20221227 | 1234 | 1899304 | 688 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 66736 | 37.0487 | -122.0616 | 2 SPANS FROM CGC 315445620316 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0141725 | OH | Sus | 35416011 | No | 2022 | DEC | Yes | Line to Ground | 1793411 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2105 | 83692105 | JUMPER | 5805 | 20221227 | 2309 | 1900024 | 414 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 8514 | 36.9723 | -121.8806 | OJ 3 SPANS SS OF CGC 315964317506 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0141857 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793551 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2105 | 83692105 | JUMPER | WIRE DOWN E OF CGC 315964317506 | 20221228 | 835 | 1900201 | 400 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 400 | 36.9724 | -121.8813 | E OF CGC 315964317506 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0141914 | OH | Sus | 0 | No | 2022 | DEC | Yes | Open Circuit | 1793636 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | SEACLIFF-0401 | 83500401 | FUSE | 11573 | 20221228 | 400 | 1900044 | 644 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 14168 | 37.011 | -121.9256 | 4 SPANS LOAD SIDE OF FUCO 11573 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0141870 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793564 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER | 65444 | 20221229 | 2325 | 1901704 | 938 | Distribution Circuit | Vegetation | Tree - fell into line | 180 | 168840 | 37.1278 | -122.1229 | 476 RIVER RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142138 | OH | Sus | 35419202 | No | 2022 | DEC | Yes | Line to Ground | 1793910 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | FUSE | 753753 | 20221229 | 847 | 1901216 | 475 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 950 | 37.0994 | -122.1169 | 4 LD SIDE OF 753753 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142053 | OH | Sus | 31633909 | No | 2022 | DEC | Yes | Line to Ground | 1793805 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2705 | 20221230 | 449 | 1901777 | 508 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 13208 | 37.0005 | -121.7403 | 1 SPAN SS OF CGC 316304518599 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142157 | OH | Sus | 31634024 | No | 2022 | DEC | Yes | Line to Ground | 1793929 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN 3 SPANS NORTH OF CGC 315700521449 | 20230102 | 754 | 1909579 | 251 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 502 | 37.0813 | -121.9754 | 3 SPANS NORTH OF CGC 315700521449 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0004655 | OH | Sus | 0 | No | 2023 | JAN | Yes | Open Circuit | 1795270 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2203 | 182852203 | JUMPER | WIRE DOWN S/E/OF 10421 | 20230106 | 1712 | 1925445 | 372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 82 | 30368 | 36.5658 | -121.9344 | S/E/OF 10421 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 23-0008523 | OH | Sus | 0 | No | 2023 | JAN | Yes | Open Circuit | 1798451 | CSO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | JUMPER | WIRE DOWN 1 SPAN LD SIDE OF CGC 411387846285 | 20230113 | 916 | 1952035 | 564 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1170 | 36.5688 | -121.9341 | 1 LOAD SIDE OF CGC 411387846285 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015385 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1804294 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 45255 | 20230113 | 905 | 1951478 | 387 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 15093 | 36.5862 | -121.9149 | 3 SPANS LD SIDE OF 45255 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015199 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1804225 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 5141 | 20230115 | 1625 | 1956176 | 109 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 1308 | 37.0947 | -122.0864 | JWO 5141 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016745 | OH | Sus | 0 | No | 2023 | JAN | Yes | Force Out | 1805449 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | OTTER-1101 | 182941101 | RECLOSER | 2052 | 20230115 | 2026 | 1956373 | 307 | Distribution Circuit | Vegetation | Tree - fell into line | 585 | 44299 | 36.3999 | -121.9022 | BETWEEN CGC 411486040122 & 411486440139 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016793 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1805488 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 5955 | 20230115 | 1645 | 1956202 | 94 | Distribution Circuit | Equipment Failure/Involved | Overhead | 164 | 15416 | 37.0022 | -121.942 | CGC# 315806418891 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 23-0016750 | OH | Sus | 0 | No | 2023 | JAN | Yes | Force Out | 1805453 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 415734 | 20230115 | 2353 | 1956451 | 632 | Distribution Circuit | Environmental/External | Flood/Erosion | 97 | 38667 | 37.0316 | -122.1893 | 4 POLES LD SIDE OF 669873 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016852 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1805550 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | OTHER | WIRE DOWN AT 6147 | 20230118 | 1733 | 1961414 | 408 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6188 | 605581 | 36.5875 | -121.9434 | 6147 ON MAINLINE | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 23-0018564 | OH | Sus | 0 | No | 2023 | JAN | Yes | Open Circuit | 1806639 | CSO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 9181 | 20230122 | 2004 | 1965041 | 894 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 12516 | 37.2288 | -122.148 | 1 SPAN SS OF CGC 315193027700 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0019970 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1807403 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 2689 | 20230122 | 2326 | 1965146 | 1484 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 47488 | 37.1274 | -122.0181 | 1 SS OF CGC 315553623434 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0020240 | OH | Sus | 45647468 | No | 2023 | JAN | Yes | Line to Ground | 1807596 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2705 | 20230122 | 1134 | 1964674 | 155 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 26 | 4030 | 37.0005 | -121.7403 | 2 SPANS SOURCE SIDE OF 12349 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0019882 | OH | Sus | 0 | No | 2023 | JAN | Yes | Three Phase Fault | 1807321 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 7959 | 20230123 | 47 | 1965165 | 1020 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 28700 | 37.0696 | -122.0916 | 2 SPANS LD SIDE OF 7959 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0019984 | OH | Sus | 45647074 | No | 2023 | JAN | Yes | Line to Line | 1807417 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | GREEN VALLEY-2101 | 83192101 | JUMPER | WIRE DOWN 1 P LD SIDE OF 6153 | 20230127 | 1412 | 1970137 | 1398 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 12582 | 36.9996 | -121.774 | 3 P LD SIDE OF 6153 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 23-0022540 | OH | Sus | 31635764 | No | 2023 | JAN | Yes | Open Circuit | 1808722 | CAW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | FUSE | 8021 | 20230201 | 1325 | 1974084 | 366 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 15450 | 36.5868 | -121.9097 | .5 SPANS LS OF CGC 411460546878 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0024000 | OH | Sus | 31636126 | No | 2023 | FEB | Yes | Line to Ground | 1809799 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2102 | 83252102 | FUSE | 2455 | 20230206 | 742 | 1977880 | 403 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 9672 | 37.0111 | -121.9871 | CGC 315660519002 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0025628 | OH | Sus | 45659348 | No | 2023 | FEB | Yes | Line to Ground | 1810955 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | FUSE | 2713 | 20230209 | 1314 | 1981045 | 354 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 5862 | 36.2534 | -121.7853 | 1 LD SIDE OF 2713 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0027161 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1811948 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER | 555726 | 20230214 | 1325 | 1985043 | 411 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1172 | 106702 | 37.0858 | -122.0674 | FUCO 4581 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0028768 | OH | Sus | 45672040 | No | 2023 | FEB | Yes | Line to Ground | 1813210 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | SWITCH | 8509 | 20230302 | 1143 | 2019736 | 8 | Distribution Circuit | Company Initiated | Return Circuit Normal | 294 | 2352 | 36.9483 | -121.8512 |  | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0031348 | OH | Sus | 0 | No | 2023 | MAR | Yes | None | 1820824 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI SUB | 8293 | SWITCH | POINT MORETTI | 20230303 | 834 | 2020930 | 580 | Distribution Circuit | Vegetation | Tree - fell into line | 670 | 388600 | 37.0313 | -122.1875 | 5 SPANS N/O R61 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0039287 | OH | Sus | 0 | No | 2023 | MAR | Yes | Force Out | 1821207 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 10427 | 20230306 | 312 | 2024484 | 1033 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1033 | 37.1044 | -122.0502 | 1 N/OF 10427 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0040624 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1822328 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2104 | 83622104 | FUSE | 6079 | 20230310 | 113 | 2030430 | 947 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 49244 | 37.0556 | -122.0327 | 150 GREEN VALLEY RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0042818 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1823600 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | SWITCH | 840759 | 20230310 | 915 | 2030636 | 579 | Distribution Circuit | Environmental/External | Flood/Erosion | 306 | 50936 | 37.0994 | -122.0531 | JUST LD SIDE OF 840759 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0042688 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1823652 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | FUSE | 6647 | 20230310 | 1227 | 2031016 | 602 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 1862 | 37.0266 | -121.7801 | 3 SPANS LD SIDE OF 6647 & 2 SPANS LD SIDE OF CGC #316224819668 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0043160 | OH | Sus | 0 | No | 2023 | MAR | Yes | Force Out | 1823766 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 9125 | 20230312 | 950 | 2033178 | 509 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 10287 | 37.1004 | -122.086 | 1 P/SS OF 5151 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0043712 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1824228 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | JUMPER | 5232 | 20230312 | 2333 | 2033805 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 788 | 824296 | 37.0752 | -122.054 | at 9247 & 4 LD SIDE OF 426822 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0043919 | OH | Sus | 0 | No | 2023 | MAR | Yes | Open Circuit | 1824433 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER | WIRE DOWN HOT 3 LD SIDE OF 6191 | 20230312 | 807 | 2033136 | 476 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 43178 | 37.052 | -122.0633 | 3 LD SIDE OF 6191 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0043710 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1824226 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | HATTON-1101 | 182291101 | JUMPER | WIRE DOWN HOT 2 SPANS LD SD OF 8171 | 20230313 | 1056 | 2034389 | 295 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 590 | 36.5453 | -121.8849 | 2 SPANS LD SD OF 8171 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 23-0044111 | OH | Sus | 0 | No | 2023 | MAR | Yes | Open Circuit | 1824522 | CSO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | JUMPER | WIRE DWN | 20230317 | 828 | 2049606 | 482 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 3264 | 36.5691 | -121.9367 | 1 W/ OF CGC 411382546311 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0047403 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1826806 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | OTHER | WIRE DOWN @ CGC 315379321278 TWDS 7243 | 20230319 | 919 | 2051860 | 503 | Distribution Circuit | Equipment Failure/Involved | Overhead | 170 | 76997 | 37.0728 | -122.0844 | at CGC 315379321278 TWDS 7243 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 23-0048469 | OH | Sus | 0 | No | 2023 | MAR | Yes | Open Circuit | 1827680 | CSO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 6161 | 20230324 | 1426 | 2066215 | 200 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 4600 | 37.1187 | -122.0198 | JEO 6161 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0052007 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1829976 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | OTHER | 5159 | 20230329 | 2241 | 2073791 | 925 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 19704 | 37.0814 | -122.0846 | SS OF CGC 315377821506 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0054718 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1831807 | PW | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | FUSE | 9775 | 20230329 | 1209 | 2073007 | 387 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 14706 | 37.141 | -122.0902 | 1 SS/OF CGC 315363823632 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0054393 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1831641 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 6713 | 20230329 | 1109 | 2072832 | 513 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 26157 | 36.4702 | -121.7242 | 2 LD SIDE OF MTR # 1008551017- EOL | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0054388 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1831638 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | 1273 | 20230331 | 954 | 2075318 | 537 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 5907 | 37.1217 | -121.9784 | 1 S/OF CGC#315706823010 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0055560 | OH | Sus | 31641135 | No | 2023 | MAR | Yes | Line to Ground | 1832218 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | OCB | 96246 | 20230403 | 1424 | 2078497 | 558 | Distribution Circuit | Vegetation | Tree - fell into line | 11722 | 503359 | 36.5786 | -121.9085 | 6029 ON MAIN LINE 2 N/OF 578112 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0056425 | OH | Sus | 0 | No | 2023 | APR | Yes | Line to Ground | 1832889 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2202 | 182852202 | OCB | 2202/2 | 20230403 | 1548 | 2078528 | 462 | Distribution Circuit | Vegetation | Tree - fell into line | 3070 | 294562 | 36.5786 | -121.9085 | COMMON NEUT DOWN AT 2834 CONGRESS / GUY INTO PRIMARY LD SIDE OF 40063 (TWD CGC 411335447200) | Clear-Strong Winds-32-90 F | Anchor or Guy | Broken, wire on ground | 23-0056486 | OH | Sus | 0 | No | 2023 | APR | Yes | Line to Ground | 1832920 | ANC | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | FUSE | 5043 | 20230404 | 643 | 2079542 | 710 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2840 | 37.061 | -122.2262 | JEO 5043 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0056827 | OH | Sus | 0 | No | 2023 | APR | Yes | Line to Ground | 1833176 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | OCB | 2101/2 | 20230412 | 500 | 2086144 | 596 | Distribution Circuit | Vegetation | Tree - fell into line | 2325 | 145750 | 37.0953 | -122.1437 | HUBBARD GULCH - 1 SPAN FROM FUSE 4709 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0059854 | OH | Sus | 0 | No | 2023 | APR | Yes | Multi-Fault | 1835018 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | SEACLIFF-0402 | 83500402 | OTHER | 12946 | 20230418 | 2222 | 2091920 | 281 | Distribution Circuit | Equipment Failure/Involved | Overhead | 213 | 59853 | 36.9875 | -121.9186 | 7533 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0062269 | OH | Sus | 31642701 | No | 2023 | APR | Yes | Open Circuit | 1836823 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | GREEN VALLEY-2101 | 83192101 | FUSE | 2705 | 20230430 | 735 | 2100395 | 150 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 4050 | 37.0005 | -121.7403 | 8 POLES LD SIDE OF 2705 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0066398 | OH | Sus | 45745387 | No | 2023 | APR | Yes | Line to Ground | 1839625 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | CAMP EVERS-2105 | 83622105 | FUSE | 2957 | 20230503 | 521 | 2103319 | 427 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 10675 | 37.0536 | -122.0766 | 2 SPANS LD SIDE 2957 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0067480 | OH | Sus | 45746724 | No | 2023 | MAY | Yes | Line to Ground | 1840337 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | FUSE | 7757 | 20230504 | 624 | 2104366 | 494 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2470 | 37.0132 | -121.9372 | 1 W/OF 7757 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0068032 | OH | Sus | 45749126 | No | 2023 | MAY | Yes | Line to Ground | 1840747 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | FUSE | 8429 | 20230513 | 623 | 2111612 | 227 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 908 | 37.1092 | -122.0598 | 1 LD SIDE OF 8429 | Clear-32-90 F | Conductor, Overhead | On Ground | 23-0071537 | OH | Sus | 0 | No | 2023 | MAY | Yes | Three Phase Fault | 1842979 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | FUSE | 9035 | 20230514 | 833 | 2112091 | 573 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 8595 | 37.0715 | -122.0745 | CGC# 315412321135 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0071643 | OH | Sus | 0 | No | 2023 | MAY | Yes | Line to Ground | 1843099 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 5188 | 20230519 | 1955 | 2117332 | 708 | Distribution Circuit | 3rd Party | Vehicle | 20 | 14160 | 37.0757 | -122.0568 | 3 SOURCE SIDE OF 555726 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0073734 | OH | Sus | 0 | No | 2023 | MAY | Yes | Line to Ground | 1844559 | PW | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | FUSE | 6343 | 20230527 | 41 | 2122446 | 728 | Distribution Circuit | 3rd Party | Vehicle | 18 | 13104 | 37.2222 | -122.1451 | 1 SS OF 3857 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 23-0076257 | OH | Sus | 0 | No | 2023 | MAY | Yes | Line to Line | 1846276 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2104 | 83692104 | OTHER | WIRE BROKEN | 20230527 | 1706 | 2122790 | 248 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1488 | 36.9996 | -121.8637 | SOURCE SIDE OF CGC# 316023618528 -BEAR VALLEY RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0076355 | OH | Sus | 45789702 | No | 2023 | MAY | Yes | Open Circuit | 1846358 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8345 | 20230601 | 226 | 2125185 | 714 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 8568 | 37.0568 | -121.9682 | 270 CANYON OAKS | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0077580 | OH | Sus | 0 | No | 2023 | JUN | Yes | Line to Ground | 1847146 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | CAMP EVERS-2106 | 83622106 | RECLOSER | 287578 | 20230615 | 2357 | 2138103 | 756 | Distribution Circuit | Vegetation | Tree - fell into line | 213 | 29169 | 37.0438 | -122.0755 | 2P W/OF 130936 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0082963 | OH | Sus | 0 | No | 2023 | JUN | Yes | Line to Ground | 1850954 | CAW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | FUSE | 8643 | 20230618 | 1930 | 2140045 | 901 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 40545 | 37.01 | -121.8859 | 2P LOAD SIDE OF 8643 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0083550 | OH | Sus | 45851787 | No | 2023 | JUN | Yes | Line to Ground | 1851494 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | OTHER | 5741 | 20230705 | 1537 | 2154821 | 294 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 7938 | 36.9993 | -122.0372 | 1P S/OF CGC# 315513018609 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0089126 | OH | Sus | 45871161 | No | 2023 | JUL | Yes | Open Circuit | 1855358 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 11006 | 20230712 | 1640 | 2161073 | 541 | Distribution Circuit | Vegetation | Tree - fell into line | 104 | 18650 | 37.05 | -122.0657 | 1 POLE N/OF CGC 315450920522 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0091479 | OH | Sus | 0 | No | 2023 | JUL | Yes | Line to Ground | 1856911 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2105 | 83622105 | RECLOSER | 922576 | 20230716 | 113 | 2163958 | 717 | Distribution Circuit | Vegetation | Tree - fell into line | 306 | 87727 | 37.0994 | -122.0532 | 2 S/OF 10431 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0092750 | OH | Sus | 31655761 | No | 2023 | JUL | Yes | Line to Ground | 1857769 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | RECLOSER | 9500 | 20230725 | 1421 | 2173487 | 96 | Distribution Circuit | Vegetation | Tree - fell into line | 3663 | 351648 | 36.5582 | -121.7507 | CGC# 411942343070 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0096613 | OH | Sus | 0 | No | 2023 | JUL | Yes | Multi-Fault | 1860417 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | DEL MONTE-2104 | 182222104 | RECLOSER | 779322 | 20230725 | 1701 | 2173769 | 589 | Distribution Circuit | Vegetation | Tree - fell into line | 169 | 4117 | 36.4868 | -121.7395 | CGC 411942343070 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0096738 | OH | Sus | 0 | No | 2023 | JUL | Yes | Multi-Fault | 1860432 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BURNS-2101 | 183582101 | OTHER | WIRE DOWN 1 SPAN LD SIDE OF 8315 | 20230727 | 227 | 2174947 | 633 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 13926 | 37.0996 | -122.1182 | 1 LD SIDE OF 8315 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 23-0097347 | OH | Sus | 31657096 | No | 2023 | JUL | Yes | Line to Ground | 1860786 | CSO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-1101 | 83041101 | RECLOSER | BL 1101 | 20230731 | 1441 | 2178709 | 782 | Distribution Circuit | Vegetation | Tree - fell into line | 744 | 93490 | 37.0926 | -122.0966 | CGC#315288722641 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0098778 | OH | Sus | 0 | No | 2023 | JUL | Yes | Line to Line | 1861876 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 2819 | 20230731 | 545 | 2178116 | 822 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 20808 | 37.0521 | -121.9787 | MAINLINE POLE at 2819- 2819 & 1 POLE LD SIDE OF 2819 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 23-0098576 | OH | Sus | 0 | No | 2023 | JUL | Yes | Line to Ground | 1861726 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER | WIRE DOWN SS OF CGC #315680920572 | 20230806 | 1417 | 2183707 | 468 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 2524 | 37.0553 | -121.9817 | WIRE DOWN SS OF CGC #315680920572 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0101032 | OH | Sus | 31662122 | No | 2023 | AUG | Yes | Line to Ground | 1863432 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | RECLOSER | 974130 | 20230819 | 1249 | 2195658 | 555 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 11805 | 37.0448 | -121.9382 | 6 SPANS LD SIDE OF 11905 - 1420 OLIVE SPRINGS RD SOQUEL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0106364 | OH | Sus | 45934025 | No | 2023 | AUG | Yes | Line to Ground | 1867053 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | OTHER | WIRE DOWN | 20230827 | 1724 | 2203430 | 490 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 8216 | 37.0093 | -121.9361 | 4P LOAD SIDE CGC # 315807518835 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0109557 | OH | Sus | 45942071 | No | 2023 | AUG | Yes | Open Circuit | 1869349 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | JUMPER | WIRE DOWN | 20230828 | 134 | 2203589 | 509 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 9140 | 37.021 | -121.9848 | 2P SOURCE SIDE OF 4141 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0109594 | OH | Sus | 31665602 | No | 2023 | AUG | Yes | Line to Ground | 1869385 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | VIEJO-2201 | 182852201 | FUSE | 8917 | 20230901 | 930 | 2207700 | 217 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 3255 | 36.5771 | -121.9274 | CGC 411399546598 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0111694 | OH | Sus | 31666986 | No | 2023 | SEP | Yes | Line to Ground | 1870764 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | RECLOSER | 67520 | 20230905 | 55 | 2209622 | 303 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2737 | 391545 | 36.9577 | -121.8525 | JUST LOAD SIDE OF 6541 (CUSTOMER OWNED LINE) | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0112415 | OH | Sus | 0 | No | 2023 | SEP | Yes | Line to Line | 1871172 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN | 20230912 | 827 | 2216476 | 279 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 3921 | 37.0398 | -122.0644 | 1 P/ LD SIDE OF CGC 315436820043 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0115397 | OH | Sus | 31668468 | No | 2023 | SEP | Yes | Line to Ground | 1873307 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BEN LOMOND-0401 | 83040401 | RECLOSER | 944178 | 20230915 | 1016 | 2219756 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 885 | 81048 | 37.0926 | -122.0964 | 1 SOURCE SIDE OF 185 - 505 RIVERSIDE AVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0117109 | OH | Sus | 31669267 | No | 2023 | SEP | Yes | Line to Ground | 1874342 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | RECLOSER | 67520 | 20230925 | 1307 | 2226675 | 531 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 2736 | 296226 | 36.9577 | -121.8525 | CGC#316046116430 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0120453 | OH | Sus | 31670303 | No | 2023 | SEP | Yes | Line to Ground | 1876624 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | OTHER | WIRE DOWN 1 SPAN SS OF CGC 316086318167 | 20231026 | 2248 | 2252889 | 803 | Distribution Circuit | Vegetation | Tree - bark fell into line | 500 | 69316 | 36.9915 | -121.8411 | 1 SP SS OF CGC 316086318167 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0133052 | OH | Sus | 46032474 | No | 2023 | OCT | Yes | Open Circuit | 1885433 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | OTTER-1102 | 182941102 | RECLOSER | 2002 | 20231103 | 713 | 2258784 | 453 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 54360 | 36.2248 | -121.7587 | EAST SIDE OF 95749 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0135446 | OH | Sus | 46047359 | No | 2023 | NOV | Yes | Line to Ground | 1887348 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 5215 | 20231118 | 2202 | 2273341 | 833 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 49980 | 37.0325 | -122.0765 | 1253 SCENIC DR | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0141029 | OH | Sus | 46061761 | No | 2023 | NOV | Yes | Line to Line | 1891700 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | ROB ROY-2105 | 83692105 | JUMPER | 1 SPAN WIRE DOWN LS OF 315976019180 | 20231119 | 208 | 2273403 | 820 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 8678 | 37.0186 | -121.879 | 1 SPAN LS OF CGC 315976019180 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0141065 | OH | Sus | 46061782 | No | 2023 | NOV | Yes | Line to Ground | 1891739 | CO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | POINT MORETTI-1101 | 82931101 | RECLOSER | 35874 | 20231123 | 1128 | 2276116 | 502 | Distribution Circuit | Equipment Failure/Involved | Overhead | 815 | 149969 | 37.0312 | -122.1882 | BETWEEN 7369 & 5413 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0142516 | OH | Sus | 46064884 | No | 2023 | NOV | Yes | Line to Line | 1892453 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1101 | 82841101 | RECLOSER | 393582 | 20231202 | 204 | 2281952 | 830 | Distribution Circuit | 3rd Party | Vehicle | 636 | 282952 | 37.1284 | -122.1222 | 1 N/OF 2877 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 23-0144877 | OH | Sus | 0 | No | 2023 | DEC | Yes | Line to Ground | 1894462 | PW | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | ROB ROY-2104 | 83692104 | FUSE | 737 | 20231211 | 108 | 2288548 | 922 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 31023 | 37.0046 | -121.8551 | 1 SPAN LD SIDE OF CGC#316021018871 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0146809 | OH | Sus | 46087446 | No | 2023 | DEC | Yes | Line to Ground | 1896669 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 1071 | 20231213 | 2214 | 2291416 | 916 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 7999 | 37.1665 | -122.1353 | CGC 315258524680 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0147363 | OH | Sus | 46091227 | No | 2023 | DEC | Yes | Line to Line | 1897638 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | GONZALES-1101 | 182131101 | OTHER | 1 PHASE WIRE DOWN CGC 412956644823 | 20231218 | 725 | 2294301 | 346 | Distribution Circuit | Equipment Failure/Involved | Overhead | 68 | 5074 | 36.541 | -121.3987 | CGC 412956644823 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 23-0147862 | OH | Sus | 46094562 | No | 2023 | DEC | Yes | Open Circuit | 1898646 | CSO | OH | No | Yes
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | RECLOSER | 12758 | 20231220 | 138 | 2296159 | 654 | Distribution Circuit | Vegetation | Tree - fell into line | 284 | 62479 | 37.1486 | -122.1745 | 1P N/OF 10025 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0148198 | OH | Sus | 0 | No | 2023 | DEC | Yes | Multi-Fault | 1899067 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2103 | 83622103 | OTHER | 12990 | 20231220 | 1739 | 2296909 | 377 | Distribution Circuit | Vegetation | Tree - fell into line | 791 | 114040 | 37.039 | -122.0214 | 1 S/OF 6101 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0148321 | OH | Sus | 46097999 | No | 2023 | DEC | Yes | Open Circuit | 1899259 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | LAURELES-1111 | 182371111 | FUSE | 6625 | 20231225 | 357 | 2299367 | 551 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 12722 | 36.3759 | -121.5909 | 15 SPANS LD SIDE OF 6625 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0148813 | OH | Sus | 46100386 | No | 2023 | DEC | Yes | Line to Line | 1899884 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | BIG BASIN-1102 | 82841102 | FUSE | 8015 | 20231229 | 936 | 2301802 | 573 | Distribution Circuit | Vegetation | Tree - fell into line | 140 | 80220 | 37.1536 | -122.1615 | CGC 315155824242 & CGC 315153124245 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0149209 | OH | Sus | 0 | No | 2023 | DEC | Yes | Line to Line | 1900500 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 3 | PAUL SWEET-2106 | 83252106 | RECLOSER | 974130 | 20231230 | 744 | 2302473 | 349 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 31759 | 37.0448 | -121.9382 | 1P LOAD SIDE OF CGC# 315806220220 - 250 OLIVE SPRINGS | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0149319 | OH | Sus | 31680546 | No | 2023 | DEC | Yes | Line to Line | 1900621 | CO | OH | No | No
CENTRAL COAST | FIELD OPS SOUTH | Tier 2 | PAUL SWEET-2105 | 83252105 | JUMPER | UN NUM FUCO 7 S/OF CGC 315508618438 | 20231231 | 940 | 2303182 | 815 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 815 | 36.9923 | -122.0348 | 5 S/OF CGC 315508618438 | Overcast-32-90 F | Insulator | Broken, wire on ground | 23-0149468 | OH | Sus | 31680680 | No | 2023 | DEC | Yes | Line to Ground | 1900787 | INS | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1105 | 83371105 | FUSE | 3837 | 20130308 | 1855 | 754320 | 565 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 7814 | 37.2609 | -122.0545 | PIERCE RD 3 SPANS S/OF RSB 4331 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0015346 | OH | Sus | 41863612 | No | 2013 | MAR | Yes | Line to Line | 99297333 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER |  | 20130416 | 1047 | 776280 | 1038 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1128 | 128140 | 37.1531 | -121.9628 | ALDERCROFT HEIGHTS RD 4 SPANS N/OF R124 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0024878 | OH | Sus | 30989931 | yes | 2013 | APR | Yes | None | 99290043 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER |  | 20130430 | 541 | 783781 | 519 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2079 | 37.1663 | -121.9838 | BET 18051 & 18001 IDYLWILD RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0028162 | OH | Sus | 41890787 | yes | 2013 | APR | Yes |  | 99287817 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1106 | 83371106 | FUSE | 2699 | 20130505 | 547 | 787365 | 1153 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 19601 | 37.2336 | -122.0047 | 5 SP LOAD SIDE 2699 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0029561 | OH | Sus | 30994514 | yes | 2013 | MAY | Yes | Line to Ground | 99286742 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 11753 | 20130505 | 654 | 787406 | 486 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 3510 | 37.2584 | -122.095 | 13840 REDWOOD GULCH | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0029613 | OH | Sus | 0 | yes | 2013 | MAY | Yes |  | 99286683 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 15769 | 20130505 | 1529 | 787947 | 736 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 3049 | 37.2474 | -122.068 | 16055 SANBORN SARATOGA | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0029668 | OH | Sus | 0 | yes | 2013 | MAY | Yes | Line to Ground | 99286635 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | FUSE | 31999 | 20130506 | 636 | 788366 | 554 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 4432 | 37.281 | -122.1189 | LOADSIDE OF 31999 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0029795 | OH | Sus | 0 | yes | 2013 | MAY | Yes | Line to Ground | 99286487 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER |  | 20130603 | 947 | 803481 | 743 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2229 | 37.1889 | -122.0344 | 19289 GREEN FOREST | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0036272 | OH | Sus | 0 | No | 2013 | JUN | Yes | None | 99282018 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | OTHER |  | 20130607 | 1927 | 805787 | 471 | Distribution Circuit | Vegetation | Tree - branch fell on line | 56 | 10814 | 37.2391 | -122.025 | 15671 PEACH HILL DR.- SARA | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0037624 | OH | Sus | 31001468 | yes | 2013 | JUN | Yes | Line to Ground | 99281328 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LA64 | 20130622 | 1717 | 814752 | 75 | Distribution Circuit | Vegetation | Tree - fell into line | 176 | 13200 | 37.1372 | -121.9672 | IFO 23513 SKYVIEW TERRACE- LG | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0041759 | OH | Sus | 0 | No | 2013 | JUN | Yes | Line to Ground | 99278522 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 3459 | 20130622 | 1709 | 814749 | 333 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 52614 | 37.1286 | -121.9532 | IFO 23513 SKYVIEW TERRACE- LG | Clear-Above 90 F | Conductor, Overhead | Broken, wire on ground | 13-0041759 | OH | Sus | 31004558 | No | 2013 | JUN | Yes | Line to Line | 99278517 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | STELLING-1110 | 83481110 | SWITCH | SL01 | 20130628 | 2043 | 819988 | 873 | Distribution Circuit | Vegetation | Tree - branch fell on line | 203 | 177219 | 37.2532 | -122.1172 | Nystrom- Erik: Near 13847 Skyline Blvd | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0043577 | OH | Sus | 31006019 | yes | 2013 | JUN | Yes | Line to Line | 99277217 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | SWITCH | SA23 | 20130711 | 412 | 829549 | 528 | Distribution Circuit | Equipment Failure/Involved | Other | 334 | 38656 | 37.1522 | -121.9967 | 1 POLE E/OF ZELLA COURT & FERN AVE- LOS GATOS | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0046560 | OH | Sus | 41924994 | No | 2013 | JUL | Yes | Line to Ground | 99274795 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 6867 | 20130716 | 2158 | 832748 | 531 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 43542 | 37.2548 | -122.0338 | RINEHART- ROGER: 14690 Aloha Ave | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0047906 | OH | Sus | 31009123 | No | 2013 | JUL | Yes | Line to Ground | 99273868 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 12853 | 20130802 | 218 | 841983 | 507 | Distribution Circuit | Equipment Failure/Involved | Other | 59 | 14523 | 37.2431 | -122.0136 | 19280 BAINTER RD DOWN WIRE | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0051894 | OH | Sus | 41936443 | No | 2013 | AUG | Yes | Line to Line | 99271263 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | HICKS-2103 | 83432103 | FUSE | 18383 | 20130901 | 1334 | 859079 | 291 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2328 | 37.2041 | -121.8961 | 18711 REYNOLDS RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0059061 | OH | Sus | 31018546 | No | 2013 | SEP | Yes |  | 99266159 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 11753 | 20130902 | 1625 | 859563 | 795 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 7950 | 37.2584 | -122.095 | PERIANDRI-V /532: load side lco 11753 redwood gulch at hwy 9 saratoga | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0059160 | OH | Sus | 41949753 | yes | 2013 | SEP | Yes | Line to Ground | 99265981 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER |  | 20130909 | 300 | 862952 | 439 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 14926 | 37.1086 | -121.9489 | 16040 REDWOOD LODGE RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0060593 | OH | Sus | 0 | No | 2013 | SEP | Yes |  | 99264984 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 21107 | 20130921 | 722 | 869852 | 852 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 4260 | 37.1185 | -121.9405 | 23580 MORRIL RD | Clear-32 - 90 F | Other | Broken, wire on ground | 13-0063662 | OH | Sus | 41962651 | yes | 2013 | SEP | Yes |  | 99262829 | NON | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | STELLING-1110 | 83481110 | RECLOSER | 60094 | 20131004 | 455 | 878081 | 1413 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 27198 | 37.2571 | -122.1203 | 2 POLES E/O 12939 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0067163 | OH | Sus | 31026017 | yes | 2013 | OCT | Yes |  | 99260283 | PW | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4417 | 20131027 | 2213 | 891970 | 977 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 21365 | 37.1978 | -122.0275 | MONAHAN/2094: IFO 20531 BLACK RD- LOS GATOS | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0072573 | OH | Sus | 41977514 | yes | 2013 | OCT | Yes | Line to Ground | 99256282 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 21069 | 20131027 | 2215 | 891681 | 617 | Distribution Circuit | Vegetation | Tree - branch fell on line | 32 | 19744 | 37.1589 | -121.9871 | CORNER OF MADRONE & REDWOOD RETREAT | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0072602 | OH | Sus | 0 | yes | 2013 | OCT | Yes |  | 99256263 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | STELLING-1110 | 83481110 | SWITCH | SL01 | 20131028 | 540 | 892054 | 663 | Distribution Circuit | Equipment Failure/Involved | Other | 203 | 113554 | 37.2532 | -122.1172 | MONAHAN/2094: AT LCO 2679 - 1 POLE E/O 15969 SKYLINE BLVD | Overcast-32 - 90 F | Conductor, Overhead | On Ground | 13-0072655 | OH | Sus | 41977513 | yes | 2013 | OCT | Yes | None | 99255951 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER |  | 20131101 | 1308 | 894972 | 522 | Distribution Circuit | Equipment Failure/Involved | Other | 941 | 102130 | 37.1623 | -121.9837 | 20901 OLD SANTA CRUZ HWY | Clear-32 - 90 F | Insulator | Broken, wire on ground | 13-0073885 | OH | Sus | 41982610 | No | 2013 | NOV | Yes | Line to Ground | 99255315 | INS | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 12073 | 20131102 | 1422 | 895400 | 694 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 16656 | 37.1322 | -121.9999 | PATTERSON- N: LINE AND BUCK at 22111 OAK FLAT | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on object | 13-0074027 | OH | Sus | 31033452 | No | 2013 | NOV | Yes | Line to Ground | 99255202 | PW | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 22527 | 20131106 | 1714 | 897548 | 818 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 23722 | 37.2437 | -122.0167 | 15750 CANNON RD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0074822 | OH | Sus | 41984785 | No | 2013 | NOV | Yes | Line to Ground | 99254512 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | OTHER |  | 20131120 | 1630 | 906151 | 540 | Distribution Circuit | Equipment Failure/Involved | Other | 26 | 12522 | 37.2687 | -122.0953 | 1700 STEVENS CANYON RD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0077483 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Open Circuit | 99252330 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | HICKS-2103 | 83432103 | SWITCH | 32765 | 20131124 | 1524 | ODB-9925 | 599 | Distribution Circuit | 3rd Party | Vehicle | 93 | 41613 | 37.2173 | -121.9118 |  | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0079097 | OH | Sus | 42036166 | No | 2013 | NOV | Yes |  | 99250841 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 4767 | 20140206 | 654 | 960523 | 459 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2295 | 37.1492 | -122.0038 | 10 SP LOAD SIDE 4767 | Rain-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0009200 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Ground | 99241164 | CSO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | RECLOSER | LC26 | 20140207 | 2259 | 962336 | 417 | Distribution Circuit | Vegetation | Tree - branch fell on line | 226 | 83748 | 37.2495 | -122.0193 | GLEN UNA DR. 1PL W/O PEPPER LN | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0009786 | OH | Sus | 42073199 | yes | 2014 | FEB | Yes |  | 99240812 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 6991 | 20140210 | 126 | 964687 | 664 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 36366 | 37.2342 | -122.0438 | 16203 SANBOARN RD | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0010218 | OH | Sus | 42073826 | yes | 2014 | FEB | Yes | Line to Ground | 99240369 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER |  | 20140226 | 2142 | 973801 | 1118 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 38822 | 37.1434 | -121.9942 | 7 SP LOAD SIDE 11533 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0013942 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Open Circuit | 99237876 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | TRANSFORMER |  | 20140227 | 813 | 973569 | 1079 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2707 | 37.0852 | -121.9537 | MTR 1008803464 | Clear-32 - 90 F | Pole-Wood | Broken, wire on object | 14-0013793 | OH | Sus | 0 | yes | 2014 | FEB | Yes |  | 99237951 | PW | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 19947 | 20140228 | 303 | 974260 | 604 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 25972 | 37.1309 | -122.0004 | HUTCHINSON RD 1P E/OF 19947 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0014176 | OH | Sus | 31059401 | yes | 2014 | FEB | Yes |  | 99237707 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 12073 | 20140228 | 1343 | 975349 | 1648 | Distribution Circuit | Equipment Failure/Involved | Other | 24 | 8199 | 37.1322 | -121.9999 | 23450 UPPER OAK FLAT RD | Rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0014496 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Line | 99237332 | PW | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 19949 | 20140301 | 1315 | 976465 | 1291 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 29693 | 37.1225 | -122.0051 | IFO 24750 HUTCHINSON RD LOS GATOS - 4 SP LOAD SIDE 19949 | Rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0014821 | OH | Sus | 31059988 | yes | 2014 | MAR | Yes | Line to Ground | 99237114 | PW | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER |  | 20140310 | 1317 | 981749 | 638 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 1150 | 37.1528 | -121.9694 | 22080 OLD SANTA CRUZ HWY | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0017030 | OH | Sus | 42090611 | No | 2014 | MAR | Yes | None | 99235660 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | FUSE | 12075 | 20140329 | 355 | 991217 | 800 | Distribution Circuit | 3rd Party | Vehicle | 3 | 2400 | 37.259 | -122.1226 | 7 POLES N/O 12075 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0021363 | OH | Sus | 31066031 | yes | 2014 | MAR | Yes |  | 99232688 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | FUSE | 9265 | 20140401 | 1309 | 993461 | 1045 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 53023 | 37.2937 | -122.1022 | 3 SPANS LD SIDE 9265 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0022205 | OH | Sus | 42100718 | yes | 2014 | APR | Yes | Line to Ground | 99231951 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4451 | 20140504 | 2214 | 1010118 | 592 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 10812 | 37.1364 | -121.9681 | 6 SPAN W/O 31297 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0029177 | OH | Sus | 31073671 | No | 2014 | MAY | Yes | Line to Ground | 99227335 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 9125 | 20140506 | 311 | 1010754 | 699 | Distribution Circuit | Vegetation | Tree - branch fell on line | 92 | 31827 | 37.1653 | -122.0175 | 4 SPANS W/O FUCO 9125 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0029476 | OH | Sus | 42117631 | yes | 2014 | MAY | Yes | Line to Line | 99227145 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | SWITCH | 29227 | 20140517 | 734 | 1019918 | 710 | Distribution Circuit | Animal | Squirrel | 21 | 12333 | 37.2502 | -122.031 | 315546727681 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0032542 | OH | Sus | 42125610 | No | 2014 | MAY | Yes | Line to Ground | 99225216 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 29533 | 20140604 | 523 | 1028228 | 637 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2548 | 37.1909 | -122.0336 | 5 SP LD SIDE OF FUCO 29533 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0036004 | OH | Sus | 31080409 | No | 2014 | JUN | Yes |  | 99222749 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 21101 | 20140615 | 947 | 1034889 | 366 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 2826 | 37.1334 | -121.965 | 23633 SCHULTIES RD- LGH | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0038466 | OH | Sus | 42139246 | No | 2014 | JUN | Yes |  | 99220958 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 32557 | 20140626 | 938 | 1040117 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2088 | 37.2516 | -122.0249 | 315563227729 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0040725 | OH | Sus | 42145234 | No | 2014 | JUN | Yes | Line to Ground | 99219333 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 29951 | 20140716 | 1004 | 1050424 | 804 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1608 | 37.2411 | -122.0415 | 7 SPANS S/O 29951 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0044887 | OH | Sus | 31089256 | No | 2014 | JUL | Yes | Line to Ground | 99216419 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | FUSE | 2243 | 20140830 | 2143 | 1075251 | 602 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 15652 | 37.278 | -122.1121 | STEVENS- ROBERT: 16360 STEVENS CANYON ROAD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0054288 | OH | Sus | 31098143 | No | 2014 | AUG | Yes | Line to Ground | 99209767 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER |  | 20140831 | 1508 | 1075465 | 1082 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 37906 | 37.1985 | -121.9943 | Nystrom- Erik: Montevina Rd at Vista Grande | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0054345 | OH | Sus | 42179142 | No | 2014 | AUG | Yes |  | 99209690 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 11753 | 20140908 | 854 | 1078466 | 696 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6960 | 37.2584 | -122.095 | LD SIDE OF C/OUTS 11753 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0055621 | OH | Sus | 31099781 | No | 2014 | SEP | Yes | None | 99208845 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1106 | 83371106 | FUSE | 29169 | 20140915 | 1922 | 1082455 | 522 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 14094 | 37.2451 | -122.0096 | 15200 FRUITVALE AVE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0057140 | OH | Sus | 42191401 | No | 2014 | SEP | Yes | Line to Ground | 99207855 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 60124 | 20141005 | 2232 | 1093319 | 1643 | Distribution Circuit | Vegetation | Tree - fell into line | 466 | 0 | 37.1461 | -121.9821 | 500 CRESCI RD- LOS GATOS | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0061527 | OH | Sus | 0 | No | 2014 | OCT | Yes |  | 99204808 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 29533 | 20141016 | 436 | 1098179 | 491 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1964 | 37.1909 | -122.0336 | Zandate/470-0297: 200' S/O 19258 Green Forest Rd | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0063980 | OH | Sus | 31107686 | No | 2014 | OCT | Yes | Line to Ground | 99203350 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER |  | 20141101 | 905 | 1107645 | 1009 | Distribution Circuit | Vegetation | Tree - fell into line | 121 | 29749 | 37.1873 | -121.9977 | Zandate/470-0297: E/O 18951 Bear Creek Rd. at LCo Pole 7663 | Drizzle-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0067652 | OH | Sus | 31112295 | yes | 2014 | NOV | Yes | None | 99200915 | PW | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER |  | 20141111 | 1911 | 1111705 | 157 | Distribution Circuit | Equipment Failure/Involved | Other | 93 | 10577 | 37.1743 | -122.0637 | 1 POLE E/O 9125 | Overcast-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0069434 | OH | Sus | 42269730 | No | 2014 | NOV | Yes | Line to Ground | 99199643 | CSO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 8977 | 20141121 | 933 | 1116174 | 466 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2796 | 37.1844 | -122.0031 | 19305 BEAR CREEK RD | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0071413 | OH | Sus | 42279952 | No | 2014 | NOV | Yes | None | 99198356 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | FUSE | 2243 | 20141123 | 623 | 1117053 | 592 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 15392 | 37.278 | -122.1121 | BILBREY/523: 9 poles s of 2243 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0071670 | OH | Sus | 42280249 | No | 2014 | NOV | Yes | Line to Line | 99198146 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 31619 | 20141125 | 1757 | 1118244 | 1202 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 1202 | 37.2628 | -122.0994 | REDWOOD GULCH RD 2 SPANS W/OF LCO 31619 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0072091 | OH | Sus | 42281172 | No | 2014 | NOV | Yes | None | 99197793 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 3459 | 20141129 | 611 | 1119203 | 484 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 25887 | 37.1286 | -121.9532 | 23565 SKYVIEW TERRACE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0072392 | OH | Sus | 42282003 | No | 2014 | NOV | Yes | Line to Ground | 99197590 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | FUSE | 18353 | 20141201 | 1204 | 1120143 | 796 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 13532 | 37.2782 | -122.1127 | 17288 STEVENS CANYON RD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0072682 | OH | Sus | 31118379 | No | 2014 | DEC | Yes | Line to Ground | 99197330 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 21049 | 20141204 | 712 | 1124231 | 1135 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 28396 | 37.1813 | -122.0306 | 21049 | Heavy rain-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0073851 | OH | Sus | 31118513 | yes | 2014 | DEC | Yes | Line to Ground | 99196433 | CAW | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 2903 | 20141204 | 1107 | 1124496 | 904 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 9796 | 37.1144 | -121.9387 | 24125 MILLER CUTOFF | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073799 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99196452 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER |  | 20141204 | 1105 | 1124601 | 891 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3564 | 37.1113 | -121.9582 | 16306 REDWOOD LODGE RD | Drizzle-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0073814 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99196446 | PW | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 15767 | 20141204 | 835 | 1124317 | 285 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2565 | 37.2363 | -122.066 | 1 SP LOAD SIDE 15767 | Drizzle-32 - 90 F | Conductor, Overhead | On Ground | 14-0073732 | OH | Sus | 31118510 | yes | 2014 | DEC | Yes | Line to Ground | 99196507 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1105 | 83371105 | FUSE | 15891 | 20141205 | 652 | 1125061 | 703 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4218 | 37.2749 | -122.0686 | SS 22000 MT EDEN RD (MTR # 1009718063) WHEN SINGLE PHASE MEEDS 3 PHASE | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073958 | OH | Sus | 0 | No | 2014 | DEC | Yes |  | 99196279 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER | 60092 | 20141206 | 533 | 1125737 | 945 | Distribution Circuit | Equipment Failure/Involved | Other | 2250 | 295014 | 37.1817 | -121.9846 | 17035 MELODY LN | Drizzle-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0074123 | OH | Sus | 0 | No | 2014 | DEC | Yes |  | 99196131 | CAW | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 21073 | 20141208 | 1452 | 1127102 | 938 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 15008 | 37.1637 | -121.9855 | CRN OF OGLALLA WAR PATH | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074415 | OH | Sus | 31120265 | No | 2014 | DEC | Yes | Line to Line | 99195726 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | LOS GATOS-1106 | 82021106 | FUSE | 1573 | 20141216 | 1819 | 1142478 | 709 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 10828 | 37.1981 | -121.9929 | 18560 MONTEVINA | Overcast-32 - 90 F | Conductor, Overhead | On Ground | 14-0077319 | OH | Sus | 31121584 | yes | 2014 | DEC | Yes | Line to Ground | 99192645 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER |  | 20141216 | 2140 | 1142591 | 1010 | Distribution Circuit | Environmental/External | Flood/Erosion | 103 | 52529 | 37.1966 | -122.0096 | HAUGEN- KIRK: 19350 beardsley | Overcast-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0077341 | OH | Sus | 31121589 | yes | 2014 | DEC | Yes | None | 99192639 | PW | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER |  | 20141220 | 720 | 1144877 | 435 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4350 | 37.14 | -121.9784 | SAME | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077786 | OH | Sus | 42301473 | No | 2014 | DEC | Yes | Line to Ground | 99192123 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 19943 | 20141221 | 2025 | 1145719 | 1048 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2096 | 37.1381 | -121.9966 | 1P E/OF 19943 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077924 | OH | Sus | 42301699 | No | 2014 | DEC | Yes | Line to Line | 99191937 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 21107 | 20141231 | 639 | 1156238 | 2162 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 10810 | 37.1185 | -121.9405 | 23580 MORRIL RD | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0079813 | OH | Sus | 31124141 | yes | 2014 | DEC | Yes | Line to Ground | 99189683 | PW | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 30193 | 20150101 | 456 | 1157913 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1866 | 37.1124 | -121.9344 | 39 OLD ORCHARD RD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0002096 | OH | Sus | 0 | No | 2015 | JAN | Yes | Line to Ground | 99189627 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 8347 | 20150220 | 1435 | 1193215 | 665 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 35245 | 37.1369 | -121.9841 | 315675723550 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0014687 | OH | Sus | 42337009 | No | 2015 | FEB | Yes | Line to Ground | 99181158 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | SWITCH | SB19 | 20150312 | 2236 | 1202927 | 1209 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 22622 | 37.1751 | -122.0105 | 7 POLES S/O FUCO 8705 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0019312 | OH | Sus | 42349116 | No | 2015 | MAR | Yes | Line to Ground | 99178308 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | STELLING-1110 | 83481110 | FUSE | 805 | 20150424 | 919 | 1224183 | 337 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 674 | 37.2569 | -122.1181 | 315297427944 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0029189 | OH | Sus | 0 | yes | 2015 | APR | Yes | Line to Line | 99172067 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER |  | 20150430 | 545 | 1227206 | 835 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 3525 | 37.1407 | -122.007 | 315611223669 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0030626 | OH | Sus | 31151785 | No | 2015 | APR | Yes | Line to Line | 99171042 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER |  | 20150523 | 509 | 1238677 | 546 | Distribution Circuit | Vegetation | Tree - fell into line | 289 | 12831 | 37.1051 | -121.9077 | 26080 ADAMS RD | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0036105 | OH | Sus | 42394474 | No | 2015 | MAY | Yes | Line to Ground | 99167293 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | FUSE | 2243 | 20150612 | 451 | 1249616 | 564 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 14664 | 37.278 | -122.1121 | 16500 STEVENS CANYON RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0040557 | OH | Sus | 0 | No | 2015 | JUN | Yes | Line to Line | 99164019 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 1429 | 20150617 | 1930 | 1252470 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 8400 | 37.1475 | -121.9749 | MT CHARLIE RD | Clear-32 - 90 F | Conductor, Overhead | On Ground | 15-0041762 | OH | Sus | 42410100 | No | 2015 | JUN | Yes | Force Out | 99163175 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 17431 | 20150618 | 1350 | 1252883 | 755 | Distribution Circuit | Vegetation | Tree - branch fell on line | 32 | 9824 | 37.1103 | -121.951 | 281 TALL TREES RD | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0041952 | OH | Sus | 42410945 | No | 2015 | JUN | Yes | Line to Ground | 99163011 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | HICKS-1116 | 83431116 | RECLOSER | 60050 | 20150619 | 2120 | 1253546 | 1088 | Distribution Circuit | 3rd Party | Vehicle | 225 | 48649 | 37.2297 | -121.9499 | MONAHAN/2094: 1 POLE N/O LCO 63387 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 15-0042234 | OH | Sus | 31162530 | No | 2015 | JUN | Yes | Line to Ground | 99162816 | CO | OH | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER | O/J @ 19301 BEAR CREEEK RD | 20150723 | 1524 | 1276312 | 720 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2223 | 37.185 | -122.0061 | DOWN WIRE AT N/O 19301 DEAR CREEK RD | Clear-32-90 F | Conductor, Overhead | On Ground | 15-0050171 | OH | Sus | 0 | No | 2015 | JUL | Yes | Force Out | 1147329 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | HICKS-1116 | 83431116 | RECLOSER | 60050 | 20150729 | 1123 | 1279386 | 880 | Distribution Circuit | Vegetation | Tree - fell into line | 225 | 45512 | 37.2297 | -121.9499 | 18701 SHANNON- LOS GATOS | Clear-32-90 F | Conductor, Overhead | On Ground | 15-0051266 | OH | Sus | 0 | yes | 2015 | JUL | Yes | Line to Ground | 1148104 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | FUSE | 18351 | 20150821 | 118 | 1292347 | 777 | Distribution Circuit | Vegetation | Tree - bark fell into line | 5 | 3885 | 37.2809 | -122.1183 | LD SIDE OF 18351 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0056474 | OH | Sus | 31177769 | No | 2015 | AUG | Yes | Line to Ground | 1151717 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER | 5209 | 20150827 | 1248 | 1295538 | 334 | Distribution Circuit | Equipment Failure/Involved | Overhead | 362 | 40140 | 37.1464 | -121.9723 | 1/S 4/O TW DOWN 1/P/E/OF 5209 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 15-0057735 | OH | Sus | 0 | No | 2015 | AUG | Yes | Line to Ground | 1152600 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 3459 | 20150905 | 713 | 1300484 | 445 | Distribution Circuit | Vegetation | Tree - branch fell on line | 160 | 32195 | 37.1287 | -121.953 | 23535 SKY VIEW (SOURCE SIDE) | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0059478 | OH | Sus | 31181861 | No | 2015 | SEP | Yes | Line to Ground | 1153857 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER | 60114 | 20150909 | 912 | 1302213 | 1068 | Distribution Circuit | Equipment Failure/Involved | Overhead | 289 | 142401 | 37.1189 | -121.9201 | LAFON/508: 1phs 12kv down 2spn ld sd of 7617 & 3spns ss of 5935 on mt bache rd | Clear-Heat Wave-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0060074 | OH | Sus | 42466634 | yes | 2015 | SEP | Yes | Line to Ground | 1154351 | CSO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | SB19 | 20150914 | 1406 | 1305576 | 733 | Distribution Circuit | Equipment Failure/Involved | Overhead | 809 | 98547 | 37.1305 | -121.9785 | OREPEZA: 17849 old Summit Rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0061286 | OH | Sus | 42470694 | yes | 2015 | SEP | Yes | Line to Ground | 1155124 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | OTHER | WIRE DOWN @ MTR# 1007820129 | 20150929 | 21 | 1313366 | 1230 | Distribution Circuit | Equipment Failure/Involved | Overhead | 500 | 22767 | 37.243 | -122.0414 | 15540 QUICKERT RD- SARATOGA | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on object | 15-0066194 | OH | Sus | 42485012 | No | 2015 | SEP | Yes | Line to Ground | 1159352 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LB44 | 20151004 | 1755 | 1316883 | 980 | Distribution Circuit | Vegetation | Tree - fell into line | 328 | 76044 | 37.1938 | -121.9959 | STORMENT- 4178 / 831-278-0287: 19451 Black Rd- L.G. | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0067852 | OH | Sus | 0 | yes | 2015 | OCT | Yes | Three Phase Fault | 1160621 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 17431 | 20151008 | 303 | 1318579 | 672 | Distribution Circuit | Vegetation | Tree - branch fell on line | 32 | 6004 | 37.1102 | -121.9509 | 16246 REDWOOD LODGE RD | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0068826 | OH | Sus | 31189527 | No | 2015 | OCT | Yes | Line to Ground | 1161273 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 7265 | 20151019 | 519 | 1325819 | 623 | Distribution Circuit | Animal | Bird found | 55 | 34265 | 37.2501 | -122.0232 | SOURCE SIDE OF LCO 9325 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0071721 | OH | Sus | 42529231 | No | 2015 | OCT | Yes | Line to Line | 1163408 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | JUMPER | WIRE DOWN | 20151020 | 1007 | 1326686 | 384 | Distribution Circuit | Vegetation | Tree - branch fell on line | 72 | 25308 | 37.1655 | -121.9751 | 2 SPANS N/O 29641 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0072165 | OH | Sus | 31193357 | No | 2015 | OCT | Yes | Line to Ground | 1163690 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | 60116 | 20151115 | 951 | 1341577 | 1209 | Distribution Circuit | Vegetation | Tree - fell into line | 947 | 77097 | 37.1734 | -121.9929 | Zandate/470-0297: 1/P S/O SW 1927 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on object | 15-0077858 | OH | Sus | 42568266 | yes | 2015 | NOV | Yes | Line to Line | 1168334 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | OTHER | WIRE DOWN MTR# 1010035455 | 20151118 | 1804 | 1345048 | 605 | Distribution Circuit | Vegetation | Tree - branch fell on line | 194 | 79398 | 37.2607 | -122.1193 | 24615 HEATHER HEIGHTS- SG | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0079018 | OH | Sus | 31201276 | No | 2015 | NOV | Yes | Force Out | 1169286 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 11239 | 20151124 | 1440 | 1348092 | 1320 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1320 | 37.2508 | -122.0946 | 2 SPANS LD SIDE OF 11239 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0080669 | OH | Sus | 42576398 | yes | 2015 | NOV | Yes | Line to Ground | 1170589 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 5203 | 20151203 | 1314 | 1352970 | 1004 | Distribution Circuit | Equipment Failure/Involved | Overhead | 100 | 38688 | 37.2354 | -122.0629 | 1 SPAN OF WIRE DOWN 1/P/N/W/OF 7163 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082558 | OH | Sus | 31203977 | yes | 2015 | DEC | Yes | Line to Ground | 1172232 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4533 | 20151204 | 544 | 1353583 | 423 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3807 | 37.1748 | -122.0608 | 20215 BEAR CREEK RD 2P W/OF LCO 4533 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082677 | OH | Sus | 31203915 | No | 2015 | DEC | Yes | Line to Line | 1172340 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 4465 | 20151211 | 1640 | 1359151 | 1390 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 25020 | 37.1081 | -121.9452 | 25119 OLD SAN JOSE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 15-0084328 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1173955 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER | 60092 | 20151215 | 1320 | 1364315 | 110 | Distribution Circuit | Vegetation | Tree - fell into line | 1133 | 78911 | 37.1825 | -121.985 | WIRE DOWN 10 POLES NORTH OF R124 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0085522 | OH | Sus | 31206680 | No | 2015 | DEC | Yes | Line to Ground | 1175246 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | FUSE | 18351 | 20151221 | 1655 | 1368128 | 230 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1150 | 37.2809 | -122.1183 | 1 SPAN LD SIDE OF 69829 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086538 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1176532 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4419 | 20151222 | 338 | 1368896 | 1460 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 21900 | 37.2037 | -122.0315 | HAUGEN- KIRK: 6 spans south of C/O's 4419 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086843 | OH | Sus | 31208372 | yes | 2015 | DEC | Yes | Line to Ground | 1176875 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 6947 | 20160105 | 434 | 1377031 | 702 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 9333 | 37.1171 | -121.9239 | HIGHLAND AND BURREL CT | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0002878 | OH | Sus | 31210477 | yes | 2016 | JAN | Yes | Line to Ground | 1178683 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | JUMPER | WIRE DOWN ON GROUND @ 23378 MORRILL RD | 20160106 | 1724 | 1378898 | 870 | Distribution Circuit | Vegetation | Tree - fell into line | 1283 | 110842 | 37.1278 | -121.9387 | LAFON/508: 12kv down & brkn x-arm & floaters for 6 spans 23378 morrill rd lg | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003603 | OH | Sus | 31210708 | yes | 2016 | JAN | Yes | Line to Line | 1179096 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4419 | 20160113 | 130 | 1382465 | 979 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 14685 | 37.2037 | -122.0315 | 20630 BLACK RD | Overcast-Fog-Drizzle-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 16-0004932 | OH | Sus | 31212363 | yes | 2016 | JAN | Yes | Line to Line | 1180210 | PW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 10003 | 20160115 | 557 | 1384297 | 526 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 12098 | 37.1041 | -121.9496 | 25256 TERRACE GROVE RD | Clear-32-90 F | Conductor, Overhead | On Ground | 16-0005511 | OH | Sus | 31213220 | No | 2016 | JAN | Yes | Line to Line | 1180589 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | SWITCH | SA25 | 20160118 | 809 | 1386024 | 1371 | Distribution Circuit | Vegetation | Tree - fell into line | 556 | 346272 | 37.1443 | -121.9858 | HAUGEN- KIRK: 1 POLE SOUTH OF OH SW 2541 | Partly Cloudy-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006031 | OH | Sus | 31213389 | yes | 2016 | JAN | Yes | Line to Ground | 1181000 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | LOS GATOS-1101 | 82021101 | FUSE | 30163 | 20160119 | 1052 | 1386935 | 230 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 5750 | 37.2246 | -121.9571 | LOS GATOS: KENNEDY & OLDE | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006356 | OH | Sus | 31213465 | yes | 2016 | JAN | Yes | None | 1181249 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER | WIRE DOWN 15999 COMSTOCK MILL RD | 20160119 | 1438 | 1387796 | 704 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4815 | 37.1018 | -121.9401 | 15999 COMSTOCK MILL RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006609 | OH | Sus | 31213465 | yes | 2016 | JAN | Yes | None | 1181416 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | SWITCH | SA25 | 20160122 | 1248 | 1390061 | 942 | Distribution Circuit | Vegetation | Tree - fell into line | 556 | 95512 | 37.1443 | -121.9858 | 3P S/OF 32261 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007449 | OH | Sus | 42616091 | yes | 2016 | JAN | Yes | Line to Line | 1182001 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 12041 | 20160122 | 1835 | 1390320 | 962 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 75998 | 37.0983 | -121.9473 | ZANDATE- LOUIE: 8 poles load side c/o 12041 tree fell into lines | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007646 | OH | Sus | 42616311 | yes | 2016 | JAN | Yes | Line to Ground | 1182134 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER | 60092 | 20160124 | 919 | 1391134 | 1270 | Distribution Circuit | Vegetation | Tree - fell into line | 1470 | 122138 | 37.1825 | -121.985 | 2 SPANS S/O 3835 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0007839 | OH | Sus | 0 | No | 2016 | JAN | Yes | Line to Ground | 1182346 | PW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | SWITCH | SA25 | 20160201 | 1005 | 1396284 | 707 | Distribution Circuit | Vegetation | Tree - branch fell on line | 555 | 70809 | 37.1443 | -121.9858 | ON BAYVIEW W/OF 30713 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009750 | OH | Sus | 42621948 | yes | 2016 | FEB | Yes | Line to Ground | 1183813 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 2903 | 20160304 | 2116 | 1416160 | 143 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 2002 | 37.1144 | -121.9385 | MILLER CUT OFF ROAD | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017359 | OH | Sus | 42647425 | No | 2016 | MAR | Yes | Line to Ground | 1189260 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | 1 P/NE/O 15208 OLD RANCH RD | 20160306 | 1259 | 1422095 | 1929 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 32384 | 37.1436 | -121.9999 | 1 P/NE/O 15208 OLD RANCH RD- POLE SAP 100518622 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0018522 | OH | Sus | 31222889 | yes | 2016 | MAR | Yes | Line to Ground | 1190359 | PW | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 15767 | 20160306 | 1031 | 1421846 | 959 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3143 | 37.2364 | -122.0661 | LAFON/508: 1 spn 12kv down at 2poles s of mtr#1007454750 | Rain-Strong Winds-Heavy Rain-Combination-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018404 | OH | Sus | 42646371 | yes | 2016 | MAR | Yes | Three Phase Fault | 1190252 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | FUSE | 2243 | 20160312 | 414 | 1429027 | 673 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 12851 | 37.2784 | -122.1112 | OWEN- JACOB: 16360 Stevens canyon rd | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020718 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192092 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | FUSE | 18353 | 20160314 | 702 | 1431005 | 574 | Distribution Circuit | Vegetation | Tree - bark fell into line | 11 | 6314 | 37.2786 | -122.1116 | 17924 STEVENS CANYON RD- CUPERTINO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021230 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192573 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 2459 | 20160405 | 753 | 1444510 | 1087 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 5822 | 37.144 | -121.9901 | LAFON/508: tree fell & broke pole & 12kv down 3spns s and w of 2459 - opn jumprs to eol | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0026139 | OH | Sus | 31229173 | No | 2016 | APR | Yes | Line to Ground | 1196185 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | OTHER | WIRE DOWN BURNING AT 17450 STEVENS CANYON RD | 20160407 | 2024 | 1446609 | 466 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2318 | 37.2802 | -122.1192 | 17450 STEVENS CANYON RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0026988 | OH | Sus | 0 | No | 2016 | APR | Yes | Line to Ground | 1196737 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 32117 | 20160410 | 1600 | 1448335 | 615 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 5196 | 37.1573 | -121.9856 | 17975 HELEN WAY | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0027612 | OH | Sus | 31230368 | No | 2016 | APR | Yes | Line to Ground | 1197202 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 5203 | 20160416 | 1657 | 1452069 | 1314 | Distribution Circuit | Vegetation | Tree - branch fell on line | 100 | 37663 | 37.2354 | -122.0629 | 15 POLES LD SIDE OF 5203 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0029139 | OH | Sus | 0 | No | 2016 | APR | Yes | Line to Ground | 1198307 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4417 | 20160428 | 1927 | 1461220 | 152 | Distribution Circuit | 3rd Party | Vehicle | 37 | 5624 | 37.1978 | -122.0278 | CARPOLE: 22 POLES E/OF 29321 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0032503 | OH | Sus | 0 | No | 2016 | APR | Yes | Line to Ground | 1200830 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1106 | 83371106 | FUSE | 4743 | 20160513 | 1940 | 1469458 | 522 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6264 | 37.2268 | -122.003 | 16530 Lucky RD los garto | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0035987 | OH | Sus | 42700725 | No | 2016 | MAY | Yes | Line to Ground | 1203409 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN 6 POLES LD SIDE OF 17943 | 20160712 | 239 | 1508610 | 608 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 14592 | 37.1348 | -121.9888 | 6 POLES LD SIDE OF 17943 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0049201 | OH | Sus | 42739797 | No | 2016 | JUL | Yes | Open Circuit | 1213367 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 2 | HICKS-1116 | 83431116 | OTHER | WIRE DOWN IFO 15280 SHANNON RD | 20160726 | 1934 | 1516672 | 636 | Distribution Circuit | Vegetation | Tree - fell into line | 232 | 91498 | 37.2256 | -121.937 | Estrada- G/1027: tree thru the line 15280 Shannon Road | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0052781 | OH | Sus | 31259691 | yes | 2016 | JUL | Yes | Line to Ground | 1215831 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 32331 | 20160729 | 2205 | 1518804 | 1018 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4449 | 37.1445 | -122.0036 | NGUYEN: IFO 17100 Old Ranch Rd. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0053786 | OH | Sus | 31260444 | No | 2016 | JUL | Yes | Line to Ground | 1216503 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 29297 | 20160805 | 917 | 1522007 | 413 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3304 | 37.1063 | -121.9447 | LAFON/508: tree fell -12kv down & damgd tx pole to 305 ridge top rd | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0055311 | OH | Sus | 0 | No | 2016 | AUG | Yes | Line to Ground | 1217453 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 4461 | 20160915 | 1556 | 1542485 | 845 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 28900 | 37.1102 | -121.9509 | ON REDWOOD LODGE ROAD W/OF ADDRESS 16035 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0065001 | OH | Sus | 31271607 | No | 2016 | SEP | Yes | Line to Ground | 1224002 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 11397 | 20160926 | 1523 | 1547951 | 10236 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 68 | 7459 | 37.1088 | -121.8439 | ZANDATE- BOBBY: Loma Prieta- Loma Chiquita Rd | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0067629 | OH | Sus | 31273619 | yes | 2016 | SEP | Yes | Three Phase Fault | 1225895 | PW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 17345 | 20161007 | 2023 | 1554867 | 297 | Distribution Circuit | 3rd Party | Vehicle | 6 | 1782 | 37.1728 | -122.0698 | 3 SPANS EAST OF 2539 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0070509 | OH | Sus | 0 | No | 2016 | OCT | Yes | Multi-Fault | 1228048 | PW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | JUMPER | WIRE DOWN @ 16246 REDWOOD LODGE RD. | 20161011 | 930 | 1556252 | 680 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 1579 | 37.1059 | -121.9566 | 16246 REDWOOD LODGE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0071104 | OH | Sus | 31276345 | No | 2016 | OCT | Yes | Line to Ground | 1228508 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 18597 | 20161015 | 2059 | 1561973 | 982 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 7856 | 37.1457 | -121.9836 | 1ST SPAN TO 5TH SPAN LD SIDE OF FUSE 18597 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072743 | OH | Sus | 42814335 | yes | 2016 | OCT | Yes | Line to Ground | 1229783 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN @ 21717 SUMMIT RD | 20161016 | 1116 | 1562767 | 318 | Distribution Circuit | Equipment Failure/Involved | Overhead | 557 | 43679 | 37.1488 | -121.9935 | 21717 SUMMIT RD | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072855 | OH | Sus | 42814335 | yes | 2016 | OCT | Yes | Line to Ground | 1229885 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 2459 | 20161017 | 410 | 1563962 | 480 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 7200 | 37.144 | -121.9901 | 2 P/W/O 2459 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0073121 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1230151 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 21101 | 20161028 | 752 | 1571544 | 450 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 5850 | 37.1336 | -121.965 | ZANDATE- BOBBY: 23405 Schulties Rd. | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076254 | OH | Sus | 42869089 | yes | 2016 | OCT | Yes | Line to Ground | 1232526 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 21295 | 20161028 | 1118 | 1571819 | 1077 | Distribution Circuit | Vegetation | Tree - fell into line | 103 | 61768 | 37.1983 | -122.0115 | LD SIDE 21295 | Rain-Strong Winds-Heavy Rain-Combination-Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076398 | OH | Sus | 31281070 | yes | 2016 | OCT | Yes | Line to Line | 1232594 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 3459 | 20161030 | 1233 | 1573199 | 858 | Distribution Circuit | Vegetation | Tree - fell into line | 159 | 32534 | 37.1287 | -121.953 | SOURCE SIDE & LOAD SIDE OF 15585 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076788 | OH | Sus | 31281293 | No | 2016 | OCT | Yes | Line to Ground | 1232889 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 5387 | 20161030 | 724 | 1572959 | 721 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5768 | 37.2294 | -122.0545 | GARCIA: 16128 SANBRN RD | Strong Winds-Rain-Heavy Rain-Drizzle-Combination-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076737 | OH | Sus | 42869645 | No | 2016 | OCT | Yes | Line to Ground | 1232845 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 21101 | 20161031 | 131 | 1573500 | 655 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 8515 | 37.1336 | -121.965 | 23280 SHULTIES RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076877 | OH | Sus | 31281420 | No | 2016 | OCT | Yes | Line to Ground | 1232980 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 12041 | 20161102 | 2212 | 1575627 | 454 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 29896 | 37.0983 | -121.9473 | S/O 519 265 OLD TURNPIKE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0077685 | OH | Sus | 42872373 | No | 2016 | NOV | Yes | Force Out | 1233623 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 4467 | 20161119 | 1918 | 1585344 | 660 | Distribution Circuit | Equipment Failure/Involved | Overhead | 275 | 8234 | 37.1041 | -121.9331 | 15245 STETSON RD | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081189 | OH | Sus | 0 | yes | 2016 | NOV | Yes | Line to Ground | 1236209 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 4465 | 20161120 | 1821 | 1585995 | 1309 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 9067 | 37.1081 | -121.9452 | Second span in from open Jumpers IFO 25219 sOQUEL sj | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0081300 | OH | Sus | 0 | yes | 2016 | NOV | Yes | Line to Line | 1236341 | CAW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LB48 | 20161214 | 2245 | 1602202 | 452 | Distribution Circuit | Vegetation | Tree - branch fell on line | 122 | 6102 | 37.1748 | -122.0608 | 22101 BEAR CREEK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085626 | OH | Sus | 31289589 | No | 2016 | DEC | Yes | Line to Ground | 1240278 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4421 | 20161215 | 1558 | 1603084 | 1439 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 74828 | 37.1899 | -122.031 | OWEN- JACOB: 20170 Thompson Rd | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085811 | OH | Sus | 42899781 | yes | 2016 | DEC | Yes | Line to Ground | 1240479 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 15769 | 20161215 | 1414 | 1602973 | 696 | Distribution Circuit | Vegetation | Tree - fell into line | 117 | 25932 | 37.2474 | -122.068 | 2/S/S/O 15769 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085765 | OH | Sus | 31289496 | yes | 2016 | DEC | Yes | Line to Ground | 1240434 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | JUMPER | WIRE DOWN | 20161216 | 151 | 1604051 | 724 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 2109 | 37.2509 | -122.0941 | 1 SPAN E/O 11239 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085941 | OH | Sus | 42899781 | yes | 2016 | DEC | Yes | Line to Ground | 1240607 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 18123 | 20161230 | 1026 | 1613305 | 422 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 6752 | 37.1326 | -121.9569 | HAUGEN- KIRK: SPAN AT LINE AND BUCK - CHASEWOOD AND NIKKIE LN | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0087396 | OH | Sus | 31292262 | No | 2016 | DEC | Yes | Line to Line | 1242833 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 15771 | 20170104 | 705 | 1617785 | 705 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 23970 | 37.2482 | -122.0708 | 2/S/W/O FIRST TAP LOAD SIDE OF 15771 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on object | 17-0003447 | OH | Sus | 31292830 | yes | 2017 | JAN | Yes | Line to Ground | 1243628 | PW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 21117 | 20170107 | 1510 | 1621916 | 1275 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 12842 | 37.1086 | -121.8338 | ZANDATE- BOBBY: IFO 29750 Loma Chiquita Rd. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004778 | OH | Sus | 31294278 | yes | 2017 | JAN | Yes | Line to Ground | 1244578 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 21101 | 20170124 | 642 | 1665234 | 1308 | Distribution Circuit | Environmental/External | Flood/Erosion | 13 | 6194 | 37.1336 | -121.965 | SCHULTES RD- LG | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0014248 | OH | Sus | 31297030 | yes | 2017 | JAN | Yes | Line to Line | 1253002 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER | WIRE DOWN MTR# 1009043402 | 20170131 | 16 | 1670966 | 1094 | Distribution Circuit | 3rd Party | Vehicle | 929 | 12476 | 37.1094 | -121.9473 | VICINITY OF MTR# 1009043402 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0016215 | OH | Sus | 31302705 | No | 2017 | JAN | Yes | Force Out | 1254586 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | OTHER | WIRE DOWN 2 SPANS S/OF TRIP SAVER 2243 | 20170204 | 2312 | 1675182 | 733 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 20524 | 37.2774 | -122.1102 | 2 SPANS S/OF 2243 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017520 | OH | Sus | 42939146 | No | 2017 | FEB | Yes | None | 1255497 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | FUSE | 18353 | 20170205 | 1910 | 1675559 | 560 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5040 | 37.2786 | -122.1116 | 4 SPANS W/OF 18353 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017630 | OH | Sus | 31303968 | No | 2017 | FEB | Yes | Line to Line | 1255595 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4421 | 20170208 | 1226 | 1681895 | 1573 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 81796 | 37.1899 | -122.031 | CHRISTMAS TREE FARM- LOADSIDE OF 4421 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019146 | OH | Sus | 42939926 | yes | 2017 | FEB | Yes | Line to Line | 1256758 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 53861 | 20170210 | 922 | 1685165 | 4643 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 29111 | 37.1733 | -122.0624 | 21000 BEAR CREEK RD.- LG | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019954 | OH | Sus | 42939943 | yes | 2017 | FEB | Yes | Line to Ground | 1257349 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 4477 | 20170210 | 652 | 1684734 | 703 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 16872 | 37.1094 | -121.9076 | RINEHART- ROGER: 3 spans south of c/o 4477 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019897 | OH | Sus | 42939943 | yes | 2017 | FEB | Yes | Line to Line | 1257313 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER | 1 PH WIRE DOWN LINE & BUCK 1P S/OF 33591 - SO | 20170226 | 1858 | 1714612 | 1118 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1284 | 185046 | 37.1264 | -121.9369 | Zandate- Louie/1058: MORRILL RD & WRIGHTS STATION RD | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0026902 | OH | Sus | 42954069 | No | 2017 | FEB | Yes | Line to Ground | 1263601 | CSO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | FUSE | 31999 | 20170226 | 1353 | 1714440 | 982 | Distribution Circuit | Environmental/External | Flood/Erosion | 3 | 2946 | 37.2811 | -122.1188 | STEVENS CANYON RD N/O CHARCOAL TAP | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0026877 | OH | Sus | 0 | No | 2017 | FEB | Yes | Line to Ground | 1263574 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | TRIP-SAVER | 11533 | 20170321 | 528 | 1731594 | 1333 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 49321 | 37.1429 | -121.9939 | AGBALOG- VINCE: same | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0032230 | OH | Sus | 42974069 | yes | 2017 | MAR | Yes | Line to Ground | 1267710 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | LOS GATOS-1102 | 82021102 | FUSE | 4015 | 20170321 | 1037 | 1731706 | 923 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 50765 | 37.23 | -121.9866 | LAFON/508: lco 4015 pole brkn & 12kv span down | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0032312 | OH | Sus | 31313574 | yes | 2017 | MAR | Yes | Line to Ground | 1267750 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER | WIRE DOWN 3 S/N OF SA07 | 20170321 | 1322 | 1732055 | 1106 | Distribution Circuit | Vegetation | Tree - fell into line | 1534 | 205478 | 37.1554 | -121.9804 | 3 S/N OF SA07 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0032417 | OH | Sus | 42974393 | yes | 2017 | MAR | Yes | Line to Ground | 1267803 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 2979 | 20170321 | 245 | 1731443 | 980 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 22120 | 37.1014 | -121.9227 | LINE AND BUCK SOUTH OF METER 1009045419 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0032293 | OH | Sus | 31313571 | yes | 2017 | MAR | Yes | Line to Ground | 1267747 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 15767 | 20170322 | 849 | 1732756 | 1031 | Distribution Circuit | Environmental/External | Flood/Erosion | 7 | 2369 | 37.2364 | -122.0661 | STEVENS- ROBERT: SAP ID 1005 266 97 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0032714 | OH | Sus | 31314018 | yes | 2017 | MAR | Yes | Line to Ground | 1268019 | PW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 1429 | 20170323 | 1608 | 1734002 | 802 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11228 | 37.1474 | -121.9749 | IFO 17550 MOUNTAIN CHARLIE RD | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0033231 | OH | Sus | 31314298 | No | 2017 | MAR | Yes | Line to Ground | 1268316 | PW | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN 25333 HUTCHINSON RD | 20170324 | 2302 | 1735080 | 1484 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8512 | 37.1211 | -122.0109 | Zandate- Louie/1058: 25333 HUTCHINSON RD | Combination-Fog-Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0033651 | OH | Sus | 42977214 | yes | 2017 | MAR | Yes | Line to Ground | 1268592 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 17431 | 20170330 | 952 | 1739163 | 1257 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 40224 | 37.1102 | -121.9509 | STEVENS- ROBERT: 221 TALL TREE HILL | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0035190 | OH | Sus | 31315907 | yes | 2017 | MAR | Yes | Line to Line | 1269836 | PW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 963 | 20170331 | 858 | 1740806 | 822 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 3828 | 37.1692 | -121.9892 | HAUGEN- KIRK: I DRIVEWAY TO 20697 HILLSIDE DR | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0035555 | OH | Sus | 31316100 | yes | 2017 | MAR | Yes | Line to Ground | 1270146 | PW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 5165 | 20170408 | 533 | 1752314 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1791 | 37.1699 | -122.0529 | NGUYEN: IFO 21855 Bear Creek Rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038217 | OH | Sus | 31318017 | yes | 2017 | APR | Yes | Line to Line | 1272277 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER | 60092 | 20170504 | 1426 | 1774730 | 124 | Distribution Circuit | Vegetation | Tree - fell into line | 1268 | 58291 | 37.1825 | -121.985 | HAUGEN- KIRK: 5TH POLE SOUTH OF 8349 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0045346 | OH | Sus | 31323577 | yes | 2017 | MAY | Yes | Multi-Fault | 1277588 | PW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | HICKS-2103 | 83432103 | FUSE | 18375 | 20170612 | 351 | 1802332 | 549 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 6039 | 37.2139 | -121.913 | 2P S/OF 18375 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0054469 | OH | Sus | 0 | No | 2017 | JUN | Yes | Line to Ground | 1284362 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LB48 | 20170621 | 234 | 1813434 | 140 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 13020 | 37.19 | -121.9942 | 3 SPANS SOUTH OF SB19 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0057179 | OH | Sus | 43042549 | yes | 2017 | JUN | Yes | Line to Ground | 1286566 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN 3P W/OF #315619523975 | 20170712 | 1439 | 1830200 | 802 | Distribution Circuit | Vegetation | Tree - branch fell on line | 36 | 24690 | 37.149 | -122.0039 | STEVENS- ROBERT: 3 spans w/o CGC # 315619523975 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0062439 | OH | Sus | 31336732 | No | 2017 | JUL | Yes | Line to Ground | 1290409 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 31271 | 20170712 | 2316 | 1830301 | 1582 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 9492 | 37.1606 | -121.9701 | STEVENS- ROBERT: 21353 SUNNYSIDE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0062472 | OH | Sus | 31336173 | No | 2017 | JUL | Yes | Line to Ground | 1290448 | PW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | FUSE | 18353 | 20170801 | 2314 | 1844279 | 866 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 7794 | 37.2786 | -122.1116 | Zandate- Louie/1058: COs 18351 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0067209 | OH | Sus | 31340130 | No | 2017 | AUG | Yes | Line to Ground | 1293807 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 15771 | 20170802 | 1120 | 1844647 | 520 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 15250 | 37.2482 | -122.071 | 1 POLE WEST OF 15775 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0067387 | OH | Sus | 43073260 | yes | 2017 | AUG | Yes | Line to Ground | 1293944 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | JUMPER | TREE DOWN | 20170813 | 1341 | 1851735 | 719 | Distribution Circuit | Vegetation | Tree - bark fell into line | 33 | 11659 | 37.1015 | -121.938 | S/O 21111 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0069958 | OH | Sus | 31342291 | No | 2017 | AUG | Yes | Line to Ground | 1295776 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 5203 | 20170817 | 1156 | 1854231 | 824 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 32741 | 37.2354 | -122.0629 | ZANDATE- BOBBY: 16500 Sanborn Rd. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0071067 | OH | Sus | 43087154 | No | 2017 | AUG | Yes | Line to Ground | 1296509 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 2 | LOS GATOS-1108 | 82021108 | FUSE | 12187 | 20170822 | 1336 | 1857058 | 1235 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 53336 | 37.2284 | -121.9932 | KELLY- 4017 / 831-682-1802: Two poles down on Overlook Rd. | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0072078 | OH | Sus | 0 | No | 2017 | AUG | Yes | Line to Ground | 1297254 | PW | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | FUSE | 1251 | 20170830 | 1407 | 1863425 | 661 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 2181 | 37.2947 | -122.0822 | S/O 33481 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0074224 | OH | Sus | 0 | No | 2017 | AUG | Yes | Line to Ground | 1298754 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 60124 | 20170831 | 1112 | 1864071 | 591 | Distribution Circuit | Vegetation | Tree - fell into line | 633 | 99153 | 37.1462 | -121.9823 | ZANDATE- BOBBY: Between LCO 19941 & LCO 19943 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0074457 | OH | Sus | 43097394 | No | 2017 | AUG | Yes | Line to Line | 1298945 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | LOS GATOS-1101 | 82021101 | JUMPER | 12KV DOWN 16401 S KENNEDY RD | 20170927 | 753 | 1886536 | 322 | Distribution Circuit | Animal | Squirrel | 658 | 21064 | 37.2211 | -121.9566 | RISER 29035 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0082014 | OH | Sus | 43118247 | No | 2017 | SEP | Yes | Line to Ground | 1304560 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 29297 | 20171018 | 744 | 1903049 | 391 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 3128 | 37.1063 | -121.9447 | WIRE DOOWN at 305 RIDGE TOP RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0088203 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1308976 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1103 | 83371103 | OTHER | LC16 | 20171107 | 958 | 1917430 | 496 | Distribution Circuit | Equipment Failure/Involved | Overhead | 657 | 63087 | 37.2626 | -122.0376 | 20800 REID LN | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0093174 | OH | Sus | 43208249 | No | 2017 | NOV | Yes | Line to Ground | 1312638 | CSO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER | WIRE DOWN 8 SPANS N/OF 2981 | 20180105 | 616 | s1323339 | 469 | Distribution Circuit | Equipment Failure/Involved | Overhead | 461 | 157825 | 37.2049 | -121.9916 | 8 SPANS NORTH OF 2981 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0003743 | OH | Sus | 43244516 | No | 2018 | JAN | Yes | Line to Ground | 1323339 | CSO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | STELLING-1110 | 83481110 | FUSE | 223709 | 20180106 | 751 | 3073 | 737 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3197 | 37.2515 | -122.123 | 2 SPANS LD SIDE OF 223709 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0004034 | OH | Sus | 0 | No | 2018 | JAN | Yes | Line to Ground | 1323452 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER | WIRE DOWN N/OF FUCO'S 43795 | 20180227 | 308 | 32471 | 755 | Distribution Circuit | Vegetation | Tree - branch fell on line | 93 | 29258 | 37.1738 | -121.9461 | Zandate- Louie/1058: 16600 SODA SPRINGS | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0017598 | OH | Sus | 43285651 | yes | 2018 | FEB | Yes | Line to Ground | 1332332 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER | 60092 | 20180313 | 204 | 42946 | 718 | Distribution Circuit | Vegetation | Tree - fell into line | 1133 | 103849 | 37.1825 | -121.985 | ALDERCROFT HILLS & OLD GOLD MINE RD | Strong Winds-Rain-Combination-Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0022062 | OH | Sus | 31383650 | yes | 2018 | MAR | Yes | Multi-Fault | 1335519 | CAW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | LA42 | 20180322 | 455 | 50100 | 1230 | Distribution Circuit | Vegetation | Tree - fell into line | 794 | 65980 | 37.1462 | -121.9823 | 22616 SUMMIT | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025263 | OH | Sus | 31385423 | yes | 2018 | MAR | Yes | Line to Line | 1337480 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 33349 | 20180322 | 543 | 50185 | 782 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 20558 | 37.1268 | -121.957 | STEVENS- ROBERT: IFO 23610 SKY VIEW TERR | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025361 | OH | Sus | 31385491 | yes | 2018 | MAR | Yes | Line to Ground | 1337540 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER | WIRE DOWN @ BLACK RD. & MONTEVINA RD | 20180511 | 632 | 83567 | 396 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1598 | 169429 | 37.1941 | -121.9949 | BLACK RD. & MONTEVINA RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0040105 | OH | Sus | 43344469 | yes | 2018 | MAY | Yes | Line to Ground | 1348212 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN | 20180701 | 407 | 122123 | 519 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 4567 | 37.1559 | -121.99 | CRIVELLO- 4176 / 831-682-1912: 37.1558683--121.9907833-531.300000-3D | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0056052 | OH | Sus | 0 | No | 2018 | JUL | Yes | Line to Ground | 1360864 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LB44 | 20180704 | 2004 | 124551 | 738 | Distribution Circuit | 3rd Party | Vehicle | 331 | 233218 | 37.1938 | -121.9959 | 19251 BLACK RD- WIRE DOWN 1 E/O 7641 & WRAPPED WIRE 1 W/O 7637 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0056999 | OH | Sus | 31398863 | No | 2018 | JUL | Yes | Line to Ground | 1361523 | PW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LB48 | 20180709 | 1550 | 127332 | 639 | Distribution Circuit | Equipment Failure/Involved | Overhead | 96 | 11589 | 37.19 | -121.9942 | 2 SPANS OF WIRE DOWN BET 8989 & 8235 | Clear-32-90 F | Insulator | Broken, wire on ground | 18-0058039 | OH | Sus | 31399329 | yes | 2018 | JUL | Yes | Line to Line | 1362342 | INS | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4449 | 20180715 | 241 | 132059 | 637 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 5733 | 37.1394 | -121.9671 | NGUYEN- NGHIA: at 4449 LD SIDE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0059918 | OH | Sus | 43401324 | No | 2018 | JUL | Yes | Line to Ground | 1363867 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | JUMPER | OJS N/OF REDWOOD GULCH RD 2/S/SOURCE SIDE LAS | 20180720 | 1810 | 136799 | 620 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 2 | 1240 | 37.2655 | -122.1023 | SAME | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0062162 | OH | Sus | 43413361 | No | 2018 | JUL | Yes | Line to Ground | 1365450 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER | WIRE DOWN PAST 21049 | 20180727 | 2312 | 142183 | 595 | Distribution Circuit | Vegetation | Tree - fell into line | 173 | 30475 | 37.1814 | -122.0294 | 3/SP/E/OF 21049 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0064525 | OH | Sus | 43422804 | No | 2018 | JUL | Yes | Line to Ground | 1367288 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER | WIRE DOWN 19930 GIST RD | 20180809 | 1511 | 152352 | 627 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4197 | 37.1946 | -122.0244 | GIST RD- S/OF BLACK RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0068438 | OH | Sus | 31402535 | No | 2018 | AUG | Yes | Line to Ground | 1370081 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 32117 | 20180812 | 820 | 153866 | 426 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 10224 | 37.1573 | -121.9856 | 1492 MARY ALICE WAY | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0069053 | OH | Sus | 43438963 | No | 2018 | AUG | Yes | Line to Ground | 1370458 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | 60116 | 20180812 | 1426 | 153998 | 381 | Distribution Circuit | Vegetation | Tree - branch fell on line | 428 | 27285 | 37.1734 | -121.9929 | KREMENLIFF- JACOB: 3 PL S/O LA42 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0069081 | OH | Sus | 43438971 | No | 2018 | AUG | Yes | Line to Ground | 1370482 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 31297 | 20180908 | 358 | 170409 | 455 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 7735 | 37.1392 | -121.9747 | 1 POLE LD SIDE OF 31297 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0077740 | OH | Sus | 43457148 | No | 2018 | SEP | Yes | Line to Ground | 1376479 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 26059 | 20180908 | 1411 | 170674 | 421 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 11367 | 37.2394 | -122.013 | REAR OF 19425 REDBERRY DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0077787 | OH | Sus | 31405686 | No | 2018 | SEP | Yes | Line to Ground | 1376589 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | OTHER | WIRE DOWN 2 SPANS SSD 15767 | 20180921 | 1115 | 178782 | 355 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 5323 | 37.2365 | -122.0656 | LAFON/508: 1spn 3phas 12kv down at take off pl 2spns source side of 15767 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0082091 | OH | Sus | 43486755 | No | 2018 | SEP | Yes | Line to Ground | 1379777 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | FUSE | 18353 | 20180922 | 1620 | 179480 | 490 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 3716 | 37.2779 | -122.112 | SARA: 18000 STEVENS CANYON RD. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0082442 | OH | Sus | 31406495 | No | 2018 | SEP | Yes | Line to Ground | 1380005 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 60124 | 20181007 | 1025 | 190113 | 883 | Distribution Circuit | Equipment Failure/Involved | Overhead | 634 | 265918 | 37.1462 | -121.9823 | VILLAGOMEZ- ROBERT /3367: 21705 AND 21570 SUMMIT RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0087898 | OH | Sus | 43498406 | yes | 2018 | OCT | Yes | Line to Line | 1383827 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER | WIRE DOWN @ N/E OF CGC# 315557024990 | 20181007 | 144 | 189965 | 861 | Distribution Circuit | Vegetation | Tree - fell into line | 1597 | 224444 | 37.1773 | -122.0261 | ACHATZ-TED: 19980 Skyline Blvd south | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0087807 | OH | Sus | 43498362 | yes | 2018 | OCT | Yes | None | 1383800 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | JUMPER | WIRE DOWN | 20181007 | 1432 | 190309 | 651 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 651 | 37.1387 | -121.9459 | VILLAGOMEZ- ROBERT /3367: 1 POLE E/O 8511 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0087981 | OH | Sus | 43498415 | yes | 2018 | OCT | Yes | Line to Ground | 1383891 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | TRIP-SAVER | 12041 | 20181024 | 514 | 201157 | 346 | Distribution Circuit | 3rd Party | Vehicle | 79 | 27334 | 37.0977 | -121.948 | 7201 SOQUEL ROAD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0093567 | OH | Sus | 31413868 | No | 2018 | OCT | Yes | Force Out | 1387767 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | OTHER | WIRE DOWN PAST 2243 | 20181109 | 816 | s1391675 | 784 | Distribution Circuit | Vegetation | Tree - fell into line | 403 | 77077 | 37.277 | -122.1112 | PAST 2243 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0098521 | OH | Sus | 43535543 | No | 2018 | NOV | Yes | Line to Ground | 1391675 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | REGULATOR | 1 PHASE DOWN | 20181122 | 247 | 221646 | 868 | Distribution Circuit | Equipment Failure/Involved | Overhead | 330 | 177232 | 37.1928 | -122.0094 | 1 WEST OF 7639- 2 S/O 18251 (MTR#1007441323) | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102228 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1394369 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 17959 | 20181128 | 722 | 226204 | 508 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3556 | 37.1238 | -122.0101 | 25333 HUTCHINSON RD- LOS GATOS | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104180 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1395707 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER | O/J N/W 17959 | 20181130 | 850 | 229948 | 690 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4830 | 37.1241 | -122.0102 | 13072 BELL RD- LOS GATOS | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 18-0105546 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Force Out | 1396568 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 31297 | 20181206 | 1912 | 235365 | 648 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 11016 | 37.1392 | -121.9747 | 23149 OLD SANTA CRUZ HWY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0107747 | OH | Sus | 31417924 | No | 2018 | DEC | Yes | Line to Ground | 1398076 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | HICKS-1116 | 83431116 | FUSE | 31171 | 20181217 | 547 | 242082 | 593 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 17790 | 37.222 | -121.9253 | BET 2463 & 2461 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0109607 | OH | Sus | 43616114 | yes | 2018 | DEC | Yes | Line to Line | 1400248 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 11753 | 20181225 | 753 | 247029 | 595 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4760 | 37.2586 | -122.0949 | 31613 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110622 | OH | Sus | 43621724 | No | 2018 | DEC | Yes | Force Out | 1401703 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | 60116 | 20181226 | 2206 | 247749 | 641 | Distribution Circuit | Vegetation | Tree - fell into line | 497 | 42847 | 37.1734 | -121.9929 | NGUYEN- NGHIA: IFO 21755 Old Santa Cruz Hwy | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110784 | OH | Sus | 31419723 | No | 2018 | DEC | Yes | Line to Ground | 1401885 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 18251 | 20181227 | 1601 | 248327 | 2181 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 206215 | 37.1941 | -122.0217 | 20514B GIST RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0110868 | OH | Sus | 31419797 | No | 2018 | DEC | Yes | Line to Ground | 1402023 | PW | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER | WIREDOWN @ 16300 OLD RANCH RD | 20190108 | 1044 | 260420 | 566 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 2723 | 37.1439 | -122.0054 | 16300 OLD RANCH RD- LOS GATOS | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0006475 | OH | Sus | 43625030 | yes | 2019 | JAN | Yes | Line to Line | 1404564 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 21117 | 20190108 | 929 | 260278 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 5718 | 37.1079 | -121.8325 | ACHATZ-TED: 30250 Loma Chiquita Rd | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0006228 | OH | Sus | 31420535 | yes | 2019 | JAN | Yes | Force Out | 1404475 | PW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 17121 | 20190119 | 957 | 276564 | 217 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 8029 | 37.1634 | -122.0139 | 460 OUTER ZAYANTE RD | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0012081 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408429 | PW | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | TRIP-SAVER | 12041 | 20190203 | 1216 | 288819 | 876 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 47988 | 37.0977 | -121.948 | WIRE DOWN 1? 3 SPANS LD SIDE OF 12041 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017540 | OH | Sus | 43665363 | yes | 2019 | FEB | Yes | Line to Ground | 1411949 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 60124 | 20190306 | 1302 | 332834 | 721 | Distribution Circuit | Vegetation | Tree - branch fell on line | 163 | 54119 | 37.1462 | -121.9823 | 15885 OLD JAPANEESE RD | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0031328 | OH | Sus | 31427519 | yes | 2019 | MAR | Yes | Line to Line | 1422327 | PW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | JUMPER | WIRE DOWN BET 2ND & 3RD SPAN W/OF 17735 | 20190327 | 152 | 348147 | 620 | Distribution Circuit | Equipment Failure/Involved | Overhead | 502 | 127160 | 37.2523 | -122.047 | BET 2ND & 3RD SPAN W/O 17735- 1 P N/O 15769 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0037284 | OH | Sus | 43718428 | yes | 2019 | MAR | Yes | Line to Ground | 1426562 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | OTHER | WIRE DOWN @ STEVENS CANYON RD AND REDWOOD GUL | 20190430 | 1335 | 371063 | 745 | Distribution Circuit | Vegetation | Tree - fell into line | 462 | 28740 | 37.2679 | -122.0938 | WIRE DOWN at STEVENS CANYON RD AND REDWOOD GULCH RD X-St.: REDWOOD GULCH RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0047584 | OH | Sus | 43756598 | No | 2019 | APR | Yes | Line to Ground | 1433722 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 4767 | 20190520 | 132 | 385719 | 658 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3290 | 37.1496 | -122.0035 | 125 JENSEN SPRINGS ROAD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0054154 | OH | Sus | 31443089 | No | 2019 | MAY | Yes | Line to Ground | 1438352 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | 60116 | 20190526 | 47 | 390550 | 1309 | Distribution Circuit | 3rd Party | Vehicle | 1504 | 183489 | 37.1734 | -121.9929 | 2 POLES SOUTH OF 4429 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0057740 | OH | Sus | 0 | No | 2019 | MAY | Yes | Line to Ground | 1441246 | PW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1105 | 83371105 | JUMPER | WIRE DOWN | 20190626 | 436 | 429208 | 468 | Distribution Circuit | Vegetation | Tree - fell into line | 103 | 46548 | 37.2293 | -122.0543 | ACHATZ-TED: North of fuse 7163 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0072069 | OH | Sus | 43857639 | No | 2019 | JUN | Yes | Open Circuit | 1452703 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 8511 | 20190715 | 1929 | 453147 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 406 | 37.1388 | -121.9466 | WRIGHT STATION ROAD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0077711 | OH | Sus | 0 | No | 2019 | JUL | Yes | Line to Ground | 1456395 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 21297 | 20190717 | 208 | 454969 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 22724 | 37.1981 | -122.0111 | 1/SP LD SIDE 21297 | Clear-Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0078150 | OH | Sus | 31457651 | No | 2019 | JUL | Yes | Line to Ground | 1456707 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1104 | 83371104 | FUSE | 2335 | 20190723 | 1628 | 469636 | 770 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 19250 | 37.2459 | -121.9992 | SARA: REAR OF 18695 MONTEWOOD DRIVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0080428 | OH | Sus | 43895690 | yes | 2019 | JUL | Yes | Line to Ground | 1458216 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1105 | 83371105 | FUSE | 15777 | 20190723 | 2137 | 469821 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3408 | 37.2542 | -122.0893 | WHITE- ERIC: 24104 BOOKER CRK RD. 2PSW | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0080482 | OH | Sus | 43897221 | yes | 2019 | JUL | Yes | Line to Ground | 1458273 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 33581 | 20190725 | 2347 | 472115 | 898 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5388 | 37.1546 | -121.9892 | 2 SPANS LD SIDE OF 33581 | Clear-32-90 F | Crossarm, Wood | Broken, wire on object | 19-0081381 | OH | Sus | 31460021 | No | 2019 | JUL | Yes | Line to Line | 1458779 | CAW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | INTERRUPTER | SB19 | 20190730 | 1038 | 475494 | 31 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 372 | 37.1752 | -122.0106 | 3/P/W/OF 9125 | Clear-32-90 F | Anchor or Guy | Broken, wire on object | 19-0082554 | OH | Sus | 0 | No | 2019 | JUL | Yes | Force Out | 1459668 | ANC | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | HICKS-1116 | 83431116 | FUSE | 18669 | 20190731 | 734 | 476007 | 768 | Distribution Circuit | Animal | Bird found | 43 | 24594 | 37.2321 | -121.9495 | 2/S/SS/33277 | Clear-Combination-Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0082823 | OH | Sus | 0 | No | 2019 | JUL | Yes | Line to Line | 1459795 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | JUMPER | WIRE DOWN BET 66177 AND 3211 | 20190831 | 841 | 549386 | 584 | Distribution Circuit | Animal | Bird found | 132 | 59643 | 37.1028 | -121.8755 | BETWEEN FUSE 3211 AND 66177 ON MAIN LINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0094310 | OH | Sus | 43942794 | No | 2019 | AUG | Yes | Open Circuit | 1466985 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 9321 | 20190901 | 143 | 550219 | 1097 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 48752 | 37.2481 | -122.0243 | 15168 PIEDMONT ROAD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0094416 | OH | Sus | 31470363 | No | 2019 | SEP | Yes | Line to Ground | 1467055 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | LOS GATOS-1107 | 82021107 | FUSE | 4403 | 20190909 | 2343 | 566096 | 930 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2309 | 172404 | 37.22 | -121.9821 | SOURCE SIDE OF FUSE 4403 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0097128 | OH | Sus | 0 | No | 2019 | SEP | Yes | Line to Ground | 1468829 | PW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN @ MTR#1003915407 | 20190928 | 1906 | 628337 | 1589 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 11303 | 37.1333 | -122.0054 | 23750 OAK FLAT RD- LOS GATOS | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0105044 | OH | Sus | 43973761 | yes | 2019 | SEP | Yes | Line to Ground | 1473821 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | OTHER | 15767 | 20200124 | 1824 | 769688 | 682 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4092 | 37.2364 | -122.0661 | 2/S/NE/O 15767 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0013591 | OH | Sus | 44164820 | No | 2020 | JAN | Yes | Line to Ground | 1509073 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 8977 | 20200206 | 1849 | 779704 | 513 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3078 | 37.1845 | -122.0032 | 5 pole n/w of 8977 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0018336 | OH | Sus | 31489446 | No | 2020 | FEB | Yes | Line to Ground | 1512493 | PW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | LOS GATOS-1101 | 82021101 | FUSE | 31049 | 20200314 | 1514 | 851316 | 454 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 3632 | 37.2192 | -121.9365 | 15292 KENNEDY RD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0032101 | OH | Sus | 44256294 | yes | 2020 | MAR | Yes | Line to Line | 1521434 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER | WIRE DOWN 2P LD SIDE OF 21101 | 20200324 | 2239 | 864011 | 448 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 6475 | 37.1327 | -121.9671 | 2 POLES LOAD SIDE OF FUCO 21101 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0035888 | OH | Sus | 44273145 | No | 2020 | MAR | Yes | Open Circuit | 1523863 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 60122 | 20200405 | 10 | 882586 | 1148 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 60844 | 37.1462 | -121.9823 | BROKEN POLE 1 LD SIDE OF 8347 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 20-0038475 | OH | Sus | 31499001 | yes | 2020 | APR | Yes | Line to Line | 1525311 | PW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | FUSE | 31999 | 20200421 | 1945 | 899076 | 435 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1305 | 37.2811 | -122.1188 | 3/S/NW/O 31999 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0043461 | OH | Sus | 0 | No | 2020 | APR | Yes | Line to Ground | 1528365 | PW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 1429 | 20200508 | 658 | 909332 | 709 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 9217 | 37.1474 | -121.9749 | STEVENS- ROBERT / 408-992-1494: 17957 MT CHARLIE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0048367 | OH | Sus | 44313888 | No | 2020 | MAY | Yes | Line to Ground | 1531445 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1106 | 83371106 | FUSE | 29169 | 20200529 | 2203 | 925881 | 633 | Distribution Circuit | Vegetation | Tree - grew into line | 25 | 15825 | 37.245 | -122.0096 | ACHATZ- TED / 408-479-1679: 19336 Monte Vista Dr | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on object | 20-0055821 | OH | Sus | 44336768 | yes | 2020 | MAY | Yes | Force Out | 1535683 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | RECLOSER | LC26 | 20200529 | 1749 | 925696 | 412 | Distribution Circuit | Vegetation | Tree - fell into line | 232 | 51398 | 37.2495 | -122.0193 | ZANDATE- BOBBY / 408-470-0297: IFO 15735 Peach Hill RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0055761 | OH | Sus | 44336765 | yes | 2020 | MAY | Yes | Line to Line | 1535622 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | OTHER | WIRE DOWN @ 19940 WRIGHT DR | 20200810 | 405 | 987459 | 450 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4260 | 37.1754 | -121.9895 | 19940 WRIGHT DR | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0081460 | OH | Sus | 31510906 | No | 2020 | AUG | Yes | Line to Ground | 1552814 | CAW | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | OTHER | 1 SPAN 3 WIRES DOWN | 20200909 | 324 | 1061720 | 754 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 24128 | 37.2482 | -122.0711 | 4 SPANS W/O 167792 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0095341 | OH | Sus | 44458759 | yes | 2020 | SEP | Yes | Force Out | 1562482 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 2 | LOS GATOS-1107 | 82021107 | FUSE | 4403 | 20200924 | 2030 | 1091924 | 655 | Distribution Circuit | Vegetation | Tree - branch fell on line | 104 | 48000 | 37.22 | -121.9821 | at CGC#315680526439 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0101291 | OH | Sus | 31514536 | No | 2020 | SEP | Yes | Line to Line | 1565971 | PW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | OTHER | WIRE DOWN 17955 MOUNTAIN CHARLIE RD. | 20201108 | 652 | 1139110 | 343 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 2744 | 37.1476 | -121.9821 | 17955 MOUNTAIN CHARLIE RD. | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0118393 | OH | Sus | 44517622 | No | 2020 | NOV | Yes | Line to Ground | 1578031 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER | WIRE DOWN 3 SPANS S/OF 4457 | 20201118 | 330 | 1148120 | 444 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 4060 | 37.1252 | -121.947 | ZANDATE- BOBBY / 408-470-0297: 3 spans S/O LCO 4457 | Clear-32-90F | Insulator | Broken, wire on ground | 20-0122219 | OH | Sus | 44542703 | No | 2020 | NOV | Yes | Line to Ground | 1580843 | INS | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 4191 | 20201126 | 338 | 1154741 | 1107 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 18314 | 37.1068 | -121.904 | 25567 FARHAVEN LN. | Clear-32-90F | Pole-Wood | Broken, wire on ground | 20-0125368 | OH | Sus | 0 | No | 2020 | NOV | Yes | Line to Ground | 1582529 | PW | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER | 60114 | 20201222 | 251 | 1196923 | 553 | Distribution Circuit | Equipment Failure/Involved | Overhead | 294 | 60501 | 37.119 | -121.9205 | 27205 LOMA PRIETA WAY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0131439 | OH | Sus | 31522321 | No | 2020 | DEC | Yes | Line to Ground | 1589000 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER | CUT JUMPERS TO ISO WIRE DOWN | 20210214 | 2248 | 1254962 | 1002 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 2144 | 37.1728 | -122.0725 | BEAR CREEK RD. 4 WAY POLE. SINGLE PHASE TAP TO THE WEST. 4/P/W/OF 4 WAY POLE. | Rain-Drizzle-Combination-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0025514 | OH | Sus | 31530300 | No | 2021 | FEB | Yes | Force Out | 1605176 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | JUMPER | JUMPERS | 20210225 | 852 | 1262274 | 767 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2301 | 37.1409 | -122.0071 | 16900 OLD RANCH RD. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0029490 | OH | Sus | 44663851 | No | 2021 | FEB | Yes | Line to Ground | 1607878 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 5387 | 20210301 | 716 | 1264400 | 687 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 6183 | 37.2296 | -122.0546 | 16456 SANDBORN ROAD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0030564 | OH | Sus | 44666620 | No | 2021 | MAR | Yes | Line to Ground | 1608543 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | OTHER | WIRE DOWN 2 SPANS S/O 988311 | 20210309 | 934 | 1275175 | 327 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 9855 | 37.2553 | -122.0902 | 2 SPANS SOUTH OF SBCO 988311 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0033842 | OH | Sus | 31532595 | No | 2021 | MAR | Yes | Line to Ground | 1610677 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | OTHER | WIRE DOWN 10 SPANS S/O 5203 | 20210613 | 112 | 1371996 | 964 | Distribution Circuit | Vegetation | Tree - fell into line | 104 | 55303 | 37.2339 | -122.0595 | 10 SPANS S/O 5203 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0073595 | OH | Sus | 31543366 | No | 2021 | JUN | Yes | Line to Ground | 1636813 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | FUSE | 18351 | 20210628 | 400 | 1386419 | 715 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2860 | 37.2808 | -122.1182 | 17300 STEVEN CANYON RD. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0080756 | OH | Sus | 31544784 | No | 2021 | JUN | Yes | Line to Ground | 1642487 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 18597 | 20210811 | 2257 | 1440602 | 472 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 4248 | 37.1457 | -121.9835 | 17955 MT CHARLIE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0103389 | OH | Sus | 44944228 | No | 2021 | AUG | Yes | Force Out | 1656756 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | OTHER | WIRE DOWN 2 SPANS S/W/O 15777 | 20210912 | 2146 | 1470309 | 457 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2594 | 37.2522 | -122.0904 | 2 SPANS S/W/O 15777 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0116586 | OH | Sus | 31551881 | No | 2021 | SEP | Yes | Line to Ground | 1665216 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | FUSE | 18353 | 20210926 | 120 | 1480753 | 703 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 6327 | 37.2779 | -122.1119 | #2 NW/O 17300 STEVENS CYN RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0122428 | OH | Sus | 31552820 | No | 2021 | SEP | Yes | Line to Ground | 1668758 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | 60116 | 20211021 | 1020 | 1504427 | 680 | Distribution Circuit | Vegetation | Tree - branch fell on line | 955 | 114319 | 37.1735 | -121.9928 | WIRE DOWN BETWEEN SA07 & 26175 DUE TO TREE BRANCH | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0134368 | OH | Sus | 31555338 | No | 2021 | OCT | Yes | Line to Line | 1676386 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | JUMPER | LINE DOWN A-B PH | 20211201 | 1317 | 1557350 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 725 | 48481 | 37.1551 | -121.9819 | 1 S/N/O 9225 | Clear-32-90 F | Conductor, Overhead | On Ground | 21-0153796 | OH | Sus | 45079440 | No | 2021 | DEC | Yes | Line to Ground | 1690557 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER | PRIM WIRE DOWN 1 SPAN S/OF CGC 315728123308 | 20211223 | 728 | 1579790 | 643 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 3453 | 37.1323 | -121.9671 | 1 SPAN S/OF CGC 315728123308 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160260 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1697696 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 17431 | 20211223 | 629 | 1579561 | 317 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 10144 | 37.1103 | -121.9511 | ZANDATE- BOBBY / 408-470-0297: 16306 Redwood Lodge Rd. | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160230 | OH | Sus | 45100221 | No | 2021 | DEC | Yes | Line to Ground | 1697658 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | OTHER | WIRE DOWN @ 15483 BOHLMAN RD. | 20211223 | 2213 | 1580227 | 265 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 3494 | 37.2454 | -122.0449 | 15483 BOLHMAN RD. | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160359 | OH | Sus | 45100798 | No | 2021 | DEC | Yes | Line to Ground | 1697802 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER | WIRE DOWN LD SIDE 33583 | 20211224 | 317 | 1580410 | 475 | Distribution Circuit | Vegetation | Tree - fell into line | 547 | 13653 | 37.1485 | -121.9932 | 21900 SUMMIT RD. | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160385 | OH | Sus | 31588354 | No | 2021 | DEC | Yes | Line to Ground | 1697829 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | RECLOSER | LB44 | 20220105 | 128 | 1595436 | 681 | Distribution Circuit | Vegetation | Tree - fell into line | 335 | 59758 | 37.1938 | -121.9958 | ZANDATE- LOUIE / 408-334-8410: 18440 BLACK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0006255 | OH | Sus | 31588902 | No | 2022 | JAN | Yes | Line to Ground | 1701079 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | FUSE | 19943 | 20220210 | 2213 | 1625224 | 468 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 936 | 37.1384 | -121.9968 | 22725 HUTCHINSON RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0021138 | OH | Sus | 31595326 | No | 2022 | FEB | Yes | Line to Ground | 1709217 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OCB | 1106/2 | 20220325 | 1908 | 1656099 | 783 | Distribution Circuit | 3rd Party | Vehicle | 335 | 38399 | 37.2264 | -121.9771 | SB15 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0038776 | OH | Sus | 0 | No | 2022 | MAR | Yes | Line to Ground | 1720108 | PW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1106 | 83371106 | FUSE | 4743 | 20220623 | 2255 | 1740656 | 893 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 4813 | 37.2268 | -122.003 | E/OF 9161 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0078002 | OH | Sus | 31606987 | No | 2022 | JUN | Yes | Line to Ground | 1747391 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | SWITCH | 60120 | 20220627 | 1437 | 1743515 | 229 | Distribution Circuit | Vegetation | Tree - fell into line | 548 | 119075 | 37.1302 | -121.9784 | AT MTR 1007855449 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0079137 | OH | Sus | 0 | No | 2022 | JUN | Yes | Three Phase Fault | 1748370 | PW | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | JUMPER | WIRE DOWN W/O 18351 | 20220709 | 1255 | 1752185 | 480 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 2262 | 37.2809 | -122.1184 | W/O 18351 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0083538 | OH | Sus | 0 | No | 2022 | JUL | Yes | Line to Ground | 1750872 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 967 | 20220911 | 203 | 1808269 | 793 | Distribution Circuit | Vegetation | Tree - fell into line | 958 | 340752 | 37.1735 | -121.9928 | HA- SONNY / 408-205-4288: 18101 idylwild | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0108957 | OH | Sus | 31615740 | No | 2022 | SEP | Yes | Force Out | 1767763 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 11911 | 20221108 | 410 | 1856627 | 565 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 2260 | 37.2502 | -122.0835 | ENT TO 24103 BIG BASIN WAY 5/SE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0128779 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Ground | 1782045 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | STELLING-1110 | 83481110 | FUSE | 18353 | 20221206 | 345 | 1876923 | 720 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 7200 | 37.2779 | -122.1119 | ZANDATE- LOUIE / 408-334-8410: 17288 STEVENS CANYON | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0136888 | OH | Sus | 31629492 | No | 2022 | DEC | Yes | Force Out | 1787731 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | SARATOGA-1107 | 83371107 | FUSE | 9325 | 20230115 | 919 | 1955699 | 536 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 5896 | 37.2471 | -122.0259 | LA FON- MIKE / 408-781-0933: 1phase 2spns 12kv TW down iro awaiting crew & tree crew | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016658 | OH | Sus | 0 | No | 2023 | JAN | Yes | Force Out | 1805395 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | CAMP EVERS-2106 | 83622106 | RECLOSER | 60124 | 20230122 | 2217 | 1965107 | 1661 | Distribution Circuit | Vegetation | Tree - fell into line | 549 | 253770 | 37.1462 | -121.9823 | NEAR 22682 SUMMIT RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0019964 | OH | Sus | 45647107 | No | 2023 | JAN | Yes | Line to Ground | 1807397 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | FUSE | 4427 | 20230128 | 759 | 1970285 | 640 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 12160 | 37.1728 | -121.9926 | 20385 IRON SPRINGS RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0022616 | OH | Sus | 31635800 | No | 2023 | JAN | Yes | Line to Ground | 1808810 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 17431 | 20230310 | 907 | 2030083 | 596 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 20264 | 37.1103 | -121.9511 | CGC 315747122657 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0042871 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1823632 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | RECLOSER | 60118 | 20230318 | 1554 | 2051394 | 154 | Distribution Circuit | Vegetation | Tree - branch fell on line | 933 | 44386 | 37.1247 | -121.9353 | SS MID SPAN OF CGC# 315747122657 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0048339 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1827542 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 2 | SARATOGA-1107 | 83371107 | FUSE | 22529 | 20230501 | 210 | 2101032 | 1021 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 26378 | 37.2399 | -122.0211 | AT CGC #315563827268 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0066527 | OH | Sus | 0 | No | 2023 | MAY | Yes | Line to Ground | 1839737 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1106 | 82021106 | OTHER | WIRE DOWN 1 SPAN SOURCE SIDE CGC 315554024980 | 20230804 | 1853 | 2182724 | 1026 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 8182 | 37.1737 | -122.0258 | 1 SPAN SOURCE SIDE CGC 315554024980 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0100802 | OH | Sus | 0 | No | 2023 | AUG | Yes | Open Circuit | 1863182 | CO | OH | No | Yes
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | JUMPER | WIRE DOWN 1 SPAN @ CGC 315799022210 | 20230928 | 207 | 2229104 | 1169 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1169 | 37.1013 | -121.9414 | CGC 315799022210 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0122108 | OH | Sus | 0 | No | 2023 | SEP | Yes | Line to Ground | 1877635 | CO | OH | No | No
DE ANZA | FIELD OPS SOUTH | Tier 3 | LOS GATOS-1107 | 82021107 | FUSE | 6947 | 20231219 | 602 | 2295307 | 615 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 8583 | 37.1169 | -121.924 | 3P S/O HIGHLAND WY | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0148075 | OH | Sus | 31679718 | No | 2023 | DEC | Yes | Line to Ground | 1898913 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ROSSMOOR-1101 | 14161101 | RECLOSER | L503R | 20130211 | 1359 | 741001 | 184 | Distribution Circuit | Equipment Failure/Involved | Other | 334 | 15396 | 37.9011 | -122.112 | Orchard S/of Ewart Dale- Lafayette | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0009344 | OH | Sus | 30976730 | No | 2013 | FEB | Yes | Line to Ground | 99301311 | CSO | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | LAKEWOOD-2107 | 13532107 | FUSE | 7701 | 20130212 | 4 | 741127 | 356 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 11392 | 37.9265 | -122.1083 | COR SHANGRI LA & SILVER DELL | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 13-0009429 | OH | Sus | 30976860 | No | 2013 | FEB | Yes | Line to Ground | 99301253 | CO | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | CLAYTON-2213 | 12022213 | FUSE | 15535 | 20130218 | 1114 | 743461 | 277 | Distribution Circuit | Equipment Failure/Involved | Other | 12 | 3324 | 37.9694 | -121.9228 | 10/S/O 15535 | Overcast-32 - 90 F | Conductor, Overhead | On Ground | 13-0010626 | OH | Sus | 30977919 | No | 2013 | FEB | Yes | Line to Ground | 99300448 | CO | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1102 | 14671102 | OCB | OCB | 20130301 | 244 | 748992 | 857 | Distribution Circuit | 3rd Party | Vehicle | 1796 | 110998 | 37.906 | -122.2082 | CORNER OF HAPPY VALLEY AND SOARES- 1/W OF RISER 7053 | Overcast-32 - 90 F | Pole-Wood | Broken, wire on object | 13-0013308 | OH | Sus | 30980275 | No | 2013 | MAR | Yes | Line to Ground | 99298625 | PW | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | MORAGA-1104 | 13801104 | FUSE | 25208 | 20130416 | 1108 | 776323 | 498 | Distribution Circuit | Equipment Failure/Involved | Other | 3 | 1494 | 37.8601 | -122.1537 | Perry-Richard: hall and fleetwood cutouts 25208 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0024898 | OH | Sus | 41884601 | yes | 2013 | APR | Yes | Line to Ground | 99290217 | CSO | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | FUSE | 18609 | 20130422 | 221 | 779131 | 925 | Distribution Circuit | Equipment Failure/Involved | Other | 31 | 13547 | 37.9653 | -122.1402 | 1020 VACA CREEK RD | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0026144 | OH | Sus | 30990980 | yes | 2013 | APR | Yes | Three Phase Fault | 99289254 | CSO | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | MORAGA-1101 | 13801101 | OTHER |  | 20130607 | 1610 | 805683 | 88 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 4181 | 37.8819 | -122.2099 | 1 span of 1 conductor down 7 poles N/W of 11190 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0037587 | OH | Sus | 41909276 | yes | 2013 | JUN | Yes | Line to Ground | 99281348 | CO | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | TASSAJARA-2112 | 14662112 | RECLOSER | D514R | 20130613 | 1238 | 809921 | 766 | Distribution Circuit | Vegetation | Tree - fell into line | 2103 | 35282 | 37.8227 | -121.9235 | UNNUMBERD RISER #####MAPPER C/OUT #11148###### | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0039414 | OH | Sus | 31002696 | No | 2013 | JUN | Yes | Line to Line | 99280002 | PW | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | CLAYTON-2212 | 12022212 | FUSE | 24991 | 20130614 | 1859 | 810642 | 560 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 14560 | 37.8677 | -121.8568 | Yaughn- Kip: 6311 morgan terr rd | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0039849 | OH | Sus | 31003054 | No | 2013 | JUN | Yes | Line to Ground | 99279793 | CO | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1102 | 14671102 | RECLOSER | L520R | 20130720 | 1806 | 835555 | 583 | Distribution Circuit | Vegetation | Tree - fell into line | 572 | 74322 | 37.9064 | -122.152 | 3915 Happy Valley Rd | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0048879 | OH | Sus | 40226967 | No | 2013 | JUL | Yes | Line to Ground | 99273230 | CO | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1101 | 14671101 | OTHER |  | 20130824 | 722 | 854891 | 912 | Distribution Circuit | Equipment Failure/Involved | Other | 1765 | 26670 | 37.9066 | -122.179 | RANCH RD & MINER RD | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0057193 | OH | Sus | 31016932 | No | 2013 | AUG | Yes | Line to Ground | 99267358 | PW | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | OTHER |  | 20130902 | 1757 | 859634 | 544 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 4 | 634 | 37.9651 | -122.1503 | 5433 ALHAMBRA VALLEY RD | Overcast-32 - 90 F | Conductor, Overhead | On Ground | 13-0059181 | OH | Sus | 41949756 | yes | 2013 | SEP | Yes | Line to Ground | 99266032 | CO | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | CLAYTON-2212 | 12022212 | FUSE | 19459 | 20131003 | 2048 | 877730 | 472 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 3304 | 37.8691 | -121.857 | 316093850131 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0067084 | OH | Sus | 31025995 | yes | 2013 | OCT | Yes | Line to Ground | 99260321 | CO | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | TASSAJARA-2112 | 14662112 | FUSE | 7884 | 20131003 | 2312 | 877856 | 731 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 10234 | 37.8356 | -121.9686 | meeker-jim: CALLE ARROYO | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0067157 | OH | Sus | 41967666 | yes | 2013 | OCT | Yes | Line to Ground | 99260287 | CO | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | SOBRANTE-1102 | 14671102 | FUSE | 1174 | 20140105 | 638 | 937367 | 342 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 2736 | 37.918 | -122.1608 | 315215652047 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0002227 | OH | Sus | 31046782 | No | 2014 | JAN | Yes | Line to Ground | 99245270 | CO | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | RESEARCH-2102 | 14692102 | FUSE | 1769 | 20140228 | 422 | 974329 | 639 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 10863 | 37.8231 | -122.0218 | 315600348523 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0014207 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Ground | 99237686 | CO | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | CLAYTON-2212 | 12022212 | FUSE | 2944 | 20140315 | 714 | 984881 | 211 | Distribution Circuit | Equipment Failure/Involved | Other | 138 | 23738 | 37.897 | -121.8594 | 316082751131 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0018296 | OH | Sus | 42093845 | No | 2014 | MAR | Yes | Line to Ground | 99234773 | CO | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | BRYANT-0402 | 13090402 | OTHER |  | 20140326 | 332 | 989787 | 494 | Distribution Circuit | Equipment Failure/Involved | Other | 262 | 25288 | 37.8634 | -122.1715 | 315179250069 | Rain-32 - 90 F | PGs, Kearneys | Broken, wire on ground | 14-0020502 | OH | Sus | 31065332 | yes | 2014 | MAR | Yes | Line to Ground | 99233200 | PGK | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | MORAGA-1103 | 13801103 | OCB | OCB | 20140401 | 1230 | 993439 | 880 | Distribution Circuit | Environmental/External | Lightning | 600 | 0 | 37.8489 | -122.1615 | 315291849451 | Lightning-32 - 90 F | Transformer | Broken, wire on ground | 14-0022175 | OH | Sus | 31066710 | yes | 2014 | APR | Yes |  | 99231304 | TX | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ROSSMOOR-1101 | 14161101 | SECTIONALIZER | L551S | 20140514 | 2023 | 1015796 | 481 | Distribution Circuit | Vegetation | Tree - fell into line | 259 | 83995 | 37.9086 | -122.1019 | 315362651833 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0031897 | OH | Sus | 42123544 | yes | 2014 | MAY | Yes | Multi-Fault | 99225648 | CO | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | MORAGA-1104 | 13801104 | FUSE | 15362 | 20140627 | 2203 | 1040913 | 427 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 9394 | 37.8535 | -122.146 | 315250749728 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0041152 | OH | Sus | 42146382 | No | 2014 | JUN | Yes | Line to Ground | 99219098 | CO | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1102 | 14671102 | FUSE | 1179 | 20140629 | 1247 | 1041452 | 504 | Distribution Circuit | Equipment Failure/Involved | Other | 58 | 29232 | 37.8963 | -122.1505 | 315242251258 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0041279 | OH | Sus | 31085755 | No | 2014 | JUN | Yes | Line to Ground | 99218941 | CO | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | CLAYTON-2212 | 12022212 | FUSE | 2944 | 20140711 | 2156 | 1048167 | 701 | Distribution Circuit | 3rd Party | Vehicle | 139 | 97439 | 37.897 | -121.8594 | 316089351087 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0044047 | OH | Sus | 31088313 | No | 2014 | JUL | Yes | Line to Line | 99217026 | PW | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | CLAYTON-2212 | 12022212 | FUSE | 12151 | 20140730 | 1458 | 1058135 | 557 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 10302 | 37.8629 | -121.8538 | 316134649324 | Clear-Above 90 F | Conductor, Overhead | Broken, wire on ground | 14-0048129 | OH | Sus | 31092171 | yes | 2014 | JUL | Yes | Line to Ground | 99214210 | CO | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | MORAGA-1101 | 13801101 | RECLOSER | N500R | 20140903 | 1321 | 1076754 | 35 | Distribution Circuit | Vegetation | Tree - fell into line | 364 | 12740 | 37.8837 | -122.1985 | 10/N/OF 8455- EAST OF WILDCAT CANYON | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0054845 | OH | Sus | 0 | No | 2014 | SEP | Yes | Line to Line | 99209367 | CO | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | RECLOSER | 95016 | 20141125 | 1356 | 1118134 | 844 | Distribution Circuit | 3rd Party | Vehicle | 728 | 161365 | 37.967 | -122.1247 | 315377453531 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0072043 | OH | Sus | 31117670 | No | 2014 | NOV | Yes | Multi-Fault | 99197835 | CO | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | LAKEWOOD-2107 | 13532107 | OTHER |  | 20150116 | 1856 | 1164947 | 1866 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5598 | 37.9291 | -122.1097 | 315359852448 | Overcast-32 - 90 F | Conductor, Overhead | On Ground | 15-0005297 | OH | Sus | 31128956 | No | 2015 | JAN | Yes | Line to Ground | 99187718 | CO | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | MORAGA-1104 | 13801104 | FUSE | 8489 | 20150209 | 1201 | 1186453 | 1149 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 42368 | 37.8643 | -122.1534 | 315211850045 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0012175 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182776 | PW | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ROSSMOOR-1106 | 14161106 | FUSE | 7770 | 20150610 | 1420 | 1248593 | 254 | Distribution Circuit | Vegetation | Tree - branch fell on line | 52 | 13208 | 37.8868 | -122.1279 | 315310350799 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0040136 | OH | Sus | 42404606 | yes | 2015 | JUN | Yes | Line to Ground | 99164349 | CO | OH | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | MORAGA-1104 | 13801104 | FUSE | 1191 | 20150704 | 955 | 1262833 | 254 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 14776 | 37.8867 | -122.1609 | Tahos & Oakridge | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0045476 | OH | Sus | 31166053 | No | 2015 | JUL | Yes | Line to Line | 1143835 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | MORAGA-1104 | 13801104 | FUSE | 8489 | 20150704 | 2237 | 1263038 | 836 | Distribution Circuit | Equipment Failure/Involved | Overhead | 121 | 69032 | 37.8643 | -122.1534 | 19 DONALD DR- ORINDA | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0045529 | OH | Sus | 42420842 | No | 2015 | JUL | Yes | Line to Ground | 1143879 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | FUSE | 18609 | 20150717 | 1203 | 1269590 | 347 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 1955 | 37.9653 | -122.1402 | OCHOA- ALFONSO: 1030 VACA CREEK RD- MARTINEZ | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0048200 | OH | Sus | 0 | No | 2015 | JUL | Yes | Force Out | 1145740 | PW | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | TASSAJARA-2104 | 14662104 | FUSE | 17689 | 20150724 | 1057 | 1276602 | 573 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 573 | 37.8225 | -121.8547 | 7/8/9/10th/p/e of 17689 | Clear-32-90 F | Conductor, Overhead | On Ground | 15-0050364 | OH | Sus | 31171433 | No | 2015 | JUL | Yes | Line to Ground | 1147446 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | MORAGA-1105 | 13801105 | FUSE | 17484 | 20150807 | 624 | 1284213 | 224 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 14784 | 37.8243 | -122.1324 | N/of SCADA 81939 (EBDO jurisdiction) | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0053461 | OH | Sus | 0 | yes | 2015 | AUG | Yes | Line to Ground | 1149541 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | RECLOSER | 82622 | 20150909 | 1602 | 1302505 | 686 | Distribution Circuit | Vegetation | Tree - fell into line | 402 | 221300 | 37.9665 | -122.1272 | 1 P/E/OF K122 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 15-0060238 | OH | Sus | 0 | yes | 2015 | SEP | Yes | Line to Ground | 1154399 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | MORAGA-1101 | 13801101 | FUSE | 18216 | 20150915 | 906 | 1306055 | 782 | Distribution Circuit | Vegetation | Tree - fell into line | 221 | 49830 | 37.8837 | -122.201 | IFO 180 EL TOYONAL | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0061433 | OH | Sus | 42472807 | yes | 2015 | SEP | Yes | Line to Ground | 1155261 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | TASSAJARA-2112 | 14662112 | FUSE | 7886 | 20151101 | 719 | 1332220 | 631 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 18579 | 37.8335 | -121.9606 | Yaughn- Kip: a/f 1918 calle arroyo | Overcast-32-90 F | Conductor, Overhead | On Ground | 15-0074513 | OH | Sus | 31196660 | No | 2015 | NOV | Yes | Line to Ground | 1165574 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | MORAGA-1101 | 13801101 | FUSE | 7117 | 20151222 | 1013 | 1369330 | 967 | Distribution Circuit | Vegetation | Tree - branch fell on line | 76 | 73492 | 37.8576 | -122.1722 | at FUCO-7117 & also 1P/of 7117 at tangent pole | Clear-32-90 F | Conductor, Overhead | On Ground | 15-0086769 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1176789 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | MORAGA-1105 | 13801105 | FUSE | 17484 | 20151223 | 724 | 1370125 | 1001 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 12076 | 37.8243 | -122.1324 | 13S/ of FUCO-7363 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086938 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Line | 1176993 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | FUSE | 628117 | 20160107 | 910 | 1379367 | 653 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4571 | 37.9782 | -122.1261 | 115 Jose Ln | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003738 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1179222 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1102 | 14671102 | FUSE | 1178 | 20160116 | 434 | 1384815 | 876 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 8760 | 37.8938 | -122.1514 | 1/E/OF 1178 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0005752 | OH | Sus | 0 | No | 2016 | JAN | Yes | Line to Ground | 1180722 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | CLAYTON-2212 | 12022212 | FUSE | 24991 | 20160120 | 35 | 1388252 | 705 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 13138 | 37.8677 | -121.8568 | POLE 110190090 & 110190091 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 16-0006701 | OH | Sus | 42613855 | No | 2016 | JAN | Yes | Line to Ground | 1181511 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ORINDA-0401 | 12350401 | SECTIONALIZER | N521S | 20160209 | 1416 | 1400859 | 65 | Distribution Circuit | Equipment Failure/Involved | Overhead | 325 | 15765 | 37.894 | -122.1882 | 2/N OF 3274 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on object | 16-0011559 | OH | Sus | 0 | No | 2016 | FEB | Yes | Force Out | 1185126 | CSO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | MORAGA-1101 | 13801101 | JUMPER | OJ HARDTAP AT 234 CRESANT DR PL#110454394 | 20160212 | 1102 | 1402502 | 388 | Distribution Circuit | 3rd Party | Vehicle | 2 | 776 | 37.8891 | -122.2072 | 234 CRESANT DR | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 16-0012386 | OH | Sus | 0 | No | 2016 | FEB | Yes | Line to Ground | 1185611 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | FUSE | 1655 | 20160302 | 1558 | 1414880 | 347 | Distribution Circuit | Vegetation | Tree - branch fell on line | 45 | 15615 | 37.9753 | -122.1268 | WANDA AND SEQUOIA | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0016836 | OH | Sus | 42644681 | No | 2016 | MAR | Yes | Line to Ground | 1188952 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | CLAYTON-2212 | 12022212 | OTHER | WIRE DOWN 6 S/OF 7764 | 20160306 | 202 | 1421180 | 760 | Distribution Circuit | Vegetation | Tree - branch fell on line | 226 | 171760 | 37.8912 | -121.8727 | 6 P/S/OF 7764 (3121 Morgan Terr Rd) | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018261 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190128 | CO | OH | No | Yes
DIABLO | FIELD OPS CENTRAL | Tier 2 | ROSSMOOR-1101 | 14161101 | FUSE | 7829 | 20160306 | 402 | 1421054 | 293 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 879 | 37.9122 | -122.1075 | Springhill rd. | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on object | 16-0018215 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190083 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1101 | 14671101 | FUSE | 7720 | 20160313 | 2132 | 1430660 | 865 | Distribution Circuit | Vegetation | Tree - fell into line | 103 | 63685 | 37.9031 | -122.171 | 50 DIABLO VIEW DR | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021070 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192436 | CO | OH | No | Yes
DIABLO | FIELD OPS CENTRAL | Tier 3 | ORINDA-0401 | 12350401 | FUSE | 5610 | 20160314 | 635 | 1430861 | 1320 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 65842 | 37.888 | -122.198 | 78 EL TOYONAL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021158 | OH | Sus | 42656169 | yes | 2016 | MAR | Yes | Line to Ground | 1192525 | CO | OH | No | Yes
DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | FUSE | 1655 | 20160402 | 1202 | 1443297 | 193 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 8685 | 37.9753 | -122.1267 | 1 P/E/OF 1655 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0025715 | OH | Sus | 42667866 | No | 2016 | APR | Yes | Line to Ground | 1195870 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | OAKLAND K SUB | 1210 | OCB | 1102/2 | 20160422 | 1412 | 1455949 | 487 | Distribution Circuit | 3rd Party | Vehicle | 24 | 2898 | 37.848 | -122.2286 | White- Al: FISH RANCH RD 6/P/S/O GRIZZLY PEAK | Drizzle-Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 16-0030717 | OH | Sus | 0 | yes | 2016 | APR | Yes | Line to Ground | 1199395 | PW | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | CLAYTON-2212 | 12022212 | FUSE | 15456 | 20160531 | 2004 | 1480197 | 1061 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1061 | 37.859 | -121.8915 | 5001 CURRY CANYON | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0040200 | OH | Sus | 42709441 | yes | 2016 | MAY | Yes | Line to Ground | 1206720 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | FUSE | 1711 | 20160602 | 2302 | 1481759 | 473 | Distribution Circuit | 3rd Party | Vehicle | 206 | 67076 | 37.965 | -122.1447 | 6E/of Alhambra Valley RD & Bear Creek Rd | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0040688 | OH | Sus | 42711475 | No | 2016 | JUN | Yes | Line to Line | 1207025 | PW | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ROSSMOOR-1101 | 14161101 | SECTIONALIZER | L551S | 20160609 | 940 | 1485823 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 258 | 90040 | 37.9086 | -122.1019 | SPRINGHILL DR AND GOYAK | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0042146 | OH | Sus | 31246477 | No | 2016 | JUN | Yes | Line to Ground | 1208178 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1103 | 14671103 | FUSE | 15023 | 20160729 | 844 | 1518328 | 551 | Distribution Circuit | 3rd Party | Vehicle | 48 | 15223 | 37.8958 | -122.2068 | 24 MONTA VISTA RD ORINDA | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0053552 | OH | Sus | 0 | No | 2016 | JUL | Yes | Line to Line | 1216397 | PW | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | RECLOSER | 95016 | 20160806 | 1953 | 1522617 | 1383 | Distribution Circuit | 3rd Party | Vehicle | 1001 | 144672 | 37.967 | -122.1249 | 13300 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0055535 | OH | Sus | 0 | No | 2016 | AUG | Yes | Line to Ground | 1217591 | PW | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ROSSMOOR-1101 | 14161101 | JUMPER | WIRE DOWN SPRINGHILL RD TWD L551S | 20160806 | 2117 | 1522652 | 508 | Distribution Circuit | Vegetation | Tree - fell into line | 260 | 131934 | 37.9083 | -122.1012 | SPRINGHILL RD. E/O SAN RELIEZ CT.- LAFAYETTE | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0055537 | OH | Sus | 31261821 | No | 2016 | AUG | Yes | Line to Ground | 1217594 | CO | OH | No | Yes
DIABLO | FIELD OPS CENTRAL | Tier 3 | MORAGA-1101 | 13801101 | RECLOSER | N500R | 20161016 | 1900 | 1563564 | 115 | Distribution Circuit | Vegetation | Tree - branch fell on line | 364 | 41860 | 37.8837 | -122.1987 | ON WILD CAT CANYON RD N/OF R6107 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072994 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Line | 1230023 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | CLAYTON-2212 | 12022212 | FUSE | 8068 | 20161026 | 1602 | 1570443 | 668 | Distribution Circuit | 3rd Party | Vehicle | 4 | 2672 | 37.8973 | -121.8599 | 1 POLE E OF 8068 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0075749 | OH | Sus | 0 | No | 2016 | OCT | Yes | Line to Line | 1232160 | PW | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | OTHER | WIRE DOWN FRANKLIN CANYON AND GOODFELLOW | 20161110 | 507 | 1579187 | 408 | Distribution Circuit | Equipment Failure/Involved | Overhead | 144 | 34227 | 37.9961 | -122.1498 | Franklin Canyon & Goodfellow | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on object | 16-0079109 | OH | Sus | 42878074 | No | 2016 | NOV | Yes | None | 1234673 | CSO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | MORAGA-1104 | 13801104 | FUSE | 8489 | 20161113 | 1327 | 1580508 | 863 | Distribution Circuit | Vegetation | Tree - fell into line | 121 | 67528 | 37.8642 | -122.1534 | 39 DONALD DR. ORINDA | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0079531 | OH | Sus | 31283706 | No | 2016 | NOV | Yes | Line to Line | 1235025 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | TASSAJARA-2104 | 14662104 | OTHER | WIRE DOWN S/OF 15769 | 20161116 | 1258 | 1582247 | 389 | Distribution Circuit | Equipment Failure/Involved | Overhead | 104 | 40030 | 37.7986 | -121.8622 | S/OF 15769 FUCO | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0080274 | OH | Sus | 42881519 | No | 2016 | NOV | Yes | Open Circuit | 1235595 | CSO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | MORAGA-1105 | 13801105 | OCB | 1105/2 | 20161119 | 302 | 1584614 | 754 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1894 | 232508 | 37.8486 | -122.1618 | School St & Country Club also School St & Moraga Way | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081036 | OH | Sus | 31284774 | yes | 2016 | NOV | Yes | Line to Ground | 1236063 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | LAS AROMAS-0401 | 13600401 | FUSE | 3637 | 20161224 | 409 | 1610113 | 362 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 4133 | 37.8973 | -122.1847 | 56 La Vuelta | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0086883 | OH | Sus | 42905475 | No | 2016 | DEC | Yes | Line to Ground | 1242069 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | ROSSMOOR-1108 | 14161108 | FUSE | 75857 | 20170205 | 1512 | 1675424 | 525 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 9450 | 37.8393 | -122.0896 | 1045 BOLLINGER CANYON | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017564 | OH | Sus | 42939170 | No | 2017 | FEB | Yes | Line to Ground | 1255530 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | CLAYTON-2212 | 12022212 | SWITCH | 7764 | 20170225 | 1650 | 1714039 | 390 | Distribution Circuit | Environmental/External | Water | 226 | 34804 | 37.893 | -121.8734 | 4 SPANS C/OF 7764 SBCO | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0026736 | OH | Sus | 42953898 | No | 2017 | FEB | Yes | Force Out | 1263427 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1102 | 14671102 | JUMPER | WIRE DOWN 3 N/OF 1144 | 20170305 | 1259 | 1720131 | 777 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 6197 | 37.9065 | -122.1435 | 3 N/OF 1144 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0028493 | OH | Sus | 42958919 | yes | 2017 | MAR | Yes | Line to Ground | 1264854 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | LAS AROMAS-0401 | 13600401 | FUSE | 3637 | 20170408 | 1459 | 1752732 | 736 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 4324 | 37.8973 | -122.1847 | 56 LA VUELTA | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038315 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Line | 1272370 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ORINDA-0401 | 12350401 | SWITCH | N521S | 20170808 | 829 | 1848315 | 1065 | Distribution Circuit | Vegetation | Tree - fell into line | 243 | 41532 | 37.894 | -122.1883 | 383 MINER RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0068698 | OH | Sus | 31341392 | No | 2017 | AUG | Yes | Line to Ground | 1294867 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | MORAGA-1101 | 13801101 | TRIP-SAVER | 18216 | 20170809 | 414 | 1848996 | 359 | Distribution Circuit | Equipment Failure/Involved | Overhead | 221 | 31319 | 37.8831 | -122.201 | 3 Camino Del Cielo | Overcast-Fog-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0068944 | OH | Sus | 31341569 | No | 2017 | AUG | Yes | Line to Ground | 1295053 | CAW | OH | No | Yes
DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1102 | 14671102 | FUSE | 17530 | 20171104 | 716 | 1915825 | 584 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 5546 | 37.91 | -122.1915 | 49 TARRY LN ORINDA | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0092610 | OH | Sus | 43207198 | No | 2017 | NOV | Yes | Line to Ground | 1312155 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | CLAYTON-2212 | 12022212 | RECLOSER | 96224 | 20171109 | 404 | 1919051 | 732 | Distribution Circuit | Vegetation | Tree - fell into line | 256 | 148564 | 37.9039 | -121.8741 | TUMBLE WEED & SHALE CLIFT | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | On Ground | 17-0093749 | OH | Sus | 43209218 | yes | 2017 | NOV | Yes | Line to Ground | 1313010 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | CLAYTON-2212 | 12022212 | FUSE | 12151 | 20180106 | 623 | 3057 | 384 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 5760 | 37.8629 | -121.8538 | 1 MILE S/OF 12151 FUCO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0003980 | OH | Sus | 43245625 | No | 2018 | JAN | Yes | None | 1323419 | CO | OH | No | Yes
DIABLO | FIELD OPS CENTRAL | Tier 2 | TASSAJARA-2109 | 14662109 | RECLOSER | 19042 | 20180108 | 723 | 3652 | 322 | Distribution Circuit | Equipment Failure/Involved | Overhead | 136 | 19819 | 37.7985 | -121.8732 | S/S CAMINO TASSAJARA E/OF FUCO 18231 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0004227 | OH | Sus | 31372711 | yes | 2018 | JAN | Yes | Line to Line | 1323608 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | MORAGA-1102 | 13801102 | OCB | 1102/2 | 20180313 | 1636 | 43531 | 17 | Distribution Circuit | 3rd Party | Vehicle | 513 | 8127 | 37.8486 | -122.1619 | 177 Moraga Way | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 18-0022413 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1335658 | PW | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1101 | 14101101 | FUSE | 2662 | 20180416 | 736 | 67639 | 488 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1338 | 37.9978 | -122.1577 | CUDD- MICHAEL: 2775 FRANKLIN CANYON RD martinez | Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0032514 | OH | Sus | 43326147 | yes | 2018 | APR | Yes | Line to Ground | 1343006 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1101 | 14101101 | FUSE | 1707 | 20180502 | 2016 | 78529 | 1205 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 9640 | 37.9652 | -122.1409 | Heagy-Lacy- Christopher: 5355 PINE TREE TRAIL- MARTINEZ | Clear-32-90 F | Pole-Wood | Broken, wire on object | 18-0037858 | OH | Sus | 31390810 | No | 2018 | MAY | Yes | Line to Line | 1346460 | PW | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | RECLOSER | 95016 | 20180513 | 2201 | 85429 | 945 | Distribution Circuit | 3rd Party | Vehicle | 728 | 93863 | 37.967 | -122.1249 | PEREZ-GABRIEL/925-250-8184: 2571 RELIEZ VALLEY RD. | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0040657 | OH | Sus | 0 | No | 2018 | MAY | Yes | Line to Line | 1348725 | PW | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | MORAGA-1101 | 13801101 | OCB | 1101/2 | 20180518 | 1059 | 89189 | 263 | Distribution Circuit | 3rd Party | Vehicle | 3 | 789 | 37.8486 | -122.1619 | 1/W/OF 33090 | Clear-32-90F | Conductor, Overhead | Broken, wire on object | 18-0042325 | OH | Sus | 43351179 | No | 2018 | MAY | Yes | Line to Ground | 1349924 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1102 | 14671102 | FUSE | 20741 | 20180527 | 1821 | 94890 | 502 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 14558 | 37.9104 | -122.1938 | 1/E OF 20741 FUCO | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0044760 | OH | Sus | 31393786 | No | 2018 | MAY | Yes | Line to Ground | 1351833 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | FUSE | 22779 | 20180613 | 1520 | 108506 | 360 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1800 | 37.9491 | -122.1868 | 2400 RANCHO DEL LARGO RD. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0050731 | OH | Sus | 43372770 | No | 2018 | JUN | Yes | Line to Ground | 1356433 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | LONE TREE-2105 | 13232105 | FUSE | 12555 | 20180616 | 1958 | 111080 | 702 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 3322 | 37.8961 | -121.7671 | 6125 BRIONES VALLEY RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0051687 | OH | Sus | 43375765 | yes | 2018 | JUN | Yes | Line to Ground | 1357132 | CO | OH | No | Yes
DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | FUSE | 12013 | 20180624 | 1944 | 117167 | 247 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1235 | 37.996 | -122.1495 | Goodfellow Dr. | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0054080 | OH | Sus | 31397493 | No | 2018 | JUN | Yes | Line to Ground | 1359102 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1102 | 14671102 | FUSE | 1155 | 20180731 | 1906 | 146253 | 455 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 20930 | 37.8923 | -122.1602 | PERRY-RICHAR 650-222-6719 2186: hidden valley and blackthorn | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0065553 | OH | Sus | 31401804 | No | 2018 | JUL | Yes | Line to Ground | 1368124 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | ROSSMOOR-1101 | 14161101 | FUSE | 7830 | 20180806 | 741 | 149627 | 403 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2015 | 37.9165 | -122.1193 | 3 SPANS W/OF 3830 FUCO | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0066984 | OH | Sus | 0 | No | 2018 | AUG | Yes | Line to Ground | 1369300 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1103 | 14671103 | OCB | 1103/2 | 20181003 | 902 | 186746 | 970 | Distribution Circuit | Animal | Squirrel | 146 | 19219 | 37.9054 | -122.208 | PERRY-RICHAR 650-222-6719 2186: wire down at manzanita dr and manzanita ter | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0085954 | OH | Sus | 43495888 | yes | 2018 | OCT | Yes | Line to Ground | 1382557 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | ROSSMOOR-1101 | 14161101 | FUSE | 7830 | 20181125 | 727 | 224016 | 233 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1165 | 37.9165 | -122.1193 | 4010 SPRINGHILL RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0103037 | OH | Sus | 0 | No | 2018 | NOV | Yes | Line to Ground | 1395009 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1102 | 14671102 | FUSE | 1181 | 20181126 | 1154 | 224873 | 939 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 8013 | 37.8976 | -122.1601 | 123 Camelia lane | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0103354 | OH | Sus | 43586281 | No | 2018 | NOV | Yes | Line to Line | 1395288 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | MORAGA-1101 | 13801101 | TRIP-SAVER | 18216 | 20181130 | 545 | 229832 | 355 | Distribution Circuit | Vegetation | Tree - fell into line | 226 | 80230 | 37.8836 | -122.2008 | 255 EL TOYONAL | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105455 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Line | 1396485 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | CLAYTON-2212 | 12022212 | FUSE | 2958 | 20190123 | 753 | 279467 | 465 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 465 | 37.8907 | -121.8716 | 1/LD SIDE OF 2958 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0013546 | OH | Sus | 31423059 | No | 2019 | JAN | Yes | Line to Ground | 1409602 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | FUSE | 5718 | 20190211 | 814 | 299597 | 534 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 20826 | 37.9979 | -122.1579 | 5/P/W OF 5718 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021007 | OH | Sus | 43676578 | yes | 2019 | FEB | Yes | Line to Ground | 1414689 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1103 | 14671103 | SWITCH | 18398SW | 20190220 | 730 | 319339 | 400 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 2982 | 37.8928 | -122.204 | LUBOVISKI- MILTON: 10 SOL BRAE WAY | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026327 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1419152 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | FUSE | 628117 | 20190311 | 633 | 335871 | 564 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4677 | 37.9781 | -122.1261 | LD SIDE OF 628117 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0032528 | OH | Sus | 43694135 | No | 2019 | MAR | Yes | Line to Ground | 1423192 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | MORAGA-1104 | 13801104 | FUSE | 2669 | 20190516 | 1157 | 382467 | 435 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 12180 | 37.8848 | -122.1571 | HS OF CGC 315230450825 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052827 | OH | Sus | 31441684 | yes | 2019 | MAY | Yes | Line to Ground | 1437321 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ROSSMOOR-1108 | 14161108 | FUSE | 17861 | 20190516 | 243 | 381875 | 542 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 7426 | 37.8804 | -122.126 | 3614 POWELL DRIVE | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052512 | OH | Sus | 31441482 | yes | 2019 | MAY | Yes | Line to Ground | 1437160 | CO | OH | No | Yes
DIABLO | FIELD OPS CENTRAL | Tier 3 | ROSSMOOR-1108 | 14161108 | FUSE | 8536 | 20190704 | 2200 | 441157 | 291 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 16005 | 37.8434 | -122.1049 | POLE#110447153 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0074668 | OH | Sus | 43867967 | No | 2019 | JUL | Yes | Line to Ground | 1454377 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1102 | 14671102 | FUSE | 1178 | 20190715 | 1543 | 452796 | 859 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 8590 | 37.8938 | -122.1513 | 1 LD SIDE OF 1178 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0077633 | OH | Sus | 31457475 | No | 2019 | JUL | Yes | Line to Ground | 1456381 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1102 | 14671102 | FUSE | 7728 | 20190722 | 1555 | 467755 | 288 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1440 | 37.9024 | -122.1508 | 18 Hilldale rd | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0079946 | OH | Sus | 31459354 | No | 2019 | JUL | Yes | Line to Ground | 1457942 | CAW | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | CLAYTON-2212 | 12022212 | TRIP-SAVER | 7758 | 20190915 | 101 | 583133 | 900 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 9036 | 37.8794 | -121.868 | 3 SPANS N/OF 15456 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0099201 | OH | Sus | 43956880 | No | 2019 | SEP | Yes | Line to Ground | 1470092 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | MORAGA-1101 | 13801101 | FUSE | 7117 | 20191203 | 413 | 728170 | 530 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1968 | 66768 | 37.8576 | -122.1722 | 179 Crest View | Partly Cloudy-Fog-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0132684 | OH | Sus | 44110962 | No | 2019 | DEC | Yes | Line to Line | 1497079 | CSO | OH | No | Yes
DIABLO | FIELD OPS CENTRAL | Tier 3 | MORAGA-1101 | 13801101 | OTHER | 1 PHASE DOWN | 20200522 | 2222 | 920100 | 1028 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 52368 | 37.8926 | -122.216 | 426 El Toyonal | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0053573 | OH | Sus | 44330854 | No | 2020 | MAY | Yes | Line to Ground | 1534221 | CO | OH | No | Yes
DIABLO | FIELD OPS CENTRAL | Tier 3 | ORINDA-0402 | 12350402 | RECLOSER | 402/2 LR | 20200808 | 246 | 984391 | 603 | Distribution Circuit | Vegetation | Tree - fell into line | 454 | 55594 | 37.8834 | -122.1937 | 40 Don Miguel | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0081201 | OH | Sus | 0 | No | 2020 | AUG | Yes | Line to Ground | 1552592 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | CLAYTON-2212 | 12022212 | FUSE | 24991 | 20200819 | 1344 | 1023293 | 338 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 6577 | 37.8678 | -121.8569 | POLE#110190077 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0087548 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Ground | 1557219 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | MORAGA-1104 | 13801104 | OCB | 1104/2 | 20201118 | 504 | 1148143 | 317 | Distribution Circuit | Equipment Failure/Involved | Overhead | 536 | 61711 | 37.8486 | -122.1619 | WENDLING/2163 925-326-8952: knox dr and hidden valley rd lafayette | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0122226 | OH | Sus | 31518854 | No | 2020 | NOV | Yes | Line to Ground | 1580851 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | CLAYTON-2212 | 12022212 | FUSE | 24991 | 20210330 | 2351 | 1303923 | 675 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 12039 | 37.8679 | -121.857 | 7070 MORGAN TERRITORY RD | Strong Winds- | Conductor, Overhead | Broken, wire on ground | 21-0043026 | OH | Sus | 31534913 | No | 2021 | MAR | Yes | Line to Ground | 1616372 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | RESEARCH-2102 | 14692102 | FUSE | 1769 | 20210412 | 1143 | 1313604 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 9766 | 37.8231 | -122.0217 | 2.5 SPANS LOAD SIDE OF 1769 | Strong Winds- | Conductor, Overhead | Broken, wire on ground | 21-0047580 | OH | Sus | 31535752 | No | 2021 | APR | Yes | Line to Ground | 1619517 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ROSSMOOR-1106 | 14161106 | FUSE | 7770 | 20210609 | 1021 | 1369320 | 204 | Distribution Circuit | 3rd Party | Vehicle | 51 | 5668 | 37.8868 | -122.1278 | 819 MOUNTAN VIEW DRIVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0072019 | OH | Sus | 31542965 | No | 2021 | JUN | Yes | Line to Ground | 1635906 | CO | OH | No | Yes
DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1102 | 14671102 | OCB | 1102/2 | 20210630 | 1028 | 1388827 | 128 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 1824 | 119948 | 37.9054 | -122.208 | C/O CRANE CT & VAN TASSEL LN | Clear-32-90 F | Insulator | Broken, wire on ground | 21-0082252 | OH | Sus | 0 | No | 2021 | JUN | Yes | Line to Ground | 1643593 | INS | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | FUSE | 16283 | 20210828 | 534 | 1456105 | 698 | Distribution Circuit | 3rd Party | Vehicle | 68 | 41983 | 37.9964 | -122.1503 | CORNER OF FRANKLIN CANYON RD & WOOLCUT LANE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0110503 | OH | Sus | 0 | No | 2021 | AUG | Yes | Three Phase Fault | 1661663 | PW | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | FUSE | 12617 | 20210923 | 2307 | 1479167 | 892 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5352 | 37.97 | -122.1602 | 2 SPANS E/O 15957 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0121810 | OH | Sus | 31552632 | No | 2021 | SEP | Yes | Line to Ground | 1668284 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ROSSMOOR-1101 | 14161101 | FUSE | 7937 | 20211223 | 1114 | 1579892 | 353 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 2978 | 37.8927 | -122.143 | GREEN- JAKE 510-619-5160: same | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160283 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1697724 | CO | OH | No | Yes
DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1102 | 14671102 | FUSE | 1155 | 20220312 | 1903 | 1647482 | 706 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 34320 | 37.8924 | -122.1603 | 4179 HIDDEN VALLEY RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0033260 | OH | Sus | 0 | No | 2022 | MAR | Yes | Three Phase Fault | 1716708 | PW | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | LAS AROMAS-0401 | 13600401 | RECLOSER | LA401R | 20220508 | 804 | 1691062 | 447 | Distribution Circuit | Equipment Failure/Involved | Overhead | 429 | 104559 | 37.8941 | -122.1785 | 145 LAS AROMAS | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0059411 | OH | Sus | 31602925 | No | 2022 | MAY | Yes | Line to Ground | 1734525 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | FUSE | 1655 | 20220519 | 239 | 1702608 | 792 | Distribution Circuit | Equipment Failure/Involved | Overhead | 47 | 37224 | 37.9752 | -122.127 | 2 POLES E/O 1655 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0063757 | OH | Sus | 0 | No | 2022 | MAY | Yes | Line to Line | 1737487 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | MORAGA-1102 | 13801102 | OCB | 1102/2 | 20220527 | 1420 | 1712644 | 404 | Distribution Circuit | 3rd Party | Vehicle | 3091 | 106008 | 37.8486 | -122.1619 | LINE & BUCK AT CREST & MIDDLE | Clear-32-90 F | Anchor or Guy | Broken, wire on ground | 22-0067612 | OH | Sus | 31604674 | No | 2022 | MAY | Yes | Line to Line | 1739992 | ANC | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ROSSMOOR-1101 | 14161101 | FUSE | 7823 | 20220624 | 2208 | 1741647 | 1040 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5200 | 37.9095 | -122.1033 | 1 SPAN LD SIDE OF CGC 315377151742 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0078413 | OH | Sus | 0 | No | 2022 | JUN | Yes | Line to Ground | 1747716 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | CLAYTON-2212 | 12022212 | RECLOSER | 204416 | 20220712 | 712 | 1754105 | 576 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 34816 | 37.8797 | -121.8678 | 2/SE OF FUCO 12151 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0084205 | OH | Sus | 0 | No | 2022 | JUL | Yes | Line to Ground | 1751349 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | ORINDA-0401 | 12350401 | RECLOSER | 401/2 LR | 20220724 | 2221 | 1764646 | 322 | Distribution Circuit | Vegetation | Tree - branch fell on line | 292 | 53524 | 37.8835 | -122.1938 | 1/W OF 5654 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0089220 | OH | Sus | 45387550 | No | 2022 | JUL | Yes | Line to Ground | 1754742 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | TASSAJARA-2104 | 14662104 | RECLOSER | 19042 | 20220903 | 441 | 1798077 | 774 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 27174 | 37.7985 | -121.8732 | 7 SPANS LD SIDE OF 13315 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0105425 | OH | Sus | 0 | No | 2022 | SEP | Yes | Line to Ground | 1765396 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | MORAGA-1105 | 13801105 | OCB | 1105/2 | 20221126 | 1936 | 1869576 | 416 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1887 | 42912 | 37.8486 | -122.1618 | CGC # 315293049000 | Clear-32-90F | Transformer (OH) | Broken, wire on ground | 22-0134232 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Line | 1785569 | TXO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ROSSMOOR-1101 | 14161101 | OTHER | WIRE ON GROUND @ 1 SPRINGHILL LN | 20221128 | 1247 | 1870453 | 396 | Distribution Circuit | Vegetation | Tree - branch fell on line | 259 | 9224 | 37.9138 | -122.1146 | 1 SPRING HILL LN | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0134499 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Ground | 1785870 | CO | OH | No | Yes
DIABLO | FIELD OPS CENTRAL | Tier 2 | MORAGA-1103 | 13801103 | JUMPER | FUCO 802141 OPEN | 20230113 | 1243 | 1952011 | 388 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 13688 | 37.8459 | -122.1548 | 1/P/W OF 802141 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015373 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1804287 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | CLAYTON-2212 | 12022212 | FUSE | 7619 | 20230115 | 1121 | 1955859 | 377 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2639 | 37.8885 | -121.8693 | 3 POLES SOUTH OF 7619 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016660 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1805396 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 3 | MORAGA-1105 | 13801105 | FUSE | 17484 | 20230205 | 508 | 1977213 | 817 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 45152 | 37.8243 | -122.1325 | 410 REDWOOD HWY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0025370 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1810666 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | SOBRANTE-1101 | 14671101 | OCB | 1101/2 | 20230324 | 723 | 2065637 | 486 | Distribution Circuit | Animal | Bird found | 362 | 30280 | 37.9054 | -122.208 | MINER RD (FUCO 9961) | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0051695 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1829832 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | CLAYTON-2212 | 12022212 | FUSE | 16798 | 20230325 | 1638 | 2067183 | 94 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 1222 | 37.8862 | -121.7755 | 8 SPANS N/OF 16798 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 23-0052527 | OH | Sus | 0 | No | 2023 | MAR | Yes | Force Out | 1830478 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | OTHER | WIRE DOWN 2 SP LD SIDE OF 5718 | 20230521 | 540 | 2117899 | 734 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 28626 | 37.9984 | -122.161 | 2 SPANS LD SIDE OF FUCO 5718 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0073950 | OH | Sus | 0 | No | 2023 | MAY | Yes | Open Circuit | 1844774 | CO | OH | No | Yes
DIABLO | FIELD OPS CENTRAL | Tier 2 | CLAYTON-2212 | 12022212 | FUSE | 9748 | 20230616 | 146 | 2138125 | 624 | Distribution Circuit | 3rd Party | Vehicle | 557 | 16138 | 37.9245 | -121.9125 | 2 P/E/O 42067 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0082993 | OH | Sus | 35458390 | No | 2023 | JUN | Yes | Line to Ground | 1850964 | PW | OH | No | Yes
DIABLO | FIELD OPS CENTRAL | Tier 3 | MORAGA-1105 | 13801105 | JUMPER | OJ @ LINE AND BUCK | 20230825 | 329 | 2202159 | 869 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 869 | 37.8335 | -122.1668 | 720 RIDGE CREST RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0109109 | OH | Sus | 45941074 | No | 2023 | AUG | Yes | Force Out | 1869023 | CO | OH | No | No
DIABLO | FIELD OPS CENTRAL | Tier 2 | ALHAMBRA-1105 | 14101105 | RECLOSER | 82622 | 20230924 | 225 | 2225740 | 436 | Distribution Circuit | Vegetation | Tree - fell into line | 410 | 104609 | 37.9665 | -122.1271 | 5675 ALHAMBRA VALLEY RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0120124 | OH | Sus | 0 | No | 2023 | SEP | Yes | Line to Ground | 1876277 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1104 | 12101104 | RECLOSER | CR204 | 20130101 | 936 | 724026 | 1184 | Distribution Circuit | Vegetation | Tree - fell into line | 366 | 123983 | 37.8317 | -122.1951 | GUNN AND SHEPHERD CANYON RD | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0001532 | OH | Sus | 30968703 | No | 2013 | JAN | Yes | Line to Ground | 99306037 | CO | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1102 | 12101102 | FUSE | 1377 | 20130221 | 859 | 745691 | 217 | Distribution Circuit | 3rd Party | Vehicle | 9 | 1953 | 37.8436 | -122.2017 | PAVANA 133/ 3335 385-8922: sw 1377 | Partly cloudy-32 - 90 F | Insulator | Broken, wire on object | 13-0011527 | OH | Sus | 41857208 | No | 2013 | FEB | Yes | Line to Ground | 99299879 | INS | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | FRANKLIN-1104 | 13921104 | RECLOSER | P136 | 20130305 | 2247 | 752066 | 1133 | Distribution Circuit | Equipment Failure/Involved | Other | 83 | 28579 | 38.0356 | -122.2583 | WIRE DOWN IN CANYON ( at TAP LINE THRU FIRE GATE 20) | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0014394 | OH | Sus | 41862231 | yes | 2013 | MAR | Yes |  | 99297889 | CO | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1104 | 12101104 | RECLOSER | CR206 | 20130306 | 2242 | 753080 | 93 | Distribution Circuit | Vegetation | Tree - fell into line | 546 | 50778 | 37.8316 | -122.1969 | PASO ROBLE 1/N/O SHEPHERD CANYON RD | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0014812 | OH | Sus | 30981417 | yes | 2013 | MAR | Yes |  | 99297685 | CO | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | SAN LEANDRO-1109 | 13111109 | RECLOSER | CR182 | 20130330 | 2114 | 763949 | 856 | Distribution Circuit | 3rd Party | Vehicle | 417 | 70416 | 37.7521 | -122.1265 | BET CR-182 TWDS 1417 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0020212 | OH | Sus | 30986505 | No | 2013 | MAR | Yes |  | 99293842 | CO | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | SAN LEANDRO-1109 | 13111109 | OTHER |  | 20130330 | 2114 | ODB-9929 | 420 | Distribution Circuit | Equipment Failure/Involved | Other | 289 | 114727 | 37.7511 | -122.1333 | MALCOLM AND SNOWDEN OPEN | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0020212 | OH | Sus | 30986505 | No | 2013 | MAR | Yes |  | 99293835 | CO | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | EL CERRITO G-1105 | 12501105 | OTHER |  | 20130528 | 2301 | 800027 | 564 | Distribution Circuit | Equipment Failure/Involved | Other | 71 | 40044 | 37.8874 | -122.2492 | P/P 255' N/E/O SUMMIT RE OPP ATLAS PL ON GOLF COURSE RD | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0035007 | OH | Sus | 30999208 | No | 2013 | MAY | Yes |  | 99282899 | CO | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | EL CERRITO G-1112 | 12501112 | FUSE | R8714 | 20130618 | 1330 | 812625 | 74 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 3404 | 37.9514 | -122.3216 | EOL PAST R8714 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0040649 | OH | Sus | 0 | No | 2013 | JUN | Yes | Line to Ground | 99279214 | CO | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | SAN LEANDRO-1109 | 13111109 | FUSE | 9166 | 20130910 | 1514 | 864057 | 711 | Distribution Circuit | Vegetation | Tree - bark fell into line | 19 | 6249 | 37.7515 | -122.1277 | MONAN AND ZEIGLER | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0061101 | OH | Sus | 31020484 | No | 2013 | SEP | Yes | Line to Line | 99264638 | PW | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1102 | 12101102 | FUSE | 1725 | 20131003 | 2348 | 877912 | 1093 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 45972 | 37.8387 | -122.2015 | STEPHENS-K 8277/ 2168 750-5433: 7001 snake rd. | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0067143 | OH | Sus | 31026007 | yes | 2013 | OCT | Yes | Line to Ground | 99260291 | PW | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND K-1103 | 12101103 | RECLOSER | CR188 | 20131003 | 2319 | 877867 | 55 | Distribution Circuit | Vegetation | Tree - branch fell on line | 675 | 37125 | 37.8332 | -122.2139 | CR27 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0067105 | OH | Sus | 31025999 | yes | 2013 | OCT | Yes | Line to Ground | 99260390 | CO | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND K-1103 | 12101103 | OTHER |  | 20131003 | 2322 | 877958 | 708 | Distribution Circuit | Equipment Failure/Involved | Other | 853 | 92644 | 37.8363 | -122.2187 | Webster J. 131 / 2173: 211 DUNCAN WY | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0067116 | OH | Sus | 0 | yes | 2013 | OCT | Yes | Line to Line | 99260307 | CO | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | RECLOSER | CR020 | 20131003 | 2313 | 877971 | 1043 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 37420 | 37.8001 | -122.1705 | REDWOOD RD 7/N/OF SKYLINE BLVD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0067131 | OH | Sus | 41967661 | yes | 2013 | OCT | Yes | Line to Ground | 99260298 | CO | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | EL CERRITO G-1105 | 12501105 | FUSE | R9871 | 20140208 | 2208 | 963628 | 916 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 44884 | 37.8868 | -122.2489 | Miles 7793: 1396 SUMMIT RD BRELELEY | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0010053 | OH | Sus | 42073723 | yes | 2014 | FEB | Yes | Line to Line | 99240556 | CO | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1104 | 12101104 | OTHER |  | 20140311 | 1821 | 982675 | 670 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 7370 | 37.8317 | -122.2004 | IFO 5948 BALBOA | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0017374 | OH | Sus | 31062483 | yes | 2014 | MAR | Yes | Line to Ground | 99235367 | CO | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | FUSE | 6641 | 20140325 | 1816 | 989688 | 524 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 5764 | 37.7907 | -122.1521 | LEVINE 1859: COLBOURN N SKYLINE | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0020474 | OH | Sus | 31065324 | No | 2014 | MAR | Yes | Line to Ground | 99233247 | CO | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1102 | 12101102 | OTHER |  | 20140414 | 540 | 999122 | 119 | Distribution Circuit | 3rd Party | Vehicle | 1300 | 132860 | 37.8427 | -122.2038 | TWD 8470- THORNHILL & SOBRANTE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0024819 | OH | Sus | 31069243 | No | 2014 | APR | Yes | Line to Ground | 99230301 | CO | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | SWITCH | 9524 | 20140519 | 107 | 1020487 | 1059 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 14490 | 37.7969 | -122.1645 | 5458 FERNHOFF RD | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0032727 | OH | Sus | 31077040 | yes | 2014 | MAY | Yes | None | 99225011 | PW | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1103 | 12101103 | OTHER |  | 20140603 | 2325 | 1028195 | 511 | Distribution Circuit | Equipment Failure/Involved | Other | 462 | 158996 | 37.8386 | -122.2136 | STEPHENS-K 8277/ 2168 750-5433: 1)WIRE DOWN IFO 6000 VALLEY VIEW & 2) OPEN JUMPER AT INTERSECTION OF | Partly cloudy-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0035998 | OH | Sus | 42133433 | No | 2014 | JUN | Yes | Line to Ground | 99222756 | CSO | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND D-1112 | 12041112 | FUSE | 6599 | 20140714 | 1946 | 1049384 | 500 | Distribution Circuit | Vegetation | Tree - branch fell on line | 81 | 40500 | 37.8606 | -122.242 | PAVANA 3335 385-8922: 7501 claremont | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0044442 | OH | Sus | 42154134 | yes | 2014 | JUL | Yes | None | 99216729 | CO | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | RECLOSER | CR008 | 20140825 | 2032 | 1072924 | 516 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1302 | 95077 | 37.8092 | -122.1906 | CR020- Redwood Rd 4/N/of Skyline Blvd | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0053174 | OH | Sus | 42176595 | No | 2014 | AUG | Yes | Line to Ground | 99210480 | CO | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1104 | 12541104 | OTHER |  | 20140925 | 1249 | 1087981 | 281 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 677 | 55323 | 37.8231 | -122.1999 | CHELTON AND BAGSHOTTE TWD C/OUTS 10404 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0059386 | OH | Sus | 31103157 | yes | 2014 | SEP | Yes | None | 99206176 | CO | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1106 | 12541106 | FUSE | 9403 | 20141025 | 1123 | 1102187 | 209 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 9 | 1881 | 37.8054 | -122.1705 | 24 POLES E/O 9403 | Partly cloudy-32 - 90 F | Insulator | Broken, wire on object | 14-0066004 | OH | Sus | 0 | yes | 2014 | OCT | Yes | Line to Ground | 99202084 | INS | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | RECLOSER | CR020 | 20141108 | 1403 | 1110634 | 525 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 18903 | 37.8001 | -122.1705 | 4P N/E OF CR020 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0069111 | OH | Sus | 31113899 | No | 2014 | NOV | Yes | Line to Ground | 99199906 | CO | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | NORTH TOWER-2201 | 42042201 | RECLOSER | P300 | 20141119 | 1144 | 1115176 | 420 | Distribution Circuit | Equipment Failure/Involved | Other | 1675 | 607640 | 38.0481 | -122.2059 | 424 DUPERU | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0070866 | OH | Sus | 31116365 | No | 2014 | NOV | Yes | Line to Line | 99198702 | PW | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1104 | 12541104 | FUSE | 9198 | 20141204 | 318 | 1124146 | 812 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 20231 | 37.8336 | -122.1878 | 7050 EXETER S/OF EVERGREEN- OAKLAND | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073690 | OH | Sus | 31119245 | yes | 2014 | DEC | Yes | Line to Ground | 99196534 | CO | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | RECLOSER | CR006 | 20141215 | 1223 | 1141296 | 1339 | Distribution Circuit | Equipment Failure/Involved | Other | 573 | 82329 | 37.7952 | -122.1579 | CATHY LN AND SKYLINE BLVD- OAKLAND | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0077022 | OH | Sus | 31121186 | yes | 2014 | DEC | Yes | Line to Ground | 99192861 | PW | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | SAN LEANDRO-1109 | 13111109 | OTHER |  | 20141220 | 315 | 1144858 | 685 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 20550 | 37.7517 | -122.1187 | N/OF 11195 SUN VALLEY DR | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077783 | OH | Sus | 42301468 | No | 2014 | DEC | Yes | None | 99192126 | CO | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | RECLOSER | CR006 | 20150113 | 200 | 1163000 | 653 | Distribution Circuit | Vegetation | Tree - branch fell on line | 573 | 60629 | 37.7952 | -122.1579 | W/OF CATHY LN ON SKYLINE BLVD- OAKLAND | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0004117 | OH | Sus | 31127857 | No | 2015 | JAN | Yes | Line to Line | 99188306 | CO | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | EL CERRITO G-1105 | 12501105 | OTHER |  | 20150521 | 253 | 1237763 | 527 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 12 | 6324 | 37.9167 | -122.2808 | LAWSON S/O COWPER | Fog-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 15-0035589 | OH | Sus | 31156322 | No | 2015 | MAY | Yes | Line to Ground | 99167582 | CAW | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1102 | 12101102 | OTHER |  | 20150620 | 1838 | 1253924 | 617 | Distribution Circuit | Equipment Failure/Involved | Overhead | 781 | 258698 | 37.8402 | -122.2036 | WIRE DOWN ON THORNHILL N/O OAKWOOD- AND OPEN JUMPERON THORNHILL W/O OAKWOOD | Partly cloudy-32 - 90 F | Jumper | Broken, wire on ground | 15-0042325 | OH | Sus | 31162570 | No | 2015 | JUN | Yes |  | 99162711 | JMP | OH | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | FUSE | 6935 | 20150830 | 1850 | 1297383 | 1061 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 25464 | 37.8055 | -122.1849 | Trinidad Ave S/of Brunell Dr | Clear-32-90 F | Conductor, Overhead | On Ground | 15-0058279 | OH | Sus | 0 | No | 2015 | AUG | Yes | Line to Ground | 1152990 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | EL CERRITO G-1105 | 12501105 | FUSE | R8781 | 20150927 | 1108 | 1312740 | 902 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 10824 | 37.8875 | -122.2486 | 3/S/OF R8784 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0065943 | OH | Sus | 0 | No | 2015 | SEP | Yes | Three Phase Fault | 1159197 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | FRANKLIN-1104 | 13921104 | RECLOSER | P136 | 20151010 | 915 | 1319809 | 1103 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 82 | 17925 | 38.0356 | -122.2583 | 4/E/OF R9139 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 15-0069396 | OH | Sus | 0 | No | 2015 | OCT | Yes | Line to Ground | 1161643 | PW | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND K-1102 | 12101102 | OCB | OCB | 20151110 | 1226 | 1339014 | 51 | Distribution Circuit | Animal | Squirrel | 2506 | 73164 | 37.848 | -122.2292 | GRIZZLY PEAK E/OF 8663 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0077042 | OH | Sus | 42566626 | No | 2015 | NOV | Yes | Line to Ground | 1167641 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1106 | 12541106 | FUSE | 9403 | 20151221 | 1930 | 1368228 | 500 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4500 | 37.8055 | -122.1705 | 1 SPAN N/OF Redwood Rd. 2600' N/O Skyline at Mile Marker- 42 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086505 | OH | Sus | 42595872 | yes | 2015 | DEC | Yes | Line to Ground | 1176499 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | EL CERRITO G-1105 | 12501105 | FUSE | R8781 | 20151222 | 1902 | 1369958 | 1144 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 13728 | 37.8875 | -122.2486 | CARTER-DAVID: 10 golf course dr cut outs R8783 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0086898 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1176927 | PW | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE | 9833 | 20160107 | 602 | 1379275 | 540 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 8288 | 37.8337 | -122.1933 | STEPHENS-KEVIN: 7250 woodrow dr | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003698 | OH | Sus | 42602584 | yes | 2016 | JAN | Yes | Line to Line | 1179188 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | FLORENCE-0401 | 12690401 | OCB | 401/2 | 20160117 | 1814 | 1385672 | 1372 | Distribution Circuit | Vegetation | Tree - fell into line | 487 | 117204 | 37.8359 | -122.2201 | 5637 MASONIC | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0005939 | OH | Sus | 31213412 | yes | 2016 | JAN | Yes | Line to Line | 1180908 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1106 | 12541106 | FUSE | 9403 | 20160117 | 1530 | 1385541 | 510 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4590 | 37.8055 | -122.1705 | GIOCOMO- BRETT 427-8096: 6430 REDWOOD RD | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0005915 | OH | Sus | 42612967 | yes | 2016 | JAN | Yes | Line to Ground | 1180887 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1102 | 12101102 | FUSE | 8248 | 20160119 | 1128 | 1387346 | 265 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 3445 | 37.8472 | -122.2127 | IFO 6544 PINENEEDLE DR. OAK. | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006391 | OH | Sus | 31213660 | yes | 2016 | JAN | Yes | Line to Ground | 1181280 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1104 | 12541104 | JUMPER | JUMPERS 4 P N/O SW 2390 | 20160119 | 713 | s1181238 | 1652 | Distribution Circuit | Vegetation | Tree - fell into line | 191 | 53969 | 37.8325 | -122.1858 | SKYLINE & EVERGREEN | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006185 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1181238 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1102 | 12101102 | FUSE | 8252 | 20160122 | 1807 | 1390296 | 539 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 15092 | 37.8496 | -122.2125 | TWAROWSKI- CHRIS: 6920 balsam | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007561 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1182043 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE | 9248 | 20160122 | 2248 | 1390420 | 407 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 8954 | 37.8343 | -122.1911 | GUNN DRIVE 2/S/O SHEPHERD | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007664 | OH | Sus | 31214418 | yes | 2016 | JAN | Yes | Line to Line | 1182153 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1102 | 12101102 | FUSE | 8248 | 20160128 | 1130 | 1393501 | 240 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 13 | 3120 | 37.8472 | -122.2127 | 6544 PINE NEEDLE DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0008912 | OH | Sus | 42619328 | No | 2016 | JAN | Yes | Line to Ground | 1183135 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1104 | 12541104 | FUSE | 1259 | 20160218 | 537 | 1407819 | 1305 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 40347 | 37.8258 | -122.1937 | 2739 CHELSEA DRIVE | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013611 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Three Phase Fault | 1186691 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1104 | 12101104 | RECLOSER | CR206 | 20160311 | 1445 | 1428098 | 1232 | Distribution Circuit | Vegetation | Tree - fell into line | 639 | 260047 | 37.8317 | -122.197 | CR206 LOAD AND SOURCE SIDE- SSD 9256- PAST 6125- LD SIDE OF 9541- SSD 9559 AND SSD 9256 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020514 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1191898 | CO | OH | No | Yes
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | FUSE | 6627 | 20160311 | 1931 | 1428741 | 2826 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 182156 | 37.8042 | -122.1818 | HAMILL- MIKE: 3520 Brunell Dr- BRUNELL W/O TRINIDAD | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020657 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Multi-Fault | 1192028 | CO | OH | No | Yes
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1103 | 12101103 | JUMPER | WIRE DOWN IFO 6060 THORNHILL | 20160313 | 1000 | 1430065 | 890 | Distribution Circuit | Vegetation | Tree - fell into line | 675 | 182226 | 37.8381 | -122.2108 | IFO 6060 THORNHILL | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020908 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Open Circuit | 1192291 | CO | OH | No | Yes
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | RECLOSER | CR020 | 20160313 | 634 | 1429932 | 1121 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 28742 | 37.8001 | -122.1706 | 3 PHASE SPAN BET LR CR266 & 9043 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020878 | OH | Sus | 31224747 | yes | 2016 | MAR | Yes | Three Phase Fault | 1192268 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | EDES-1112 | 13681112 | OTHER | WIRE DOWN AT MALCOLM AND ELVESSA | 20160429 | 812 | 1461406 | 177 | Distribution Circuit | Equipment Failure/Involved | Overhead | 294 | 51338 | 37.7525 | -122.1297 | ELVISA AND MALCOLM | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0032528 | OH | Sus | 31235251 | yes | 2016 | APR | Yes | Line to Ground | 1200890 | CO | OH | No | Yes
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND K-1103 | 12101103 | OTHER | WIRE DOWN 1 SPAN LOAD SIDE OF 6533 | 20160511 | 1707 | 1468260 | 1152 | Distribution Circuit | Vegetation | Tree - fell into line | 142 | 163584 | 37.8375 | -122.2124 | 1 span ld side 6533 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0035432 | OH | Sus | 0 | No | 2016 | MAY | Yes | Line to Ground | 1203061 | CO | OH | No | Yes
EAST BAY | FIELD OPS CENTRAL | Tier 2 | SAN LEANDRO-1109 | 13111109 | FUSE | 9166 | 20160602 | 1104 | 1481374 | 361 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 6859 | 37.7515 | -122.1277 | 10940 MONAN ST | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0040532 | OH | Sus | 42710867 | No | 2016 | JUN | Yes | Line to Ground | 1206934 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | EL CERRITO G-1112 | 12501112 | FUSE | R8714 | 20160622 | 2156 | 1494358 | 443 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 20378 | 37.9515 | -122.3216 | 6138 PARK AVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0045180 | OH | Sus | 42729942 | No | 2016 | JUN | Yes | Line to Ground | 1210447 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | SPRUCE-0402 | 13340402 | FUSE | R3383 | 20160630 | 852 | 1498765 | 983 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 20643 | 37.9025 | -122.2642 | 641 VISTAMONT AVE BERKELEY | Overcast-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 16-0046815 | OH | Sus | 0 | No | 2016 | JUN | Yes | Line to Ground | 1211611 | PW | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | EL CERRITO G-1105 | 12501105 | SECTIONALIZER | R7302 | 20160718 | 431 | 1511639 | 1084 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4639 | 37.8888 | -122.248 | 1. 1ST TAP PASS R8833 2. HS OF R9129 | Overcast-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0050553 | OH | Sus | 31257863 | No | 2016 | JUL | Yes | Line to Ground | 1214371 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1106 | 12541106 | FUSE | 6579 | 20160719 | 1705 | 1512696 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2300 | 37.7984 | -122.152 | 7867 Redwood Rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0051021 | OH | Sus | 42744471 | No | 2016 | JUL | Yes | Line to Ground | 1214667 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | WALDO-0402 | 13350402 | OTHER | WIRE DOWN TERRACE AND COLUSA SSD OF C114 | 20160722 | 515 | 1514031 | 464 | Distribution Circuit | 3rd Party | Vehicle | 460 | 85108 | 37.9119 | -122.2963 | TERRACE DR & COLUSA (E/OF C114 CAP BANK) | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0051740 | OH | Sus | 0 | No | 2016 | JUL | Yes | Line to Ground | 1215065 | CO | OH | No | Yes
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE | 6739 | 20160831 | 718 | 1534673 | 1602 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 48456 | 37.8177 | -122.1987 | VILLALOBOS- CARLOS: 2106 MASTLANDS DR. OAKLAND | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0061228 | OH | Sus | 0 | No | 2016 | AUG | Yes | Line to Ground | 1221550 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND J-1105 | 12091105 | OTHER | WIRE DOWN @ MOUNTAIN BLVD AND MOOUNTAIN VIEW | 20160901 | 110 | 1535163 | 860 | Distribution Circuit | 3rd Party | Vehicle | 307 | 86788 | 37.7822 | -122.1744 | STEPHENS-KEVIN: mountian blvd at mountian view | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 16-0061499 | OH | Sus | 0 | No | 2016 | SEP | Yes | Force Out | 1221733 | PW | OH | No | Yes
EAST BAY | FIELD OPS CENTRAL | Tier 2 | PALO SECO-0401 | 13180401 | FUSE | 4137 | 20160907 | 1946 | 1538075 | 1214 | Distribution Circuit | Vegetation | Tree - branch fell on line | 312 | 236643 | 37.8153 | -122.203 | MELVIN RDAND BRENTWWOD RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0063033 | OH | Sus | 42782536 | No | 2016 | SEP | Yes | Line to Ground | 1222708 | PW | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND J-1102 | 12091102 | FUSE | 6625 | 20161006 | 630 | 1553754 | 573 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 14234 | 37.7884 | -122.1776 | STEPHENS-KEVIN: 5012 leona | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0070025 | OH | Sus | 31275507 | No | 2016 | OCT | Yes | Line to Line | 1227683 | CAW | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | PALO SECO-0401 | 13180401 | FUSE | 4137 | 20161019 | 1629 | 1566177 | 1269 | Distribution Circuit | Vegetation | Tree - fell into line | 312 | 185583 | 37.8153 | -122.203 | COR OF MELVIN RD & BRENTWOOD RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0074093 | OH | Sus | 0 | No | 2016 | OCT | Yes | Line to Ground | 1230847 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | SPRUCE-0401 | 13340401 | FUSE | R4135 | 20161030 | 1345 | s1232907 | 915 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 80520 | 37.9074 | -122.279 | 91 FRANCISCIAN WAY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076790 | OH | Sus | 31281285 | No | 2016 | OCT | Yes | Line to Ground | 1232907 | CO | OH | No | Yes
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1102 | 12101102 | FUSE | 9897 | 20161119 | 2133 | 1585404 | 666 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 8658 | 37.8392 | -122.1969 | 7256 HOMEWOOD DR OAKLAND- at FUCO 9897 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081194 | OH | Sus | 42882760 | yes | 2016 | NOV | Yes | Line to Ground | 1236216 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1104 | 12541104 | OTHER | WIRE DOWN OUTAGE @6750 LONGWALK DR | 20161120 | 1155 | 1585702 | 940 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 6864 | 37.8263 | -122.1897 | 6750 LONGWALK DR | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081255 | OH | Sus | 42882778 | yes | 2016 | NOV | Yes | Open Circuit | 1236283 | CO | OH | No | Yes
EAST BAY | FIELD OPS CENTRAL | Tier 2 | EDES-1112 | 13681112 | RECLOSER | CR282 | 20161215 | 2358 | 1603966 | 421 | Distribution Circuit | Vegetation | Tree - fell into line | 766 | 55216 | 37.7543 | -122.1482 | SEQUOYAH RD OAKLAND | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085921 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1240587 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | EL CERRITO G-1105 | 12501105 | FUSE | R8819 | 20170205 | 1832 | 1675534 | 281 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 843 | 37.922 | -122.291 | 3 SPANS LOAD SIDE OF R8819 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0017574 | OH | Sus | 0 | No | 2017 | FEB | Yes | Line to Ground | 1255540 | PW | OH | No | Yes
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1102 | 12101102 | FUSE | 1181 | 20170227 | 842 | 1714861 | 1023 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 26102 | 37.8411 | -122.2049 | 1815 WOODHAVEN | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0026996 | OH | Sus | 31307898 | No | 2017 | FEB | Yes | Line to Ground | 1263691 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1106 | 12541106 | OTHER | WIRE DOWN 5 POLES E/OF 9403 | 20170413 | 2247 | 1757554 | 778 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 12253 | 37.8063 | -122.1681 | STEPHENS-KEVIN: redwood rd. 5/p/east of c/o 9403 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0040165 | OH | Sus | 42994033 | yes | 2017 | APR | Yes | Line to Ground | 1273778 | CO | OH | No | Yes
EAST BAY | FIELD OPS CENTRAL | Tier 2 | HOLLYWOOD-0401 | 13170401 | JUMPER | OJ @ 4338 RIDGEVIEW TO EOL | 20170615 | 1713 | 1805352 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 13271 | 37.8115 | -122.2109 | 4338 RIDGEVIEW | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0055575 | OH | Sus | 43040241 | No | 2017 | JUN | Yes | Line to Ground | 1285120 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1106 | 12541106 | FUSE | 9403 | 20170621 | 1124 | 1813801 | 216 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 2160 | 37.8054 | -122.1705 | 15P W/OF 6579 | Clear-32-90 F | Insulator | Broken, wire on ground | 17-0057341 | OH | Sus | 43042973 | yes | 2017 | JUN | Yes | Line to Ground | 1286663 | INS | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1106 | 12541106 | FUSE | 9403 | 20170705 | 1341 | 1824030 | 306 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3060 | 37.8054 | -122.1705 | 25 POLE E/OF 9403 FUCO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0060629 | OH | Sus | 43049333 | No | 2017 | JUL | Yes | Line to Ground | 1289134 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | EL CERRITO G-1112 | 12501112 | FUSE | R9145 | 20170827 | 1345 | 1860419 | 220 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 5500 | 37.9385 | -122.3048 | 6832 del monte ave | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0073170 | OH | Sus | 0 | yes | 2017 | AUG | Yes | Line to Ground | 1298045 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1104 | 12541104 | FUSE | 8963 | 20170828 | 522 | 1861026 | 417 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 13344 | 37.8276 | -122.1935 | TWAROWSKI- CHRIS 650-826-6246: FUSES 8963 CORNER OF CHELTON AND STOCKBRIDGE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0073287 | OH | Sus | 31345487 | yes | 2017 | AUG | Yes | Line to Ground | 1298157 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND K-1104 | 12101104 | RECLOSER | CR210 | 20171011 | 1534 | 1898691 | 1434 | Distribution Circuit | Vegetation | Tree - fell into line | 419 | 125641 | 37.8299 | -122.2106 | COLTON & GASPAR | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086426 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1307517 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | FUSE | 9749 | 20171024 | 35 | 1908364 | 784 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 22736 | 37.81 | -122.1975 | STEPHENS-KEVIN: same | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0089929 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Line | 1310317 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | WALDO-0402 | 13350402 | OTHER | WIRE DOWN TERRACE @ PARK WY | 20171102 | 13 | 1914070 | 504 | Distribution Circuit | Equipment Failure/Involved | Overhead | 462 | 95050 | 37.912 | -122.2904 | COR PARKWAY AND TERRACE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0091937 | OH | Sus | 43205566 | No | 2017 | NOV | Yes | Line to Ground | 1311702 | CO | OH | No | Yes
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | RECLOSER | CR020 | 20171207 | 913 | 1938026 | 1065 | Distribution Circuit | 3rd Party | Vehicle | 79 | 33965 | 37.8 | -122.1706 | at POLE 110134458 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0100477 | OH | Sus | 0 | No | 2017 | DEC | Yes | Line to Line | 1318140 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1104 | 12101104 | OTHER | WIRE DOWN @ 8501 SKYLINE AND PINEHILLS | 20171210 | 2031 | 1940158 | 582 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1513 | 173825 | 37.8315 | -122.1857 | 8501 SKYLINE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0101051 | OH | Sus | 31369161 | No | 2017 | DEC | Yes | Line to Ground | 1318748 | CO | OH | No | Yes
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1102 | 12101102 | FUSE | 9327 | 20180108 | 1002 | 3796 | 263 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1052 | 37.8682 | -122.2172 | 6 poles LD side of FUCO-9327 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0004294 | OH | Sus | 43246257 | yes | 2018 | JAN | Yes | Multi-Fault | 1323625 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND K-1103 | 12101103 | FUSE | 9898 | 20180322 | 1328 | 50810 | 1057 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 23556 | 37.8357 | -122.214 | 5763 FLORENCE TERRACE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025578 | OH | Sus | 31384752 | yes | 2018 | MAR | Yes | Line to Ground | 1337637 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | SAN LEANDRO-1109 | 13111109 | SWITCH | 9859 | 20180406 | 1956 | 61346 | 646 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 23298 | 37.7475 | -122.1196 | 4859 Lowry | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0030134 | OH | Sus | 31387717 | yes | 2018 | APR | Yes | Line to Ground | 1341004 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE | 8989 | 20180421 | 1929 | 71438 | 756 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 20220 | 37.8311 | -122.2019 | TREE WIRE DOWN: 5936 BALBOA DR AND PASA ROBLE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0034366 | OH | Sus | 31389640 | No | 2018 | APR | Yes | None | 1344170 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1104 | 12541104 | FUSE | 9019 | 20180514 | 2234 | 86209 | 267 | Distribution Circuit | Equipment Failure/Involved | Overhead | 196 | 34947 | 37.8153 | -122.1951 | 3 SPANS LD SIDE OF 9019 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0041044 | OH | Sus | 31392084 | No | 2018 | MAY | Yes | Line to Ground | 1349013 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | ARLINGTON-0401 | 13700401 | OTHER | WIRE DOWN 1/N/O R3377 | 20181015 | 1841 | 195932 | 533 | Distribution Circuit | Equipment Failure/Involved | Overhead | 138 | 51793 | 37.891 | -122.2608 | 1/N/O R3377 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0090695 | OH | Sus | 43507397 | No | 2018 | OCT | Yes | Line to Ground | 1385864 | CSO | OH | No | Yes
EAST BAY | FIELD OPS CENTRAL | Tier 2 | FAIRVIEW-2207 | 13432207 | FUSE | R1001 | 20181203 | 1538 | 232986 | 467 | Distribution Circuit | Equipment Failure/Involved | Overhead | 504 | 56968 | 38.0485 | -122.2217 | 579 Kendall ave | Strong Winds-Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0106605 | OH | Sus | 43605435 | No | 2018 | DEC | Yes | Line to Ground | 1397383 | CO | OH | No | Yes
EAST BAY | FIELD OPS CENTRAL | Tier 2 | SPRUCE-0402 | 13340402 | FUSE | R3383 | 20181228 | 1811 | 249067 | 429 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 9009 | 37.9025 | -122.2642 | 1SE/of R3383 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110990 | OH | Sus | 43623205 | No | 2018 | DEC | Yes | Force Out | 1402191 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | BERKELEY F-1103 | 12061103 | FUSE | R8029 | 20190101 | 53 | 251237 | 2277 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 19331 | 37.8695 | -122.245 | 5 SPANS PAST R8029 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0003398 | OH | Sus | 31420132 | No | 2019 | JAN | Yes | Line to Line | 1402604 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND J-1105 | 12091105 | RECLOSER | CR256 | 20190118 | 1116 | 275653 | 723 | Distribution Circuit | 3rd Party | Vehicle | 383 | 114724 | 37.7779 | -122.1693 | MT. VIEW & MT. BLVD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011721 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408172 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | EL CERRITO G-1105 | 12501105 | FUSE | R8833 | 20190120 | 720 | 277122 | 2045 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 14315 | 37.894 | -122.2423 | 10 SPANS N/OF R8833 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012526 | OH | Sus | 43641148 | yes | 2019 | JAN | Yes | Line to Ground | 1408874 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE | 8940 | 20190203 | 709 | 288499 | 741 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 17784 | 37.8359 | -122.1929 | 18 CHICO CT | Rain-Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017466 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411881 | CO | OH | No | Yes
EAST BAY | FIELD OPS CENTRAL | Tier 2 | FAIRVIEW-2207 | 13432207 | JUMPER | CENTER PHASE WIRE DOWN 1/W OF R4984 | 20190221 | 712 | 320264 | 688 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2881 | 38.0486 | -122.2216 | 1/W OF R4984 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0026944 | OH | Sus | 43683429 | yes | 2019 | FEB | Yes | Line to Ground | 1419460 | CSO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND K-1103 | 12101103 | FUSE | 7970 | 20190306 | 350 | 332157 | 913 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 21912 | 37.8358 | -122.2186 | LD SIDE OF 7970 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031087 | OH | Sus | 43690691 | yes | 2019 | MAR | Yes | Line to Ground | 1422195 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1104 | 12541104 | FUSE | 8961 | 20190413 | 1150 | 360217 | 325 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 13 | 4225 | 37.8199 | -122.1955 | LD SIDE OF 8961 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0042205 | OH | Sus | 0 | No | 2019 | APR | Yes | Line to Ground | 1430072 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1101 | 12101101 | OTHER | 1 PHASE 1 SPAN DOWN ON HS OF R9921 | 20190611 | 1853 | 406692 | 673 | Distribution Circuit | Equipment Failure/Involved | Overhead | 246 | 165558 | 37.8538 | -122.2357 | HS OF R9921 | Clear-Heat Wave-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0066300 | OH | Sus | 43839117 | yes | 2019 | JUN | Yes | Line to Ground | 1448231 | CO | OH | No | Yes
EAST BAY | FIELD OPS CENTRAL | Tier 2 | SAN LEANDRO-1109 | 13111109 | JUMPER | 1 PHASE 1 SPAN DOWN | 20190722 | 1727 | 468273 | 1142 | Distribution Circuit | Vegetation | Tree - fell into line | 311 | 14413 | 37.7461 | -122.1212 | at FUCO-1071 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0079992 | OH | Sus | 43893879 | No | 2019 | JUL | Yes | Line to Ground | 1457956 | CO | OH | No | Yes
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND K-1103 | 12101103 | FUSE | 7970 | 20190812 | 2355 | 504806 | 904 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 22600 | 37.8358 | -122.2186 | WEST- GREG/3334 510-672-3166: 1552 fernhood dr | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0087113 | OH | Sus | 31462349 | No | 2019 | AUG | Yes | Line to Ground | 1462553 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1102 | 12101102 | FUSE | 1726 | 20190926 | 210 | 615645 | 388 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 10864 | 37.8427 | -122.2122 | S/W/Corner Valley View & Beauforest Dr | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0103842 | OH | Sus | 43969669 | yes | 2019 | SEP | Yes | Line to Ground | 1473055 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | FAIRVIEW-2207 | 13432207 | RECLOSER | P150 | 20191031 | 1716 | 697062 | 558 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1865 | 138161 | 38.0454 | -122.1903 | C/O CARQUINEZ SCENIC AND CANYON LAKE DR BETWEEN P155 AND R3859 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0119756 | OH | Sus | 44087245 | yes | 2019 | OCT | Yes | Line to Ground | 1488572 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | VALLEY VIEW-1106 | 14341106 | FUSE | R8867 | 20200206 | 1837 | 779689 | 832 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 68224 | 37.9553 | -122.2698 | 6107 HILLSIDE DR | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0018331 | OH | Sus | 31489477 | No | 2020 | FEB | Yes | Line to Ground | 1512487 | PW | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | JUMPER | WIRE DOWN 1 PHASE AT 9319 | 20200718 | 2242 | 967537 | 824 | Distribution Circuit | Vegetation | Tree - bark fell into line | 35 | 27632 | 37.8086 | -122.1977 | AT 9319 PER R. BRADLEY | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0073382 | OH | Sus | 31509160 | No | 2020 | JUL | Yes | Line to Ground | 1547617 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1101 | 12541101 | FUSE | 9541 | 20210630 | 2320 | 1389304 | 233 | Distribution Circuit | Equipment Failure/Involved | Overhead | 54 | 12582 | 37.8347 | -122.1903 | 4 SPANS LOAD SIDE OF 9541 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0082934 | OH | Sus | 44887523 | No | 2021 | JUN | Yes | Line to Ground | 1644048 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND J-1102 | 12091102 | OTHER | OJ 1 POLE N/O 5125 LEONA ST | 20210726 | 436 | 1414532 | 666 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 12086 | 37.7876 | -122.1764 | 5125 LEONA ST | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0094771 | OH | Sus | 0 | No | 2021 | JUL | Yes | Line to Ground | 1651658 | CO | OH | No | Yes
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND J-1102 | 12091102 | FUSE | 797701 | 20211006 | 705 | 1488203 | 441 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5292 | 37.7978 | -122.1842 | LD SIDE OF TAP LINE- LD SIDE OF 797701 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0126426 | OH | Sus | 31553655 | No | 2021 | OCT | Yes | Line to Ground | 1671242 | CSO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1104 | 12541104 | FUSE | 32264 | 20211010 | 2018 | 1491739 | 956 | Distribution Circuit | 3rd Party | Vehicle | 9 | 8604 | 37.817 | -122.203 | MOUNTAIN BLVD AT 315088248336 | Clear-32-90 F | Pole-Wood | Broken, wire on object | 21-0128499 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1672434 | PW | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1106 | 12541106 | FUSE | 9403 | 20211109 | 817 | 1538485 | 435 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3915 | 37.8055 | -122.1704 | 11/W/OF 6579 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0143828 | OH | Sus | 31578082 | No | 2021 | NOV | Yes | Line to Ground | 1683018 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1102 | 12101102 | RECLOSER | CR014 | 20211223 | 357 | 1579569 | 821 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1343 | 330604 | 37.8516 | -122.2055 | back yard 6848 thornhill | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160245 | OH | Sus | 45100393 | No | 2021 | DEC | Yes | Line to Ground | 1697678 | CO | OH | No | Yes
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | RECLOSER | 950688 | 20220122 | 419 | 1608571 | 858 | Distribution Circuit | Vegetation | Tree - fell into line | 436 | 163038 | 37.7953 | -122.1577 | 1 SPAN S/E OF 6574 | Strong Winds- | Conductor, Overhead | Broken, wire on ground | 22-0012898 | OH | Sus | 0 | No | 2022 | JAN | Yes | Three Phase Fault | 1704223 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1104 | 12541104 | OTHER | WIRE DOWN 1 SPAN LD S/O 9587 | 20220124 | 834 | 1610204 | 396 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 396 | 37.819 | -122.2068 | LD SIDE OF 9587 FUSE | Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0013455 | OH | Sus | 45145322 | No | 2022 | JAN | Yes | Line to Ground | 1704728 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | FG-4 (EL CERRITO G-1204) TIE | 12501204 | FUSE | 74014 | 20220201 | 1821 | 1618712 | 163 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 25046 | 37.9006 | -122.2663 | 726 HILLDALE AVE | Strong Winds- | Conductor, Overhead | Broken, wire on ground | 22-0017280 | OH | Sus | 0 | No | 2022 | FEB | Yes | Line to Ground | 1706782 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND X-1106 | 12541106 | FUSE | 6579 | 20220702 | 642 | 1747687 | 314 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1888 | 37.7984 | -122.1518 | 3 POLES E/OF 6579 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0081354 | OH | Sus | 0 | No | 2022 | JUL | Yes | Line to Ground | 1749646 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | RECLOSER | CR008 | 20221020 | 2256 | 1841721 | 747 | Distribution Circuit | Vegetation | Tree - fell into line | 1332 | 85824 | 37.8093 | -122.1905 | 21/P/E/OF 9403 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0123411 | OH | Sus | 0 | No | 2022 | OCT | Yes | Line to Ground | 1777916 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | EL CERRITO G-1105 | 12501105 | OTHER | WIRE DOWN 1125 BREWSER DR | 20221227 | 330 | 1898194 | 1115 | Distribution Circuit | Vegetation | Tree - fell into line | 5990 | 413937 | 37.9221 | -122.2935 | 1125 BREWSTER DR- EL CERITTO | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0141536 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793212 | CO | OH | No | Yes
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND D-1112 | 12041112 | RECLOSER | 411646 | 20221229 | 1111 | 1901347 | 654 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 35529 | 37.8633 | -122.2356 | COMBO 9787 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142057 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793811 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | EDES-1112 | 13681112 | FUSE | 6633 | 20230111 | 2034 | 1949059 | 2139 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 17409 | 37.775 | -122.1604 | 315205946931 | Clear-32-90F | Conductor, Overhead | Broken, wire on object | 23-0014017 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1803367 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | FUSE | 6627 | 20230112 | 352 | 1949313 | 675 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 26244 | 37.8043 | -122.1819 | 3109 BUTTERS (1/S/OF 6947) | Clear-32-90F | Conductor, Overhead | Broken, wire on object | 23-0014242 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1803593 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | JUMPER | OJ N/OF 85 MAIDEN LN | 20230302 | 1041 | 2019639 | 883 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 22018 | 37.8085 | -122.1977 | 85 MAINDEN LN | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0038730 | OH | Sus | 31639406 | No | 2023 | MAR | Yes | Line to Ground | 1820819 | CAW | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | EL CERRITO G-1105 | 12501105 | FUSE | R8474 | 20230324 | 1959 | 2066610 | 106 | Distribution Circuit | Equipment Failure/Involved | Overhead | 136 | 10656 | 37.9154 | -122.282 | S/W OF COWPER RD AND KENSINGTON RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0051017 | OH | Sus | 0 | No | 2023 | MAR | Yes | Force Out | 1830007 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 3 | OAKLAND K-1104 | 12101104 | FUSE | 8819 | 20230324 | 1338 | 2066156 | 252 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 3528 | 37.8369 | -122.1893 | EOL TREE CAME DOWN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0051913 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1829926 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | SAN LEANDRO-1109 | 13111109 | TRANSFORMER | 315318845994 | 20230329 | 304 | 2072243 | 756 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 9544 | 37.7521 | -122.1204 | JENKINS- MARCUS 510-385-4363: Grass Valley Rd 115? e/o Sun Valley Dr | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0054001 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1831473 | CO | OH | No | No
EAST BAY | FIELD OPS CENTRAL | Tier 2 | OAKLAND X-1106 | 12541106 | RECLOSER | CR008 | 20230902 | 37 | 2208295 | 751 | Distribution Circuit | 3rd Party | Vehicle | 1330 | 190180 | 37.8093 | -122.1905 | 14370 SKYLINE BLVD (LD SIDE OF LR-950688) OIS 2208297 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 23-0112036 | OH | Sus | 0 | No | 2023 | SEP | Yes | Line to Ground | 1870893 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | COPPERMINE-1104 | 252411104 | OTHER |  | 20130206 | 803 | 739016 | 273 | Distribution Circuit | 3rd Party | Vehicle | 405 | 13487 | 36.942 | -119.5046 | MTR# 1005525341 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0008326 | OH | Sus | 30975722 | No | 2013 | FEB | Yes | Line to Ground | 99301974 | PW | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | FUSE | D9781 | 20130219 | 2106 | 744631 | 870 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 15660 | 36.9881 | -119.3896 | MARKARIAN-FRED / 559-289-4068: 5 SPANS N/O D-9781 | Snow-Below 32 F | Conductor, Overhead | On Ground | 13-0011073 | OH | Sus | 41856436 | yes | 2013 | FEB | Yes | Line to Ground | 99300202 | CO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | SAND CREEK-1103 | 254601103 | RECLOSER | 7140 | 20130219 | 2200 | 744685 | 361 | Distribution Circuit | Environmental/External | Ice or snow | 436 | 44731 | 36.6757 | -119.1893 | 31965 GEORGE SMITH RD | Rain-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0011065 | OH | Sus | 41856541 | yes | 2013 | FEB | Yes | Line to Ground | 99300258 | CSO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | FUSE | D2995 | 20130220 | 834 | 744947 | 453 | Distribution Circuit | Equipment Failure/Involved | Other | 130 | 58890 | 37.0055 | -119.4068 | 28408 TOLLHOUSE RD | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0011221 | OH | Sus | 41856724 | yes | 2013 | FEB | Yes | Three Phase Fault | 99300080 | CO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | FUSE | D8242 | 20130220 | 659 | 744841 | 711 | Distribution Circuit | Equipment Failure/Involved | Other | 8 | 5688 | 37.0713 | -119.4805 | MTR# 1004201331 | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 13-0011258 | OH | Sus | 41856731 | yes | 2013 | FEB | Yes | Line to Ground | 99300059 | CO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1102 | 254151102 | FUSE | D8071 | 20130220 | 502 | 744804 | 733 | Distribution Circuit | Equipment Failure/Involved | Other | 22 | 16126 | 37.0459 | -119.5007 | 31163 BLUE HERON | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0011127 | OH | Sus | 30978357 | yes | 2013 | FEB | Yes | Line to Ground | 99300182 | CO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | TIVY VALLEY-1107 | 252941107 | FUSE | 7986F | 20130330 | 1635 | 763862 | 599 | Distribution Circuit | Equipment Failure/Involved | Other | 46 | 8813 | 36.7963 | -119.3089 | BENEGAR- AL / 559-908-7191: END OF HOPEWELL ROAD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0020190 | OH | Sus | 0 | No | 2013 | MAR | Yes | Line to Ground | 99293927 | CO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | TIVY VALLEY-1107 | 252941107 | FUSE | 7793F | 20130406 | 1615 | 767585 | 480 | Distribution Circuit | Equipment Failure/Involved | Other | 11 | 3420 | 36.8188 | -119.3417 | 1 W/OF MTR# 653R15 | Partly cloudy-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0022003 | OH | Sus | 41877768 | No | 2013 | APR | Yes |  | 99292535 | CSO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | SAND CREEK-1103 | 254601103 | FUSE | 89437 | 20130416 | 1619 | 776615 | 351 | Distribution Circuit | Equipment Failure/Involved | Other | 7 | 1489 | 36.6815 | -119.1801 | OKAMURA- DALE / 559/903-3864: 3 E/O SQUAW VALLEY- S/S SAND CREEK | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0025043 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Ground | 99290150 | PW | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1102 | 254151102 | FUSE | D8329 | 20130517 | 1508 | 794357 | 491 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 13748 | 37.0093 | -119.572 | MTR# 1005847326 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0032707 | OH | Sus | 30997195 | No | 2013 | MAY | Yes | Line to Ground | 99284553 | CO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | TIVY VALLEY-1107 | 252941107 | FUSE | 7972F | 20130605 | 1807 | 804469 | 244 | Distribution Circuit | Equipment Failure/Involved | Other | 185 | 44335 | 36.726 | -119.2362 | 3 N/OF 7972F IN POND OR 1 N/OF MTR#1005160910 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0036885 | OH | Sus | 0 | No | 2013 | JUN | Yes | None | 99281680 | CO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1102 | 254061102 | RECLOSER | 7050 | 20130721 | 2222 | 836216 | 1155 | Distribution Circuit | Vegetation | Tree - fell into line | 320 | 196122 | 36.6978 | -119.0113 | ON MAIN LINE 2 SPANS LD SIDE OF 3201F | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0048977 | OH | Sus | 41930406 | No | 2013 | JUL | Yes | Line to Ground | 99273064 | CO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER | 7170 | 20130721 | 2214 | 836217 | 677 | Distribution Circuit | Vegetation | Tree - fell into line | 346 | 231219 | 36.7265 | -118.9948 | OKAMURA- DALE: 3 POLES SOURCE SIDE OF SW 7174 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0048980 | OH | Sus | 31010055 | No | 2013 | JUL | Yes | Three Phase Fault | 99273061 | PW | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | SAND CREEK-1103 | 254601103 | OTHER |  | 20130721 | 2239 | 836468 | 1121 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 84017 | 36.6369 | -118.9571 | MTR# 1005161070 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0049068 | OH | Sus | 0 | No | 2013 | JUL | Yes | Line to Ground | 99272988 | CO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER | 7220 | 20130814 | 608 | 848021 | 197 | Distribution Circuit | Animal | Bird found | 679 | 90689 | 36.716 | -119.0341 | BENEGAR- AL / 559-908-7191: MILLWOOD E/O DUNLAP RD | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 13-0054445 | OH | Sus | 41943095 | No | 2013 | AUG | Yes | Line to Ground | 99269477 | CO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | RECLOSER | R314 | 20131011 | 1323 | 883317 | 301 | Distribution Circuit | 3rd Party | Vehicle | 412 | 98012 | 36.9957 | -119.4093 | D3820 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0069047 | OH | Sus | 41971607 | No | 2013 | OCT | Yes | Line to Ground | 99258864 | CO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | SAND CREEK-1103 | 254601103 | FUSE | 7995F | 20131111 | 1730 | 899714 | 1102 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 18178 | 36.6375 | -118.9557 | 1 SS OF MTR#1005281146 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0075500 | OH | Sus | 31035218 | No | 2013 | NOV | Yes | Line to Line | 99253893 | PW | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1102 | 254061102 | FUSE | 3755F | 20131210 | 1407 | 925140 | 393 | Distribution Circuit | Equipment Failure/Involved | Other | 12 | 4716 | 36.6861 | -119.0297 | MTR# 1005283033 | Clear-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 13-0081816 | OH | Sus | 31041792 | No | 2013 | DEC | Yes | Line to Line | 99248387 | CAW | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | OTHER |  | 20140209 | 1040 | 964199 | 343 | Distribution Circuit | Equipment Failure/Involved | Other | 153 | 48794 | 37.0806 | -119.428 | MTR# 1004794974 | Drizzle-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0010143 | OH | Sus | 31055599 | yes | 2014 | FEB | Yes | Line to Ground | 99240483 | CAW | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | SAND CREEK-1103 | 254601103 | OTHER |  | 20140228 | 2011 | 975874 | 404 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 620 | 36.6724 | -119.1655 | MTR# 768R96 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0014659 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Ground | 99237386 | CO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | TIVY VALLEY-1107 | 252941107 | FUSE | 7957F | 20140228 | 1338 | 975338 | 482 | Distribution Circuit | Vegetation | Tree - branch fell on line | 54 | 26028 | 36.8023 | -119.317 | MTR# 1005062105 | Lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0014578 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Three Phase Fault | 99237449 | CO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | FUSE | 86689 | 20140305 | 1859 | 979233 | 279 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 1674 | 36.9323 | -119.4334 | BET 1ST & 2ND POLELD SIDE OF 86689 | Partly cloudy-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0015808 | OH | Sus | 42087553 | yes | 2014 | MAR | Yes | Line to Ground | 99236545 | CSO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | OTHER |  | 20140422 | 1149 | 1002943 | 301 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 35 | 10535 | 37.0913 | -119.4664 | 2 LD SIDE OF R322 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0026535 | OH | Sus | 31070958 | No | 2014 | APR | Yes | Line to Ground | 99229216 | CO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1102 | 254061102 | RECLOSER | 7050 | 20140426 | 1233 | 1004993 | 33 | Distribution Circuit | Equipment Failure/Involved | Other | 321 | 7738 | 36.6978 | -119.0113 | LD SIDE OF 3201F ON MAIN LINE | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0027504 | OH | Sus | 0 | yes | 2014 | APR | Yes | Line to Ground | 99228526 | CO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1103 | 254061103 | FUSE | 7989F | 20140426 | 29 | 1004919 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 215 | 110080 | 36.7853 | -118.9177 | MTR# 1005908047 | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0027512 | OH | Sus | 0 | yes | 2014 | APR | Yes | Line to Line | 99228543 | CO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1102 | 254061102 | SWITCH | 3084D | 20140428 | 941 | 1005739 | 178 | Distribution Circuit | Equipment Failure/Involved | Other | 4 | 712 | 36.7231 | -118.9814 | LD SIDE OF 3201F ON MAIN LINE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0027504 | OH | Sus | 0 | No | 2014 | APR | Yes | Line to Ground | 99228283 | CO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1102 | 254061102 | FUSE | 7953F | 20140809 | 1536 | 1063653 | 269 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 6526 | 36.6861 | -119.0436 | MTR#1005057583 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0050097 | OH | Sus | 0 | No | 2014 | AUG | Yes | Line to Ground | 99212772 | CO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1102 | 254061102 | OCB | OCB | 20141101 | 852 | 1107614 | 1804 | Distribution Circuit | Vegetation | Tree - branch fell on line | 720 | 250417 | 36.7095 | -119.029 | 3 SPANS E/OF 3201F ON MAIN LINE | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0067696 | OH | Sus | 0 | yes | 2014 | NOV | Yes | Line to Ground | 99200765 | CO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER | 7170 | 20141214 | 913 | 1140304 | 439 | Distribution Circuit | Equipment Failure/Involved | Other | 347 | 149394 | 36.7265 | -118.9948 | 6 P LD SIDE OF 7971D | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076861 | OH | Sus | 0 | No | 2014 | DEC | Yes | Line to Line | 99193166 | CO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | TIVY VALLEY-1107 | 252941107 | FUSE | 7979F | 20141214 | 1411 | 1140518 | 594 | Distribution Circuit | Equipment Failure/Involved | Other | 19 | 4518 | 36.727 | -119.2178 | MTR# 1005908913 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0076887 | OH | Sus | 0 | No | 2014 | DEC | Yes | Line to Ground | 99193144 | PW | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1103 | 254061103 | FUSE | 7991F | 20150223 | 1256 | 1194740 | 263 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 1578 | 36.7641 | -118.9404 | POLE 18 & 19 | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 15-0015241 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99180755 | CO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1102 | 254151102 | RECLOSER | R902 | 20150307 | 1442 | 1200526 | 668 | Distribution Circuit | 3rd Party | Vehicle | 678 | 80965 | 37.0347 | -119.5181 | 1 POLE N/OF D9770 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0018010 | OH | Sus | 31139316 | No | 2015 | MAR | Yes | Line to Ground | 99179025 | PW | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1103 | 254061103 | OTHER |  | 20150611 | 1548 | 1249475 | 361 | Distribution Circuit | Vegetation | Tree - branch fell on line | 348 | 62097 | 36.7391 | -118.9686 | W/OF 7256F ON MAIN LINE | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0040507 | OH | Sus | 42405130 | No | 2015 | JUN | Yes | Line to Ground | 99164089 | CO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 3 | AUBERRY-1101 | 254151101 | FUSE | D2385 | 20150624 | 1335 | 1255850 | 311 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 33 | 10263 | 37.0554 | -119.362 | BENTLEY- STEVE: 36399 Peterson Rd Auberry | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0043152 | OH | Sus | 31164037 | No | 2015 | JUN | Yes | Line to Line | 99162151 | CO | OH | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1102 | 254151102 | FUSE | D2748 | 20150728 | 1846 | 1278976 | 416 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 22249 | 37.017 | -119.5136 | MARKARIAN-FRED / 559-289-4068: 30493 GOOSEBERRY | Clear-Above 90 | Pole-Wood | Broken, wire on ground | 15-0051117 | OH | Sus | 0 | No | 2015 | JUL | Yes | Line to Ground | 1147967 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1102 | 254061102 | FUSE | 7849F | 20150817 | 2057 | 1290631 | 702 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 34398 | 36.6937 | -119.0524 | OKAMURA- DALE: 46371 ORCHARD DRIVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0055696 | OH | Sus | 42453049 | yes | 2015 | AUG | Yes | Line to Line | 1151243 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | FUSE | D8567 | 20150913 | 1254 | 1304991 | 630 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 10710 | 37.0459 | -119.3869 | 2P W/OF D8567 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0061098 | OH | Sus | 0 | No | 2015 | SEP | Yes | Line to Line | 1154988 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | SAND CREEK-1103 | 254601103 | RECLOSER | 7140 | 20151026 | 1416 | 1329458 | 510 | Distribution Circuit | 3rd Party | Vehicle | 437 | 62759 | 36.6751 | -119.1899 | PASQUA MARK: george smith/otter | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 15-0073402 | OH | Sus | 31195062 | No | 2015 | OCT | Yes | Line to Line | 1164644 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | TIVY VALLEY-1107 | 252941107 | JUMPER | WIRE DOWN HOT | 20151026 | 1835 | 1329551 | 252 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 3380 | 36.8189 | -119.3441 | SOURCE SIDE OF 7490 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0073469 | OH | Sus | 0 | No | 2015 | OCT | Yes | Line to Ground | 1164664 | CSO | OH | No | Yes
FRESNO | FIELD OPS SOUTH | Tier 2 | KERCKHOFF-1101 | 252561101 | RECLOSER | R308 | 20151110 | 1410 | 1339320 | 1459 | Distribution Circuit | Animal | Bird found | 14 | 8304 | 37.099 | -119.5182 | RENVILLE- GREG: 5 POLES N/O D4501 3 POLES IN A ROW | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 15-0077145 | OH | Sus | 0 | No | 2015 | NOV | Yes | Line to Ground | 1167678 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | RECLOSER | R2838 | 20160106 | 957 | 1378420 | 623 | Distribution Circuit | Vegetation | Tree - fell into line | 414 | 81656 | 37.0876 | -119.4688 | SS OF SW 318 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0003407 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1178992 | CAW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 3 | AUBERRY-1101 | 254151101 | FUSE | D5467 | 20160107 | 1240 | 1379678 | 258 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 1806 | 37.0475 | -119.3222 | 7 E/OF MTR# 1004822729 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003888 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1179333 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1103 | 254061103 | FUSE | 3044F | 20160110 | 1248 | 1381268 | 1527 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 71558 | 36.7858 | -118.912 | 2 POLES LD SIDE OF MTR # 1005756222 WIRE DOWN | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0004370 | OH | Sus | 0 | No | 2016 | JAN | Yes | Line to Ground | 1179815 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1102 | 254061102 | RECLOSER | 7050 | 20160131 | 1618 | 1395142 | 1581 | Distribution Circuit | Environmental/External | Ice or snow | 318 | 148950 | 36.6985 | -119.0118 | 1 P W/OF 7606D | Overcast-Fog-32-90 F | Conductor, Overhead | On Ground | 16-0009457 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1183534 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | SAND CREEK-1103 | 254601103 | FUSE | 3206F | 20160131 | 2128 | 1395687 | 1246 | Distribution Circuit | Environmental/External | Ice or snow | 17 | 20197 | 36.6125 | -119.0035 | 47246 DRY CREEK DR- at MTR# 1009961312- 2 S/OF MTR & 4 S/OF MTR | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009608 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1183690 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | TIVY VALLEY-1107 | 252941107 | RECLOSER | 81422 | 20160201 | 927 | 1396190 | 526 | Distribution Circuit | Vegetation | Tree - fell into line | 1023 | 97560 | 36.7282 | -119.2576 | Nelson- Chad/ 559-309-4421: POLE 7987F P2P | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | On Ground | 16-0009713 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Line | 1183792 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | FUSE | D8356 | 20160306 | 938 | 1421706 | 643 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 11 | 7073 | 36.978 | -119.3676 | MTR# 1008993291 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0018394 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190244 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | FUSE | D8625 | 20160306 | 1107 | 1421920 | 793 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 793 | 37.0823 | -119.415 | 2ND POLE FROM END OF TAP | Partly Cloudy-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0018437 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190274 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | JUMPER | WIRE DOWN B PHASE | 20160314 | 814 | 1431038 | 224 | Distribution Circuit | Vegetation | Tree - fell into line | 128 | 2510 | 37.016 | -119.4021 | 28425 GIBBS RANCH RD | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021191 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Open Circuit | 1192547 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | SAND CREEK-1103 | 254601103 | FUSE | 3206F | 20160419 | 2112 | 1454047 | 144 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 2448 | 36.6125 | -119.0035 | 5 P W/OF 3206F | Clear-32-90 F | Woodpin | Broken, wire on object | 16-0029830 | OH | Sus | 0 | No | 2016 | APR | Yes | Force Out | 1198830 | WP | OH | No | Yes
FRESNO | FIELD OPS SOUTH | Tier 3 | AUBERRY-1101 | 254151101 | OTHER | D328 | 20160523 | 738 | 1474999 | 716 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 5 | 3580 | 37.0357 | -119.326 | MTR# 1006305779 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0037756 | OH | Sus | 0 | No | 2016 | MAY | Yes | Three Phase Fault | 1204839 | CO | OH | No | Yes
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1102 | 254151102 | FUSE | D9401 | 20160612 | 327 | 1487383 | 682 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1364 | 36.9935 | -119.5294 | 2 W/OF D9401 | Partly Cloudy-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0042670 | OH | Sus | 0 | yes | 2016 | JUN | Yes | Line to Line | 1208584 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 3 | AUBERRY-1101 | 254151101 | FUSE | D2308 | 20160614 | 1254 | 1488736 | 316 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 11376 | 37.0779 | -119.342 | 39046 WOODLAND RD- SHAVER LAKE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0043218 | OH | Sus | 0 | No | 2016 | JUN | Yes | Line to Line | 1209014 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 3 | AUBERRY-1101 | 254151101 | FUSE | D12996 | 20161028 | 635 | 1571451 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6900 | 37.0373 | -119.3344 | METER 1004849097 | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0076402 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1232596 | CAW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | SAND CREEK-1103 | 254601103 | RECLOSER | 7110 | 20161031 | 1757 | 1574185 | 839 | Distribution Circuit | Vegetation | Tree - fell into line | 300 | 89062 | 36.6347 | -118.9966 | MTR# 1006935370 & 7 N/O AND 4 E/O 7995F- CEMETARY RD- ESHOM | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0077088 | OH | Sus | 0 | No | 2016 | OCT | Yes | Line to Line | 1233135 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | OTHER | WIRE DOWN @ MTR# 1010143580 | 20161114 | 2151 | 1581317 | 203 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1003 | 113935 | 36.9636 | -119.4587 | MTR# 1010143580 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0079805 | OH | Sus | 42879698 | No | 2016 | NOV | Yes | Line to Ground | 1235267 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1102 | 254151102 | OCB | 1102/2 | 20161114 | 1550 | 1581092 | 442 | Distribution Circuit | 3rd Party | Vehicle | 1615 | 367527 | 37.0682 | -119.4963 | 1/P/S/W OF TAP LINE D12521 ON MAIN LINE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0079755 | OH | Sus | 0 | No | 2016 | NOV | Yes | Line to Ground | 1235220 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | OTHER | WIRE DOWN 5 SPANS N/ OF C57 TWDS D4502 | 20161127 | 1033 | 1589982 | 326 | Distribution Circuit | Equipment Failure/Involved | Overhead | 277 | 57299 | 37.0742 | -119.4295 | LINE & BUCK 5 SPANS N/ OF C57 | Snow-Overcast-Fog-Drizzle-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0082462 | OH | Sus | 0 | yes | 2016 | NOV | Yes | Line to Ground | 1237206 | CSO | OH | No | Yes
FRESNO | FIELD OPS SOUTH | Tier 3 | AUBERRY-1101 | 254151101 | FUSE | D3816 | 20161128 | 1114 | 1590539 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 640 | 37.0385 | -119.2899 | MTR# 1009535211 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0082737 | OH | Sus | 31285974 | No | 2016 | NOV | Yes | Line to Ground | 1237403 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | FUSE | D4386 | 20161215 | 2315 | 1603933 | 340 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 9180 | 36.9333 | -119.3674 | MTR# 1004659892 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085912 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Line | 1240577 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1103 | 254061103 | TRIP-SAVER | 7991F | 20170112 | 1541 | 1641758 | 289 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1734 | 36.7634 | -118.9421 | 39 P W/OF 7991F | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on object | 17-0008491 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1247859 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1103 | 254061103 | SWITCH | 3043D | 20170115 | 1028 | 1643982 | 149 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 6854 | 36.7858 | -118.9118 | BETWEEN TREE CONNECT 20-21 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0009259 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Ground | 1248526 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | SAND CREEK-1103 | 254601103 | FUSE | 7826F | 20170210 | 255 | 1684466 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 12864 | 36.6845 | -119.1805 | 1 N/OF FEATHER LANE & SQUAW VALLEY RD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019759 | OH | Sus | 42942311 | yes | 2017 | FEB | Yes | Line to Ground | 1257230 | CO | OH | No | Yes
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1102 | 254151102 | RECLOSER | R902 | 20170409 | 216 | 1753246 | 927 | Distribution Circuit | 3rd Party | Vehicle | 783 | 167814 | 37.0347 | -119.5181 | MCKINNEY-RICHARD/408-309-5478: HWY 168 AND GOOSEBERRY | Fog-32-90 F | Pole-Wood | Broken, wire on ground | 17-0038400 | OH | Sus | 0 | No | 2017 | APR | Yes | Three Phase Fault | 1272451 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1102 | 254061102 | RECLOSER | 7360 | 20170718 | 1615 | 1835200 | 1400 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 65 | 13608 | 36.6765 | -119.0165 | 92479- N/OF 92479- 2 W/OF 7624D & MORE | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0063754 | OH | Sus | 0 | No | 2017 | JUL | Yes | Multi-Fault | 1291498 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | FUSE | D5938 | 20170812 | 321 | 1850966 | 423 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 3807 | 37.0659 | -119.4014 | N/W/OF D5938 | Clear-32-90 F | Insulator | Broken, wire on object | 17-0069792 | OH | Sus | 31342211 | No | 2017 | AUG | Yes | Line to Line | 1295627 | INS | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | FUSE | D12537 | 20180106 | 1402 | 3235 | 423 | Distribution Circuit | 3rd Party | Vehicle | 4 | 1692 | 37.0113 | -119.4186 | MTR# 1004254709 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 18-0004044 | OH | Sus | 0 | No | 2018 | JAN | Yes | Line to Line | 1323459 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | SAND CREEK-1103 | 254601103 | JUMPER | OJ @ HARD TAP @ GEORGE SMITH & MAGPIE | 20180311 | 126 | 41809 | 524 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1572 | 36.6915 | -119.2315 | MTR # 1005907836 | Partly Cloudy-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 18-0021629 | OH | Sus | 0 | No | 2018 | MAR | Yes | Open Circuit | 1335185 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER | 7170 | 20180512 | 1901 | 85075 | 511 | Distribution Circuit | Vegetation | Tree - fell into line | 364 | 68247 | 36.7263 | -118.9956 | 4TH THRU 6TH SPAN SOURCE SIDE OF 7971D | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0040553 | OH | Sus | 0 | No | 2018 | MAY | Yes | Three Phase Fault | 1348614 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1102 | 254151102 | FUSE | D8087 | 20180603 | 1556 | 100138 | 527 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 200 | 61540 | 37.0662 | -119.5039 | 1 N OF D8086 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0046767 | OH | Sus | 43361553 | No | 2018 | JUN | Yes | Three Phase Fault | 1353422 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER | 7170 | 20180614 | 1249 | 109231 | 307 | Distribution Circuit | Equipment Failure/Involved | Overhead | 364 | 66160 | 36.7263 | -118.9956 | 2 SP LD SIDE 7247D | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0051037 | OH | Sus | 31396067 | No | 2018 | JUN | Yes | Line to Line | 1356668 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | FUSE | D955 | 20180701 | 2053 | 122580 | 319 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 13717 | 37.0791 | -119.4166 | D8625 4 SPANS TO THE SOUTH | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0056129 | OH | Sus | 31398584 | No | 2018 | JUL | Yes | Line to Ground | 1360932 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 3 | AUBERRY-1101 | 254151101 | FUSE | D12994 | 20180705 | 649 | 124683 | 439 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 3951 | 37.0415 | -119.3433 | MTR 1004849113 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0057073 | OH | Sus | 43389112 | No | 2018 | JUL | Yes | Line to Ground | 1361578 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | KERCKHOFF-1101 | 252561101 | FUSE | D7588 | 20180911 | 21 | 172011 | 302 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 8598 | 37.0965 | -119.4994 | SOURCE SIDE OF CGC# 418566064554 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0078381 | OH | Sus | 43461957 | No | 2018 | SEP | Yes | Line to Ground | 1377003 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | TIVY VALLEY-1107 | 252941107 | JUMPER | WIRE DOWN3P/E/OF 89845 | 20181024 | 1412 | 201674 | 121 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1074 | 122492 | 36.7263 | -119.2289 | 3P/E/OF 89845 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0093849 | OH | Sus | 0 | No | 2018 | OCT | Yes | Line to Ground | 1387968 | CO | OH | No | Yes
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1103 | 254061103 | FUSE | 3741F | 20181130 | 1738 | 230544 | 541 | Distribution Circuit | Animal | Other | 12 | 3142 | 36.7266 | -119.0972 | 1P N/OF MTR# 1008867366 | Partly Cloudy-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 18-0105717 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Line | 1396669 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | SHEPHERD-2111 | 252062111 | FUSE | D7929 | 20190108 | 109 | 260069 | 539 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 23074 | 36.9851 | -119.6 | 3 POLES S/OF D12307 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0006071 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1404385 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | FUSE | D7447 | 20190203 | 417 | 288477 | 689 | Distribution Circuit | Vegetation | Tree - fell into line | 113 | 42259 | 36.9756 | -119.367 | D8064 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0017470 | OH | Sus | 31424562 | yes | 2019 | FEB | Yes | Line to Ground | 1411885 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | RECLOSER | R2845 | 20190221 | 812 | 320317 | 1084 | Distribution Circuit | Vegetation | Tree - fell into line | 976 | 209099 | 37.0536 | -119.4614 | SS OF D2385 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0026774 | OH | Sus | 31426226 | yes | 2019 | FEB | Yes | Line to Ground | 1419395 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 3 | AUBERRY-1101 | 254151101 | FUSE | D320 | 20190305 | 452 | 331163 | 453 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 6081 | 37.0379 | -119.3363 | FULL- LARAMIE/559-317-8357: beyond D328 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0030646 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1421956 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | JUMPER | WIRE DOWN S/OF CGC# 419083359509 | 20190305 | 1432 | 331874 | 636 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2544 | 36.9647 | -119.3151 | S/OF CGC# 419083359509 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0030994 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Line | 1422104 | CO | OH | No | Yes
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | RECLOSER | R2578 | 20190310 | 1629 | 335616 | 436 | Distribution Circuit | 3rd Party | Vehicle | 1364 | 182548 | 37.0177 | -119.4272 | 28717 BURROUGH VALLEY RD- AUBERRY- MAINLINE POLE WAS HIT | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0032433 | OH | Sus | 0 | No | 2019 | MAR | Yes | Line to Line | 1423112 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1102 | 254061102 | FUSE | 7068F | 20190430 | 1001 | 371123 | 663 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6630 | 36.7218 | -118.8891 | 5 LD SIDE OF 7068F | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0047605 | OH | Sus | 0 | No | 2019 | APR | Yes | Line to Ground | 1433728 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | FUSE | D2995 | 20190510 | 413 | 377592 | 614 | Distribution Circuit | Vegetation | Tree - branch fell on line | 129 | 62038 | 37.0061 | -119.4065 | 3P/SW/OF D12182 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0050618 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1435768 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 3 | AUBERRY-1101 | 254151101 | FUSE | D5466 | 20190510 | 359 | 377587 | 661 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 3062 | 37.0453 | -119.3299 | MTR# 1009000731 | Partly Cloudy-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0050619 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1435769 | CAW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 3 | AUBERRY-1101 | 254151101 | FUSE | D12996 | 20190510 | 658 | 377689 | 644 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5646 | 37.0373 | -119.3344 | E/OF CGC 419027061925 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0050761 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1435899 | CO | OH | No | Yes
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1102 | 254151102 | FUSE | D2095 | 20190510 | 41 | 377494 | 913 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 10375 | 37.0681 | -119.504 | 32752 FRASIER RD | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0050599 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1435746 | PW | OH | No | Yes
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1102 | 254151102 | FUSE | D2828 | 20190510 | 447 | 377602 | 903 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 18060 | 37.0343 | -119.4674 | MTR# 1009244366 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0050641 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Line | 1435791 | CAW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | OTHER | WIRE DOWN 1 POLE/N/OF D12560 | 20190518 | 914 | 384135 | 402 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 419 | 43061 | 36.969 | -119.491 | 1 POLE N/OF D12560 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053629 | OH | Sus | 31442269 | yes | 2019 | MAY | Yes | Line to Ground | 1437874 | CO | OH | No | Yes
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1102 | 254151102 | FUSE | D7755 | 20190519 | 909 | 385002 | 498 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 13446 | 37.0427 | -119.5007 | 4 P E/OF D7755 | Overcast-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0053921 | OH | Sus | 31442850 | yes | 2019 | MAY | Yes | Line to Ground | 1438130 | CAW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | FUSE | D12556 | 20190729 | 1804 | 474979 | 471 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 6846 | 36.9644 | -119.4663 | 1 N/OF AND 1 W/OF D12556 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 19-0082368 | OH | Sus | 43900478 | No | 2019 | JUL | Yes | Line to Ground | 1459480 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1102 | 254151102 | OCB | 1102/2 | 20190901 | 1308 | 550432 | 312 | Distribution Circuit | Vegetation | Tree - fell into line | 1637 | 16672 | 37.0682 | -119.4963 | CGC# 418518663077- 33438 CALKINS RD- AUBERRY CA | Clear-32-90 F | Pole-Wood | Broken, wire on object | 19-0094452 | OH | Sus | 0 | No | 2019 | SEP | Yes | Line to Ground | 1467087 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 3 | AUBERRY-1101 | 254151101 | RECLOSER | 176050 | 20200317 | 112 | 856158 | 915 | Distribution Circuit | Equipment Failure/Involved | Overhead | 175 | 104108 | 37.053 | -119.3706 | W/OF D326 | Partly Cloudy-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0033115 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Ground | 1522260 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | SAND CREEK-1103 | 254601103 | OTHER | WIRE DOWN 1 S/LD SIDE MTR#1008713672 | 20200406 | 741 | 883943 | 379 | Distribution Circuit | Environmental/External | Ice or snow | 72 | 24675 | 36.6524 | -118.9575 | 1P LD SIDE OF MTR# 1008713672 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0038871 | OH | Sus | 44282804 | yes | 2020 | APR | Yes | Line to Ground | 1525661 | CO | OH | No | Yes
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER | 7040 | 20200506 | 1550 | 908377 | 171 | Distribution Circuit | Vegetation | Tree - fell into line | 408 | 69768 | 36.7388 | -119.1217 | 2 P W/OF 267155 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0047911 | OH | Sus | 44312137 | No | 2020 | MAY | Yes | Line to Ground | 1531152 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1102 | 254061102 | OTHER | WIRE DOWN 1 N/OF 58509 | 20200518 | 146 | 915578 | 384 | Distribution Circuit | Environmental/External | Lightning | 65 | 23503 | 36.6518 | -119.0023 | AT POLE N/OF 58509 | Overcast-Fog-Drizzle-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0051100 | OH | Sus | 0 | yes | 2020 | MAY | Yes | Line to Ground | 1533019 | CSO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 3 | AUBERRY-1101 | 254151101 | FUSE | D12992 | 20200519 | 1326 | 917663 | 373 | Distribution Circuit | 3rd Party | Vehicle | 2 | 746 | 37.0553 | -119.3624 | 3 P W/OF D12992 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 20-0051890 | OH | Sus | 0 | No | 2020 | MAY | Yes | Line to Line | 1533411 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 3 | AUBERRY-1101 | 254151101 | FUSE | D2385 | 20200604 | 2127 | 931260 | 531 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 11903 | 37.0552 | -119.3614 | MTR# 1004849157 & 1 SE/OF MTR# 1004849157 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0057926 | OH | Sus | 31505085 | yes | 2020 | JUN | Yes | Line to Line | 1537290 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | SAND CREEK-1103 | 254601103 | RECLOSER | 7070 | 20200813 | 1334 | 996336 | 226 | Distribution Circuit | Equipment Failure/Involved | Overhead | 295 | 66670 | 36.6481 | -119.1491 | 53730 DRUM VALLEY RD MTR 1005062139 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0083157 | OH | Sus | 44435270 | yes | 2020 | AUG | Yes | Line to Line | 1553978 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | FUSE | D2994 | 20201228 | 223 | 1199749 | 847 | Distribution Circuit | 3rd Party | Vehicle | 60 | 11939 | 37.0325 | -119.4427 | E/OF LINE AND BUCK 2 P/N/OF CGC 418718262010 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 20-0132016 | OH | Sus | 0 | No | 2020 | DEC | Yes | Line to Line | 1589742 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | SWITCH | 335 | 20210208 | 1237 | 1250787 | 142 | Distribution Circuit | Equipment Failure/Involved | Overhead | 763 | 108346 | 37.0667 | -119.4244 | 2 SPANS E/OF SW 718 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0023107 | OH | Sus | 0 | No | 2021 | FEB | Yes | Line to Ground | 1603812 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-0001 | 254060001 | JUMPER | 7050 | 20210212 | 708 | 1253522 | 463 | Distribution Circuit | Equipment Failure/Involved | Overhead | 294 | 112117 | 36.6985 | -119.0118 | 2 W/OF 7172 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0024945 | OH | Sus | 44651922 | No | 2021 | FEB | Yes | Open Circuit | 1604834 | CO | OH | No | Yes
FRESNO | FIELD OPS SOUTH | Tier 2 | SAND CREEK-1103 | 254601103 | FUSE | 7955F | 20210304 | 829 | 1268161 | 901 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2703 | 36.6215 | -118.9633 | 2 POLES E/OF FUCO 7955F | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0032366 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1609659 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | FUSE | D3738 | 20210306 | 2313 | 1272648 | 234 | Distribution Circuit | Equipment Failure/Involved | Overhead | 62 | 14508 | 37.0773 | -119.4322 | 41838 MERRIMAN LANE | Clear-32-90 F | Other | Broken, wire on object | 21-0033114 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1610168 | NON | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | FUSE | D4387 | 20210618 | 253 | 1377088 | 807 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 29052 | 36.9285 | -119.3581 | 21 S/OF D4387 | Strong Winds- | Pole-Wood | Broken, wire on ground | 21-0075982 | OH | Sus | 0 | No | 2021 | JUN | Yes | Line to Ground | 1638371 | PW | OH | No | Yes
FRESNO | FIELD OPS SOUTH | Tier 2 | BALCH NO 1-1101 | 252501101 | RECLOSER | 105414 LINE RECLOSER | 20210618 | 405 | 1377177 | 640 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 16000 | 36.9083 | -119.0863 | 2 LOADSIDE OF 105414 | Strong Winds- | Insulator | Broken, wire on ground | 21-0075958 | OH | Sus | 0 | No | 2021 | JUN | Yes | Line to Line | 1638361 | INS | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | SAND CREEK-1103 | 254601103 | RECLOSER | 45190 | 20210710 | 1305 | 1398001 | 255 | Distribution Circuit | Vegetation | Tree - fell into line | 522 | 19492 | 36.6921 | -119.154 | CGC # 419664149373 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0087472 | OH | Sus | 0 | No | 2021 | JUL | Yes | Force Out | 1646908 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1102 | 254061102 | RECLOSER | 7050 | 20210828 | 736 | 1456189 | 532 | Distribution Circuit | Vegetation | Tree - fell into line | 308 | 109978 | 36.698 | -119.011 | 3 S/OF 7167 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0110520 | OH | Sus | 31550651 | No | 2021 | AUG | Yes | Line to Line | 1661679 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | SAND CREEK-1103 | 254601103 | FUSE | 7825F | 20211223 | 1104 | 1579852 | 269 | Distribution Circuit | 3rd Party | Vehicle | 25 | 6725 | 36.6832 | -119.1864 | CGC# 419449449344- 6P NORTHWEST OF 7825F- 37171 MISTLETOE RD | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0160285 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1697725 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1102 | 254151102 | OCB | 1102/2 | 20220814 | 234 | 1780494 | 385 | Distribution Circuit | 3rd Party | Vehicle | 1658 | 459782 | 37.0682 | -119.4963 | D12524 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0097270 | OH | Sus | 0 | No | 2022 | AUG | Yes | Multi-Fault | 1760108 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1102 | 254151102 | RECLOSER | 37466 | 20221204 | 707 | 1875660 | 508 | Distribution Circuit | Equipment Failure/Involved | Overhead | 407 | 133002 | 37.0118 | -119.5269 | D9402 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0136411 | OH | Sus | 45579786 | No | 2022 | DEC | Yes | Line to Line | 1787360 | CO | OH | No | Yes
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1103 | 254061103 | RECLOSER | 7080 | 20221211 | 533 | 1885124 | 722 | Distribution Circuit | Vegetation | Tree - fell into line | 280 | 202160 | 36.7424 | -118.9595 | 25 LD SIDE OF 7080 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138823 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1789651 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | DUNLAP-1102 | 254061102 | JUMPER | SOUTH PHASE DOWN 1 E/OF 26D | 20230118 | 1532 | 1961192 | 138 | Distribution Circuit | Equipment Failure/Involved | Overhead | 52 | 6360 | 36.7243 | -118.9671 | 1 E/OF 26D | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0018509 | OH | Sus | 0 | No | 2023 | JAN | Yes | Open Circuit | 1806613 | CO | OH | No | Yes
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | RECLOSER | R2845 | 20230305 | 1909 | 2024118 | 1294 | Distribution Circuit | Vegetation | Tree - branch fell on line | 841 | 333663 | 37.0539 | -119.4608 | PATTON- LANDON 559-573-5990: EOL beyond D326 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0040454 | OH | Sus | 45680925 | No | 2023 | MAR | Yes | Line to Ground | 1822205 | CO | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1102 | 254151102 | RECLOSER | R2850 | 20230316 | 2116 | 2049329 | 419 | Distribution Circuit | 3rd Party | Vehicle | 225 | 15295 | 37.0349 | -119.5239 | D12943 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0047269 | OH | Sus | 0 | No | 2023 | MAR | Yes | Multi-Fault | 1826731 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | RECLOSER | R2845 | 20231003 | 722 | 2233384 | 620 | Distribution Circuit | 3rd Party | Vehicle | 843 | 180780 | 37.0539 | -119.4608 | JOHNSON- MASON: Highway 168 and Beal fire road | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0123620 | OH | Sus | 35493319 | No | 2023 | OCT | Yes | Line to Line | 1878746 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | TIVY VALLEY-1107 | 252941107 | RECLOSER | 869946 | 20231010 | 1406 | 2240063 | 481 | Distribution Circuit | 3rd Party | Vehicle | 287 | 25867 | 36.8168 | -119.3407 | 3 POLES LD SIDE OF CGC 419122952957 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0126627 | OH | Sus | 35495454 | No | 2023 | OCT | Yes | Line to Line | 1881002 | PW | OH | No | No
FRESNO | FIELD OPS SOUTH | Tier 2 | AUBERRY-1101 | 254151101 | OTHER | CARPOLE 2-PHASES WIRE DOWN HOT | 20231022 | 115 | 2248693 | 901 | Distribution Circuit | 3rd Party | Vehicle | 16 | 11914 | 37.08 | -119.4499 | CGC# 418693363680 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0130982 | OH | Sus | 0 | No | 2023 | OCT | Yes | Line to Ground | 1883945 | PW | OH | No | Yes
FRESNO | FIELD OPS SOUTH | Tier 2 | SAND CREEK-1103 | 254601103 | FUSE | 3398F | 20231223 | 700 | 2298675 | 132 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 660 | 36.6925 | -119.251 | 33703 WOLVERINE LN | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0148649 | OH | Sus | 46099568 | No | 2023 | DEC | Yes | Line to Ground | 1899709 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | OTHER |  | 20130101 | 925 | 723998 | 755 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3020 | 39.8103 | -123.791 | 114959017799 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0001556 | OH | Sus | 41832824 | No | 2013 | JAN | Yes | None | 99306202 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | FUSE | 1415 | 20130107 | 2057 | 726895 | 793 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 7137 | 38.9147 | -123.2662 | 2 SPANS SOURCESIDE OF MTR1008390924 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0002663 | OH | Sus | 0 | No | 2013 | JAN | Yes | Three Phase Fault | 99305458 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | OTHER |  | 20130108 | 1125 | 727085 | 233 | Distribution Circuit | Vegetation | Tree - branch fell on line | 460 | 59972 | 40.793 | -124.0214 | 114406253813 | Partly cloudy-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0002799 | OH | Sus | 41835354 | No | 2013 | JAN | Yes |  | 99305375 | CSO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 8652 | 20130116 | 2245 | 730923 | 485 | Distribution Circuit | Equipment Failure/Involved | Other | 255 | 5457 | 40.1065 | -123.928 | at FUCO 2595 SS ON MAINLINE | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0004683 | OH | Sus | 30971728 | No | 2013 | JAN | Yes | Line to Ground | 99304319 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 3079 | 20130117 | 1318 | 731161 | 787 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 35 | 27545 | 40.7987 | -123.4049 | 116254653534 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0004888 | OH | Sus | 41842131 | No | 2013 | JAN | Yes | Line to Line | 99304220 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UKIAH-1115 | 42771115 | FUSE | 3391 | 20130128 | 1237 | 735608 | 353 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 8825 | 39.1408 | -123.1717 | SILVER/3461: 2 SPANS FROM 3391 TOWARDS END OF LINE-CRANE TERRACE | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0006571 | OH | Sus | 30973747 | No | 2013 | JAN | Yes | Line to Ground | 99302999 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UPPER LAKE-1101 | 42871101 | RECLOSER | 1276 | 20130203 | 714 | 737892 | 385 | Distribution Circuit | Equipment Failure/Involved | Other | 446 | 49257 | 39.1574 | -122.9904 | 7170 SCOTTS VALLEY ROAD LAKEPORT | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0007755 | OH | Sus | 41848484 | No | 2013 | FEB | Yes | Line to Ground | 99302303 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 1767 | 20130205 | 1411 | 738750 | 319 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 8 | 2552 | 39.6705 | -123.7785 | 1 SPAN LOAD SIDE OF FUCO 1767 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0008251 | OH | Sus | 0 | No | 2013 | FEB | Yes | Line to Ground | 99302037 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3909 | 20130205 | 958 | 738588 | 325 | Distribution Circuit | Equipment Failure/Involved | Other | 29 | 9425 | 39.3997 | -123.7151 | 20 SPANS LOAD SIDE OF FUCO 3909 | Overcast-32 - 90 F | Crossarm, Wood | Broken, wire on object | 13-0008104 | OH | Sus | 0 | No | 2013 | FEB | Yes | None | 99302068 | CAW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1801 | 20130207 | 1940 | 739748 | 710 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 8510 | 40.058 | -123.9807 | 114443026993 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0008798 | OH | Sus | 41850314 | No | 2013 | FEB | Yes | Line to Ground | 99301690 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 3304 | 20130219 | 647 | 743681 | 409 | Distribution Circuit | Vegetation | Tree - fell into line | 620 | 140991 | 41.1057 | -123.6882 | GOODMAN-BILL: upper cappell rd | Sleet or ice-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0010686 | OH | Sus | 0 | yes | 2013 | FEB | Yes |  | 99300399 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARRIS-1109 | 192431109 | FUSE | 819 | 20130223 | 1659 | 746734 | 369 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 9594 | 40.7709 | -124.1182 | 114134853062 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0012073 | OH | Sus | 41858095 | No | 2013 | FEB | Yes | Line to Line | 99299553 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | SWITCH | 7439 | 20130305 | 1714 | 751874 | 620 | Distribution Circuit | Equipment Failure/Involved | Other | 558 | 67143 | 38.8005 | -123.5731 | 215511041756 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0014329 | OH | Sus | 0 | yes | 2013 | MAR | Yes | Line to Ground | 99297897 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 5819 | 20130305 | 2232 | 752051 | 770 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3080 | 38.8315 | -123.6191 | 1 SPAN EAST OF FUCO 5819 AND 1 SPAN WEST OF FUCO 5819 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0014389 | OH | Sus | 0 | yes | 2013 | MAR | Yes |  | 99297890 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | SWITCH | WDB4 | 20130306 | 1256 | 752889 | 304 | Distribution Circuit | Environmental/External | Ice or snow | 5 | 881 | 40.4485 | -123.5284 | 1 S/OF 4137 | Heavy rain-32 - 90 F | Conductor, Overhead | On Ground | 13-0014647 | OH | Sus | 0 | yes | 2013 | MAR | Yes | Line to Ground | 99297731 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | SWITCH | WDB4 | 20130306 | 652 | 752901 | 983 | Distribution Circuit | Equipment Failure/Involved | Other | 19 | 18677 | 40.4654 | -123.528 | 12 SPANS PAST FUSES | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0014654 | OH | Sus | 0 | yes | 2013 | MAR | Yes | Line to Ground | 99297730 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | FUSE | 4157 | 20130306 | 1704 | 753022 | 501 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3006 | 40.4085 | -123.4702 | MM 7.0 HWY 36 | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0014784 | OH | Sus | 0 | yes | 2013 | MAR | Yes | None | 99297704 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | RECLOSER | 83354 | 20130306 | 135 | 752248 | 677 | Distribution Circuit | Vegetation | Tree - fell into line | 367 | 85681 | 38.8809 | -123.6619 | WILLIAMS- MIKE/3454: 34010 S HWY 1 / 1 SP S/S 4411 TWDS DISC 9287 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0014433 | OH | Sus | 0 | yes | 2013 | MAR | Yes | Three Phase Fault | 99297879 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | FUSE | 3729 | 20130311 | 744 | 755033 | 376 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 752 | 40.2821 | -123.8725 | 114790035074 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0015548 | OH | Sus | 0 | No | 2013 | MAR | Yes | Line to Ground | 99297052 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOPLAND-1101 | 42251101 | FUSE | 2901 | 20130322 | 1841 | 760542 | 773 | Distribution Circuit | Equipment Failure/Involved | Other | 16 | 12368 | 38.9577 | -123.1144 | MTR# 485A85 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0018561 | OH | Sus | 30984988 | No | 2013 | MAR | Yes |  | 99295093 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1260 | 20130323 | 903 | 760765 | 632 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 29206 | 39.1295 | -123.7111 | MAIN LINE 1 SPAN FROM 8623 TWDS 427 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0018660 | OH | Sus | 30985064 | No | 2013 | MAR | Yes | Multi-Fault | 99295024 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 4439 | 20130326 | 1314 | 761977 | 403 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 6851 | 38.7951 | -123.5663 | WILLIAMS- MIKE/3454: MM 3.59 at 46701 COLLINS LANDING RD / 5 SPANS L/S C/O 4439 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0019271 | OH | Sus | 0 | No | 2013 | MAR | Yes |  | 99294558 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | SECTIONALIZER | 6064 | 20130327 | 1641 | 762580 | 370 | Distribution Circuit | Equipment Failure/Involved | Other | 62 | 22940 | 40.2952 | -123.8204 | 114922635878 | Partly cloudy-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0019616 | OH | Sus | 41874400 | No | 2013 | MAR | Yes | Line to Ground | 99294347 | CSO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2505 | 20130404 | 733 | 766358 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 188 | 22891 | 40.307 | -124.2967 | 113573635960 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0021364 | OH | Sus | 30987365 | No | 2013 | APR | Yes |  | 99292934 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 37202 | 20130406 | 34 | 767297 | 580 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 35380 | 41.1887 | -123.7087 | 115181268660 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0021922 | OH | Sus | 30987755 | No | 2013 | APR | Yes | Multi-Fault | 99292603 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 2213 | 20130407 | 2328 | 769283 | 860 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 6880 | 39.3491 | -123.7849 | 4 SPANS LD FUCO 2213 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0022281 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Ground | 99292256 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | SWITCH | 5989 | 20130407 | 2138 | 768703 | 964 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 48095 | 39.4074 | -123.7339 | 215137563778 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022170 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Ground | 99292331 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MAPLE CREEK-1101 | 192101101 | OCB | OCB | 20130407 | 2106 | 767878 | 684 | Distribution Circuit | Vegetation | Tree - fell into line | 145 | 30636 | 40.7678 | -123.874 | 114822552618 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0022076 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Ground | 99292370 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 5415 | 20130410 | 1822 | 772619 | 467 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 21 | 9807 | 39.3709 | -123.3593 | 4001 MUIR MILL RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0023512 | OH | Sus | 41880979 | No | 2013 | APR | Yes | Line to Line | 99291245 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MIDDLETOWN-1102 | 43141102 | FUSE | 90509 | 20130412 | 1230 | 773714 | 342 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 684 | 38.7688 | -122.5896 | 5 SPANS LOAD SIDE OF FUCO 90509 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0024000 | OH | Sus | 0 | No | 2013 | APR | Yes | Line to Ground | 99290919 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | OTHER |  | 20130416 | 1643 | 776636 | 544 | Distribution Circuit | Vegetation | Tree - branch fell on line | 184 | 85189 | 40.3254 | -123.9235 | 114641936756 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0025048 | OH | Sus | 41884870 | yes | 2013 | APR | Yes | Line to Ground | 99290146 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3911 | 20130417 | 1939 | 777483 | 591 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2955 | 39.3598 | -123.656 | 6 SPANS LD SIDE OF 3911 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0025396 | OH | Sus | 30990238 | yes | 2013 | APR | Yes | Line to Line | 99289846 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER |  | 20130417 | 1854 | 777496 | 474 | Distribution Circuit | Vegetation | Tree - branch fell on line | 808 | 235732 | 40.1224 | -123.8356 | BET LR 1510 AND 54634 ON THE MAINLINE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0025393 | OH | Sus | 41885314 | yes | 2013 | APR | Yes |  | 99289800 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 3304 | 20130418 | 1010 | 777689 | 1038 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 620 | 563908 | 41.1057 | -123.6882 | 115362468134 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0025527 | OH | Sus | 30990318 | No | 2013 | APR | Yes |  | 99289621 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | OTHER |  | 20130423 | 806 | 780005 | 526 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 526 | 38.6893 | -122.6707 | 18475 IDA CLAYTON | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0026581 | OH | Sus | 30991660 | yes | 2013 | APR | Yes | None | 99288959 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HIGHLANDS-1104 | 43361104 | FUSE | 1023 | 20130429 | 1030 | 783337 | 500 | Distribution Circuit | Vegetation | Tree - fell into line | 279 | 88500 | 38.9215 | -122.5945 | Stone/3466: at MTR 1009542162 (7 SPANS BEYOND COMBO'S 1023) | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0027957 | OH | Sus | 30993088 | No | 2013 | APR | Yes |  | 99287931 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UKIAH-1114 | 42771114 | FUSE | 3347 | 20130429 | 1732 | 783627 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 9792 | 39.1248 | -123.2838 | 3 SPANS LOAD SIDE OF 3347 | Clear-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 13-0028111 | OH | Sus | 30993208 | No | 2013 | APR | Yes | Line to Ground | 99287879 | CAW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 6084 | 20130430 | 1816 | 784409 | 599 | Distribution Circuit | Vegetation | Tree - fell into line | 130 | 20012 | 40.0617 | -123.962 | 114550025842 | Partly cloudy-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 13-0028430 | OH | Sus | 30993466 | yes | 2013 | APR | Yes | Multi-Fault | 99287580 | CAW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | REDBUD-1101 | 43191101 | FUSE | 58855 | 20130501 | 243 | 784717 | 437 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 874 | 39.0291 | -122.5865 | MID SPAN ON 1 SPAN TAP | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0028499 | OH | Sus | 41891243 | yes | 2013 | MAY | Yes | Line to Line | 99287560 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | RECLOSER | 4622 | 20130502 | 2202 | 786084 | 465 | Distribution Circuit | Vegetation | Tree - branch fell on line | 372 | 172980 | 39.5149 | -123.764 | 8 SPANS LD SIDE OF 4622 ON MAINLINE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0029125 | OH | Sus | 30994004 | No | 2013 | MAY | Yes | Three Phase Fault | 99287054 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | FUSE | 1961 | 20130502 | 1658 | 785966 | 410 | Distribution Circuit | 3rd Party | Vehicle | 6 | 2460 | 39.4036 | -123.1214 | 21501 RIDGEWAY HWY TWDS EOL | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0029070 | OH | Sus | 30993993 | No | 2013 | MAY | Yes | None | 99287150 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | OCB | OCB | 20130504 | 1757 | 786999 | 425 | Distribution Circuit | Equipment Failure/Involved | Other | 755 | 85835 | 40.2864 | -123.8374 | 114896335604 | Strong winds-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0029486 | OH | Sus | 41892792 | yes | 2013 | MAY | Yes |  | 99286827 | CSO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 3304 | 20130504 | 1639 | 786946 | 1820 | Distribution Circuit | Vegetation | Tree - fell into line | 620 | 985622 | 41.1057 | -123.6882 | 115457169230 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0029471 | OH | Sus | 30994500 | yes | 2013 | MAY | Yes | Three Phase Fault | 99286771 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 2497 | 20130504 | 1620 | 786927 | 676 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 25012 | 39.6728 | -123.5127 | MTR#59J425- 44050 BRIGGS LANE- LAYTONVILLE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0029481 | OH | Sus | 41892789 | yes | 2013 | MAY | Yes | Line to Line | 99286830 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 5695 | 20130509 | 917 | 790453 | 593 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 21941 | 40.7901 | -123.4429 | 116070053353 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0030767 | OH | Sus | 30995451 | No | 2013 | MAY | Yes | Three Phase Fault | 99285779 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER 1101 | 192381101 | FUSE | 1913 | 20130524 | 811 | 797916 | 1810 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 14480 | 40.4488 | -124.2666 | 113716741445 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0034276 | OH | Sus | 0 | No | 2013 | MAY | Yes | Line to Ground | 99283434 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | RECLOSER | 2600 | 20130527 | 1129 | 799068 | 640 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 23078 | 39.0852 | -123.4853 | GALLETTI- TIM: tree top fell into line 4 spans from FUCO 895 TWDS LR 2600 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0034563 | OH | Sus | 41904109 | yes | 2013 | MAY | Yes | Line to Line | 99283152 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3905 | 20130528 | 125 | 799418 | 500 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 500 | 39.3098 | -123.7949 | 1ST SPAN LD SIDE OF 3905 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0034631 | OH | Sus | 30998949 | No | 2013 | MAY | Yes | Line to Ground | 99283064 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HIGHLANDS-1103 | 43361103 | FUSE | 4859 | 20130602 | 450 | 802398 | 705 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 5285 | 38.8505 | -122.5625 | AT MTR # 1008033390 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0035900 | OH | Sus | 31000244 | No | 2013 | JUN | Yes | Line to Ground | 99282288 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 3025 | 20130603 | 1531 | 803346 | 594 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 15210 | 40.8111 | -123.4846 | 115881554236 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0036232 | OH | Sus | 41906730 | No | 2013 | JUN | Yes |  | 99282039 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | OTHER |  | 20130612 | 2127 | 809617 | 425 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 1310 | 39.2248 | -123.7625 | 1 SPAN SOURCE SIDE OF MTR # 1009747149 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0039186 | OH | Sus | 41912560 | No | 2013 | JUN | Yes | Line to Ground | 99280118 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 37202 | 20130615 | 1319 | 810949 | 591 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 51 | 30141 | 41.1887 | -123.7087 | HWY 169 at MM 31.87 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0039943 | OH | Sus | 31003125 | No | 2013 | JUN | Yes | Line to Ground | 99279694 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1102 | 43311102 | OCB | OCB | 20130615 | 1717 | 811053 | 536 | Distribution Circuit | 3rd Party | Vehicle | 2848 | 256080 | 38.9326 | -122.741 | 17 SPANS LOAD SIDE OF LR 716- MM 25.82 | Clear-32 - 90 F | Pole-Wood | Broken, wire on object | 13-0039967 | OH | Sus | 31003132 | No | 2013 | JUN | Yes | Three Phase Fault | 99279637 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | FUSE | 5399 | 20130620 | 1438 | 813798 | 272 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 1904 | 40.8166 | -124.0285 | 114405954711 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0041271 | OH | Sus | 41916917 | No | 2013 | JUN | Yes |  | 99278854 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3219 | 20130621 | 1202 | 814251 | 285 | Distribution Circuit | Equipment Failure/Involved | Other | 40 | 12520 | 41.0327 | -123.6668 | 115402662327 | Clear-32 - 90 F | Insulator | Broken, wire on ground | 13-0041526 | OH | Sus | 31004256 | No | 2013 | JUN | Yes |  | 99278661 | INS | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 2981 | 20130624 | 1847 | 816456 | 398 | Distribution Circuit | Vegetation | Tree - branch fell on line | 61 | 24278 | 39.4809 | -123.7871 | 1ST SPAN LD SIDE OF 2981 AT 32530 FOREST LANE IN FT BRAGG | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0042312 | OH | Sus | 41918070 | yes | 2013 | JUN | Yes | Line to Ground | 99278149 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | RECLOSER | 23444 | 20130625 | 1555 | 817258 | 460 | Distribution Circuit | Vegetation | Tree - branch fell on line | 164 | 21245 | 38.8487 | -123.6437 | ON MAINLINE PASS 8177 TWDS 3661 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0042665 | OH | Sus | 31005252 | yes | 2013 | JUN | Yes | Line to Line | 99277936 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 3273 | 20130627 | 1723 | 818728 | 79 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 553 | 39.1938 | -123.7233 | 11 SPANS LOAD SIDE OF 3273 (30751 NAVARRO RIVER RD) | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0043241 | OH | Sus | 31005805 | yes | 2013 | JUN | Yes | Line to Ground | 99277534 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 893 | 20130628 | 924 | 819199 | 579 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1737 | 39.0574 | -123.4508 | 2 SPANS LOAD SIDE OF 893 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0043403 | OH | Sus | 41919619 | yes | 2013 | JUN | Yes | Line to Ground | 99277356 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 7155 | 20130702 | 2359 | 824491 | 354 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 32922 | 41.0509 | -123.6675 | 115408462977 | Heat wave-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0044846 | OH | Sus | 0 | yes | 2013 | JUL | Yes | Three Phase Fault | 99276238 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | RECLOSER | 37222 | 20130702 | 342 | 823408 | 834 | Distribution Circuit | Equipment Failure/Involved | Other | 147 | 122598 | 38.914 | -123.2725 | ESPINOLA/3430: 7 spans ss cap4652 twds 37222 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0044493 | OH | Sus | 41921034 | yes | 2013 | JUL | Yes | Multi-Fault | 99276415 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1103 | 43351103 | RECLOSER | 630 | 20130718 | 2140 | 833958 | 362 | Distribution Circuit | Equipment Failure/Involved | Other | 1576 | 332899 | 39.1186 | -122.8327 | 1 SPAN MAIN LINE SS FUCO 1541 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0048524 | OH | Sus | 0 | No | 2013 | JUL | Yes |  | 99273523 | CSO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 5209 | 20130726 | 652 | 838712 | 309 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 36 | 5982 | 41.0953 | -123.6953 | 115358164690 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0050261 | OH | Sus | 31011135 | No | 2013 | JUL | Yes | Line to Line | 99272246 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 5233 | 20130727 | 2140 | 839626 | 618 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 23196 | 39.2281 | -123.7661 | 10 POLES LD SIDE OF 5233 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0050641 | OH | Sus | 31011423 | No | 2013 | JUL | Yes | Line to Line | 99271978 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | OTHER |  | 20130727 | 2150 | 839683 | 733 | Distribution Circuit | Vegetation | Tree - fell into line | 538 | 353466 | 41.191 | -123.6875 | 115362468134 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0050649 | OH | Sus | 31011426 | No | 2013 | JUL | Yes | Line to Ground | 99271974 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MAPLE CREEK-1101 | 192101101 | FUSE | 6529 | 20130805 | 312 | 843108 | 468 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1404 | 40.7487 | -123.8677 | 7 SPANS LOAD SIDE OF FUCO 6529 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0052313 | OH | Sus | 41937863 | No | 2013 | AUG | Yes | Line to Line | 99270967 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 8575 | 20130810 | 1430 | 846172 | 218 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 5014 | 39.4209 | -123.7807 | 1 SPAN LD SIDE OF 8575 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0053801 | OH | Sus | 0 | No | 2013 | AUG | Yes | Line to Line | 99270012 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | OCB | OCB | 20130816 | 1946 | 849954 | 986 | Distribution Circuit | Vegetation | Tree - fell into line | 371 | 53414 | 40.2863 | -123.8376 | 114704636027 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0055285 | OH | Sus | 31015454 | No | 2013 | AUG | Yes | Line to Ground | 99268877 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HIGHLANDS-1103 | 43361103 | RECLOSER | 520 | 20130816 | 747 | 849389 | 209 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 842 | 166078 | 38.8824 | -122.5913 | SS OF FUCO 6511 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0055049 | OH | Sus | 41944510 | No | 2013 | AUG | Yes | Line to Line | 99269030 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1770 | 20130818 | 1620 | 850559 | 85 | Distribution Circuit | Equipment Failure/Involved | Other | 340 | 10014 | 39.9155 | -123.7638 | 115059321699 | Clear-Above 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0055469 | OH | Sus | 41944869 | No | 2013 | AUG | Yes | Line to Ground | 99268716 | CSO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8947 | 20130824 | 1446 | 855110 | 614 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3070 | 39.6459 | -123.7488 | 2 POLES LD SIDE OF 8947 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0057271 | OH | Sus | 41947220 | No | 2013 | AUG | Yes | Line to Line | 99267307 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 4451 | 20130914 | 851 | 866003 | 649 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 4543 | 38.7905 | -123.5103 | 2 SPANS LOAD SIDE OF FUCO 4451 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0062016 | OH | Sus | 31021372 | No | 2013 | SEP | Yes | Line to Line | 99264013 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 826 | 20130920 | 1817 | 869554 | 576 | Distribution Circuit | Equipment Failure/Involved | Other | 1808 | 405507 | 39.4204 | -123.36 | GALLETTI- TIM: Wire down 1 span beyond FCO 9221. St Francis Ranch | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0063533 | OH | Sus | 31023125 | No | 2013 | SEP | Yes | Line to Ground | 99262924 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1104 | 42661104 | OTHER |  | 20130920 | 1202 | 869197 | 333 | Distribution Circuit | Vegetation | Tree - fell into line | 1387 | 131852 | 39.4057 | -123.3683 | 16 SPANS PAST 7397 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0063426 | OH | Sus | 0 | No | 2013 | SEP | Yes | Line to Ground | 99263000 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 6445 | 20130928 | 112 | 874553 | 413 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4956 | 39.4258 | -123.7812 | 2 SPANS PAST FUCO | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0065484 | OH | Sus | 31024824 | No | 2013 | SEP | Yes | Line to Line | 99261393 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | HOOPA-1101 | 192401101 | OTHER |  | 20130929 | 117 | 875056 | 783 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 8241 | 41.0345 | -123.6718 | 115393062441 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0065613 | OH | Sus | 0 | No | 2013 | SEP | Yes | Line to Ground | 99261257 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | BRIDGEVILLE-1102 | 192461102 | FUSE | 3723 | 20130930 | 320 | 875303 | 569 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 5121 | 40.3504 | -123.7144 | 115269837093 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0065700 | OH | Sus | 41965831 | No | 2013 | SEP | Yes |  | 99261157 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 1677 | 20130930 | 247 | 875302 | 361 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 5415 | 39.4154 | -123.7817 | 1 SPAN SOUTH OF FUCO | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0065681 | OH | Sus | 41965568 | No | 2013 | SEP | Yes | Line to Ground | 99261171 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | SWITCH | 4519 | 20131002 | 2111 | 876774 | 704 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 107078 | 38.6963 | -123.3211 | AT LINE AND BUCK POLE 1 SPAN SS FUCO 4587 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0066636 | OH | Sus | 0 | No | 2013 | OCT | Yes |  | 99260665 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 8249 | 20131002 | 1050 | 876484 | 488 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 8 | 3904 | 40.2303 | -123.8505 | 114840933466 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0066458 | OH | Sus | 41966922 | No | 2013 | OCT | Yes |  | 99260746 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 2999 | 20131008 | 1617 | 881427 | 388 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 9312 | 39.4472 | -123.7431 | 1 SPAN PAST FUSES | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0068203 | OH | Sus | 31027028 | No | 2013 | OCT | Yes | Line to Line | 99259499 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE | 5013 | 20131028 | 252 | 891977 | 595 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1785 | 39.1271 | -122.9954 | 1 POLE LD 5013 AND BET 3RD AND 4TH POLE | Clear-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 13-0072581 | OH | Sus | 41977566 | yes | 2013 | OCT | Yes | Line to Ground | 99256278 | CAW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | OTHER |  | 20131102 | 1601 | 895442 | 797 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 41228 | 39.465 | -123.7835 | BET 6673 AND 1487 ON THE MAINLINE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0074030 | OH | Sus | 31033455 | No | 2013 | NOV | Yes | Line to Ground | 99255199 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 93234 | 20131120 | 1640 | 906042 | 626 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 64337 | 40.2353 | -123.8347 | 114855533309 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0077467 | OH | Sus | 31037546 | yes | 2013 | NOV | Yes | Multi-Fault | 99252333 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 2540 | 20131120 | 316 | 905255 | 655 | Distribution Circuit | Vegetation | Tree - fell into line | 308 | 173012 | 40.2431 | -124.1271 | 113839734913 | Fog-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 13-0077220 | OH | Sus | 31037246 | yes | 2013 | NOV | Yes | Line to Line | 99252618 | CAW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 4153 | 20131120 | 2311 | 906465 | 878 | Distribution Circuit | 3rd Party | Vehicle | 51 | 44778 | 39.4425 | -123.4131 | 26801 RIDGE RD at MTR#5000124651 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0077563 | OH | Sus | 31037563 | yes | 2013 | NOV | Yes | Three Phase Fault | 99252316 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOPLAND-1101 | 42251101 | FUSE | 2701 | 20131123 | 1825 | 914125 | 1251 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1251 | 39.0183 | -123.0421 | HOPLAND RD NEAR DORST RANCH | Clear-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 13-0079048 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Line | 99250891 | CAW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | OTHER |  | 20131123 | 745 | 913523 | 1834 | Distribution Circuit | Equipment Failure/Involved | Other | 282 | 46556 | 40.4738 | -123.562 | 115646842006 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0079021 | OH | Sus | 0 | yes | 2013 | NOV | Yes | None | 99250897 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1103 | 43351103 | FUSE | 1663 | 20131123 | 840 | 913598 | 580 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 20600 | 39.1233 | -122.8477 | MTR#1008033040 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078974 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Three Phase Fault | 99251092 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOPLAND-1101 | 42251101 | SWITCH | 3765 | 20131126 | 1042 | 915658 | 558 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4464 | 39.0109 | -123.0666 | ON MAINLINE 9 SPANS BEYOND 2701 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0079441 | OH | Sus | 42036791 | No | 2013 | NOV | Yes | None | 99250541 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 2006 | 20131201 | 729 | 917371 | 532 | Distribution Circuit | Equipment Failure/Involved | Other | 393 | 59499 | 40.2239 | -123.8263 | 114912833479 | Partly cloudy-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0079879 | OH | Sus | 42037521 | No | 2013 | DEC | Yes |  | 99250195 | CSO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 37202 | 20131206 | 2315 | 921421 | 954 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 36586 | 41.1893 | -123.71 | 115293968082 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081154 | OH | Sus | 0 | yes | 2013 | DEC | Yes | None | 99249042 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 8435 | 20131206 | 2315 | 922897 | 1260 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 25200 | 41.2086 | -123.756 | 115158368887 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081337 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Line | 99248886 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MENDOCINO-1101 | 42951101 | SWITCH | 4729 | 20131206 | 2040 | 921300 | 475 | Distribution Circuit | Vegetation | Tree - fell into line | 225 | 28177 | 39.3116 | -123.2198 | 13000 TOMKI RD- AT SW623 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081054 | OH | Sus | 0 | yes | 2013 | DEC | Yes | None | 99249173 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | FUSE | 1417 | 20131206 | 2027 | 921289 | 1137 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 97719 | 39.3883 | -123.1163 | 4 SPANS FROM FUCO 1941 TWD 1961 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081080 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99249071 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 37506 | 20131206 | 1841 | 921224 | 1224 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 92532 | 39.4832 | -123.3603 | ON MAIN LINE 1 SPAN FROM FUCO 92673 TWDS SW 2527 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081043 | OH | Sus | 0 | yes | 2013 | DEC | Yes |  | 99249077 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1102 | 192171102 | FUSE | 3209 | 20131206 | 1828 | 921149 | 557 | Distribution Circuit | Environmental/External | Ice or snow | 16 | 8912 | 40.9887 | -123.6395 | GOODMAN-BILL: hwy 96 at mm 4.0 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081042 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99249184 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | BRIDGEVILLE-1102 | 192461102 | OTHER |  | 20131207 | 725 | 922026 | 518 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 10912 | 40.3572 | -123.7198 | 2 SPANS LD SIDE OF MTR#1008802783 | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0081289 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Line | 99248924 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | BRIDGEVILLE-1102 | 192461102 | FUSE | 3785 | 20131207 | 758 | 922084 | 222 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 519 | 40.3865 | -123.7425 | 2 SPANS LD SIDE OF MTR#1008802783 | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0081298 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99248917 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 7155 | 20131207 | 733 | 922053 | 670 | Distribution Circuit | Vegetation | Tree - branch fell on line | 93 | 62310 | 41.0509 | -123.6675 | 115409562957 | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081261 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99248945 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 5681 | 20131207 | 945 | 922340 | 695 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 13205 | 41.0713 | -123.6947 | 115313963923 | Snow-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 13-0081300 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99248916 | CAW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 5295 | 20131207 | 1910 | 923109 | 1115 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5575 | 41.291 | -123.5671 | 115695771572 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081420 | OH | Sus | 0 | yes | 2013 | DEC | Yes |  | 99248765 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3153 | 20131207 | 1335 | 923308 | 1415 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 11320 | 41.061 | -123.6776 | 115375963415 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081423 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Line | 99248762 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1101 | 192171101 | FUSE | 3059 | 20131207 | 830 | 921891 | 675 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 43200 | 40.9412 | -123.6136 | 115537958894 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081230 | OH | Sus | 0 | yes | 2013 | DEC | Yes | None | 99248973 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | OTHER |  | 20131210 | 1910 | 925331 | 448 | Distribution Circuit | Equipment Failure/Involved | Other | 860 | 140364 | 39.4295 | -123.3716 | 3 SPANS SS OF SW 6253 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081840 | OH | Sus | 42044713 | No | 2013 | DEC | Yes |  | 99248338 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | REDBUD-1101 | 43191101 | OTHER |  | 20131212 | 654 | 926167 | 348 | Distribution Circuit | Equipment Failure/Involved | Other | 2106 | 168356 | 39.0281 | -122.6798 | 2 SPANS SOURCE SIDE LR 800 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0082041 | OH | Sus | 42045541 | No | 2013 | DEC | Yes | Line to Ground | 99248139 | CSO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | OTHER |  | 20131217 | 1246 | 929129 | 701 | Distribution Circuit | Vegetation | Tree - fell into line | 538 | 339821 | 41.1936 | -123.6768 | 115390668220 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0082659 | OH | Sus | 31043586 | No | 2013 | DEC | Yes |  | 99247349 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | FUSE | 3799 | 20131217 | 1104 | 929025 | 441 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 6174 | 39.3791 | -123.1073 | MTR 500012140 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0082648 | OH | Sus | 42047958 | No | 2013 | DEC | Yes | Line to Ground | 99247362 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | OTHER |  | 20131218 | 107 | 929335 | 535 | Distribution Circuit | Equipment Failure/Involved | Other | 13 | 6895 | 38.9222 | -123.6727 | 4 SPANS LD FUCO 3761 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0082707 | OH | Sus | 31043596 | No | 2013 | DEC | Yes | None | 99247294 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | NEWBURG-1132 | 192151132 | OTHER |  | 20131219 | 238 | 929815 | 437 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 14573 | 40.5999 | -124.1264 | 10 POLES LD FUCO 3425 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0082825 | OH | Sus | 42048648 | yes | 2013 | DEC | Yes | Line to Ground | 99247112 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | OTHER |  | 20131223 | 1715 | 932456 | 486 | Distribution Circuit | Animal | Bird found | 933 | 278371 | 38.7171 | -123.4556 | 4 SPANS FROM 4097 TWDS 3659 AT MTR#1009543789 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0083297 | OH | Sus | 0 | No | 2013 | DEC | Yes | Line to Ground | 99246386 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 7743 | 20131230 | 229 | 935251 | 726 | Distribution Circuit | 3rd Party | Vehicle | 6 | 4356 | 39.3001 | -123.7907 | 2 SPANS LOAD SIDE OF 7743 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0083632 | OH | Sus | 31045753 | No | 2013 | DEC | Yes | Line to Ground | 99245890 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | OTHER |  | 20140105 | 1144 | 937424 | 411 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 411 | 38.9046 | -123.6262 | 1 SPAN PAST FUCO | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0002247 | OH | Sus | 42053024 | No | 2014 | JAN | Yes |  | 99245292 | CSO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3349 | 20140111 | 1458 | 940382 | 647 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 647 | 41.0551 | -123.6723 | 115388563168 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0003553 | OH | Sus | 42057019 | No | 2014 | JAN | Yes | Line to Ground | 99244597 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | OTHER |  | 20140115 | 1103 | 942184 | 244 | Distribution Circuit | Vegetation | Tree - fell into line | 140 | 26791 | 40.2685 | -123.8723 | 13/SP/LOADSIDE/O/LR8860 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0004286 | OH | Sus | 42059825 | No | 2014 | JAN | Yes | None | 99244159 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 5501 | 20140117 | 728 | 943131 | 557 | Distribution Circuit | 3rd Party | Vehicle | 3 | 1671 | 38.7809 | -122.7029 | AT MTR#1006591256 | Clear-32 - 90 F | Pole-Wood | Broken, wire on object | 14-0004800 | OH | Sus | 31050261 | No | 2014 | JAN | Yes | Three Phase Fault | 99243885 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | BRIDGEVILLE-1102 | 192461102 | OTHER |  | 20140123 | 819 | 945818 | 416 | Distribution Circuit | Equipment Failure/Involved | Other | 41 | 14585 | 40.4338 | -123.7653 | 115096440288 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0005814 | OH | Sus | 42064319 | yes | 2014 | JAN | Yes | None | 99243221 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1121 | 192021121 | FUSE | 6213 | 20140124 | 207 | 946638 | 478 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3824 | 40.8177 | -123.995 | 2 SPANS LOAD SIDE OF 6213 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0006073 | OH | Sus | 42064692 | yes | 2014 | JAN | Yes | Line to Line | 99243058 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2531 | 20140127 | 846 | 949936 | 574 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1148 | 40.1508 | -124.029 | 114332730257 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0006577 | OH | Sus | 31052435 | No | 2014 | JAN | Yes | Line to Ground | 99242596 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MAPLE CREEK-1101 | 192101101 | OCB | OCB | 20140127 | 829 | 949903 | 284 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 104 | 0 | 40.7678 | -123.874 | 5 SPANS FROM POLE 8/4 TWDS 6047 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0006510 | OH | Sus | 42065795 | No | 2014 | JAN | Yes |  | 99242642 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3051 | 20140201 | 1341 | 957286 | 629 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 28 | 17612 | 39.2735 | -123.698 | 39451 COMPTCHE ROAD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0008072 | OH | Sus | 42068966 | No | 2014 | FEB | Yes |  | 99241814 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 7531 | 20140207 | 1440 | 961497 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1242 | 38.7228 | -123.4038 | 2 SPANS PAST FUSES | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0009679 | OH | Sus | 31055406 | yes | 2014 | FEB | Yes | Line to Ground | 99240959 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 9201 | 20140207 | 1333 | 961425 | 307 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 3377 | 39.3174 | -123.7899 | 3 SPANS PAST FUSES | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0009644 | OH | Sus | 42073030 | yes | 2014 | FEB | Yes |  | 99240975 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3285 | 20140207 | 1751 | 961904 | 359 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1061 | 39.3177 | -123.7453 | 2 SPANS FROM EOL | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0009738 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Ground | 99240914 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HUMBOLDT BAY-1102 | 192341102 | FUSE | 4301 | 20140207 | 1420 | 961587 | 264 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 5807 | 40.7035 | -124.1537 | 114062250570 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0009670 | OH | Sus | 42073069 | yes | 2014 | FEB | Yes |  | 99240965 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | RECLOSER | 4622 | 20140210 | 444 | 964718 | 388 | Distribution Circuit | Vegetation | Tree - fell into line | 370 | 143560 | 39.5149 | -123.764 | 3 SPANS PAST LR 4622 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0010229 | OH | Sus | 42073830 | yes | 2014 | FEB | Yes | Line to Ground | 99240364 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 4617 | 20140211 | 1945 | 966213 | 315 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 630 | 39.5062 | -123.7675 | 25901 NORTH HWY 1- FT BRAGG | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0010763 | OH | Sus | 42076506 | No | 2014 | FEB | Yes | Line to Ground | 99240015 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UKIAH-1114 | 42771114 | FUSE | 437 | 20140211 | 153 | 965584 | 756 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 39318 | 39.0784 | -123.2142 | AT METER#1008858978 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0010549 | OH | Sus | 31055878 | No | 2014 | FEB | Yes | Multi-Fault | 99240167 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3163 | 20140226 | 2011 | 973147 | 644 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 24472 | 39.6527 | -123.7828 | 7 SPANS LD FUCO 3163 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0013658 | OH | Sus | 31059384 | yes | 2014 | FEB | Yes | Line to Line | 99238010 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | RECLOSER | 23444 | 20140226 | 1541 | 972822 | 389 | Distribution Circuit | Vegetation | Tree - branch fell on line | 166 | 15521 | 38.8487 | -123.6437 | ONE SPAN FROM 8177 TWDS 3661 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0013553 | OH | Sus | 42083599 | yes | 2014 | FEB | Yes |  | 99238161 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1103 | 43141103 | FUSE | 1469 | 20140226 | 2209 | 973309 | 666 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1332 | 38.7289 | -122.5521 | 2 SPANS LD FUCO 1469 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0013728 | OH | Sus | 31059395 | yes | 2014 | FEB | Yes | Line to Ground | 99237990 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2411 | 20140226 | 2023 | 973173 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 10319 | 39.4806 | -123.361 | at MTR # H21648 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0013654 | OH | Sus | 42083761 | yes | 2014 | FEB | Yes | Line to Line | 99238012 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3173 | 20140228 | 928 | 974967 | 260 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 520 | 39.6337 | -123.7826 | 4 SPANS LD SIDE OF 3173 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0014396 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Ground | 99237563 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 7287 | 20140228 | 719 | 974558 | 176 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 2816 | 38.8139 | -123.5858 | 3 SPANS LOAD SIDE OF FUCO 7287 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0014297 | OH | Sus | 0 | yes | 2014 | FEB | Yes |  | 99237616 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | RECLOSER | J2N2 | 20140228 | 211 | 974215 | 649 | Distribution Circuit | Equipment Failure/Involved | Other | 94 | 31242 | 39.0852 | -123.4853 | 500' E/O CUTOUTS 2605 ON GREENWOOD RD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0014171 | OH | Sus | 42084284 | yes | 2014 | FEB | Yes | Multi-Fault | 99237708 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 563 | 20140228 | 1633 | 975591 | 233 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 6990 | 38.8954 | -123.623 | 16 SPANS LD SIDE OF 563 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0014597 | OH | Sus | 31059933 | yes | 2014 | FEB | Yes | Line to Line | 99237433 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | SWITCH | J2N2 | 20140303 | 1129 | 977610 | 396 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 43287 | 38.9097 | -123.6341 | 6 SPANS FROM 47952 TWDS 7527 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0015078 | OH | Sus | 31060156 | No | 2014 | MAR | Yes | Line to Ground | 99236932 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CARLOTTA-1121 | 192291121 | FUSE | 5543 | 20140304 | 320 | 977953 | 560 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1680 | 40.5238 | -124.0275 | 114369844029 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0015242 | OH | Sus | 42085691 | No | 2014 | MAR | Yes | Line to Ground | 99236826 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1121 | 192021121 | FUSE | 1217 | 20140305 | 924 | 978928 | 266 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 17024 | 40.839 | -124.0234 | 114433855233 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0015606 | OH | Sus | 0 | yes | 2014 | MAR | Yes |  | 99236615 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER | 8860 | 20140306 | 1608 | 980080 | 377 | Distribution Circuit | Vegetation | Tree - branch fell on line | 138 | 12966 | 40.2837 | -123.8726 | 114765434384 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0016272 | OH | Sus | 0 | yes | 2014 | MAR | Yes |  | 99236222 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1102 | 192461102 | RECLOSER | 55612 | 20140308 | 1147 | 980917 | 718 | Distribution Circuit | Equipment Failure/Involved | Other | 55 | 19906 | 40.4666 | -123.8012 | 115039340743 | Overcast-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0016691 | OH | Sus | 42088865 | No | 2014 | MAR | Yes | Line to Ground | 99235918 | CSO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1102 | 43311102 | RECLOSER | 64464 | 20140316 | 134 | 985221 | 664 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 56012 | 38.9442 | -122.6754 | 5 SPANS LOAD SIDE LR 64464 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0018372 | OH | Sus | 42093980 | No | 2014 | MAR | Yes |  | 99234677 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1106 | 43351106 | FUSE | 4115 | 20140317 | 1520 | 985893 | 189 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 378 | 38.9915 | -122.7473 | 3 SPANS LOADSIDE OF 4115 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0018651 | OH | Sus | 42094437 | No | 2014 | MAR | Yes | None | 99234464 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3757 | 20140319 | 1700 | 986878 | 124 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 6696 | 40.2285 | -123.8633 | 114796632673 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0019242 | OH | Sus | 42095714 | No | 2014 | MAR | Yes | None | 99234123 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HIGHLANDS-1103 | 43361103 | RECLOSER | 520 | 20140328 | 1020 | 990923 | 348 | Distribution Circuit | Equipment Failure/Involved | Other | 843 | 184460 | 38.8824 | -122.5913 | 1 SPAN FROM 508476 TWDS 2029 | Drizzle-32 - 90 F | Woodpin | Broken, wire on object | 14-0021226 | OH | Sus | 42099383 | No | 2014 | MAR | Yes |  | 99232770 | WP | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOPLAND-1101 | 42251101 | FUSE | 697 | 20140329 | 1037 | 991358 | 573 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 5157 | 38.9691 | -123.0647 | 1 SPAN SOURCE SIDE 1008842071 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0021395 | OH | Sus | 31065958 | yes | 2014 | MAR | Yes | Three Phase Fault | 99232653 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | OTHER |  | 20140329 | 930 | 991305 | 372 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1860 | 38.8929 | -122.7861 | 1 SPAN SOURCE SIDE METER | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0021385 | OH | Sus | 0 | yes | 2014 | MAR | Yes | Line to Ground | 99232663 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | FUSE | 1997 | 20140329 | 946 | 991339 | 644 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4508 | 40.2843 | -124.0598 | 114302834899 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0021403 | OH | Sus | 42099570 | yes | 2014 | MAR | Yes | Line to Ground | 99232646 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 3657 | 20140330 | 1310 | 991990 | 870 | Distribution Circuit | Vegetation | Tree - fell into line | 194 | 147668 | 38.7801 | -122.6824 | AT MTR # 1009794801 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0021559 | OH | Sus | 31066156 | yes | 2014 | MAR | Yes | Line to Ground | 99232408 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UKIAH-1114 | 42771114 | OTHER |  | 20140330 | 1811 | 992069 | 497 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 611 | 39.0978 | -123.2215 | ESPINOLA- CHRISTOPHER: at address 1 mile up shepherd lane | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0021597 | OH | Sus | 31066224 | yes | 2014 | MAR | Yes | Line to Ground | 99232441 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 1747 | 20140401 | 1735 | 993676 | 1435 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7175 | 39.8368 | -123.6857 | 115258118840 | Drizzle-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0022304 | OH | Sus | 31066797 | yes | 2014 | APR | Yes | Line to Line | 99231948 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 7221 | 20140404 | 629 | 995027 | 459 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 918 | 39.5219 | -123.7621 | ONE SPAN LOAD SIDE OF FUCO 7221 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0022966 | OH | Sus | 42102229 | No | 2014 | APR | Yes | Line to Ground | 99231516 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 56048 | 20140414 | 1841 | 999519 | 695 | Distribution Circuit | Vegetation | Tree - fell into line | 367 | 17051 | 40.1476 | -124.0197 | 114106433252 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0025047 | OH | Sus | 42107623 | No | 2014 | APR | Yes | Line to Line | 99230177 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 1885 | 20140417 | 2120 | 1001087 | 530 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 530 | 38.6655 | -123.3122 | 4 SPANS LOAD SIDE OF 1885 | Partly cloudy-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0025836 | OH | Sus | 31070171 | No | 2014 | APR | Yes | Line to Line | 99229727 | CAW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 3995 | 20140420 | 808 | 1001857 | 738 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4428 | 39.6968 | -123.6561 | 1 POLE SS OF MTR#9J3211- WILDERNESS LODGE RD | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0026077 | OH | Sus | 31070480 | No | 2014 | APR | Yes | Line to Line | 99229518 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1569 | 20140427 | 1530 | 1005492 | 260 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 1560 | 40.0192 | -123.7961 | 114981525515 | Partly cloudy-32 - 90 F | Insulator | Broken, wire on object | 14-0027636 | OH | Sus | 42113907 | No | 2014 | APR | Yes | Line to Ground | 99228381 | INS | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER | 7514 | 20140427 | 1616 | 1005500 | 409 | Distribution Circuit | Equipment Failure/Involved | Other | 1287 | 300148 | 40.9333 | -123.6249 | 115668757213 | Clear-32 - 90 F | Crossarm, Wood | Broken, wire on object | 14-0027641 | OH | Sus | 31071954 | No | 2014 | APR | Yes | None | 99228377 | CAW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1260 | 20140502 | 1417 | 1009259 | 327 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 13965 | 39.1295 | -123.7111 | BET TAP 8641 & 8621 33001 PHILO GREENWOOD RD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0028976 | OH | Sus | 31073470 | No | 2014 | MAY | Yes | Line to Line | 99227555 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MAPLE CREEK-1101 | 192101101 | OTHER |  | 20140505 | 353 | 1010137 | 393 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2191 | 40.7542 | -123.8714 | 114814751980 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0029192 | OH | Sus | 42116889 | yes | 2014 | MAY | Yes | Line to Ground | 99227331 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3147 | 20140506 | 843 | 1010859 | 347 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 6593 | 39.5053 | -123.7369 | 12 PAST FUSES | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0029591 | OH | Sus | 42117804 | yes | 2014 | MAY | Yes | Line to Line | 99227075 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8961 | 20140507 | 908 | 1011440 | 142 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 142 | 39.5605 | -123.7264 | GARCIA/3467: one span beyond fuco 8961 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0029907 | OH | Sus | 42118046 | No | 2014 | MAY | Yes | Line to Ground | 99226891 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MIDDLETOWN-1101 | 43141101 | RECLOSER | 622 | 20140511 | 702 | 1013425 | 426 | Distribution Circuit | 3rd Party | Vehicle | 389 | 95530 | 38.7461 | -122.6206 | AT MTR 1009370006 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0030907 | OH | Sus | 31075386 | No | 2014 | MAY | Yes | Line to Line | 99226294 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | OTHER |  | 20140513 | 1856 | 1014872 | 569 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 1138 | 38.8436 | -123.6309 | 6 SPANS LOAD SIDE OF 5265 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0031568 | OH | Sus | 31076031 | yes | 2014 | MAY | Yes | Line to Ground | 99225869 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1121 | 192021121 | FUSE | 1217 | 20140516 | 908 | 1016694 | 322 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 64 | 20608 | 40.839 | -124.0234 | 114455754969 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0032364 | OH | Sus | 42125262 | No | 2014 | MAY | Yes | Line to Ground | 99225324 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 5587 | 20140521 | 726 | 1021826 | 364 | Distribution Circuit | Animal | Bird found | 6 | 2184 | 39.0569 | -123.4462 | 5 PAST FUSES | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0033426 | OH | Sus | 42127999 | No | 2014 | MAY | Yes | Line to Ground | 99224555 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE | 2335 | 20140525 | 1041 | 1023762 | 589 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 15903 | 39.1926 | -122.9706 | STOCKTON- KEN: 10965 BACHELOR VALLEY | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0034204 | OH | Sus | 42129669 | No | 2014 | MAY | Yes | Line to Ground | 99224024 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 8207 | 20140528 | 1608 | 1025485 | 612 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 5508 | 39.9943 | -123.9263 | 114566124041 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0034812 | OH | Sus | 42130790 | No | 2014 | MAY | Yes | Line to Line | 99223584 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1102 | 43311102 | OCB | OCB | 20140528 | 427 | 1024984 | 394 | Distribution Circuit | Equipment Failure/Involved | Other | 3028 | 347308 | 38.9326 | -122.741 | 7 SPANS SS OF LR 716 WIRE DOWN & 10 SPANS SS OF LR 716 BROKEN WOODPIN CONDUTOR CONTACTING XARM | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0034583 | OH | Sus | 42130340 | No | 2014 | MAY | Yes | Line to Ground | 99223728 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 1659 | 20140605 | 811 | 1028863 | 331 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 47 | 15557 | 39.3879 | -123.3237 | MTR#59J433 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0036283 | OH | Sus | 31080667 | No | 2014 | JUN | Yes | Line to Line | 99222531 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 5681 | 20140606 | 1521 | 1029684 | 879 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 12750 | 41.0713 | -123.6947 | 115319563903 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0036745 | OH | Sus | 31081226 | No | 2014 | JUN | Yes | Line to Line | 99222294 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER | 3902 | 20140617 | 1602 | 1035863 | 756 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1232 | 40.343 | -123.9165 | 114609039265 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0038951 | OH | Sus | 31083188 | No | 2014 | JUN | Yes | Three Phase Fault | 99220636 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 3221 | 20140625 | 1940 | 1039813 | 456 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 8664 | 39.4413 | -123.7798 | 6 SPANS LOAD SIDE OF 3221 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0040638 | OH | Sus | 31084992 | yes | 2014 | JUN | Yes | Line to Line | 99219443 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | SECTIONALIZER | 6064 | 20140625 | 1029 | 1039499 | 372 | Distribution Circuit | Vegetation | Tree - branch fell on line | 62 | 23064 | 40.2952 | -123.8204 | 114921335857 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0040498 | OH | Sus | 42144942 | yes | 2014 | JUN | Yes | Line to Ground | 99219490 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1487 | 20140626 | 507 | 1039982 | 353 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 946 | 39.4656 | -123.7838 | 3 SPANS LOAD SIDE OF FUCO 1487 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0040663 | OH | Sus | 42145053 | No | 2014 | JUN | Yes | Line to Ground | 99219401 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 8301 | 20140627 | 1759 | 1040819 | 676 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 13878 | 39.4882 | -123.4221 | 1 SPAN SOURCE SIDE OF FUCO 9121 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0041145 | OH | Sus | 42146380 | No | 2014 | JUN | Yes | Line to Ground | 99219105 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CALPELLA-1101 | 43411101 | FUSE | 7445 | 20140710 | 1437 | 1047463 | 448 | Distribution Circuit | Vegetation | Tree - branch fell on line | 32 | 14336 | 39.2338 | -123.1661 | ESPINOLA- CHRISTOPHER: at MTR 1009774604 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0043769 | OH | Sus | 31088098 | yes | 2014 | JUL | Yes |  | 99217225 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 3657 | 20140717 | 430 | 1050919 | 505 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 194 | 26045 | 38.7801 | -122.6824 | 11393 ROSE ANDERSON ROAD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0045050 | OH | Sus | 0 | No | 2014 | JUL | Yes |  | 99216317 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1104 | 42661104 | FUSE | 8681 | 20140717 | 1817 | 1051296 | 707 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 6363 | 39.3547 | -123.3345 | 18300 SHAFFER RANCH RD- WILLITS | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0045277 | OH | Sus | 31089573 | No | 2014 | JUL | Yes | Line to Line | 99216167 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 4609 | 20140719 | 850 | 1051904 | 402 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1206 | 40.2215 | -123.8075 | 3 SPANS LOAD SIDE OF FUCO 4609 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0045569 | OH | Sus | 31089831 | No | 2014 | JUL | Yes | Line to Line | 99215986 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 4639 | 20140719 | 1852 | 1052106 | 1360 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 6542 | 39.7145 | -123.4909 | MTR 1008393514 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0045628 | OH | Sus | 31089883 | No | 2014 | JUL | Yes | Line to Line | 99215909 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3185 | 20140721 | 1037 | 1052786 | 445 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2670 | 39.5317 | -123.7597 | 4 SPANS LD SIDE OF 3185 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0045816 | OH | Sus | 0 | No | 2014 | JUL | Yes | Line to Ground | 99215744 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER | 532 | 20140810 | 1314 | 1063954 | 546 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 531 | 76295 | 38.8576 | -122.7223 | 4 SPANS FROM 1035 TWDS 9789 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0050144 | OH | Sus | 42166491 | No | 2014 | AUG | Yes |  | 99212715 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 4945 | 20140810 | 209 | 1063787 | 881 | Distribution Circuit | 3rd Party | Vehicle | 29 | 18239 | 39.4378 | -123.3915 | 13 SPANS LD SIDE OF 4945 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0050120 | OH | Sus | 0 | No | 2014 | AUG | Yes |  | 99212746 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | BRIDGEVILLE-1102 | 192461102 | FUSE | 4689 | 20140820 | 109 | 1069091 | 474 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 948 | 40.351 | -123.7147 | 115244537631 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0051926 | OH | Sus | 42174082 | No | 2014 | AUG | Yes | Line to Line | 99211395 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER |  | 20140820 | 1607 | 1069433 | 503 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 7723 | 40.1936 | -123.7677 | 115065331866 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0052117 | OH | Sus | 31096186 | No | 2014 | AUG | Yes | Line to Ground | 99211293 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER | 35592 | 20140825 | 1009 | 1072628 | 797 | Distribution Circuit | 3rd Party | Vehicle | 364 | 88148 | 39.3947 | -123.7794 | CAR POLE AT 30603 SIMPSON LANE (3 SPANS LOAD SIDE OF LR 35592) | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0053014 | OH | Sus | 31096859 | No | 2014 | AUG | Yes | Line to Line | 99210483 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1750 | 20140830 | 1054 | 1075099 | 898 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 23840 | 40.0848 | -123.8079 | 114824927106 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0054242 | OH | Sus | 31098127 | No | 2014 | AUG | Yes | Line to Ground | 99209823 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 1325 | 20140917 | 1553 | 1083358 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 12913 | 38.8761 | -122.775 | 3 spans north of 10675 Bottle Rock Rd | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0057577 | OH | Sus | 42193248 | No | 2014 | SEP | Yes | Line to Line | 99207604 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1703 | 20140918 | 1456 | 1084182 | 714 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3570 | 39.9528 | -123.7767 | 115037423093 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0057909 | OH | Sus | 42193893 | yes | 2014 | SEP | Yes | Line to Ground | 99207378 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3287 | 20140919 | 555 | 1084372 | 423 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 26226 | 39.3137 | -123.7463 | 2 AND 3 SPANS SOURCE SIDE 461 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0057959 | OH | Sus | 42194110 | No | 2014 | SEP | Yes | Line to Line | 99207313 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 3295 | 20140924 | 1757 | 1086966 | 458 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 4620 | 39.4427 | -123.7706 | 4 SPANS LD FUCO 3295 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0059051 | OH | Sus | 0 | No | 2014 | SEP | Yes | Line to Ground | 99206550 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 2500 | 20140924 | 644 | 1086461 | 906 | Distribution Circuit | Vegetation | Tree - fell into line | 440 | 65382 | 40.1078 | -123.9291 | ON MAINLINE SOURCESIDE OF 65936 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0058833 | OH | Sus | 0 | No | 2014 | SEP | Yes | Line to Ground | 99206674 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | OTHER |  | 20140924 | 1624 | 1086935 | 463 | Distribution Circuit | Vegetation | Tree - bark fell into line | 618 | 89984 | 38.813 | -123.5954 | 1 SPANS SS 7301 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0059040 | OH | Sus | 0 | No | 2014 | SEP | Yes | Line to Ground | 99206559 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | OTHER |  | 20140928 | 234 | 1089637 | 978 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2934 | 38.7763 | -123.4827 | 13 SPANS LOAD SIDE OF FUCO 4451 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0060012 | OH | Sus | 42198721 | No | 2014 | SEP | Yes | Line to Ground | 99205823 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 2500 | 20140930 | 1610 | 1090884 | 843 | Distribution Circuit | Vegetation | Tree - fell into line | 440 | 95727 | 40.1078 | -123.9291 | 114518729005 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0060535 | OH | Sus | 42199872 | No | 2014 | SEP | Yes | Line to Line | 99205455 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | REDBUD-1101 | 43191101 | FUSE | 97031 | 20141001 | 1149 | 1091243 | 902 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 902 | 39.0691 | -122.6437 | 2613 LONG VALLEY ROAD- CLEARLAKE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0060786 | OH | Sus | 31104820 | No | 2014 | OCT | Yes | Line to Ground | 99205332 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 2309 | 20141006 | 853 | 1093426 | 374 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2992 | 38.8925 | -122.7398 | 2 SPANS PAST FUSES | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0061653 | OH | Sus | 31105723 | No | 2014 | OCT | Yes | Line to Line | 99204732 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CALPELLA-1101 | 43411101 | FUSE | 6187 | 20141007 | 1330 | 1094113 | 450 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4950 | 39.2431 | -123.151 | MTR 1009774634 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0061984 | OH | Sus | 42202898 | No | 2014 | OCT | Yes | Line to Line | 99204571 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 64793 | 20141007 | 737 | 1093862 | 836 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 836 | 38.8667 | -123.6508 | 28505 S HWY 1 | Fog-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0061870 | OH | Sus | 31105864 | No | 2014 | OCT | Yes | Line to Ground | 99204615 | CSO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1757 | 20141015 | 28 | 1097421 | 301 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 7231 | 40.0692 | -123.8296 | 114882627330 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0063666 | OH | Sus | 42208704 | yes | 2014 | OCT | Yes | Line to Ground | 99203515 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 2147 | 20141015 | 557 | 1097688 | 513 | Distribution Circuit | Vegetation | Tree - branch fell on line | 32 | 16416 | 38.7124 | -122.6434 | 1 SPAN SS OF MTR1008686588 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0063718 | OH | Sus | 31107522 | yes | 2014 | OCT | Yes | Line to Line | 99203484 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3139 | 20141020 | 759 | 1099520 | 441 | Distribution Circuit | Vegetation | Tree - branch fell on line | 53 | 23373 | 39.5109 | -123.7644 | 2 SPANS LOADSIDE OF FUCO 3139 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0064604 | OH | Sus | 42212928 | No | 2014 | OCT | Yes | Line to Ground | 99202933 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 1033 | 20141020 | 1330 | 1099753 | 793 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 21411 | 38.7814 | -122.6852 | 3 SPANS SOURCESIDE OF MTR#1008647890 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0064708 | OH | Sus | 0 | No | 2014 | OCT | Yes | Three Phase Fault | 99202875 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1101 | 192171101 | FUSE | 3021 | 20141020 | 902 | 1099579 | 385 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 15015 | 40.9628 | -123.8377 | 114881161144 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0064628 | OH | Sus | 31108736 | No | 2014 | OCT | Yes | Line to Ground | 99202914 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER | 3090 | 20141024 | 1315 | 1101744 | 424 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 19504 | 40.889 | -123.5934 | 115602456816 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0065783 | OH | Sus | 31110029 | No | 2014 | OCT | Yes |  | 99202269 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER 1101 | 192381101 | FUSE | 1909 | 20141025 | 847 | 1102210 | 499 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 11976 | 40.5118 | -124.1601 | 114010343576 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0066077 | OH | Sus | 0 | yes | 2014 | OCT | Yes | Line to Ground | 99202030 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | OTHER |  | 20141025 | 831 | 1102190 | 238 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 952 | 39.4804 | -123.7877 | 2 SPANS PAST MTR 1006278997 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0065953 | OH | Sus | 0 | yes | 2014 | OCT | Yes | Line to Ground | 99202130 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 411 | 20141025 | 150 | 1101960 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 3708 | 39.447 | -123.7526 | 29862 MADSEN LN | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0065890 | OH | Sus | 0 | yes | 2014 | OCT | Yes | Line to Line | 99202182 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER | 1690 | 20141025 | 1711 | 1102862 | 1462 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 21135 | 40.1679 | -123.6112 | 115409429111 | Rain-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0066127 | OH | Sus | 0 | yes | 2014 | OCT | Yes | Line to Line | 99201946 | CAW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 4367 | 20141025 | 1711 | 1102934 | 1488 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 22320 | 40.1476 | -123.6372 | 2250 RANCHO SEQUOIA RD | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0066215 | OH | Sus | 0 | yes | 2014 | OCT | Yes | Line to Line | 99201876 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | OCB | OCB | 20141025 | 815 | 1102177 | 2007 | Distribution Circuit | Vegetation | Tree - fell into line | 361 | 709513 | 40.2863 | -123.8376 | 114782535200 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0065950 | OH | Sus | 0 | yes | 2014 | OCT | Yes | Line to Line | 99201960 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | OTHER |  | 20141025 | 304 | 1101980 | 552 | Distribution Circuit | Vegetation | Tree - branch fell on line | 186 | 94733 | 40.296 | -123.8271 | 2374 ELK CRK MTR#1008024164 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0065889 | OH | Sus | 0 | yes | 2014 | OCT | Yes | None | 99202183 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1750 | 20141025 | 1530 | 1102768 | 1733 | Distribution Circuit | Equipment Failure/Involved | Other | 159 | 229676 | 40.0848 | -123.8079 | WIRE DOWN BET 7313 & 1869 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0066125 | OH | Sus | 0 | yes | 2014 | OCT | Yes | None | 99201947 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 56048 | 20141025 | 119 | 1101957 | 2051 | Distribution Circuit | Vegetation | Tree - fell into line | 177 | 117717 | 40.1476 | -124.0197 | 5 SPANS FROM 8183 TWDS 9362 | Drizzle-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0065874 | OH | Sus | 0 | yes | 2014 | OCT | Yes | Line to Line | 99201963 | CAW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1787 | 20141025 | 654 | 1102098 | 416 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 6240 | 40.011 | -123.9305 | 114601224868 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0065965 | OH | Sus | 0 | yes | 2014 | OCT | Yes | Three Phase Fault | 99202123 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 8197 | 20141025 | 529 | 1102723 | 673 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 673 | 40.2706 | -124.2184 | 113816035022 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0066059 | OH | Sus | 0 | yes | 2014 | OCT | Yes | Line to Line | 99202040 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 6084 | 20141025 | 1457 | 1102731 | 1422 | Distribution Circuit | Vegetation | Tree - branch fell on line | 63 | 89586 | 40.0617 | -123.962 | 114513626589 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0066063 | OH | Sus | 0 | yes | 2014 | OCT | Yes |  | 99201954 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2531 | 20141025 | 119 | 1103124 | 2534 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 5068 | 40.1508 | -124.029 | 114332730257 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0066186 | OH | Sus | 0 | yes | 2014 | OCT | Yes | Line to Line | 99201900 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 3174 | 20141025 | 415 | 1101996 | 915 | Distribution Circuit | Vegetation | Tree - fell into line | 489 | 442197 | 41.2232 | -123.6557 | 115643371350 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0065891 | OH | Sus | 0 | yes | 2014 | OCT | Yes | Line to Line | 99202181 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER | 4300 | 20141025 | 942 | 1102306 | 174 | Distribution Circuit | 3rd Party | Vehicle | 980 | 88620 | 38.9109 | -122.7643 | AT LR 532 | Fog-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0065986 | OH | Sus | 0 | yes | 2014 | OCT | Yes | Line to Line | 99202100 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 921 | 20141025 | 1207 | 1102491 | 409 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3272 | 39.7023 | -123.497 | 2 SPANS PAST FUCO | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0066020 | OH | Sus | 0 | yes | 2014 | OCT | Yes | Line to Ground | 99202073 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 8049 | 20141025 | 740 | 1102134 | 658 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 3290 | 39.5037 | -123.4558 | MTR#5000042848 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0065973 | OH | Sus | 0 | yes | 2014 | OCT | Yes | Line to Line | 99202111 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 2971 | 20141025 | 717 | 1102112 | 540 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 9720 | 40.8074 | -123.4787 | 115906053617 | Rain-32 - 90 F | Conductor, Underground | Broken, wire on ground | 14-0065994 | OH | Sus | 0 | yes | 2014 | OCT | Yes | Line to Ground | 99202093 | CU | UG | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 5987 | 20141026 | 927 | 1103182 | 653 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 653 | 40.2351 | -124.1498 | 114006333748 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0066209 | OH | Sus | 0 | No | 2014 | OCT | Yes | Line to Ground | 99201880 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | OTHER |  | 20141026 | 1720 | 1103202 | 518 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1554 | 38.9069 | -123.2311 | AT MTR 5000119682 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0066225 | OH | Sus | 0 | No | 2014 | OCT | Yes | Line to Ground | 99201824 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER |  | 20141028 | 651 | 1105174 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 249 | 25036 | 40.0849 | -123.9482 | 114551527961 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0066477 | OH | Sus | 42217047 | No | 2014 | OCT | Yes | Open Circuit | 99201650 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MIDDLETOWN-1102 | 43141102 | RECLOSER | 1312 | 20141028 | 1201 | 1105380 | 554 | Distribution Circuit | Vegetation | Tree - fell into line | 704 | 55051 | 38.8089 | -122.5709 | 18450 PARK POINT COURT /MTR#1008031391 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0066588 | OH | Sus | 31111193 | No | 2014 | OCT | Yes | Multi-Fault | 99201595 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 2341 | 20141115 | 1712 | 1113360 | 659 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 9135 | 38.8762 | -122.7303 | AT MTR#1008158810 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0070255 | OH | Sus | 31115331 | No | 2014 | NOV | Yes | Line to Line | 99199120 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3173 | 20141119 | 723 | 1114972 | 402 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 804 | 39.6337 | -123.7826 | 8 PAST FUSES | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0070819 | OH | Sus | 42277732 | No | 2014 | NOV | Yes |  | 99198730 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8533 | 20141119 | 1050 | 1115094 | 180 | Distribution Circuit | Equipment Failure/Involved | Other | 4 | 720 | 39.4882 | -123.7822 | 2 LS FUSES | Drizzle-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0070847 | OH | Sus | 42278028 | No | 2014 | NOV | Yes | None | 99198713 | CSO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 2971 | 20141119 | 1109 | 1115159 | 822 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 14796 | 40.8074 | -123.4787 | 2 SPANS LD SIDE OF 2971- UNDERWOOD MTN RD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0070911 | OH | Sus | 31116360 | No | 2014 | NOV | Yes | Line to Line | 99198681 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1873 | 20141120 | 235 | 1115469 | 420 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 840 | 40.0089 | -123.791 | 114982925104 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0070996 | OH | Sus | 42278213 | No | 2014 | NOV | Yes | Line to Line | 99198619 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MENDOCINO-1101 | 42951101 | FUSE | 919 | 20141122 | 2330 | 1117012 | 592 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2960 | 39.3876 | -123.2545 | 1ST SPAN LD SIDE OF 919- 6700 RIDGEWOOD RD | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0071651 | OH | Sus | 42280241 | No | 2014 | NOV | Yes | None | 99198161 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | OTHER |  | 20141122 | 116 | 1116507 | 447 | Distribution Circuit | Equipment Failure/Involved | Other | 162 | 28680 | 39.4714 | -123.3602 | AT FUCO 9211 ON MAIN LINE | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0071546 | OH | Sus | 42280127 | No | 2014 | NOV | Yes | Line to Ground | 99198273 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 3769 | 20141122 | 510 | 1116525 | 446 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 18090 | 39.4348 | -123.3795 | ESPINOLA- CHRISTOPHER: 25026 cobb dr | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0071551 | OH | Sus | 0 | No | 2014 | NOV | Yes |  | 99198269 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | OTHER |  | 20141202 | 1848 | 1121469 | 366 | Distribution Circuit | Vegetation | Tree - fell into line | 369 | 119725 | 39.5233 | -123.7616 | 27100 N HWY 1 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073077 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99197022 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 3109 | 20141202 | 948 | 1120732 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 23890 | 39.4628 | -123.7931 | 13 SPANS PAST FUSES | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0072870 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99197194 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 4479 | 20141202 | 719 | 1120515 | 391 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 7038 | 38.777 | -123.5138 | 39971 GUALALA CT | Drizzle-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0072813 | OH | Sus | 31118564 | yes | 2014 | DEC | Yes | Line to Line | 99197235 | CSO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 7871 | 20141202 | 1030 | 1120767 | 635 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 3175 | 38.9202 | -123.624 | WATSON- ARLIS JR: 3 SPANS LOAD SIDE OF COS | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0072993 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99197138 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MIDDLETOWN-1101 | 43141101 | RECLOSER | 622 | 20141204 | 809 | 1124291 | 512 | Distribution Circuit | 3rd Party | Vehicle | 391 | 32871 | 38.7461 | -122.6206 | 2 POLES LD OF LR 622 TWD 6717 | Overcast-32 - 90 F | Anchor or Guy | Broken, wire on ground | 14-0073729 | OH | Sus | 31119282 | yes | 2014 | DEC | Yes | Line to Ground | 99196510 | ANC | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | RECLOSER | 4622 | 20141205 | 1855 | 1125556 | 559 | Distribution Circuit | Vegetation | Tree - fell into line | 371 | 137417 | 39.5149 | -123.764 | MILE MARKER 77 ON HWY 101 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074093 | OH | Sus | 0 | No | 2014 | DEC | Yes | Line to Line | 99196150 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER | 31304 | 20141205 | 1929 | 1125584 | 519 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 42621 | 39.4147 | -123.7702 | AT FUCO 3071 TWD 5989 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074098 | OH | Sus | 0 | No | 2014 | DEC | Yes | Line to Line | 99196149 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | OTHER |  | 20141205 | 2325 | 1125984 | 981 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4905 | 38.8082 | -123.5901 | 2 SPANS PAST OPEN JUMPERS | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074157 | OH | Sus | 0 | No | 2014 | DEC | Yes | Line to Ground | 99196080 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3259 | 20141205 | 1825 | 1125513 | 1169 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 22211 | 41.3047 | -123.5344 | AT METER#1008022018 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074087 | OH | Sus | 0 | No | 2014 | DEC | Yes | Line to Line | 99196152 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | OTHER |  | 20141206 | 117 | 1125696 | 776 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 23960 | 38.9049 | -123.6181 | 39651 EUREKA HILL RD | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0074117 | OH | Sus | 0 | No | 2014 | DEC | Yes | None | 99196137 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | OTHER |  | 20141208 | 1007 | 1126871 | 277 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1662 | 39.4078 | -123.3047 | 4 SPANS SOURCE SIDE METER 1006275542 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074332 | OH | Sus | 0 | No | 2014 | DEC | Yes | Line to Ground | 99195853 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1104 | 42661104 | FUSE | 9109 | 20141209 | 1837 | 1127885 | 563 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 563 | 39.4133 | -123.4018 | 1 SPAN LOAD SIDE OF 9109 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074596 | OH | Sus | 42293642 | No | 2014 | DEC | Yes | Line to Line | 99195588 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1121 | 192021121 | FUSE | 1217 | 20141210 | 2331 | 1128712 | 973 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 62272 | 40.839 | -124.0234 | 114436855136 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074778 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99195323 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 87163 | 20141210 | 2346 | 1128724 | 794 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 16238 | 39.2257 | -123.7477 | 4 SPANS LOAD SIDE FUCO | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074810 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99195316 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 1637 | 20141210 | 2119 | 1128651 | 2648 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 50312 | 40.1474 | -123.6278 | RICHARDS- MARV: TO CREW | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074772 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99194421 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER |  | 20141210 | 745 | 1128032 | 794 | Distribution Circuit | Vegetation | Tree - fell into line | 370 | 206161 | 40.2288 | -124.111 | 15 SPANS FROM 8033 TWDS 7199 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074631 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99195532 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | FUSE | 1417 | 20141210 | 2307 | 1128700 | 1103 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 105888 | 39.3883 | -123.1163 | AT METER 1008709653 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074782 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99195321 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 8505 | 20141214 | 1720 | 1140617 | 689 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 8957 | 39.378 | -123.7983 | 1ST SPAN LD SIDE OF 8505 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076912 | OH | Sus | 42296504 | No | 2014 | DEC | Yes | Line to Line | 99193122 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3173 | 20141216 | 1646 | 1142427 | 854 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1708 | 39.6337 | -123.7826 | 2 SPANS FROM EOL | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077325 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99192644 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 8515 | 20141216 | 1405 | 1142309 | 166 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 830 | 38.6538 | -123.3999 | 4 SPANS PAST FUSES | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077285 | OH | Sus | 42299157 | yes | 2014 | DEC | Yes | Line to Line | 99192733 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 4213 | 20141216 | 721 | 1141902 | 260 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 5720 | 38.8305 | -122.7267 | 15785 RAINBOW DR | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077175 | OH | Sus | 42298099 | yes | 2014 | DEC | Yes | Line to Line | 99192827 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | RECLOSER | 29362 | 20141216 | 1453 | 1142347 | 644 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 96 | 61265 | 40.8943 | -123.7723 | 114994957951 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077265 | OH | Sus | 31121494 | yes | 2014 | DEC | Yes | Line to Ground | 99192746 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 85938 | 20141218 | 1000 | 1143620 | 175 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 175 | 39.4417 | -123.7514 | 1ST SPAN LD SIDE OF 85938 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077560 | OH | Sus | 0 | No | 2014 | DEC | Yes | Line to Line | 99192377 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 47881 | 20141218 | 1200 | 1143734 | 780 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 780 | 39.5089 | -123.383 | 1ST SPAN LD SIDE OF 47881 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077593 | OH | Sus | 31122056 | No | 2014 | DEC | Yes | Line to Ground | 99192282 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CARLOTTA-1121 | 192291121 | FUSE | 4065 | 20141219 | 606 | 1144105 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1182 | 40.5266 | -124.002 | 114431144043 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077656 | OH | Sus | 42301171 | No | 2014 | DEC | Yes | None | 99192261 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER 1101 | 192381101 | FUSE | 1915 | 20141219 | 1439 | 1144674 | 1146 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 2519 | 40.4649 | -124.2549 | 113772141924 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077748 | OH | Sus | 42301436 | No | 2014 | DEC | Yes | Line to Ground | 99192140 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | OTHER |  | 20141221 | 411 | 1145580 | 1089 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 15694 | 41.0766 | -123.6868 | HOSTLER CREEK AND MARSHALL LANE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077886 | OH | Sus | 31122432 | No | 2014 | DEC | Yes | Line to Ground | 99191997 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1106 | 43351106 | FUSE | 4123 | 20141221 | 205 | 1145321 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 47080 | 39 | -122.753 | 1 SPAN PAST FUCO | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077852 | OH | Sus | 42301641 | No | 2014 | DEC | Yes | Line to Ground | 99192032 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 1679 | 20141222 | 704 | 1145875 | 369 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 17343 | 40.2783 | -123.7929 | 115068334702 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077959 | OH | Sus | 0 | No | 2014 | DEC | Yes | Line to Ground | 99191897 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1121 | 192021121 | FUSE | 1269 | 20141224 | 1526 | 1147076 | 1014 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 7098 | 40.8153 | -123.9937 | 114488154514 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078280 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99191397 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | FUSE | 5457 | 20141224 | 1148 | 1147342 | 1037 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6222 | 40.8002 | -124.0383 | AT 3553 GREENWOOD HEIGHTS | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078320 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99191488 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER 1101 | 192381101 | FUSE | 1909 | 20141224 | 1138 | 1147327 | 936 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 5678 | 40.5118 | -124.1601 | 114012443561 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078251 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99191551 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | OTHER |  | 20141224 | 1350 | 1147466 | 571 | Distribution Circuit | Vegetation | Tree - grew into line | 11 | 6281 | 39.4824 | -123.7843 | 3 SPANS SS 6789 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078322 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99191486 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3969 | 20141224 | 1050 | 1147221 | 315 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 17955 | 39.3819 | -123.7744 | 12 SPANS PAST FUCO | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078234 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99191567 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER | 31304 | 20141224 | 1322 | 1147444 | 350 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 29130 | 39.4147 | -123.7702 | 3 SPANS SS OF 3909 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078261 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99191541 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 1677 | 20141224 | 1200 | 1147359 | 625 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 9375 | 39.4154 | -123.7817 | 19200 GORSTROM LN | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078270 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99191533 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1102 | 43311102 | RECLOSER | 64464 | 20141224 | 1437 | 1147554 | 243 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 28188 | 38.9442 | -122.6753 | 8 SPANS LOAD SIDE LR | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078283 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99191522 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | FUSE | 3909 | 20141224 | 954 | 1147443 | 1825 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 5475 | 40.404 | -123.9522 | 114559639573 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078238 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99191401 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3963 | 20141227 | 933 | 1149193 | 499 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1497 | 39.3532 | -123.559 | 3 SPANS LD SIDE OF 3963 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078658 | OH | Sus | 0 | No | 2014 | DEC | Yes | Line to Line | 99191094 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 6305 | 20150103 | 903 | 1158746 | 717 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2151 | 38.6569 | -123.3433 | 3 SPANS LOAD SIDE OF FUCO 6305 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0002270 | OH | Sus | 31124675 | No | 2015 | JAN | Yes | Line to Ground | 99189429 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 5657 | 20150105 | 944 | 1159393 | 976 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2902 | 40.0413 | -123.7812 | at 448 twin trees AND 4 SPANS LD SIDE OF 5657 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0002505 | OH | Sus | 31125122 | No | 2015 | JAN | Yes | Line to Line | 99189231 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | OTHER |  | 20150116 | 1213 | 1164793 | 293 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 2678 | 40.2167 | -123.7813 | 115029032743 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0005198 | OH | Sus | 0 | No | 2015 | JAN | Yes | None | 99187770 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | OCB | OCB | 20150116 | 2107 | 1165009 | 1366 | Distribution Circuit | Equipment Failure/Involved | Other | 2440 | 326907 | 38.7863 | -123.522 | 4 SPANS FROM SBCO 8845 TWDS SW 825 | Fog-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0005300 | OH | Sus | 31128981 | No | 2015 | JAN | Yes | Multi-Fault | 99187715 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1121 | 192021121 | FUSE | 1269 | 20150117 | 2203 | 1165326 | 411 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5754 | 40.8153 | -123.9937 | 114509253972 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0005459 | OH | Sus | 0 | No | 2015 | JAN | Yes | Line to Line | 99187665 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | REDBUD-1101 | 43191101 | FUSE | 82667 | 20150117 | 1051 | 1165141 | 947 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 947 | 39.0201 | -122.6865 | 2 SPANS PAST FUCO | Fog-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0005394 | OH | Sus | 0 | No | 2015 | JAN | Yes | Line to Ground | 99187692 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 3304 | 20150118 | 605 | 1165340 | 1341 | Distribution Circuit | Vegetation | Tree - fell into line | 627 | 708974 | 41.1058 | -123.688 | 115445468896 | Rain-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 15-0005462 | OH | Sus | 31129067 | No | 2015 | JAN | Yes | Three Phase Fault | 99187648 | CAW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1815 | 20150205 | 2243 | 1173019 | 615 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 17835 | 39.868 | -123.717 | FLECKLIN-PAUL/623/530-906-3142: 68100 PAGE AND JATES RD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009767 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99185347 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1121 | 192021121 | FUSE | 1269 | 20150209 | 659 | 1185773 | 423 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 5922 | 40.8153 | -123.9937 | S/O 7403 FICKLE HILL RD. | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012148 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183146 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER 1101 | 192381101 | OTHER |  | 20150209 | 1244 | 1186953 | 1411 | Distribution Circuit | Equipment Failure/Involved | Other | 7 | 8974 | 40.4364 | -124.3903 | 11 SPANS S/S OF 93155 | Strong winds-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0012273 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182759 | CSO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 62921 | 20150209 | 2035 | 1187199 | 990 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3960 | 39.8658 | -123.7122 | 67651 HWY 101 N ON FRONTAGE ROAD- LEGGETT | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012319 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182740 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 6467 | 20150209 | 2312 | 1187260 | 1016 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5080 | 39.8486 | -123.7097 | Cates-Doug/ 3878 /805-441-8785: 66000 drive trough tree rd 3 spans load side c/o 6467 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012333 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182733 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER |  | 20150209 | 1256 | 1186529 | 380 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 760 | 40.1272 | -123.8464 | Bradley- GERALDINE: 2298 BRICELAND RD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012166 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183134 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 6315 | 20150209 | 827 | 1185973 | 1788 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 12516 | 38.8497 | -123.6011 | S/S IVERSON RD.- 3-1/4 MI. E/O HWY 1- 300' W O MM 3.00 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012133 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182779 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | TRANSFORMER |  | 20150209 | 819 | 1185958 | 839 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 959 | 38.8344 | -123.5498 | JONES- MICHAEL: 9spans from C/O s 2345 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012282 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183073 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 5085 | 20150209 | 746 | 1185879 | 1964 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 33388 | 39.7076 | -123.5007 | MEADOW LN. 2 SPANS N/O TEN CREEK RD | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0012069 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99182517 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MIDDLETOWN-1101 | 43141101 | FUSE | 1071 | 20150209 | 500 | 1186594 | 1283 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 57735 | 38.7342 | -122.6314 | S OF 1071 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012193 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183122 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | FUSE | 1311 | 20150209 | 903 | 1186058 | 2492 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 32396 | 39.0072 | -123.4152 | 22201 MT VIEW RD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012185 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99182774 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | FUSE | 887 | 20150209 | 845 | 1187020 | 2155 | Distribution Circuit | Equipment Failure/Involved | Other | 28 | 60340 | 39.062 | -123.4354 | INDIAN CREEK RD. S/O PHILO | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012263 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182762 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | FUSE | 3739 | 20150209 | 1058 | 1187089 | 1987 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 3974 | 39.031 | -123.3865 | RAND-DAN/1508/530-913-6400: 4 spans east of c/o 3739 hwy 128 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012281 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182755 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | OTHER |  | 20150209 | 1255 | 1186186 | 1739 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 24216 | 39.4622 | -123.3491 | PATTERSON- N: 2 S/E/OF 3677 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012247 | OH | Sus | 0 | yes | 2015 | FEB | Yes | None | 99182764 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1104 | 42661104 | FUSE | 8681 | 20150209 | 749 | 1185884 | 583 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5247 | 39.3547 | -123.3345 | 100' W/O 17681 SHAFER RANCH RD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012085 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183187 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4593 | 20150210 | 1006 | 1187734 | 304 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 608 | 38.7355 | -123.3305 | PATTERSON TAP- PURCHASED LINE FROM DEPT. OF FORESTRY | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012478 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182652 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3247 | 20150210 | 401 | 1187337 | 704 | Distribution Circuit | Vegetation | Tree - branch fell on line | 82 | 57728 | 39.3284 | -123.7986 | 12121 PINEWOOD RD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012361 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182713 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 5233 | 20150210 | 722 | 1187533 | 544 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 22304 | 39.2282 | -123.7661 | ALBION LITTLE RIVER RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012356 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182715 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1260 | 20150210 | 930 | 1187683 | 768 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 72336 | 39.1295 | -123.7111 | GREENWOOD RD N/O ELK SUB | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012404 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182695 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 5533 | 20150210 | 435 | 1187453 | 645 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 18705 | 39.1895 | -123.7553 | HWY 1 & CAMERON RD. | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012416 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182686 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 1701 | 20150210 | 1206 | 1187886 | 134 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 2010 | 39.2234 | -123.7481 | 4 SPANS LD SIDE OF 1701 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012475 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182654 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 3975 | 20150210 | 1151 | 1187855 | 179 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 12530 | 39.2093 | -123.7102 | S/S ALBION RIDGE RD. E/O MIDDLE RIDGE RD. | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012524 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182623 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3159 | 20150210 | 227 | 1187303 | 473 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 11825 | 39.4817 | -123.7947 | 4 SPANS LD SIDE OF 3159 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012345 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182728 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 1767 | 20150210 | 445 | 1187457 | 105 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 840 | 39.6705 | -123.7785 | 2 SPANS LD SIDE OF 1767 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012348 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182724 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 979 | 20150210 | 1137 | 1187833 | 425 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3400 | 39.6552 | -123.7627 | MTR 90L733 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012470 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182506 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8567 | 20150210 | 1250 | 1187929 | 410 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 3690 | 39.5109 | -123.756 | RO 26450 SIMPSON | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012500 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182504 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 1603 | 20150210 | 453 | 1187568 | 468 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 29016 | 39.3904 | -123.8004 | McKinney/3244: N/OF C/O 5579 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012377 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182710 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3969 | 20150210 | 241 | 1187310 | 664 | Distribution Circuit | Vegetation | Tree - branch fell on line | 57 | 37848 | 39.3819 | -123.7744 | MITCHELL CREEK DR N/O GIBNEY LANE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012454 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182663 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3071 | 20150210 | 1129 | 1187822 | 366 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 366 | 39.4054 | -123.7237 | RENVILLE- GREG: 3 SPANS S/O FUSES | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012534 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182620 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3961 | 20150210 | 1200 | 1187875 | 156 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 2808 | 39.3597 | -123.647 | 40' S/O HWY 20 BETW. M.P. 11.17 & 11.50 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012538 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182616 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1757 | 20150210 | 216 | 1187299 | 931 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 14896 | 39.4416 | -123.7279 | SEVERAL SPANS PAST FUSES | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012536 | OH | Sus | 0 | yes | 2015 | FEB | Yes | None | 99182618 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 4365 | 20150210 | 739 | 1187246 | 441 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2205 | 39.961 | -123.7696 | 17 SPANS LOAD SIDE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012358 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182513 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 66323 | 20150210 | 1405 | 1187984 | 343 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 6860 | 39.8476 | -123.6988 | 65400 HWY 271- LEGGETT | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012530 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182621 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2555 | 20150210 | 1546 | 1188051 | 49 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 147 | 40.2735 | -124.2259 | EOL | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012563 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182502 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 2345 | 20150210 | 930 | 1187627 | 123 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 369 | 38.8337 | -123.5646 | IVERSEN RD. & FISH ROCK RD. EAST | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012389 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Multi-Fault | 99182511 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 48371 | 20150210 | 2034 | 1187700 | 105 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 105 | 39.6438 | -123.5315 | 4360 BRANSCOMB RD.- LAYTONVILLE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012598 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182583 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 5699 | 20150210 | 328 | 1187318 | 1112 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 15568 | 39.277 | -123.5861 | 1 SPAN PAST FUCO | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012385 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182706 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 4415 | 20150210 | 726 | 1187541 | 417 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 20850 | 39.2651 | -123.5917 | DOCKER HILL TAP | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012387 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182705 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 9155 | 20150210 | 942 | 1187694 | 1148 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 9184 | 39.1702 | -123.5699 | AT RISER 5439 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012516 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182629 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 2317 | 20150210 | 730 | 1187546 | 2099 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 14693 | 39.2646 | -123.5665 | 30000 COMPTCHE-UKIAH RD. E/O GRIMES RANCH | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012567 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182501 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 9135 | 20150210 | 744 | 1187996 | 1001 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4004 | 39.2534 | -123.5887 | 8025 FLYNN CRK RD E/S 3000' S/O COMPTCHE UKIAH RD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012568 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182603 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 9075 | 20150210 | 1632 | 1188086 | 753 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 14307 | 39.1238 | -123.4903 | 3 SPANS LOADSIDE OF OJ/SS/O/MTR1009997271 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012622 | OH | Sus | 0 | yes | 2015 | FEB | Yes | None | 99182571 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 5365 | 20150210 | 1814 | 1188141 | 234 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 468 | 39.4472 | -123.4265 | ALL OVER | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012583 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182591 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | OTHER |  | 20150221 | 1242 | 1193572 | 736 | Distribution Circuit | Vegetation | Tree - branch fell on line | 227 | 33822 | 40.0348 | -123.9498 | 25 SPANS LD SIDE OF LR 6084 at MTR#1008024462 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0014762 | OH | Sus | 42337146 | No | 2015 | FEB | Yes | None | 99181078 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 8391 | 20150222 | 1321 | 1194032 | 806 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 2 | 1612 | 39.2767 | -123.7131 | 4 SPANS LD SIDE OF 8391 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0014853 | OH | Sus | 42337167 | No | 2015 | FEB | Yes | Line to Ground | 99180981 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1817 | 20150223 | 516 | 1194326 | 1905 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4051 | 39.8644 | -123.7248 | 115127319838 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0014958 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99180712 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 6467 | 20150223 | 722 | 1194371 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1010 | 39.8486 | -123.7097 | 115204819164 | Strong winds-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0014993 | OH | Sus | 42337494 | yes | 2015 | FEB | Yes | Line to Ground | 99180856 | CSO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3047 | 20150227 | 1141 | 1196704 | 259 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 25 | 6475 | 39.2612 | -123.7308 | 5 SPANS LOAD SIDE OF 3047 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0016208 | OH | Sus | 42340005 | No | 2015 | FEB | Yes | Line to Ground | 99180140 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1106 | 43351106 | FUSE | 4123 | 20150304 | 1844 | 1199450 | 276 | Distribution Circuit | Equipment Failure/Involved | Other | 107 | 29532 | 39 | -122.753 | 2983 BUCKINGHAM DR | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0017374 | OH | Sus | 42342337 | No | 2015 | MAR | Yes | Line to Ground | 99179381 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | FUSE | 3937 | 20150306 | 1219 | 1200117 | 457 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5484 | 40.3233 | -123.919 | 399 MADRONE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0017809 | OH | Sus | 31139190 | No | 2015 | MAR | Yes | Line to Ground | 99179140 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOPLAND-1101 | 42251101 | FUSE | 2701 | 20150307 | 839 | 1200405 | 159 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 159 | 39.0183 | -123.0421 | AT FUCO 2701 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0017981 | OH | Sus | 42344407 | No | 2015 | MAR | Yes | Line to Line | 99179045 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | FUSE | 3719 | 20150310 | 1952 | 1201886 | 593 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 53370 | 38.9047 | -123.2249 | 2 SPANS LOAD SIDE OF METER#1006276451 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0018714 | OH | Sus | 42347969 | No | 2015 | MAR | Yes | Line to Line | 99178638 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 2373 | 20150314 | 230 | 1203405 | 570 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2280 | 38.9035 | -122.758 | 9210 WILDCAT RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0019556 | OH | Sus | 31141248 | No | 2015 | MAR | Yes | Line to Ground | 99178176 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARTLEY-1102 | 43211102 | OCB | OCB | 20150315 | 713 | 1203774 | 246 | Distribution Circuit | Animal | Bird found | 1474 | 89731 | 39.0775 | -122.933 | 3039 LAKESHORE BLVD IN LAKEPORT | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0019661 | OH | Sus | 42350145 | No | 2015 | MAR | Yes | Line to Line | 99178085 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | RECLOSER | 3700 | 20150316 | 725 | 1203992 | 530 | Distribution Circuit | Equipment Failure/Involved | Other | 242 | 128260 | 38.9964 | -123.3568 | MTR#424J81 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0019742 | OH | Sus | 31141597 | No | 2015 | MAR | Yes | Line to Line | 99177999 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3261 | 20150321 | 1650 | 1206411 | 1247 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 12 | 14964 | 41.19 | -123.6909 | 115347068050 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0021164 | OH | Sus | 31142695 | No | 2015 | MAR | Yes | Line to Line | 99177282 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1793 | 20150324 | 1400 | 1207505 | 430 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3440 | 40.0259 | -123.9474 | 114506025592 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0021811 | OH | Sus | 42356967 | No | 2015 | MAR | Yes | None | 99176950 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3969 | 20150328 | 2358 | 1209344 | 662 | Distribution Circuit | Vegetation | Tree - branch fell on line | 57 | 37734 | 39.3819 | -123.7744 | 9/S/LD SIDE OF FUSES 3969 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0022777 | OH | Sus | 42358803 | No | 2015 | MAR | Yes | Line to Ground | 99176387 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 9141 | 20150331 | 1433 | 1210793 | 667 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3052 | 39.2215 | -123.5986 | 11 SPANS LD SIDE OF 9141 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0023363 | OH | Sus | 31144993 | No | 2015 | MAR | Yes | Line to Line | 99176031 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 37506 | 20150403 | 849 | 1212068 | 328 | Distribution Circuit | Vegetation | Tree - bark fell into line | 89 | 23757 | 39.4832 | -123.3603 | 30000 N HWY 101 (PAST FUCO 92673) | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0023996 | OH | Sus | 0 | No | 2015 | APR | Yes | Line to Ground | 99175556 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 67443 | 20150404 | 1146 | 1212671 | 1405 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 32315 | 41.2621 | -123.7728 | 115130970878 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0024209 | OH | Sus | 31145805 | No | 2015 | APR | Yes | Line to Ground | 99175381 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER | 75382 | 20150404 | 1243 | 1212563 | 738 | Distribution Circuit | Vegetation | Tree - fell into line | 416 | 76746 | 38.9063 | -122.6735 | ON MAINLINE 1 SPAN FROM 3689 TWD 3691 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0024194 | OH | Sus | 0 | No | 2015 | APR | Yes | Line to Ground | 99175427 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 1637 | 20150407 | 543 | 1214501 | 345 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 6555 | 40.1474 | -123.6278 | 115428830049 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0024755 | OH | Sus | 0 | yes | 2015 | APR | Yes | Line to Ground | 99175038 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER |  | 20150407 | 903 | 1214648 | 368 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 11336 | 40.2971 | -124.3053 | 15 SPANS LD SIDE OF 2505 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0024803 | OH | Sus | 0 | yes | 2015 | APR | Yes | Line to Ground | 99175011 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER | 75382 | 20150407 | 1318 | 1215069 | 476 | Distribution Circuit | Vegetation | Tree - fell into line | 416 | 61339 | 38.9063 | -122.6735 | 2 SPANS FROM 3689 TWD 6273 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0024956 | OH | Sus | 0 | yes | 2015 | APR | Yes | Line to Line | 99174772 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MAPLE CREEK-1101 | 192101101 | FUSE | 5917 | 20150413 | 1933 | 1218904 | 602 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 602 | 40.7492 | -123.8676 | 114814751980 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0026423 | OH | Sus | 31147999 | yes | 2015 | APR | Yes | Line to Ground | 99173782 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 2807 | 20150414 | 1800 | 1219528 | 1117 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 2 | 672 | 39.7035 | -123.3899 | 1 SPAN LOAD SIDE OF 2807 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0026732 | OH | Sus | 42368686 | No | 2015 | APR | Yes | Line to Ground | 99173543 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | OCB | OCB | 20150423 | 1413 | 1223723 | 489 | Distribution Circuit | Equipment Failure/Involved | Other | 1276 | 323788 | 38.786 | -123.5221 | 1 SPAN LD SIDE OF 9287 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0029002 | OH | Sus | 42373352 | yes | 2015 | APR | Yes | Line to Ground | 99172197 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MAPLE CREEK-1101 | 192101101 | FUSE | 5917 | 20150425 | 504 | 1224693 | 311 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 311 | 40.7492 | -123.8676 | 114814751980 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0029460 | OH | Sus | 31150792 | yes | 2015 | APR | Yes | Line to Ground | 99171900 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 3304 | 20150503 | 19 | 1228554 | 802 | Distribution Circuit | Vegetation | Tree - fell into line | 626 | 439189 | 41.1058 | -123.688 | 115449969275 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0031298 | OH | Sus | 31152521 | No | 2015 | MAY | Yes | Three Phase Fault | 99170635 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 6461 | 20150505 | 2038 | 1229691 | 711 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 19908 | 41.2967 | -123.5599 | 115716171924 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0032042 | OH | Sus | 31153020 | No | 2015 | MAY | Yes | Line to Ground | 99170250 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 4599 | 20150509 | 1405 | 1232059 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2240 | 40.2376 | -123.8334 | 114876833543 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0033093 | OH | Sus | 42383855 | No | 2015 | MAY | Yes | Line to Line | 99169431 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 4744 | 20150511 | 1042 | 1232628 | 313 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 189 | 32187 | 40.2784 | -124.2438 | 113628936873 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0033294 | OH | Sus | 0 | No | 2015 | MAY | Yes | Line to Ground | 99169264 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER 1101 | 192381101 | OTHER |  | 20150513 | 2232 | 1234063 | 518 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1 | 518 | 40.4927 | -124.207 | at MTR#1009639- 3627 PRICE CREEK RD | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0033942 | OH | Sus | 42387398 | No | 2015 | MAY | Yes | Line to Ground | 99168790 | CSO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 37506 | 20150523 | 1947 | 1238882 | 677 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 35434 | 39.4832 | -123.3603 | ON MAIN LINE 4 SPANS NORTH OF FUCO 925741 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0036181 | OH | Sus | 31156784 | No | 2015 | MAY | Yes | Line to Ground | 99167212 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 7299 | 20150531 | 1539 | 1241737 | 353 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 706 | 38.8127 | -123.5951 | 1 SPAN LOAD SIDE OF 7299 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0037493 | OH | Sus | 42398074 | No | 2015 | MAY | Yes | Line to Ground | 99166306 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 4223 | 20150603 | 922 | 1243023 | 119 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 238 | 39.8243 | -123.6556 | 115357918198 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0038089 | OH | Sus | 31158805 | No | 2015 | JUN | Yes | Line to Ground | 99165844 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5731 | 20150604 | 1317 | 1243643 | 873 | Distribution Circuit | 3rd Party | Vehicle | 50 | 20525 | 39.269 | -123.7818 | 1 POLE SOUTH OF 4985 ON MAINLINE | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0038501 | OH | Sus | 31159127 | No | 2015 | JUN | Yes | Three Phase Fault | 99165615 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | FUSE | 4917 | 20150604 | 1727 | 1243793 | 363 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 363 | 40.3261 | -123.9256 | 114629936770 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0038566 | OH | Sus | 0 | No | 2015 | JUN | Yes | Line to Line | 99165587 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | FUSE | 1413 | 20150605 | 2344 | 1244620 | 495 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4950 | 38.9037 | -123.3154 | 20111 FISH ROCK ROAD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0038991 | OH | Sus | 42401461 | yes | 2015 | JUN | Yes | Line to Ground | 99165279 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | FUSE | 9247 | 20150606 | 1538 | 1244920 | 437 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1748 | 39.0409 | -123.4019 | 2 SPANS SOURCE SIDE OF METER#1008729339 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0039056 | OH | Sus | 31159498 | No | 2015 | JUN | Yes | Line to Line | 99165223 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | REDBUD-1102 | 43191102 | OTHER |  | 20150609 | 1526 | 1247861 | 659 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 659 | 39.0052 | -122.7254 | ON HARD TAP 7 SPANS LD SIDE OF 3623 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0039866 | OH | Sus | 31160195 | yes | 2015 | JUN | Yes | Line to Ground | 99164573 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2117 | 20150610 | 802 | 1248260 | 315 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 3987 | 39.4567 | -123.3861 | 26063 PEACOCK RD.- WILLITS | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0039976 | OH | Sus | 42404406 | yes | 2015 | JUN | Yes | Line to Line | 99164430 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 4365 | 20150611 | 1315 | 1249308 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2200 | 39.961 | -123.7696 | 8/SPANS/LOADSIDE/O/1703 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0040446 | OH | Sus | 42405117 | No | 2015 | JUN | Yes | None | 99164117 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 37202 | 20150619 | 1901 | 1253514 | 633 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 63 | 39879 | 41.189 | -123.7101 | 115244268392 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0042222 | OH | Sus | 31162526 | No | 2015 | JUN | Yes | Line to Ground | 99162818 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 8652 | 20150625 | 1344 | 1256489 | 673 | Distribution Circuit | 3rd Party | Vehicle | 248 | 30165 | 40.1065 | -123.928 | 114582128208 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0043363 | OH | Sus | 31164307 | yes | 2015 | JUN | Yes | Three Phase Fault | 99161970 | PW | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3335 | 20150626 | 736 | 1256891 | 336 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 13776 | 41.0995 | -123.7118 | 115271065302 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0043518 | OH | Sus | 31164369 | yes | 2015 | JUN | Yes | Line to Line | 99161852 | CO | OH | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 4923 | 20150629 | 844 | 1258495 | 438 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5256 | 38.9453 | -123.6467 | 39320 BUCKRIDGE RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0043965 | OH | Sus | 0 | No | 2015 | JUN | Yes | Three Phase Fault | 99161379 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARTLEY-1101 | 43211101 | JUMPER | 94485 HI SIDE OJ | 20150708 | 1710 | 1265112 | 702 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2808 | 39.0666 | -122.9214 | AT FUCO 94485 | Partly Cloudy-32-90 F | Cutout, fuse holder | Broken, wire on ground | 15-0046405 | OH | Sus | 0 | yes | 2015 | JUL | Yes | Open Circuit | 1144443 | CFH | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER | 4634 | 20150709 | 826 | 1265366 | 325 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1100 | 125096 | 39.3615 | -123.1275 | 2 SPANS FROM ABB 1449 TWDS LR 64118 | Overcast-Fog-Drizzle-32-90 F | Insulator | Broken, wire on ground | 15-0046518 | OH | Sus | 0 | yes | 2015 | JUL | Yes | Line to Ground | 1144562 | INS | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MAPLE CREEK-1101 | 192101101 | FUSE | 6529 | 20150710 | 745 | 1266004 | 539 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1617 | 40.7487 | -123.8678 | 2 SPANS LD SIDE OF 6529 | Overcast-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 15-0046729 | OH | Sus | 31167696 | No | 2015 | JUL | Yes | Line to Line | 1144700 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1514 | 20150714 | 633 | 1267629 | 647 | Distribution Circuit | 3rd Party | Vehicle | 559 | 20564 | 40.0478 | -123.79 | at FUCO 87169- HWY 101 200' S/O Milky Way- Piercy | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0047264 | OH | Sus | 0 | No | 2015 | JUL | Yes | Line to Line | 1145112 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HIGHLANDS-1103 | 43361103 | FUSE | 9661 | 20150729 | 1751 | 1279833 | 8518 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 144 | 254744 | 38.8942 | -122.5482 | Morgan Valley RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0051473 | OH | Sus | 0 | yes | 2015 | JUL | Yes | Force Out | 1148185 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4597 | 20150809 | 1232 | 1285524 | 952 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 8568 | 38.729 | -123.3499 | 3 SPANS SS OF 4599 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0053922 | OH | Sus | 0 | No | 2015 | AUG | Yes | Three Phase Fault | 1149930 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3757 | 20150812 | 1738 | 1287468 | 584 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 14640 | 40.2286 | -123.8633 | ON HARD TAP 1 SPAN SS OF 6789 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0054643 | OH | Sus | 0 | No | 2015 | AUG | Yes | Line to Ground | 1150456 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 2345 | 20150817 | 1733 | 1290517 | 490 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 676 | 38.8337 | -123.5647 | 15 SPANS LOAD SIDE OF 2345 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0055664 | OH | Sus | 0 | yes | 2015 | AUG | Yes | Line to Ground | 1151213 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CALPELLA-1101 | 43411101 | FUSE | 6657 | 20150819 | 620 | 1291286 | 381 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 5403 | 39.2812 | -123.2624 | MTR#5000122598 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0055982 | OH | Sus | 0 | No | 2015 | AUG | Yes | Line to Ground | 1151424 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HIGHLANDS-1104 | 43361104 | RECLOSER | 84640 | 20150823 | 1404 | 1293328 | 968 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 16815 | 38.936 | -122.6187 | 5 SPANS LOAD SIDE OF 86953 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0056827 | OH | Sus | 31178327 | No | 2015 | AUG | Yes | Multi-Fault | 1151953 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CARLOTTA-1121 | 192291121 | FUSE | 7723 | 20150824 | 1633 | 1293914 | 707 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 19089 | 40.5141 | -123.9909 | 5 SPANS LOADSIDE OF 7723 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 15-0057069 | OH | Sus | 0 | No | 2015 | AUG | Yes | Line to Ground | 1152128 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 5407 | 20150825 | 1943 | 1294589 | 446 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 892 | 40.8886 | -123.561 | 2 SPANS LOADSIDE OF 5407 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0057352 | OH | Sus | 0 | No | 2015 | AUG | Yes | Line to Ground | 1152303 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CALPELLA-1101 | 43411101 | JUMPER | OJ'S 2 POLES S/OF MTR# 1009790470 | 20150829 | 641 | 1296602 | 343 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1029 | 39.2567 | -123.1442 | GALLETTI- TIM: WIRE DOWN/ BURNT XARM at 7276 BLACK BART TRAIL | Overcast-32-90 F | Insulator | Broken, wire on ground | 15-0058141 | OH | Sus | 31180186 | yes | 2015 | AUG | Yes | Line to Ground | 1152844 | INS | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 3079 | 20150907 | 824 | 1301164 | 728 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 25480 | 40.7987 | -123.4049 | 2 SPANS SS OF 2987 ON MAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0059646 | OH | Sus | 31182055 | No | 2015 | SEP | Yes | Three Phase Fault | 1154008 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MIDDLETOWN-1101 | 43141101 | OCB | OCB | 20150912 | 2114 | 1304746 | 12889 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 969 | 8844 | 38.7527 | -122.6087 | Multiple Damage Locations | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 15-0061044 | OH | Sus | 0 | No | 2015 | SEP | Yes | Force Out | 1154929 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MIDDLETOWN-1102 | 43141102 | OCB | OCB | 20150912 | 1840 | 1304700 | 12603 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 787 | 4058 | 38.7529 | -122.6088 | VARIOUS | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0061034 | OH | Sus | 0 | No | 2015 | SEP | Yes | Force Out | 1154919 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MIDDLETOWN-1103 | 43141103 | OCB | OCB | 20150912 | 2114 | 1304747 | 11244 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 49 | 2259 | 38.7526 | -122.6086 | VARIOUS | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 15-0061045 | OH | Sus | 0 | No | 2015 | SEP | Yes | Force Out | 1154930 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 5643 | 20150913 | 1126 | 1304968 | 352 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 56 | 10835 | 39.3848 | -123.7847 | 17451 AMETHYST | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0061086 | OH | Sus | 42470143 | No | 2015 | SEP | Yes | Line to Ground | 1154976 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HIGHLANDS-1104 | 43361104 | FUSE | 8877 | 20150913 | 1340 | 1305000 | 162 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 2106 | 38.9258 | -122.6139 | 16021 DAM RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0061091 | OH | Sus | 0 | No | 2015 | SEP | Yes | Line to Ground | 1154980 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER | 75382 | 20150913 | 512 | 1304871 | 13658 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 308 | 736 | 38.9063 | -122.6735 | MULTIPLE LOCATIONS | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 15-0061059 | OH | Sus | 0 | No | 2015 | SEP | Yes | None | 1154944 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | SWITCH | 4313 | 20150913 | 554 | 1304874 | 7422 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 237 | 237 | 38.8799 | -122.7335 | Multiple Damage Locations | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 15-0061061 | OH | Sus | 0 | No | 2015 | SEP | Yes | None | 1154946 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARTLEY-1101 | 43211101 | OCB | OCB | 20150914 | 1721 | 1305713 | 272 | Distribution Circuit | 3rd Party | Vehicle | 2992 | 283301 | 39.077 | -122.9333 | CORNER OF 11'TH AND NORTH MAIN | Partly Cloudy-32-90 F | Anchor or Guy | Broken, wire on ground | 15-0061335 | OH | Sus | 42470697 | yes | 2015 | SEP | Yes | Line to Ground | 1155154 | ANC | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1101 | 192461101 | OCB | OCB | 20150921 | 1423 | 1309561 | 762 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 13197 | 40.4798 | -123.7798 | Trumbo- Maurice 408 646 7337: 0.5 miles past bridgeville sub on hwy 36- mm29.1 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0062556 | OH | Sus | 42481132 | No | 2015 | SEP | Yes | Line to Ground | 1156136 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | RECLOSER | 608 | 20150924 | 714 | 1311129 | 289 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 5014 | 38.6769 | -123.314 | 8 SPANS FROM 4563 TWDS LR 608 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0063019 | OH | Sus | 0 | No | 2015 | SEP | Yes | Line to Ground | 1156486 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | FUSE | 1959 | 20151017 | 1526 | 1324289 | 174 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 174 | 40.337 | -124.0306 | LOAD SIDE OF MTR #1008278597 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 15-0071320 | OH | Sus | 0 | yes | 2015 | OCT | Yes | Line to Line | 1163012 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1102 | 43311102 | RECLOSER | 596 | 20151019 | 758 | 1325870 | 978 | Distribution Circuit | 3rd Party | Vehicle | 1115 | 136885 | 38.9407 | -122.781 | 4600 KONOCTI RD | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 15-0071745 | OH | Sus | 0 | No | 2015 | OCT | Yes | Line to Line | 1163418 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CARLOTTA-1121 | 192291121 | RECLOSER | 44150 | 20151028 | 848 | 1330285 | 58 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 638 | 40.4948 | -123.9879 | 1 SPAN WEST OF 4071 TWD 44150 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0073785 | OH | Sus | 42554693 | No | 2015 | OCT | Yes | Force Out | 1164942 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | OTHER | WIRE DOWN | 20151030 | 429 | 1331382 | 491 | Distribution Circuit | 3rd Party | Vehicle | 704 | 273183 | 39.5078 | -123.767 | 1 SPAN SS OF 4617 | Fog-32-90 F | Pole-Wood | Broken, wire on ground | 15-0074188 | OH | Sus | 0 | No | 2015 | OCT | Yes | Line to Ground | 1165295 | PW | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 2653 | 20151102 | 850 | 1333131 | 378 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3024 | 38.9311 | -123.6918 | 1 AND 3 SPANS PAST FUSES | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0074802 | OH | Sus | 31196779 | yes | 2015 | NOV | Yes | Line to Line | 1165856 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | SECTIONALIZER | 6064 | 20151104 | 1212 | 1335321 | 293 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 63 | 18459 | 40.2952 | -123.8205 | 2 SPANS LOADSIDE OF MTR#1007959810 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0075565 | OH | Sus | 42559672 | No | 2015 | NOV | Yes | Line to Ground | 1166459 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3099 | 20151109 | 942 | 1337906 | 162 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 14256 | 39.4211 | -123.7804 | WATSON- ARLIS JR: 20109 hanson RD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0076628 | OH | Sus | 42564046 | yes | 2015 | NOV | Yes | Line to Line | 1167354 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 8201 | 20151113 | 1500 | 1340706 | 792 | Distribution Circuit | 3rd Party | Vehicle | 9 | 4568 | 40.0546 | -123.9749 | MTR#012411 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 15-0077687 | OH | Sus | 0 | No | 2015 | NOV | Yes | Line to Line | 1168148 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 6789 | 20151115 | 932 | 1341539 | 240 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 3360 | 40.2183 | -123.8718 | 5 SPANS PAST METER 1009362636 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0077863 | OH | Sus | 0 | yes | 2015 | NOV | Yes | Line to Ground | 1168340 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1569 | 20151123 | 1352 | 1347454 | 335 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 6 | 2010 | 40.0192 | -123.7961 | at MTR 1008673782 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0080160 | OH | Sus | 0 | No | 2015 | NOV | Yes | Line to Line | 1170200 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | FUSE | 6779 | 20151124 | 2122 | 1348299 | 941 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4744 | 40.7967 | -124.0326 | at MTR#1006221976 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0080964 | OH | Sus | 0 | yes | 2015 | NOV | Yes | Line to Line | 1170855 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1121 | 192021121 | FUSE | 1217 | 20151203 | 733 | 1352338 | 327 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 16350 | 40.8391 | -124.0234 | 1/SP/SOURCESIDE/OF/8815 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082391 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1172098 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1121 | 192021121 | FUSE | 1269 | 20151203 | 641 | 1352821 | 729 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 10206 | 40.8153 | -123.9938 | 7 SPANS LOAD SIDE OF 8833 FICKLE HILL RD | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 15-0082474 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1172169 | PW | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CARLOTTA-1121 | 192291121 | FUSE | 5429 | 20151203 | 1003 | 1352521 | 315 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 945 | 40.5514 | -124.1124 | 2 SPANS LOAD SIDE OF 5429 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082470 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1172167 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER 1101 | 192381101 | JUMPER | 1 SS OF MTR #1009766342 | 20151203 | 652 | 1353029 | 520 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1433 | 40.509 | -124.1549 | 1 SPAN SS OF MTR #1009766342 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082538 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1172222 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1793 | 20151203 | 1249 | 1352853 | 291 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2328 | 40.0259 | -123.9474 | 6 SPANS LOAD SIDE OF 1793 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082560 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1172233 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER | 445166 | 20151203 | 831 | 1352409 | 479 | Distribution Circuit | Vegetation | Tree - branch fell on line | 315 | 150885 | 38.6936 | -123.4237 | 1 SPAN SOURCESIDE OF 92493 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082447 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1172147 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1102 | 43311102 | FUSE | 88607 | 20151203 | 1132 | 1352697 | 211 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 15403 | 38.9491 | -122.8481 | 1 SPAN SOURCESIDE OF MTR1009250655 TWD 88607 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082477 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Three Phase Fault | 1172172 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 97045 | 20151203 | 826 | 1352389 | 554 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1108 | 38.901 | -123.6779 | EOL | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082386 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1172091 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER | 4230 | 20151203 | 432 | 1352187 | 242 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 6050 | 40.4175 | -124.0895 | BET LR 4230 & SBCO908763 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082334 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Three Phase Fault | 1172026 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1102 | 192171102 | OTHER | WIRE DOWN BET POLE 24/0 & 24/1 | 20151204 | 1347 | 1353906 | 444 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 888 | 40.9919 | -123.6425 | BET POLE 24/0 & 24/1 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082818 | OH | Sus | 31204314 | No | 2015 | DEC | Yes | Line to Line | 1172441 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | JUMPER | AT METER 51R190 | 20151205 | 2048 | 1354472 | 267 | Distribution Circuit | Vegetation | Tree - branch fell on line | 72 | 12217 | 40.7975 | -124.0321 | at MTR#51R190 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082991 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Ground | 1172589 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 6645 | 20151206 | 425 | 1354558 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 3900 | 39.2425 | -123.7696 | JONES- MICHAEL: 3/S/LOADISE OF 6645 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083013 | OH | Sus | 42583659 | No | 2015 | DEC | Yes | Line to Line | 1172616 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 7415 | 20151209 | 2139 | 1356537 | 391 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 1955 | 39.227 | -123.7445 | 3401 ALBION RIDGE RD- 2 SPANS LD SIDE OF 7415 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083712 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1173351 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 2010 | 20151209 | 2353 | 1356583 | 2293 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 108214 | 40.1417 | -123.808 | 3 SPANS LOAD SIDE OF 7861 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083695 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Multi-Fault | 1173334 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HUMBOLDT BAY-1102 | 192341102 | FUSE | 4301 | 20151209 | 2103 | 1356926 | 1067 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 23309 | 40.7036 | -124.1537 | 11 SPANS LOAD SIDE OF 4301 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083752 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1173391 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MAPLE CREEK-1101 | 192101101 | FUSE | 5917 | 20151209 | 1911 | 1356508 | 474 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 474 | 40.7493 | -123.8676 | 6 SPANS LD SIDE OF FUCO 5917 at 7TH POLE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083688 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1173326 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | FUSE | 1217 | 20151210 | 700 | 1357283 | 430 | Distribution Circuit | Vegetation | Tree - branch fell on line | 64 | 27520 | 40.8391 | -124.0234 | HANSON- SCOTT 707-834-6310: 6350 Fickle Hill Rd. | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083867 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1173510 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 56048 | 20151210 | 19 | 1356866 | 761 | Distribution Circuit | Equipment Failure/Involved | Overhead | 370 | 280930 | 40.1476 | -124.0197 | BRYAN- JOSEPH 707 298 1053: 15 SPNS LD SD C/O 2531 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083754 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1173393 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 67443 | 20151210 | 945 | 1357557 | 1742 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 38324 | 41.2621 | -123.7729 | 1/4 MILE LD SIDE OF 67443 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084056 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1173670 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MENDOCINO-1101 | 42951101 | FUSE | 3443 | 20151210 | 136 | 1356872 | 467 | Distribution Circuit | Animal | Other | 134 | 19885 | 39.267 | -123.2042 | O`Haire- Sean: meter 1010026031 | Overcast-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 15-0083720 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1173359 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 3023 | 20151210 | 52 | 1356837 | 2526 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 17682 | 40.9122 | -123.8162 | MTR1008277363 | Partly Cloudy-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083939 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1173583 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 7283 | 20151210 | 654 | 1357190 | 2172 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2172 | 40.9118 | -123.7052 | 1 PAST FUSES | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083968 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1173607 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 2937 | 20151210 | 49 | 1356943 | 1340 | Distribution Circuit | Vegetation | Tree - bark fell into line | 66 | 23586 | 40.8928 | -123.5859 | MTR 1008673429 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083739 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1173378 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | SWITCH | 7313 | 20151211 | 1319 | 1358927 | 541 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2164 | 40.029 | -123.9173 | MTR# 1008027517 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084318 | OH | Sus | 0 | yes | 2015 | DEC | Yes | None | 1173940 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3369 | 20151211 | 137 | 1358361 | 1399 | Distribution Circuit | Vegetation | Tree - bark fell into line | 18 | 25182 | 41.3725 | -123.5024 | MTR#1008024624 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084203 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1173822 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 7535 | 20151211 | 1114 | 1358825 | 676 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3380 | 41.1275 | -123.7251 | 4 SPANS SS OF TRANSF FEEDING MTR 1008025493 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084305 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1173930 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5211 | 20151214 | 949 | 1363339 | 589 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1178 | 39.2909 | -123.7656 | 43000 COMPTCHE UKAIH RD at DEAD END | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0085326 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1175012 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1122 | 192321122 | FUSE | 1653 | 20151217 | 755 | 1365476 | 540 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 25920 | 40.2385 | -123.6316 | 1 SPAN SOURCESIDE OF MTR#1009650360 AND SECOND LOCATION ADJACENT SPAN | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0085923 | OH | Sus | 31207207 | No | 2015 | DEC | Yes | Line to Ground | 1175755 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 4197 | 20151218 | 950 | 1366098 | 305 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 4575 | 39.3121 | -123.7664 | AT MTR #1009205714 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086072 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Line | 1176002 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1757 | 20151220 | 1530 | 1367156 | 738 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 14760 | 40.0692 | -123.8296 | at MTR1009916414 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086324 | OH | Sus | 31207693 | No | 2015 | DEC | Yes | Three Phase Fault | 1176287 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | FUSE | 4137 | 20151220 | 1051 | 1367052 | 408 | Distribution Circuit | Equipment Failure/Involved | Overhead | 72 | 26451 | 40.4496 | -123.5272 | 1 SPAN LOADSIDE OF MTR#1008688343 | Overcast-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on object | 15-0086301 | OH | Sus | 42595311 | No | 2015 | DEC | Yes | Force Out | 1176262 | CSO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 607 | 20151221 | 751 | 1367519 | 349 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 16403 | 38.8644 | -122.6928 | 6 POLES LOADSIDE OF 607 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 15-0086397 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1176380 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | RECLOSER | 1308 | 20151221 | 1211 | 1367805 | 262 | Distribution Circuit | Vegetation | Tree - fell into line | 292 | 66776 | 39.1869 | -123.5808 | ON MAINLINE- 4 SPANS SOURCE SIDE OF 5141 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086451 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1176440 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 8373 | 20151221 | 1620 | 1368099 | 180 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 540 | 38.9126 | -123.6368 | 4 SPANS S/OF 8373 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 15-0086494 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1176488 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 7695 | 20151222 | 859 | 1369202 | 363 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 363 | 39.2713 | -123.7629 | 2 SPANS LOADSIDE OF 7695 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086751 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1176767 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 5673 | 20151222 | 1317 | 1369478 | 393 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1179 | 39.1757 | -123.576 | 17001 APPIAN WAY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086793 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1176816 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3157 | 20151223 | 1446 | 1370470 | 144 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 456 | 39.6479 | -123.773 | 2 SPANS FROM EOL | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086989 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Ground | 1177052 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | BRIDGEVILLE-1102 | 192461102 | FUSE | 3707 | 20151225 | 1857 | 1371835 | 1374 | Distribution Circuit | Environmental/External | Ice or snow | 7 | 9618 | 40.4378 | -123.7835 | 4 SPANS FROM 3711 TWD 3707 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087431 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Ground | 1177512 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | BRIDGEVILLE-1102 | 192461102 | FUSE | 4689 | 20151225 | 855 | 1371652 | 3543 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 7086 | 40.3511 | -123.7147 | at EOL TWDS TRANSF#115259537615 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0087492 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Line | 1177578 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 8189 | 20151225 | 1132 | 1371708 | 1673 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 18403 | 40.2704 | -124.2234 | 2/SP/LDSIDE/O/8189 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087303 | OH | Sus | 0 | No | 2015 | DEC | Yes | Three Phase Fault | 1177385 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | FUSE | 1997 | 20151225 | 1317 | 1371740 | 2833 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 19831 | 40.2843 | -124.0598 | 12 SPANS LOADSIDE OF 1997 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087496 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Ground | 1177582 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER | 2936 | 20151225 | 34 | 1371536 | 2434 | Distribution Circuit | Vegetation | Tree - fell into line | 284 | 688961 | 40.8671 | -123.5147 | fischer rd- 35 SPANS LD SIDE OF 2936 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 15-0087242 | OH | Sus | 0 | No | 2015 | DEC | Yes | Three Phase Fault | 1177323 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 3055 | 20151225 | 1359 | 1371750 | 1283 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 42339 | 40.8734 | -123.5189 | MTR#1008024007 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087293 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Ground | 1177374 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 2939 | 20151225 | 1053 | 1371691 | 1863 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 137862 | 40.8935 | -123.587 | 4/S/LD OF 2939- at MTR1008028210 & 1//SS/OF MTR 1008028210 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0087299 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Line | 1177380 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 2959 | 20151225 | 218 | 1371564 | 2342 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 65576 | 40.8752 | -123.5172 | MTR#1008028174 & 1 SPAN SS OF 7881 TWD2959 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 15-0087305 | OH | Sus | 0 | No | 2015 | DEC | Yes | Three Phase Fault | 1177387 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 4671 | 20151225 | 542 | 1371606 | 2566 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 43622 | 40.8944 | -123.5734 | 311 COUNCILMAN RD- 1 SPAN NORTH OF 4671 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 15-0087475 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Ground | 1177558 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | BRIDGEVILLE-1102 | 192461102 | FUSE | 3711 | 20151226 | 1914 | 1372204 | 1293 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1293 | 40.4222 | -123.8078 | WATSON- ARLIS `Kip`: 3 spans load side of 3711 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087518 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Ground | 1177608 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 3001 | 20151226 | 906 | 1371990 | 487 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 14625 | 40.9376 | -123.6729 | 1 SPAN LOAD SIDE OF 3001 | Partly Cloudy-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 15-0087412 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Line | 1177492 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 8453 | 20151226 | 903 | 1371987 | 1633 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 5664 | 40.8945 | -123.5611 | 6 SPANS LOAD SIDE OF 8453 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 15-0087430 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Line | 1177511 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 6775 | 20151226 | 1523 | 1372138 | 83 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 1245 | 40.8848 | -123.625 | MTR# 1008022001 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087444 | OH | Sus | 0 | No | 2015 | DEC | Yes | Force Out | 1177525 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1101 | 192461101 | FUSE | 4121 | 20151227 | 1337 | 1372679 | 1443 | Distribution Circuit | Environmental/External | Ice or snow | 3 | 4329 | 40.4809 | -123.7182 | 3 LOCATIONS LD SIDE OF 4121 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087517 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Line | 1177607 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 654897 | 20151227 | 649 | 1372333 | 654 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4578 | 41.188 | -123.7056 | LAKE PRAIRIE RD at LCO 56979- WEITCHPEC | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087505 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Line | 1177594 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | JUMPER | WIRE DOWN MAINLINE AT 3199 TWD 3273 | 20151227 | 2114 | 1373067 | 1350 | Distribution Circuit | Vegetation | Tree - fell into line | 491 | 650572 | 41.2626 | -123.6079 | MAINLINE at 3199 AND at MTR#1008025598 LD SIDE OF 3199 | Snow-Overcast-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 15-0087601 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Line | 1177692 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | FUSE | 3739 | 20151227 | 1941 | 1373007 | 464 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 928 | 39.031 | -123.3865 | 3 SPANS LD SIDE OF 3739 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087596 | OH | Sus | 0 | No | 2015 | DEC | Yes | Three Phase Fault | 1177687 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 7283 | 20151227 | 1209 | 1372577 | 154 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 154 | 40.9118 | -123.7052 | 2 POLES LOAD SIDE OF 7283 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087515 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Line | 1177605 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 2899 | 20151227 | 547 | 1372326 | 462 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 9240 | 40.871 | -123.5776 | 7 SPANS LOAD SIDE OF 2899 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087484 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Line | 1177568 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 4671 | 20151227 | 829 | 1372355 | 398 | Distribution Circuit | Vegetation | Tree - bark fell into line | 17 | 6766 | 40.8944 | -123.5734 | MTR1008028136 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 15-0087501 | OH | Sus | 0 | No | 2015 | DEC | Yes | None | 1177588 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1965 | 20151228 | 238 | 1373121 | 820 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 31980 | 40.122 | -123.8339 | at EOL TWD TRANSF#114880329072 | Rain-Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 15-0087609 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Line | 1177700 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 8435 | 20151228 | 906 | 1373210 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 8980 | 41.2086 | -123.7561 | 7 spans LDSIDE OF MTR#1008694108 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087628 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Line | 1177747 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 6633 | 20151228 | 546 | 1373146 | 954 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3816 | 41.2555 | -123.6489 | 3 SPANS SOURCESIDE OF 6635 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 15-0087660 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Line | 1177802 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 3009 | 20151228 | 341 | 1373123 | 624 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2496 | 40.9057 | -123.7476 | Hacker- Jesse 530 906 2191: hwy 299 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 15-0087611 | OH | Sus | 0 | No | 2015 | DEC | Yes | None | 1177702 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 7283 | 20151228 | 659 | 1373164 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 439 | 40.9118 | -123.7052 | 2ND SPAN LD SIDE OF 7283 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 15-0087624 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Ground | 1177730 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3283 | 20151229 | 1537 | 1374307 | 1171 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5855 | 41.296 | -123.5646 | 4 SPANS SS OF MTR1009643072 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087791 | OH | Sus | 31209409 | No | 2015 | DEC | Yes | Line to Ground | 1178011 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER | 2936 | 20151230 | 1809 | 1374962 | 1634 | Distribution Circuit | Environmental/External | Flood/Erosion | 284 | 50299 | 40.8671 | -123.5147 | 2 SPANS SS OF 2977- BURNT RANCH | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087875 | OH | Sus | 0 | No | 2015 | DEC | Yes | Three Phase Fault | 1178174 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2551 | 20160106 | 448 | 1377997 | 490 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 7350 | 40.301 | -124.2976 | 1 LS FUSES | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003326 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1178934 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 1363 | 20160106 | 433 | 1378064 | 445 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 17133 | 38.9158 | -123.6386 | MTR# E64120 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003275 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1178896 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | JUMPER | WIRE DOWN | 20160106 | 1136 | 1378540 | 520 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5866 | 40.8861 | -123.5083 | 1 SS OF TRANSF FEEDING MTR# 1009637325- WALLEN RANCH RD | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003462 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1179028 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | SWITCH | 3359 | 20160107 | 937 | 1379488 | 222 | Distribution Circuit | Vegetation | Tree - branch fell on line | 118 | 9820 | 41.343 | -123.5095 | 1 SPAN PAST 3361 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003753 | OH | Sus | 31211180 | yes | 2016 | JAN | Yes | None | 1179241 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HIGHLANDS-1103 | 43361103 | RECLOSER | 4630 | 20160110 | 1656 | 1381224 | 588 | Distribution Circuit | 3rd Party | Vehicle | 160 | 22344 | 38.9098 | -122.6174 | 2 POLES FROM 4630 TWDS 2349 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0004362 | OH | Sus | 31211852 | No | 2016 | JAN | Yes | Multi-Fault | 1179807 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER | 3 SPANS LD SD R-373 | 20160111 | 406 | 1381328 | 413 | Distribution Circuit | Equipment Failure/Involved | Overhead | 810 | 126503 | 40.1289 | -123.8661 | 3 SPANS FROM R-373 TWDS 2579 | Overcast-Fog-Drizzle-32-90 F | PGs, Kearneys | Broken, wire on ground | 16-0004420 | OH | Sus | 42604118 | No | 2016 | JAN | Yes | Line to Ground | 1179862 | PGK | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER 1101 | 192381101 | FUSE | 1899 | 20160112 | 2210 | 1382412 | 435 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4785 | 40.5108 | -124.1613 | 1/P/SS/OF MTR 1009744065 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0004916 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1180191 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4599 | 20160113 | 319 | 1382488 | 671 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3355 | 38.7488 | -123.3525 | 23 PAST FUSES 4599 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0004975 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1180246 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3773 | 20160113 | 141 | 1382461 | 476 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 7140 | 40.226 | -123.7906 | at MTR 1007960739 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0004943 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1180225 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | RECLOSER | 2600 | 20160113 | 301 | 1382499 | 431 | Distribution Circuit | Vegetation | Tree - bark fell into line | 92 | 30835 | 39.0852 | -123.4853 | MAINLINE BET 2625 & 2605 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0004950 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1180232 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 6653 | 20160114 | 1311 | 1383821 | 329 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2632 | 38.8154 | -123.5975 | 1 SPAN LOADSIDE OF 6653 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 16-0005408 | OH | Sus | 0 | No | 2016 | JAN | Yes | Line to Ground | 1180522 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3261 | 20160114 | 1800 | 1384040 | 752 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 8272 | 41.19 | -123.6909 | 1 SPAN SS OF MTR#1008025559 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0005472 | OH | Sus | 42611331 | No | 2016 | JAN | Yes | Line to Ground | 1180554 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3125 | 20160115 | 347 | 1384283 | 427 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 18200 | 39.4934 | -123.7816 | 1ST SPAN LD SIDE OF FUCO 8541 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0005499 | OH | Sus | 42611897 | No | 2016 | JAN | Yes | Line to Line | 1180584 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 1587 | 20160115 | 44 | 1384264 | 511 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 511 | 40.2961 | -123.8303 | 6 SPANS LD SIDE OF FUCO 1587 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0005497 | OH | Sus | 42611337 | No | 2016 | JAN | Yes | Line to Line | 1180581 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | OTHER | WIRE DOWN 1 SPAN LD SIDE 7439 | 20160116 | 1830 | 1385237 | 434 | Distribution Circuit | Vegetation | Tree - fell into line | 1314 | 100933 | 38.8012 | -123.574 | 1 SPAN LOADSIDE OF 7439 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0005810 | OH | Sus | 42612881 | No | 2016 | JAN | Yes | Line to Ground | 1180777 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | JUMPER | OJ'S 6 SPANS LOASIDE OF 1579 | 20160117 | 1459 | 1385528 | 311 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 1555 | 39.3045 | -123.7878 | 44694 CRESTWOOD DRIVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0005933 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1180903 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 5181 | 20160117 | 1630 | 1385588 | 682 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2046 | 39.8728 | -123.7104 | 1 SPAN LOADSIDE OF 5181 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0005925 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1180897 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 1510 | 20160117 | 1245 | 1385486 | 557 | Distribution Circuit | Vegetation | Tree - fell into line | 810 | 227545 | 40.1223 | -123.8349 | 6/S/LOADSIE OF LR1510 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0005897 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Multi-Fault | 1180868 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 2747 | 20160117 | 1208 | 1385466 | 517 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 10340 | 39.6779 | -123.4951 | GALLETTI- TIM: TREE THROUGH LINE at 1222 BRANSCOMB RD. WIRE DOWN at FCO 2747. LAKESIDE DR. | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0005902 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Force Out | 1180873 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | REDBUD-1101 | 43191101 | RECLOSER | 800 | 20160117 | 1622 | 1385579 | 692 | Distribution Circuit | Equipment Failure/Involved | Overhead | 648 | 123596 | 39.0289 | -122.68 | 3 SPANS FROM 4809 TOWARDS 454 | Overcast-Fog-Heavy Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0005921 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1180892 | CSO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | COVELO-1101 | 43061101 | FUSE | 6699 | 20160118 | 1010 | 1386299 | 1032 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3272 | 39.7398 | -123.1599 | 1ST SPAN LOAD SIDE OF 6699 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006088 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1181050 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3287 | 20160119 | 939 | 1387268 | 284 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 17608 | 39.3138 | -123.7464 | 15 SPANS LOADSIDE OF 3287 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006326 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1181232 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3751 | 20160119 | 947 | 1387064 | 208 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 2704 | 40.2213 | -123.8262 | 4/S/LOADSIDE OF 3571 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006298 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Three Phase Fault | 1181216 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 2653 | 20160119 | 816 | 1386844 | 243 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1944 | 38.9311 | -123.6918 | 6/S/LS/OF 2653 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006255 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1181184 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | JUMPER | OJ'S 2 SPANS SS OF MTR#1009715881 | 20160120 | 1100 | 1388559 | 170 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 170 | 39.5839 | -123.4434 | SAME | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006850 | OH | Sus | 42614217 | No | 2016 | JAN | Yes | Line to Ground | 1181621 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1121 | 192021121 | FUSE | 1269 | 20160121 | 2148 | 1389602 | 579 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 8106 | 40.8153 | -123.9938 | MAIN LINE 1 SPAN BEYOND 1255 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007253 | OH | Sus | 0 | No | 2016 | JAN | Yes | Line to Line | 1181903 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3769 | 20160121 | 2206 | 1389614 | 565 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 8475 | 40.2643 | -123.8276 | AT MTR #1008918386 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007248 | OH | Sus | 0 | No | 2016 | JAN | Yes | Line to Line | 1181896 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 6527 | 20160122 | 742 | 1389729 | 480 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 2880 | 40.5486 | -124.3537 | 8 SPANS LOADSIDE OF 6527 | Partly Cloudy-Fog-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0007373 | OH | Sus | 42615849 | yes | 2016 | JAN | Yes | Line to Ground | 1181972 | CSO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | OTHER | MAIN LINE WIRE DOWN | 20160122 | 853 | 1389840 | 492 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 21920 | 39.134 | -123.6493 | MAINLINE AT CUTOUTS 8281 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007383 | OH | Sus | 42615856 | yes | 2016 | JAN | Yes | Open Circuit | 1181978 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 8439 | 20160122 | 2032 | 1390371 | 193 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 11194 | 39.3481 | -123.3393 | 3 POLES W/OF MTR #5000121300 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007609 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1182097 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HIGHLANDS-1103 | 43361103 | FUSE | 7117 | 20160123 | 1026 | 1390688 | 593 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 53 | 28216 | 38.8685 | -122.6233 | at MTR#1009650176- 13171 HWY 29 LOWER LAKE | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0007745 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1182239 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | OTHER | 29362 | 20160123 | 1125 | 1390776 | 790 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 46600 | 40.8943 | -123.7723 | 3 SPANS SS OF LR 91926- BAIR RD 3 MILES N/O HWY 299 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007769 | OH | Sus | 31214514 | yes | 2016 | JAN | Yes | Line to Ground | 1182265 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 8049 | 20160125 | 337 | 1391756 | 743 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 743 | 40.1069 | -123.9249 | 1 SPAN LD SIDE OF 8049 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0008046 | OH | Sus | 31214828 | No | 2016 | JAN | Yes | Line to Line | 1182519 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 1947 | 20160129 | 2115 | 1394294 | 1274 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 34398 | 40.2218 | -123.7972 | 4/S/LOADISE OF 1947 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009245 | OH | Sus | 31215832 | No | 2016 | JAN | Yes | Line to Line | 1183332 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2775 | 20160129 | 1602 | 1394165 | 315 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 4095 | 39.5172 | -123.3911 | 2 SPANS LOAD SIDE OF 2775 WEST OF MAIN LINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009213 | OH | Sus | 42620138 | No | 2016 | JAN | Yes | Line to Line | 1183298 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 7253 | 20160131 | 1542 | 1395033 | 358 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 1014 | 39.4189 | -123.7782 | 19210 BENSON LANE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009449 | OH | Sus | 42621130 | yes | 2016 | JAN | Yes | Line to Ground | 1183526 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARRIS-1109 | 192431109 | FUSE | 893 | 20160203 | 904 | 1397549 | 356 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 9968 | 40.7584 | -124.0501 | 2 SPANS LD SIDE OF 0893 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0010277 | OH | Sus | 42623455 | No | 2016 | FEB | Yes | Line to Line | 1184181 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3021 | 20160218 | 1018 | 1408231 | 1450 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 10454 | 39.3319 | -123.8051 | 1 SPAN SS 1009717459 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013884 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186870 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 6693 | 20160218 | 457 | 1407795 | 626 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 626 | 38.6459 | -123.397 | 4 SPANS FROM 4535 TWDS 6693 | Clear-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013625 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186703 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | JUMPER | OJ 10 SPANS FROM 2007 | 20160218 | 1508 | 1408711 | 926 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 8016 | 39.4242 | -123.406 | 3853 PRIMROSE DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013949 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186898 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 8249 | 20160219 | 629 | 1408976 | 652 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3158 | 40.2304 | -123.8505 | 3 SPANS FROM MTR#1007965464 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0014027 | OH | Sus | 0 | No | 2016 | FEB | Yes | Line to Ground | 1186970 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1106 | 43351106 | FUSE | 9865 | 20160302 | 1030 | 1414679 | 551 | Distribution Circuit | 3rd Party | Vehicle | 88 | 48488 | 39.0015 | -122.78 | 6855 GRANDE VISTA DR | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0016719 | OH | Sus | 31222617 | No | 2016 | MAR | Yes | Line to Line | 1188918 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | JUMPER | WIRE DOWN LD SIDE OF 3141 | 20160303 | 1328 | 1415288 | 352 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 12112 | 39.6508 | -123.7618 | BOTH SOURCE AND LOAD SIDE OF CUTOUT POLE 3141 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017047 | OH | Sus | 42646492 | No | 2016 | MAR | Yes | Line to Ground | 1189073 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | FUSE | 3931 | 20160306 | 2126 | 1422810 | 508 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 10668 | 40.338 | -123.9124 | MAIN LINE 2 SPANS FROM 7327 TWD 7453 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018612 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Three Phase Fault | 1190456 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1789 | 20160306 | 911 | 1421625 | 509 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 7635 | 40.0246 | -123.9427 | 6 SPANS LD SIDE OF 1789 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018446 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190282 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 8189 | 20160306 | 1545 | 1422359 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 5750 | 40.27 | -124.2241 | AT FUCO 8189 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018559 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190400 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2505 | 20160306 | 2342 | 1423168 | 677 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 23695 | 40.3068 | -124.2964 | 13 SPANS LOAD SIDE OF 2505 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018678 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190521 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 5113 | 20160307 | 827 | 1423471 | 0 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 301 | 38.7189 | -123.38 | 36500 ANNAPOLIS RD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018752 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190587 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 1579 | 20160307 | 1443 | 1424177 | 157 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 2669 | 39.3056 | -123.792 | 2 PAST FUSES | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018973 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190731 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5731 | 20160307 | 2110 | 1424716 | 395 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 9419 | 39.2692 | -123.7817 | MAIN LINE AT FUCO 1007 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0019107 | OH | Sus | 42648205 | yes | 2016 | MAR | Yes | Line to Ground | 1190865 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | FUSE | 7373 | 20160307 | 1722 | 1424306 | 265 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2385 | 40.3264 | -123.9226 | AT MTR #1008027323 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0019013 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190762 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1106 | 43351106 | FUSE | 90581 | 20160308 | 1005 | 1425095 | 318 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 36 | 11448 | 39.0844 | -122.7886 | 1 SPAN LD SIDE OF 90581 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0019228 | OH | Sus | 31223596 | yes | 2016 | MAR | Yes | Line to Ground | 1190983 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE | 777 | 20160310 | 1943 | 1426862 | 883 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 18366 | 39.1691 | -123.0122 | 5845 HWY 20 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020089 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1191605 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 3041 | 20160311 | 400 | 1427026 | 523 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 15690 | 39.1862 | -123.7002 | 1 SPAN SOURCE SIDE OF MTR #5000120495 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020195 | OH | Sus | 42655225 | yes | 2016 | MAR | Yes | Line to Line | 1191719 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3173 | 20160311 | 752 | 1427182 | 548 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1096 | 39.6337 | -123.7825 | 7 SPANS LOAD SIDE OF 3173 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020266 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1191758 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 6081 | 20160311 | 254 | 1427009 | 334 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 60468 | 39.3922 | -123.7995 | AT MTR 1008730980 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020187 | OH | Sus | 42655192 | yes | 2016 | MAR | Yes | Three Phase Fault | 1191710 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER | 1602 | 20160311 | 750 | 1427186 | 631 | Distribution Circuit | Environmental/External | Flood/Erosion | 87 | 50514 | 40.1834 | -123.5765 | 4 SPANS SOURCESIDE OF SBCO 6975 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020211 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1191731 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 9405 | 20160311 | 916 | 1427277 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 14168 | 38.8153 | -123.5819 | AT MTR #1006219880 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020322 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1191792 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 6415 | 20160311 | 921 | 1427284 | 471 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 471 | 38.9159 | -123.6536 | 3 SPANS LOAD SIDE OF 6415 | Clear-32-90 F | Insulator | Broken, wire on ground | 16-0020376 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1191815 | INS | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 8483 | 20160312 | 1237 | 1429404 | 306 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 4374 | 38.7338 | -123.3741 | 27 SPANS PAST FUCO | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020784 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1192163 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | OTHER | WIRE DOWN | 20160312 | 937 | 1429279 | 802 | Distribution Circuit | Vegetation | Tree - fell into line | 236 | 81362 | 39.2282 | -123.7663 | AT FUCO 5233 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020756 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192135 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1575 | 20160312 | 1554 | 1429587 | 558 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1674 | 39.9693 | -123.7995 | AT TAP THAT FEEDS MTR 1008279547 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020816 | OH | Sus | 42655826 | yes | 2016 | MAR | Yes | Line to Ground | 1192198 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 4451 | 20160313 | 1826 | 1430494 | 1399 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 9793 | 38.7902 | -123.5109 | 3 SPAN LD SIDE OF 4451 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021226 | OH | Sus | 42656309 | yes | 2016 | MAR | Yes | Line to Ground | 1192571 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER | 64118 | 20160313 | 157 | 1429860 | 916 | Distribution Circuit | Vegetation | Tree - fell into line | 670 | 206988 | 39.362 | -123.1283 | MTR#1008727900- 10211 MAIN ST. POTTER VALLEY | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020870 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192260 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UKIAH-1114 | 42771114 | FUSE | 91159 | 20160313 | 1209 | 1430167 | 319 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1595 | 39.1383 | -123.1768 | 1 SPAN PAST FUCO | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020953 | OH | Sus | 31224754 | yes | 2016 | MAR | Yes | Line to Ground | 1192331 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 37506 | 20160313 | 1602 | 1430375 | 464 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 25455 | 39.4831 | -123.3611 | AT MTR #1008392386 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021022 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192395 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | JUMPER | WIRE DOWN AT MTR #1009765095 | 20160314 | 2055 | 1431523 | 934 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1868 | 38.7744 | -123.4781 | AT MTR #1009765095 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021474 | OH | Sus | 42656753 | yes | 2016 | MAR | Yes | Line to Ground | 1192761 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | OTHER | 37506 | 20160314 | 54 | 1430785 | 443 | Distribution Circuit | Vegetation | Tree - branch fell on line | 89 | 17829 | 39.4831 | -123.3611 | AT MTR #1008731193 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021121 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192489 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CARLOTTA-1121 | 192291121 | OTHER | WIRE DOWN | 20160316 | 654 | 1432344 | 466 | Distribution Circuit | Environmental/External | Flood/Erosion | 27 | 2959 | 40.5257 | -124.0023 | 1309 CUMMINGS CRK | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0021824 | OH | Sus | 0 | No | 2016 | MAR | Yes | Line to Ground | 1193022 | PW | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | FUSE | 1411 | 20160316 | 522 | 1432319 | 578 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 15028 | 38.9188 | -123.2852 | MM 36.79 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021811 | OH | Sus | 42658420 | No | 2016 | MAR | Yes | Line to Line | 1193014 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3769 | 20160317 | 1833 | 1433466 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 7710 | 40.2642 | -123.8276 | STARTING AT 2 SPANS PAST FUCO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0022338 | OH | Sus | 42659338 | No | 2016 | MAR | Yes | Line to Ground | 1193381 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3769 | 20160322 | 740 | 1435917 | 275 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 4125 | 40.2642 | -123.8276 | 1 SPAN LOADSIDE OF MTR#15G008 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0023162 | OH | Sus | 42661012 | No | 2016 | MAR | Yes | Line to Line | 1193987 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 5415 | 20160322 | 726 | 1435903 | 339 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 2943 | 39.3713 | -123.3607 | 2 SPANS SS OF MTR #0J2803 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0023158 | OH | Sus | 42661120 | No | 2016 | MAR | Yes | Line to Line | 1193986 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | FUSE | 1997 | 20160325 | 717 | 1438352 | 498 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 3486 | 40.2852 | -124.0595 | Trumbo- Maurice 408 646 7337: 6-7 spans beyond cutouts 1997 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0024035 | OH | Sus | 42663168 | No | 2016 | MAR | Yes | Line to Ground | 1194616 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CALPELLA-1101 | 43411101 | FUSE | 1147 | 20160329 | 2119 | 1441338 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 9692 | 39.2294 | -123.162 | BETWEEN POLE 2/7 AND 2/8 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0024896 | OH | Sus | 31228046 | No | 2016 | MAR | Yes | Line to Line | 1195281 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 6743 | 20160404 | 100 | 1443823 | 720 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 11530 | 41.2848 | -123.547 | 3/S/SIDE OF MTR#1008028134 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0025847 | OH | Sus | 0 | No | 2016 | APR | Yes | Line to Ground | 1195996 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 1363 | 20160404 | 1248 | 1444166 | 162 | Distribution Circuit | Vegetation | Tree - bark fell into line | 57 | 9234 | 38.9153 | -123.6397 | 5 PAST FUSES | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0025998 | OH | Sus | 42668622 | No | 2016 | APR | Yes | Line to Ground | 1196088 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARTLEY-1101 | 43211101 | RECLOSER | 738 | 20160405 | 1533 | 1444918 | 126 | Distribution Circuit | 3rd Party | Vehicle | 1181 | 100796 | 39.0622 | -122.931 | AT CAP BK 516 POLE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0026333 | OH | Sus | 0 | No | 2016 | APR | Yes | Line to Line | 1196295 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 2653 | 20160409 | 2108 | 1447993 | 890 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 7120 | 38.932 | -123.6916 | 12 SPANS LOAD SIDE OF 2653 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0027544 | OH | Sus | 42671741 | yes | 2016 | APR | Yes | Line to Line | 1197126 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 3304 | 20160413 | 1642 | 1450196 | 584 | Distribution Circuit | Vegetation | Tree - fell into line | 637 | 331208 | 41.1053 | -123.6888 | 1 SPAN SOURCE SIDE OF 3351 | Overcast-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0028402 | OH | Sus | 0 | No | 2016 | APR | Yes | Line to Ground | 1197807 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HIGHLANDS-1102 | 43361102 | RECLOSER | 75140 | 20160414 | 22 | s1197994 | 465 | Distribution Circuit | Vegetation | Tree - fell into line | 2594 | 265224 | 38.9543 | -122.6103 | 555 REDWOOD ST | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0028460 | OH | Sus | 0 | No | 2016 | APR | Yes | Line to Ground | 1197994 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | OTHER | WIRE DOWN | 20160414 | 336 | 1450413 | 581 | Distribution Circuit | Vegetation | Tree - fell into line | 495 | 282429 | 41.2532 | -123.6364 | 2 SPANS LOAD SIDE 3273 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0028468 | OH | Sus | 0 | No | 2016 | APR | Yes | Line to Ground | 1197878 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HUMBOLDT BAY-1102 | 192341102 | FUSE | 5301 | 20160414 | 832 | 1450498 | 468 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 1872 | 40.7008 | -124.138 | 20 SPANS LD SIDE OF 5301 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0028591 | OH | Sus | 0 | No | 2016 | APR | Yes | Line to Line | 1197969 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MAPLE CREEK-1101 | 192101101 | FUSE | 6235 | 20160415 | 1539 | 1451599 | 756 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 5800 | 40.7678 | -123.8718 | 7 POLES LD SIDE OF 3105 | Clear-32-90 F | PGs, Kearneys | Broken, wire on ground | 16-0029039 | OH | Sus | 42680301 | yes | 2016 | APR | Yes | Line to Line | 1198199 | PGK | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER | 75382 | 20160417 | 942 | 1452298 | 1010 | Distribution Circuit | 3rd Party | Vehicle | 412 | 163218 | 38.9065 | -122.6735 | 11725 Loch Lomond Rd & 1 SPAN S/OF MTR# 23R742 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0029191 | OH | Sus | 0 | No | 2016 | APR | Yes | Multi-Fault | 1198370 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | JUMPER | WIRE DOWN | 20160420 | 1544 | 1454513 | 328 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 54 | 13008 | 39.3622 | -123.7815 | SMITH- JOSEPH: METER NUMBER 18584R | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 16-0030075 | OH | Sus | 42683327 | No | 2016 | APR | Yes | Line to Ground | 1199005 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3757 | 20160422 | 112 | 1455394 | 738 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 26654 | 40.2283 | -123.863 | 1 POLE SOURCE SIDE OF MTR# H72194 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0030423 | OH | Sus | 0 | yes | 2016 | APR | Yes | Line to Line | 1199263 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 2969 | 20160422 | 1011 | 1455611 | 533 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 11726 | 40.8093 | -123.4812 | 1ST AND 2ND SPANS LD SIDE OF FUCO 2969 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0030637 | OH | Sus | 31233531 | yes | 2016 | APR | Yes | Line to Line | 1199350 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 8629 | 20160425 | 544 | 1457820 | 282 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 564 | 39.1336 | -123.6381 | 2/S/LS/OF 8639 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0031184 | OH | Sus | 0 | yes | 2016 | APR | Yes | Line to Ground | 1199864 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8961 | 20160425 | 1001 | 1458260 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 439 | 39.5609 | -123.7256 | GARCIA- DAN 707-489-0177: camp 2 ten mile rd- 1span load side of fuco 8961 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0031305 | OH | Sus | 42685145 | yes | 2016 | APR | Yes | Line to Line | 1199974 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | JUMPER | WIRE DOWN ON GROUND BROKEN 12 SPANS S/O 3969 | 20160425 | 1541 | 1458858 | 174 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 10440 | 39.3749 | -123.7737 | 12 SPANS SOUTH OF 3969 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0031415 | OH | Sus | 0 | yes | 2016 | APR | Yes | Line to Ground | 1200029 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 1603 | 20160426 | 1137 | 1459404 | 701 | Distribution Circuit | 3rd Party | Vehicle | 62 | 43462 | 39.3904 | -123.8009 | at 5601 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0031659 | OH | Sus | 0 | No | 2016 | APR | Yes | Line to Line | 1200250 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | RECLOSER | 1308 | 20160428 | 1648 | 1461145 | 619 | Distribution Circuit | Vegetation | Tree - fell into line | 292 | 41694 | 39.1863 | -123.5804 | 30000 COMPTCHE UKIAH RD MTR 1009902607 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0032497 | OH | Sus | 0 | No | 2016 | APR | Yes | Line to Ground | 1200824 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 4079 | 20160429 | 1938 | 1461840 | 1052 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 4362 | 38.9031 | -122.7595 | WOODARD-KYLE: 9345 wildcat rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0032757 | OH | Sus | 0 | yes | 2016 | APR | Yes | Line to Ground | 1201019 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | OTHER | WIRE DOWN 3 SS FU 1987 | 20160502 | 641 | 1463025 | 617 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 9872 | 40.5025 | -124.2798 | 2 SPANS SS FU 1987 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0033194 | OH | Sus | 42688721 | No | 2016 | MAY | Yes | Line to Ground | 1201475 | CSO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1102 | 43311102 | RECLOSER | 596 | 20160505 | 1032 | 1465040 | 568 | Distribution Circuit | Environmental/External | Lightning | 1118 | 112314 | 38.9406 | -122.78 | SS MTR 1009717049 | Overcast-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0034004 | OH | Sus | 42691012 | yes | 2016 | MAY | Yes | Line to Line | 1202080 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CARLOTTA-1121 | 192291121 | FUSE | 7723 | 20160516 | 2302 | 1470863 | 768 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 5636 | 40.5143 | -123.991 | Trumbo- Maurice 408 646 7337: 791 fox creek | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0036397 | OH | Sus | 42702466 | No | 2016 | MAY | Yes | Line to Line | 1203740 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | COVELO-1101 | 43061101 | FUSE | 6699 | 20160518 | 1824 | 1472326 | 741 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1482 | 39.7397 | -123.1599 | MTR 1009715885 | Clear-32-90 F | Crossarm, Steel | Broken, wire on ground | 16-0036911 | OH | Sus | 31240740 | yes | 2016 | MAY | Yes | Line to Ground | 1204125 | CAS | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 4427 | 20160519 | 1854 | 1473077 | 55 | Distribution Circuit | Vegetation | Tree - branch fell on line | 82 | 4510 | 38.8168 | -123.5843 | IN 1ST SPAN W/OF 5531 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0037247 | OH | Sus | 42704146 | No | 2016 | MAY | Yes | Line to Ground | 1204341 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 4439 | 20160519 | 1950 | 1473106 | 667 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 1889 | 38.795 | -123.5664 | 1ST POLE W/OF LINE AND BUCK ON TAP TO WEST 1 SPAN S/OF MTR 5000126372 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0037250 | OH | Sus | 42704150 | No | 2016 | MAY | Yes | Line to Ground | 1204345 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 5781 | 20160520 | 727 | 1473340 | 588 | Distribution Circuit | 3rd Party | Vehicle | 195 | 103611 | 39.2263 | -123.7286 | 29801 ALBION RIDGE ROAD | Clear-32-90 F | Pole-Wood | Broken, wire on object | 16-0037317 | OH | Sus | 0 | yes | 2016 | MAY | Yes | Line to Ground | 1204403 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1108 | 43311108 | FUSE | 607 | 20160520 | 235 | 1473272 | 800 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 37600 | 38.8644 | -122.6929 | 4 SPANS LD SIDE FU 607 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0037274 | OH | Sus | 31241018 | yes | 2016 | MAY | Yes | Line to Line | 1204381 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 893 | 20160520 | 1501 | 1473753 | 680 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2720 | 39.0578 | -123.4518 | 4 POLES LOAD SIDE OF 893 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0037479 | OH | Sus | 42705062 | yes | 2016 | MAY | Yes | Line to Ground | 1204514 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UPPER LAKE-1101 | 42871101 | OTHER | WIRE DOWN | 20160521 | 1655 | 1474512 | 738 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 30840 | 39.1705 | -123.0144 | 5498 BLUE LAKE RD 2 SPANS LOAD SIDE OF 777 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0037622 | OH | Sus | 31241352 | No | 2016 | MAY | Yes | Line to Ground | 1204675 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1913 | 20160526 | 1000 | 1477492 | 1652 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 13216 | 40.4483 | -124.267 | 14 SPANS LD SIDE OF FU 1913 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0038802 | OH | Sus | 42707669 | No | 2016 | MAY | Yes | Line to Ground | 1205532 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3369 | 20160526 | 1558 | 1477710 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 27449 | 41.3725 | -123.5016 | WALPOLE- JIM 707-497-9748: 1 SP L/S OF 3369 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0038829 | OH | Sus | 42707772 | No | 2016 | MAY | Yes | Line to Ground | 1205544 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 8652 | 20160527 | 1543 | 1478205 | 506 | Distribution Circuit | Vegetation | Tree - fell into line | 249 | 19915 | 40.1065 | -123.9278 | 4 SPANS SS FU 6469 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0039159 | OH | Sus | 31242665 | No | 2016 | MAY | Yes | Line to Ground | 1205802 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | OTHER | WIRE DOWN 4 SPANS S/SIDE LCO 3351 | 20160527 | 1459 | 1478181 | 917 | Distribution Circuit | Vegetation | Tree - fell into line | 637 | 506569 | 41.2144 | -123.656 | HANSON- SCOTT 707-834-6310: 4 SPANS SOURCE SIDE OF LCO3351 TWRDS 3167 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0039143 | OH | Sus | 31242666 | No | 2016 | MAY | Yes | Open Circuit | 1205788 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 84085 | 20160528 | 1027 | 1478413 | 910 | Distribution Circuit | 3rd Party | Vehicle | 11 | 10010 | 41.2761 | -123.8073 | 2 SS FU 54527 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0039508 | OH | Sus | 0 | No | 2016 | MAY | Yes | Line to Ground | 1206140 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1102 | 192461102 | FUSE | 99497 | 20160529 | 1536 | 1478991 | 784 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2352 | 40.4647 | -123.8599 | Mello- Adam 530 401 5814: 1 sp load side 99497 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0039631 | OH | Sus | 0 | No | 2016 | MAY | Yes | Line to Line | 1206257 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1815 | 20160531 | 235 | 1479363 | 142 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 4118 | 39.868 | -123.7169 | 3 SPANS SS OF MTR 5000016874 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0039744 | OH | Sus | 0 | yes | 2016 | MAY | Yes | Line to Ground | 1206375 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER | 3902 | 20160602 | 1734 | 1481620 | 637 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1507 | 40.3428 | -123.9157 | 10 SPANS SS OF 61801 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0040641 | OH | Sus | 42711461 | No | 2016 | JUN | Yes | Line to Line | 1206977 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 3304 | 20160603 | 1219 | 1482095 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 637 | 85417 | 41.1053 | -123.6888 | 50 SPANS LOAD SIDE OF LE 37202 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0040813 | OH | Sus | 31245444 | yes | 2016 | JUN | Yes | Line to Line | 1207132 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 4519 | 20160604 | 1116 | 1482826 | 828 | Distribution Circuit | 3rd Party | Vehicle | 15 | 2662 | 40.0891 | -123.7972 | MID SPAN ON LD SIDE HARD TAP RUNNING SOUTH | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0041063 | OH | Sus | 0 | No | 2016 | JUN | Yes | Line to Line | 1207326 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 93234 | 20160605 | 1002 | 1483259 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 57846 | 40.2355 | -123.8346 | 23 spans load side LR 93234 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0041148 | OH | Sus | 0 | No | 2016 | JUN | Yes | Line to Line | 1207428 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 4837 | 20160605 | 1801 | 1483478 | 578 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 578 | 40.2853 | -124.2514 | 2 SPANS LD SIDE OF 4837 at MTR#1008027469 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0041192 | OH | Sus | 42712455 | No | 2016 | JUN | Yes | Line to Ground | 1207471 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARRIS-1109 | 192431109 | FUSE | 5889 | 20160606 | 1422 | 1484059 | 187 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 2767 | 40.7659 | -124.0674 | 4 SPANS LD SIDE OF 5889 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0041450 | OH | Sus | 31245833 | No | 2016 | JUN | Yes | Line to Line | 1207635 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1101 | 192171101 | FUSE | 2933 | 20160607 | 1359 | 1484707 | 758 | Distribution Circuit | Vegetation | Tree - fell into line | 150 | 53850 | 40.9589 | -123.6298 | MTR# 1008025049 | Clear-Above 90 | Crossarm, Wood | Broken, wire on ground | 16-0041710 | OH | Sus | 0 | No | 2016 | JUN | Yes | Three Phase Fault | 1207845 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1907 | 20160616 | 1031 | 1490018 | 328 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 5051 | 40.4872 | -124.2599 | 2 SPANS SS/OF 1987 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0043728 | OH | Sus | 42726462 | No | 2016 | JUN | Yes | Line to Ground | 1209412 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3969 | 20160619 | 1207 | 1492239 | 433 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 60 | 6100 | 39.3811 | -123.7737 | HARD TAP FEEDING MTR#1008944952 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0044317 | OH | Sus | 0 | No | 2016 | JUN | Yes | Line to Ground | 1209793 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 6789 | 20160627 | 2132 | 1497112 | 534 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 7476 | 40.218 | -123.8718 | 18 SPANS LD SIDE OF 6789 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0046162 | OH | Sus | 42732262 | yes | 2016 | JUN | Yes | Line to Ground | 1211203 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | RECLOSER | 2600 | 20160701 | 114 | 1499253 | 751 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 20886 | 39.0853 | -123.485 | REGE- ROBERT: 10 SPANS L/S OF LR 2600 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0047250 | OH | Sus | 42734121 | yes | 2016 | JUL | Yes | Line to Line | 1211910 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1108 | 43311108 | RECLOSER | 1278 | 20160703 | 1616 | 1500617 | 1074 | Distribution Circuit | 3rd Party | Vehicle | 443 | 45567 | 38.9559 | -122.7274 | TAP 2/P LINE SIDE OF 426288 | Clear-Above 90 | Pole-Wood | Broken, wire on ground | 16-0047693 | OH | Sus | 0 | No | 2016 | JUL | Yes | Line to Ground | 1212237 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 5415 | 20160708 | 1834 | 1503060 | 378 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 2730 | 39.3713 | -123.3607 | OJ 5100 WILLIAMS RANCH RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0048731 | OH | Sus | 42737856 | No | 2016 | JUL | Yes | Line to Line | 1212961 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3073 | 20160709 | 2106 | 1507628 | 482 | Distribution Circuit | Equipment Failure/Involved | Overhead | 172 | 39224 | 41.062 | -123.6942 | Goodman- Bill: bald hills rd 2 spans s/s of 3335 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0048839 | OH | Sus | 42737981 | No | 2016 | JUL | Yes | Line to Ground | 1213073 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | FUSE | 3753 | 20160712 | 821 | 1508687 | 574 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5166 | 38.8897 | -123.1918 | REGE- ROBERT: 28574 ELKHORN RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0049289 | OH | Sus | 31256920 | No | 2016 | JUL | Yes | Three Phase Fault | 1213460 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 2939 | 20160712 | 1317 | 1508893 | 246 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 18204 | 40.8935 | -123.5871 | 1 SPAN NORTH OF 2955 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0049398 | OH | Sus | 42740361 | No | 2016 | JUL | Yes | Line to Line | 1213509 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3127 | 20160717 | 1319 | 1511481 | 634 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1902 | 41.2808 | -123.5873 | 5 SPANS LD SIDE OF FUCO 3127 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0050472 | OH | Sus | 42742270 | No | 2016 | JUL | Yes | Line to Ground | 1214291 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | JUMPER | 6/P/LD SIDE OF 5265 | 20160725 | 1947 | 1515951 | 538 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 538 | 38.8445 | -123.6306 | 30601 S. HWY 1 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0052431 | OH | Sus | 42747108 | yes | 2016 | JUL | Yes | Line to Ground | 1215603 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1101 | 192171101 | FUSE | 2985 | 20160730 | 939 | 1518932 | 1041 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 11994 | 40.9442 | -123.621 | 1 SPAN SS OF CGC 115523559027 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0053832 | OH | Sus | 31260489 | No | 2016 | JUL | Yes | Line to Line | 1216553 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 7871 | 20160801 | 2001 | 1520023 | 671 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 3355 | 38.922 | -123.6227 | 1 SPAN LD SIDE FU 7871 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0054299 | OH | Sus | 31260860 | No | 2016 | AUG | Yes | Line to Ground | 1216879 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HIGHLANDS-1103 | 43361103 | FUSE | 52131 | 20160802 | 2342 | 1520711 | 288 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 576 | 38.8495 | -122.5597 | 1 SPAN SS OF EOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0054587 | OH | Sus | 42757787 | No | 2016 | AUG | Yes | Line to Ground | 1217055 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1101 | 192171101 | JUMPER | TREE THROUGH LINES | 20160804 | 1623 | 1521649 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 20776 | 40.9802 | -123.6321 | MTR 1008025001 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0055175 | OH | Sus | 31261561 | No | 2016 | AUG | Yes | Line to Ground | 1217370 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HIGHLANDS-1103 | 43361103 | FUSE | 5869 | 20160813 | 1751 | 1526176 | 5406 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 4 | 392 | 38.8997 | -122.571 | LD SIDE OF FUCO 5869 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 16-0057194 | OH | Sus | 0 | No | 2016 | AUG | Yes | None | 1218809 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HIGHLANDS-1103 | 43361103 | FUSE | 5871 | 20160813 | 1751 | 1526214 | 5689 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 19 | 57 | 38.8972 | -122.5674 | FIRE IN AREA | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0057199 | OH | Sus | 0 | No | 2016 | AUG | Yes | Force Out | 1218814 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 3695 | 20160814 | 2332 | 1526442 | 828 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 828 | 39.0591 | -123.5134 | 2 SPANS SS OF MTR 1008389527 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0057245 | OH | Sus | 0 | No | 2016 | AUG | Yes | Line to Ground | 1218867 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 8437 | 20160817 | 1223 | 1527917 | 517 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 16544 | 41.2105 | -123.7574 | 26 SPANS LD SIDE OF LINE REG 678 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0058002 | OH | Sus | 0 | No | 2016 | AUG | Yes | Line to Line | 1219362 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | OTHER | 3067 | 20160819 | 1623 | 1529181 | 242 | Distribution Circuit | 3rd Party | Vehicle | 393 | 95106 | 39.2235 | -123.755 | 1 LD OF MTR#1006276616 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0058677 | OH | Sus | 0 | No | 2016 | AUG | Yes | Line to Line | 1219747 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1106 | 43351106 | RECLOSER | 526 | 20160822 | 128 | 1530063 | 594 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1751 | 224733 | 39.0763 | -122.783 | BETWEEN 83647 & 588793 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0058880 | OH | Sus | 0 | No | 2016 | AUG | Yes | Force Out | 1219949 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | REDBUD-1101 | 43191101 | OTHER | WIRE DOWN AT 4343 | 20160822 | 1649 | 1530499 | 928 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 568 | 151750 | 39.0706 | -122.604 | Smith- Cody: 2667 shasta rd | Partly Cloudy-Above 90 | Crossarm, Wood | Broken, wire on ground | 16-0059175 | OH | Sus | 31264806 | No | 2016 | AUG | Yes | Line to Ground | 1220093 | CAW | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 97300 | 20160829 | 643 | 1533549 | 341 | Distribution Circuit | 3rd Party | Vehicle | 444 | 41745 | 39.9723 | -123.8008 | BRYAN- JOSEPH 707 298 1053: pole #110388690 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0060596 | OH | Sus | 0 | No | 2016 | AUG | Yes | Line to Ground | 1221134 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | OTHER | 5187 | 20160903 | 1858 | 1536434 | 382 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 3438 | 39.2861 | -123.7796 | 4 SPANS LD SIDE OF 5187- 44246 GORDON LANE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0062274 | OH | Sus | 0 | No | 2016 | SEP | Yes | Force Out | 1222210 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 3787 | 20160903 | 1731 | 1536410 | 291 | Distribution Circuit | Vegetation | Tree - branch fell on line | 32 | 7519 | 40.1224 | -123.834 | at MTR#1009229789- OAKRIDGE DR- REDWAY | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0062268 | OH | Sus | 42781112 | No | 2016 | SEP | Yes | Line to Line | 1222205 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1903 | 20160904 | 1124 | 1536558 | 252 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 1764 | 40.5282 | -124.1667 | 3 SP LOAD SIDE 1903 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0062313 | OH | Sus | 42781132 | No | 2016 | SEP | Yes | Multi-Fault | 1222254 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 7749 | 20160906 | 1452 | 1537386 | 241 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 5 | 1205 | 39.3132 | -123.7338 | FELICICH- DAVID: tree cut and fell into line | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0062718 | OH | Sus | 42781964 | No | 2016 | SEP | Yes | Line to Ground | 1222509 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 4501 | 20160908 | 1112 | 1538436 | 358 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 786 | 38.7018 | -123.4261 | 3 SPANS EAST OF 1309 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0063211 | OH | Sus | 0 | No | 2016 | SEP | Yes | Three Phase Fault | 1222843 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 7221 | 20160912 | 1508 | 1540404 | 214 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 428 | 39.523 | -123.7613 | LAST SPAN TWD EOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0064050 | OH | Sus | 42786022 | No | 2016 | SEP | Yes | Line to Line | 1223387 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | OTHER | WIRE DOWN 1 POLE N/OF 1593 | 20160915 | 451 | 1541982 | 484 | Distribution Circuit | Equipment Failure/Involved | Overhead | 314 | 44497 | 39.3962 | -123.8011 | GARCIA- DAN 707-489-0177: 2 work locations boice and n mitchell crk rd | Partly Cloudy-Fog-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0064809 | OH | Sus | 0 | No | 2016 | SEP | Yes | Open Circuit | 1223847 | CSO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | OTHER | 5401 | 20160920 | 825 | 1544546 | 133 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 798 | 40.0044 | -123.7871 | 5 SPANS LOAD SIDE OF 5401 at MTR 1008696106 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0065910 | OH | Sus | 42795024 | No | 2016 | SEP | Yes | Open Circuit | 1224647 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | JUMPER | WIRE DOWN | 20160924 | 1147 | 1547041 | 392 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1884 | 38.8432 | -123.6318 | 6 SPANS LD SIDE OF FUCO 5265 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0067218 | OH | Sus | 42797626 | No | 2016 | SEP | Yes | Line to Ground | 1225570 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 56048 | 20160930 | 1852 | 1550758 | 939 | Distribution Circuit | Vegetation | Tree - fell into line | 370 | 78090 | 40.1477 | -124.0196 | 5 SPANS LD SIDE OF 8185 | Clear-32-90 F | Conductor, Overhead | On Ground | 16-0068839 | OH | Sus | 0 | No | 2016 | SEP | Yes | Multi-Fault | 1226764 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3909 | 20161001 | 407 | 1550849 | 1241 | Distribution Circuit | 3rd Party | Vandalism | 26 | 32266 | 39.3995 | -123.7153 | TRANSMISSION POLE 37/1 AT HWY 20 MILE MARKER 6.0 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0068866 | OH | Sus | 0 | No | 2016 | OCT | Yes | Multi-Fault | 1226800 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3755 | 20161011 | 1239 | 1556450 | 443 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 3858 | 40.2296 | -123.8491 | 5 SPANS LD SIDE OF MTR #1006978347 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0071168 | OH | Sus | 42812148 | No | 2016 | OCT | Yes | Line to Line | 1228533 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HIGHLANDS-1103 | 43361103 | JUMPER | 52131 | 20161011 | 1410 | 1556519 | 105 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 210 | 38.8495 | -122.5597 | I SPAN FROM EOL ON 52131 TAG | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0071182 | OH | Sus | 0 | No | 2016 | OCT | Yes | Open Circuit | 1228538 | CSO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 1783 | 20161013 | 2246 | 1557866 | 382 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 5730 | 39.4154 | -123.7836 | 31633 VERONICA LD FT BRAGG | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0071815 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Line | 1228990 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 4744 | 20161013 | 1844 | 1557755 | 476 | Distribution Circuit | Vegetation | Tree - fell into line | 190 | 33090 | 40.2786 | -124.2442 | 6 SPANS LOAD SIDE 2505 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0071768 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1228942 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER | 4230 | 20161013 | 1521 | 1557655 | 219 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 5475 | 40.4173 | -124.0895 | BET 4230 & 750641 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0071733 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Line | 1228921 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 6305 | 20161015 | 1728 | 1561640 | 1409 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4227 | 38.6572 | -123.3438 | 7 SPANS FROM EOL | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072632 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Line | 1229674 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 1593 | 20161015 | 1514 | 1561326 | 766 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 13022 | 39.3951 | -123.8011 | 32201 MITCHELL WAY | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 16-0072589 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Line | 1229636 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | JUMPER | WIRE DOWN @ MTR#1008696103 | 20161015 | 1420 | 1561248 | 630 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1260 | 40.2374 | -123.8362 | MTR#1008696103 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072588 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Open Circuit | 1229635 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | OTHER | WIRE DOWN | 20161015 | 1822 | 1561751 | 1045 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 55095 | 40.2174 | -123.8701 | WIRE DOWN AT MTR #1007960761 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072636 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Open Circuit | 1229677 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | TRANSFORMER | 114602528261 | 20161015 | 1436 | 1561240 | 284 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 284 | 40.0928 | -123.9306 | MTR#043647 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072554 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1229604 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 8207 | 20161015 | 1409 | 1561763 | 651 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5208 | 39.9939 | -123.9257 | 1 SPAN LD SIDE OF 8207 & 2 SPANS LD SIDE OF 5391 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072617 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Line | 1229660 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | OTHER | WIRE DOWN | 20161015 | 1315 | 1561119 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 19652 | 38.8021 | -123.5337 | 2 SPANS LD SIDE OF 4445 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072525 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1229580 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 1079 | 20161015 | 1712 | 1561625 | 310 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 25420 | 38.8145 | -122.7087 | 11482 GIFFORD SPGS RD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072623 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Multi-Fault | 1229665 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 97045 | 20161015 | 1517 | 1561330 | 484 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1452 | 38.9008 | -123.6782 | 2 SPANS LOAD SIDE OF 97045 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072567 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1229616 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 1801 | 20161016 | 1602 | 1563227 | 298 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 3576 | 39.4154 | -123.7825 | 19051 PINE TREE LANE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072946 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Line | 1229977 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1510 | 20161016 | 1333 | 1562929 | 392 | Distribution Circuit | Vegetation | Tree - fell into line | 815 | 20767 | 40.1221 | -123.8352 | 6 SPANS LD OF 2529 ON MAINLINE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072880 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1229912 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | JUMPER | 6073 | 20161017 | 411 | 1564445 | 2094 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 12723 | 38.664 | -123.2522 | ON MAIN LINE 4 POLES LD SIDE OF MTR 1008652025 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0073199 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1230254 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1101 | 192171101 | OTHER | MTR 1008022181 3 PHASE WIRE DOWN | 20161017 | 1933 | 1564833 | 400 | Distribution Circuit | Vegetation | Tree - fell into line | 590 | 61932 | 40.9751 | -123.6303 | 2/P/LINE OF 6829 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0073399 | OH | Sus | 31278244 | yes | 2016 | OCT | Yes | Line to Ground | 1230322 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 3079 | 20161018 | 419 | 1564933 | 748 | Distribution Circuit | Vegetation | Tree - branch fell on line | 36 | 26928 | 40.7984 | -123.4043 | MAIN LINE BET FUCO 802411 & 3113 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0073525 | OH | Sus | 31278252 | No | 2016 | OCT | Yes | Three Phase Fault | 1230455 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 4365 | 20161021 | 1732 | 1567284 | 1257 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 6285 | 39.9608 | -123.7701 | 13 SPANS LD SIDE OF 4365 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0074685 | OH | Sus | 31279570 | No | 2016 | OCT | Yes | Line to Ground | 1231288 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CALPELLA-1101 | 43411101 | FUSE | 7497 | 20161024 | 1949 | 1569119 | 426 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 426 | 39.2515 | -123.2181 | 150' LD SIDE OF 7497 | Rain-32-90 F | Crossarm, Wood | Broken, wire on object | 16-0075183 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1231752 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER | 37410 | 20161024 | 1708 | 1569007 | 1052 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 25017 | 40.3263 | -123.9227 | at 3931 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0075166 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Line | 1231734 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1102 | 192171102 | FUSE | 814035 | 20161025 | 1204 | 1569540 | 838 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2514 | 40.9503 | -123.6386 | 2 POLES LD SIDE OF 814035- 730 HWY 96 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0075366 | OH | Sus | 0 | No | 2016 | OCT | Yes | Line to Line | 1231902 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1102 | 43311102 | OCB | 1102/2 | 20161027 | 1036 | 1570750 | 940 | Distribution Circuit | 3rd Party | Vehicle | 2739 | 178328 | 38.9326 | -122.741 | at RISER CUTOUTS 6561 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0075888 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1232296 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | OTHER | WIRE DOWN | 20161027 | 625 | 1570561 | 357 | Distribution Circuit | Vegetation | Tree - grew into line | 250 | 20445 | 40.4167 | -123.9687 | 6 SPANS LD SIDE OF 92331 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0075801 | OH | Sus | 42868370 | yes | 2016 | OCT | Yes | Force Out | 1232219 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 2519 | 20161028 | 1305 | 1571974 | 387 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 5805 | 40.2783 | -124.2438 | MTR# 1008023866 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076495 | OH | Sus | 31281125 | yes | 2016 | OCT | Yes | Line to Line | 1232629 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 4353 | 20161030 | 824 | 1572976 | 546 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4368 | 39.8827 | -123.7351 | MTR 1008780141 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076750 | OH | Sus | 42869649 | No | 2016 | OCT | Yes | Line to Ground | 1232857 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | FUSE | 7071 | 20161105 | 2056 | 1577113 | 529 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 11638 | 39.0325 | -123.37 | mtr1008030115 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0078219 | OH | Sus | 42873727 | No | 2016 | NOV | Yes | Line to Line | 1234025 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 1485 | 20161106 | 830 | 1577262 | 263 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 789 | 39.2271 | -123.7658 | FELICICH- DAVID: loadside of c o 1485 at entrance to albion campground | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0078270 | OH | Sus | 42873743 | No | 2016 | NOV | Yes | Line to Ground | 1234088 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1108 | 43311108 | RECLOSER | 1278 | 20161108 | 2001 | 1578507 | 107 | Distribution Circuit | 3rd Party | Vehicle | 443 | 41311 | 38.9559 | -122.7274 | 7 POLES S/OF LR 426288 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0078795 | OH | Sus | 0 | No | 2016 | NOV | Yes | Line to Line | 1234434 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 5985 | 20161111 | 2352 | 1579928 | 416 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5824 | 39.5625 | -123.7645 | 30120 hwy 1 ft bragg | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0079419 | OH | Sus | 42879059 | No | 2016 | NOV | Yes | Line to Ground | 1234882 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1955 | 20161114 | 923 | 1580801 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 577 | 40.4537 | -124.2324 | 2 LD SIDE OF FUCO 1955 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0079773 | OH | Sus | 42879670 | No | 2016 | NOV | Yes | Line to Ground | 1235229 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1907 | 20161116 | 1945 | 1582516 | 634 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 10144 | 40.4872 | -124.2599 | 2 SPANS SS SBCO 7455 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0080378 | OH | Sus | 42881644 | No | 2016 | NOV | Yes | Line to Ground | 1235649 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 37202 | 20161116 | 216 | 1581920 | 546 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 34944 | 41.1894 | -123.7104 | 3 SPANS LD SIDE LR 37202 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0080122 | OH | Sus | 42881214 | No | 2016 | NOV | Yes | Line to Ground | 1235471 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UKIAH-1114 | 42771114 | FUSE | 437 | 20161116 | 2318 | 1582590 | 922 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 28503 | 39.0797 | -123.2168 | 3 SPANS SS FU 781 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0080379 | OH | Sus | 31284469 | No | 2016 | NOV | Yes | Line to Ground | 1235650 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | JUMPER | HOT WIRE DOWN | 20161120 | 1104 | 1585731 | 493 | Distribution Circuit | Vegetation | Tree - fell into line | 177 | 87261 | 39.6259 | -123.7817 | 8 SPANS LD SIDE OF AND MORE | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081252 | OH | Sus | 31284955 | yes | 2016 | NOV | Yes | Line to Ground | 1236281 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | OTHER | 1 OF 3 WIRES DOWN | 20161120 | 1916 | 1586018 | 718 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 68210 | 40.902 | -123.7847 | 15 SPANS LD SIDE OF 29362 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081298 | OH | Sus | 42882851 | yes | 2016 | NOV | Yes | Line to Ground | 1236335 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3755 | 20161121 | 821 | 1586300 | 995 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 8950 | 40.2296 | -123.8491 | LS 3755 4 SPANS OF WIRE DWN DUE TO TREE ON LINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081439 | OH | Sus | 0 | No | 2016 | NOV | Yes | Line to Ground | 1236452 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 6633 | 20161121 | 937 | 1586407 | 862 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3448 | 41.2495 | -123.6496 | SOURCE SIDE OF 6635 3 SPANS TWD 6633 FUCO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081478 | OH | Sus | 42883372 | No | 2016 | NOV | Yes | Line to Ground | 1236474 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | FUSE | 7535 | 20161121 | 1630 | 1586842 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 14972 | 38.914 | -123.2952 | 2 SPANS SS OF MTR# 1008687723 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081525 | OH | Sus | 31285257 | No | 2016 | NOV | Yes | Line to Ground | 1236503 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 4681 | 20161122 | 2154 | 1587460 | 618 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 6798 | 41.0696 | -123.6811 | E/O HWY 96 HOSLER FIELD HOOPA | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081845 | OH | Sus | 31285473 | No | 2016 | NOV | Yes | Line to Line | 1236692 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 2941 | 20161126 | 1641 | 1589392 | 505 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 42 | 21210 | 40.8794 | -123.5403 | MTR# 1008025371 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0082316 | OH | Sus | 0 | yes | 2016 | NOV | Yes | Line to Line | 1237074 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5187 | 20161127 | 2235 | 1590206 | 350 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 3150 | 39.2861 | -123.7796 | 8 SPANS LD SIDE OF 5187 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0082533 | OH | Sus | 42884935 | yes | 2016 | NOV | Yes | Line to Ground | 1237272 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 5661 | 20161207 | 2245 | 1596575 | 367 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 9175 | 39.392 | -123.7986 | 4/S/LS/OF 5661 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084469 | OH | Sus | 0 | No | 2016 | DEC | Yes | Line to Line | 1239027 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3173 | 20161208 | 146 | 1596750 | 624 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1248 | 39.6337 | -123.7825 | 5 SPANS FROM EOL | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084494 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Line | 1239054 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 3089 | 20161208 | 924 | 1597013 | 426 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1278 | 40.8937 | -123.5704 | 1 SPAN LOAD SIDE OF 3089 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084579 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Line | 1239124 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | JUMPER | WIRE DOWN 2 SPANS LOAD SIDE OF 77909 | 20161209 | 857 | 1597683 | 274 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 7572 | 39.3969 | -123.7711 | 2 SPANS LOAD SIDE OF 77909 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084752 | OH | Sus | 42894067 | No | 2016 | DEC | Yes | Open Circuit | 1239303 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 7701 | 20161210 | 310 | 1598235 | 435 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1740 | 39.2627 | -123.7185 | Garcia- Dan/1260: 41210 airport rd- 3 spans load s/o fuco 7701 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084890 | OH | Sus | 42894391 | yes | 2016 | DEC | Yes | Line to Line | 1239427 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | FUSE | 3987 | 20161214 | 1223 | 1601899 | 856 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 21400 | 40.3073 | -123.9026 | 2 SPANS NORTH OF MTR#1008027453 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085573 | OH | Sus | 0 | No | 2016 | DEC | Yes | Line to Line | 1240232 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | RECLOSER | 518 | 20161214 | 431 | 1601534 | 1035 | Distribution Circuit | Vegetation | Tree - fell into line | 198 | 58712 | 39.7981 | -123.5405 | HARD TAP FEEDING MTR#5000098233 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085498 | OH | Sus | 0 | No | 2016 | DEC | Yes | Line to Line | 1240126 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 1497 | 20161215 | 336 | 1602254 | 727 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5008 | 39.4879 | -123.7764 | MTR # 1008393869 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085655 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1240318 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3075 | 20161215 | 29 | 1602216 | 791 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 13440 | 39.3883 | -123.8123 | FELICICH- DAVID: 32900 pearl dr meter #1006187965 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085632 | OH | Sus | 42899951 | yes | 2016 | DEC | Yes | Line to Line | 1240288 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 5579 | 20161215 | 647 | 1602306 | 536 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2144 | 39.386 | -123.7993 | 2 SPANS LD SIDE OF 5579 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085660 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1240323 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER | 445166 | 20161215 | 737 | 1602357 | 396 | Distribution Circuit | Vegetation | Tree - branch fell on line | 317 | 113625 | 38.6937 | -123.4237 | 1 SS OF 1465 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085677 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1240351 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 2603 | 20161215 | 311 | 1602250 | 574 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 8660 | 39.0759 | -123.5189 | MAR VISTA & PT CABRILLO DR.- MENDOCINO | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085640 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1240297 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 2010 | 20161230 | 1449 | 1613525 | 389 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 9634 | 40.1419 | -123.8077 | 3 SPANS LD OF 2010- BET BUCK TO 8293 & TX#114956029980 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0087420 | OH | Sus | 42907893 | No | 2016 | DEC | Yes | Multi-Fault | 1242863 | CSO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 1297 | 20161230 | 1223 | 1613488 | 240 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 240 | 38.8862 | -123.6668 | LAST SPAN at EOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0087413 | OH | Sus | 42907834 | No | 2016 | DEC | Yes | Line to Ground | 1242856 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | RECLOSER | 4646 | 20161231 | 1907 | 1614036 | 1047 | Distribution Circuit | 3rd Party | Vehicle | 309 | 323523 | 38.8289 | -122.7293 | MTR# 1008029379 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0087508 | OH | Sus | 0 | No | 2016 | DEC | Yes | Three Phase Fault | 1242957 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 1637 | 20170102 | 1250 | 1614906 | 2738 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 42610 | 40.1473 | -123.6276 | 1 SPAN LD SIDE OF 1637/ DAMAGE LOCATIONS LD SIDE OF 4367 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0002826 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Ground | 1243144 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 6064 | 20170102 | 1018 | 1614792 | 326 | Distribution Circuit | Equipment Failure/Involved | Other | 66 | 21516 | 40.2942 | -123.8196 | Bryan- Joe/ K3426-T2067: 9726 DYERVILLE LOOP RD | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0002793 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Ground | 1243108 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 1947 | 20170102 | 1254 | 1614912 | 381 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 10287 | 40.2218 | -123.7973 | 6 SPANS LD SIDE OF 1947 & 7 SPANS LD SIDE OF 1947 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0002820 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Line | 1243138 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 56048 | 20170102 | 1140 | 1614852 | 1020 | Distribution Circuit | Vegetation | Tree - branch fell on line | 443 | 145315 | 40.1477 | -124.0196 | 2 SPANS SS OF 56048- 1 SPAN SS OF 5935- 1 SPAN SS OF MTR#1008023293 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0002799 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Ground | 1243114 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1971 | 20170102 | 1156 | 1614864 | 1540 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 12320 | 40.1113 | -123.8905 | 2 SPANS LD SIDE OF FUCO 1971 | Overcast-Rain-32-90 F | Conductor, Overhead | On Ground | 17-0002844 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Ground | 1243163 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HUMBOLDT BAY-1102 | 192341102 | FUSE | 5301 | 20170102 | 2041 | 1615151 | 593 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 10562 | 40.7008 | -124.138 | 3 SPANS LD SIDE OF 5301 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0002866 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Line | 1243186 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MAPLE CREEK-1101 | 192101101 | OCB | 1101/2 | 20170102 | 1537 | 1615009 | 199 | Distribution Circuit | Vegetation | Tree - fell into line | 144 | 21168 | 40.7683 | -123.8741 | 10 SPANS FROM 6047 TWD 7777 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0002821 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Ground | 1243139 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 3805 | 20170102 | 1558 | 1615021 | 372 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1488 | 39.4618 | -123.2676 | 4 SPANS LD SIDE OF 3805 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0002831 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Ground | 1243148 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | OTHER | WIRE DOWN 2 SPANS LD SIDE OF 29362 | 20170102 | 1528 | 1615008 | 1470 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 70983 | 40.9108 | -123.8135 | 21 SPANS LD SIDE OF 29362 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0002856 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Ground | 1243176 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 8333 | 20170104 | 740 | 1617946 | 124 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 124 | 39.445 | -123.791 | 219 N. SANDERSON WAY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003460 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243637 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 5233 | 20170104 | 1851 | 1618814 | 1505 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 28595 | 40.9521 | -123.6775 | 3200 BRANNON MTN RD | Clear-Strong Winds-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0003860 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243899 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3247 | 20170105 | 2019 | 1619881 | 4023 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4023 | 41.1041 | -123.6898 | LAFFOND- D 530-902-6529 / 1973: TREE at C/O 3337 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0004119 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Ground | 1244050 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | FUSE | 1999 | 20170105 | 1228 | 1619504 | 402 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 402 | 40.2687 | -124.0411 | 3/S/LD SIDE OF 1999 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004065 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Ground | 1244015 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3173 | 20170107 | 859 | 1621065 | 456 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 912 | 39.6337 | -123.7825 | 2&5/P/LD 3173 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004634 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244456 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3939 | 20170107 | 736 | 1620906 | 654 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6540 | 39.4081 | -123.7277 | N/S HWY 20 at P.M. 5.00 (PYORRE TAP) | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004642 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244464 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1607 | 20170107 | 1035 | 1621452 | 687 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2748 | 39.4419 | -123.773 | 31012 SHERWOOD RD. ( N/S RD. ) | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004768 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244571 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | OTHER | WIRE DOWN @ 33755 YARDARM DR | 20170107 | 651 | 1620889 | 547 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 20702 | 38.6755 | -123.4193 | 33755 YARDARM DR | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004558 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244387 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3321 | 20170107 | 1900 | 1622173 | 1283 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2566 | 41.0548 | -123.6724 | LD SIDE OF 3321 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004849 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244651 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER | 532 | 20170107 | 1140 | 1621602 | 772 | Distribution Circuit | Vegetation | Tree - fell into line | 328 | 27439 | 38.8576 | -122.7221 | at MTR 1006775039 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0004660 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244481 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1879 | 20170112 | 946 | 1641240 | 121 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 1452 | 39.8178 | -123.7635 | MTR 1009744125 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008362 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247771 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER | 2531 | 20170112 | 1413 | 1641956 | 1327 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2654 | 40.151 | -124.0289 | 4 SPANS LD SIDE OF FUCO 2531 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0008529 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247889 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 5415 | 20170112 | 905 | 1641171 | 746 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 13720 | 39.3713 | -123.3607 | Rege- Robert/1102: 2701 MUIR MILL RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008332 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247756 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 4365 | 20170113 | 800 | 1642267 | 465 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2325 | 39.9608 | -123.7701 | 6 SPANS LD SIDE OF 4365 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008669 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1248018 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1106 | 43351106 | RECLOSER | 38632 | 20170113 | 1604 | 1642826 | 517 | Distribution Circuit | Vegetation | Tree - fell into line | 259 | 16348 | 38.9913 | -122.7481 | 4 POLES LD SIDE OF FUCO 1145 ON MAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008852 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1248121 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 3223 | 20170116 | 2356 | 1644860 | 802 | Distribution Circuit | 3rd Party | Vehicle | 194 | 101828 | 39.4415 | -123.7786 | SHERWOOD & MARSBEN RD 1 P/E/OF 1607 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0009471 | OH | Sus | 0 | No | 2017 | JAN | Yes | Three Phase Fault | 1248729 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | TRIP-SAVER | 5065 | 20170203 | 23 | 1673417 | 397 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 21438 | 39.3644 | -123.7985 | 44220 CASPER ORCHARD RD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017068 | OH | Sus | 42937449 | yes | 2017 | FEB | Yes | Line to Line | 1255162 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 90655 | 20170203 | 56 | 1673646 | 599 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 599 | 39.3884 | -123.7762 | MTR 1008394756 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017117 | OH | Sus | 42937806 | yes | 2017 | FEB | Yes | Line to Line | 1255200 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | RECLOSER | 95294 | 20170204 | 1543 | 1674962 | 564 | Distribution Circuit | Vegetation | Tree - fell into line | 202 | 113928 | 39.5748 | -123.7698 | Garcia- Dan/1260: mm 73 hwy 1 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0017478 | OH | Sus | 0 | No | 2017 | FEB | Yes | Line to Ground | 1255451 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3367 | 20170206 | 6 | 1675801 | 407 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 13431 | 39.4861 | -123.7885 | 23595 GREEN TREE LN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017671 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1255638 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 1803 | 20170206 | 10 | 1675854 | 870 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 35670 | 40.2013 | -123.4814 | 1 SPAN SOUTH OF 5673 TWD 1847 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017670 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1255637 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3169 | 20170208 | 1125 | 1681816 | 500 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1000 | 39.6461 | -123.7439 | 7 SPANS LD SIDE OF FU 3169 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019094 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256714 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | SWITCH | 270163 | 20170208 | 603 | 1681446 | 372 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 17856 | 39.463 | -123.7831 | 8 SPANS LD SIDE OF SBCO 270163 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018864 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1256605 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 6789 | 20170208 | 1841 | 1682504 | 1183 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 16562 | 40.218 | -123.8718 | 1 SPAN LD SIDE OF FU 6789 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019154 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256766 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 97300 | 20170208 | 1106 | 1681792 | 377 | Distribution Circuit | Equipment Failure/Involved | Overhead | 456 | 147036 | 39.9723 | -123.8008 | AT SBCO 864261 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0018975 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1256661 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8947 | 20170210 | 632 | 1684596 | 504 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2520 | 39.6456 | -123.7506 | 2 SPANS LD/S/O FUCO 8947 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019853 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1257289 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 4231 | 20170210 | 143 | 1684419 | 2357 | Distribution Circuit | Environmental/External | Flood/Erosion | 11 | 25927 | 40.3194 | -123.8119 | 5/S/LD SIDE of 4231 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0020316 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1257698 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | JUMPER | OPEN HIGHSIDE JUMPERS @4939 TO EOL | 20170210 | 510 | 1684519 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 61570 | 39.4296 | -123.3916 | 2/S/LD/OF 4939TREE | Clear-32-90 F | Crossarm, Wood | Broken, wire on object | 17-0019771 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Open Circuit | 1257241 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1103 | 192221103 | FUSE | 2531 | 20170212 | 1044 | 1686663 | 141 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 282 | 40.151 | -124.0289 | 4 POLES LD SIDE OF 2531 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0020466 | OH | Sus | 0 | No | 2017 | FEB | Yes | Line to Line | 1257838 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | OTHER | WIRE DOWN | 20170215 | 1345 | 1689363 | 524 | Distribution Circuit | Vegetation | Tree - fell into line | 335 | 87190 | 40.373 | -124.064 | BET 4230 AND 908763 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021356 | OH | Sus | 0 | No | 2017 | FEB | Yes | Line to Ground | 1258574 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3769 | 20170216 | 206 | 1689815 | 830 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11620 | 40.2642 | -123.8276 | 3 SP LD SD METER#1010157961 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021697 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1258839 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | SECTIONALIZER | 1780 | 20170216 | 946 | 1690316 | 2011 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 12318 | 40.062 | -123.8498 | 21-23 SPANS LD SIDE OF 1780 | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0021577 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1258774 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 8652 | 20170216 | 550 | 1690029 | 644 | Distribution Circuit | Vegetation | Tree - fell into line | 251 | 159347 | 40.1065 | -123.9278 | 1- mainline 6 spans SS 2529- 2-mainline at fused cutouts 2529 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021486 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1258693 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 4160 | 20170216 | 1045 | 1690392 | 547 | Distribution Circuit | Vegetation | Tree - fell into line | 416 | 190036 | 40.4272 | -123.481 | 2 SPANS SS OF FUCO 5193 ON MAIN LINE | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0021613 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Force Out | 1258798 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 2625 | 20170216 | 529 | 1690009 | 500 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4602 | 39.0997 | -123.5713 | 1 LD SIDE OF MTR# 1009365610 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021508 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1258710 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4557 | 20170219 | 1650 | 1701806 | 2510 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 75300 | 38.6377 | -123.3159 | at LINE & BUCK TO MTR#5000120460 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023513 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260499 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3941 | 20170219 | 223 | 1701003 | 844 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 30731 | 39.3929 | -123.7713 | 17239 FRANKLIN RD | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023317 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260322 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | RECLOSER | 47952 | 20170219 | 2321 | 1702198 | 818 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 89980 | 38.9145 | -123.6392 | 1 SPAN LD SIDE OF 47952 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023608 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1260604 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 2653 | 20170219 | 2357 | 1702255 | 922 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 7376 | 38.932 | -123.6916 | 6 SPANS LOAD SIDE OF 2653 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023622 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1260621 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4573 | 20170226 | 1955 | 1714648 | 887 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 28384 | 38.7197 | -123.3444 | MAIN LINE AT 9787 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0026930 | OH | Sus | 42954071 | No | 2017 | FEB | Yes | Force Out | 1263629 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | NEWBURG-1131 | 192151131 | FUSE | 7525 | 20170227 | 225 | 1714751 | 684 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5472 | 40.5678 | -124.1102 | MTR# 1008930076 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0026939 | OH | Sus | 31307893 | No | 2017 | FEB | Yes | Three Phase Fault | 1263639 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 6789 | 20170301 | 1236 | 1716897 | 638 | Distribution Circuit | 3rd Party | Vehicle | 14 | 8932 | 40.218 | -123.8718 | 2ND POLE LD SIDE OF FUCO 6789 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0027668 | OH | Sus | 0 | No | 2017 | MAR | Yes | Line to Line | 1264175 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 1885 | 20170305 | 1642 | 1720393 | 1266 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 114 | 38.6662 | -123.3121 | 6 SPANS LOAD SIDE OF 1885 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0028550 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Three Phase Fault | 1264912 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | RECLOSER | 29362 | 20170305 | 2356 | 1720487 | 2549 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 211060 | 40.8941 | -123.7726 | SS LR 91926 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0028579 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Line | 1264938 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CALPELLA-1101 | 43411101 | FUSE | 6369 | 20170306 | 939 | 1720892 | 418 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 418 | 39.319 | -123.3146 | 1 SPAN SS OF FUCO 6371 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0028703 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Three Phase Fault | 1265035 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 2010 | 20170306 | 540 | 1720602 | 734 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 12425 | 40.1419 | -123.8077 | 1 SPAN LD SIDE OF MTR 1008023417 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0028601 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Ground | 1264962 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 2499 | 20170306 | 636 | 1720619 | 498 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 7968 | 39.668 | -123.5141 | 4 SPANS LOAD SIDE OF 2499 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0028733 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Three Phase Fault | 1265052 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 2459 | 20170306 | 955 | 1720859 | 625 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 6875 | 39.5239 | -123.3873 | GALLETTI- TIM: WIRE DOWN 5 POLES LS OF FCO 2459- SHIMMINS RIDGE | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0028864 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Force Out | 1265137 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | SWITCH | 2001 | 20170306 | 637 | 1720675 | 109 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 2725 | 40.3384 | -124.0323 | WIRE DOWN 5 SPANS LD SIDE OF SBCO 750641 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0028637 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Line | 1264979 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2117 | 20170306 | 412 | 1720537 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 11024 | 39.4569 | -123.3861 | 26671 HAWK TERRACE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0028593 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Line | 1264953 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 37506 | 20170306 | 413 | 1720588 | 727 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 27132 | 39.4831 | -123.3611 | GALLETTI- TIM: TREE THROUGH LINE at F.CO 92673- M.M 53.26 N. HWY 101- WILLITS | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0028606 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Line | 1264964 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2411 | 20170306 | 352 | 1720615 | 683 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 11611 | 39.4803 | -123.3611 | 2 SPANS LD SIDE MTR 1008842029 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0028612 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Ground | 1264967 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2849 | 20170306 | 400 | 1720559 | 1980 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 19800 | 39.4867 | -123.276 | 3/S/LD SIDE OF 2849 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on object | 17-0028826 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Ground | 1265114 | CSO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1102 | 192171102 | FUSE | 3341 | 20170306 | 434 | 1721096 | 936 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 936 | 40.9872 | -123.6399 | LD SIDE FU 3341 | Overcast-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 17-0028803 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Ground | 1265088 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1102 | 192171102 | FUSE | 3217 | 20170306 | 1401 | 1721122 | 1389 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5556 | 40.9694 | -123.6421 | LD SIDE OF FU 3217 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0028857 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Ground | 1265134 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 1375 | 20170308 | 1615 | 1722763 | 283 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 566 | 38.9993 | -123.6836 | 9 SPANS E/OF 1375 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0029487 | OH | Sus | 31311348 | No | 2017 | MAR | Yes | Line to Line | 1265569 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | JUMPER | WIRE DOWN 2 POLES LD SIDE OF 55437 | 20170308 | 1512 | 1722694 | 806 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 806 | 40.9168 | -123.8306 | 2 POLES LD SIDE OF 55437 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0029502 | OH | Sus | 0 | No | 2017 | MAR | Yes | Open Circuit | 1265589 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HUMBOLDT BAY-1102 | 192341102 | FUSE | 5435 | 20170312 | 15 | 1725299 | 930 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 42625 | 40.7123 | -124.1628 | at FUCO 4301 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0030206 | OH | Sus | 31311860 | No | 2017 | MAR | Yes | Line to Ground | 1266135 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | RECLOSER | 47952 | 20170315 | 913 | 1727562 | 530 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 58300 | 38.9145 | -123.6392 | 25425 10 MILE C/OFF RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0030903 | OH | Sus | 42970946 | No | 2017 | MAR | Yes | Line to Line | 1266701 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER | 2936 | 20170315 | 652 | 1727392 | 606 | Distribution Circuit | Vegetation | Tree - fell into line | 573 | 185362 | 40.8665 | -123.5144 | LAFFOND- D 530-902-6529 / 1973: 2nd span in from LR 2936 on fisher rd. Burnt Ranch | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0030846 | OH | Sus | 42970775 | No | 2017 | MAR | Yes | Line to Ground | 1266623 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER | 1690 | 20170319 | 353 | 1730036 | 613 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 34941 | 40.1677 | -123.6109 | 13788 Alderpoint RD meter #1007960774 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0031741 | OH | Sus | 42973095 | No | 2017 | MAR | Yes | Line to Ground | 1267337 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UKIAH-1115 | 42771115 | FUSE | 899 | 20170319 | 2226 | 1730326 | 805 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 6543 | 39.1781 | -123.1891 | 100FT ON FAWN PLACE S/OF DEERWOOD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0031794 | OH | Sus | 0 | No | 2017 | MAR | Yes | Line to Line | 1267401 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 8187 | 20170320 | 840 | 1730524 | 202 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 202 | 38.7661 | -123.5213 | 2 SPANS LD SIDE OF 8187 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0031873 | OH | Sus | 31312375 | yes | 2017 | MAR | Yes | Line to Ground | 1267460 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3247 | 20170321 | 924 | 1731755 | 2016 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2016 | 41.1041 | -123.6898 | 8 SPANS SS OF FUCO 3337 TWD 3247 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0032500 | OH | Sus | 42974443 | yes | 2017 | MAR | Yes | Line to Ground | 1267836 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3199 | 20170321 | 1657 | 1732366 | 1136 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2272 | 41.2635 | -123.6075 | 1ST SPAN TO THE WEST LD SIDE OF 3199 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0032551 | OH | Sus | 42974450 | yes | 2017 | MAR | Yes | Line to Line | 1267883 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | RECLOSER | 5002 | 20170321 | 924 | 1731758 | 884 | Distribution Circuit | Environmental/External | Flood/Erosion | 590 | 504675 | 40.9462 | -123.6409 | Tree fell through line 4 spans source side of 6283 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0032258 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Line | 1267737 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | RECLOSER | 4218 | 20170323 | 2239 | 1734283 | 632 | Distribution Circuit | Vegetation | Tree - branch fell on line | 125 | 30104 | 40.7595 | -123.9934 | 5588 KNEELAND RD at COMBO 7093 ON THE MAINLINE | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0033297 | OH | Sus | 0 | No | 2017 | MAR | Yes | Multi-Fault | 1268388 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1899 | 20170323 | 613 | 1733481 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4829 | 40.5106 | -124.1608 | 19/p/ld/s of 1899 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0033006 | OH | Sus | 0 | No | 2017 | MAR | Yes | Line to Line | 1268188 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | FUSE | 6115 | 20170324 | 507 | 1734396 | 608 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 608 | 40.4152 | -123.9362 | 5 SPANS LD SIDE OF 6115 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0033411 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Line | 1268446 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3247 | 20170326 | 1816 | 1736041 | 343 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 343 | 41.1041 | -123.6898 | AT 3247 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0033888 | OH | Sus | 0 | No | 2017 | MAR | Yes | Line to Line | 1268834 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 4628 | 20170330 | 136 | 1738790 | 720 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 47088 | 39.24 | -123.7713 | ON MAINLINE N/OF 8953 & S/OF 8733 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0034901 | OH | Sus | 42979233 | yes | 2017 | MAR | Yes | Multi-Fault | 1269617 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3151 | 20170330 | 1910 | 1740230 | 286 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 4290 | 39.3416 | -123.811 | 4 LD SIDE OF FU 3151 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0035277 | OH | Sus | 42980709 | yes | 2017 | MAR | Yes | Line to Ground | 1269908 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2571 | 20170330 | 1846 | 1740163 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6210 | 40.136 | -123.9844 | 2/S/LD/S/OF 2571 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0035373 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Ground | 1270002 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8961 | 20170331 | 1806 | 1741704 | 1015 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1015 | 39.5609 | -123.7256 | 1 LD SIDE FU 8961 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0035687 | OH | Sus | 42981840 | yes | 2017 | MAR | Yes | Line to Ground | 1270234 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 3003 | 20170410 | 1045 | 1754308 | 564 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1128 | 40.9403 | -123.6697 | 2 SPANS LOAD SIDE OF FUCO 3003 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038854 | OH | Sus | 42991500 | No | 2017 | APR | Yes | Line to Ground | 1272889 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5917 | 20170411 | 1803 | 1755604 | 565 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4520 | 39.285 | -123.7862 | 2ND SPAN NORTH OF FUCO 5917 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0039320 | OH | Sus | 0 | No | 2017 | APR | Yes | Line to Ground | 1273207 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CARLOTTA-1121 | 192291121 | FUSE | 7723 | 20170411 | 1931 | 1755661 | 894 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 24138 | 40.5143 | -123.991 | 1/S/LD/S TO 7723 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0039376 | OH | Sus | 42992905 | No | 2017 | APR | Yes | Line to Ground | 1273264 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 7881 | 20170412 | 941 | 1755976 | 955 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 11460 | 40.8778 | -123.5132 | LD SIDE OF 7881 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0039523 | OH | Sus | 0 | No | 2017 | APR | Yes | Line to Ground | 1273379 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 6054 | 20170413 | 532 | 1756689 | 642 | Distribution Circuit | Vegetation | Tree - fell into line | 565 | 60747 | 40.2854 | -123.8367 | at MTR#1006986428 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0039761 | OH | Sus | 0 | yes | 2017 | APR | Yes | Three Phase Fault | 1273506 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 2094 | 20170413 | 1357 | 1757130 | 877 | Distribution Circuit | Vegetation | Tree - fell into line | 304 | 70662 | 40.436 | -123.4882 | 8 SPANS SS OF 4107 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0039990 | OH | Sus | 31319437 | yes | 2017 | APR | Yes | Line to Ground | 1273649 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UKIAH-1114 | 42771114 | FUSE | 2009 | 20170413 | 1505 | 1757192 | 220 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 2420 | 39.1144 | -123.1178 | 3 SPANS FROM EOL | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0040069 | OH | Sus | 42993858 | yes | 2017 | APR | Yes | Line to Line | 1273686 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1909 | 20170416 | 1259 | 1758888 | 591 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 14184 | 40.5115 | -124.1597 | 5 SPANS LD SIDE OF 1909 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0040613 | OH | Sus | 0 | No | 2017 | APR | Yes | Line to Line | 1274101 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 1033 | 20170417 | 1810 | 1759776 | 12 | Distribution Circuit | 3rd Party | Vehicle | 8 | 96 | 38.7814 | -122.6848 | 1 WEST AND 1 SOUTH OF 1033 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0040910 | OH | Sus | 0 | No | 2017 | APR | Yes | Force Out | 1274323 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | RECLOSER | 47952 | 20170422 | 1037 | 1764764 | 488 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 48038 | 38.9145 | -123.6392 | 1/S/LD/S OF MTR#3J2128 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0042114 | OH | Sus | 42999485 | No | 2017 | APR | Yes | Line to Ground | 1275266 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 94127 | 20170423 | 1653 | 1765429 | 557 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2785 | 39.2277 | -123.7423 | 1 S/OF 94127 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0042231 | OH | Sus | 42999587 | No | 2017 | APR | Yes | Line to Ground | 1275397 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 66809 | 20170424 | 715 | 1765798 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1635 | 41.2799 | -123.8407 | 4 SPANS LD SIDE OF 66809 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0042368 | OH | Sus | 31321155 | No | 2017 | APR | Yes | Line to Ground | 1275498 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | RECLOSER | 474 | 20170424 | 419 | 1765676 | 423 | Distribution Circuit | Vegetation | Tree - fell into line | 218 | 92214 | 38.9128 | -123.6795 | 2 SPANS LD SIDE OF 1361 TWD 47952 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0042282 | OH | Sus | 31321150 | No | 2017 | APR | Yes | Line to Line | 1275441 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 1510 | 20170425 | 726 | 1766505 | 699 | Distribution Circuit | Vegetation | Tree - fell into line | 833 | 235706 | 40.1221 | -123.8352 | Bryan- Joe/ K3426-T2067: 8 load side 1510 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0042643 | OH | Sus | 0 | No | 2017 | APR | Yes | Line to Ground | 1275625 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | SWITCH | 1925 | 20170429 | 937 | 1770327 | 165 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 4290 | 40.4632 | -124.3036 | 7/S/LD/S/OF 1925 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0043875 | OH | Sus | 0 | No | 2017 | APR | Yes | Force Out | 1276491 | CSO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 2537 | 20170429 | 1142 | 1770385 | 446 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 446 | 39.5875 | -123.4578 | LD SIDE TO 2537 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0043893 | OH | Sus | 31321699 | No | 2017 | APR | Yes | Line to Ground | 1276509 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 37202 | 20170504 | 858 | 1774391 | 546 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 30810 | 41.1894 | -123.7104 | SS FUCO 8435- MM 32.27 ON HWY 169 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0045179 | OH | Sus | 31323731 | yes | 2017 | MAY | Yes | Line to Ground | 1277499 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER | WIRE DOWN | 20170505 | 1402 | 1775535 | 343 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 4648 | 40.1181 | -123.8333 | EEL RIVER LANE- at MTR#1008024346 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0045687 | OH | Sus | 43007855 | No | 2017 | MAY | Yes | Line to Ground | 1277795 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | OTHER | HOT WIRE ON GRD GREENWOOD HEIGHTS DR & BURKE | 20170506 | 1118 | 1776183 | 842 | Distribution Circuit | Vegetation | Tree - fell into line | 354 | 113630 | 40.7951 | -124.0274 | Stapleton- Travis/1981: burke and kneeland | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0045785 | OH | Sus | 43008043 | yes | 2017 | MAY | Yes | Line to Ground | 1277908 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5731 | 20170506 | 1500 | 1776547 | 897 | Distribution Circuit | Vegetation | Tree - fell into line | 121 | 37752 | 39.2692 | -123.7817 | WIRE DOWN at 3317 ON MAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0045831 | OH | Sus | 0 | yes | 2017 | MAY | Yes | Three Phase Fault | 1277958 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | OTHER | HOT WIRE DOWN @MR1009202115 TO EOL | 20170506 | 1515 | 1776465 | 1290 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2580 | 39.1407 | -123.6432 | at MTR1009202115 | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0045838 | OH | Sus | 0 | yes | 2017 | MAY | Yes | Line to Ground | 1277965 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3059 | 20170506 | 1233 | 1776204 | 1323 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 47628 | 39.4152 | -123.7708 | 9/S/W/OF 3059 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0045792 | OH | Sus | 0 | yes | 2017 | MAY | Yes | Force Out | 1277918 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 3223 | 20170506 | 1349 | 1776317 | 561 | Distribution Circuit | Vegetation | Tree - fell into line | 196 | 109956 | 39.4416 | -123.779 | at 300295 TREE ACROSS OH | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0045802 | OH | Sus | 0 | yes | 2017 | MAY | Yes | Line to Ground | 1277929 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER | 37410 | 20170506 | 1527 | 1776498 | 2922 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 93846 | 40.3263 | -123.9227 | Bryan- Joe/ K3426-T2067: 3 sp src sd r1593 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0045813 | OH | Sus | 0 | yes | 2017 | MAY | Yes | Line to Ground | 1277940 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 1102/2 | 20170506 | 1321 | 1776296 | 1815 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1761 | 146907 | 40.1033 | -123.7926 | Rapich- Robert/ K1987-T1995: south of dean creek | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0045794 | OH | Sus | 0 | yes | 2017 | MAY | Yes | Line to Ground | 1277921 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1965 | 20170506 | 1335 | 1776425 | 624 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 10793 | 40.1219 | -123.834 | at MTR1008024346 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0045819 | OH | Sus | 0 | yes | 2017 | MAY | Yes | Line to Line | 1277946 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARRIS-1109 | 192431109 | FUSE | 5889 | 20170506 | 1419 | 1776356 | 1746 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 34920 | 40.7659 | -124.0674 | MULTIPLE LD SIDE OF FU 5889 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0045986 | OH | Sus | 0 | yes | 2017 | MAY | Yes | Line to Ground | 1278117 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HUMBOLDT BAY-1102 | 192341102 | FUSE | 7619 | 20170506 | 1508 | 1776456 | 766 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 10724 | 40.7002 | -124.1458 | 6 SPANS LOAD SIDE OF 7619 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0045842 | OH | Sus | 0 | yes | 2017 | MAY | Yes | Line to Line | 1277970 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CARLOTTA-1121 | 192291121 | JUMPER | WIRE DOWN 1 LD SIDE FU 4067 | 20170507 | 1112 | 1777005 | 727 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 727 | 40.5242 | -123.9971 | 1 LD SIDE FU 4067 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0046005 | OH | Sus | 0 | yes | 2017 | MAY | Yes | Line to Ground | 1278133 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | OTHER | WIRE DOWN | 20170507 | 2001 | 1777311 | 420 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 7500 | 39.2269 | -123.7511 | SOURCE SIDE OF MTR#1008953898 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0046059 | OH | Sus | 0 | yes | 2017 | MAY | Yes | Line to Ground | 1278184 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1787 | 20170507 | 940 | 1776955 | 1753 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 24542 | 40.0106 | -123.9297 | 5 SPANS SOURCE SIDE OF 8207- FIRST TRANSFORMER LD SIDE OF 8207 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0046003 | OH | Sus | 0 | yes | 2017 | MAY | Yes | Three Phase Fault | 1278132 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 80357 | 20170507 | 1323 | 1777106 | 627 | Distribution Circuit | 3rd Party | Vehicle | 13 | 8151 | 39.4596 | -123.3915 | 1 POLE LD SIDE OF INTERSECTION OF COYOTE AND POPPY IN WILLITS | Clear-32-90 F | Pole-Wood | Broken, wire on object | 17-0046020 | OH | Sus | 0 | yes | 2017 | MAY | Yes | Line to Line | 1278148 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | OCB | 1141/2 | 20170508 | 1245 | 1777721 | 523 | Distribution Circuit | Vegetation | Tree - fell into line | 185 | 55575 | 40.2866 | -123.8369 | MTR#1010141276 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0046219 | OH | Sus | 0 | yes | 2017 | MAY | Yes | Line to Line | 1278322 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 6789 | 20170508 | 1300 | 1777734 | 400 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 4890 | 40.218 | -123.8718 | 18 LD SIDE OF 6789 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0046248 | OH | Sus | 0 | yes | 2017 | MAY | Yes | Line to Ground | 1278335 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | JUMPER | HOT WIRE DOWN @ MTR 1006187315 | 20170511 | 1646 | 1780278 | 569 | Distribution Circuit | 3rd Party | Vehicle | 14 | 7636 | 39.4424 | -123.3895 | MTR 1006187315 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0047387 | OH | Sus | 0 | No | 2017 | MAY | Yes | Line to Ground | 1279131 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER | 95324 | 20170514 | 1741 | 1781963 | 178 | Distribution Circuit | Vegetation | Tree - fell into line | 223 | 26806 | 40.284 | -123.8723 | 25 SPANS LD SIDE OF 95324 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0047829 | OH | Sus | 0 | No | 2017 | MAY | Yes | Three Phase Fault | 1279505 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 4589 | 20170514 | 1116 | 1781790 | 206 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 412 | 38.6586 | -123.4034 | Felicich- David: three spans sorce side of mtr#1006274002 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0047810 | OH | Sus | 43016247 | No | 2017 | MAY | Yes | Line to Line | 1279483 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 6789 | 20170518 | 1759 | 1785100 | 484 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 6776 | 40.218 | -123.8718 | 17 SPANS LD SIDE OF 6789 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0048993 | OH | Sus | 43019532 | No | 2017 | MAY | Yes | Line to Ground | 1280362 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 93234 | 20170520 | 359 | 1785939 | 467 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 43431 | 40.2355 | -123.8346 | 22 SPANS LD SIDE OF LR 93234 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0049315 | OH | Sus | 31326960 | No | 2017 | MAY | Yes | Line to Line | 1280573 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1101 | 192171101 | FUSE | 2985 | 20170522 | 1358 | 1787812 | 710 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 9916 | 40.9442 | -123.621 | 2 SPANS SS OF MTR 1008026219 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0049699 | OH | Sus | 0 | yes | 2017 | MAY | Yes | Line to Ground | 1280895 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | RECLOSER | 1294 | 20170525 | 949 | 1790267 | 223 | Distribution Circuit | Vegetation | Tree - fell into line | 624 | 58584 | 38.8037 | -123.5835 | Thorpe- Tim/2094: LS O fucos 7299 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0050581 | OH | Sus | 43023143 | No | 2017 | MAY | Yes | Line to Line | 1281558 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1102 | 192171102 | OCB | 1102/2 | 20170525 | 1652 | 1790753 | 1628 | Distribution Circuit | Vegetation | Tree - fell into line | 148 | 77756 | 40.9479 | -123.6402 | 1 SPAN SS OF FUCO 3341 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0050777 | OH | Sus | 31328129 | No | 2017 | MAY | Yes | Line to Ground | 1281616 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 600433 | 20170528 | 1308 | 1792343 | 322 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3220 | 39.5133 | -123.7332 | 1 SPAN W/OF MTR# 1009650210 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0051233 | OH | Sus | 43024658 | No | 2017 | MAY | Yes | Line to Line | 1281935 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3239 | 20170529 | 530 | 1792523 | 333 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 9441 | 41.0765 | -123.6874 | SINGLE ? TAP 4/S/LD SIDE OF 3239 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0051274 | OH | Sus | 31328524 | No | 2017 | MAY | Yes | Line to Ground | 1281976 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8961 | 20170604 | 713 | 1796574 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 470 | 39.5609 | -123.7256 | 4 LD SIDE OF FUSE 8961 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0052610 | OH | Sus | 31329680 | No | 2017 | JUN | Yes | Line to Ground | 1282990 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 97300 | 20170607 | 2127 | 1799155 | 533 | Distribution Circuit | Vegetation | Tree - fell into line | 443 | 15664 | 39.9723 | -123.8008 | Bryan- Joe/ K3426-T2067: 1 sp ld sd 1770 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0053488 | OH | Sus | 43030055 | No | 2017 | JUN | Yes | Three Phase Fault | 1283643 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1879 | 20170608 | 1515 | 1799694 | 523 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 2656 | 39.8178 | -123.7635 | 3 SPANS SOURCE SIDE OF EOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0053799 | OH | Sus | 43030573 | yes | 2017 | JUN | Yes | Line to Ground | 1283813 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2823 | 20170615 | 1501 | 1805231 | 719 | Distribution Circuit | 3rd Party | Vehicle | 251 | 180469 | 39.3949 | -123.3133 | 1 POLE SS OF MTR# 1003428961 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0055557 | OH | Sus | 0 | No | 2017 | JUN | Yes | Three Phase Fault | 1285112 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 6789 | 20170620 | 239 | 1811966 | 888 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 12432 | 40.218 | -123.8718 | 18 SPANS LD SIDE OF 6789 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0056867 | OH | Sus | 0 | yes | 2017 | JUN | Yes | Line to Line | 1286308 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | FUSE | 1997 | 20170620 | 134 | 1811933 | 143 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1001 | 40.2852 | -124.0595 | 8 SPANS LD SIDE OF 1997 | Clear-32-90 F | Insulator | Broken, wire on object | 17-0056856 | OH | Sus | 0 | yes | 2017 | JUN | Yes | Force Out | 1286293 | INS | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER | 4230 | 20170620 | 1151 | 1812485 | 1033 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 9256 | 40.4173 | -124.0895 | Mello- Adam/ K4736-T1963: 10 sp source 5737 solid blades | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0057001 | OH | Sus | 43042175 | yes | 2017 | JUN | Yes | Line to Line | 1286402 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | JUMPER | WIRE DOWN S/S/SOURCE SIDE 3155 | 20170625 | 940 | 1817598 | 953 | Distribution Circuit | Vegetation | Tree - branch fell on line | 488 | 457303 | 41.281 | -123.5865 | WIRE DOWN 2 SPANS SOURCE 3155 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0058431 | OH | Sus | 43044673 | No | 2017 | JUN | Yes | Line to Ground | 1287533 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1104 | 42661104 | FUSE | 2785 | 20170625 | 23 | 1817464 | 924 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 23100 | 39.4043 | -123.3869 | 19/10 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0058406 | OH | Sus | 31333780 | No | 2017 | JUN | Yes | Line to Ground | 1287503 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | JUMPER | WIRE DOWN | 20170628 | 821 | 1819626 | 774 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 64 | 24874 | 39.2887 | -123.5829 | 4 LD SIDE MTR 1010109461 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0059194 | OH | Sus | 43046450 | No | 2017 | JUN | Yes | Line to Ground | 1288170 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1122 | 192321122 | OCB | 1122/2 | 20170629 | 30 | 1820294 | 1170 | Distribution Circuit | Vegetation | Tree - fell into line | 103 | 96805 | 40.2139 | -123.5966 | 1653 | Overcast-32-90 F | Insulator | Broken, wire on ground | 17-0059342 | OH | Sus | 31334392 | No | 2017 | JUN | Yes | Line to Line | 1288235 | INS | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UKIAH-1111 | 42771111 | JUMPER | TREE THROUGH LINES | 20170630 | 947 | 1821399 | 388 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 3 | 1164 | 39.2274 | -123.3115 | 4 LD SIDE OF LINE & BUCK FEEDING MTR 1008942878 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0059751 | OH | Sus | 31334636 | No | 2017 | JUN | Yes | Open Circuit | 1288546 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 7893 | 20170709 | 1129 | 1827366 | 875 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 21000 | 38.8772 | -122.7203 | at MTR 10108159168 | Clear-Above 90 | Pole-Wood | Broken, wire on ground | 17-0061544 | OH | Sus | 0 | No | 2017 | JUL | Yes | Line to Ground | 1289757 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3769 | 20170710 | 1232 | 1828225 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 5910 | 40.2642 | -123.8276 | 5 SPANS LD SIDE FU 3769 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0061771 | OH | Sus | 31336232 | No | 2017 | JUL | Yes | Line to Ground | 1289947 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1771 | 20170712 | 2010 | 1830250 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4616 | 40.0718 | -123.8298 | 4 SPANS LD SIDE OF FUCO 1771 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0062445 | OH | Sus | 0 | No | 2017 | JUL | Yes | Line to Line | 1290419 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 97300 | 20170714 | 840 | 1831321 | 170 | Distribution Circuit | Vegetation | Tree - fell into line | 444 | 59880 | 39.9723 | -123.8008 | 7 SPANS LD SIDE OF LR 1770 OR SOUTH OF | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0062865 | OH | Sus | 31336956 | No | 2017 | JUL | Yes | Line to Ground | 1290741 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 5589 | 20170715 | 1842 | 1832366 | 323 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 969 | 39.388 | -123.7997 | 1/S/SS TO MTR#101043592 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0063153 | OH | Sus | 43060259 | No | 2017 | JUL | Yes | Line to Ground | 1290968 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | FUSE | 3965 | 20170716 | 1130 | 1832697 | 198 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 198 | 40.3417 | -123.8803 | 2 SPANS LD SIDE OF 3965 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0063223 | OH | Sus | 43060361 | No | 2017 | JUL | Yes | Line to Ground | 1291033 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 4160 | 20170716 | 1319 | 1832740 | 413 | Distribution Circuit | Vegetation | Tree - fell into line | 416 | 52038 | 40.4272 | -123.481 | MTR#1008671450 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0063236 | OH | Sus | 0 | No | 2017 | JUL | Yes | Line to Ground | 1291042 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1770 | 20170722 | 1313 | 1837676 | 468 | Distribution Circuit | Vegetation | Tree - fell into line | 344 | 65643 | 39.9153 | -123.7634 | 2 SPANS LD SIDE OF 44055 ON MAIN LINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0064722 | OH | Sus | 43065929 | No | 2017 | JUL | Yes | Line to Line | 1292106 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | JUMPER | WIRE DOWN LD SIDE LR 3050 | 20170722 | 1225 | 1837671 | 1462 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 16 | 23227 | 40.8835 | -123.7695 | 2 SPANS LD SIDE OF MTR 5000096012 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0064721 | OH | Sus | 43065926 | No | 2017 | JUL | Yes | Line to Ground | 1292104 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 2499 | 20170723 | 1817 | 1838215 | 804 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 12864 | 39.668 | -123.5141 | tree fell 50' ss to 3483 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0064854 | OH | Sus | 0 | No | 2017 | JUL | Yes | Line to Ground | 1292219 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 3079 | 20170802 | 554 | 1844323 | 3218 | Distribution Circuit | Vegetation | Tree - branch fell on line | 36 | 5832 | 40.7984 | -123.4043 | BETWEEN 12TH & 13TH POLE LD SIDE OF 3079 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0067270 | OH | Sus | 0 | yes | 2017 | AUG | Yes | Three Phase Fault | 1293837 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | RECLOSER | 4218 | 20170808 | 2138 | 1848865 | 98 | Distribution Circuit | 3rd Party | Vehicle | 21 | 2058 | 40.7595 | -123.9934 | 1/S/SS/OF 6049 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0068911 | OH | Sus | 0 | No | 2017 | AUG | Yes | Line to Line | 1295014 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3769 | 20170811 | 1108 | 1850479 | 318 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 1962 | 40.2642 | -123.8276 | 2 SPANS SS OF MTR# 1010028433 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0069646 | OH | Sus | 43082908 | No | 2017 | AUG | Yes | Line to Ground | 1295528 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 1102/2 | 20170814 | 614 | 1851909 | 914 | Distribution Circuit | Vegetation | Tree - fell into line | 1802 | 959989 | 40.1033 | -123.7926 | 1 SPAN EAST AND 1 SPAN WEST OF SW 2127 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0070003 | OH | Sus | 0 | No | 2017 | AUG | Yes | Line to Ground | 1295821 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER | 1690 | 20170828 | 2356 | 1862140 | 1071 | Distribution Circuit | Vegetation | Tree - branch fell on line | 57 | 3892 | 40.1677 | -123.6109 | 2 SPANS S/OF 1839 ON THE MAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0073645 | OH | Sus | 43095598 | yes | 2017 | AUG | Yes | Line to Line | 1298378 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 2497 | 20170905 | 644 | 1870282 | 464 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 10528 | 39.6727 | -123.5128 | 2 SPANS LD SIDE OF MTR#1009671711- 1540 FITCH RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0075976 | OH | Sus | 43099533 | No | 2017 | SEP | Yes | Line to Ground | 1300217 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 93234 | 20170913 | 1432 | 1878404 | 386 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 35898 | 40.2355 | -123.8346 | Rapich- Robert/ K1987-T1995: mtr 1010268361 on main line | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0078695 | OH | Sus | 43110165 | yes | 2017 | SEP | Yes | Line to Line | 1302219 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | RECLOSER | 4218 | 20170914 | 841 | 1878722 | 137 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 21 | 2877 | 40.7595 | -123.9934 | 1 SPAN FROM 4634 TWD 1177 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0078868 | OH | Sus | 43110373 | No | 2017 | SEP | Yes | Line to Ground | 1302311 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | JUMPER | WIRE DOWN 2 P/SS OF 1687 SW 1687 | 20170914 | 1356 | 1879052 | 337 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 19722 | 40.3072 | -123.8189 | Rapich- Robert/ K1987-T1995: 2 spans source side 1687 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0079010 | OH | Sus | 43110703 | No | 2017 | SEP | Yes | Force Out | 1302407 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER | 31304 | 20170918 | 905 | 1880795 | 346 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 40262 | 39.4151 | -123.7704 | 29601 HIGHWAY 20 FORT BRAGG | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0079671 | OH | Sus | 43113027 | No | 2017 | SEP | Yes | Multi-Fault | 1302991 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 2540 | 20170920 | 635 | 1882190 | 880 | Distribution Circuit | Vegetation | Tree - fell into line | 310 | 152743 | 40.2432 | -124.127 | LD SIDE FUCO 2555 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0080197 | OH | Sus | 31352214 | No | 2017 | SEP | Yes | Line to Ground | 1303307 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARRIS-1109 | 192431109 | RECLOSER | 4634 | 20170927 | 1906 | 1887095 | 614 | Distribution Circuit | Equipment Failure/Involved | Overhead | 165 | 35394 | 40.7606 | -124.0542 | Stapleton- Travis/1981: 2 spans east of and then 1 span south of lr4218 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0082303 | OH | Sus | 43118560 | No | 2017 | SEP | Yes | Line to Ground | 1304682 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 9869 | 20171010 | 934 | 1897393 | 1753 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1753 | 38.9161 | -122.8018 | 4 SPANS LD SIDE 9869 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086066 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Line | 1307266 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | COVELO-1101 | 43061101 | FUSE | 6641 | 20171018 | 146 | 1903006 | 2103 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8702 | 39.7388 | -123.1632 | 1 POLE SS OF 6699 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0088159 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Line | 1308954 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4597 | 20171026 | 1629 | 1910381 | 953 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 8577 | 38.729 | -123.3496 | 12 LD SIDE OF FUSES | Clear-Above 90 | Conductor, Overhead | On Ground | 17-0090691 | OH | Sus | 43201729 | No | 2017 | OCT | Yes | Line to Line | 1310744 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8961 | 20171026 | 1149 | 1910069 | 216 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 216 | 39.5609 | -123.7256 | 3/LD/OF 8961 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0090554 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1310681 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3287 | 20171107 | 1155 | 1917565 | 162 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 61 | 9882 | 39.3135 | -123.747 | 2/S/SS/TO 7933 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0093245 | OH | Sus | 43208291 | No | 2017 | NOV | Yes | Line to Ground | 1312687 | CSO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1907 | 20171108 | 1320 | 1918467 | 171 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 2056 | 40.4872 | -124.2599 | at MTR 1008829462 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0093598 | OH | Sus | 0 | yes | 2017 | NOV | Yes | Line to Ground | 1312888 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1104 | 42661104 | FUSE | 1355 | 20171108 | 1148 | 1918300 | 316 | Distribution Circuit | Vegetation | Tree - fell into line | 145 | 17056 | 39.3636 | -123.3228 | MTR#1006277435 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0093549 | OH | Sus | 0 | yes | 2017 | NOV | Yes | Line to Ground | 1312877 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | FUSE | 3947 | 20171110 | 1306 | 1920134 | 149 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 298 | 40.3287 | -123.9212 | 3/s/ld/side of 3947 | Partly Cloudy-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0094312 | OH | Sus | 43212819 | No | 2017 | NOV | Yes | Line to Ground | 1313341 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 8207 | 20171110 | 1824 | 1920348 | 492 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3936 | 39.9939 | -123.9257 | 33/S/LD/SIDE OF 8207 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0094359 | OH | Sus | 0 | No | 2017 | NOV | Yes | Line to Ground | 1313373 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HIGHLANDS-1103 | 43361103 | FUSE | 195063 | 20171112 | 1419 | 1920916 | 558 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7254 | 38.8201 | -122.5075 | 14/P/LOADSIDE OF 195063- 22644 JERUSALEM GRD RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0094526 | OH | Sus | 43213088 | No | 2017 | NOV | Yes | Line to Line | 1313544 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | FUSE | 4143 | 20171112 | 1631 | 1920939 | 744 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 3 | 2232 | 40.4452 | -123.4952 | HWY 35- 400 FT E OF MAD RIVER RD TURNOFF ON LEFT | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0094543 | OH | Sus | 31365088 | No | 2017 | NOV | Yes | Line to Line | 1313559 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER | 7514 | 20171114 | 1951 | 1922563 | 1161 | Distribution Circuit | Vegetation | Tree - fell into line | 1310 | 1491520 | 40.9334 | -123.6249 | ON MAINLINE 1 SPAN N/OF FUCO 2921- HWY 299 GYPON LN / ENCHANTED LN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0095017 | OH | Sus | 43214548 | No | 2017 | NOV | Yes | Line to Line | 1314026 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HIGHLANDS-1103 | 43361103 | JUMPER | WIRE DOWN FEEEDING MTR# 1006501934 | 20171115 | 2007 | 1923300 | 434 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1302 | 38.8367 | -122.5431 | SS TO MTR# 1006501934- 15007 SPRUCE GROVE RD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0095381 | OH | Sus | 0 | yes | 2017 | NOV | Yes | Line to Ground | 1314270 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 93234 | 20171120 | 1128 | 1926521 | 227 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 21111 | 40.2355 | -123.8346 | 6 SPANS LD SIDE OF 1581 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | On Ground | 17-0096498 | OH | Sus | 43217862 | No | 2017 | NOV | Yes | Line to Ground | 1315141 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER | 2936 | 20171120 | 1314 | 1926667 | 1513 | Distribution Circuit | Vegetation | Tree - fell into line | 290 | 437525 | 40.8665 | -123.5144 | CROSSWY- DARRELL: 1 POLE LOADSIDE OF 2936- 10 LD SIDE OF 2936 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0096539 | OH | Sus | 43217949 | No | 2017 | NOV | Yes | Line to Ground | 1315158 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | TRIP-SAVER | 4923 | 20171124 | 1519 | 1928726 | 1209 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 14164 | 38.9464 | -123.6449 | 1 SPAN SS MTR 1006717251 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0097403 | OH | Sus | 0 | No | 2017 | NOV | Yes | Line to Ground | 1315657 | CSO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 8207 | 20171126 | 1140 | 1929595 | 1370 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 7630 | 39.9939 | -123.9257 | 33 POLES LD SIDE OF 8207 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0097663 | OH | Sus | 43222343 | No | 2017 | NOV | Yes | Line to Line | 1315885 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 1931 | 20171127 | 903 | 1930009 | 487 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4383 | 39.7372 | -123.811 | AT MILE MARKER 87.95 HWY 1 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0097751 | OH | Sus | 43222358 | yes | 2017 | NOV | Yes | Line to Line | 1315975 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 9847 | 20171127 | 740 | 1929898 | 306 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 612 | 38.6955 | -122.5984 | at 9847 1ST SPAN LD SIDE TO SOUTH | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0097742 | OH | Sus | 43222357 | yes | 2017 | NOV | Yes | Line to Ground | 1315965 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 2625 | 20171127 | 614 | 1929813 | 456 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3648 | 39.0997 | -123.5713 | 24513 PHILO GREENWOOD RD | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 17-0097733 | OH | Sus | 43222359 | yes | 2017 | NOV | Yes | Line to Ground | 1315956 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | OTHER | WIRE DOWN 4/S/S/SIDE 3174 | 20171129 | 1520 | 1932042 | 737 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 2043 | 447531 | 41.2225 | -123.6538 | 4 SPANS SS LR 3174 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0098434 | OH | Sus | 43224393 | No | 2017 | NOV | Yes | Line to Ground | 1316574 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 8517 | 20171203 | 723 | 1934113 | 464 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 464 | 38.6528 | -123.3991 | 1ST SPAN LD SIDE OF 8517 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0099342 | OH | Sus | 43226561 | No | 2017 | DEC | Yes | Line to Ground | 1317205 | CSO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2831 | 20171207 | 1108 | 1938229 | 742 | Distribution Circuit | Vegetation | Tree - fell into line | 210 | 25072 | 39.3834 | -123.3013 | 2 LD SIDE OF FUCO 7669 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0100549 | OH | Sus | 31368693 | No | 2017 | DEC | Yes | Line to Ground | 1318228 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | OTHER | WIRE DOWN | 20171221 | 1550 | 1949794 | 642 | Distribution Circuit | Equipment Failure/Involved | Overhead | 352 | 50165 | 38.8694 | -122.6888 | MTR 23R742 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102966 | OH | Sus | 43239753 | No | 2017 | DEC | Yes | Line to Ground | 1321494 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MENDOCINO-1101 | 42951101 | FUSE | 3443 | 20171221 | 512 | 1949213 | 382 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 136 | 9246 | 39.267 | -123.2043 | ON HARD TAP FEEDING MTR#1010026031 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0102905 | OH | Sus | 43239441 | No | 2017 | DEC | Yes | Line to Ground | 1321314 | CSO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 8953 | 20171230 | 1443 | 1953446 | 271 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 3 | 813 | 39.2428 | -123.7752 | 1ST SPAN N/OF 8953 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0103679 | OH | Sus | 31371619 | No | 2017 | DEC | Yes | Line to Line | 1322488 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 5233 | 20180104 | 2156 | 2327 | 769 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 5293 | 39.2282 | -123.7663 | OJ'S/11/S/LD SIDE OF 5233 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0003741 | OH | Sus | 43244781 | yes | 2018 | JAN | Yes | Line to Ground | 1323250 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MENDOCINO-1101 | 42951101 | FUSE | 340549 | 20180105 | 13 | 2359 | 1002 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 8 | 8016 | 39.3749 | -123.2517 | GALLETTI- TIM: TREE THROUGH LINE- BROKEN POLE AND WIRE DOWN at 5380 WILD IRIS | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0003746 | OH | Sus | 31372274 | No | 2018 | JAN | Yes | Line to Line | 1323256 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER | 4628 | 20180109 | 1234 | 5136 | 312 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 20184 | 39.24 | -123.7713 | Garcia- D/1260: 2 spans ld s/o lr 4628 n hwy 1 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0004744 | OH | Sus | 43246889 | yes | 2018 | JAN | Yes | Line to Line | 1323895 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | JUMPER | WIRE DOWN 10900 GURLEY LN | 20180109 | 1505 | 5286 | 175 | Distribution Circuit | Equipment Failure/Involved | Overhead | 84 | 2001 | 39.3156 | -123.7852 | Felicich- David: at 10900 gurley ln | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0004814 | OH | Sus | 43246896 | yes | 2018 | JAN | Yes | Line to Ground | 1323920 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 9201 | 20180110 | 1406 | 6084 | 203 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 2233 | 39.3173 | -123.7894 | 44701 LARKIN RD- MENDICINO | Clear-32-90 F | Conductor, Overhead | On Ground | 18-0005096 | OH | Sus | 43251182 | No | 2018 | JAN | Yes | Line to Line | 1324147 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 37506 | 20180110 | 931 | 5826 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 11134 | 39.4831 | -123.3611 | WIRE DOWN ACROSS HWY 101 at MM 56.80 NORTH OF SW 2527 | Clear-32-90 F | Conductor, Overhead | On Ground | 18-0004999 | OH | Sus | 43250926 | No | 2018 | JAN | Yes | Line to Ground | 1324078 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4599 | 20180111 | 821 | 6428 | 267 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1335 | 38.7481 | -123.3506 | 14 LD SIDE OF 4599 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0005216 | OH | Sus | 43251651 | No | 2018 | JAN | Yes | Three Phase Fault | 1324223 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | SWITCH | 4089 | 20180114 | 1413 | 8049 | 492 | Distribution Circuit | Environmental/External | Lightning | 51 | 12351 | 40.4813 | -123.5763 | 1 SPAN SS OF FUCO 99545 ON MAINLINE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0006061 | OH | Sus | 0 | No | 2018 | JAN | Yes | Line to Ground | 1324808 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 7531 | 20180122 | 1928 | 12217 | 935 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1870 | 38.7232 | -123.4036 | 8 SPANS LD SIDE OF FUCO 7531 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0007983 | OH | Sus | 43259308 | No | 2018 | JAN | Yes | Line to Ground | 1325944 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1103 | 43351103 | FUSE | 4755 | 20180122 | 33 | 11730 | 317 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 26311 | 39.1306 | -122.8547 | MTR#1A0908 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 18-0007719 | OH | Sus | 43258395 | No | 2018 | JAN | Yes | Line to Ground | 1325818 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 37506 | 20180122 | 720 | 11773 | 558 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 24567 | 39.4831 | -123.3611 | 11 SPANS SS OF 47881 AND 6 SPANS SS OF 47881 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0007751 | OH | Sus | 43258908 | No | 2018 | JAN | Yes | Line to Ground | 1325837 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1907 | 20180124 | 732 | 12968 | 390 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 5867 | 40.4872 | -124.2599 | 4 E/OF 7455 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0008408 | OH | Sus | 0 | No | 2018 | JAN | Yes | Line to Ground | 1326215 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | RECLOSER | 2502 | 20180124 | 1127 | 13189 | 688 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 20420 | 39.5665 | -123.3983 | 2 SPANS SS OF 8923 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0008511 | OH | Sus | 0 | No | 2018 | JAN | Yes | Line to Ground | 1326278 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE | 775 | 20180124 | 1652 | 13405 | 1258 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5032 | 39.173 | -122.9412 | at 775 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0008697 | OH | Sus | 0 | No | 2018 | JAN | Yes | Line to Ground | 1326321 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 1999 | 20180124 | 1427 | 13303 | 424 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 10512 | 39.4312 | -123.3728 | at mtr#1006182609 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0008638 | OH | Sus | 0 | No | 2018 | JAN | Yes | Line to Ground | 1326302 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 1837 | 20180125 | 1124 | 13986 | 1738 | Distribution Circuit | 3rd Party | Vehicle | 6 | 10428 | 40.2029 | -123.4817 | POLE 19 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 18-0009025 | OH | Sus | 0 | No | 2018 | JAN | Yes | Line to Ground | 1326517 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | OTHER | WIRE DOWN AT MTR# 1008280331 | 20180125 | 730 | 13614 | 1464 | Distribution Circuit | Environmental/External | Ice or snow | 232 | 90599 | 40.4652 | -123.5252 | MTR#1008280331 / 1 SPAN SS OF MTR 1010237550 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0008791 | OH | Sus | 43261380 | No | 2018 | JAN | Yes | Line to Ground | 1326418 | CSO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 6789 | 20180126 | 1828 | 14853 | 347 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 4858 | 40.218 | -123.8718 | 17/P/LD/SIDE 6789- 3525 THOMAS RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0009421 | OH | Sus | 31376121 | No | 2018 | JAN | Yes | Line to Line | 1326754 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1514 | 20180205 | 1718 | 19794 | 565 | Distribution Circuit | Vegetation | Tree - fell into line | 569 | 32402 | 40.0478 | -123.7896 | Marshall- John/K1931-T2070: HWY 101 1 MILE S/O BENBOW INN- 20 POLES LS OF 7201 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 18-0011676 | OH | Sus | 43267573 | No | 2018 | FEB | Yes | Line to Line | 1328349 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1709 | 20180212 | 849 | 23046 | 310 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1240 | 39.8782 | -123.7262 | 5/S/LD SIDE OF 1709 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0013387 | OH | Sus | 0 | No | 2018 | FEB | Yes | Line to Line | 1329591 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | RECLOSER | 1308 | 20180215 | 120 | 24976 | 845 | Distribution Circuit | Equipment Failure/Involved | Overhead | 293 | 142052 | 39.1863 | -123.5804 | 1 SPAN FROM 9131 TWD 2699 & at MTR#1008805824 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0014437 | OH | Sus | 43278224 | No | 2018 | FEB | Yes | Line to Ground | 1330164 | CSO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | BRIDGEVILLE-1102 | 192461102 | FUSE | 3785 | 20180218 | 2314 | 26939 | 1317 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 46886 | 40.3855 | -123.7427 | 10 LD SIDE OF 3717 ON MAIN LINE- MTR#1010110379 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0015327 | OH | Sus | 0 | yes | 2018 | FEB | Yes | Line to Line | 1330768 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 496769 | 20180218 | 1348 | 26680 | 136 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 4080 | 39.4808 | -123.7806 | 6 SPANS E/OF 496769 | Clear-32-90 F | Conductor, Underground | Broken, wire on ground | 18-0015230 | UG | Sus | 43280556 | yes | 2018 | FEB | Yes | Line to Ground | 1330667 | CU | UG | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | RECLOSER | 29362 | 20180218 | 2310 | 26930 | 914 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 85148 | 40.8941 | -123.7726 | CAHOON- DEREK: 2 SPANS SOURCE SIDE OF 3027 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0015319 | OH | Sus | 0 | yes | 2018 | FEB | Yes | Line to Ground | 1330758 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1907 | 20180219 | 713 | 27056 | 1803 | Distribution Circuit | Environmental/External | Ice or snow | 16 | 20800 | 40.4872 | -124.2599 | 3 & 7 SPANS FROM EOL- 10 POLES SOURCE SIDE OF 7455 | Partly Cloudy-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0015373 | OH | Sus | 0 | yes | 2018 | FEB | Yes | Line to Ground | 1330816 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 1947 | 20180219 | 207 | 26971 | 671 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 18117 | 40.2218 | -123.7973 | 8 POLES LD SIDE OF 1947 | Partly Cloudy-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0015328 | OH | Sus | 0 | yes | 2018 | FEB | Yes | Line to Ground | 1330769 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 1857 | 20180219 | 1359 | 27351 | 166 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 830 | 40.2208 | -123.819 | LAST SPAN LD SIDE OF 1857 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0015430 | OH | Sus | 0 | yes | 2018 | FEB | Yes | Line to Ground | 1330861 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | SECTIONALIZER | 1780 | 20180219 | 1340 | 27952 | 1659 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 6487 | 40.062 | -123.8498 | 30 spans ld side of 1780 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0015702 | OH | Sus | 0 | yes | 2018 | FEB | Yes | Line to Ground | 1331036 | CSO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 4589 | 20180219 | 1040 | 27221 | 458 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 883 | 38.6586 | -123.4034 | 3 SPANS LD SIDE OF 4589 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0015397 | OH | Sus | 0 | yes | 2018 | FEB | Yes | Line to Ground | 1330843 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1108 | 43311108 | RECLOSER | 950 | 20180221 | 2001 | 28953 | 662 | Distribution Circuit | 3rd Party | Vehicle | 1027 | 72049 | 38.954 | -122.7265 | 2 POLES FROM 4179 TWD 3355 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 18-0016115 | OH | Sus | 0 | No | 2018 | FEB | Yes | Line to Line | 1331292 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 2500 | 20180225 | 1350 | 31241 | 772 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 443 | 78107 | 40.1079 | -123.9289 | 1 SPAN SOURCE SIDE OF FUSES 2585 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0017065 | OH | Sus | 31381207 | No | 2018 | FEB | Yes | Line to Line | 1332003 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | FUSE | 5869 | 20180301 | 1707 | 35386 | 1320 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 54974 | 40.2616 | -123.3183 | MTR#1006582839- NEAR 20054 MAD RIVER RD | Overcast-Snow-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0018878 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333235 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 2094 | 20180301 | 2158 | 35744 | 1086 | Distribution Circuit | Vegetation | Tree - fell into line | 285 | 43683 | 40.436 | -123.4882 | 2 SPANS LD SIDE OF 4107 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0018915 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Three Phase Fault | 1333272 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | OTHER | 1 SPAN LD SIDE OF FUCO 2279 | 20180301 | 2234 | 35907 | 911 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2733 | 40.4252 | -123.4786 | 1 SPAN LD SIDE OF FUCO 2279 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0018953 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333308 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 9011 | 20180301 | 2149 | 35825 | 950 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 5700 | 39.079 | -123.4803 | 1 POLE LD SIDE OF MTR#1008994928 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0018922 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333276 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1817 | 20180302 | 1633 | 36555 | 4367 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 14664 | 39.8643 | -123.7245 | 6 SPANS LD SIDE OF 1817 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019249 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333448 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 56048 | 20180302 | 1605 | 36539 | 4592 | Distribution Circuit | Environmental/External | Ice or snow | 54 | 204678 | 40.1477 | -124.0196 | NUMEROUS LOCATIONS BET 56048 AND 8033 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0019206 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333408 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2531 | 20180302 | 1556 | 38153 | 4559 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 9118 | 40.151 | -124.0289 | LD SIDE OF 2531 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019612 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Open Circuit | 1333804 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 8185 | 20180302 | 1605 | 38154 | 4435 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 17740 | 40.1776 | -124.0889 | LD SIDE OF 8185 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019613 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Open Circuit | 1333805 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1997 | 20180302 | 1346 | 38475 | 6021 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 42147 | 40.2852 | -124.0595 | NUMEROUS LOCATIONS OF TBL FROM 1997 TO EOL | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0019905 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1334090 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | JUMPER | OJ'S 1 LD OF MTR#1008024854 | 20180302 | 1154 | 36319 | 1620 | Distribution Circuit | Environmental/External | Ice or snow | 12 | 19440 | 40.2928 | -123.3575 | at MTR#1008024853 | Overcast-Drizzle-32-90 F | Insulator | Broken, wire on object | 18-0019117 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Force Out | 1333388 | INS | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER | 4230 | 20180302 | 900 | 36122 | 23 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 575 | 40.4173 | -124.0895 | BET SB 908763 AND SW 2001 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019041 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333357 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 1679 | 20180303 | 601 | 37350 | 697 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 32062 | 40.2781 | -123.7929 | 4 SPANS SS OF 8055 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019458 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333651 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 2026 | 20180303 | 959 | 37328 | 4988 | Distribution Circuit | Environmental/External | Ice or snow | 25 | 124700 | 39.8515 | -123.7181 | 15 SPANS LD SIDE OF LR 2026 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019463 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333655 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | RECLOSER | 682 | 20180303 | 549 | 37116 | 606 | Distribution Circuit | Vegetation | Tree - branch fell on line | 110 | 23823 | 39.6298 | -123.5825 | Behind lumber mill 14550 Branscomb RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0019339 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333539 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 2499 | 20180303 | 653 | 37341 | 2020 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 25350 | 39.668 | -123.5141 | 9 SPANS LD SIDE OF 2499 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019379 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333588 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 3887 | 20180303 | 1221 | 37505 | 131 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 8908 | 39.6587 | -123.6345 | 20 SPANS LD SIDE OF 3887 & TREE ON THE LINE 25 SPANS LD SIDE OF 3887 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019421 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333619 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2531 | 20180308 | 940 | 40402 | 359 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 718 | 40.151 | -124.0289 | SPAN at EOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0020953 | OH | Sus | 0 | No | 2018 | MAR | Yes | Force Out | 1334779 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER | 1690 | 20180312 | 1344 | 42526 | 890 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 50730 | 40.1677 | -123.6109 | MTR # 1008024451 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0021917 | OH | Sus | 0 | No | 2018 | MAR | Yes | Multi-Fault | 1335419 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 8183 | 20180314 | 1204 | 44062 | 341 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 341 | 40.1539 | -124.0694 | 2/S/LD SIDE OF 8183 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0022753 | OH | Sus | 43300739 | yes | 2018 | MAR | Yes | Line to Ground | 1335866 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | SWITCH | 1595 | 20180315 | 1712 | 45007 | 1164 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 46560 | 40.3067 | -123.9019 | at 8315 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 18-0023153 | OH | Sus | 0 | No | 2018 | MAR | Yes | Force Out | 1336075 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 6423 | 20180315 | 1201 | 44715 | 573 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 16044 | 39.4878 | -123.4249 | 8/S/LD/SIDE OF 6423 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023046 | OH | Sus | 0 | No | 2018 | MAR | Yes | Line to Ground | 1336049 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER | 35592 | 20180322 | 615 | 50209 | 471 | Distribution Circuit | Vegetation | Tree - fell into line | 371 | 65541 | 39.3941 | -123.7793 | 16656 MITCHELL CREEK | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025293 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1337495 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3939 | 20180323 | 126 | 51442 | 690 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6900 | 39.4081 | -123.7277 | 27954 HWY 20 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025859 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1337794 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MIDDLETOWN-1101 | 43141101 | FUSE | 3601 | 20180326 | 1700 | 53936 | 651 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3255 | 38.7304 | -122.6215 | 3 SPANS LOADSIDE OF 3601 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0026824 | OH | Sus | 31385977 | No | 2018 | MAR | Yes | Line to Line | 1338637 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | FUSE | 4079 | 20180402 | 1743 | 58252 | 342 | Distribution Circuit | Vegetation | Tree - grew into line | 2 | 684 | 40.493 | -123.5971 | POLE #8 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0028640 | OH | Sus | 43313495 | No | 2018 | APR | Yes | Line to Ground | 1340008 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 6081 | 20180406 | 911 | 60706 | 378 | Distribution Circuit | Vegetation | Tree - fell into line | 165 | 26574 | 39.3922 | -123.7995 | 2 & 3 POLES LD SIDE OF 738867 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0029847 | OH | Sus | 31387613 | yes | 2018 | APR | Yes | Three Phase Fault | 1340889 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER | 445166 | 20180406 | 1233 | 60900 | 759 | Distribution Circuit | Vegetation | Tree - fell into line | 315 | 119002 | 38.6937 | -123.4237 | Thorpe- Tim/2094: 1367 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0029989 | OH | Sus | 0 | yes | 2018 | APR | Yes | Line to Ground | 1340942 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1106 | 43351106 | FUSE | 4123 | 20180406 | 2136 | 61387 | 1237 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 35441 | 39 | -122.7528 | at 2700 BUCKINGHAM DR ON GREENWAY DR | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0030161 | OH | Sus | 0 | yes | 2018 | APR | Yes | Multi-Fault | 1341032 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | RECLOSER | 474 | 20180406 | 1211 | 60874 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 218 | 123824 | 38.9128 | -123.6795 | 17 SPANS LD SIDE OF 474 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0029961 | OH | Sus | 0 | yes | 2018 | APR | Yes | Line to Ground | 1340932 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1104 | 42661104 | SWITCH | 3863 | 20180406 | 1700 | 61167 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 1034 | 88135 | 39.3975 | -123.3464 | ESPINOLA-1995: at co 95653 on baechtol rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0030102 | OH | Sus | 0 | yes | 2018 | APR | Yes | Multi-Fault | 1340983 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 561 | 20180407 | 41 | 61440 | 865 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 91690 | 38.7886 | -123.5253 | 4 SPANS SS OF SBCO 4467 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0030174 | OH | Sus | 0 | yes | 2018 | APR | Yes | Three Phase Fault | 1341044 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | JUMPER | OJ'S SS OF MTR 1010302992 | 20180408 | 2224 | 62710 | 736 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1472 | 39.6574 | -123.7685 | SS OF MTR 1010302992 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0030430 | OH | Sus | 43317076 | No | 2018 | APR | Yes | Line to Ground | 1341313 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1103 | 43141103 | FUSE | 4105 | 20180409 | 1207 | 63167 | 356 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 7 | 2492 | 38.7271 | -122.551 | 19491 BUTTS CANYON RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0030619 | OH | Sus | 31387931 | No | 2018 | APR | Yes | Line to Line | 1341479 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5969 | 20180411 | 1800 | 64936 | 1090 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2180 | 39.2861 | -123.6655 | 4 SPANS LOADSIDE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0031467 | OH | Sus | 0 | yes | 2018 | APR | Yes | Line to Ground | 1342101 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 3273 | 20180411 | 1733 | 64865 | 1304 | Distribution Circuit | Environmental/External | Flood/Erosion | 7 | 9128 | 39.1934 | -123.7224 | 30951 NAVARRO RIVER RD | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0031442 | OH | Sus | 0 | yes | 2018 | APR | Yes | Line to Ground | 1342073 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER | WIRE DOWN 3 SP E/O 83959 | 20180411 | 1525 | 64784 | 500 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 17412 | 40.1156 | -123.8243 | 3 SPANS LOADSIDE 83959 | Overcast-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0031403 | OH | Sus | 0 | yes | 2018 | APR | Yes | Line to Ground | 1342049 | CSO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1801 | 20180411 | 1515 | 65062 | 1441 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 44671 | 40.058 | -123.9805 | 1/P/SS OF MTR#1008026875 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0031455 | OH | Sus | 0 | yes | 2018 | APR | Yes | Line to Ground | 1342086 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | JUMPER | WIRE DOWN AT 3329 PRIMEROSE DR | 20180413 | 1327 | 66434 | 125 | Distribution Circuit | Equipment Failure/Involved | Overhead | 947 | 77795 | 39.4256 | -123.3945 | 3329 PRIMEROSE DR - WILLITS | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0032126 | OH | Sus | 43324737 | No | 2018 | APR | Yes | Line to Ground | 1342587 | CSO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 4153 | 20180416 | 2049 | 68397 | 891 | Distribution Circuit | 3rd Party | Vehicle | 49 | 43659 | 39.4425 | -123.4131 | 12 SPANS LD SIDE OF FUCO 4153 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0032875 | OH | Sus | 0 | yes | 2018 | APR | Yes | Three Phase Fault | 1343193 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | FUSE | 3965 | 20180417 | 1536 | 69036 | 449 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 449 | 40.3417 | -123.8803 | 7 SPANS LD SIDE OF 3965- 3272 DYERVILLE LP RD REDCREST | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0033186 | OH | Sus | 43326978 | No | 2018 | APR | Yes | Line to Ground | 1343373 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1108 | 43311108 | RECLOSER | 38632 | 20180427 | 420 | 74749 | 357 | Distribution Circuit | Vegetation | Tree - branch fell on line | 259 | 33172 | 38.9913 | -122.7481 | MTR# 1007973576 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0036046 | OH | Sus | 43331864 | No | 2018 | APR | Yes | Line to Ground | 1345266 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | JUMPER | WIRE DOWN/FAILED BUMP | 20180501 | 1811 | 77766 | 711 | Distribution Circuit | Equipment Failure/Involved | Overhead | 821 | 262741 | 40.1231 | -123.8373 | Allen- Derrick/K1616-T1243: 8 spans load side LR 1510 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0037412 | OH | Sus | 43334915 | No | 2018 | MAY | Yes | Line to Ground | 1346185 | CSO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 8437 | 20180508 | 1809 | 81956 | 1054 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 33728 | 41.2105 | -123.7574 | 2 MILES NORTH OF 8519 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0039401 | OH | Sus | 0 | No | 2018 | MAY | Yes | Line to Line | 1347604 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 5097 | 20180510 | 1148 | 83101 | 369 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 2190 | 38.9019 | -123.6034 | 2 SPANS WEST OF EOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0039878 | OH | Sus | 31391154 | No | 2018 | MAY | Yes | Line to Line | 1348068 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER | 37410 | 20180511 | 1551 | 84219 | 494 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 5926 | 40.3263 | -123.9227 | 1 SS OF 3931 FU | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0040389 | OH | Sus | 31391817 | yes | 2018 | MAY | Yes | Line to Ground | 1348399 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | OTHER | WIRE DOWN 7 LD SIDE OF 1767 | 20180511 | 834 | 83684 | 782 | Distribution Circuit | Equipment Failure/Involved | Overhead | 822 | 267466 | 40.0928 | -123.7901 | 7 SPANS LOADSIDE OF 1767 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0040155 | OH | Sus | 43345998 | yes | 2018 | MAY | Yes | Line to Ground | 1348234 | CSO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | JUMPER | OJ'S 1 SS/OF MTR# 1008881429 | 20180511 | 1639 | 84265 | 570 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 1410 | 39.6698 | -123.5192 | GALLETTI- TIM: TREE THROUGH LINE at 2000 BRANSCOMB RD. 5 POLES LS OF FCO 2499 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0040416 | OH | Sus | 31391812 | yes | 2018 | MAY | Yes | Open Circuit | 1348425 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 37202 | 20180525 | 2028 | 94291 | 549 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 32174 | 41.1894 | -123.7104 | POLE# 37 ON HWY 169 1/2 MILE/W/OF MTR# 1007960294 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0044588 | OH | Sus | 0 | yes | 2018 | MAY | Yes | Line to Line | 1351664 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 5415 | 20180527 | 1701 | 94857 | 433 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 9526 | 39.3713 | -123.3607 | 3601 NUIRMILL RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0044758 | OH | Sus | 0 | No | 2018 | MAY | Yes | Multi-Fault | 1351832 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1899 | 20180529 | 1637 | 96296 | 561 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 6171 | 40.5106 | -124.1608 | 4 SPANS SS OF MTR 1009744065 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0045422 | OH | Sus | 43357194 | yes | 2018 | MAY | Yes | Multi-Fault | 1352217 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1757 | 20180609 | 1501 | 105260 | 324 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 5184 | 39.4416 | -123.7285 | MTR# P54944 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0049282 | OH | Sus | 43366684 | yes | 2018 | JUN | Yes | Line to Ground | 1355323 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 7701 | 20180616 | 1611 | 110842 | 179 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 1253 | 39.2627 | -123.7185 | 4 SPANS LD SIDE OF 7701 | Clear-32-90F | Conductor, Overhead | Broken, wire on object | 18-0051640 | OH | Sus | 0 | yes | 2018 | JUN | Yes | Line to Line | 1357082 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | TRIP-SAVER | 3113 | 20180619 | 754 | 112533 | 516 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 102 | 15379 | 39.5073 | -123.7645 | 26500 SPRUCE LN | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0052196 | OH | Sus | 43376615 | No | 2018 | JUN | Yes | Line to Line | 1357678 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | OTHER | WIRE DOWN 1 S/LOAD SIDE 3739 | 20180627 | 1801 | s1360008 | 791 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 21357 | 40.2205 | -123.7975 | 1 SPAN LOADSIDE OF 3739 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0055205 | OH | Sus | 0 | No | 2018 | JUN | Yes | Line to Ground | 1360008 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | OTHER | 1770 | 20180627 | 2119 | 119854 | 422 | Distribution Circuit | Vegetation | Tree - branch fell on line | 345 | 75544 | 39.9153 | -123.7634 | WIRE DOWN BET 4TH AND 5TH SPANS NORTH OF 35706 | Clear-32-90 F | Conductor, Overhead | On Ground | 18-0055211 | OH | Sus | 0 | No | 2018 | JUN | Yes | Line to Ground | 1360016 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 6323 | 20180628 | 1758 | 120560 | 727 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 7270 | 41.059 | -123.6928 | 2 SPANS LOADSIDE- PINE CREEK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0055575 | OH | Sus | 0 | No | 2018 | JUN | Yes | Line to Line | 1360329 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER | WIRE DOWN HOT 1 SP S/S OF MTR#1008869018 | 20180701 | 23 | 122109 | 620 | Distribution Circuit | Vegetation | Tree - fell into line | 311 | 22872 | 40.2685 | -124.2395 | 1ST SPAN SS OF TRANSF MTR# 1008869018 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0056043 | OH | Sus | 0 | No | 2018 | JUL | Yes | Force Out | 1360856 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1903 | 20180702 | 1522 | 123195 | 503 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 3018 | 40.5282 | -124.1667 | BET 4-5 POLES LD SIDE OF 1903 1 SPAN DOWN AND BET 5-6 POLES LD SIDE OF 1903 3 SPANS DOWN | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0056400 | OH | Sus | 0 | No | 2018 | JUL | Yes | Three Phase Fault | 1361148 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | JUMPER | WIRE DOWN 13 SPANS LD SIDE OF 5097 | 20180703 | 1035 | 123821 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 2877 | 38.8954 | -123.5962 | 13 SPANS LD SIDE OF 5097 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0056738 | OH | Sus | 0 | No | 2018 | JUL | Yes | Line to Ground | 1361352 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | RECLOSER | 37586 | 20180704 | 1526 | 124473 | 916 | Distribution Circuit | 3rd Party | Vehicle | 127 | 32269 | 39.6174 | -123.4629 | at SW 2543- ON HWY 162- .3 MI FROM 101 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0056986 | OH | Sus | 0 | No | 2018 | JUL | Yes | Line to Line | 1361514 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2505 | 20180707 | 2108 | 126342 | 949 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 33215 | 40.3068 | -124.2964 | AT C/OUTS 8077 MAINLINE WIRE DOWN | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0057726 | OH | Sus | 0 | No | 2018 | JUL | Yes | Line to Ground | 1362019 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1108 | 43311108 | RECLOSER | 950 | 20180715 | 1936 | 132357 | 65 | Distribution Circuit | 3rd Party | Vehicle | 1028 | 59582 | 38.954 | -122.7265 | 4 W/OF 3355 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0060007 | OH | Sus | 0 | No | 2018 | JUL | Yes | Line to Ground | 1363927 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1771 | 20180716 | 1552 | 133104 | 661 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5288 | 40.0718 | -123.8298 | 1 SPAN LD SIDE OF FUCO 1771 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0060352 | OH | Sus | 31400078 | No | 2018 | JUL | Yes | Line to Ground | 1364226 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER | 1602 | 20180719 | 529 | 135273 | 923 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 73380 | 40.1834 | -123.5765 | CGC 115700931658 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0061308 | OH | Sus | 0 | yes | 2018 | JUL | Yes | Line to Ground | 1364900 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | RECLOSER | 4698 | 20180723 | 1511 | 138405 | 354 | Distribution Circuit | 3rd Party | Vehicle | 720 | 44840 | 39.4911 | -123.7844 | 4999 RISER POLE | Clear-32-90F | Pole-Wood | Broken, wire on object | 18-0062842 | OH | Sus | 0 | No | 2018 | JUL | Yes | Multi-Fault | 1366044 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 2939 | 20180724 | 1809 | 139420 | 506 | Distribution Circuit | Vegetation | Tree - branch fell on line | 74 | 37444 | 40.8935 | -123.5871 | 2 SPANS LD SIDE OF 2939 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0063287 | OH | Sus | 43417447 | yes | 2018 | JUL | Yes | Three Phase Fault | 1366370 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 9209 | 20180727 | 2017 | 142144 | 977 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 10747 | 39.492 | -123.3624 | GALLETTI- TIM: TREE BRANCH INTO LINE 2 POLES LS OF FCO 9209. 29200 N HWY 101 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0064499 | OH | Sus | 0 | No | 2018 | JUL | Yes | Line to Ground | 1367258 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARTLEY-1101 | 43211101 | FUSE | 58175 | 20180729 | 1638 | 148372 | 8612 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 5 | 55 | 39.081 | -122.9632 | BURNED POLE 10 SPANS LD SIDE OF 58175 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0066529 | OH | Sus | 0 | No | 2018 | JUL | Yes | None | 1368895 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 9059 | 20180729 | 1139 | 143567 | 481 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4329 | 39.104 | -123.4974 | 22690 GREENWOOD RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0064779 | OH | Sus | 0 | No | 2018 | JUL | Yes | Line to Ground | 1367520 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE | 3635 | 20180729 | 1611 | 147384 | 8909 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 6 | 0 | 39.2077 | -122.926 | RANCH FIRE | Clear-32-90F | Conductor, Overhead | On Ground | 18-0066094 | OH | Sus | 0 | No | 2018 | JUL | Yes | None | 1368538 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE | 1287 | 20180729 | 1611 | 148778 | 11748 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 5 | 0 | 39.2103 | -122.9301 | BEYOND 1287 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0066703 | OH | Sus | 0 | No | 2018 | JUL | Yes | Multi-Fault | 1369019 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | RECLOSER | 1904 | 20180730 | 2313 | 145586 | 1042 | Distribution Circuit | Vegetation | Tree - fell into line | 336 | 129718 | 39.3218 | -123.095 | 6281 HORSESHOE CIRCLE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0065206 | OH | Sus | 0 | No | 2018 | JUL | Yes | Three Phase Fault | 1367899 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARTLEY-1102 | 43211102 | FUSE | 4207 | 20180802 | 2113 | 147920 | 875 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4375 | 39.07 | -122.9205 | 528 CRYSTAL LAKE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0066311 | OH | Sus | 0 | No | 2018 | AUG | Yes | Line to Line | 1368702 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1102 | 43311102 | OCB | 1102/2 | 20180802 | 1554 | 147758 | 895 | Distribution Circuit | Vegetation | Tree - fell into line | 2792 | 384442 | 38.9326 | -122.741 | 6 SPANS LD SIDE OF SW 491 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0066244 | OH | Sus | 0 | No | 2018 | AUG | Yes | Line to Ground | 1368659 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | OTHER | 4571 | 20180808 | 1003 | 151343 | 209 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 131 | 27379 | 40.7928 | -124.0232 | 2 SPANS LD SIDE OF 4571 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0067921 | OH | Sus | 0 | No | 2018 | AUG | Yes | Force Out | 1369870 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2721 | 20180821 | 238 | 159102 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 32179 | 39.3879 | -123.3241 | MTR 1009672517 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0071924 | OH | Sus | 31403772 | No | 2018 | AUG | Yes | Line to Line | 1372217 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | OTHER | WIRE DOWN | 20180822 | 820 | 160167 | 304 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 796 | 39.5089 | -123.7485 | 1 SS OF MTR# 1010374938 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0072380 | OH | Sus | 43445944 | No | 2018 | AUG | Yes | Line to Ground | 1372665 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HIGHLANDS-1102 | 43361102 | RECLOSER | 75140 | 20180825 | 1450 | 162272 | 725 | Distribution Circuit | 3rd Party | Vehicle | 2591 | 363269 | 38.9543 | -122.6103 | 3 SPANS W/OF SBCO 8489 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0073436 | OH | Sus | 0 | No | 2018 | AUG | Yes | Line to Line | 1373473 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3247 | 20180831 | 948 | 166219 | 263 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 263 | 41.1041 | -123.6898 | 5 SPANS LD SIDE OF 3247 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0075485 | OH | Sus | 0 | No | 2018 | AUG | Yes | Line to Line | 1375018 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | RECLOSER | 2502 | 20180901 | 122 | 166620 | 743 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 32692 | 39.5665 | -123.3983 | 2 SPANS E/OF MTR# 1010390839 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0075769 | OH | Sus | 43452471 | No | 2018 | SEP | Yes | Line to Line | 1375163 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | FUSE | 4079 | 20180906 | 1758 | 169583 | 267 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 534 | 40.493 | -123.5971 | 1 LD SIDE OF 4079 | Clear-32-90 F | Insulator | Broken, wire on object | 18-0077324 | OH | Sus | 0 | No | 2018 | SEP | Yes | Force Out | 1376165 | INS | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 5421 | 20180919 | 733 | 177171 | 3277 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 18 | 11436 | 39.1394 | -123.5038 | 2ND & 3RD SPAN LD SIDE OF 531 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0081140 | OH | Sus | 0 | No | 2018 | SEP | Yes | Line to Line | 1379060 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | REDBUD-1102 | 43191102 | OCB | 1102/2 | 20180921 | 2110 | 179128 | 923 | Distribution Circuit | Animal | Bird found | 3493 | 281055 | 39.0273 | -122.6627 | 4 SPANS SS OF LR 922 | Clear-32-90 F | Conductor, Overhead | On Ground | 18-0082278 | OH | Sus | 43487122 | No | 2018 | SEP | Yes | Line to Ground | 1379845 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3775 | 20181002 | 2245 | 186341 | 914 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 9140 | 40.2268 | -123.7887 | CURNOW- RAY/K1616-T1270: hodges rd | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0085850 | OH | Sus | 31410763 | yes | 2018 | OCT | Yes | Line to Line | 1382455 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 5233 | 20181010 | 1637 | 192731 | 1463 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 5870 | 39.2282 | -123.7663 | ON 2ND HARD TAP LD SIDE OF 5233(11SPANS LD SIDE) | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0089261 | OH | Sus | 43504269 | No | 2018 | OCT | Yes | Line to Line | 1384744 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HIGHLANDS-1104 | 43361104 | FUSE | 3097 | 20181011 | 14 | 192875 | 704 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 15376 | 38.9402 | -122.6199 | 2 W/OF THE INTERSECTION OF OAK AND 29TH | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0089282 | OH | Sus | 43504271 | No | 2018 | OCT | Yes | Line to Ground | 1384769 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | OTHER | 1899 | 20181016 | 1044 | 196475 | 391 | Distribution Circuit | 3rd Party | Vehicle | 11 | 2081 | 40.5106 | -124.1608 | WIRE DOWN ON HARD TAP FEEDING CGC 113978543418 | Clear-32-90 F | Anchor or Guy | Broken, wire on ground | 18-0090952 | OH | Sus | 0 | No | 2018 | OCT | Yes | Force Out | 1386084 | ANC | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3053 | 20181024 | 1705 | 201780 | 335 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3350 | 39.2748 | -123.6863 | 6 SPANS LD SIDE OF 717215 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0093952 | OH | Sus | 43516105 | No | 2018 | OCT | Yes | Line to Line | 1388001 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | OTHER | 4/S/LD/SIDE OF 5187 | 20181115 | 147 | 215616 | 303 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 2669 | 39.2859 | -123.7772 | 4/S/LD/SIDE OF 5187 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0099857 | OH | Sus | 43539353 | No | 2018 | NOV | Yes | Force Out | 1392700 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UKIAH-1115 | 42771115 | FUSE | 899 | 20181115 | 1424 | 216107 | 158 | Distribution Circuit | Equipment Failure/Involved | Overhead | 87 | 13746 | 39.1781 | -123.1891 | 1691 DEERWOOD DR | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0100085 | OH | Sus | 0 | No | 2018 | NOV | Yes | Force Out | 1392860 | CSO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 979 | 20181117 | 1243 | 217295 | 467 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 1636 | 39.6556 | -123.7635 | ON HARD TAP TO MTR#1010302991 (2 SPANS FROM OJ'S) | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0100664 | OH | Sus | 31416080 | No | 2018 | NOV | Yes | Line to Ground | 1393245 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MENDOCINO-1101 | 42951101 | RECLOSER | 37462 | 20181122 | 724 | 221836 | 238 | Distribution Circuit | Equipment Failure/Involved | Overhead | 779 | 185402 | 39.2651 | -123.2054 | 3 P SS LR 450 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102322 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Line | 1394468 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | OTHER | HOT WIRE DOWN @ 661 WOOD LN | 20181122 | 2240 | 222472 | 835 | Distribution Circuit | Vegetation | Tree - fell into line | 1013 | 17331 | 40.8961 | -123.605 | 661 WOOD LN - SALYER | Overcast-Rain-32-90 F | Conductor, Overhead | On Ground | 18-0102436 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Open Circuit | 1394588 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3073 | 20181123 | 1919 | 223175 | 1186 | Distribution Circuit | Vegetation | Tree - fell into line | 173 | 36522 | 41.062 | -123.6942 | TREE THROUGH LINE ON HARD TAP 1 NORTH OF 7031 ON MAINLINE | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102669 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1394761 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5211 | 20181128 | 2327 | 227128 | 563 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1126 | 39.2904 | -123.7653 | 2 SPANS LD SIDE OF 5211 | Clear-32-90 F | Conductor, Overhead | On Ground | 18-0104667 | OH | Sus | 43587894 | yes | 2018 | NOV | Yes | Line to Ground | 1395981 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 8207 | 20181203 | 459 | 232043 | 455 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3640 | 39.9939 | -123.9257 | 1 SPAN SS OF CGC# 114603424505 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0106369 | OH | Sus | 43605280 | No | 2018 | DEC | Yes | Line to Line | 1397278 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 4053 | 20181203 | 1239 | 232706 | 230 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 13110 | 38.8552 | -123.5885 | 7 SPANS LD SIDE OF 4053 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0106484 | OH | Sus | 43605420 | No | 2018 | DEC | Yes | Line to Line | 1397359 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | RECLOSER | 4218 | 20181214 | 913 | 240053 | 556 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 4596 | 40.7595 | -123.9934 | 2 SPANS LD SIDE OF 7093 ON MAINLINE | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0109152 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Ground | 1399645 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | BRIDGEVILLE-1102 | 192461102 | FUSE | 3711 | 20181214 | 1230 | 240428 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 470 | 40.4217 | -123.8072 | 4 SPANS LD SIDE/ SW OF FUCO 3711 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0109228 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Ground | 1399735 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | OTHER | WIRE DOWN @ CGC 113961833800 | 20181214 | 805 | 239864 | 702 | Distribution Circuit | Vegetation | Tree - fell into line | 312 | 211311 | 40.2407 | -124.1642 | CGC# 113961833800- 41774 MATTOLE RD | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0109176 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Force Out | 1399683 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 84085 | 20181214 | 1445 | 240540 | 1508 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 51272 | 41.2761 | -123.8073 | 7 POLES LD SIDE OF 84085 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0109273 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Force Out | 1399775 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER | 4230 | 20181214 | 1025 | 240155 | 118 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 3068 | 40.4173 | -124.0895 | MT PIERCE/WIRE DOWN AT SBCO 750641 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0109175 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Line | 1399682 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 1855 | 20181214 | 730 | 239885 | 319 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 10208 | 39.3784 | -123.275 | GALLETTI- TIM: TREE THROUGH LINE at 5720 RIDGEWOOD RD/NORTH | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0109133 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Ground | 1399594 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1514 | 20181215 | 301 | 240802 | 970 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 579 | 60256 | 40.0478 | -123.7896 | FCO 1871 TWD SB 7203 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0109323 | OH | Sus | 0 | No | 2018 | DEC | Yes | Line to Ground | 1399844 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1260 | 20181216 | 1140 | 241474 | 463 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 33410 | 39.1293 | -123.7112 | 34100 GREENWOOD RD | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0109484 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Ground | 1400107 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 5935 | 20181216 | 1319 | 241558 | 411 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 811 | 40.1129 | -123.9617 | 3P FROM EOL TO THE SOUTH | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0109492 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Line | 1400118 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 1329 | 20181216 | 2133 | 241809 | 1007 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 6328 | 38.8582 | -122.7694 | 4 SPANS W/O BOTTLE ROCK RD. S/O GLENNBROOK RESORT | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0109555 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Ground | 1400186 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 5763 | 20181219 | 1612 | 244073 | 1540 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 10780 | 40.1123 | -123.9367 | 1790 BLUE SLIDE CREEK RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0110052 | OH | Sus | 0 | No | 2018 | DEC | Yes | Line to Line | 1400901 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER | 4300 | 20181219 | 1610 | 244067 | 657 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 797 | 61869 | 38.9109 | -122.7636 | at MTR#1009745212- 11806 WESTERN PINE RD | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 18-0110034 | OH | Sus | 0 | No | 2018 | DEC | Yes | Line to Ground | 1400884 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4155 | 20181224 | 1802 | 246699 | 1138 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1138 | 38.7229 | -123.3437 | 2 SPANS LD SIDE OF FUCO 4155 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110558 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Line | 1401637 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | OTHER | 8341 | 20181224 | 910 | 246072 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1280 | 40.7998 | -124.0435 | 3 SPANS LD SIDE OF 8341 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110446 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Ground | 1401524 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CLEAR LAKE-1101 | 42141101 | FUSE | 154613 | 20181224 | 1428 | 246377 | 1420 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 9940 | 39.0079 | -122.7804 | 1 SPAN LD SIDE OF 154613 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110523 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Ground | 1401602 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 5681 | 20181224 | 2046 | 246793 | 919 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 9190 | 39.4801 | -123.7868 | 4 LD SIDE OF FUCO 5681 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110598 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Ground | 1401678 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MENDOCINO-1101 | 42951101 | FUSE | 334473 | 20181224 | 1331 | 246244 | 1487 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 10367 | 39.3762 | -123.2482 | HARD TAP FEEDING CGC#216471362747 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110588 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Line | 1401668 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | JUMPER | WIRE DOWN 1/SS/OF DEAD END | 20181224 | 1822 | 246717 | 1247 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4649 | 38.8263 | -122.7197 | SMITH- CODY: 16210 HIGHWAY 175 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110556 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Ground | 1401635 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2823 | 20181224 | 1328 | 246294 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 252 | 16715 | 39.3949 | -123.3133 | 1ST HARD TAP LD SIDE OF 2823 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110470 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Ground | 1401548 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 4943 | 20181224 | 1314 | 246213 | 336 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 16457 | 39.4387 | -123.3913 | at CGC#216022664860 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110468 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Line | 1401546 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8961 | 20181227 | 1540 | 248391 | 1330 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1330 | 39.5609 | -123.7256 | Felicich- David: from load side CO 8961 three spans down | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110870 | OH | Sus | 43622467 | No | 2018 | DEC | Yes | Line to Ground | 1402026 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | JUMPER | WIRE DOWN 2 SPANS LD SIDE OF 9787 | 20190105 | 1610 | 254546 | 279 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 5953 | 38.7278 | -123.3426 | 2 SPANS LD SIDE OF 9787 OPEN | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0004895 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Multi-Fault | 1403430 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1121 | 192021121 | OTHER | 1217 | 20190105 | 748 | 253472 | 272 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 17952 | 40.8388 | -124.0229 | 4 SPANS LOAD SIDE OF FUSES 8815 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0004637 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Multi-Fault | 1403207 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | JUMPER | 7455 | 20190105 | 1118 | 254431 | 492 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 4621 | 40.5025 | -124.2815 | 1 SPAN LD OF 7455 | Overcast-Fog-Drizzle-Strong Winds-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0004827 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403372 | CSO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 7359 | 20190105 | 1823 | 254738 | 1257 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 2514 | 40.2394 | -123.8167 | LD SIDE OF 7359 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005041 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Multi-Fault | 1403514 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 8223 | 20190105 | 807 | 253492 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2388 | 38.7 | -123.425 | EOL- LD SIDE OF FUSES 8223 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0004645 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Multi-Fault | 1403213 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 5621 | 20190105 | 1027 | 253541 | 253 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 1826 | 38.7797 | -123.5437 | MTR# 1008391872- 38050 OLD COAST HWY | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0004673 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403233 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | RECLOSER | 47952 | 20190105 | 1034 | 253704 | 330 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 36630 | 38.9145 | -123.6392 | 1 POLE SS OF 8207 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0004708 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403263 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1102 | 192461102 | FUSE | 3463 | 20190108 | 2007 | 260970 | 928 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 10208 | 40.4786 | -123.8889 | WIRE DOWN 1 SPAN LD SIDE OF 3463 | Clear-32-90 F | Conductor, Overhead | On Ground | 19-0006607 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1404688 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | OTHER | WIRE DOWN | 20190108 | 2320 | 261097 | 838 | Distribution Circuit | Vegetation | Tree - branch fell on line | 191 | 159824 | 40.2959 | -123.8293 | 1 EAST OF 1587 ON MAINLINE- 2152 ELK CREEK RD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0006609 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Open Circuit | 1404690 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 7325 | 20190108 | 651 | 260127 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 464 | 38.8052 | -123.5867 | 1ST SPAN LD SIDE OF 7325 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0006110 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1404410 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 9077 | 20190108 | 1450 | 260726 | 240 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 7920 | 39.1246 | -123.4904 | MID SPAN JUST PAST 9075 ON SINGLE ? | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0006420 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Force Out | 1404554 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 7661 | 20190108 | 1944 | 260963 | 1035 | Distribution Circuit | Vegetation | Tree - bark fell into line | 3 | 3105 | 39.4046 | -123.3217 | 7661 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0006562 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1404643 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1260 | 20190109 | 244 | 261211 | 558 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 41570 | 39.1293 | -123.7112 | ON MAINLINE 2 SPANS E/OF 8629 | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0006665 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1404737 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 8047 | 20190109 | 720 | 261293 | 610 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 3660 | 40.0536 | -123.9626 | 3 SPANS E/O 8047 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0006786 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1404840 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1101 | 192461101 | RECLOSER | 1101/2 | 20190118 | 2254 | 276410 | 1150 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 17436 | 40.4798 | -123.7803 | 4 SAPNS LD SIDE OF 4101 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012028 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Multi-Fault | 1408368 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 5557 | 20190118 | 944 | 275473 | 386 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 772 | 39.5191 | -123.7623 | 2 LD SIDE OF FUCO 5557 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011691 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408162 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | OCB | 1141/2 | 20190118 | 1617 | 276093 | 1363 | Distribution Circuit | Vegetation | Tree - branch fell on line | 394 | 55404 | 40.2866 | -123.8369 | BIONDINI- JUSTIN/K1914-T2370: Elk Creek Rd and Ave of Giants | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0011932 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408267 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 4589 | 20190118 | 1449 | 275973 | 1456 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2912 | 38.6586 | -123.4034 | 3RD & 4TH SPAN LD SIDE OF 4589 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011867 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Three Phase Fault | 1408245 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER | 7514 | 20190118 | 0 | 275093 | 947 | Distribution Circuit | Vegetation | Tree - fell into line | 1315 | 898512 | 40.9334 | -123.6249 | 1 SPAN SS OF FUSES 2939 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011495 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Multi-Fault | 1408037 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 5421 | 20190119 | 1953 | 276982 | 995 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 16915 | 39.1394 | -123.5038 | MTR#K28227 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012223 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408575 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1101 | 192171101 | FUSE | 5769 | 20190119 | 422 | 276464 | 483 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4897 | 40.9581 | -123.6292 | 3 SPANS LOADSIDE AND 1 SPAN SOUTH OF 5769 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012052 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408397 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 9201 | 20190120 | 1018 | 277198 | 223 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 2453 | 39.3173 | -123.7894 | 2 SPANS LOADSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012547 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Force Out | 1408886 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 3 | BRIDGEVILLE-1102 | 192461102 | OTHER | HOT WIRE DOWN 6 SS/OF 3713 | 20190120 | 1235 | 277266 | 460 | Distribution Circuit | Vegetation | Tree - fell into line | 274 | 30272 | 40.4422 | -123.7789 | 6 SS/OF 3713 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012598 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408924 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 8773 | 20190120 | 1921 | 277648 | 986 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 986 | 39.2458 | -123.7643 | 1 SPAN TAP LD SIDE OF 8773 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012770 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1409103 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 5625 | 20190120 | 1035 | 277210 | 274 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 274 | 38.8127 | -123.5429 | 2 SPANS LOADSIDE | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012543 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408885 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3073 | 20190120 | 1247 | 277263 | 1731 | Distribution Circuit | Vegetation | Tree - fell into line | 174 | 39578 | 41.062 | -123.6942 | MTR# 1010320676 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012577 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408907 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 3304 | 20190120 | 1528 | 277364 | 1442 | Distribution Circuit | Vegetation | Tree - fell into line | 656 | 403724 | 41.1053 | -123.6888 | 2 SS 3167 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012580 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Multi-Fault | 1408909 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 5247 | 20190120 | 817 | 277138 | 1803 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 27045 | 40.8533 | -123.5731 | 27 SPANS LOADSIDE OF 5247 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012561 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408896 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3169 | 20190121 | 2006 | 278594 | 2529 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 5058 | 41.1893 | -123.6954 | TOP OF NEW VILLAGE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0012945 | OH | Sus | 31422840 | No | 2019 | JAN | Yes | Multi-Fault | 1409290 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | JUMPER | 551 | 20190201 | 2022 | 285722 | 708 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 12036 | 39.3266 | -123.7929 | 6 SPANS LD SIDE OF 551 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016792 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1411251 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | TRIP-SAVER | 2637 | 20190201 | 2258 | 285828 | 947 | Distribution Circuit | Vegetation | Tree - fell into line | 255 | 114754 | 38.9563 | -123.6415 | Thorpe- Tim/2094: 38995 Mountain View Rd- 1 POLE N/OF 2655 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0016820 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411279 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 4205 | 20190203 | 1432 | 289104 | 222 | Distribution Circuit | Vegetation | Tree - fell into line | 337 | 23353 | 38.8369 | -122.7262 | EMERFORD & FOX | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017587 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412007 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | FUSE | 5399 | 20190211 | 1940 | 300664 | 1107 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 7749 | 40.8167 | -124.0285 | 190 MTR 10079440352 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021428 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1414947 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3751 | 20190211 | 1654 | 300176 | 1174 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 14088 | 40.221 | -123.8264 | 1 P/SS/OF 3751 | Overcast-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0021191 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414785 | CAW | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 1815 | 20190211 | 1522 | 300059 | 1313 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 39390 | 39.868 | -123.7169 | MILE MARKER 104.8 ON HWY 1 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021164 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414768 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER | 75382 | 20190220 | 9 | 319299 | 1068 | Distribution Circuit | Vegetation | Tree - fell into line | 369 | 67167 | 38.9065 | -122.6735 | 5 SPANS SS OF FUCO 3689 ON THE MAINLINE-11175 SIEGLER SPRINGS NORTH | Overcast-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0026301 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1419131 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UPPER LAKE-1101 | 42871101 | RECLOSER | 1276 | 20190220 | 1316 | 319759 | 584 | Distribution Circuit | 3rd Party | Vehicle | 290 | 31829 | 39.1586 | -122.989 | POLE FEEDING MTR 1009763900 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0026496 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1419230 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1101/2 | 20190225 | 1759 | 323409 | 2506 | Distribution Circuit | Vegetation | Tree - fell into line | 1496 | 133833 | 39.129 | -123.7111 | AT SBCO 55363 | Overcast-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 19-0027971 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1420082 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3069 | 20190225 | 1118 | 323004 | 215 | Distribution Circuit | Vegetation | Tree - fell into line | 177 | 27998 | 39.4158 | -123.7779 | 19361 BENSON LN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0027810 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420024 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3059 | 20190225 | 1524 | 323275 | 241 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 8676 | 39.4152 | -123.7708 | 19310 SUMMERS LANE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0027943 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1420067 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | TRANSFORMER | 214983664222 | 20190225 | 2203 | 323588 | 906 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1027 | 39.4165 | -123.7762 | 31220 hwy 20 MTR #1010450497 | Clear-32-90 F | Transformer (OH) | Broken, wire on ground | 19-0028044 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420154 | TXO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 4539 | 20190225 | 2039 | 323566 | 861 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3444 | 38.7379 | -122.6424 | 5 SPANS LD SIDE OF FUCO 4539 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028041 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1420150 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | RECLOSER | 37498 | 20190228 | 2045 | 328448 | 693 | Distribution Circuit | Vegetation | Tree - fell into line | 144 | 79704 | 40.2998 | -123.3426 | 4 SPANS SOUTH OF 4169 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029583 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1421143 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1793 | 20190301 | 1556 | 329035 | 1190 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 9520 | 40.0258 | -123.9471 | 1 SPAN LD SIDE FU 1793 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029871 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1421358 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 9141 | 20190303 | 1247 | 330179 | 763 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3039 | 39.2218 | -123.5996 | 16 SPANS LD SIDE OF FU 9141 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0030284 | OH | Sus | 0 | No | 2019 | MAR | Yes | Line to Ground | 1421738 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 4053 | 20190305 | 1835 | 331824 | 1250 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 15608 | 38.8552 | -123.5885 | 2 POLES LD SIDE OF FUCO 4053 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0030996 | OH | Sus | 43690648 | yes | 2019 | MAR | Yes | Line to Ground | 1422106 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 2653 | 20190305 | 1600 | 331626 | 264 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2112 | 38.932 | -123.6916 | 6 SPANS LD SIDE OF FUCO 2653 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0030943 | OH | Sus | 43690596 | yes | 2019 | MAR | Yes | Line to Ground | 1422076 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 1451 | 20190306 | 540 | 332211 | 485 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1940 | 38.7182 | -123.3834 | MTR 1008393744 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031260 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1422300 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARCIA-0401 | 43040401 | FUSE | 4491 | 20190306 | 614 | 332236 | 322 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1610 | 38.892 | -123.5415 | 8 SPANS LD SIDE OF FUCO 4491 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031186 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Force Out | 1422247 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 4451 | 20190306 | 148 | 332107 | 2052 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 8340 | 38.7903 | -123.5105 | 1010470859 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0031117 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Line | 1422211 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | JUMPER | OJ'S 13 SPANS LD SIDE OF FUCO 2345 | 20190306 | 1240 | 332854 | 284 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 284 | 38.8335 | -123.5539 | 13 SPANS LD SIDE OF FUCO 2345 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031321 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1422323 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | JUMPER | WIRE DOWN | 20190306 | 320 | 332147 | 455 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2730 | 38.7384 | -122.6388 | 4 SPANS LD SIDE OF 1039 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031078 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Open Circuit | 1422188 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 970821 | 20190306 | 2015 | 333308 | 915 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 915 | 39.369 | -123.383 | 1 SPAN LD SIDE OF FUCO 970821 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031529 | OH | Sus | 31427750 | yes | 2019 | MAR | Yes | Line to Line | 1422461 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 1373 | 20190308 | 1521 | 334582 | 1148 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 12628 | 39.2403 | -123.5957 | 11 SPANS LD SIDE OF FUCO 1373 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0032184 | OH | Sus | 43693097 | No | 2019 | MAR | Yes | Line to Line | 1422865 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3301 | 20190309 | 757 | 334855 | 264 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 2934 | 39.4163 | -123.7915 | 2 SPANS LD SIDE OF SB 49013 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0032248 | OH | Sus | 31427938 | No | 2019 | MAR | Yes | Line to Line | 1422937 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 8721 | 20190312 | 1405 | 337334 | 194 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 4462 | 39.3655 | -123.7983 | 44301 JOHNSON PARK RD 1 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033103 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1423594 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 461 | 20190312 | 1633 | 337592 | 275 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 4675 | 39.3124 | -123.7323 | 8173 OUTLAW SPRINGS RD MENDO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033183 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Line | 1423646 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CALPELLA-1101 | 43411101 | FUSE | 7497 | 20190312 | 1647 | 337621 | 260 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1040 | 39.2515 | -123.2181 | 1ST SPAN LD SIDE OF 7497 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033203 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Line | 1423664 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1607 | 20190312 | 1333 | 337298 | 192 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 768 | 39.4419 | -123.773 | 2 SP/LD/SIDE OF 1607 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033065 | OH | Sus | 43701467 | yes | 2019 | MAR | Yes | Line to Ground | 1423571 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 4367 | 20190312 | 1928 | 337962 | 1010 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 15150 | 40.1473 | -123.6358 | SS TRANSF 115409329962 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033263 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1423725 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | JUMPER | OJ @ CORNER TWD MTR# 1008936787 | 20190312 | 1718 | 337472 | 404 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2020 | 39.0195 | -123.3845 | MTR# 1008936787 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033173 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Open Circuit | 1423635 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UPPER LAKE-1101 | 42871101 | JUMPER | WIRE DOWN HOT | 20190312 | 1621 | 337627 | 350 | Distribution Circuit | Vegetation | Tree - branch fell on line | 290 | 77124 | 39.1593 | -122.9979 | THORNTON- ELLIS/T2348-K3415: 4585 LAUREL DELL | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033160 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Open Circuit | 1423624 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 8391 | 20190313 | 1035 | 338459 | 288 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 576 | 39.2765 | -123.7122 | LD SIDE OF FUSES | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033414 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1423873 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1102 | 192171102 | RECLOSER | 5012 | 20190314 | 939 | 339238 | 637 | Distribution Circuit | Equipment Failure/Involved | Overhead | 576 | 366912 | 40.8894 | -123.5579 | MTR 123J68 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0033773 | OH | Sus | 43706140 | No | 2019 | MAR | Yes | Line to Ground | 1424113 | CSO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | REDBUD-1101 | 43191101 | RECLOSER | 91960 | 20190325 | 1349 | 346988 | 412 | Distribution Circuit | Vegetation | Tree - fell into line | 535 | 62217 | 39.0203 | -122.678 | 1 SPAN LD SIDE OF 91960 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0036742 | OH | Sus | 0 | No | 2019 | MAR | Yes | Line to Ground | 1426235 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3173 | 20190327 | 359 | 348193 | 442 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 884 | 39.6337 | -123.7825 | 3 SPANS LD SIDE OF 3173 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0037341 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Line | 1426601 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | OTHER | HOT WIRE DOWN SOURE SIDE TO 3939 | 20190328 | 1330 | 349533 | 385 | Distribution Circuit | Vegetation | Tree - fell into line | 136 | 8134 | 39.4074 | -123.7279 | IN SPAN FEEDING FUCO 3939 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0037990 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Force Out | 1427011 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 5407 | 20190401 | 438 | 351664 | 812 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1624 | 40.8887 | -123.561 | MTR 1008868419 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0038764 | OH | Sus | 0 | No | 2019 | APR | Yes | Line to Ground | 1427641 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | RECLOSER | 2502 | 20190408 | 816 | 355512 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 13357 | 39.5665 | -123.3983 | 4/SP/SS/OF 8923 | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0040439 | OH | Sus | 31432945 | No | 2019 | APR | Yes | Line to Ground | 1428734 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 9201 | 20190409 | 1423 | 356747 | 208 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 2288 | 39.3173 | -123.7894 | 1ST AND 2ND POLE LD SIDE OF 9201 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0040991 | OH | Sus | 0 | yes | 2019 | APR | Yes | Line to Ground | 1429107 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | JUMPER | OJ @ TAP 2/SP/N/OF 503683 | 20190409 | 1015 | 356557 | 265 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 265 | 39.3888 | -123.7714 | 1/SS/OF MTR# 1010320992 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0040867 | OH | Sus | 0 | yes | 2019 | APR | Yes | Line to Ground | 1429068 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1607 | 20190409 | 1623 | 356962 | 164 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 656 | 39.4419 | -123.773 | 2 SPANS LD SIDE OF 1607 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0041027 | OH | Sus | 0 | yes | 2019 | APR | Yes | Line to Ground | 1429133 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | OTHER | WIRE DOWN 5 E/O 262813 | 20190409 | 2049 | 357566 | 3765 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 17605 | 38.814 | -123.5666 | 5 SPANS E/OF 262813 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0041170 | OH | Sus | 0 | yes | 2019 | APR | Yes | Open Circuit | 1429260 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1101 | 192171101 | RECLOSER | 7514 | 20190409 | 1528 | 356880 | 551 | Distribution Circuit | Vegetation | Tree - fell into line | 1317 | 683659 | 40.9334 | -123.6249 | C/OUTS 2917 MAINLINE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0041002 | OH | Sus | 0 | yes | 2019 | APR | Yes | Line to Ground | 1429117 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 87163 | 20190410 | 1452 | 358263 | 214 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 4922 | 39.2261 | -123.7481 | 3401 D RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0041423 | OH | Sus | 43736453 | yes | 2019 | APR | Yes | Line to Ground | 1429492 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 7155 | 20190414 | 1757 | 360630 | 530 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 51940 | 41.0509 | -123.6676 | 1 SPAN LOADSIDE OF 7155 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0042341 | OH | Sus | 43738676 | No | 2019 | APR | Yes | Line to Ground | 1430175 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | RECLOSER | 34008 | 20190414 | 211 | 360415 | 1074 | Distribution Circuit | 3rd Party | Vehicle | 571 | 146488 | 39.4366 | -123.3893 | 1/P/SS 8031 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0042262 | OH | Sus | 31434140 | No | 2019 | APR | Yes | Three Phase Fault | 1430105 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 4759 | 20190414 | 213 | 360413 | 781 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 8591 | 39.4175 | -123.404 | 1 POLE LD SIDE OF 4759 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0042270 | OH | Sus | 31434180 | No | 2019 | APR | Yes | Line to Line | 1430119 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | FUSE | 118473 | 20190419 | 2137 | 364068 | 905 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 6335 | 38.8917 | -123.1804 | 2 SPANS NORTH OF 118473- 28995 HWY 128 YORKVILLE(VIDMAR RANCH) | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0044509 | OH | Sus | 0 | No | 2019 | APR | Yes | Line to Ground | 1431661 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | OTHER | WIRE DOWN SS 3223 | 20190421 | 1237 | 364904 | 375 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 503 | 91825 | 39.4417 | -123.7791 | 1ST SPAN SS OF FUCO 3223 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0044690 | OH | Sus | 31435183 | No | 2019 | APR | Yes | Line to Ground | 1431855 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1102 | 192171102 | FUSE | 5437 | 20190504 | 625 | 373510 | 1076 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 9684 | 40.9649 | -123.6413 | 1/P/SS/OF 7459 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0048831 | OH | Sus | 0 | No | 2019 | MAY | Yes | Line to Line | 1434530 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 7531 | 20190515 | 1846 | 381939 | 997 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1994 | 38.7232 | -123.4036 | 2 LD SIDE OF 7531 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052525 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Line | 1437175 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1102 | 192461102 | FUSE | 3473 | 20190515 | 1529 | 381043 | 547 | Distribution Circuit | 3rd Party | Vehicle | 25 | 13675 | 40.4651 | -123.8566 | 6 SPANS LD SIDE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0052249 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Multi-Fault | 1436904 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8971 | 20190515 | 530 | 380539 | 384 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 384 | 39.6587 | -123.7827 | EOL | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0051957 | OH | Sus | 31440236 | yes | 2019 | MAY | Yes | Multi-Fault | 1436741 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1103 | 43351103 | FUSE | 4755 | 20190515 | 1940 | 381296 | 176 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 14432 | 39.1306 | -122.8547 | MTR 1008984537 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052312 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Multi-Fault | 1436954 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 2699 | 20190515 | 1717 | 381157 | 500 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 7907 | 39.265 | -123.5896 | 2 LD SIDE OF CGC 215508558585 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052302 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Line | 1436944 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | TRIP-SAVER | 3113 | 20190516 | 1626 | 382846 | 313 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 11997 | 39.5073 | -123.7645 | 8 SP LD SIDE OF 3115 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052981 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Line | 1437379 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER | 8746 | 20190516 | 936 | 382262 | 629 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2228 | 40.3969 | -123.943 | 14 SPANS SS OF FUCO 61801 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052655 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1437256 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 7303 | 20190516 | 1639 | 382930 | 121 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 121 | 38.8064 | -123.5888 | 2ND SPAN LD SIDE OF FUCO 7303 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052965 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1437368 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | FUSE | 1943 | 20190516 | 1922 | 383043 | 970 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 14550 | 39.4075 | -123.1248 | 4 SP LD SIDE OF 1943 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053049 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1437441 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 2506 | 20190516 | 837 | 382168 | 667 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 38201 | 39.4625 | -123.3374 | ESPINOLA- CHRIS: 2 spans ss of 2779 twds 9211 on Schow rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052611 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Line | 1437222 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2823 | 20190516 | 1702 | 382895 | 313 | Distribution Circuit | Vegetation | Tree - fell into line | 253 | 73460 | 39.3949 | -123.3133 | 1 SP LD SIDE OF 2823 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052985 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1437384 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1104 | 42661104 | FUSE | 8821 | 20190516 | 529 | 381948 | 531 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3186 | 39.4062 | -123.3699 | 5 SPANS LD SIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052556 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Multi-Fault | 1437193 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 1245 | 20190516 | 2048 | 383109 | 904 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 3425 | 39.3761 | -123.3532 | CGC 216178262507 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053105 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Line | 1437497 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 9219 | 20190518 | 1942 | 384506 | 848 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 8480 | 39.4293 | -123.3703 | 2 SPANS LD SIDE 9219 ON NORTH TAP | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053734 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1437947 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1121 | 192021121 | SWITCH | 6213 | 20190521 | 838 | 386724 | 442 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3978 | 40.8177 | -123.9949 | 3 SPANS LD SIDE OF FUCO 6213 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052690 | OH | Sus | 31433923 | yes | 2019 | MAY | Yes | Line to Line | 1438732 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | OTHER | WIRE DOWN | 20190521 | 1957 | 387464 | 918 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 918 | 39.3151 | -123.7715 | 6 SPANS N/W OF FUCO 5009 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0055090 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1438917 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 600433 | 20190521 | 834 | 386710 | 288 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 2604 | 39.5133 | -123.7332 | 3 SPAN SS OF CGC#215141568005 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0054775 | OH | Sus | 43791121 | yes | 2019 | MAY | Yes | Line to Ground | 1438782 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3183 | 20190521 | 1032 | 386883 | 378 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 756 | 39.552 | -123.7226 | 10 SPANS LD SIDE OF 3183 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0054868 | OH | Sus | 43791127 | yes | 2019 | MAY | Yes | Line to Line | 1438825 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 2861 | 20190521 | 1040 | 386900 | 240 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 12677 | 38.6967 | -123.4278 | MTR#1010333270 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0054845 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Line | 1438816 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 1099 | 20190521 | 1118 | 386939 | 250 | Distribution Circuit | Vegetation | Tree - fell into line | 172 | 38361 | 38.8201 | -122.7186 | 4 LD SIDE OF FUSE 1099 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0054882 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1438829 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3755 | 20190526 | 223 | 390560 | 730 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 11680 | 40.2296 | -123.8491 | 1 SPAN SS OF CGC#114819533293 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0057746 | OH | Sus | 43798261 | No | 2019 | MAY | Yes | Line to Line | 1441254 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 93234 | 20190527 | 1242 | 391256 | 448 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 41664 | 40.2355 | -123.8346 | 1ST SPAN SS OF HARD TAP FEEDING CGC#114860533272 ON THE MAINLINE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0057969 | OH | Sus | 43798521 | No | 2019 | MAY | Yes | Multi-Fault | 1441479 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1565 | 20190531 | 1320 | 394563 | 101 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 101 | 40.0347 | -123.7858 | 3 SPANS LOADSIDE OF 1565 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0060809 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1443779 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 3273 | 20190601 | 1350 | 395215 | 410 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2870 | 39.1934 | -123.7224 | MTR#5000125809 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0061171 | OH | Sus | 31449379 | yes | 2019 | JUN | Yes | Line to Line | 1444030 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 35706 | 20190601 | 1909 | 395404 | 1253 | Distribution Circuit | Vegetation | Tree - fell into line | 275 | 86940 | 39.8714 | -123.7119 | 6 SPANS LD SIDE OF FUCO 44055 ON THE MAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0061209 | OH | Sus | 43813864 | yes | 2019 | JUN | Yes | Line to Ground | 1444058 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 549 | 20190602 | 1700 | 395888 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 5295 | 38.8632 | -122.7168 | MTR#1008159643 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0061549 | OH | Sus | 31450165 | yes | 2019 | JUN | Yes | Line to Line | 1444408 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4597 | 20190607 | 1014 | 400545 | 589 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5301 | 38.729 | -123.3496 | 13 SPANS LD SIDE OF 4597 | Clear-32-90 F | Conductor, Overhead | On Ground | 19-0064216 | OH | Sus | 0 | yes | 2019 | JUN | Yes | Multi-Fault | 1446448 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 1587 | 20190611 | 2209 | 407045 | 931 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 931 | 40.296 | -123.8298 | 4/LD SIDE OF 1587- 2095 ELK CREEK RD | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0066414 | OH | Sus | 31453379 | yes | 2019 | JUN | Yes | Line to Ground | 1448345 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | OTHER | WIRE DOWN TWD CGC 215097058380 & 215096558410 | 20190614 | 1331 | 412353 | 214 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 3826 | 39.2582 | -123.7327 | LINE & BUCK FEEDING CGC#215097058380 & 215096558410 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0067832 | OH | Sus | 43843935 | No | 2019 | JUN | Yes | Open Circuit | 1449253 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 3131 | 20190615 | 1731 | 415133 | 1359 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 69309 | 40.8752 | -123.5263 | MTR # 100802334 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0068102 | OH | Sus | 0 | No | 2019 | JUN | Yes | Line to Ground | 1449504 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3757 | 20190616 | 2036 | 417119 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 27270 | 40.2283 | -123.863 | 1 SPAN SS OF MTR# 114809233085 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0068368 | OH | Sus | 0 | No | 2019 | JUN | Yes |  | 1449773 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1108 | 43311108 | RECLOSER | 1278 | 20190616 | 511 | 415696 | 1624 | Distribution Circuit | 3rd Party | Vehicle | 444 | 63568 | 38.9559 | -122.7274 | 2P E/OF 426288 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0068204 | OH | Sus | 0 | No | 2019 | JUN | Yes | Line to Line | 1449609 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 3902 | 20190620 | 333 | 422157 | 509 | Distribution Circuit | Vegetation | Tree - fell into line | 1024 | 150504 | 40.1419 | -123.8077 | Allen- Derrick/K1130-T1243: 2821 Salmon Cr. Rd. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0070026 | OH | Sus | 43850810 | yes | 2019 | JUN | Yes | Line to Ground | 1451016 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1102 | 192461102 | FUSE | 3473 | 20190625 | 743 | 428208 | 537 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 13425 | 40.4651 | -123.8566 | 21260 HWY 36 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0071901 | OH | Sus | 0 | No | 2019 | JUN | Yes | Line to Line | 1452623 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1971 | 20190625 | 1905 | 429094 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4800 | 40.1113 | -123.8905 | 2/S/LD SIDE OD 1971 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0072041 | OH | Sus | 31455432 | No | 2019 | JUN | Yes | Line to Ground | 1452672 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 2603 | 20190702 | 1955 | 440156 | 1055 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 7815 | 39.0759 | -123.5189 | 6301 SIGNAL RIDGE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0074178 | OH | Sus | 31456202 | No | 2019 | JUL | Yes | Line to Ground | 1454150 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | REDBUD-1102 | 43191102 | OTHER | WIRE DOWN | 20190702 | 1649 | 440077 | 464 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3405 | 208032 | 39.0273 | -122.6627 | 5 SPANS LD SIDE OF SBCO 6373 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0074123 | OH | Sus | 43866940 | No | 2019 | JUL | Yes | Open Circuit | 1454104 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 4447 | 20190705 | 1534 | 441510 | 1496 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 28793 | 38.7909 | -123.524 | N/OF 4451 ON HARD TAP - NO ACCESS | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0074872 | OH | Sus | 43868890 | No | 2019 | JUL | Yes | Three Phase Fault | 1454462 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 5547 | 20190707 | 21 | 442061 | 760 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 6282 | 39.1968 | -123.5881 | CGC# 215522055580 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0074992 | OH | Sus | 43869185 | No | 2019 | JUL | Yes | Line to Ground | 1454575 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 6653 | 20190708 | 1430 | 442920 | 276 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2208 | 38.8154 | -123.5974 | 33771 S HWY 1 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0075354 | OH | Sus | 31456598 | No | 2019 | JUL | Yes | Line to Ground | 1454813 | CSO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 5511 | 20190710 | 1449 | 444497 | 484 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2904 | 38.8016 | -123.5746 | at SINGLE ? TAP 2 WIRES DOWN JUST PAST 5511 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0076106 | OH | Sus | 43876680 | No | 2019 | JUL | Yes | Line to Ground | 1455295 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 5097 | 20190712 | 1208 | 446213 | 202 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 2828 | 38.9019 | -123.6034 | 5 SPANS LD SIDE OF FU 5097 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0076832 | OH | Sus | 43878570 | No | 2019 | JUL | Yes | Line to Ground | 1455812 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1106 | 43351106 | FUSE | 1599 | 20190715 | 859 | 450817 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 10373 | 39.0771 | -122.7832 | MTR 1008686806 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0077372 | OH | Sus | 31457462 | No | 2019 | JUL | Yes | Line to Ground | 1456309 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER | 23444 | 20190720 | 2204 | 464861 | 1073 | Distribution Circuit | 3rd Party | Vehicle | 167 | 24066 | 38.849 | -123.644 | MTR#1010374979- 43101 IVERSEN RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0079530 | OH | Sus | 0 | No | 2019 | JUL | Yes | Multi-Fault | 1457632 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | FUSE | 1959 | 20190730 | 2239 | 475924 | 841 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 34481 | 39.2929 | -123.082 | 4TH POLE LD SIDE OF FUCO 1959 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0082776 | OH | Sus | 0 | No | 2019 | JUL | Yes | Line to Line | 1459778 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2775 | 20190801 | 1627 | 477418 | 520 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 6760 | 39.5168 | -123.3918 | 2ND SPAN E/OF 2775 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0083579 | OH | Sus | 31460727 | No | 2019 | AUG | Yes | Line to Line | 1460222 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 3304 | 20190810 | 506 | 498638 | 754 | Distribution Circuit | Equipment Failure/Involved | Overhead | 658 | 496132 | 41.105 | -123.6883 | 3 MILES LD SIDE OF 3304 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0086448 | OH | Sus | 0 | yes | 2019 | AUG | Yes | Line to Ground | 1461992 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 5563 | 20190816 | 710 | 515125 | 331 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 2979 | 40.1042 | -123.9061 | 5/S LD SIDE OF 5563 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0088744 | OH | Sus | 43925499 | yes | 2019 | AUG | Yes | Line to Line | 1463626 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | OCB | 1101/2 | 20190819 | 1713 | 523893 | 683 | Distribution Circuit | Vegetation | Tree - branch fell on line | 782 | 410686 | 40.9479 | -123.6402 | 3/SP/W/OF 6283 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0089645 | OH | Sus | 0 | No | 2019 | AUG | Yes | Line to Ground | 1464330 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 46545 | 20190825 | 910 | 538051 | 667 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 667 | 40.1713 | -123.6083 | 1/S LD SIDE OF 46545 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0091874 | OH | Sus | 31469605 | No | 2019 | AUG | Yes | Force Out | 1465647 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | FUSE | 6779 | 20190830 | 808 | 547797 | 750 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 6750 | 40.7967 | -124.0327 | at END OF FERNWOOD LANE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0094026 | OH | Sus | 0 | No | 2019 | AUG | Yes | Line to Line | 1466832 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 1363 | 20190903 | 1017 | 551255 | 293 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 16701 | 38.9153 | -123.6397 | 25 SPANS LD SIDE OF FUCO 1363 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0094741 | OH | Sus | 31470506 | No | 2019 | SEP | Yes | Line to Ground | 1467346 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3321 | 20190912 | 1404 | 575813 | 1450 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 5 | 1994 | 39.4049 | -123.7415 | 29619 HWY 20 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0098420 | OH | Sus | 0 | No | 2019 | SEP | Yes | Line to Ground | 1469615 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER | 23444 | 20190915 | 306 | 583140 | 730 | Distribution Circuit | 3rd Party | Vehicle | 168 | 49642 | 38.849 | -123.644 | 1 SPAN LD SIDE OF 23444 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0099199 | OH | Sus | 0 | No | 2019 | SEP | Yes | Line to Ground | 1470090 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 66809 | 20190915 | 1005 | 583261 | 719 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 20132 | 41.2799 | -123.8407 | 8 SPANS LOADSIDE 68817 ON MAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0099255 | OH | Sus | 0 | No | 2019 | SEP | Yes | Line to Ground | 1470139 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 8953 | 20190917 | 655 | 585675 | 296 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 888 | 39.2428 | -123.7752 | 5200 N HWY 1 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0099991 | OH | Sus | 43958050 | No | 2019 | SEP | Yes | Line to Ground | 1470548 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2503 | 20190919 | 658 | 592491 | 1063 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5315 | 40.3229 | -124.2812 | CURNOW- RAY/K1616-T1270: 741 chambvers | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0101191 | OH | Sus | 0 | No | 2019 | SEP | Yes | Line to Ground | 1471276 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1101 | 192171101 | FUSE | 394285 | 20190927 | 227 | 619857 | 408 | Distribution Circuit | 3rd Party | Vehicle | 4 | 1632 | 40.9448 | -123.6188 | 4 POLES LD SIDE OF FUCO 394285 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0104358 | OH | Sus | 43972232 | No | 2019 | SEP | Yes | Line to Ground | 1473350 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | OTHER | WIRE DOWN 1 SP LD SIDE 9137 | 20190929 | 717 | 628485 | 331 | Distribution Circuit | Equipment Failure/Involved | Overhead | 295 | 71626 | 39.2522 | -123.5906 | 1 SPAN LD SIDE OF FUCO 9137 ON MAINLINE | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0105125 | OH | Sus | 43973920 | No | 2019 | SEP | Yes | Open Circuit | 1473906 | CSO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POTTER VALLEY P H-1105 | 42281105 | FUSE | 1961 | 20190930 | 836 | 630195 | 565 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3390 | 39.4019 | -123.1224 | 2.5 SPANS LOAD SIDE OF 1961 20801 VAN ARSDALE RD | Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0105377 | OH | Sus | 31473723 | No | 2019 | SEP | Yes | Line to Ground | 1474123 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 5561 | 20191019 | 1443 | 673816 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 8120 | 39.381 | -123.8003 | 3085 GIBNEY RD | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0113736 | OH | Sus | 44010819 | No | 2019 | OCT | Yes | Line to Ground | 1481238 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 3337 | 20191019 | 840 | 671355 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 325 | 41.1129 | -123.701 | 7 SPANS OF LD SIDE FUCO 3337 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0113672 | OH | Sus | 31475145 | No | 2019 | OCT | Yes | Line to Ground | 1481140 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 7217 | 20191105 | 1758 | 700389 | 964 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1928 | 39.5245 | -123.7608 | 27201 HIGHWAY 1 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0121622 | OH | Sus | 44091103 | No | 2019 | NOV | Yes | Line to Ground | 1489426 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1106 | 43351106 | FUSE | 4131 | 20191107 | 824 | 701671 | 217 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 868 | 39.0087 | -122.7528 | 1/SP/E/OF 4131 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0122298 | OH | Sus | 44092984 | No | 2019 | NOV | Yes | Line to Ground | 1489789 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARTLEY-1101 | 43211101 | OCB | 1101/2 | 20191111 | 1613 | 704558 | 1106 | Distribution Circuit | Animal | Bird found | 3019 | 331055 | 39.0766 | -122.9334 | 1756 MARTIN ST- LAKEPORT | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0123639 | OH | Sus | 44097344 | No | 2019 | NOV | Yes | Line to Line | 1490523 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | RECLOSER | 4698 | 20191123 | 817 | 713371 | 754 | Distribution Circuit | 3rd Party | Vehicle | 721 | 543634 | 39.4911 | -123.7844 | Felicich- David: 24970 N Hwy 1 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0127919 | OH | Sus | 0 | No | 2019 | NOV | Yes | Line to Line | 1493560 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 7667 | 20191125 | 951 | 714263 | 754 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2262 | 39.3809 | -123.2947 | 3201 RIDGEWOOD RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0128318 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Multi-Fault | 1493908 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | JUMPER | OJ ON TAP 1/E/OF MTR 1008393307 | 20191128 | 1113 | 722879 | 197 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 394 | 39.6574 | -123.7685 | 3 SPANS SS OF MTR# 1008393307 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0130876 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Open Circuit | 1495563 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3291 | 20191130 | 1506 | 724467 | 274 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 4932 | 39.3097 | -123.7501 | Garcia- Dan/T1260-K3467: 42265 little lake | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0131482 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Ground | 1496181 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 3109 | 20191130 | 1621 | 724775 | 381 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 32766 | 39.4629 | -123.7936 | 8 SPANS LOADSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0131507 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Ground | 1496207 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 1523 | 20191130 | 1819 | 724797 | 153 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 1530 | 40.2899 | -123.8126 | 2'ND HARDTAP LOADSIDE OF 1523 | Partly Cloudy-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0131575 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Ground | 1496272 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | JUMPER | OJ 1/SP/SS OF MTR# 1009737398 | 20191130 | 1819 | 725386 | 999 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 999 | 40.2881 | -123.816 | MTR# 1009737398 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0131908 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Ground | 1496605 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | OTHER | WIRE DWN BETWEEN 7287 AND 7289 | 20191130 | 1438 | 724384 | 291 | Distribution Circuit | Vegetation | Tree - fell into line | 252 | 67980 | 38.8146 | -123.5857 | BETWEEN 7287 AND 7289 ON MAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0131454 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Ground | 1496152 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 4943 | 20191130 | 1107 | 724168 | 314 | Distribution Circuit | Vegetation | Tree - branch fell on line | 161 | 50554 | 39.4387 | -123.3913 | CGC 216024164933 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0131404 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Ground | 1496107 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 7287 | 20191201 | 714 | 725723 | 623 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 10591 | 38.8139 | -123.5856 | 3 SPANS LD OF 7287 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0131935 | OH | Sus | 0 | No | 2019 | DEC | Yes | Line to Line | 1496631 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3969 | 20191207 | 747 | 732287 | 208 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 12272 | 39.3811 | -123.7737 | 15351 MITCHELL CRK DR sap 102187902 | Clear | Conductor, Overhead | Broken, wire on ground | 19-0134714 | OH | Sus | 0 | yes | 2019 | DEC | Yes | Open Circuit | 1498507 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3969 | 20191207 | 1144 | 732653 | 118 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 6962 | 39.3811 | -123.7737 | LD SIDE OF FUCO 3969 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0134767 | OH | Sus | 0 | yes | 2019 | DEC | Yes | Line to Line | 1498569 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1770 | 20191207 | 426 | 732149 | 135 | Distribution Circuit | Equipment Failure/Involved | Overhead | 351 | 12609 | 39.9153 | -123.7634 | 13 SPANS LD SIDE OF LR 1770 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0134672 | OH | Sus | 0 | yes | 2019 | DEC | Yes | Line to Line | 1498424 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | RECLOSER | 23444 | 20191208 | 1405 | 733863 | 212 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 26100 | 38.849 | -123.644 | ON MAINLINE at 6223 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0135046 | OH | Sus | 0 | No | 2019 | DEC | Yes | Line to Ground | 1498840 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 4337 | 20191208 | 1523 | 733881 | 290 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3190 | 38.8525 | -122.6827 | 8 SPANS LD SIDE OF FU 4337 | Clear-32-90 F | Crossarm, Wood | Broken, wire on object | 19-0135058 | OH | Sus | 31480893 | No | 2019 | DEC | Yes | Force Out | 1498852 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 7313 | 20191212 | 147 | 737061 | 557 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1114 | 38.8124 | -123.5949 | LD SIDE OF 7313 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0136065 | OH | Sus | 31481215 | No | 2019 | DEC | Yes | Line to Line | 1499930 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | OTHER | WIRE DOWN 2 SPANS LD SIDE OF 9689 | 20200110 | 1924 | 759133 | 335 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1046 | 311850 | 38.7247 | -123.4629 | 2 SPANS LD SIDE OF 9689 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0007596 | OH | Sus | 44154460 | No | 2020 | JAN | Yes | Open Circuit | 1505599 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | FUSE | 7177 | 20200114 | 1017 | 760804 | 724 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2896 | 40.4323 | -123.4771 | 3 SPANS LD SIDE 7177 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0008665 | OH | Sus | 0 | No | 2020 | JAN | Yes | Line to Ground | 1506278 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2595 | 20200118 | 110 | 765339 | 788 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 788 | 40.0754 | -123.9572 | 2ND SPAN LD SIDE OF FUCO 2595 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0011021 | OH | Sus | 0 | No | 2020 | JAN | Yes | Line to Ground | 1507486 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | JUMPER | WIRE DOWN | 20200118 | 2152 | 765898 | 848 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 4225 | 40.2639 | -124.043 | 2 SPANS LD OF MTR#1008278598 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0011135 | OH | Sus | 0 | No | 2020 | JAN | Yes | Line to Ground | 1507649 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2415 | 20200121 | 1901 | 767579 | 1356 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 9665 | 39.5006 | -123.337 | 1 SPAN LOADSIDE OF 2415 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0012151 | OH | Sus | 0 | No | 2020 | JAN | Yes | Line to Ground | 1508346 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | JUMPER | WIRE DOWN | 20200121 | 1040 | 767225 | 291 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 9009 | 40.9055 | -123.7241 | 20 SPANS LD SIDE OF 3139 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0009566 | OH | Sus | 0 | No | 2020 | JAN | Yes | Line to Ground | 1508080 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | OTHER | WIRE DOWN 2 SPANS SS OF 6795 | 20200122 | 906 | 767800 | 549 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3493 | 41.2577 | -123.6025 | 2 SPANS SSOF 6795 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0012377 | OH | Sus | 44161361 | No | 2020 | JAN | Yes | Line to Ground | 1508486 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 8953 | 20200124 | 810 | 769144 | 283 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 849 | 39.2428 | -123.7752 | 1 SPAN W/OF 8953 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0013129 | OH | Sus | 44163499 | No | 2020 | JAN | Yes | Line to Ground | 1508867 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 4213 | 20200125 | 1034 | 769940 | 511 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 16 | 8176 | 38.8305 | -122.7267 | 10/S LD SIDE OF 4213 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0013671 | OH | Sus | 0 | No | 2020 | JAN | Yes | Line to Ground | 1509203 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 5657 | 20200128 | 1948 | 772179 | 1186 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 4 | 4744 | 39.0402 | -123.5217 | 1ST TRANSF LD SIDE OF FUCO 5657 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 20-0014770 | OH | Sus | 0 | No | 2020 | JAN | Yes | Line to Ground | 1509930 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UKIAH-1113 | 42771113 | FUSE | 1227 | 20200202 | 627 | 775433 | 511 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 4851 | 39.121 | -123.2073 | 3 SPANS FROM EOL at 450 CRESTVIEW DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0016280 | OH | Sus | 0 | yes | 2020 | FEB | Yes | Line to Ground | 1511052 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 6423 | 20200202 | 707 | 775458 | 855 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 18764 | 39.4878 | -123.4249 | MTR#1010222614 (30000 TIMBERLINE RD) | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0016291 | OH | Sus | 0 | yes | 2020 | FEB | Yes | Line to Line | 1511063 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1101 | 192461101 | RECLOSER | 69866 | 20200207 | 408 | 779797 | 516 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 15446 | 40.4693 | -123.7011 | 1 SPAN LD SIDE OF SW 679610 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0018368 | OH | Sus | 31489724 | No | 2020 | FEB | Yes | Three Phase Fault | 1512531 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | JUMPER | WIRE DOWN 2 LD SIDE OF FU 5575 | 20200208 | 1410 | 780674 | 370 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1850 | 39.4635 | -123.7923 | 2 LD SIDE OF FU 5575 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0018834 | OH | Sus | 0 | No | 2020 | FEB | Yes | Line to Ground | 1512830 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 9025 | 20200218 | 1510 | 794936 | 503 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 33198 | 39.0657 | -123.4424 | 2 SPANS LD SIDE OF FU 9025 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0023172 | OH | Sus | 31491642 | No | 2020 | FEB | Yes | Line to Ground | 1516056 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1907 | 20200219 | 240 | 795239 | 309 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 4907 | 40.4871 | -124.2598 | 4 SS SBCO 77379 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0023237 | OH | Sus | 44196767 | No | 2020 | FEB | Yes | Line to Ground | 1516104 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 881 | 20200221 | 1549 | 800274 | 491 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 3437 | 39.0626 | -123.4436 | LD SIDE OF FUSES 881 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0024848 | OH | Sus | 31491797 | No | 2020 | FEB | Yes | Three Phase Fault | 1516986 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1899 | 20200301 | 1434 | 820797 | 446 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 4906 | 40.5113 | -124.1605 | 25 POLES BEYOND 1899 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0027529 | OH | Sus | 44226116 | No | 2020 | MAR | Yes | Line to Ground | 1518730 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 6467 | 20200302 | 1400 | 823433 | 538 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 5 | 2690 | 39.8477 | -123.709 | 1 SPAN LD SIDE OF 6467 FUCO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0027963 | OH | Sus | 44226905 | yes | 2020 | MAR | Yes | Line to Ground | 1519015 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 6865 | 20200305 | 1140 | 832917 | 340 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 28576 | 40.2936 | -123.8176 | ON MAINLINE 6 SPANS E/O FUSE 4951 | Overcast-32-90 F | Insulator | Broken, wire on ground | 20-0029158 | OH | Sus | 0 | No | 2020 | MAR | Yes | Line to Line | 1519684 | INS | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | REDBUD-1101 | 43191101 | RECLOSER | 708166 | 20200325 | 655 | 864071 | 284 | Distribution Circuit | Animal | Bird found | 685 | 75698 | 39.0231 | -122.678 | 1 SPAN IN ON HARD TAP 5 N/OF 832969 TO WEST | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0035908 | OH | Sus | 44273564 | No | 2020 | MAR | Yes | Line to Ground | 1523876 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2551 | 20200326 | 503 | 865806 | 700 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 11200 | 40.3008 | -124.2972 | CGC 113603036082 | Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0036299 | OH | Sus | 0 | No | 2020 | MAR | Yes | Line to Ground | 1524044 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | OTHER | WIRE DOWN | 20200404 | 1025 | 882266 | 481 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 11280 | 39.0779 | -123.5238 | CGC# 215679051750 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0038399 | OH | Sus | 44281569 | No | 2020 | APR | Yes | Line to Ground | 1525235 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4595 | 20200421 | 1206 | 898818 | 386 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2702 | 38.7274 | -123.3399 | 4 SP LD SIDE OF 4595 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0043281 | OH | Sus | 0 | No | 2020 | APR | Yes | Line to Line | 1528313 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1899 | 20200424 | 1341 | 900817 | 500 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 5500 | 40.5113 | -124.1605 | 15/S/LS OF 1899 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0044460 | OH | Sus | 31501204 | No | 2020 | APR | Yes | Line to Ground | 1528949 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | FUSE | 1413 | 20200508 | 1241 | 909641 | 438 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4818 | 38.9037 | -123.3146 | 2 SPANS LD SIDE 960297 ON MAIN LINE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0048592 | OH | Sus | 0 | No | 2020 | MAY | Yes | Line to Ground | 1531567 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2823 | 20200517 | 2112 | 915501 | 556 | Distribution Circuit | Vegetation | Tree - fell into line | 251 | 139556 | 39.3949 | -123.3133 | 2 SPANS LOAD SIDE OF 2823 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0051088 | OH | Sus | 0 | yes | 2020 | MAY | Yes | Line to Line | 1533008 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | RECLOSER | 630456 | 20200520 | 1011 | 918300 | 295 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 12390 | 40.5269 | -124.1642 | 1 SPAN SS OF FUCO 1899 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0052336 | OH | Sus | 44327749 | No | 2020 | MAY | Yes | Multi-Fault | 1533613 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1770 | 20200520 | 147 | 918024 | 770 | Distribution Circuit | Vegetation | Tree - fell into line | 349 | 92148 | 39.9153 | -123.7634 | 3 SS/OF 624583 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0052121 | OH | Sus | 31503416 | No | 2020 | MAY | Yes | Three Phase Fault | 1533484 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | OTHER | WIRE DOWN 8 SP LD SIDE 3071 | 20200524 | 1232 | 920542 | 272 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 272 | 39.4029 | -123.7249 | 8 SPANS LD SIDE OF 3071 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0053703 | OH | Sus | 44331169 | No | 2020 | MAY | Yes | Open Circuit | 1534328 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 3295 | 20200529 | 424 | 924915 | 437 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 4196 | 39.4427 | -123.7708 | 1/SP/LD SIDE OF 1008995562 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0055492 | OH | Sus | 44334613 | yes | 2020 | MAY | Yes | Line to Ground | 1535434 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | JUMPER | WIRE DOWN | 20200530 | 2223 | 926636 | 762 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2285 | 39.2427 | -123.7754 | 1 SPAN LD SIDE OF 8953 TWD WEST | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0056005 | OH | Sus | 0 | yes | 2020 | MAY | Yes | Line to Ground | 1535870 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 91948 | 20200606 | 1418 | 932811 | 159 | Distribution Circuit | Vegetation | Tree - fell into line | 117 | 9168 | 39.4275 | -123.3154 | Dickson- Josh 707 293-6004: at CGC # 216330063650 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0058444 | OH | Sus | 31505138 | yes | 2020 | JUN | Yes | Line to Ground | 1537675 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | OTHER | WIRE DOWN | 20200607 | 1629 | 933652 | 231 | Distribution Circuit | Vegetation | Tree - fell into line | 629 | 40997 | 38.8324 | -123.6232 | MAIN LINE BET FUCO 7321 & FUCO 7319 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0058645 | OH | Sus | 44344703 | yes | 2020 | JUN | Yes | Open Circuit | 1537866 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3049 | 20200612 | 823 | 937699 | 324 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 4860 | 39.2615 | -123.7105 | 2/SP/SS OF MTR 1003694604 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0060548 | OH | Sus | 31505824 | yes | 2020 | JUN | Yes | Line to Line | 1539267 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UPPER LAKE-1101 | 42871101 | RECLOSER | 1276 | 20200616 | 1538 | 940447 | 343 | Distribution Circuit | Vegetation | Tree - fell into line | 290 | 41902 | 39.1586 | -122.989 | PEARSON- PAUL: 7001 scotts valley rd | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0061893 | OH | Sus | 44357413 | No | 2020 | JUN | Yes | Line to Ground | 1540214 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | FUSE | 1897 | 20200622 | 2148 | 944855 | 562 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1124 | 40.3378 | -124.0316 | 1 MILE LD SIDE OF 1897 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0063814 | OH | Sus | 44362300 | yes | 2020 | JUN | Yes | Line to Ground | 1541608 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1965 | 20200624 | 1622 | 946511 | 381 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 5927 | 40.1219 | -123.834 | OFF TAP 7/S/LD SIDE OF 1965 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0064599 | OH | Sus | 31506882 | No | 2020 | JUN | Yes | Line to Ground | 1542216 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1106 | 43351106 | FUSE | 4123 | 20200627 | 317 | 948524 | 1011 | Distribution Circuit | Equipment Failure/Involved | Overhead | 107 | 13827 | 39 | -122.7528 | 8100 SODA BAY RD | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0065619 | OH | Sus | 0 | No | 2020 | JUN | Yes | Line to Ground | 1542847 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | JUMPER | WIRE DOWN 2 SPANS SS OF MTR 1008990380 | 20200629 | 859 | 951104 | 414 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 17176 | 39.3693 | -123.7658 | 2 SPANS SS OF MTR 1008990380 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0066133 | OH | Sus | 44370481 | No | 2020 | JUN | Yes | Open Circuit | 1543260 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | OTHER | 3965 | 20200629 | 826 | 951624 | 417 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 417 | 40.3417 | -123.8803 | 6 SPANS LD SIDE OF 3965 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0066065 | OH | Sus | 31507287 | No | 2020 | JUN | Yes | Open Circuit | 1543229 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HUMBOLDT BAY-1102 | 192341102 | FUSE | 5301 | 20200709 | 1350 | 961013 | 255 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 4 | 1020 | 40.7008 | -124.138 | 15 SPANS LD SIDE OF 5301 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0070173 | OH | Sus | 0 | No | 2020 | JUL | Yes | Line to Ground | 1545482 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 1757 | 20200714 | 2031 | 964792 | 1042 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 16672 | 39.4416 | -123.7285 | 21007 COMPANY RANCH RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0071988 | OH | Sus | 44390883 | No | 2020 | JUL | Yes | Line to Line | 1546677 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 2006 | 20200720 | 2010 | 968756 | 597 | Distribution Circuit | 3rd Party | Vehicle | 393 | 197211 | 40.2235 | -123.8263 | 2 SPANS N/OF SBCO 3783 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0073899 | OH | Sus | 0 | yes | 2020 | JUL | Yes | Multi-Fault | 1547982 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 249707 | 20200805 | 1400 | 979532 | 136 | Distribution Circuit | 3rd Party | Vehicle | 1 | 136 | 40.0623 | -123.8382 | 5 SPANS LD SIDE 249707 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0080100 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Three Phase Fault | 1552004 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1103 | 192171103 | RECLOSER | 181562 | 20200805 | 1124 | 979338 | 880 | Distribution Circuit | Vegetation | Tree - fell into line | 2339 | 710365 | 40.9476 | -123.6386 | 220 COUNCILMAN RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0079984 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Multi-Fault | 1551953 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1967 | 20200820 | 311 | 1024052 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 898 | 40.1272 | -123.8515 | 5 SPANS LD SIDE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0087811 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Ground | 1557402 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1102 | 43311102 | FUSE | 52837 | 20200820 | 1103 | 1025512 | 267 | Distribution Circuit | 3rd Party | Vehicle | 2 | 534 | 38.9331 | -122.7514 | 2 LD SIDE OF FUSES 52837 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0087997 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Three Phase Fault | 1557527 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 6789 | 20200822 | 2246 | 1027413 | 1078 | Distribution Circuit | 3rd Party | Vehicle | 14 | 15092 | 40.218 | -123.8718 | 2/P/SS/OF 6713 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0089025 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Line | 1558142 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 9405 | 20200902 | 1624 | 1050713 | 420 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 23 | 9660 | 38.8153 | -123.5819 | 1 POLE SOURCE SIDE OF MTR# 1006219880 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0092877 | OH | Sus | 0 | No | 2020 | SEP | Yes | Line to Ground | 1560548 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 547 | 20200928 | 412 | 1095980 | 902 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 19844 | 38.8481 | -122.7563 | 3 SPANS S/OF 547 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0102259 | OH | Sus | 0 | yes | 2020 | SEP | Yes | Line to Line | 1566811 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 826 | 20201009 | 601 | 1113895 | 342 | Distribution Circuit | Equipment Failure/Involved | Overhead | 870 | 132633 | 39.4204 | -123.3598 | BARRINGTON- SORREL/T1102-K3455: 24000 sherwood rd | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0106754 | OH | Sus | 0 | No | 2020 | OCT | Yes | Line to Ground | 1569527 | CSO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 7871 | 20201105 | 1451 | 1136811 | 368 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1472 | 38.922 | -123.6227 | LD SIDE OF 7871 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0117530 | OH | Sus | 31517837 | No | 2020 | NOV | Yes | Line to Ground | 1577319 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | BRIDGEVILLE-1102 | 192461102 | FUSE | 3723 | 20201113 | 1348 | 1143704 | 254 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 2032 | 40.3504 | -123.7146 | 35101 ALDERPOINT RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0120734 | OH | Sus | 0 | No | 2020 | NOV | Yes | Line to Line | 1579575 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARRIS-1109 | 192431109 | FUSE | 811 | 20201113 | 553 | 1143219 | 289 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1156 | 40.768 | -124.0904 | WALPOLE- JAMES/K4283-T1913: 3707 PIGEON PT. RD. | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0120399 | OH | Sus | 0 | No | 2020 | NOV | Yes | Line to Line | 1579384 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CARLOTTA-1121 | 192291121 | OTHER | WIRE DOWN 1/SS/OF 44150 | 20201117 | 919 | 1147136 | 251 | Distribution Circuit | Vegetation | Tree - branch fell on line | 212 | 51573 | 40.495 | -123.9883 | 1/S/SS/OF 44150 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0121780 | OH | Sus | 0 | No | 2020 | NOV | Yes | Open Circuit | 1580569 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 262813 | 20201121 | 1146 | 1151252 | 279 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 3069 | 38.8138 | -123.5702 | LD SIDE OF FUCO 262813 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0123774 | OH | Sus | 44564503 | No | 2020 | NOV | Yes | Line to Ground | 1581817 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | RECLOSER | 37222 | 20201201 | 727 | 1156855 | 517 | Distribution Circuit | Equipment Failure/Involved | Overhead | 152 | 78584 | 38.9147 | -123.272 | 6 SPANS SS/OF 3719 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0126201 | OH | Sus | 44572259 | No | 2020 | DEC | Yes | Line to Ground | 1583218 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 9141 | 20201213 | 648 | 1182293 | 462 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2772 | 39.2218 | -123.5996 | 16 SPANS LD SIDE 9141 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0130105 | OH | Sus | 44587548 | No | 2020 | DEC | Yes | Line to Line | 1586851 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 6423 | 20201213 | 49 | 1182228 | 788 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 22064 | 39.4878 | -123.4249 | 14 SPANS LD SIDE | Clear-32-90F | Pole-Wood | Broken, wire on ground | 20-0130070 | OH | Sus | 0 | No | 2020 | DEC | Yes | Line to Line | 1586782 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | OTHER | WIRE DOWN LD SIDE OF CGC# 215489542530 | 20201215 | 1016 | 1187248 | 331 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 5192 | 38.8232 | -123.5842 | MTR # 1010519482 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0130538 | OH | Sus | 44588521 | No | 2020 | DEC | Yes | Line to Ground | 1587529 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 496769 | 20201217 | 1639 | 1193008 | 399 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 30 | 11970 | 39.481 | -123.7812 | WESTWOOD DR AND ROSS RANCH RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0130985 | OH | Sus | 31521931 | No | 2020 | DEC | Yes | Line to Line | 1588230 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 771991 | 20201225 | 831 | 1198492 | 344 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3096 | 40.2989 | -123.8216 | 1 SPAN LD SIDE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0131759 | OH | Sus | 0 | No | 2020 | DEC | Yes | Multi-Fault | 1589471 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HUMBOLDT BAY-1102 | 192341102 | FUSE | 5301 | 20201225 | 928 | 1198507 | 679 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2716 | 40.7008 | -124.138 | 11 LD SIDE OF 5301 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0131772 | OH | Sus | 0 | No | 2020 | DEC | Yes | Line to Line | 1589485 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 7675 | 20201226 | 914 | 1199026 | 336 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 336 | 39.4743 | -123.3655 | 1 POLE FROM EOL | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0131877 | OH | Sus | 0 | No | 2020 | DEC | Yes | Line to Line | 1589593 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 7449 | 20210103 | 901 | 1202724 | 624 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3744 | 40.2155 | -123.8344 | 15 SPANS LD SIDE AND 2 SPANS SOUTH OF 7449 | Clear-32-90 F | Conductor, Overhead | On Ground | 21-0004419 | OH | Sus | 31526380 | No | 2021 | JAN | Yes | Multi-Fault | 1590525 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 8439 | 20210104 | 1334 | 1203854 | 285 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 17955 | 39.349 | -123.3401 | 3 LOAD SIDE OF 8439 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0004811 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1590764 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER | 31304 | 20210106 | 902 | 1205205 | 478 | Distribution Circuit | 3rd Party | Vehicle | 140 | 58680 | 39.415 | -123.7702 | 29901 HWY 20- FORT BRAGG | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0005497 | OH | Sus | 0 | No | 2021 | JAN | Yes | Three Phase Fault | 1591187 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 5681 | 20210106 | 914 | 1205236 | 605 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 9680 | 41.0713 | -123.6946 | 1 SPAN LD SIDE OF FUSES | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 21-0005656 | OH | Sus | 0 | No | 2021 | JAN | Yes | Multi-Fault | 1591277 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | OCB | 1141/2 | 20210108 | 116 | 1206526 | 230 | Distribution Circuit | Vegetation | Tree - fell into line | 392 | 40512 | 40.2866 | -123.8369 | 15 SPANS SOURCE SIDE TO 6807 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0006371 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1591656 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER | 95324 | 20210112 | 2053 | 1209415 | 499 | Distribution Circuit | Vegetation | Tree - fell into line | 881 | 131781 | 40.284 | -123.8723 | 2 SPANS FROM 8299 GOING TWD 8297 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 21-0007993 | OH | Sus | 0 | No | 2021 | JAN | Yes | Three Phase Fault | 1592653 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MAPLE CREEK-1101 | 192101101 | FUSE | 6235 | 20210113 | 617 | 1209477 | 433 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 4406 | 40.7679 | -123.8719 | 9 SPANS LD SIDE OF 3105 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0008132 | OH | Sus | 44623846 | No | 2021 | JAN | Yes | Line to Line | 1592836 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 1999 | 20210129 | 2010 | 1242591 | 1330 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 94430 | 39.4312 | -123.3728 | 24148 BIRCH CIRCLE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0019184 | OH | Sus | 0 | No | 2021 | JAN | Yes | Open Circuit | 1601049 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 4943 | 20210129 | 2015 | 1242608 | 1077 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 22617 | 39.4387 | -123.3914 | TREE 4P/LD SIDE OJ at 216039165018 | Clear-32-90 F | Conductor, Overhead | On Ground | 21-0018698 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1600557 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | OTHER | WIRE DOWN 2 SPANS LD SIDE OF 93234 | 20210201 | 1632 | 1245346 | 223 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 21185 | 40.2356 | -123.8348 | 2 SPANS LD SIDE 93234 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0020597 | OH | Sus | 0 | No | 2021 | FEB | Yes | Open Circuit | 1602247 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1104 | 42661104 | FUSE | 8025 | 20210202 | 1258 | 1246051 | 387 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2322 | 39.3588 | -123.3195 | LD SIDE OF 8025 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0020907 | OH | Sus | 0 | No | 2021 | FEB | Yes | Line to Line | 1602449 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 899734 | 20210205 | 1329 | 1248861 | 316 | Distribution Circuit | Vegetation | Tree - branch fell on line | 519 | 89765 | 40.2476 | -123.8326 | ALLEN- DERRICK /K1130-T1243: 1507 Salmon Creek Rd | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0022439 | OH | Sus | 0 | No | 2021 | FEB | Yes | Line to Line | 1603301 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3157 | 20210213 | 431 | 1254144 | 655 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2620 | 39.6475 | -123.7736 | EOL | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0025298 | OH | Sus | 0 | No | 2021 | FEB | Yes | Line to Line | 1605012 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 6307 | 20210220 | 814 | 1258369 | 388 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1552 | 39.3532 | -123.7908 | CGC 214940961852 | Clear-32-90 F | Conductor, Overhead | On Ground | 21-0027627 | OH | Sus | 0 | No | 2021 | FEB | Yes | Force Out | 1606502 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1899 | 20210221 | 718 | 1258834 | 341 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 3751 | 40.5113 | -124.1605 | 15 SPANS LD SIDE OF FUCO 1899 | Clear-32-90F | Conductor, Overhead | On Ground | 21-0027821 | OH | Sus | 0 | No | 2021 | FEB | Yes | Line to Line | 1606634 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 262813 | 20210301 | 2129 | 1265091 | 848 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 9328 | 38.8138 | -123.5702 | SAP ID 102199847 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0030979 | OH | Sus | 31531830 | No | 2021 | MAR | Yes | Line to Line | 1608805 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | OCB | 1101/2 | 20210305 | 953 | 1269008 | 320 | Distribution Circuit | Vegetation | Tree - branch fell on line | 784 | 151566 | 40.9479 | -123.6402 | FUCO 5389 & FUCO 95035 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0032600 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1609842 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1101 | 192461101 | FUSE | 4593 | 20210306 | 1202 | 1271960 | 576 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4032 | 40.4831 | -123.6368 | WIRE DOWN 14 SPANS LD SIDE OF 1455 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0033093 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1610147 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 746077 | 20210306 | 1640 | 1272353 | 374 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 25159 | 38.6832 | -123.4251 | WIRE DOWN 1 SPA LD SIDE OF 1407 (MAIN LINE) | Clear-32-90 F | Conductor, Overhead | On Ground | 21-0033088 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1610144 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 37506 | 20210308 | 2003 | 1274589 | 893 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 44179 | 39.4823 | -123.3615 | 1 NW/OF 925741 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0033649 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1610520 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 2853 | 20210309 | 833 | 1274917 | 703 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 18380 | 39.4684 | -123.3974 | HARD TAP SS TO CGC# 216002766431 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0033858 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Line | 1610687 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | RECLOSER | 34008 | 20210310 | 224 | 1276649 | 691 | Distribution Circuit | Vegetation | Tree - branch fell on line | 571 | 85025 | 39.4366 | -123.3892 | 2 SPANS SS OF 6095 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0034287 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1610822 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3051 | 20210315 | 528 | 1282474 | 335 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 9380 | 39.2725 | -123.6974 | 11 SPANS LD SIDE OF FUCO 3051 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0036379 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Line | 1612073 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1101 | 192461101 | OTHER | WIRE DOWN 1 SPAN LD SIDE OF 4119 | 20210315 | 202 | 1282460 | 493 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4437 | 40.4837 | -123.729 | 1 SPAN LD SIDE OF 4119 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0036356 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Line | 1612058 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARRIS-1109 | 192431109 | FUSE | 5745 | 20210315 | 158 | 1282416 | 761 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3805 | 40.771 | -124.0946 | 170 MISTY HILL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0036400 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Line | 1612080 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 4365 | 20210316 | 1358 | 1285250 | 438 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2628 | 39.9606 | -123.7701 | 5 LD SIDE OF FU 4365 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0037255 | OH | Sus | 44686261 | No | 2021 | MAR | Yes | Line to Ground | 1612663 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 94127 | 20210325 | 1254 | 1297701 | 189 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 945 | 39.2277 | -123.7425 | 1 LD SIDE OF FUSES | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0041019 | OH | Sus | 44705040 | No | 2021 | MAR | Yes | Line to Ground | 1615063 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | RECLOSER | 4814 | 20210403 | 1027 | 1306352 | 384 | Distribution Circuit | Equipment Failure/Involved | Overhead | 78 | 24685 | 40.482 | -124.229 | 11 SPANS LD SIDE OF 1911 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0044420 | OH | Sus | 44720588 | No | 2021 | APR | Yes | Line to Ground | 1617372 | CSO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | OTHER | WIRE DOWN 4 SPANS E/O CGC# 215047559515 | 20210404 | 1121 | 1306701 | 518 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 1260 | 39.2883 | -123.7504 | 4 SPANS E/O CGC# 215047559515 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0044542 | OH | Sus | 31535245 | No | 2021 | APR | Yes | Open Circuit | 1617469 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 7217 | 20210425 | 127 | 1333292 | 466 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 932 | 39.5241 | -123.7609 | WIRE DOWN ACROSS HWY 1 at 7217 CUT OUT POLE TO EOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0052833 | OH | Sus | 0 | No | 2021 | APR | Yes | Line to Ground | 1622890 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 8652 | 20210425 | 425 | 1333305 | 423 | Distribution Circuit | Equipment Failure/Involved | Overhead | 264 | 109096 | 40.1069 | -123.9276 | 3RD SPAN LD SIDE OF 6469 ON MAIN LINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0052837 | OH | Sus | 0 | No | 2021 | APR | Yes | Line to Ground | 1622894 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 6637 | 20210507 | 1419 | 1343486 | 216 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 3240 | 39.3406 | -123.7661 | LAST SPAN AT EOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0058624 | OH | Sus | 0 | No | 2021 | MAY | Yes | Line to Ground | 1626645 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1965 | 20210509 | 1716 | 1344484 | 347 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 13533 | 40.1219 | -123.8338 | 9 SPANS LD SIDE OF 1965 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 21-0059019 | OH | Sus | 31539983 | No | 2021 | MAY | Yes | Line to Line | 1627011 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MENDOCINO-1101 | 42951101 | FUSE | 789577 | 20210509 | 1118 | 1344400 | 385 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2695 | 39.2688 | -123.1972 | EOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0059003 | OH | Sus | 0 | No | 2021 | MAY | Yes | Line to Ground | 1626994 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 2500 | 20210515 | 1610 | 1350224 | 263 | Distribution Circuit | Environmental/External | Lightning | 115 | 22181 | 39.4489 | -123.3133 | Espinola- Christopher: 3 spans load side SB 81535 | Lightning-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0061893 | OH | Sus | 0 | No | 2021 | MAY | Yes | Multi-Fault | 1629059 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 1457 | 20210519 | 1726 | 1353908 | 311 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2799 | 39.2195 | -123.7292 | 2 SPANS LD SIDE OF FUCO 1457 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0063577 | OH | Sus | 44810627 | No | 2021 | MAY | Yes | Line to Line | 1630380 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | RECLOSER | 47952 | 20210519 | 1458 | 1353736 | 205 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 22755 | 38.9145 | -123.6392 | 1 SPAN SOURCE SIDE OF FUCO 7527 ON MAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0063491 | OH | Sus | 44810479 | No | 2021 | MAY | Yes | Line to Line | 1630334 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MENDOCINO-1101 | 42951101 | FUSE | 93499 | 20210520 | 1357 | 1354666 | 265 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1060 | 39.265 | -123.2068 | 1 SPAN LD SIDE OF FUCO 93499 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0063981 | OH | Sus | 0 | No | 2021 | MAY | Yes | Line to Ground | 1630653 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | JUMPER | 5087 | 20210602 | 740 | 1363831 | 383 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 3470 | 39.2883 | -123.7501 | 4227 COFFEE LN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0068733 | OH | Sus | 31541843 | No | 2021 | JUN | Yes | Line to Ground | 1633809 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 2557 | 20210602 | 1956 | 1364373 | 1343 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8058 | 39.5922 | -123.4518 | 2-4 SPANS LD SIDE OF 2557 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0069186 | OH | Sus | 31541952 | No | 2021 | JUN | Yes | Line to Line | 1634038 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER | 95324 | 20210607 | 1104 | 1367544 | 211 | Distribution Circuit | Vegetation | Tree - fell into line | 222 | 11352 | 40.284 | -123.8719 | 10 SPANS S.S. OF 1595 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0070856 | OH | Sus | 31542702 | No | 2021 | JUN | Yes | Line to Line | 1635201 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | RECLOSER | 95294 | 20210609 | 1703 | 1369679 | 370 | Distribution Circuit | Vegetation | Tree - fell into line | 204 | 69155 | 39.5753 | -123.7698 | 1 SPAN S.S OF FUCO 3173 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0072299 | OH | Sus | 31542976 | No | 2021 | JUN | Yes | Line to Line | 1636001 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | EEL RIVER-1102 | 192381102 | FUSE | 1899 | 20210611 | 952 | 1370736 | 593 | Distribution Circuit | 3rd Party | Vehicle | 11 | 6523 | 40.5113 | -124.1605 | 1/2 MI LD SIDE OF FU 1899 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0073175 | OH | Sus | 0 | No | 2021 | JUN | Yes | Line to Ground | 1636501 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | OCB | 1101/2 | 20210612 | 121 | 1371318 | 697 | Distribution Circuit | Vegetation | Tree - fell into line | 907 | 124819 | 38.9122 | -123.6787 | MTR# 1010310876 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0073406 | OH | Sus | 31542998 | No | 2021 | JUN | Yes | Line to Ground | 1636618 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 4451 | 20210614 | 44 | 1372332 | 975 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 6825 | 38.7903 | -123.5105 | Thorpe- Tim/2094: 3 LS O 4451 Fucos | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0073732 | OH | Sus | 44856482 | No | 2021 | JUN | Yes | Line to Line | 1636958 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARRIS-1109 | 192431109 | FUSE | 861 | 20210614 | 1245 | 1372983 | 599 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 1047 | 40.7682 | -124.1164 | CGC# 114140552885 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0074060 | OH | Sus | 31543479 | No | 2021 | JUN | Yes | Line to Line | 1637159 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 4423 | 20210626 | 1541 | 1385798 | 126 | Distribution Circuit | Vegetation | Tree - branch fell on line | 111 | 8766 | 38.8941 | -123.6231 | 1 SPAN SOURCE SIDE OF FUCO 8201 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0080332 | OH | Sus | 0 | No | 2021 | JUN | Yes | Line to Ground | 1641996 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1102 | 43311102 | JUMPER | TREE THROUGH LINE @ CGC 218097746554 | 20210630 | 352 | 1388521 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 326 | 41838 | 38.943 | -122.6698 | CGC218097746554 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 21-0081927 | OH | Sus | 31544949 | No | 2021 | JUN | Yes | Open Circuit | 1643237 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 5255 | 20210630 | 2334 | 1389417 | 897 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4296 | 39.677 | -123.4903 | 2 SPANS LD SIDE OF FUCO 5505 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0082945 | OH | Sus | 0 | No | 2021 | JUN | Yes | Line to Ground | 1644057 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1106 | 43351106 | JUMPER | WIRE DOWN | 20210713 | 140 | 1402528 | 601 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 5906 | 39.0377 | -122.743 | 3 SPANS LD SIDE OF FUCO 405 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0088576 | OH | Sus | 31546064 | No | 2021 | JUL | Yes | Line to Ground | 1647706 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | OTHER | WIRE DOWN 2 LD SIDE CGC 215279544420 | 20210719 | 1813 | 1408428 | 1031 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4037 | 38.8738 | -123.6576 | 2 SPANS LD SIDE OF CGC 215279544420 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0092024 | OH | Sus | 44913403 | No | 2021 | JUL | Yes | Line to Ground | 1649724 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 5209 | 20210721 | 308 | 1409486 | 725 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 24650 | 41.0953 | -123.6952 | 1 POLE SS OF TX#115341164674 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0092662 | OH | Sus | 0 | No | 2021 | JUL | Yes | Line to Ground | 1650103 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARRIS-1109 | 192431109 | FUSE | 893 | 20210727 | 155 | 1415432 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 10500 | 40.7585 | -124.0501 | AT FUCO 0899 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0095306 | OH | Sus | 44921822 | No | 2021 | JUL | Yes | Line to Ground | 1651953 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 1513 | 20210824 | 1051 | 1451640 | 149 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 5662 | 39.4165 | -123.7889 | 9 POLES LD SIDE OF FUCO 1513 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0108643 | OH | Sus | 0 | No | 2021 | AUG | Yes | Multi-Fault | 1660468 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 3295 | 20210826 | 2014 | 1454941 | 827 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 10751 | 39.4431 | -123.7698 | 5 POLES N/W OF 3295 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0109915 | OH | Sus | 0 | No | 2021 | AUG | Yes | Line to Line | 1661305 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 79817 | 20210831 | 1735 | 1459389 | 321 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 15087 | 39.2079 | -123.7281 | 32700 MIDDLE RIDGE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0111833 | OH | Sus | 0 | No | 2021 | AUG | Yes | Line to Ground | 1662590 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 2343 | 20210903 | 656 | 1461358 | 457 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 7051 | 38.8617 | -122.7189 | 1 SPAN LD SIDE OF FUCO 2343 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0113130 | OH | Sus | 0 | No | 2021 | SEP | Yes | Line to Ground | 1663235 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1770 | 20210916 | 700 | 1472880 | 503 | Distribution Circuit | Vegetation | Tree - fell into line | 372 | 71973 | 39.9152 | -123.7633 | ON MAINLINE at FUCO 1709 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0118196 | OH | Sus | 0 | No | 2021 | SEP | Yes | Three Phase Fault | 1666144 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UKIAH-1114 | 42771114 | FUSE | 3363 | 20210918 | 607 | 1474301 | 324 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 29160 | 39.0913 | -123.2212 | TREE FEEL 5 SPANS LD SIDE OF 3363. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0119242 | OH | Sus | 0 | No | 2021 | SEP | Yes | Line to Line | 1666734 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3137 | 20210919 | 931 | 1475536 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 155 | 51460 | 39.2609 | -123.7281 | 41151 AIRPORT RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0119566 | OH | Sus | 0 | No | 2021 | SEP | Yes | Line to Line | 1667050 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | REDBUD-1101 | 43191101 | FUSE | 1139 | 20210919 | 727 | 1475426 | 827 | Distribution Circuit | 3rd Party | Vehicle | 26 | 21502 | 39.0281 | -122.6675 | 6 SPANS LD SIE OF 1139 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0119552 | OH | Sus | 0 | No | 2021 | SEP | Yes | Three Phase Fault | 1667037 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 1510 | 20210925 | 257 | 1480031 | 710 | Distribution Circuit | 3rd Party | Vehicle | 834 | 592140 | 40.1222 | -123.835 | 3RD POLE LD SIDE OF R373 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0122272 | OH | Sus | 0 | No | 2021 | SEP | Yes | Line to Ground | 1668576 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LUCERNE-1106 | 43351106 | FUSE | 94963 | 20210929 | 1114 | 1483334 | 203 | Distribution Circuit | 3rd Party | Vehicle | 15 | 3045 | 39.0429 | -122.7694 | MTR# 1006242128 | Clear-32-90 F | Pole-Wood | Broken, wire on object | 21-0123792 | OH | Sus | 31553134 | No | 2021 | SEP | Yes | Force Out | 1669685 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 3395 | 20211019 | 1600 | 1502189 | 370 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 740 | 39.1334 | -123.641 | 2 SPANS LD SIDE 3395 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0133305 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1675772 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | OTHER | WIRE DOWN 1 SPAN LD SIDE 83235 | 20211019 | 1806 | 1502285 | 154 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 154 | 39.3874 | -123.7742 | 1 SPAN LD SIDE 83235 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0133326 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1675782 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 6671 | 20211019 | 2155 | 1502457 | 845 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 17745 | 38.9137 | -123.6803 | IN THE SPAN SOURCE SIDE OF 3761 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0133380 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1675809 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 55437 | 20211019 | 2005 | 1502390 | 1445 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1445 | 40.917 | -123.8301 | LD SIDE OF FUCO 55437 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0133376 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1675806 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 8652 | 20211021 | 1313 | 1504692 | 448 | Distribution Circuit | Vegetation | Tree - fell into line | 253 | 67969 | 40.1069 | -123.9276 | ALLEN- DERRICK /K1130-T1243: Sunny Valley Ln | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0134549 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Line | 1676450 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER | 7514 | 20211021 | 757 | 1504102 | 838 | Distribution Circuit | Vegetation | Tree - fell into line | 535 | 79054 | 40.8894 | -123.5579 | 1/P/SS OF MTR 115828856814 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0134224 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1676288 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER | 3002 | 20211027 | 1006 | 1522911 | 451 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 446 | 83023 | 39.2855 | -123.7929 | 8001 HWY 1- LITTLE RIVER | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0138679 | OH | Sus | 0 | No | 2021 | OCT | Yes | Multi-Fault | 1679561 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 3304 | 20211104 | 2049 | 1535216 | 962 | Distribution Circuit | Vegetation | Tree - fell into line | 670 | 644540 | 41.1057 | -123.6878 | 40 POLES LD SIDE OF LR 3304 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0142568 | OH | Sus | 31577713 | No | 2021 | NOV | Yes | Line to Ground | 1681880 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 6084 | 20211108 | 2357 | 1538220 | 721 | Distribution Circuit | Vegetation | Tree - branch fell on line | 132 | 95172 | 40.0618 | -123.9616 | 4 SPAS LD SIDE OF 4373 ON MAIN LINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0143645 | OH | Sus | 0 | No | 2021 | NOV | Yes | Line to Ground | 1682882 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 2499 | 20211109 | 1047 | 1538755 | 602 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 15 | 9030 | 39.6678 | -123.5142 | 10 SPANS LD SIDE OF 2499 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0144031 | OH | Sus | 0 | No | 2021 | NOV | Yes | Three Phase Fault | 1683100 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | TRANSFORMER | 215746052495 | 20211113 | 1303 | 1543095 | 441 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 577 | 39.099 | -123.4993 | 1 SPAN LD SIDE OF METER# 1009649801 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0145326 | OH | Sus | 0 | No | 2021 | NOV | Yes | Line to Ground | 1684072 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1122 | 192021122 | FUSE | 4571 | 20211115 | 1857 | 1545593 | 256 | Distribution Circuit | Vegetation | Tree - branch fell on line | 131 | 33536 | 40.7929 | -124.0234 | at 5287 FUCO ON MAIN LINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0145891 | OH | Sus | 45067041 | No | 2021 | NOV | Yes | Line to Ground | 1684638 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HIGHLANDS-1103 | 43361103 | FUSE | 95777 | 20211120 | 634 | 1550602 | 570 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1710 | 38.9301 | -122.6093 | 4 SPANS OF WIRE DOWN & CORNER POLE BROKEN LD SIDE OF FUCO 95777 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0148956 | OH | Sus | 0 | No | 2021 | NOV | Yes | Force Out | 1686851 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3961 | 20211122 | 743 | 1552777 | 321 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 4173 | 39.3595 | -123.6472 | CGC 215444061815 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0149361 | OH | Sus | 45072954 | No | 2021 | NOV | Yes | Line to Ground | 1687312 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | RECLOSER | 1308 | 20211209 | 1509 | 1563111 | 345 | Distribution Circuit | Vegetation | Tree - branch fell on line | 296 | 85194 | 39.1859 | -123.5798 | 1/SPAN/LD SIDE OF 9131 ON MAINLINE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0156368 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1693015 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 6645 | 20211212 | 427 | 1564983 | 367 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4404 | 39.2439 | -123.7705 | 1 SPAN LD SIDE OF FUCO 6645 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 21-0156765 | OH | Sus | 31580600 | No | 2021 | DEC | Yes | Line to Ground | 1693629 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | OTHER | WIRE DOWN 3 SPANS S/SIDE OF CGC# 217986243443 | 20211216 | 1114 | 1574701 | 162 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 162 | 38.8567 | -122.7067 | WOODARD-KYLE/T2565: 13044 loch lomond rd | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158880 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1695911 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | RECLOSER | 3700 | 20211217 | 714 | 1575483 | 441 | Distribution Circuit | Equipment Failure/Involved | Overhead | 248 | 97560 | 38.9971 | -123.3571 | Welsh- Tyler 707-806-9777: SAP ID 102214543 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0159290 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1696347 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CARLOTTA-1121 | 192291121 | OTHER | 5429 | 20211221 | 910 | 1578518 | 230 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 690 | 40.5516 | -124.1126 | 2 SPANS LD SIDE OF 5429 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0159962 | OH | Sus | 45098781 | No | 2021 | DEC | Yes | Force Out | 1697316 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 6423 | 20211228 | 839 | 1586571 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 16716 | 39.4878 | -123.4249 | CGC #215949766288 | Clear-32-90F | Conductor, Overhead | On Ground | 21-0161317 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1698944 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 3805 | 20211228 | 2207 | 1587620 | 953 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3812 | 39.4604 | -123.2679 | 3 SPANS LD-SIDE OF FU 3805 | Clear-32-90F | Conductor, Overhead | On Ground | 21-0161507 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1699268 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | FUSE | 4151 | 20220102 | 831 | 1592423 | 1790 | Distribution Circuit | Environmental/External | Ice or snow | 6 | 10740 | 40.4787 | -123.658 | LOADSIDE FUCO 4151 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0005184 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Ground | 1700375 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3751 | 20220103 | 1304 | 1593616 | 165 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 1980 | 40.2212 | -123.8262 | CGC 114890632708 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0005565 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Line | 1700681 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 7893 | 20220103 | 2023 | 1594300 | 1282 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 9488 | 38.8777 | -122.7191 | CGC 217985844240 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0005773 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Ground | 1700821 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | RECLOSER | 572 | 20220103 | 1507 | 1593823 | 317 | Distribution Circuit | Vegetation | Tree - fell into line | 255 | 61433 | 39.6732 | -123.506 | BARRINGTON- SORREL/T1102-K3455: 3 spans SS of 8021 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0005608 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Ground | 1700698 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LOW GAP-1101 | 192411101 | FUSE | 4079 | 20220104 | 1132 | 1594868 | 358 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 358 | 40.4931 | -123.5975 | 10 AND 11 SPANS LD SIDE OF 4079 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0005983 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Line | 1700931 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1102 | 42661102 | FUSE | 4307 | 20220106 | 642 | 1596346 | 419 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2933 | 39.4113 | -123.3636 | FUCO 4307 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 22-0006680 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Ground | 1701251 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1102 | 192171102 | FUSE | 3217 | 20220111 | 934 | 1600054 | 414 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1656 | 40.9695 | -123.6421 | LD SIDE 3217 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0008491 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Line | 1702072 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 1815 | 20220123 | 1351 | 1609916 | 524 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 15720 | 39.8679 | -123.7167 | 3/LD SIDE OF 1815 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0013222 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Line | 1704552 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2531 | 20220123 | 1414 | 1609995 | 166 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 332 | 40.151 | -124.029 | 4/LD SIDE OF 2531 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0013207 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Line | 1704539 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 3259 | 20220125 | 1223 | 1611966 | 198 | Distribution Circuit | Equipment Failure/Involved | Overhead | 82 | 16236 | 38.8796 | -122.7334 | 4/S/LD SIDE 3259 | Clear-32-90 F | Insulator | Broken, wire on object | 22-0014109 | OH | Sus | 0 | No | 2022 | JAN | Yes | Force Out | 1705050 | INS | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UKIAH-1114 | 42771114 | JUMPER | WIRE DOWN 7/S/SS 2159 | 20220203 | 1024 | 1620289 | 224 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1008 | 96634 | 38.997 | -123.1131 | Dickson- Josh 707 293-6004: 7 SPANS SSD OF SW 2159 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0003295 | OH | Sus | 35219879 | No | 2022 | FEB | Yes | Line to Ground | 1707357 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | OCB | 1101/2 | 20220209 | 1108 | 1624019 | 519 | Distribution Circuit | 3rd Party | Vehicle | 1268 | 109871 | 40.1033 | -123.7926 | 54139 C/O Hwy 271 & County Road 442B- PIERCY | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0020273 | OH | Sus | 0 | No | 2022 | FEB | Yes | Three Phase Fault | 1708755 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | FUSE | 2415 | 20220209 | 1231 | 1624139 | 319 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 638 | 39.4858 | -123.352 | 11 SPANS FROM 2415 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0020467 | OH | Sus | 0 | No | 2022 | FEB | Yes | Line to Ground | 1708812 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1770 | 20220219 | 335 | 1632262 | 504 | Distribution Circuit | Vegetation | Tree - fell into line | 340 | 20628 | 39.9152 | -123.7633 | 3 SPANS LD SIDE 8053. 2 PHASES DOWN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0024396 | OH | Sus | 45183120 | No | 2022 | FEB | Yes | Three Phase Fault | 1711285 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1122 | 192321122 | OCB | 1122/2 | 20220301 | 1107 | 1639916 | 299 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 30199 | 40.2139 | -123.5966 | 1 SPAN LD SIDE OF FUCO 1841 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0028048 | OH | Sus | 31596455 | No | 2022 | MAR | Yes | Line to Line | 1713707 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 7737 | 20220304 | 1322 | 1642273 | 334 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2004 | 39.2926 | -123.7714 | 2 SPANS LD SIDE OF 7737 at LINE & BUCK TO THE EAST | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0030035 | OH | Sus | 0 | No | 2022 | MAR | Yes | Line to Ground | 1714655 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER | 75382 | 20220304 | 1910 | 1642664 | 1006 | Distribution Circuit | Vegetation | Tree - fell into line | 378 | 87174 | 38.9069 | -122.6736 | 7 SPANS LD SIDE OF FUSE 607 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0030202 | OH | Sus | 0 | No | 2022 | MAR | Yes | Line to Ground | 1714745 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | RECLOSER | 3700 | 20220305 | 618 | 1642834 | 325 | Distribution Circuit | Equipment Failure/Involved | Overhead | 248 | 80600 | 38.9971 | -123.3571 | BARRINGTON- SORREL/T1102-K3455: 3 spans s/o 66101 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0030255 | OH | Sus | 0 | No | 2022 | MAR | Yes | Multi-Fault | 1714797 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | OTHER | WIRE DOWN 1 WEST OF 3099 TWD CGC 115558557795 | 20220319 | 2015 | 1651829 | 484 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 14784 | 40.9084 | -123.6074 | 1 WEST OF 3099 TWD CGC 115558557795 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0036042 | OH | Sus | 31597866 | No | 2022 | MAR | Yes | Line to Ground | 1718384 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 1985 | 20220327 | 1157 | 1656708 | 563 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2252 | 39.3514 | -123.3215 | 18581 SHAFFER RANCH RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0039005 | OH | Sus | 31599683 | No | 2022 | MAR | Yes | Line to Line | 1720346 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLOW CREEK-1101 | 192171101 | FUSE | 55437 | 20220328 | 1110 | 1658042 | 871 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1 | 871 | 40.917 | -123.8301 | 1 SPAN LD SIDE OF 55437 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0039441 | OH | Sus | 0 | No | 2022 | MAR | Yes | Line to Line | 1720683 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 4599 | 20220331 | 1457 | 1660573 | 227 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 1589 | 40.2378 | -123.8333 | 6 SPANS LD SIDE OF 4599 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0041370 | OH | Sus | 0 | No | 2022 | MAR | Yes | Line to Line | 1721783 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | RECLOSER | 3700 | 20220409 | 634 | 1666544 | 422 | Distribution Circuit | Vegetation | Tree - fell into line | 247 | 92930 | 38.9971 | -123.3571 | BETWEEN FU 94197 & 6215 ON MAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0044808 | OH | Sus | 45247393 | No | 2022 | APR | Yes | Line to Ground | 1723988 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | FUSE | 7017 | 20220409 | 1208 | 1666824 | 288 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 4320 | 40.4359 | -123.9971 | 6 SPANS SS OF 3941 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0044932 | OH | Sus | 31600551 | No | 2022 | APR | Yes | Line to Line | 1724105 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER | 952 | 20220411 | 1429 | 1669056 | 346 | Distribution Circuit | Vegetation | Tree - fell into line | 281 | 20262 | 39.2695 | -123.7813 | 2 SS/OF 717215 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0045588 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Ground | 1724641 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1102 | 192461102 | OTHER | WIRE DOWN FEEDING CGC 114849441666 | 20220411 | 1606 | 1669515 | 168 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 2221 | 40.4618 | -123.8526 | HARD TAP FEEDING CGC 114849441666 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0045754 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Ground | 1724758 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UKIAH-1113 | 42771113 | FUSE | 3425 | 20220411 | 1317 | 1668815 | 239 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 2390 | 39.1307 | -123.2135 | 5/LD SIDE OF 3425 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0045562 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Ground | 1724630 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CALPELLA-1101 | 43411101 | FUSE | 1055 | 20220414 | 800 | 1672222 | 344 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 7224 | 39.2556 | -123.1482 | 10 SPANS LD SIDE OF 1055 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0048025 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Ground | 1726571 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | OCB | 1141/2 | 20220416 | 2216 | 1675037 | 348 | Distribution Circuit | Vegetation | Tree - fell into line | 384 | 71353 | 40.2866 | -123.8369 | 1/SP/SS OF 6807 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0050669 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Ground | 1728752 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | SWITCH | 5151 | 20220416 | 1033 | 1674310 | 480 | Distribution Circuit | Vegetation | Tree - bark fell into line | 2 | 960 | 38.7042 | -123.4277 | 1 SPAN W/OF 1309 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0050566 | OH | Sus | 45258400 | No | 2022 | APR | Yes | Open Circuit | 1728670 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | OTHER | WIRE DOWN LD SIDE 37410 | 20220418 | 1321 | 1675867 | 748 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 23415 | 40.3314 | -123.9185 | 6/SP LD SIDE OF 37410 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0051119 | OH | Sus | 45260269 | No | 2022 | APR | Yes | Line to Ground | 1729079 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5527 | 20220420 | 1132 | 1677327 | 293 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 4688 | 39.3321 | -123.8056 | 1 SPAN LD SIDE 5527 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0052017 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Ground | 1729673 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | RECLOSER | 4622 | 20220420 | 2119 | 1677831 | 455 | Distribution Circuit | Vegetation | Tree - fell into line | 377 | 165588 | 39.5158 | -123.7632 | 27730 NORTH HWY 1- FORT BRAGG | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0052242 | OH | Sus | 31601504 | No | 2022 | APR | Yes | Multi-Fault | 1729756 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 461681 | 20220420 | 2342 | 1677858 | 692 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 18684 | 40.2217 | -123.7967 | 8 SPANS LD SIDE OF 461681 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0052354 | OH | Sus | 45262415 | No | 2022 | APR | Yes | Line to Ground | 1729814 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 249707 | 20220425 | 1704 | 1681281 | 271 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 271 | 40.062 | -123.8391 | CGC# 114861726930 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0054266 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Ground | 1730984 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4155 | 20220427 | 1110 | 1682787 | 246 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 246 | 38.7229 | -123.3438 | 3 LD SIDE OF 4155 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0055114 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Line | 1731594 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 9289 | 20220427 | 439 | 1682231 | 341 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 18414 | 38.8137 | -123.5783 | 3 SPANS LD SIDE OF FUSES 9289 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0054865 | OH | Sus | 45269000 | No | 2022 | APR | Yes | Line to Ground | 1731379 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1102 | 43311102 | RECLOSER | 716 | 20220427 | 1229 | 1682710 | 511 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 775 | 106194 | 38.9241 | -122.7205 | 15 LD SIDE OF 6121 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 22-0055110 | OH | Sus | 31602040 | No | 2022 | APR | Yes | Multi-Fault | 1731589 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 908370 | 20220502 | 1207 | 1686511 | 364 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 8072 | 39.2262 | -123.748 | 3721 ALBION RIDGE RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0056918 | OH | Sus | 45275104 | No | 2022 | MAY | Yes | Line to Ground | 1732955 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 2807 | 20220502 | 1051 | 1686581 | 764 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 764 | 39.7043 | -123.3905 | 1 SPAN FROM 2807 1 PHASE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0056955 | OH | Sus | 0 | No | 2022 | MAY | Yes | Line to Line | 1732967 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | FUSE | 4681 | 20220506 | 321 | 1689524 | 759 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 8349 | 41.0697 | -123.6807 | CGC 115369963826 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0058751 | OH | Sus | 0 | No | 2022 | MAY | Yes | Line to Line | 1734026 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1102 | 192171102 | JUMPER | ENERGIZED WIRE DOWN | 20220506 | 1615 | 1690138 | 188 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 3024 | 40.9889 | -123.6367 | HIGHTOWER- WALT: HWY 299 11 polea load of 3209 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0059149 | OH | Sus | 45283740 | No | 2022 | MAY | Yes | Line to Ground | 1734265 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER | TEMP LR 1142/2 | 20220507 | 1038 | 1690637 | 461 | Distribution Circuit | Vegetation | Tree - fell into line | 1192 | 247737 | 40.324 | -123.9223 | 9 SPANS S/S OF 1595 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0059288 | OH | Sus | 0 | No | 2022 | MAY | Yes | Line to Ground | 1734422 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 1697 | 20220511 | 1109 | 1694108 | 917 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 3 | 2751 | 40.1887 | -123.4867 | 6 POLES LD SIDE OF FUCO 1697 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0060918 | OH | Sus | 0 | No | 2022 | MAY | Yes | Line to Ground | 1735534 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | RECLOSER | 1308 | 20220511 | 1659 | 1694179 | 381 | Distribution Circuit | Vegetation | Tree - fell into line | 296 | 96162 | 39.1859 | -123.5798 | FIRST SPAN LD SIDE OF REG 6173 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0060947 | OH | Sus | 0 | No | 2022 | MAY | Yes | Line to Ground | 1735546 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 4451 | 20220518 | 1448 | 1702229 | 402 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 2814 | 38.7903 | -123.5105 | 7 SPANS LD SIDE OF 4451 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0063671 | OH | Sus | 0 | No | 2022 | MAY | Yes | Line to Ground | 1737419 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1787 | 20220519 | 1247 | 1704571 | 643 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 4272 | 40.011 | -123.9299 | CGC 114597024730 POLE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0064141 | OH | Sus | 0 | No | 2022 | MAY | Yes | Line to Ground | 1737690 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1965 | 20220519 | 1614 | 1704865 | 559 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 8374 | 40.1219 | -123.8338 | 520 EEL RIVER LN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0064202 | OH | Sus | 45302836 | No | 2022 | MAY | Yes | Line to Ground | 1737709 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 3587 | 20220522 | 1723 | 1707432 | 794 | Distribution Circuit | 3rd Party | Vehicle | 54 | 42876 | 38.8764 | -122.7662 | 1 SPAN S/S FUCO 7769 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0064995 | OH | Sus | 0 | No | 2022 | MAY | Yes | Line to Line | 1738369 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | OTHER | 1775 | 20220529 | 1729 | 1713754 | 456 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 5481 | 39.7204 | -123.8049 | 3/S/LD SIDE 2061 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0067992 | OH | Sus | 0 | No | 2022 | MAY | Yes | Open Circuit | 1740296 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 3775 | 20220530 | 628 | 1713861 | 258 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 2838 | 40.227 | -123.789 | ALLEN- DERRICK /K1130-T1243: Hodges Rd | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0068027 | OH | Sus | 45322555 | No | 2022 | MAY | Yes | Line to Ground | 1740332 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | OTHER | 8573 | 20220603 | 147 | 1717082 | 343 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 4459 | 39.4205 | -123.7775 | 1/S/LD SIDE 8573 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0069657 | OH | Sus | 45327250 | No | 2022 | JUN | Yes | Open Circuit | 1741331 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 3304 | 20220607 | 1358 | 1721618 | 589 | Distribution Circuit | Vegetation | Tree - fell into line | 672 | 395808 | 41.1057 | -123.6878 | 41 LD SIDE OF 3304 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0071156 | OH | Sus | 45331639 | No | 2022 | JUN | Yes | Line to Line | 1742561 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3283 | 20220613 | 1504 | 1730386 | 159 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 1113 | 39.3121 | -123.7827 | 44061 LITTLE LAKE RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0073808 | OH | Sus | 45342356 | No | 2022 | JUN | Yes | Line to Line | 1744319 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3941 | 20220613 | 818 | 1729848 | 422 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 14790 | 39.3929 | -123.7712 | 1 SPAN FROM LINE & BUCK TO S- E TWD CGC 215008463598 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0073587 | OH | Sus | 45342104 | No | 2022 | JUN | Yes | Line to Line | 1744212 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER | 3902 | 20220613 | 1653 | 1730482 | 441 | Distribution Circuit | Equipment Failure/Involved | Overhead | 575 | 117227 | 40.3429 | -123.9164 | ALLEN- DERRICK /K1130-T1243: 2403 Elk Creek Rd | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0073831 | OH | Sus | 45342491 | No | 2022 | JUN | Yes | Line to Ground | 1744329 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1102 | 43311102 | RECLOSER | 64664 | 20220705 | 1258 | 1749333 | 279 | Distribution Circuit | Vegetation | Tree - fell into line | 507 | 74673 | 38.9433 | -122.8017 | 14 SPANS LD SIDE OF 86749 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0081891 | OH | Sus | 45363752 | No | 2022 | JUL | Yes | Line to Ground | 1750022 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3945 | 20220707 | 1746 | 1750931 | 411 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 6165 | 39.2891 | -123.7942 | 9300 N HWY 1 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0082933 | OH | Sus | 45367614 | No | 2022 | JUL | Yes | Line to Ground | 1750507 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER | 532 | 20220709 | 2227 | 1752341 | 704 | Distribution Circuit | Vegetation | Tree - fell into line | 373 | 65885 | 38.8576 | -122.722 | 2 SPANS LD SIDE OF FUCO 4213 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0083601 | OH | Sus | 31608340 | No | 2022 | JUL | Yes | Line to Ground | 1750919 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CALPELLA-1101 | 43411101 | RECLOSER | 542 | 20220712 | 248 | 1754026 | 471 | Distribution Circuit | Vegetation | Tree - branch fell on line | 391 | 184161 | 39.2357 | -123.1786 | Welsh- Tyler 707-806-9777: 3460 Black Bart tr | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0084169 | OH | Sus | 0 | No | 2022 | JUL | Yes | Line to Ground | 1751324 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 1750 | 20220724 | 1532 | 1764543 | 643 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 18764 | 40.0847 | -123.808 | 4 SPANS LD SIDE OF 1785 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0089171 | OH | Sus | 0 | No | 2022 | JUL | Yes | Line to Line | 1754702 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | OTHER | WIRE DOWN 1 LD SIDE 7711 ON MAIN LINE | 20220726 | 1450 | 1766100 | 358 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 281 | 38424 | 39.2684 | -123.7027 | PARDINI- JAKE: 39900 airport rd | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0089997 | OH | Sus | 31610332 | No | 2022 | JUL | Yes | Line to Ground | 1755292 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 8279 | 20220804 | 1003 | 1773131 | 404 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 8888 | 40.0887 | -123.8094 | CURNOW- RAY/K1616-T1270: Old bricland | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0093695 | OH | Sus | 0 | No | 2022 | AUG | Yes | Multi-Fault | 1757656 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | RECLOSER | 3700 | 20220822 | 1523 | 1787468 | 354 | Distribution Circuit | Vegetation | Tree - fell into line | 247 | 34639 | 38.9971 | -123.3571 | WIRE DOWN BETWEEN 216501545420 AND 216500545435 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0100598 | OH | Sus | 0 | No | 2022 | AUG | Yes | Line to Line | 1762280 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | OTHER | WIRE DOWN @ CGC 115751871390 | 20220826 | 1643 | 1792479 | 638 | Distribution Circuit | Vegetation | Tree - fell into line | 488 | 53300 | 41.2853 | -123.5467 | CGC 115751871390 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0102565 | OH | Sus | 31614586 | No | 2022 | AUG | Yes | Open Circuit | 1763608 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8971 | 20220829 | 435 | 1793774 | 526 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 526 | 39.658 | -123.7833 | SAP ID 102308461 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0102915 | OH | Sus | 0 | No | 2022 | AUG | Yes | Line to Line | 1763946 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3907 | 20220831 | 549 | 1795415 | 516 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3612 | 39.6793 | -123.7876 | 1ST SPAN GOING E/OF 3907 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0103872 | OH | Sus | 0 | No | 2022 | AUG | Yes | Line to Ground | 1764552 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | OTHER | WIRE DOWN 6 SPANS LD SIDE 3965 | 20220903 | 1438 | 1798437 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 232 | 40.3402 | -123.8742 | 6 SPANS LD SIDE OF 3965 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0105525 | OH | Sus | 0 | No | 2022 | SEP | Yes | Line to Ground | 1765484 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER | 69032 | 20220905 | 1905 | 1800596 | 302 | Distribution Circuit | Vegetation | Tree - fell into line | 127 | 11855 | 39.2996 | -123.7895 | 43390 COMPTCHE UKIAH RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0106045 | OH | Sus | 45439018 | No | 2022 | SEP | Yes | Line to Ground | 1765890 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 3921 | 20220918 | 1638 | 1815036 | 277 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 10907 | 39.2057 | -123.7076 | MTR# 1010925048 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0111746 | OH | Sus | 0 | No | 2022 | SEP | Yes | Line to Ground | 1769778 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | OTHER | WIRE DOWN SS 7289 | 20220918 | 1159 | 1814308 | 727 | Distribution Circuit | Vegetation | Tree - branch fell on line | 633 | 172735 | 38.8147 | -123.5858 | LD SIDE 7289 ON MAIN LINE | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 22-0111628 | OH | Sus | 0 | No | 2022 | SEP | Yes | Line to Ground | 1769660 | CSO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MIDDLETOWN-1101 | 43141101 | OCB | 1101/2 | 20220919 | 1910 | 1816845 | 1113 | Distribution Circuit | Vegetation | Tree - fell into line | 2110 | 457294 | 38.7529 | -122.6079 | 10422 TWIN OAKS DR | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0112376 | OH | Sus | 0 | No | 2022 | SEP | Yes | None | 1770196 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | RECLOSER | 37426 | 20220919 | 1144 | 1816312 | 631 | Distribution Circuit | Vegetation | Tree - fell into line | 668 | 148214 | 38.9121 | -123.6808 | Thorpe- Tim/2094: Fucos 2647 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0112120 | OH | Sus | 0 | No | 2022 | SEP | Yes | Line to Line | 1770098 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | KONOCTI-1102 | 43311102 | RECLOSER | 965078 | 20221004 | 1124 | 1828438 | 234 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 1215 | 158286 | 38.93 | -122.7428 | 1/S/SS FS 410004 | Clear-32-90F | Conductor, Overhead | On Ground | 22-0117643 | OH | Sus | 0 | No | 2022 | OCT | Yes | Line to Ground | 1774014 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 1555 | 20221008 | 1341 | 1831965 | 234 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 3510 | 39.4879 | -123.7738 | 32163 TOP OF THE HILL LN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0119420 | OH | Sus | 31618013 | No | 2022 | OCT | Yes | Line to Line | 1775088 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 97300 | 20221012 | 1445 | 1835902 | 653 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 442 | 56534 | 39.9724 | -123.8009 | 2 SPANS LD SIDE OF 6467 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0120757 | OH | Sus | 31618236 | No | 2022 | OCT | Yes | Line to Ground | 1775969 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 746077 | 20221017 | 1337 | 1839110 | 152 | Distribution Circuit | Animal | Bird found | 83 | 12616 | 38.6832 | -123.4251 | Thorpe- Tim/2094: 2 l/so 634801 sbco | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0122190 | OH | Sus | 45496745 | No | 2022 | OCT | Yes | Line to Line | 1777043 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1102 | 192251102 | RECLOSER | 75970 | 20221017 | 1320 | 1839091 | 519 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 49 | 6966 | 40.471 | -124.1364 | 7863 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 22-0122160 | OH | Sus | 31618727 | No | 2022 | OCT | Yes | Line to Ground | 1777025 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 3787 | 20221022 | 1243 | 1842782 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 12128 | 40.1225 | -123.8338 | 1/S/LD SIDE 3787 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0123889 | OH | Sus | 0 | No | 2022 | OCT | Yes | Line to Line | 1778281 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | RECLOSER | 76842 | 20221026 | 1517 | 1846293 | 427 | Distribution Circuit | Vegetation | Tree - fell into line | 172 | 25046 | 38.6805 | -123.313 | 13/S/LD SIDE 4597 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0125121 | OH | Sus | 31619416 | No | 2022 | OCT | Yes | Line to Ground | 1779315 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CALPELLA-1101 | 43411101 | JUMPER | WIRE DOWN 1 S/LD SIDE C16712457675 | 20221101 | 1642 | 1850505 | 365 | Distribution Circuit | Equipment Failure/Involved | Overhead | 390 | 21438 | 39.2447 | -123.1619 | WIRE DOWN 1 S/LD SIDE CGC 216712457675 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 22-0126679 | OH | Sus | 0 | No | 2022 | NOV | Yes | Open Circuit | 1780625 | CSO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 79817 | 20221101 | 758 | 1849641 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 22560 | 39.2079 | -123.7281 | 5/P/LD SIDE 79817 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0126451 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Line | 1780518 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3111 | 20221101 | 808 | 1849675 | 403 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 45136 | 39.4901 | -123.786 | 3 SPANS LD SIDE 3111 TO WEST | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0126398 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Line | 1780467 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | OTHER | WIRE DOWN 32443 ODOM LN | 20221101 | 733 | 1849619 | 462 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4178 | 39.479 | -123.7861 | 32443 ODOM LN | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0126474 | OH | Sus | 0 | No | 2022 | NOV | Yes | Open Circuit | 1780531 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 719015 | 20221101 | 902 | 1849621 | 216 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 4536 | 39.3967 | -123.771 | 3 SPANS LD SIDE 719015 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0126401 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Ground | 1780473 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 97300 | 20221101 | 711 | 1849606 | 319 | Distribution Circuit | Vegetation | Tree - fell into line | 442 | 95319 | 39.9724 | -123.8009 | 5 SPANS SS/OF 2026 | Clear-32-90F | Conductor, Overhead | On Ground | 22-0126321 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Line | 1780370 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARRIS-1108 | 192431108 | RECLOSER | 2062 | 20221101 | 359 | 1849572 | 383 | Distribution Circuit | Vegetation | Tree - branch fell on line | 832 | 162601 | 40.757 | -124.1469 | PONNAY- ANTHONY/K1912-T1514: 6282 Hinman ln. | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0126298 | OH | Sus | 0 | No | 2022 | NOV | Yes | Multi-Fault | 1780357 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARRIS-1109 | 192431109 | FUSE | 6257 | 20221101 | 645 | 1849586 | 358 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3222 | 40.7711 | -124.0735 | 1 LD SIDE OF MTR# 1008688321 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0126387 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Line | 1780457 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | RECLOSER | 2600 | 20221101 | 819 | 1849731 | 581 | Distribution Circuit | Vegetation | Tree - fell into line | 555 | 36729 | 39.0853 | -123.4851 | 2 SPANS SS/OF 148421 FOR LR 2600/ 11 SPANS LD SIDE OF 5547 FOR LR 928 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0126352 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Line | 1780399 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | OTHER | WIRE DOWN 1/SS OF 4779 | 20221108 | 820 | 1856898 | 688 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 17122 | 39.5065 | -123.4389 | TREE 4/SS OF 7251 & WIRE DOWN 1/SS OF 4779 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0128857 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Ground | 1782090 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 1931 | 20221109 | 722 | 1858764 | 453 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4077 | 39.737 | -123.8119 | 9 POLES LD SIDE OF 1931 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0129547 | OH | Sus | 45515646 | No | 2022 | NOV | Yes | Multi-Fault | 1782572 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MIDDLETOWN-1102 | 43141102 | OTHER | WIRE DOWN SPRUCE GROVE AND HWY 29 | 20221109 | 1557 | 1859471 | 393 | Distribution Circuit | Equipment Failure/Involved | Overhead | 701 | 18869 | 38.8201 | -122.5724 | SPRUCE GROVE AND HWY 29 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 22-0129779 | OH | Sus | 45516147 | No | 2022 | NOV | Yes | Line to Ground | 1782671 | CSO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 7219 | 20221119 | 1614 | 1866151 | 1156 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1156 | 39.5262 | -123.7602 | 2 SPANS LD SIDE OF 7219 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0132861 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Line | 1784824 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER | 532 | 20221201 | 406 | 1872646 | 151 | Distribution Circuit | Vegetation | Tree - fell into line | 374 | 56474 | 38.8576 | -122.722 | 1 SP LD SD OF 532 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 22-0135385 | OH | Sus | 0 | No | 2022 | DEC | Yes | Three Phase Fault | 1786595 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE | 929 | 20221204 | 1000 | 1875785 | 357 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 2142 | 39.1763 | -122.9163 | 1 SPAN LD SIDE | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 22-0136455 | OH | Sus | 31629483 | No | 2022 | DEC | Yes | Line to Ground | 1787408 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | RECLOSER | 1298 | 20221208 | 930 | 1878813 | 457 | Distribution Circuit | Vegetation | Tree - branch fell on line | 914 | 342014 | 39.1422 | -123.7286 | Thorpe- Tim/2094: 3300 S hwy 1 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0137580 | OH | Sus | 45583456 | No | 2022 | DEC | Yes | Multi-Fault | 1788460 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 8652 | 20221209 | 1216 | 1879730 | 290 | Distribution Circuit | Vegetation | Tree - fell into line | 254 | 72788 | 40.1069 | -123.9276 | CURNOW- RAY/K1616-T1270: Briceland thorn | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0137895 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1788752 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 2307 | 20221211 | 2338 | 1886547 | 731 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 29971 | 38.9025 | -122.7556 | CGC 217863945065 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0139108 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1789921 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 586551 | 20221212 | 1120 | 1887217 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 1289 | 40.2282 | -123.7729 | FIRST SPAN LDSIDE OF 586651 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0139214 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1790075 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 2309 | 20221212 | 107 | 1886552 | 874 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 6992 | 38.8925 | -122.7399 | 1 SPAN LD SIDE OF FUSES | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0139115 | OH | Sus | 0 | No | 2022 | DEC | Yes | Open Circuit | 1789930 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 2195 | 20221212 | 140 | 1886586 | 771 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 18504 | 38.8607 | -122.7096 | 2 SPANS LD SIDE OF FUSES | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0139116 | OH | Sus | 0 | No | 2022 | DEC | Yes | Multi-Fault | 1789931 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | RECLOSER | 4300 | 20221212 | 210 | 1886572 | 811 | Distribution Circuit | Vegetation | Tree - fell into line | 750 | 491591 | 38.9109 | -122.7637 | BET 6733 & 2201 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0139117 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1789932 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | TRIP-SAVER | 4421 | 20221212 | 213 | 1887025 | 1036 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 16576 | 38.8649 | -122.7182 | LOADSIDE OF 4421 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0139172 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1790034 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 3209 | 20221222 | 1038 | 1895775 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 332 | 39.7226 | -123.8073 | 7 LD SIDE OF 3209 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0141004 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1792648 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | JUMPER | WIRE DOWN | 20221222 | 847 | 1895659 | 148 | Distribution Circuit | Equipment Failure/Involved | Overhead | 136 | 18163 | 39.413 | -123.3096 | 1/2 SPAN N/OF 5635 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 22-0140984 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1792580 | CSO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 8652 | 20221223 | 1355 | 1896467 | 403 | Distribution Circuit | Vegetation | Tree - fell into line | 254 | 100754 | 40.1069 | -123.9276 | 8 SPANS LD SIDE OF COMBOS 816641 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0141087 | OH | Sus | 0 | No | 2022 | DEC | Yes | Multi-Fault | 1792763 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | OTHER | WIRE DOWN AT 3071 ON MAINLINE | 20221226 | 2231 | 1897758 | 2626 | Distribution Circuit | Vegetation | Tree - fell into line | 144 | 137702 | 39.4055 | -123.7242 | 3071 ON MAINLINE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0141400 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793075 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER | 79628 | 20221227 | 52 | 1897853 | 1039 | Distribution Circuit | Equipment Failure/Involved | Overhead | 371 | 296429 | 39.312 | -123.786 | 44071 LITTLE LAKE RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0141408 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793083 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 3223 | 20221227 | 414 | 1898287 | 794 | Distribution Circuit | Vegetation | Tree - fell into line | 200 | 158800 | 39.4417 | -123.7791 | at SBCO 300295 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0141509 | OH | Sus | 0 | No | 2022 | DEC | Yes | Multi-Fault | 1793185 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | MENDOCINO-1101 | 42951101 | RECLOSER | 48750 | 20221227 | 302 | 1898129 | 991 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 103580 | 39.3316 | -123.2248 | SAP ID 102175645 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0141452 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793128 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1104 | 42661104 | OTHER | WIRE DOWN 7 LD SIDE OF 1429 | 20221227 | 301 | 1898125 | 617 | Distribution Circuit | Vegetation | Tree - fell into line | 121 | 74215 | 39.3565 | -123.3327 | 7/LD SIDE OF 1429 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0141527 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793202 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ARCATA-1121 | 192021121 | FUSE | 1269 | 20221228 | 353 | 1900042 | 528 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 7392 | 40.8153 | -123.9938 | 2 SPAN LD SIDE OF FUCO 1255 ON MAIN LINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0141884 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793585 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 3771 | 20221228 | 1336 | 1900517 | 357 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2499 | 40.2417 | -123.8335 | 1/LD SIDE OF 3771 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0141956 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1793688 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 37506 | 20221229 | 553 | 1900885 | 353 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 18733 | 39.4823 | -123.3615 | MAINLINE SPAN NORTH OF 92673 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142022 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793759 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | TRANSFORMER | 214971064660 | 20221230 | 846 | 1901888 | 436 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 20412 | 39.428 | -123.78 | PARDINI- JAKE: 20031 Hanson rd | Clear-32-90F | Transformer (OH) | Broken, wire on ground | 22-0142180 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793961 | TXO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 6084 | 20221230 | 1023 | 1902002 | 100 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 4437 | 40.0618 | -123.9616 | CGC 114557125724 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142189 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793972 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | FUSE | 4475 | 20221230 | 714 | 1901913 | 611 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 8554 | 38.8216 | -123.6032 | 4 LD SIDE OF 4475 | Clear-32-90F | Conductor, Overhead | On Ground | 22-0142201 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793985 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | REDBUD-1102 | 43191102 | RECLOSER | 922 | 20221230 | 1336 | 1902188 | 408 | Distribution Circuit | Equipment Failure/Involved | Overhead | 216 | 59818 | 38.999 | -122.6724 | KNIFFIN- ANDREW: Corner of Frances Ln and Lakeshore Dr. | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142235 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1794025 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UKIAH-1114 | 42771114 | FUSE | 91159 | 20221230 | 1511 | 1902383 | 188 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1128 | 39.1383 | -123.1769 | 2 SPANS LD SIDE OF 91159 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142264 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1794053 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 6423 | 20221230 | 1355 | 1902285 | 310 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 8680 | 39.4878 | -123.4249 | 7 SPANS LD SIDE OF FUCO 6423 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142273 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1794064 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 2531 | 20230101 | 1305 | 1908612 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 758 | 40.151 | -124.0291 | CURNOW- RAY/K1616-T1270: 3 SPANS LD SIDE OF 2531 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0004421 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1795019 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | RECLOSER | 1052 | 20230103 | 131 | 1910884 | 741 | Distribution Circuit | Vegetation | Tree - fell into line | 606 | 101058 | 39.3099 | -123.7939 | PARDINI- JAKE: 8951 RD 500A | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0004941 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1795546 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 65936 | 20230103 | 828 | 1911095 | 457 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 457 | 40.1358 | -123.9861 | 1 SPAN LD SIDE OF FUCO 65936 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0005043 | OH | Sus | 0 | No | 2023 | JAN | Yes | Multi-Fault | 1795609 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | JUMPER | WIRE DOWN | 20230103 | 1040 | 1911439 | 438 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1010 | 38.7042 | -123.4278 | AT SBCO 5151 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0005176 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1795702 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 48371 | 20230103 | 828 | 1911094 | 259 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 259 | 39.6425 | -123.5316 | 1 SPAN LD SIDE OF FUCO 48371 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0005036 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1795606 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | FUSE | 915 | 20230106 | 1750 | 1925564 | 26 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 260 | 39.704 | -123.6545 | 4 SS CGC 215349575265 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0008555 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1798479 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3283 | 20230111 | 846 | 1947239 | 336 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2352 | 39.3121 | -123.7827 | 2SPANS LOAD SIDE OF 3283 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0013490 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1802994 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | RECLOSER | 198780 | 20230111 | 1029 | 1947550 | 321 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 24717 | 39.386 | -123.7739 | 6 SS OF CGC 2150001062610 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0013499 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1803000 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 900560 | 20230112 | 931 | 1949821 | 472 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 16992 | 40.307 | -124.2967 | 11 SPANS LD SIDE OF 900560 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0014694 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1803851 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | FUSE | 2653 | 20230112 | 1207 | 1950056 | 333 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2664 | 38.932 | -123.692 | 3 SPANS LD SIDE OF FUCO 2653 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0014577 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1803795 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | FUSE | 729653 | 20230112 | 354 | 1949314 | 701 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3868 | 39.3705 | -123.3619 | 4SPANS LD SIDE TO THE SOUTH OF 729658 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0014387 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1803699 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | FUSE | 1729 | 20230113 | 4 | 1951186 | 1019 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 7133 | 39.8253 | -123.6738 | 4 SPAN LD SIDE 1729 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0015387 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1804295 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 54487 | 20230115 | 1445 | 1956072 | 70 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 70 | 40.133 | -123.983 | 1 LD SIDE OF FUSES | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016713 | OH | Sus | 0 | No | 2023 | JAN | Yes | Multi-Fault | 1805430 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 91810 | 20230118 | 1624 | 1961243 | 418 | Distribution Circuit | Vegetation | Tree - fell into line | 649 | 54562 | 39.4457 | -123.3807 | 5 SPANS LD SIDE OF CGC 216109465351 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0018547 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1806626 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 3063 | 20230119 | 145 | 1961756 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 26542 | 39.2846 | -123.7929 | Felicich- David: 8025 hwy1 little river | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0018651 | OH | Sus | 31634841 | No | 2023 | JAN | Yes | Three Phase Fault | 1806714 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 951123 | 20230130 | 1029 | 1971908 | 938 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 12194 | 38.8184 | -122.7014 | MTR 1011072158 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0022976 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1809192 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOPLAND-1101 | 42251101 | FUSE | 9395 | 20230201 | 1652 | 1974204 | 407 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 12 | 4884 | 38.9478 | -123.1656 | 8 LD SIDE OF 9395 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0024133 | OH | Sus | 0 | No | 2023 | FEB | Yes | Force Out | 1809829 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | CARLOTTA-1121 | 192291121 | RECLOSER | 44150 | 20230203 | 136 | 1975483 | 639 | Distribution Circuit | Vegetation | Tree - branch fell on line | 395 | 140960 | 40.4949 | -123.9881 | 9 SPANS LD SIDE 4071 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0024702 | OH | Sus | 45658535 | No | 2023 | FEB | Yes | Line to Line | 1810169 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | FUSE | 1787 | 20230205 | 543 | 1977215 | 402 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 6030 | 40.011 | -123.9299 | 6 LD SIDE OF 1787 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0025393 | OH | Sus | 0 | No | 2023 | FEB | Yes | Force Out | 1810686 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 2500 | 20230206 | 640 | 1977840 | 534 | Distribution Circuit | Vegetation | Tree - fell into line | 478 | 250284 | 40.1083 | -123.9286 | ALLEN- DERRICK /K1130-T1243:4 SPANS LD SIDE OF 2500 ON MAIN LINE at 1550 Blue Slide | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0025538 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Line | 1810817 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | RECLOSER | 2936 | 20230206 | 400 | 1977800 | 763 | Distribution Circuit | Vegetation | Tree - fell into line | 254 | 193802 | 40.8669 | -123.5147 | HIGHTOWER- WALT: Fco. 2963 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0025523 | OH | Sus | 0 | No | 2023 | FEB | Yes | Multi-Fault | 1810807 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HARTLEY-1101 | 43211101 | SWITCH | 1159 | 20230209 | 1442 | 1981127 | 190 | Distribution Circuit | Equipment Failure/Involved | Overhead | 214 | 40660 | 39.1561 | -122.9953 | 4610 LAUREL BELL RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 23-0027213 | OH | Sus | 0 | No | 2023 | FEB | Yes | Force Out | 1811963 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 5187 | 20230213 | 1426 | 1983913 | 250 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2250 | 39.2861 | -123.7795 | 6 LD SIDE OF 5187 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0028229 | OH | Sus | 45670947 | No | 2023 | FEB | Yes | None | 1812848 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 1917 | 20230213 | 1450 | 1983828 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 6400 | 39.2922 | -123.7706 | 9911 WARNER LANE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0028293 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Line | 1812863 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 6865 | 20230213 | 1443 | 1983811 | 176 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 17072 | 40.2935 | -123.8177 | CGC 114964535424 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0028298 | OH | Sus | 45670949 | No | 2023 | FEB | Yes | Line to Line | 1812868 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE | 1105 | 20230213 | 1539 | 1983932 | 547 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6564 | 39.1669 | -122.9795 | 7/LD SIDE OF 1105 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0028313 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Line | 1812879 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | RECLOSER | 23444 | 20230216 | 1316 | 1987009 | 252 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 19665 | 38.849 | -123.644 | LD SIDE OF 4469 MAIN LINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0029765 | OH | Sus | 45674922 | No | 2023 | FEB | Yes | Line to Ground | 1813772 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 1679 | 20230222 | 948 | 1997103 | 402 | Distribution Circuit | Environmental/External | Ice or snow | 46 | 18492 | 40.2779 | -123.7927 | 1 SPAN LD SIDE OF 1679 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0032429 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1815892 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 8652 | 20230222 | 203 | 1996332 | 835 | Distribution Circuit | Equipment Failure/Involved | Overhead | 239 | 213371 | 40.1069 | -123.9276 | CENTER PHA DOWN MAINLINE SS OF 2595- TREE BRANCH 11 SPANS LD SIDE OF FUCO 1787 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0032017 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1815616 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1101 | 42601101 | JUMPER | WIRE DOWN 6 SPANS S/S OF CGC 215531859658 | 20230303 | 1110 | 2021172 | 447 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3898 | 38.8705 | -123.2175 | 6 SPANS S/S OF CGC 215531859658 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0039413 | OH | Sus | 0 | No | 2023 | MAR | Yes | Force Out | 1821270 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | FUSE | 3729 | 20230304 | 1300 | 2022450 | 295 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 295 | 40.2815 | -123.8723 | 1 SPANS LD SIDE OF CGC TRIMBLE 707 367 1468 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0039987 | OH | Sus | 0 | No | 2023 | MAR | Yes | Three Phase Fault | 1821743 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | JUMPER | WIRE DOWN @CGC 115444429847 | 20230304 | 830 | 2022160 | 3059 | Distribution Circuit | Equipment Failure/Involved | Overhead | 54 | 32230 | 40.141 | -123.6298 | ALLEN- DERRICK /K1130-T1243: 14297 Alderpoint rd | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0039896 | OH | Sus | 0 | No | 2023 | MAR | Yes | Force Out | 1821656 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | RECLOSER | 91810 | 20230304 | 2354 | 2022999 | 456 | Distribution Circuit | Vegetation | Tree - fell into line | 671 | 315221 | 39.4457 | -123.3807 | BARRINGTON- SORREL/T1102-K3455: Laytonville side 3 SS of 4779 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0040176 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1821924 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1103 | 42661103 | FUSE | 7913 | 20230304 | 2352 | 2023562 | 682 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1364 | 39.5138 | -123.435 | BARRINGTON- SORREL/T1102-K3455: 3 SS of riser | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0033398 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1822025 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4581 | 20230305 | 821 | 2023482 | 414 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 7228 | 38.7172 | -123.3624 | 3/S/O 4581 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 23-0040272 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1822011 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BRIDGEVILLE-1102 | 192461102 | RECLOSER | 55612 | 20230305 | 606 | 2023284 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 28340 | 40.4664 | -123.8013 | 1 S/S OF MTR# 1010947990 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0040222 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1821970 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | RECLOSER | 1690 | 20230305 | 840 | 2023464 | 530 | Distribution Circuit | Environmental/External | Ice or snow | 26 | 13153 | 40.1678 | -123.6111 | FUCO 1637 ON MAINLINE | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0040260 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1822005 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | OTHER | WIRE DOWN AT 218006043445 | 20230305 | 114 | 2023109 | 839 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 41869 | 38.8583 | -122.6997 | WIRE DOWN ON HARD TAP GOING EAST BY CGC# 218006043445 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 23-0040204 | OH | Sus | 0 | No | 2023 | MAR | Yes | Open Circuit | 1821952 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | JUMPER | HOT WIRE DOWN 1/W/O CGC 218012243762 | 20230305 | 459 | 2023305 | 615 | Distribution Circuit | Environmental/External | Ice or snow | 980 | 175540 | 38.8657 | -122.6979 | 1/W/O CGC 218012243762 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0040216 | OH | Sus | 0 | No | 2023 | MAR | Yes | None | 1821972 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 3 | KONOCTI-1102 | 43311102 | FUSE | 2309 | 20230305 | 758 | 2023405 | 451 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3608 | 38.8925 | -122.7399 | 2 SPANS LD SIDE OF FUCO 2309 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0040298 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1822036 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | RECLOSER | 4646 | 20230305 | 836 | 2023458 | 340 | Distribution Circuit | Vegetation | Tree - fell into line | 213 | 48946 | 38.8291 | -122.7295 | CGC# 217839442605 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0040256 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1822003 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | POINT ARENA-1101 | 43381101 | RECLOSER | 83354 | 20230305 | 18 | 2023015 | 711 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 27018 | 38.8812 | -123.6619 | Thorpe- Tim/2094: 1 ss/o fucos 96625 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0040177 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1821925 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UKIAH-1114 | 42771114 | FUSE | 430057 | 20230305 | 742 | 2023515 | 503 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 13581 | 39.044 | -123.2644 | 6 SPANS LD SIDE 430057 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0040281 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1822018 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | OTHER | 4231 | 20230308 | 1522 | 2026848 | 110 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 1320 | 40.3195 | -123.812 | 2/S/NW OF 4231 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0041790 | OH | Sus | 0 | No | 2023 | MAR | Yes | Open Circuit | 1822958 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | RECLOSER | 448108 | 20230308 | 415 | 2026203 | 553 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 13433 | 39.6878 | -123.4955 | Dickson- Josh 707 293-6004: at cgc 215761574000 | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 23-0041460 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1822792 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | RECLOSER | 572 | 20230308 | 905 | 2026459 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 183 | 36927 | 39.6732 | -123.506 | 1 S/S OF CGC#215712073467 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0041503 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1822863 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | LAYTONVILLE-1102 | 42681102 | FUSE | 7913 | 20230308 | 622 | 2026183 | 778 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 17116 | 39.5138 | -123.435 | Welsh- Tyler 707-806-9777: 1 South of 4779 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0041610 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1822879 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | RECLOSER | 1294 | 20230316 | 1359 | 2048604 | 277 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 632 | 79263 | 38.8037 | -123.5835 | Thorpe- Tim/2094: Sbco 9287 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0047071 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1826596 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | BIG RIVER-1101 | 43081101 | FUSE | 2933 | 20230320 | 1341 | 2053240 | 261 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 7 | 1827 | 39.2713 | -123.7735 | CGC 214979058845 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0048966 | OH | Sus | 31640094 | No | 2023 | MAR | Yes | Line to Line | 1827947 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARCIA-0401 | 43040401 | JUMPER | WIRE DOWN 5 SPANS LD SIDE OF 4491 | 20230320 | 719 | 2052772 | 441 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2205 | 38.8961 | -123.5396 | 5 SPANS LD SIDE OF 4491 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0048694 | OH | Sus | 0 | No | 2023 | MAR | Yes | Force Out | 1827865 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 827 | 20230328 | 335 | 2069491 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 6492 | 39.456 | -123.789 | 31701 JOHNSON LN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0053257 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1830988 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 3 | WILLITS-1104 | 42661104 | OTHER | HOT WIRE DOWN 8 SP LD SIDE 627552 | 20230328 | 959 | 2070073 | 285 | Distribution Circuit | 3rd Party | Vehicle | 163 | 43752 | 39.441 | -123.3939 | 8 SPANS LD SIDE OF 627552 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0053489 | OH | Sus | 0 | No | 2023 | MAR | Yes | Force Out | 1831141 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | OTHER | WIRE DOWN 2/S/LD SIDE CGC 214894363384 | 20230403 | 1620 | 2078910 | 240 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 1555 | 39.3934 | -123.8076 | 2/S/LD SIDE CGC 214894363384 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0056539 | OH | Sus | 45714858 | No | 2023 | APR | Yes | Open Circuit | 1832949 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLITS-1103 | 42661103 | SWITCH | 2527 | 20230404 | 1608 | 2080188 | 260 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 4940 | 39.5179 | -123.3916 | 1/S/N/OF CGC 216050868096 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0057178 | OH | Sus | 45715664 | No | 2023 | APR | Yes | Force Out | 1833282 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3059 | 20230410 | 1051 | 2084393 | 196 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 6860 | 39.4151 | -123.7708 | 15 SPANS LD SIDE OF 3059 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0059101 | OH | Sus | 0 | No | 2023 | APR | Yes | Open Circuit | 1834557 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 827 | 20230412 | 1630 | 2086961 | 476 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 11424 | 39.456 | -123.789 | 31784 JOHNSON LN- FOR BRAGG | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0060375 | OH | Sus | 0 | No | 2023 | APR | Yes | Line to Line | 1835291 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | RECLOSER | 1294 | 20230412 | 1428 | 2086814 | 561 | Distribution Circuit | Vegetation | Tree - fell into line | 632 | 168902 | 38.8037 | -123.5835 | Thorpe- Tim/2094: TREE 2 ls/o 188809- BRANCH 35640 TIMBERWOOD DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0060267 | OH | Sus | 0 | No | 2023 | APR | Yes | Line to Ground | 1835261 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | FUSE | 4599 | 20230413 | 2225 | 2088192 | 780 | Distribution Circuit | 3rd Party | Vehicle | 7 | 5460 | 40.2378 | -123.8333 | 5 SPANS LD SIDE OF 4599 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0060940 | OH | Sus | 0 | No | 2023 | APR | Yes | Line to Ground | 1835695 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 1457 | 20230420 | 1527 | 2093252 | 208 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 1872 | 39.2195 | -123.7292 | 9 LD SIDE OF 1457 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0063166 | OH | Sus | 45737480 | No | 2023 | APR | Yes | Line to Ground | 1837291 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 4597 | 20230503 | 234 | 2103303 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5544 | 38.7292 | -123.3494 | 12/S/LD SIDE 4597 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0067457 | OH | Sus | 0 | No | 2023 | MAY | Yes | Three Phase Fault | 1840329 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | OTHER | WIRE DOWN LD SIDE 4622 | 20230507 | 41 | 2106498 | 591 | Distribution Circuit | Vegetation | Tree - fell into line | 374 | 221034 | 39.5162 | -123.7631 | ON LD SIDE OF 4622 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0069256 | OH | Sus | 45751262 | No | 2023 | MAY | Yes | Open Circuit | 1841445 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | UPPER LAKE-1101 | 42871101 | FUSE | 775 | 20230516 | 1138 | 2114118 | 539 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1617 | 39.1728 | -122.9412 | CHEW- SETH: 1645 hwy 20 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0072354 | OH | Sus | 31645741 | No | 2023 | MAY | Yes | Three Phase Fault | 1843642 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 4415 | 20230519 | 2155 | 2117360 | 1394 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 89216 | 39.2653 | -123.594 | Welsh- Tyler 707-806-9777: 102171658- 33150 COMPTCHE UKIAH RD -- 3/S/LD SIDE 4415 | Partly Cloudy-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 23-0073772 | OH | Sus | 0 | No | 2023 | MAY | Yes | Line to Line | 1844598 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | RECLOSER | 8860 | 20230523 | 1417 | 2119890 | 530 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 85860 | 40.2832 | -123.8721 | 8-9 SPANS LD SIDE OF 8860 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0074792 | OH | Sus | 45771954 | No | 2023 | MAY | Yes | Multi-Fault | 1845397 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | OCB | 1141/2 | 20230615 | 608 | 2137412 | 194 | Distribution Circuit | Vegetation | Tree - fell into line | 386 | 56702 | 40.2866 | -123.8369 | LD SIDE OF 1577 | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0082560 | OH | Sus | 31652413 | No | 2023 | JUN | Yes | Line to Ground | 1850747 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1141 | 192311141 | FUSE | 3965 | 20230622 | 30 | 2142793 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 568 | 40.3421 | -123.8806 | 11 SPANS LOAD SIDE OF 3965 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0084503 | OH | Sus | 0 | No | 2023 | JUN | Yes | Line to Line | 1852281 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 1102/2 | 20230627 | 1335 | 2147102 | 687 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1819 | 147042 | 40.1033 | -123.7926 | 3 LD SIDE OF 8041 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0086158 | OH | Sus | 0 | No | 2023 | JUN | Yes | Line to Ground | 1853507 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1122 | 192321122 | OCB | 1122/2 | 20230629 | 1644 | 2149209 | 552 | Distribution Circuit | Vegetation | Tree - fell into line | 101 | 21630 | 40.2139 | -123.5966 | FUSES 1651 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0087325 | OH | Sus | 0 | No | 2023 | JUN | Yes | Line to Ground | 1854141 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 4399 | 20230701 | 2139 | 2151563 | 891 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 6237 | 40.0838 | -123.8183 | 5 LD SIDE OF 4399 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0088089 | OH | Sus | 31654220 | No | 2023 | JUL | Yes | Line to Line | 1854728 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | FUSE | 4365 | 20230715 | 430 | 2163136 | 393 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1965 | 39.9606 | -123.7701 | 12 SPANS LD SIDE OF 4365 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0092548 | OH | Sus | 0 | No | 2023 | JUL | Yes | Multi-Fault | 1857640 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | TRANSFORMER | 214951866337 | 20230718 | 1444 | 2166816 | 561 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2692 | 39.4744 | -123.7894 | PARDINI- JAKE: 32775 Tucker Ln | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0093887 | OH | Sus | 0 | No | 2023 | JUL | Yes | Line to Ground | 1858548 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | WILLOW CREEK-1103 | 192171103 | FUSE | 4767 | 20230730 | 2358 | 2178058 | 1005 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 10050 | 40.9042 | -123.5771 | CGC# 115644457519 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0098531 | OH | Sus | 0 | No | 2023 | JUL | Yes | Line to Ground | 1861669 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 37202 | 20230804 | 1626 | 2182656 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 44706 | 41.1893 | -123.7102 | 18 POLES LD SIDE OF 8437 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0100774 | OH | Sus | 0 | No | 2023 | AUG | Yes | Line to Line | 1863162 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | REDBUD-1102 | 43191102 | RECLOSER | 523244 | 20230810 | 604 | 2187282 | 391 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2827 | 422477 | 39.0253 | -122.6596 | SMITH- CODY/2089: Corner of lakeshore dr and Francis dr | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0102496 | OH | Sus | 45923044 | No | 2023 | AUG | Yes | Line to Line | 1864472 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOPLAND-1101 | 42251101 | OTHER | WIRE DOWN 2 LD SIDE CGC 216698050492 | 20230814 | 1828 | 2190849 | 223 | Distribution Circuit | Vegetation | Tree - branch fell on line | 306 | 37425 | 39.0483 | -123.1646 | 2 LD SIDE 216698050492 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0104263 | OH | Sus | 0 | No | 2023 | AUG | Yes | Open Circuit | 1865671 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | FUSE | 46545 | 20230819 | 1532 | 2195954 | 471 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 471 | 40.1708 | -123.6086 | JUST LD SIDE OF 46545 FOR TWO SPANS | Strong Winds | Conductor, Overhead | Broken, wire on ground | 23-0106431 | OH | Sus | 0 | No | 2023 | AUG | Yes | Line to Ground | 1867099 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOOPA-1101 | 192401101 | RECLOSER | 3174 | 20230819 | 149 | 2195399 | 1100 | Distribution Circuit | Vegetation | Tree - fell into line | 488 | 536800 | 41.2233 | -123.6557 | 8 SPANS LOAD SIDE OF 6325 FUCO ON MAIN LINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0106316 | OH | Sus | 45934022 | No | 2023 | AUG | Yes | Line to Line | 1866964 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 1510 | 20230824 | 231 | 2200798 | 916 | Distribution Circuit | Vegetation | Tree - fell into line | 835 | 666003 | 40.1222 | -123.835 | 14 SPANS LD SIDE OF 2557 at SAP ID 10100986517 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0108400 | OH | Sus | 0 | No | 2023 | AUG | Yes | Line to Ground | 1868487 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 8961 | 20230825 | 1850 | 2202536 | 75 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 75 | 39.5607 | -123.7259 | 4 SPANS LD SIDE OF FUCO 8961 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0109311 | OH | Sus | 0 | No | 2023 | AUG | Yes | Line to Ground | 1869109 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1102 | 42681102 | RECLOSER | 37586 | 20230930 | 2121 | 2231959 | 864 | Distribution Circuit | 3rd Party | Vehicle | 128 | 110592 | 39.6174 | -123.4633 | 8 POLES LD SIDE OF FUSES 2493 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 23-0123043 | OH | Sus | 0 | No | 2023 | SEP | Yes | Line to Line | 1878271 | PW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FRUITLAND-1142 | 192311142 | RECLOSER | 866852 | 20231007 | 1242 | 2237678 | 415 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 4977 | 40.3383 | -123.913 | at 3965 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0125732 | OH | Sus | 31671755 | No | 2023 | OCT | Yes | Line to Ground | 1880216 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT SEWARD-1121 | 192321121 | OCB | 1121/2 | 20231011 | 246 | 2240350 | 438 | Distribution Circuit | Vegetation | Tree - fell into line | 234 | 68527 | 40.2139 | -123.5967 | CURNOW- RAY/K1616-T1270: Alderpoint | Partly Cloudy-Fog-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0126809 | OH | Sus | 31672236 | No | 2023 | OCT | Yes | Line to Line | 1881075 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | SWITCH | 732869 | 20231029 | 520 | 2254801 | 835 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5010 | 39.525 | -123.7299 | 3 SPANS N/OF LINE & BUCK LOAD SIDE OF 732869 | Clear-32-90 F | Conductor, Overhead | On Ground | 23-0133678 | OH | Sus | 0 | No | 2023 | OCT | Yes | Force Out | 1885972 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1102 | 42761102 | FUSE | 3321 | 20231106 | 339 | 2260983 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3270 | 39.4051 | -123.7417 | 1 LD SIDE OF 3321 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0136103 | OH | Sus | 0 | No | 2023 | NOV | Yes | Line to Line | 1887982 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | ELK-1101 | 42981101 | FUSE | 3273 | 20231117 | 902 | 2271370 | 495 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3465 | 39.1937 | -123.7234 | 30751 NAVARRO RIVER RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0140485 | OH | Sus | 46061014 | No | 2023 | NOV | Yes | Line to Ground | 1891357 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1104 | 42761104 | FUSE | 3119 | 20231118 | 2302 | 2273366 | 696 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 42456 | 39.4514 | -123.7905 | 21601 N PETALMA AVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0141047 | OH | Sus | 0 | No | 2023 | NOV | Yes | Line to Ground | 1891717 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | HOPLAND-1101 | 42251101 | FUSE | 499 | 20231204 | 1329 | 2283638 | 511 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 39 | 7837 | 38.9576 | -123.1012 | CGC 216872246695 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0145353 | OH | Sus | 0 | No | 2023 | DEC | Yes | Line to Ground | 1895045 | CAW | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1101 | 192221101 | RECLOSER | 438596 | 20231206 | 1125 | 2285166 | 351 | Distribution Circuit | Vegetation | Tree - fell into line | 147 | 40155 | 39.9605 | -123.7829 | TREE 11/N/O 928067- BRANCH 1 LD SIDE 651404 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0145865 | OH | Sus | 46080108 | No | 2023 | DEC | Yes | Multi-Fault | 1895617 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | RIO DELL-1101 | 192251101 | RECLOSER | 37410 | 20231206 | 534 | 2284773 | 288 | Distribution Circuit | Vegetation | Tree - fell into line | 340 | 64377 | 40.3263 | -123.9228 | 5/n/o 1595 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0145741 | OH | Sus | 46079417 | No | 2023 | DEC | Yes | Line to Line | 1895441 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | PHILO-1102 | 42601102 | FUSE | 9077 | 20231210 | 731 | 2288268 | 460 | Distribution Circuit | Vegetation | Tree - branch fell on line | 32 | 6053 | 39.1243 | -123.4903 | 2.5 SPANS LD SIDE OF CGC 215809553675 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0146733 | OH | Sus | 0 | No | 2023 | DEC | Yes | Line to Line | 1896577 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | LAYTONVILLE-1101 | 42681101 | RECLOSER | 364398 | 20231211 | 954 | 2289118 | 233 | Distribution Circuit | Equipment Failure/Involved | Overhead | 500 | 116500 | 39.845 | -123.6921 | 1 E/OF 1717 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0146852 | OH | Sus | 46087412 | No | 2023 | DEC | Yes | Multi-Fault | 1896841 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 1379 | 20231218 | 203 | 2294022 | 411 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2466 | 39.4878 | -123.7786 | 2 SS OF CGC 214985166935 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0147830 | OH | Sus | 46093157 | No | 2023 | DEC | Yes | Line to Ground | 1898591 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GUALALA-1112 | 42841112 | OTHER | WIRE DOWN AT 44500 GUALALA RD | 20231219 | 1615 | 2295929 | 400 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2750 | 38.7827 | -123.4977 | 44500 GUALALA RD | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0148140 | OH | Sus | 0 | No | 2023 | DEC | Yes | Open Circuit | 1899002 | CO | OH | No | Yes
HUMBOLDT | FIELD OPS NORTH | Tier 2 | FORT BRAGG A-1101 | 42761101 | FUSE | 7221 | 20231229 | 1127 | 2301857 | 204 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 408 | 39.523 | -123.7613 | 2 LD SIDE OF 7221 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0149211 | OH | Sus | 0 | No | 2023 | DEC | Yes | Line to Ground | 1900504 | CO | OH | No | No
HUMBOLDT | FIELD OPS NORTH | Tier 2 | GARBERVILLE-1102 | 192221102 | RECLOSER | 4744 | 20231229 | 711 | 2301689 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 198 | 40662 | 40.2785 | -124.2441 | 8 LD SIDE 2551 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0149183 | OH | Sus | 0 | No | 2023 | DEC | Yes | Line to Ground | 1900444 | CO | OH | No | No
KERN | FIELD OPS SOUTH | Tier 2 | POSO MOUNTAIN-2101 | 253642101 | FUSE | 9942 | 20130129 | 1513 | 736141 | 1234 | Distribution Circuit | 3rd Party | Gun Shot | 14 | 17276 | 35.5546 | -118.9019 | VALENCIA- BERT _ 661-864-5628: 2 PLS SW OF FUCO 9942 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0006909 | OH | Sus | 41847085 | No | 2013 | JAN | Yes | Line to Ground | 99302805 | CO | OH | No
KERN | FIELD OPS SOUTH | Tier 2 | POSO MOUNTAIN-2101 | 253642101 | FUSE | 13974 | 20130219 | 1229 | 743810 | 391 | Distribution Circuit | Equipment Failure/Involved | Other | 3 | 1173 | 35.6075 | -118.9581 | 1 POLE S/OF 13974 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0010874 | OH | Sus | 41856278 | yes | 2013 | FEB | Yes | Line to Ground | 99300338 | CO | OH | No
KERN | FIELD OPS SOUTH | Tier 2 | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 3988 | 20131008 | 1321 | 881328 | 138 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 24 | 3312 | 35.5533 | -118.9352 | EOL IDLE TAP N/OF L996 TWD WEST | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0068111 | OH | Sus | 0 | No | 2013 | OCT | Yes | Multi-Fault | 99259513 | CO | OH | No
KERN | FIELD OPS SOUTH | Tier 2 | POSO MOUNTAIN-2101 | 253642101 | FUSE | 8663 | 20140124 | 645 | 946677 | 756 | Distribution Circuit | Equipment Failure/Involved | Other | 8 | 6048 | 35.5571 | -118.8148 | SCOTT-DAVID/3366/661-342-0822: 8 POLES N/O 8663 | Strong winds-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0006143 | OH | Sus | 0 | yes | 2014 | JAN | Yes | Line to Ground | 99243019 | CAW | OH | No
KERN | FIELD OPS SOUTH | Tier 2 | POSO MOUNTAIN-2101 | 253642101 | RECLOSER | 1703 | 20150411 | 1830 | 1217657 | 977 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 977 | 35.5587 | -118.9787 | E/OF LINE & BUCK BET 1703 & 92953 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0026030 | OH | Sus | 42367385 | No | 2015 | APR | Yes | Line to Ground | 99174028 | CO | OH | No
KERN | FIELD OPS SOUTH | Tier 2 | POSO MOUNTAIN-2101 | 253642101 | OCB | 76778 | 20151015 | 547 | 1322361 | 2031 | Distribution Circuit | Environmental/External | Lightning | 106 | 108871 | 35.5593 | -118.9571 | 2P N/OF 83297 | Partly Cloudy-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0070510 | OH | Sus | 0 | yes | 2015 | OCT | Yes | Line to Ground | 1162407 | CO | OH | No | No
KERN | FIELD OPS SOUTH | Tier 2 | POSO MOUNTAIN-2101 | 253642101 | OTHER | 3990 | 20151230 | 1312 | 1374878 | 219 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 2847 | 35.5581 | -118.9767 | 4 POLES S/OF 3990 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0087867 | OH | Sus | 31209644 | No | 2015 | DEC | Yes | Line to Ground | 1178165 | PW | OH | No | No
KERN | FIELD OPS SOUTH | Tier 2 | POSO MOUNTAIN-2101 | 253642101 | FUSE | 13974 | 20161224 | 810 | 1610160 | 797 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2391 | 35.607 | -118.9582 | 3 P N/ OF 13974 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0086899 | OH | Sus | 0 | No | 2016 | DEC | Yes | Line to Ground | 1242087 | PW | OH | No | No
KERN | FIELD OPS SOUTH | Tier 2 | POSO MOUNTAIN-2101 | 253642101 | FUSE | 13972 | 20170203 | 1444 | 1674149 | 931 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2793 | 35.6338 | -118.9581 | MTR# 1009390228 | Combination-Overcast-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017335 | OH | Sus | 42938962 | yes | 2017 | FEB | Yes | Line to Ground | 1255301 | CO | OH | No | No
KERN | FIELD OPS SOUTH | Tier 2 | TEJON-1102 | 252931102 | FUSE | 88811 | 20170603 | 1715 | 1796454 | 1540 | Distribution Circuit | 3rd Party | Vehicle | 23 | 8972 | 34.8375 | -118.8661 | TALLMAN-SEAN_2031_661-619-8501: at 1586 lebec rd | Clear-32-90 F | Pole-Wood | Broken, wire on object | 17-0052555 | OH | Sus | 0 | No | 2017 | JUN | Yes | Line to Ground | 1282919 | PW | OH | No | No
KERN | FIELD OPS SOUTH | Tier 2 | POSO MOUNTAIN-2101 | 253642101 | FUSE | 13971 | 20180428 | 1311 | 75944 | 427 | Distribution Circuit | 3rd Party | Gun Shot | 5 | 2135 | 35.6349 | -118.9563 | 5 DOGS SHTG RNG BET POLES SAP ID 100216263 & 103233788 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0036481 | OH | Sus | 43333201 | No | 2018 | APR | Yes | Multi-Fault | 1345590 | CO | OH | No | No
KERN | FIELD OPS SOUTH | Tier 2 | POSO MOUNTAIN-2101 | 253642101 | FUSE | 13971 | 20180719 | 2000 | 135927 | 224 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1120 | 35.6349 | -118.9563 | 13P/E/OF 13971 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0061650 | OH | Sus | 43411326 | yes | 2018 | JUL | Yes | Line to Ground | 1365166 | CO | OH | No | No
KERN | FIELD OPS SOUTH | Tier 2 | POSO MOUNTAIN-2101 | 253642101 | JUMPER | 3 PHASE WIRE DOWN | 20181003 | 2159 | 187815 | 612 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 29 | 14041 | 35.635 | -118.9635 | MTR# 1009567132 | Clear-Lightning-32-90 F | Pole-Wood | Broken, wire on ground | 18-0086546 | OH | Sus | 0 | yes | 2018 | OCT | Yes | Line to Ground | 1382918 | PW | OH | No | No
KERN | FIELD OPS SOUTH | Tier 2 | POSO MOUNTAIN-2101 | 253642101 | OCB | 2101/2 | 20190131 | 1117 | 284658 | 958 | Distribution Circuit | Equipment Failure/Involved | Overhead | 147 | 93124 | 35.5593 | -118.9571 | 3P/N/OF 4456 | Overcast-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0016241 | OH | Sus | 31424305 | No | 2019 | JAN | Yes | Three Phase Fault | 1410986 | CSO | OH | No | No
KERN | FIELD OPS SOUTH | Tier 2 | POSO MOUNTAIN-2103 | 253642103 | OCB | 2103/2 | 20231227 | 742 | 2300386 | 620 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 10206 | 35.5593 | -118.9575 | LEYENDECKER- TOM: 22 poles load side of 9942 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0148969 | OH | Sus | 46101879 | No | 2023 | DEC | Yes | Line to Ground | 1900095 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1106 | 182601106 | RECLOSER | V50 | 20130109 | 1357 | 727596 | 417 | Distribution Circuit | 3rd Party | Vehicle | 486 | 102554 | 35.0771 | -120.5827 | 1 POLE SE/OF CGC#51225989494 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0003103 | OH | Sus | 0 | yes | 2013 | JAN | Yes | Line to Ground | 99305219 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | FUSE | 5045 | 20130110 | 1301 | 728181 | 374 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 9596 | 35.5495 | -121.0885 | MTR at 1006242721 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0003428 | OH | Sus | 41837793 | No | 2013 | JAN | Yes |  | 99305051 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CAMBRIA-1102 | 182771102 | FUSE | 5027 | 20130219 | 1508 | 743982 | 512 | Distribution Circuit | Equipment Failure/Involved | Other | 52 | 23204 | 35.5945 | -121.117 | MTR 4846R9 | Rain-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0011001 | OH | Sus | 30978306 | yes | 2013 | FEB | Yes |  | 99300303 | CSO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ZACA-1101 | 182681101 | FUSE | 1601 | 20130227 | 955 | 748154 | 388 | Distribution Circuit | 3rd Party | Gun Shot | 2 | 776 | 34.7337 | -120.1278 | FOXEN CYN. | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0012826 | OH | Sus | 41859581 | No | 2013 | FEB | Yes | Line to Line | 99298880 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | MESA-1101 | 182821101 | SWITCH | 89913 | 20130303 | 1034 | 750449 | 26 | Distribution Circuit | 3rd Party | Vandalism | 105 | 2730 | 35.0054 | -120.4401 | NE 101 BRIDGE & SANTA MARIA RIVER | Overcast-32 - 90 F | Conductor, Overhead | On Ground | 13-0013722 | OH | Sus | 0 | No | 2013 | MAR | Yes | Multi-Fault | 99298366 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1102 | 182601102 | FUSE | 3815 | 20130327 | 2048 | 762647 | 657 | Distribution Circuit | 3rd Party | Vehicle | 72 | 41088 | 35.0885 | -120.5647 | EL CAMPO & GREEN PL. | Fog-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0019630 | OH | Sus | 30985956 | No | 2013 | MAR | Yes | Line to Ground | 99294316 | PW | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | CAYUCOS-1102 | 182551102 | FUSE | 4133 | 20130330 | 858 | 763701 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 2223 | 35.4758 | -120.8195 | TAP FEEDING 10440 SANTA RITA RD | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0020142 | OH | Sus | 41875186 | No | 2013 | MAR | Yes | Line to Ground | 99293955 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | V74 | 20130415 | 1521 | 775401 | 618 | Distribution Circuit | Vegetation | Tree - fell into line | 754 | 79416 | 35.5459 | -121.0679 | FUCO 9547 ON SS TWD V74 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0024616 | OH | Sus | 30989682 | yes | 2013 | APR | Yes |  | 99290467 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1102 | 182601102 | OTHER |  | 20130418 | 654 | 777584 | 442 | Distribution Circuit | 3rd Party | Vehicle | 10 | 4405 | 35.0826 | -120.5517 | 2SP SS OF 9591 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0025445 | OH | Sus | 41885475 | No | 2013 | APR | Yes | Line to Ground | 99289771 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1101 | 182631101 | RECLOSER | V12 | 20130503 | 1955 | 786635 | 435 | Distribution Circuit | Equipment Failure/Involved | Other | 199 | 49045 | 35.2952 | -120.6364 | MTR# 1006489681 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0029359 | OH | Sus | 41892652 | No | 2013 | MAY | Yes | Three Phase Fault | 99286938 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 9201 | 20130505 | 1212 | 787702 | 628 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 6280 | 35.2381 | -120.4732 | 3955 UPPER LOPEZ CYN MTR#4M3783 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0029645 | OH | Sus | 30994569 | yes | 2013 | MAY | Yes | Line to Ground | 99286656 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PASO ROBLES-1103 | 182611103 | OTHER |  | 20130515 | 1425 | 793380 | 684 | Distribution Circuit | 3rd Party | Vehicle | 14 | 7306 | 35.6739 | -120.7298 | SAME AS ADDRESS | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0032127 | OH | Sus | 30996714 | No | 2013 | MAY | Yes | None | 99284881 | PW | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PASO ROBLES-1103 | 182611103 | FUSE | 4019 | 20130515 | 1453 | 793382 | 86 | Distribution Circuit | 3rd Party | Vehicle | 30 | 2580 | 35.6667 | -120.7255 | NACIMIENTO LAKE DR & MUSTARD CRK | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0032127 | OH | Sus | 0 | No | 2013 | MAY | Yes | Line to Line | 99284876 | PW | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | V74 | 20130527 | 2014 | 799289 | 452 | Distribution Circuit | Vegetation | Tree - fell into line | 521 | 64457 | 35.5459 | -121.0679 | JOHNSON 3834: 1680 BURTON | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 13-0034596 | OH | Sus | 30998937 | yes | 2013 | MAY | Yes | Line to Ground | 99283125 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | SANTA MARIA-1108 | 182671108 | RECLOSER | M80 | 20130531 | 1240 | 801289 | 333 | Distribution Circuit | Equipment Failure/Involved | Other | 377 | 76338 | 35.0145 | -120.3599 | MTR #1007468222 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0035678 | OH | Sus | 41906000 | No | 2013 | MAY | Yes | Line to Ground | 99282463 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | ZACA-1102 | 182681102 | FUSE | 8091 | 20130602 | 340 | 802392 | 660 | Distribution Circuit | 3rd Party | Vehicle | 49 | 15279 | 34.6916 | -120.0621 | 1 POLE N/OF RISER 8327 | Clear-32 - 90 F | Pole-Wood | Broken, wire on object | 13-0035902 | OH | Sus | 31000242 | No | 2013 | JUN | Yes | Line to Line | 99282287 | PW | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V14 | 20130603 | 238 | 802965 | 362 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 497 | 53032 | 35.1794 | -120.6187 | 670 HANFORD | Overcast-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 13-0036016 | OH | Sus | 0 | No | 2013 | JUN | Yes | Line to Ground | 99282138 | CAW | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2113 | 183052113 | RECLOSER | A08 | 20130606 | 1450 | 804983 | 290 | Distribution Circuit | Animal | Bird found | 908 | 107380 | 35.4625 | -120.6222 | SS FUSE 5799 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0037206 | OH | Sus | 41908747 | No | 2013 | JUN | Yes | Line to Ground | 99281527 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V08 | 20130616 | 58 | 811158 | 682 | Distribution Circuit | 3rd Party | Vehicle | 353 | 98302 | 35.2449 | -120.6492 | BUCKLEY RD. E/OF SANTA FE | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0039988 | OH | Sus | 31003180 | No | 2013 | JUN | Yes | Line to Ground | 99279631 | PW | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | FOOTHILL-1101 | 182951101 | OTHER |  | 20130701 | 1754 | 823281 | 400 | Distribution Circuit | Equipment Failure/Involved | Other | 58 | 17785 | 35.3103 | -120.8125 | 1 SPAN SS OF 10545 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on object | 13-0044425 | OH | Sus | 0 | yes | 2013 | JUL | Yes | Open Circuit | 99276506 | CSO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | ATASCADERO-1101 | 182541101 | FUSE | 30225 | 20130712 | 1721 | 830563 | 464 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 68 | 13617 | 35.491 | -120.731 | BOLSA RD- ATASCADERO | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0047116 | OH | Sus | 31008304 | No | 2013 | JUL | Yes | Line to Ground | 99274491 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1103 | 183101103 | FUSE | 7369 | 20130718 | 701 | 833397 | 403 | Distribution Circuit | Equipment Failure/Involved | Other | 287 | 35817 | 34.6641 | -120.3827 | HAPGOOD & HWY 246 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0048220 | OH | Sus | 41929446 | No | 2013 | JUL | Yes | Multi-Fault | 99273660 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 4563 | 20130725 | 1542 | 838500 | 725 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2175 | 35.18 | -120.6976 | EDIE-BOB/5500/805-714-5101: 7 spans load side of 4563 | Clear-32 - 90 F | Other | Broken, wire on ground | 13-0050204 | OH | Sus | 41933047 | No | 2013 | JUL | Yes | Line to Ground | 99272318 | NON | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | FOOTHILL-1101 | 182951101 | OTHER |  | 20130805 | 1506 | 843474 | 641 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 726 | 35.2838 | -120.7463 | 7515 LOS OSOS VALLEY RD | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0052538 | OH | Sus | 31013058 | No | 2013 | AUG | Yes | Open Circuit | 99270841 | CSO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 10793 | 20130805 | 729 | 843127 | 316 | Distribution Circuit | Equipment Failure/Involved | Other | 11 | 1310 | 35.2277 | -120.6492 | MITCHELL: PRI WIRE DOWN ACROSS FROM 538 COUNTRY LN | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0052364 | OH | Sus | 41938002 | No | 2013 | AUG | Yes | Line to Ground | 99270911 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1103 | 182541103 | OTHER |  | 20130809 | 1639 | 845823 | 641 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 2206 | 35.4571 | -120.6541 | 10320 ATASCADERO AVE | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0053704 | OH | Sus | 31013977 | No | 2013 | AUG | Yes | Open Circuit | 99270105 | PW | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | BUELLTON-1102 | 183041102 | FUSE | 20195 | 20130918 | 2010 | 868290 | 449 | Distribution Circuit | Vegetation | Tree - branch fell on line | 43 | 13574 | 34.5827 | -120.1457 | 5 SP SS OF 7845 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0062989 | OH | Sus | 41961494 | No | 2013 | SEP | Yes |  | 99263305 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SISQUOC-1102 | 182811102 | FUSE | 6845 | 20131011 | 1345 | 883336 | 301 | Distribution Circuit | Equipment Failure/Involved | Other | 55 | 6772 | 34.831 | -120.2329 | ZACA MESA WINERY | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0069056 | OH | Sus | 31027900 | No | 2013 | OCT | Yes | Line to Ground | 99258859 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CAMBRIA-1102 | 182771102 | RECLOSER | W50 | 20131019 | 1032 | 887060 | 723 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 612 | 411120 | 35.567 | -121.1052 | ONE POLE LOAD SIDE OF W50 | Drizzle-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0070756 | OH | Sus | 31029632 | No | 2013 | OCT | Yes | Multi-Fault | 99257555 | PW | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | ATASCADERO-1101 | 182541101 | FUSE | 30225 | 20131028 | 1147 | 892551 | 460 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 31280 | 35.491 | -120.731 | 13575 SANTA LUCIA RD- 2 SPANS W/OF 30225 | Drizzle-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0072755 | OH | Sus | 31031817 | yes | 2013 | OCT | Yes | Line to Ground | 99256144 | PW | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | V74 | 20131203 | 1209 | 918600 | 221 | Distribution Circuit | Vegetation | Tree - fell into line | 522 | 33762 | 35.5459 | -121.0679 | BURTON BETWEEN BERWICK & KAY | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0080314 | OH | Sus | 31039738 | yes | 2013 | DEC | Yes | Line to Ground | 99249812 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | SWITCH | V41 | 20131203 | 1736 | 918848 | 57 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 3135 | 35.5455 | -121.076 | BURTON BETWEEN KAY & BERWICK | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0080314 | OH | Sus | 31039738 | yes | 2013 | DEC | Yes | Line to Ground | 99249769 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1102 | 182601102 | FUSE | 79899 | 20131206 | 353 | 920481 | 657 | Distribution Circuit | Animal | Other | 40 | 7380 | 35.065 | -120.5551 | 1831 VIEJO- NIPOMO | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 13-0080846 | OH | Sus | 31040807 | yes | 2013 | DEC | Yes |  | 99249330 | PW | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PURISIMA-1101 | 182971101 | RECLOSER | Y44 | 20131210 | 957 | 924906 | 86 | Distribution Circuit | 3rd Party | Customer Equipment | 180 | 15356 | 34.7191 | -120.4307 | 3602 HARRIS GRADE | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0081739 | OH | Sus | 0 | No | 2013 | DEC | Yes | Multi-Fault | 99248431 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2109 | 183052109 | FUSE | 6055 | 20131214 | 1517 | 927712 | 1504 | Distribution Circuit | 3rd Party | Vehicle | 302 | 71118 | 35.4542 | -120.4871 | 423 BLUE RD | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0082371 | OH | Sus | 31042892 | No | 2013 | DEC | Yes | Line to Ground | 99247741 | PW | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V08 | 20131216 | 1744 | 928599 | 576 | Distribution Circuit | 3rd Party | Vehicle | 353 | 42156 | 35.2449 | -120.6492 | MOLNAR- NICK: Buckley rd and Hoover rd | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0082559 | OH | Sus | 31043362 | No | 2013 | DEC | Yes |  | 99247510 | PW | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1104 | 183101104 | FUSE | 6085 | 20140113 | 1645 | 941341 | 495 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 495 | 34.5744 | -120.5173 | 12 SPANS S/OF FUSE-6085 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0003862 | OH | Sus | 42057849 | No | 2014 | JAN | Yes | Line to Ground | 99244410 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2113 | 183052113 | RECLOSER | A12 | 20140205 | 639 | 959907 | 423 | Distribution Circuit | Equipment Failure/Involved | Other | 129 | 29801 | 35.381 | -120.444 | 2 SPANS S/O CUT OUTS 6337 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0008850 | OH | Sus | 42070612 | No | 2014 | FEB | Yes | Line to Ground | 99241211 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 2421 | 20140208 | 545 | 962529 | 705 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5640 | 35.1972 | -120.6841 | 1 SPAN LOAD SIDE OF 2421 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0009832 | OH | Sus | 42073339 | yes | 2014 | FEB | Yes |  | 99240788 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OILFIELDS-1103 | 182391103 | RECLOSER | N48 | 20140213 | 731 | 966768 | 629 | Distribution Circuit | Equipment Failure/Involved | Other | 274 | 63188 | 35.7987 | -120.9744 | 7 POLES SW OF 2683 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0010981 | OH | Sus | 31056580 | No | 2014 | FEB | Yes | Line to Line | 99239830 | PW | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | MESA-1101 | 182821101 | FUSE | 15599 | 20140226 | 2305 | 973362 | 403 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 12229 | 35.0619 | -120.5197 | JUST SOURCE SIDE OF 8269 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0013710 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Ground | 99238050 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1101 | 182541101 | FUSE | 2381 | 20140228 | 1228 | 975168 | 302 | Distribution Circuit | Vegetation | Tree - branch fell on line | 70 | 21140 | 35.465 | -120.6854 | 1 SPAN LOAD SIDE OF 2381 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0014474 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Ground | 99237511 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | FUSE | 9179 | 20140301 | 500 | 976029 | 497 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 6226 | 35.5439 | -121.072 | Bradford & Preston in Cambria | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0014723 | OH | Sus | 0 | yes | 2014 | MAR | Yes | Line to Ground | 99237301 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V18 | 20140301 | 426 | 976016 | 318 | Distribution Circuit | Vegetation | Tree - palm frond fell into line | 985 | 97162 | 35.183 | -120.7038 | MTR 88030R | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0014708 | OH | Sus | 0 | yes | 2014 | MAR | Yes | Line to Ground | 99237312 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2113 | 183052113 | RECLOSER | A70 | 20140301 | 1004 | 976323 | 602 | Distribution Circuit | 3rd Party | Vehicle | 500 | 171442 | 35.5026 | -120.649 | MTR #1003224073 | Rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0014757 | OH | Sus | 0 | yes | 2014 | MAR | Yes | Line to Ground | 99237270 | PW | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | GOLDTREE-1105 | 182581105 | OCB | OCB | 20140308 | 1430 | 980952 | 345 | Distribution Circuit | Equipment Failure/Involved | Other | 2454 | 258676 | 35.3198 | -120.6927 | N/OF 5009- HIGHLAND & MT BISHOP- SLO | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0016703 | OH | Sus | 31061771 | No | 2014 | MAR | Yes | Multi-Fault | 99235864 | PW | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | W54 | 20140330 | 1923 | 992083 | 503 | Distribution Circuit | Equipment Failure/Involved | Other | 141 | 27143 | 35.5455 | -121.0844 | 676 RANDALL DR | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0021590 | OH | Sus | 42099738 | yes | 2014 | MAR | Yes | Multi-Fault | 99232407 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | GOLDTREE-1108 | 182581108 | FUSE | 10607 | 20140402 | 633 | 993946 | 317 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 4438 | 35.3161 | -120.6921 | LD SIDE OF MTR 1008471424 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0022357 | OH | Sus | 42100986 | yes | 2014 | APR | Yes | Line to Ground | 99231922 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1104 | 183101104 | OTHER |  | 20140427 | 1015 | 1005413 | 390 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 390 | 34.6331 | -120.5004 | 550 SAN PASQUAL RD | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0027631 | OH | Sus | 42113903 | No | 2014 | APR | Yes | Open Circuit | 99228386 | CSO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 3785 | 20140506 | 1741 | 1011239 | 814 | Distribution Circuit | Vegetation | Tree - fell into line | 820 | 173229 | 35.1803 | -120.7293 | 1) ON MAIN LINE SS OF MTR 5000031906- 2) ON MAIN LINE LOAD SIDE OF 4775 TAP. | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0029799 | OH | Sus | 42118081 | yes | 2014 | MAY | Yes | Line to Ground | 99226951 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1102 | 182601102 | FUSE | 14639 | 20140519 | 619 | 1020511 | 251 | Distribution Circuit | Equipment Failure/Involved | Other | 9 | 2820 | 35.0764 | -120.5471 | Just LD side of 14639 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0032745 | OH | Sus | 42125944 | yes | 2014 | MAY | Yes | Line to Ground | 99224999 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SANTA YNEZ-1102 | 182721102 | FUSE | 20195 | 20140527 | 1522 | 1024811 | 267 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 9024 | 34.5827 | -120.1457 | ELDER 5512: 3 POLES SS/RISER 20185 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0034557 | OH | Sus | 42130168 | No | 2014 | MAY | Yes | Line to Ground | 99223765 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1102 | 182601102 | FUSE | 15327 | 20140531 | 2210 | 1026913 | 830 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1660 | 35.0757 | -120.5428 | 1794 POMEROY RD. | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0035395 | OH | Sus | 42132341 | No | 2014 | MAY | Yes | Line to Ground | 99223132 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | MORRO BAY-1101 | 183011101 | SWITCH | 5243 | 20140610 | 2000 | 1032646 | 445 | Distribution Circuit | Equipment Failure/Involved | Other | 12 | 5340 | 35.3562 | -120.8295 | south Bay BLVD & State Park RD- 1 pole LS of 5243 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0037658 | OH | Sus | 0 | yes | 2014 | JUN | Yes | Line to Ground | 99221660 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PURISIMA-1101 | 182971101 | OTHER |  | 20140617 | 1647 | 1035901 | 589 | Distribution Circuit | Equipment Failure/Involved | Other | 51 | 25945 | 34.6878 | -120.4283 | COR OF VIA FELIZ & CALLE PRIMERA | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0038966 | OH | Sus | 42141074 | No | 2014 | JUN | Yes | Open Circuit | 99220630 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SANTA YNEZ-1104 | 182721104 | FUSE | 11361 | 20140620 | 1036 | 1037206 | 814 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 20422 | 34.636 | -119.976 | 7351 HAPPY CYN RD. | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0039640 | OH | Sus | 31083865 | No | 2014 | JUN | Yes |  | 99220195 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1103 | 183101103 | FUSE | 20015 | 20140710 | 1742 | 1047561 | 520 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 10278 | 34.6642 | -120.3728 | 1830 TULAROSA RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0043801 | OH | Sus | 42152771 | yes | 2014 | JUL | Yes |  | 99217208 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | GOLDTREE-1105 | 182581105 | OCB | OCB | 20140723 | 1216 | 1054059 | 667 | Distribution Circuit | 3rd Party | Vehicle | 2457 | 131567 | 35.3198 | -120.6927 | PEREZ- MARIO: TAFT AND CALIF. | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0046429 | OH | Sus | 31090709 | No | 2014 | JUL | Yes | Line to Ground | 99215372 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1104 | 183101104 | FUSE | 6345 | 20140728 | 2207 | 1057109 | 563 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 9027 | 34.6404 | -120.5021 | 1 POLE LOAD SIDE OF MTR#1008675219 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0047601 | OH | Sus | 42160377 | yes | 2014 | JUL | Yes | Line to Line | 99214513 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SANTA MARIA-1108 | 182671108 | FUSE | 63535 | 20140730 | 2236 | 1058491 | 844 | Distribution Circuit | Equipment Failure/Involved | Other | 13 | 8332 | 35.1028 | -120.3864 | 1 POLE SS OF MTR 1009572508 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0048186 | OH | Sus | 31092208 | yes | 2014 | JUL | Yes | Line to Ground | 99214147 | PW | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE | 6139 | 20140803 | 150 | 1060178 | 280 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1120 | 35.5322 | -120.7711 | 1SP LD SIDE OF MTR 1008498067 | Partly cloudy-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0048778 | OH | Sus | 42162654 | No | 2014 | AUG | Yes |  | 99213690 | CSO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1101 | 182631101 | RECLOSER | V12 | 20140813 | 616 | 1065735 | 349 | Distribution Circuit | Equipment Failure/Involved | Other | 200 | 30614 | 35.2952 | -120.6364 | 1 SPAN SS OF FU-9451 | Partly cloudy-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0050662 | OH | Sus | 31094669 | No | 2014 | AUG | Yes | Multi-Fault | 99212308 | CSO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CAMBRIA-1102 | 182771102 | RECLOSER | W50 | 20140820 | 554 | 1069109 | 372 | Distribution Circuit | Equipment Failure/Involved | Other | 611 | 227292 | 35.567 | -121.1052 | 364 NORFOLK | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0051927 | OH | Sus | 31096025 | No | 2014 | AUG | Yes | Multi-Fault | 99211129 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | ATASCADERO-1101 | 182541101 | FUSE | 30225 | 20140830 | 1528 | 1075152 | 587 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 39916 | 35.491 | -120.731 | 4 SP LD SIDE OF FUCO 30225 | Clear-Above 90 F | Conductor, Overhead | Broken, wire on ground | 14-0054261 | OH | Sus | 31098125 | No | 2014 | AUG | Yes | Line to Ground | 99209811 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE | 6607 | 20141004 | 1538 | 1092725 | 886 | Distribution Circuit | Vegetation | Tree - branch fell on line | 133 | 37852 | 35.5106 | -120.7137 | FUSES 2835- 2700 ALTURAS RD | Clear-Above 90 F | Conductor, Overhead | Broken, wire on ground | 14-0061415 | OH | Sus | 41887942 | No | 2014 | OCT | Yes | Line to Line | 99204907 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 9313 | 20141025 | 1421 | 1102682 | 881 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 14977 | 35.132 | -120.5558 | MTR#1005764110 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0066084 | OH | Sus | 31110136 | yes | 2014 | OCT | Yes |  | 99202024 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PASO ROBLES-1103 | 182611103 | RECLOSER | N54 | 20141027 | 1409 | 1103709 | 299 | Distribution Circuit | Animal | Bird found | 1986 | 137838 | 35.6545 | -120.7256 | CGC 511868080520/2 SPANS LD SIDE OF FUCO 12037 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0066395 | OH | Sus | 42216737 | No | 2014 | OCT | Yes | Line to Ground | 99201713 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1104 | 183101104 | FUSE | 6345 | 20141110 | 1343 | 1111249 | 784 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 11130 | 34.6404 | -120.5021 | ELDER 5512: 807 SAN PASQUAL RD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0069346 | OH | Sus | 31114145 | No | 2014 | NOV | Yes | Three Phase Fault | 99199722 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | MORRO BAY-1101 | 183011101 | FUSE | 75931 | 20141202 | 924 | 1120714 | 436 | Distribution Circuit | Equipment Failure/Involved | Other | 35 | 8133 | 35.3626 | -120.8343 | MTR 5000008721 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0072864 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99197200 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2110 | 183052110 | FUSE | 30185 | 20141205 | 1540 | 1125398 | 614 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 4238 | 35.5985 | -120.8319 | AT MTR 1009175570 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074077 | OH | Sus | 42291573 | No | 2014 | DEC | Yes | Line to Line | 99196198 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | BUELLTON-1102 | 183041102 | FUSE | 7721 | 20141213 | 849 | 1139562 | 731 | Distribution Circuit | Equipment Failure/Involved | Other | 7 | 2277 | 34.5883 | -120.158 | 3 SP SS OF 182295 | Partly cloudy-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0076689 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99193393 | CSO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SANTA YNEZ-1104 | 182721104 | OTHER |  | 20141213 | 1651 | 1140073 | 137 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 137 | 34.6312 | -120.0264 | 2 POLE LOAD SIDE OF MAIN LINE MTR#1008627237 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076804 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99193295 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CAMBRIA-1102 | 182771102 | OTHER |  | 20141215 | 1826 | 1141666 | 528 | Distribution Circuit | Vegetation | Tree - fell into line | 1243 | 83135 | 35.5731 | -121.1066 | 1 POLE SS OF MTR#1006260716 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077103 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99192934 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | W12 | 20141215 | 1620 | 1141552 | 385 | Distribution Circuit | Vegetation | Tree - fell into line | 929 | 46691 | 35.5487 | -121.0892 | Burton and Berwick | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077090 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99192946 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 4923 | 20141220 | 442 | 1144848 | 498 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 3394 | 35.2128 | -120.7266 | LOAD SIDE OF SIREN 312 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077778 | OH | Sus | 42301467 | No | 2014 | DEC | Yes | Line to Ground | 99192130 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | FUSE | 4747 | 20141231 | 1014 | 1156719 | 376 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 30456 | 35.5503 | -121.0856 | MTR 1008746032 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079698 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99190015 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 2015 | 20150214 | 1247 | 1190114 | 583 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 15705 | 35.1488 | -120.5879 | 1 SPAN LOAD SIDE OF 11005 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0013347 | OH | Sus | 42334022 | No | 2015 | FEB | Yes | Line to Line | 99182015 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 3211 | 20150215 | 1315 | 1190447 | 465 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 7275 | 35.1492 | -120.5997 | 507 ERHART | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0013452 | OH | Sus | 42334049 | No | 2015 | FEB | Yes | Line to Line | 99181926 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE | 4479 | 20150219 | 1201 | 1192625 | 239 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1195 | 35.5353 | -120.7779 | 2 SPANS SS OF FUSES 4481 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0014321 | OH | Sus | 42335797 | No | 2015 | FEB | Yes | Line to Line | 99181339 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ZACA-1102 | 182681102 | FUSE | 7975 | 20150226 | 2307 | 1196458 | 468 | Distribution Circuit | Equipment Failure/Involved | Other | 21 | 7058 | 34.6568 | -120.0898 | MAIN TAP 1 SP PAST FUCO 20699 | Fog-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0016054 | OH | Sus | 31137354 | No | 2015 | FEB | Yes | Line to Ground | 99180241 | PW | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | BUELLTON-1101 | 183041101 | FUSE | 7305 | 20150315 | 2142 | 1203954 | 230 | Distribution Circuit | Equipment Failure/Involved | Other | 5 | 1890 | 34.6221 | -120.2437 | 1607 W. HWY 236- BUELLTON MTR#1008681087 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0019707 | OH | Sus | 42350157 | No | 2015 | MAR | Yes | Line to Ground | 99178050 | CSO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2110 | 183052110 | RECLOSER | N30 | 20150318 | 449 | 1204885 | 595 | Distribution Circuit | Equipment Failure/Involved | Other | 83 | 49385 | 35.6263 | -120.8962 | 1 span s/o fuses 93301 Chimney Rock Rd. | Clear-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 15-0020244 | OH | Sus | 31141981 | No | 2015 | MAR | Yes | Line to Ground | 99177770 | CAW | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PASO ROBLES-1103 | 182611103 | FUSE | 4019 | 20150524 | 1043 | 1239011 | 550 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 22790 | 35.6667 | -120.7255 | 6 SP LS OF 4019 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0036222 | OH | Sus | 31156799 | No | 2015 | MAY | Yes | Three Phase Fault | 99167186 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2113 | 183052113 | RECLOSER | A10 | 20150620 | 1521 | 1253873 | 1457 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 408 | 131281 | 35.4108 | -120.5657 | LAS PALITAS AND PARKKHILL | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0042292 | OH | Sus | 31162567 | No | 2015 | JUN | Yes | Force Out | 99162723 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | ATASCADERO-1101 | 182541101 | FUSE | 30225 | 20150628 | 250 | 1258012 | 651 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 12323 | 35.491 | -120.731 | 13505 SANTA LUCIA- ATASCADERO | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0043807 | OH | Sus | 31164731 | No | 2015 | JUN | Yes | Line to Ground | 99161548 | CO | OH | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 5321 | 20150629 | 623 | 1258431 | 441 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 7497 | 35.2356 | -120.4723 | PEREZ- MARIO: UPPER LOPEZ CANYON | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0043915 | OH | Sus | 42417030 | No | 2015 | JUN | Yes | Line to Ground | 99161422 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2110 | 183052110 | OTHER | 1 SP LS OF MTR#1008493290 | 20150703 | 150 | 1262219 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 978 | 35.6787 | -120.956 | 1 SP LS OF MTR#1008493290 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0045239 | OH | Sus | 31165791 | yes | 2015 | JUL | Yes | Line to Ground | 1143656 | CO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1101 | 182541101 | FUSE | 7433 | 20150729 | 1215 | 1279425 | 516 | Distribution Circuit | 3rd Party | Vehicle | 92 | 39462 | 35.4691 | -120.6973 | 10535 SAN MARCOS X-ST PORTAL - ATASCADERO- 1 SPAN SS OF FUSE-7339 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0051316 | OH | Sus | 0 | yes | 2015 | JUL | Yes | Line to Line | 1148121 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN MIGUEL-1106 | 182661106 | FUSE | 6963 | 20150801 | 2 | 1281064 | 817 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 7353 | 35.9989 | -120.645 | 13 SPANS LD SIDE OF 6963 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0052039 | OH | Sus | 31173256 | No | 2015 | AUG | Yes | Line to Ground | 1148543 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2111 | 183052111 | OTHER | WIRE DOWN MAIN LINE LD SIDE OF TAP WITH 6595 | 20150816 | 2206 | 1289945 | 549 | Distribution Circuit | Vegetation | Tree - branch fell on line | 171 | 14718 | 35.502 | -120.7089 | MAIN LINE LOAD SIDE OF TAP WITH 6595 | Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0055415 | OH | Sus | 0 | yes | 2015 | AUG | Yes | Line to Ground | 1151039 | CO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 3 | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 3255 | 20150822 | 1520 | 1293019 | 295 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1030 | 35.2413 | -120.7793 | 2/S/O LINE AND BUCK ON COON CREEK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 15-0056756 | OH | Sus | 31178245 | No | 2015 | AUG | Yes | Line to Ground | 1151906 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | BUELLTON-1101 | 183041101 | FUSE | 63819 | 20150906 | 1927 | 1301043 | 495 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 863 | 34.6204 | -120.254 | 2090 W. HWY-246- BUELLTON | Clear-32-90 F | Insulator | Broken, wire on ground | 15-0059612 | OH | Sus | 42465602 | No | 2015 | SEP | Yes | Line to Ground | 1153979 | INS | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | MORRO BAY-1102 | 183011102 | FUSE | 10163 | 20151007 | 1504 | 1318382 | 685 | Distribution Circuit | 3rd Party | Vehicle | 134 | 77896 | 35.3079 | -120.8328 | 1550 Bayview heights | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0068730 | OH | Sus | 0 | No | 2015 | OCT | Yes | Line to Ground | 1161200 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1108 | 182601108 | FUSE | 10055 | 20151109 | 745 | 1337696 | 385 | Distribution Circuit | 3rd Party | Vehicle | 6 | 2310 | 35.0899 | -120.5598 | PEREZ- MARIO: POLE | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0076584 | OH | Sus | 31198777 | yes | 2015 | NOV | Yes | Line to Ground | 1167327 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SANTA MARIA-1108 | 182671108 | OTHER | WIRE DOWN @ 7345 | 20151109 | 555 | 1337658 | 664 | Distribution Circuit | Equipment Failure/Involved | Overhead | 441 | 203063 | 35.0064 | -120.3587 | LD SIDE OF SW 7345 | Rain-Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0076534 | OH | Sus | 42564041 | yes | 2015 | NOV | Yes | Line to Ground | 1167287 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | FOOTHILL-1102 | 182951102 | OCB | 1102/2 | 20151115 | 803 | 1341446 | 801 | Distribution Circuit | 3rd Party | Vehicle | 3276 | 496047 | 35.2865 | -120.7064 | at V-06 POLE & POLE 1 SPAN LOAD SIDE (EAST) OF V-06 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 15-0077835 | OH | Sus | 0 | yes | 2015 | NOV | Yes | Line to Line | 1168312 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 2293 | 20151115 | 818 | 1341474 | 1002 | Distribution Circuit | Equipment Failure/Involved | Overhead | 520 | 56273 | 35.1919 | -120.4565 | PEREZ- MARIO: SEWER PLANT/ 2/P PAST MTR# M07690 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0077866 | OH | Sus | 0 | yes | 2015 | NOV | Yes | Line to Line | 1168343 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1104 | 183101104 | FUSE | 6085 | 20151118 | 804 | 1344555 | 821 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 821 | 34.574 | -120.5173 | 16-18 SPANS FROM END OF LINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0078832 | OH | Sus | 42570731 | No | 2015 | NOV | Yes | Line to Line | 1169180 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | JUMPER | WIRE DWN LD S/O 10971 | 20151125 | 639 | 1348396 | 405 | Distribution Circuit | Animal | Bird found | 292 | 20878 | 35.5476 | -121.0793 | LS 10971 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0080980 | OH | Sus | 31202933 | No | 2015 | NOV | Yes | Line to Ground | 1170876 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2111 | 183052111 | RECLOSER | N30 | 20151201 | 1203 | 1351300 | 644 | Distribution Circuit | Equipment Failure/Involved | Overhead | 526 | 42427 | 35.6261 | -120.8962 | 1 SP SS 6291- 16624 CHIMNEY ROCK | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0081983 | OH | Sus | 31203682 | No | 2015 | DEC | Yes | Line to Ground | 1171743 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2113 | 183052113 | FUSE | 3947 | 20151227 | 406 | 1372324 | 1005 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 56895 | 35.4286 | -120.4773 | NW OF MTR 1007755960 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 15-0087486 | OH | Sus | 42597908 | No | 2015 | DEC | Yes | Line to Ground | 1177570 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1103 | 182541103 | RECLOSER | A14 | 20160102 | 2311 | 1376070 | 922 | Distribution Circuit | 3rd Party | Vehicle | 170 | 35922 | 35.3237 | -120.5163 | AT LR 76144 PARK HILL RD .5 MIL N/OF POZO TURN OFF | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0002540 | OH | Sus | 0 | No | 2016 | JAN | Yes | Multi-Fault | 1178454 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 9309 | 20160106 | 1237 | 1378544 | 576 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4032 | 35.1426 | -120.5789 | MTR# 1006256650 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003468 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Force Out | 1179033 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | FOOTHILL-1101 | 182951101 | JUMPER | OJ ON HARD TAP FEEDING MTR#1008441492 | 20160108 | 2335 | 1380563 | 455 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 6825 | 35.3106 | -120.7376 | 804 OCONNOR WAY | Clear-32-90 F | Conductor, Overhead | On Ground | 16-0004169 | OH | Sus | 31211477 | No | 2016 | JAN | Yes | Force Out | 1179587 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CAMBRIA-1101 | 182771101 | FUSE | 5319 | 20160119 | 1504 | 1387838 | 1721 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 74003 | 35.6951 | -121.2913 | ARROJO DE LA CRUZ CREEK | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 16-0006568 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Three Phase Fault | 1181389 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 2241 | 20160119 | 1710 | 1387998 | 1670 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 18432 | 35.1958 | -120.6845 | MTR 5000073427 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0006630 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1181439 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1101 | 182541101 | FUSE | 2379 | 20160130 | 2230 | 1394643 | 513 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 12825 | 35.4651 | -120.6834 | 1 SPAN SOUTH EAST OF INTERSEC OF SIERRA VISTA AND CASITAS RD - 8707 SIERRA VISTA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009340 | OH | Sus | 31216081 | No | 2016 | JAN | Yes | Line to Ground | 1183429 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | FUSE | 9545 | 20160131 | 1459 | 1394936 | 409 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 4830 | 35.5429 | -121.0742 | 1090 ELLIS | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009429 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1183505 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1105 | 182631105 | FUSE | 3043 | 20160225 | 828 | 1412038 | 367 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 11377 | 35.2878 | -120.6501 | at MTR#1008718409 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0015529 | OH | Sus | 0 | No | 2016 | FEB | Yes | Line to Ground | 1188073 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CAMBRIA-1102 | 182771102 | FUSE | 3865 | 20160307 | 102 | 1422968 | 1066 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 86346 | 35.5742 | -121.1038 | BUCKLEY & CHARLING | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018634 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190480 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | CAYUCOS-1102 | 182551102 | FUSE | 4133 | 20160307 | 1013 | 1423726 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 17920 | 35.4761 | -120.8197 | 2 SPANS LOAD SIDE OF 4133 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018976 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190733 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 15185 | 20160307 | 317 | 1423060 | 507 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 8136 | 35.1493 | -120.5715 | 2 P N/W MTR#1008473032 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018699 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190542 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | V74 | 20160307 | 636 | 1423054 | 1074 | Distribution Circuit | Vegetation | Tree - fell into line | 331 | 13954 | 35.5457 | -121.0679 | MOLNAR- NICK: Bradford between pierce and kay | Overcast-Fog-Heavy Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0018714 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Multi-Fault | 1190555 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | V78 | 20160307 | 931 | 1423632 | 1775 | Distribution Circuit | Vegetation | Tree - branch fell on line | 125 | 101785 | 35.5731 | -121.0412 | MOLNAR- NICK: 1 span loadside of5861 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018835 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190645 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 10723 | 20160307 | 540 | 1423325 | 1192 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 83440 | 35.1985 | -120.4302 | MTR 1009775598 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018879 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190678 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 10013 | 20160307 | 235 | 1423030 | 1119 | Distribution Circuit | Equipment Failure/Involved | Overhead | 160 | 179040 | 35.1942 | -120.7262 | TAKE OFF POLE TO TAP FEEDING 10021 | Clear-Strong Winds-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0018669 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190512 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ZACA-1102 | 182681102 | RECLOSER | Y54 | 20160307 | 438 | 1423162 | 1002 | Distribution Circuit | Equipment Failure/Involved | Overhead | 303 | 273306 | 34.6533 | -120.0714 | ELDER 5512: TWO SPANS LOAD OF Y54 AND WIRE DOWN ON HARD TAP at MTR# 1008442859 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 16-0018673 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190517 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE | 5581 | 20160311 | 1009 | 1427347 | 1903 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 29821 | 35.5552 | -120.8377 | MTR # 1007174695 // 10055 DOVER CANYON RD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020379 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1191816 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE | 2679 | 20160312 | 1127 | 1429385 | 377 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4524 | 35.5461 | -120.8234 | COX- BOB: 4885 Shadow Canyon- Templeton | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020774 | OH | Sus | 42655790 | yes | 2016 | MAR | Yes | Line to Line | 1192153 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | V74 | 20160313 | 1307 | 1430213 | 798 | Distribution Circuit | Vegetation | Tree - fell into line | 522 | 25947 | 35.5457 | -121.0679 | TAP FEEDING 14837 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0020947 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192325 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE | 30563 | 20160326 | 2244 | 1439250 | 1014 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 29406 | 35.5131 | -120.7111 | 7805 DEL RIO ROAD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0024216 | OH | Sus | 0 | No | 2016 | MAR | Yes | Three Phase Fault | 1194774 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2110 | 183052110 | FUSE | 2669 | 20160410 | 2044 | 1448484 | 491 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2455 | 35.5746 | -120.7938 | BETWEEN METER # 1009175523 & C/OUTS 6579 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0027649 | OH | Sus | 42675791 | No | 2016 | APR | Yes | Line to Ground | 1197240 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PURISIMA-1101 | 182971101 | OTHER | WIRE DOWN @ MTR# 1008778858 | 20160424 | 1110 | 1457036 | 812 | Distribution Circuit | Vegetation | Tree - fell into line | 2075 | 154288 | 34.7083 | -120.4618 | BRIGGS- JOHN: 3916 Rigel | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0031023 | OH | Sus | 42684594 | yes | 2016 | APR | Yes | Line to Ground | 1199700 | CO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | FOOTHILL-1101 | 182951101 | FUSE | 3561 | 20160503 | 842 | 1463791 | 414 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 4554 | 35.2924 | -120.7159 | 399 O'CONNER WAY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0033462 | OH | Sus | 0 | No | 2016 | MAY | Yes | Line to Ground | 1201694 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | FOOTHILL-1101 | 182951101 | FUSE | 9973 | 20160512 | 1047 | 1468597 | 224 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 7616 | 35.2868 | -120.7204 | 1 SPAN SS OF MTR# 1008720517 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0035574 | OH | Sus | 31238280 | No | 2016 | MAY | Yes | Line to Ground | 1203200 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 2293 | 20160512 | 2015 | 1468946 | 1405 | Distribution Circuit | Equipment Failure/Involved | Overhead | 48 | 54088 | 35.1919 | -120.4565 | MCKELL- JIM: load side of 2293 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0035728 | OH | Sus | 0 | No | 2016 | MAY | Yes | Line to Ground | 1203270 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1103 | 183101103 | FUSE | 20917 | 20160520 | 1600 | 1473796 | 505 | Distribution Circuit | 3rd Party | Vehicle | 1 | 505 | 34.6643 | -120.3976 | 1 SP LD SIDE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0037477 | OH | Sus | 0 | yes | 2016 | MAY | Yes | Line to Line | 1204513 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | GOLDTREE-1105 | 182581105 | OCB | 1105/2 | 20160607 | 2225 | 1484966 | 962 | Distribution Circuit | 3rd Party | Vehicle | 2473 | 110926 | 35.3203 | -120.6932 | 1 PL W/OF 14113 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0041795 | OH | Sus | 0 | No | 2016 | JUN | Yes | Line to Ground | 1207916 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OILFIELDS-1103 | 182391103 | FUSE | 5935 | 20160622 | 2319 | 1494379 | 608 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 5972 | 35.5428 | -120.7645 | MCKELL- JAMES: Indian camp and cloudy meadow | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0045209 | OH | Sus | 31249011 | No | 2016 | JUN | Yes | Line to Line | 1210476 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE | 3871 | 20160623 | 2204 | 1494957 | 146 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 584 | 35.5975 | -120.8014 | NEAR TRANSFORMER 511691777800 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0045486 | OH | Sus | 0 | No | 2016 | JUN | Yes | Line to Line | 1210636 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | CAYUCOS-1102 | 182551102 | JUMPER | OJ 1/SS OF 4133 | 20160628 | 1841 | 1497863 | 516 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 8256 | 35.4759 | -120.8197 | 1 SPAN SOURCE SIDE OF FUSE 4133 | Partly Cloudy-Heat Wave-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0046452 | OH | Sus | 0 | yes | 2016 | JUN | Yes | Open Circuit | 1211372 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | ATASCADERO-1103 | 182541103 | FUSE | 34413 | 20160629 | 1833 | 1498452 | 565 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 6687 | 35.4593 | -120.7503 | COX- BOB: 3 spans s/o intersection of Morro Rd & Toro Creek-to the Cal fire station | Partly Cloudy-Heat Wave-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0046752 | OH | Sus | 31250291 | No | 2016 | JUN | Yes | Line to Line | 1211557 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | BUELLTON-1101 | 183041101 | OTHER | WIRE DOWN TAP TWD MTR 1008342715 | 20160702 | 1551 | 1500239 | 414 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 2996 | 34.6431 | -120.2796 | MTR# 1008342715 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0047594 | OH | Sus | 42735319 | No | 2016 | JUL | Yes | Line to Ground | 1212135 | CSO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2113 | 183052113 | RECLOSER | A12 | 20160712 | 1418 | 1508960 | 425 | Distribution Circuit | Vegetation | Tree - branch fell on line | 131 | 18883 | 35.3806 | -120.4432 | 1 LD SIDE OF 7193 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0049403 | OH | Sus | 31257021 | No | 2016 | JUL | Yes | Line to Ground | 1213513 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1104 | 182631104 | OTHER | WIRE DOWN 1 POLE S/S OF 15889 | 20160715 | 519 | 1510438 | 645 | Distribution Circuit | Equipment Failure/Involved | Overhead | 208 | 62404 | 35.1838 | -120.5025 | 1 POLE SS 15889 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0050086 | OH | Sus | 0 | No | 2016 | JUL | Yes | Line to Ground | 1214002 | CSO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1101 | 182541101 | FUSE | 30459 | 20160724 | 1359 | 1515101 | 837 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 31400 | 35.4755 | -120.6805 | 1 SPAN LD SIDE OF MTR#1008187360 (NEXT 3 POLES DOWN ON GROUND) | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0052110 | OH | Sus | 0 | No | 2016 | JUL | Yes | Line to Ground | 1215378 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2113 | 183052113 | RECLOSER | A12 | 20160728 | 241 | 1517550 | 466 | Distribution Circuit | Vegetation | Tree - branch fell on line | 131 | 22592 | 35.3806 | -120.4432 | COX- BOB: second span load side of SW-5131 Parkhill Rd-next to Transmission line | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0053127 | OH | Sus | 31259855 | yes | 2016 | JUL | Yes | Line to Ground | 1216123 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | RECLOSER | Q10 | 20160903 | 213 | 1536182 | 913 | Distribution Circuit | 3rd Party | Vehicle | 743 | 175804 | 35.1351 | -120.5694 | AT MTR #1006257414 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 16-0062194 | OH | Sus | 0 | No | 2016 | SEP | Yes | Three Phase Fault | 1222138 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1105 | 182601105 | OCB | 1105/2 | 20160906 | 1416 | 1537360 | 543 | Distribution Circuit | Animal | Bird found | 6046 | 241784 | 35.101 | -120.581 | 2 POLES E/OF SW 3149 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0062674 | OH | Sus | 31269465 | No | 2016 | SEP | Yes | Line to Ground | 1222498 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | FUSE | 4747 | 20160922 | 1422 | 1546201 | 848 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 12093 | 35.5503 | -121.0856 | MTR 1008746034 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0066719 | OH | Sus | 0 | No | 2016 | SEP | Yes | Line to Ground | 1225268 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1108 | 182601108 | FUSE | 65305 | 20160929 | 226 | 1549707 | 450 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 6450 | 35.0684 | -120.5597 | 2141 HALCYON | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0068308 | OH | Sus | 31274120 | No | 2016 | SEP | Yes | Line to Ground | 1226401 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | ATASCADERO-1101 | 182541101 | FUSE | 2795 | 20161021 | 1706 | 1567273 | 371 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 5733 | 35.4835 | -120.7237 | IFO 12085 CENEGAL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0074667 | OH | Sus | 31279566 | No | 2016 | OCT | Yes | Line to Ground | 1231271 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1101 | 182541101 | RECLOSER | A02 | 20161028 | 457 | 1571407 | 439 | Distribution Circuit | Equipment Failure/Involved | Overhead | 487 | 55215 | 35.4838 | -120.6842 | 5700 LLANO | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0076204 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Multi-Fault | 1232479 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | FOOTHILL-1101 | 182951101 | OTHER | 3561 | 20161113 | 1239 | 1580490 | 297 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3267 | 35.2924 | -120.7159 | 6 LD SIDE OF 3561 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0079530 | OH | Sus | 31283705 | No | 2016 | NOV | Yes | Force Out | 1235024 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2113 | 183052113 | FUSE | 5655 | 20161114 | 1315 | 1580994 | 1005 | Distribution Circuit | Equipment Failure/Involved | Overhead | 54 | 19590 | 35.4577 | -120.4619 | METER # 1010088907 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0079725 | OH | Sus | 0 | No | 2016 | NOV | Yes | Line to Ground | 1235203 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 3781 | 20161120 | 1431 | 1585829 | 429 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 9484 | 35.1942 | -120.5641 | 2 SPANS LOADSIDE 3781 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081268 | OH | Sus | 42882842 | yes | 2016 | NOV | Yes | Line to Ground | 1236300 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | FOOTHILL-1101 | 182951101 | FUSE | 9973 | 20161202 | 1242 | 1593529 | 252 | Distribution Circuit | Animal | Bird found | 35 | 8820 | 35.2868 | -120.7204 | at METER # 1008720528 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0083651 | OH | Sus | 31286853 | No | 2016 | DEC | Yes | Line to Ground | 1238203 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | SANTA MARIA-1108 | 182671108 | JUMPER | WIRE DOWN 2 POLES LD SIDE OF LINE & BUCK PAST | 20161211 | 802 | 1599594 | 360 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 12600 | 35.0176 | -120.3316 | WIRE DOWN 2 POLES LD SIDE OF LINE & BUCK PAST | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0085063 | OH | Sus | 0 | No | 2016 | DEC | Yes | Open Circuit | 1239622 | CSO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | V74 | 20161215 | 1424 | 1602887 | 453 | Distribution Circuit | Vegetation | Tree - fell into line | 381 | 18320 | 35.5457 | -121.0679 | 1665 BURTON DR | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085748 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1240418 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE | 3551 | 20161216 | 846 | 1604427 | 454 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1920 | 35.4906 | -120.688 | 1 LD SIDE OF 1007461889 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0086010 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1240709 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PASO ROBLES-1104 | 182611104 | JUMPER | OJS 1 SPAN S/OF 31873 | 20161221 | 816 | 1608184 | 323 | Distribution Circuit | 3rd Party | Vehicle | 5 | 1575 | 35.6498 | -120.7208 | MCKELL- JAMES: adelaida rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0086605 | OH | Sus | 0 | No | 2016 | DEC | Yes | Line to Ground | 1241618 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V60 | 20161221 | 650 | 1608159 | 210 | Distribution Circuit | Animal | Bird found | 1177 | 82000 | 35.1846 | -120.7043 | STOWELL- DOUG: 1691 SEE CYN RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0086595 | OH | Sus | 31290944 | No | 2016 | DEC | Yes | Line to Ground | 1241585 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CAMBRIA-1101 | 182771101 | FUSE | 5319 | 20170112 | 854 | 1641156 | 652 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 11200 | 35.6951 | -121.2913 | 1 SS OF 193563 | Overcast-Fog-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0008380 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247780 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2113 | 183052113 | FUSE | 6347 | 20170124 | 1508 | 1665988 | 207 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 455 | 35.386 | -120.4711 | OPEN JUMPER at 6347 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0014510 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1253183 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SANTA YNEZ-1102 | 182721102 | FUSE | 20613 | 20170126 | 808 | 1667573 | 185 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 2220 | 34.6068 | -120.1256 | 3 SPANS LD SIDE OF 20613 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | On Ground | 17-0015260 | OH | Sus | 42932895 | No | 2017 | JAN | Yes | Line to Ground | 1253827 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1101 | 182631101 | FUSE | 5287 | 20170130 | 354 | 1670141 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 29001 | 35.372 | -120.6468 | 15 LD SIDE OF 5287 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0015968 | OH | Sus | 42934810 | No | 2017 | JAN | Yes | Line to Ground | 1254390 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SANTA YNEZ-1102 | 182721102 | FUSE | 20613 | 20170130 | 422 | 1670130 | 317 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 4121 | 34.6068 | -120.1256 | MTR 1008545022 | Fog-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0015967 | OH | Sus | 42934809 | No | 2017 | JAN | Yes | Line to Ground | 1254389 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | SAN LUIS OBISPO-1107 | 182631107 | JUMPER | WIRE DOWN SOURCE MTR 22068R | 20170131 | 1933 | 1671651 | 552 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 1455 | 35.1921 | -120.6766 | WIRE DOWN SOURCE MTR 22068R | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0016462 | OH | Sus | 42936004 | No | 2017 | JAN | Yes | Line to Ground | 1254745 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE | 4601 | 20170208 | 1646 | 1682330 | 578 | Distribution Circuit | 3rd Party | Vehicle | 88 | 15492 | 35.4902 | -120.6874 | LAYUGAN- JIM: 5020 ARDILLA | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 17-0019132 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256746 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1103 | 182631103 | FUSE | 69045 | 20170223 | 1040 | 1711883 | 602 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 5042 | 35.2239 | -120.6257 | 5458 EDNA RD | Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0025989 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1262742 | CO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1108 | 182601108 | FUSE | 8631 | 20170226 | 1144 | 1714322 | 181 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 3801 | 35.0678 | -120.594 | 2594 FOWLER LN | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0026863 | OH | Sus | 31307885 | No | 2017 | FEB | Yes | Line to Line | 1263562 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1103 | 182601103 | FUSE | 9891 | 20170308 | 932 | 1722331 | 776 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 31248 | 35.1301 | -120.5745 | 9161 | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 17-0029322 | OH | Sus | 31311203 | No | 2017 | MAR | Yes | Multi-Fault | 1265474 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ZACA-1102 | 182681102 | OTHER | WIRE DOWN 6 P N/O Y26 | 20170314 | 726 | 1726638 | 315 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2171 | 284873 | 34.6289 | -120.1886 | 6 P N/O Y26 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0030594 | OH | Sus | 42969269 | No | 2017 | MAR | Yes | Line to Ground | 1266431 | CO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | FOOTHILL-1101 | 182951101 | OCB | 1101/2 | 20170320 | 451 | 1730366 | 604 | Distribution Circuit | 3rd Party | Vehicle | 771 | 43745 | 35.2865 | -120.7064 | LOS OSOS VALLEY RD AND JACARANDA RD at FCO 2801 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0031823 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Ground | 1267431 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SISQUOC-1102 | 182811102 | FUSE | 6845 | 20170327 | 1708 | 1737089 | 861 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 39480 | 34.8311 | -120.2334 | 3 SPANS S/S OF METER # 500031254 | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0034293 | OH | Sus | 31315154 | yes | 2017 | MAR | Yes | Line to Ground | 1269131 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ZACA-1101 | 182681101 | RECLOSER | Y70 | 20170327 | 2234 | 1737122 | 696 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 18414 | 34.7339 | -120.1265 | ELDER 5512: 6893 FOXEN CANYON RD | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0034283 | OH | Sus | 42978270 | yes | 2017 | MAR | Yes | Line to Line | 1269117 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2113 | 183052113 | FUSE | 3945 | 20170331 | 1139 | 1741157 | 405 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 3037 | 35.4397 | -120.4882 | 2 SPAN LOAD SIDE MTR 1007998317 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0035592 | OH | Sus | 42981610 | yes | 2017 | MAR | Yes | Line to Ground | 1270169 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PASO ROBLES-1103 | 182611103 | RECLOSER | N52 | 20170404 | 1329 | 1744013 | 821 | Distribution Circuit | 3rd Party | Vehicle | 1746 | 167151 | 35.6885 | -120.7653 | Spinola- Richard: NACIMIENTO LAKE DR. | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0036460 | OH | Sus | 0 | No | 2017 | APR | Yes | Three Phase Fault | 1270948 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1103 | 183101103 | FUSE | 7195 | 20170412 | 1652 | 1756121 | 345 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1380 | 34.6086 | -120.3651 | LOAD SIDE CLOUTS | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0039665 | OH | Sus | 42993316 | No | 2017 | APR | Yes | Line to Ground | 1273416 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | BUELLTON-1101 | 183041101 | FUSE | 20149 | 20170419 | 716 | 1760786 | 301 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 5493 | 34.5313 | -120.2913 | 3 SPANS L/S OF 22063 | Partly Cloudy-Fog-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0041351 | OH | Sus | 42997553 | No | 2017 | APR | Yes | Line to Ground | 1274663 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ZACA-1102 | 182681102 | FUSE | 1225 | 20170420 | 1632 | 1762112 | 287 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 6888 | 34.6447 | -120.1151 | 2800 Ontiveros Rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0041787 | OH | Sus | 42998398 | No | 2017 | APR | Yes | Line to Ground | 1274973 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | FUSE | 15567 | 20170425 | 1603 | 1766973 | 736 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 10541 | 35.5574 | -121.0828 | 2830 BUTRON CIR MTR#1008472844 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0042886 | OH | Sus | 0 | No | 2017 | APR | Yes | Line to Ground | 1275767 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 11005 | 20170426 | 1857 | 1767857 | 480 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1440 | 35.1579 | -120.5866 | AT C/OUTS LOAD SIDE | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0043185 | OH | Sus | 43001611 | No | 2017 | APR | Yes | Line to Ground | 1275965 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | FOOTHILL-1101 | 182951101 | OCB | 1101/2 | 20170504 | 535 | 1774240 | 539 | Distribution Circuit | 3rd Party | Vehicle | 774 | 94046 | 35.2865 | -120.7064 | at FUSE 14409 ON MAINLINE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0045095 | OH | Sus | 0 | yes | 2017 | MAY | Yes | Line to Line | 1277442 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1104 | 182631104 | OTHER | 1104/2 | 20170509 | 1503 | 1778744 | 322 | Distribution Circuit | Equipment Failure/Involved | Overhead | 602 | 59048 | 35.1792 | -120.618 | AT LR V14 | Partly Cloudy-32-90 F | Insulator | Broken, wire on ground | 17-0042469 | OH | Sus | 31294872 | No | 2017 | MAY | Yes | Line to Ground | 1278618 | INS | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2110 | 183052110 | OTHER | WIRE DOWN 1 N/O LR N32 | 20170514 | 1915 | 1781999 | 465 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 1539 | 337188 | 35.6826 | -120.9357 | 1 P LD SIDE OF N32 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0047837 | OH | Sus | 43016254 | No | 2017 | MAY | Yes | Line to Ground | 1279513 | CAW | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 10895 | 20170602 | 553 | 1795323 | 414 | Distribution Circuit | Animal | Bird found | 183 | 69790 | 35.1945 | -120.7141 | MTR #5000018651 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0052217 | OH | Sus | 31329214 | No | 2017 | JUN | Yes | Line to Line | 1282686 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | MESA-1101 | 182821101 | JUMPER | WIRE DOWN/ OJ | 20170607 | 1942 | 1799077 | 303 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 303 | 35.0852 | -120.5077 | SPAN SOURCE SIDE OF CGC 512500158633 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0053483 | OH | Sus | 31330358 | No | 2017 | JUN | Yes | Line to Ground | 1283636 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN MIGUEL-1104 | 182661104 | FUSE | 5599 | 20170609 | 1915 | 1800783 | 503 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1006 | 35.818 | -120.5241 | WIRE DOWN SOURCE SIDE OF METER 1008492715 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0054121 | OH | Sus | 43031299 | No | 2017 | JUN | Yes | Line to Ground | 1284010 | CO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2113 | 183052113 | FUSE | 3945 | 20170609 | 1515 | 1800647 | 656 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 38704 | 35.4397 | -120.4882 | at METER 1007997515 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0054100 | OH | Sus | 0 | No | 2017 | JUN | Yes | Three Phase Fault | 1283992 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2113 | 183052113 | FUSE | 3945 | 20170610 | 734 | 1801029 | 583 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 59 | 34397 | 35.4397 | -120.4882 | COX- BOB: 4 poles load side of fuses 3945 on Black Mountain Resort Rd- Creston | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0054182 | OH | Sus | 31331007 | No | 2017 | JUN | Yes | Line to Ground | 1284077 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2113 | 183052113 | FUSE | 5293 | 20170610 | 1651 | 1801282 | 444 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 11544 | 35.3817 | -120.449 | 10250 HUER HUERO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0054216 | OH | Sus | 43036001 | No | 2017 | JUN | Yes | Line to Line | 1284109 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 2015 | 20170614 | 1542 | 1804526 | 617 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 13335 | 35.149 | -120.5881 | 1 SPAN L/S OF 11005 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0055270 | OH | Sus | 43038422 | No | 2017 | JUN | Yes | Line to Ground | 1284882 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 9201 | 20170617 | 848 | 1806633 | 508 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 5588 | 35.2377 | -120.4734 | 3162 UPPER LOPEZ CANYON- at 9201 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0055924 | OH | Sus | 31332308 | yes | 2017 | JUN | Yes | Line to Ground | 1285405 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2111 | 183052111 | JUMPER | OJS NEAR MTR: 1008267267 | 20170624 | 2351 | 1817457 | 759 | Distribution Circuit | Vegetation | Tree - branch fell on line | 88 | 3467 | 35.5073 | -120.7122 | 1008267267 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0058403 | OH | Sus | 0 | No | 2017 | JUN | Yes | Line to Ground | 1287500 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2113 | 183052113 | RECLOSER | A10 | 20170626 | 1921 | 1818691 | 1402 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 401 | 72193 | 35.4107 | -120.5657 | 4750 PARK HILL RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0058751 | OH | Sus | 0 | No | 2017 | JUN | Yes | Line to Line | 1287786 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2110 | 183052110 | FUSE | 6491 | 20170716 | 1313 | 1832768 | 332 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1304 | 35.6613 | -120.9192 | 2 SP S/S OF 6491 | Clear-Above 90 | Connector or Splice (OH) | Broken, wire on ground | 17-0063242 | OH | Sus | 0 | No | 2017 | JUL | Yes | Line to Ground | 1291047 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1108 | 182601108 | JUMPER | WIRE DOWN END OF STANTON RD | 20170720 | 1344 | 1836440 | 1009 | Distribution Circuit | Equipment Failure/Involved | Overhead | 222 | 45999 | 35.0592 | -120.5605 | END OF STANTON & END OF ZENON | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0064321 | OH | Sus | 31338232 | No | 2017 | JUL | Yes | Multi-Fault | 1291813 | CAW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2111 | 183052111 | OTHER | WIRE DOWN @ MTR 1008267265 | 20170720 | 442 | 1836061 | 466 | Distribution Circuit | Vegetation | Tree - branch fell on line | 962 | 19556 | 35.509 | -120.706 | AT MTR1008267265 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0064080 | OH | Sus | 43063638 | No | 2017 | JUL | Yes | Open Circuit | 1291701 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1104 | 183101104 | FUSE | 7761 | 20170722 | 306 | 1837439 | 209 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 209 | 34.5668 | -120.4989 | BEYOND PRIMARY METERING ON CUST PRIVATE LINE | Overcast-Fog-32-90 F | Conductor, Overhead | On Ground | 17-0064684 | OH | Sus | 0 | No | 2017 | JUL | Yes | Line to Ground | 1292063 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2110 | 183052110 | OTHER | WIRE DOWN 2/S 6371 | 20170728 | 1820 | 1841953 | 830 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 8300 | 35.7287 | -120.9899 | WIRE DOWN 2/S 6371 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0066392 | OH | Sus | 43070109 | No | 2017 | JUL | Yes | Open Circuit | 1293167 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN MIGUEL-1106 | 182661106 | FUSE | 5577 | 20170807 | 2033 | 1848180 | 427 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 15372 | 35.809 | -120.6698 | at METER # 1008186639 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0068605 | OH | Sus | 31341352 | No | 2017 | AUG | Yes | Line to Ground | 1294790 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | ZACA-1102 | 182681102 | FUSE | 6871 | 20170812 | 907 | 1851049 | 476 | Distribution Circuit | Equipment Failure/Involved | Overhead | 305 | 26070 | 34.6781 | -120.0398 | 3462 BRINKERHOFF | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0069829 | OH | Sus | 43083241 | No | 2017 | AUG | Yes | Line to Ground | 1295658 | CO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ZACA-1102 | 182681102 | FUSE | 20523 | 20170812 | 2057 | 1851345 | 873 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 4640 | 34.6581 | -120.0594 | 1 POLE SOUTH | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0069897 | OH | Sus | 0 | No | 2017 | AUG | Yes | Multi-Fault | 1295719 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V60 | 20170816 | 1047 | 1853645 | 293 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1197 | 76515 | 35.1846 | -120.7043 | 3350 MEADOW BROOK LN | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 17-0070750 | OH | Sus | 43086516 | No | 2017 | AUG | Yes | Line to Ground | 1296321 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | ATASCADERO-1101 | 182541101 | FUSE | 2795 | 20170823 | 506 | 1857412 | 355 | Distribution Circuit | Vegetation | Tree - branch fell on line | 48 | 9456 | 35.4835 | -120.7237 | 12100 CENEGAL RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0072201 | OH | Sus | 43092557 | No | 2017 | AUG | Yes | Line to Ground | 1297337 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE | 3551 | 20170828 | 2056 | 1862054 | 607 | Distribution Circuit | Vegetation | Tree - bark fell into line | 9 | 5463 | 35.4906 | -120.688 | 3679 ARDILLA RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0073640 | OH | Sus | 0 | yes | 2017 | AUG | Yes | Line to Ground | 1298371 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ZACA-1101 | 182681101 | RECLOSER | Y72 | 20170910 | 2200 | 1874546 | 954 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 56286 | 34.7208 | -120.1303 | 2 SPAN LOAD SIDE Y72 | Heavy Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0077366 | OH | Sus | 0 | No | 2017 | SEP | Yes | Line to Ground | 1301258 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1108 | 182601108 | RECLOSER | V50 | 20170920 | 456 | 1882180 | 600 | Distribution Circuit | 3rd Party | Vehicle | 488 | 49815 | 35.0771 | -120.5828 | HALCYON RD S/O PRODUCE LN at C/O 15057 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0080181 | OH | Sus | 0 | No | 2017 | SEP | Yes | Line to Ground | 1303300 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PURISIMA-1101 | 182971101 | OCB | 1101/2 | 20170929 | 1448 | 1888280 | 2980 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3212 | 511659 | 34.7008 | -120.4357 | MITCHELL- DAN: CREW TO REPLACE BURNT POLES MULTIPLE LOCATIONS BETWEEN CB & Y44 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0082949 | OH | Sus | 31353676 | No | 2017 | SEP | Yes | Line to Line | 1305044 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CAMBRIA-1101 | 182771101 | FUSE | 5319 | 20171010 | 844 | 1897204 | 400 | Distribution Circuit | 3rd Party | Vehicle | 13 | 5200 | 35.6951 | -121.2913 | AT C/OUTS LOAD SIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085953 | OH | Sus | 43174626 | No | 2017 | OCT | Yes | Multi-Fault | 1307218 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V60 | 20171021 | 2250 | 1907082 | 780 | Distribution Circuit | 3rd Party | Vehicle | 1198 | 151607 | 35.1846 | -120.7043 | 3 POLES S/W OF 10895 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0089439 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1309911 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OILFIELDS-1103 | 182391103 | RECLOSER | N48 | 20171030 | 716 | 1911936 | 378 | Distribution Circuit | Equipment Failure/Involved | Overhead | 275 | 88740 | 35.7984 | -120.9743 | Spinola- Richard: 75245 INTERLAKE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0091174 | OH | Sus | 43203100 | No | 2017 | OCT | Yes | Line to Ground | 1311155 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | SANTA MARIA-1108 | 182671108 | RECLOSER | M80 | 20171111 | 1157 | 1920559 | 873 | Distribution Circuit | Vegetation | Tree - fell into line | 383 | 29093 | 35.0164 | -120.3591 | 2/N OF MTR 1006592380 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0094408 | OH | Sus | 0 | No | 2017 | NOV | Yes | Line to Line | 1313437 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1102 | 182601102 | OTHER | WIRE DOWN 4/E/O 14029 | 20171127 | 414 | 1929900 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 8011 | 35.0851 | -120.5798 | 4/E/O 14029 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0097715 | OH | Sus | 0 | yes | 2017 | NOV | Yes | Open Circuit | 1315934 | CO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1103 | 183101103 | FUSE | 7195 | 20171214 | 1438 | 1943142 | 724 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2896 | 34.6084 | -120.3651 | 3800 SAN JULIAN RD | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0101672 | OH | Sus | 0 | No | 2017 | DEC | Yes | Line to Ground | 1319566 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | MORRO BAY-1102 | 183011102 | FUSE | 3449 | 20171220 | 1200 | 1948637 | 430 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 38 | 16340 | 35.3064 | -120.8581 | 4 SPANS S/S OF 5393 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0102785 | OH | Sus | 31370719 | yes | 2017 | DEC | Yes | Line to Ground | 1321150 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OILFIELDS-1103 | 182391103 | FUSE | 32835 | 20180104 | 1637 | 2166 | 554 | Distribution Circuit | Vegetation | Tree - fell into line | 275 | 22102 | 35.8363 | -121.04 | at 32835- 1 POLE S/OF 32835 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0003702 | OH | Sus | 0 | yes | 2018 | JAN | Yes | Line to Ground | 1323211 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | MORRO BAY-1101 | 183011101 | FUSE | 14949 | 20180108 | 1104 | 3858 | 1099 | Distribution Circuit | 3rd Party | Vehicle | 8 | 8792 | 35.4242 | -120.7843 | STOWELL- DOUG: HWY 41 AT C/O 15141 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 18-0004312 | OH | Sus | 43246284 | yes | 2018 | JAN | Yes | Three Phase Fault | 1323631 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SANTA YNEZ-1101 | 182721101 | RECLOSER | Y52 | 20180110 | 106 | 5569 | 1064 | Distribution Circuit | Equipment Failure/Involved | Overhead | 193 | 66070 | 34.5981 | -120.0296 | 2 SP S/OF 1645 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0004904 | OH | Sus | 0 | No | 2018 | JAN | Yes | Line to Ground | 1323990 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SANTA YNEZ-1101 | 182721101 | RECLOSER | Y52 | 20180116 | 1428 | 9068 | 233 | Distribution Circuit | Equipment Failure/Involved | Overhead | 193 | 23519 | 34.5981 | -120.0296 | 1 SPAN LS 1645 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0006506 | OH | Sus | 43254866 | No | 2018 | JAN | Yes | Line to Ground | 1325072 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | GOLDTREE-1105 | 182581105 | FUSE | 11067 | 20180119 | 13 | 10585 | 861 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 12915 | 35.3178 | -120.6796 | ENGLE- TODD: 4 pls S/W of 9389 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0007224 | OH | Sus | 0 | No | 2018 | JAN | Yes | Line to Line | 1325471 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2113 | 183052113 | RECLOSER | A70 | 20180209 | 255 | 21738 | 425 | Distribution Circuit | Animal | Bird found | 1679 | 117217 | 35.5024 | -120.649 | 2 SP LS 2941 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0012691 | OH | Sus | 43271923 | No | 2018 | FEB | Yes | Line to Line | 1329055 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | TRANSFORMER | 510815175987 | 20180313 | 1314 | 43339 | 231 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1386 | 35.5492 | -121.0892 | CGC 510815175987 | Overcast-Drizzle-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0022296 | OH | Sus | 43300008 | yes | 2018 | MAR | Yes | Line to Ground | 1335626 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V60 | 20180322 | 1856 | 51239 | 571 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1206 | 686604 | 35.1846 | -120.7043 | 13 LD SIDE OF V60 | Overcast-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0025784 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Three Phase Fault | 1337720 | CAW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2113 | 183052113 | TRIP-SAVER | 6055 | 20180327 | 1734 | 54653 | 686 | Distribution Circuit | Equipment Failure/Involved | Overhead | 299 | 19854 | 35.4549 | -120.4869 | MTR#1007831190 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0027182 | OH | Sus | 0 | No | 2018 | MAR | Yes | Line to Line | 1338907 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1103 | 182541103 | OTHER | WIRE DOWN @ MTR 1007829444 | 20180425 | 2032 | 74053 | 348 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 543 | 35.3419 | -120.4007 | LAYUGAN- JIM: 12250 RIVER RD | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0035675 | OH | Sus | 43331263 | No | 2018 | APR | Yes | Line to Ground | 1345044 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE | 6089 | 20180428 | 1 | 75718 | 713 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 14942 | 35.5351 | -120.807 | LAYUGAN- JIM: 2525 WINERY CANYON RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0036424 | OH | Sus | 43333168 | No | 2018 | APR | Yes | Line to Line | 1345497 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | JUMPER | WIRE DOWN 1 SS 14829 | 20180503 | 2340 | 79224 | 570 | Distribution Circuit | Equipment Failure/Involved | Overhead | 382 | 59638 | 35.5463 | -121.0711 | ARLISS & PICKWICK at 14829 FUSES & PICKWICK AND HUDSON at 14831 FUSES | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0038160 | OH | Sus | 43335957 | No | 2018 | MAY | Yes | Open Circuit | 1346704 | CSO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1101 | 182541101 | FUSE | 2609 | 20180505 | 1715 | 80028 | 1072 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 12120 | 35.4755 | -120.6808 | MTR#1008220637 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0038559 | OH | Sus | 0 | No | 2018 | MAY | Yes | Line to Line | 1347006 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1104 | 183101104 | FUSE | 6085 | 20180509 | 1331 | 82477 | 1514 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1514 | 34.574 | -120.5173 | JUDD- JEFF: Wire down 8-12 spans load side of fuses 6085 | Clear-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0039697 | OH | Sus | 43339949 | No | 2018 | MAY | Yes | Line to Ground | 1347861 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 4923 | 20180521 | 1913 | 91264 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7371 | 35.2129 | -120.7264 | SECOND POLE FROM THE EOL AT S0310 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0043019 | OH | Sus | 31393075 | No | 2018 | MAY | Yes | Multi-Fault | 1350617 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V60 | 20180525 | 1828 | 94257 | 438 | Distribution Circuit | Animal | Bird found | 1212 | 204558 | 35.1846 | -120.7043 | SOUTH OF MTR 1009622272 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0044577 | OH | Sus | 0 | yes | 2018 | MAY | Yes | Line to Line | 1351653 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE | 30273 | 20180528 | 2047 | 95396 | 502 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 7028 | 35.5217 | -120.7127 | 3 SPANS L/S OF 30273 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0044921 | OH | Sus | 43356664 | yes | 2018 | MAY | Yes | Line to Ground | 1351948 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | OTHER | WIRE DOWN @ MTR 1010373253 | 20180608 | 1903 | 104714 | 295 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 2473 | 35.1531 | -120.5941 | MTR 1010373253 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0049130 | OH | Sus | 31395199 | No | 2018 | JUN | Yes | Open Circuit | 1355114 | CO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | MESA-1101 | 182821101 | SWITCH | 8061 | 20180609 | 46 | 104872 | 373 | Distribution Circuit | Animal | Bird found | 163 | 16825 | 35.0732 | -120.5161 | 1 SPAN S/OF 7017 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0049171 | OH | Sus | 43366428 | yes | 2018 | JUN | Yes | None | 1355163 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2110 | 183052110 | FUSE | 7387 | 20180616 | 1415 | 110811 | 639 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 17811 | 35.7088 | -120.9689 | MTR 1007833689 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0051645 | OH | Sus | 0 | yes | 2018 | JUN | Yes | Line to Ground | 1357087 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2113 | 183052113 | FUSE | 30887 | 20180713 | 1622 | 131017 | 774 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2322 | 35.508 | -120.6422 | 3375 WHY 41 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0059657 | OH | Sus | 31399709 | No | 2018 | JUL | Yes | Multi-Fault | 1363555 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2110 | 183052110 | FUSE | 7387 | 20180717 | 1111 | 133764 | 446 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 9121 | 35.7088 | -120.9689 | 6550 COW CAMP LOOP | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0060637 | OH | Sus | 31400283 | yes | 2018 | JUL | Yes | Line to Line | 1364473 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2110 | 183052110 | FUSE | 5585 | 20180721 | 1451 | 137215 | 1679 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 110814 | 35.683 | -120.9386 | 2 LD SIDE OF 5585 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 18-0062364 | OH | Sus | 31400770 | No | 2018 | JUL | Yes | Line to Ground | 1365628 | CAW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | RECLOSER | V36 | 20180805 | 1016 | 149280 | 345 | Distribution Circuit | Equipment Failure/Involved | Overhead | 328 | 113160 | 35.145 | -120.5299 | 1/E/O MTR 1008752578 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 18-0066883 | OH | Sus | 31402058 | No | 2018 | AUG | Yes | Line to Ground | 1369181 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1103 | 182541103 | RECLOSER | A14 | 20180822 | 2152 | 160579 | 557 | Distribution Circuit | 3rd Party | Vehicle | 130 | 19231 | 35.3237 | -120.5163 | 5 SPANS SS SBCO 30327 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0072641 | OH | Sus | 31403950 | No | 2018 | AUG | Yes | Line to Line | 1372784 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1102 | 182601102 | FUSE | 15239 | 20181015 | 2231 | 196002 | 464 | Distribution Circuit | Animal | Bird found | 50 | 23200 | 35.0973 | -120.5676 | 1/2 SPAN SOURCE SIDE OF 10205 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0090717 | OH | Sus | 43507433 | No | 2018 | OCT | Yes | Line to Ground | 1385899 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE | 5581 | 20181017 | 1902 | 197672 | 822 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 13690 | 35.5552 | -120.8377 | 1 ld sie of mtr 1010237920 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0091524 | OH | Sus | 0 | No | 2018 | OCT | Yes | Line to Line | 1386482 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2113 | 183052113 | RECLOSER | A70 | 20181021 | 32 | 199495 | 712 | Distribution Circuit | 3rd Party | Vehicle | 1680 | 302559 | 35.5024 | -120.649 | 1 SPAN LD SIDE 30911 & SS OF 3307 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0092526 | OH | Sus | 43513041 | No | 2018 | OCT | Yes | Line to Line | 1387142 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE | 30273 | 20181104 | 1925 | 208680 | 427 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5978 | 35.5217 | -120.7127 | 3 SPANS L/S OF 30273 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0096974 | OH | Sus | 43526802 | No | 2018 | NOV | Yes | Line to Ground | 1390457 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | FOOTHILL-1101 | 182951101 | OCB | 1101/2 | 20181120 | 1307 | 219184 | 305 | Distribution Circuit | Equipment Failure/Involved | Overhead | 217 | 21149 | 35.2865 | -120.7064 | 2260 LOS OSOS VALLEY RD | Clear-32-90 F | Transformer (OH) | Broken, wire on ground | 18-0101510 | OH | Sus | 0 | No | 2018 | NOV | Yes | Line to Ground | 1393856 | TXO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | FUSE | 15567 | 20181130 | 1553 | 230369 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 6910 | 35.5574 | -121.0828 | MTR# 1009704187 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105672 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1396627 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1101 | 182631101 | RECLOSER | V12 | 20181211 | 800 | 237643 | 734 | Distribution Circuit | Vegetation | Tree - fell into line | 212 | 83345 | 35.2948 | -120.637 | 2 SPANS LD OF MEER 1008720363 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0108428 | OH | Sus | 0 | No | 2018 | DEC | Yes | Multi-Fault | 1398841 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | BUELLTON-1101 | 183041101 | FUSE | 1715 | 20181212 | 1553 | 238893 | 822 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 3732 | 34.6594 | -120.1808 | MTR#1006881501 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0108871 | OH | Sus | 31418098 | No | 2018 | DEC | Yes | Three Phase Fault | 1399259 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | BUELLTON-1101 | 183041101 | FUSE | 20639 | 20181219 | 1028 | 243803 | 244 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1362 | 34.6279 | -120.2873 | 2 SPAN LD SIDE OF 20639 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0109988 | OH | Sus | 43618695 | No | 2018 | DEC | Yes | Line to Ground | 1400830 | CSO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 10895 | 20181229 | 652 | 249154 | 400 | Distribution Circuit | Equipment Failure/Involved | Overhead | 189 | 71887 | 35.1945 | -120.7141 | 4 POLES L/S OF MTR# 5000018651 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on object | 18-0111031 | OH | Sus | 43623280 | No | 2018 | DEC | Yes | Line to Ground | 1402240 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1102 | 182601102 | FUSE | 14259 | 20190201 | 2334 | 285849 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 20328 | 35.078 | -120.5493 | CONGRESS AND STATON///1 SPAN LD OF FUSES 14259 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016827 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1411286 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CAMBRIA-1101 | 182771101 | RECLOSER | V76 | 20190203 | 738 | 288545 | 644 | Distribution Circuit | Animal | Bird found | 67 | 37538 | 35.647 | -121.1906 | 10759 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017458 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1411874 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2113 | 183052113 | FUSE | 7099 | 20190203 | 1815 | 289204 | 216 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 972 | 35.495 | -120.6441 | at CGC512136273628 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017626 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412038 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 4923 | 20190302 | 356 | 329375 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 6682 | 35.2129 | -120.7264 | 3150 DAVIS CANYON RD. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0030012 | OH | Sus | 43688516 | yes | 2019 | MAR | Yes | Line to Line | 1421502 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ZACA-1102 | 182681102 | FUSE | 7973 | 20190302 | 728 | 329432 | 110 | Distribution Circuit | Vegetation | Tree - branch fell on line | 43 | 4730 | 34.6579 | -120.0911 | MTR 1006881829 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0030013 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Line | 1421505 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE | 5581 | 20190303 | 1132 | 330138 | 701 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 15310 | 35.5552 | -120.8377 | 1 SPANS SOURCE SIDE OF CGC#511590076135 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0030271 | OH | Sus | 43689166 | No | 2019 | MAR | Yes | Line to Line | 1421723 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2111 | 183052111 | OTHER | 1 SPANS SOURCE SIDE 2527 WIRE DOWN | 20190304 | 1331 | 330891 | 341 | Distribution Circuit | Vegetation | Tree - fell into line | 216 | 21744 | 35.5059 | -120.7009 | 1 SPANS SOURCE SIDE 2527 WIRE DOWN | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0030530 | OH | Sus | 43689929 | No | 2019 | MAR | Yes | Line to Ground | 1421897 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | MORRO BAY-1102 | 183011102 | FUSE | 5393 | 20190306 | 720 | 332373 | 667 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3335 | 35.2837 | -120.8818 | RANGERS RESIDENCE JUST AFTER HAZARD CYN- MONTANA DE ORO STAT | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031349 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1422335 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1103 | 182541103 | FUSE | 170543 | 20190307 | 714 | 333676 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1064 | 35.3702 | -120.5621 | 4 SP SS MTR#1010394157 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0031684 | OH | Sus | 31427825 | No | 2019 | MAR | Yes | Line to Line | 1422590 | CAW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | V74 | 20190312 | 1605 | 337550 | 711 | Distribution Circuit | Vegetation | Tree - fell into line | 382 | 167019 | 35.5457 | -121.0679 | ENGLE- TODD/661-342-0850: 2356 Kay | Clear-32-90 F | Conductor, Overhead | On Ground | 19-0033138 | OH | Sus | 31428788 | yes | 2019 | MAR | Yes | Line to Line | 1423613 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | FUSE | 10045 | 20190312 | 1816 | 337870 | 839 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3356 | 35.5506 | -121.0822 | BRIGGS- John/805-305-9173: 3 locations | Partly Cloudy-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0033229 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1423690 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 4563 | 20190320 | 757 | 343630 | 410 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1230 | 35.18 | -120.6976 | 9 SP LS 4563 TREE DOWN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0035315 | OH | Sus | 31429944 | yes | 2019 | MAR | Yes | Line to Line | 1425278 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2113 | 183052113 | TRIP-SAVER | 6055 | 20190402 | 1101 | 352421 | 791 | Distribution Circuit | 3rd Party | Vehicle | 298 | 27362 | 35.4549 | -120.4869 | 4 SPANS L/S OF 6055 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0039124 | OH | Sus | 0 | yes | 2019 | APR | Yes | Multi-Fault | 1427845 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | JUMPER | OJ | 20190419 | 830 | 363561 | 250 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 749 | 35.148 | -120.5895 | 1 SPAN LD SIDE OF Q08/ ON TAP LINE | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0044238 | OH | Sus | 0 | No | 2019 | APR | Yes | Force Out | 1431488 | CO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | MORRO BAY-1102 | 183011102 | FUSE | 10573 | 20190421 | 714 | 364820 | 512 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 3584 | 35.306 | -120.8122 | AT MTR 1008474135 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0044668 | OH | Sus | 43746541 | No | 2019 | APR | Yes | Line to Line | 1431833 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | FOOTHILL-1101 | 182951101 | FUSE | 13049 | 20190510 | 2223 | 378262 | 991 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 8919 | 35.2902 | -120.8047 | AT MTR 000007447 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0050956 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Line | 1435986 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1101 | 182631101 | FUSE | 217493 | 20190518 | 747 | 384018 | 326 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 16300 | 35.2872 | -120.6494 | 1355 OLD STAGE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053613 | OH | Sus | 43787132 | yes | 2019 | MAY | Yes | Line to Ground | 1437844 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PASO ROBLES-1103 | 182611103 | RECLOSER | N52 | 20190530 | 810 | 393256 | 499 | Distribution Circuit | 3rd Party | Vehicle | 1753 | 171603 | 35.6885 | -120.7653 | FUCO 92206 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0059906 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Line | 1443145 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE | 6907 | 20190604 | 2319 | 398084 | 714 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4998 | 35.5326 | -120.7399 | MTR 1001027945 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0062991 | OH | Sus | 0 | yes | 2019 | JUN | Yes | Line to Ground | 1445536 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE | 6023 | 20190611 | 2155 | 407031 | 755 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 4060 | 35.5205 | -120.7116 | 6650 SANTA CRUZ RD 1ST POLE PAST CGC 511945974659- 6505 SANTA CRUZ RD | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0066401 | OH | Sus | 31453376 | yes | 2019 | JUN | Yes | Line to Ground | 1448331 | CAW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ZACA-1102 | 182681102 | RECLOSER | Y54 | 20190628 | 1500 | 434334 | 180 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 312 | 56160 | 34.6533 | -120.0714 | BETWEEN 20523 FUCO AND 95929 FUCO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0073204 | OH | Sus | 0 | No | 2019 | JUN | Yes | Line to Ground | 1453467 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | MORRO BAY-1102 | 183011102 | FUSE | 3449 | 20190702 | 1902 | 440133 | 568 | Distribution Circuit | 3rd Party | Vehicle | 38 | 14834 | 35.3064 | -120.8581 | PECHO VALLEY RD MONTANA DE ORO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0074146 | OH | Sus | 43866947 | No | 2019 | JUL | Yes | Multi-Fault | 1454118 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SANTA YNEZ-1104 | 182721104 | FUSE | 11361 | 20190706 | 1358 | 441914 | 402 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 14213 | 34.6357 | -119.9762 | at MTR # 1006881505 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0074960 | OH | Sus | 31456430 | No | 2019 | JUL | Yes | Open Circuit | 1454534 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PURISIMA-1101 | 182971101 | RECLOSER | Y44 | 20190713 | 1246 | 449040 | 459 | Distribution Circuit | Equipment Failure/Involved | Overhead | 183 | 18256 | 34.7193 | -120.4307 | ELDER- John/5512/805-680-8334: 4 SPANS N/11257 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0077070 | OH | Sus | 43878845 | No | 2019 | JUL | Yes | Line to Line | 1456012 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SANTA YNEZ-1101 | 182721101 | RECLOSER | Y52 | 20190827 | 2119 | 543111 | 854 | Distribution Circuit | Equipment Failure/Involved | Overhead | 189 | 128382 | 34.5981 | -120.0296 | 2 N/OF LR 980192 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0092793 | OH | Sus | 31469615 | No | 2019 | AUG | Yes | Line to Line | 1466198 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2111 | 183052111 | RECLOSER | A66 | 20190902 | 700 | 550674 | 1044 | Distribution Circuit | Vegetation | Tree - fell into line | 969 | 238446 | 35.5213 | -120.7126 | FUCO 5967 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0094505 | OH | Sus | 31470370 | No | 2019 | SEP | Yes | Line to Ground | 1467134 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1102 | 182601102 | FUSE | 9671 | 20190904 | 2054 | 553946 | 825 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4125 | 35.0823 | -120.5694 | SS OF MTR# 1009259146 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0095448 | OH | Sus | 31470618 | yes | 2019 | SEP | Yes | Line to Ground | 1467743 | CO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V60 | 20190908 | 1743 | 562595 | 490 | Distribution Circuit | Vegetation | Tree - fell into line | 1226 | 153188 | 35.1846 | -120.7043 | MTR# 101880729 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0096591 | OH | Sus | 43947780 | No | 2019 | SEP | Yes | Line to Ground | 1468509 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2108 | 183052108 | FUSE | 2547 | 20190915 | 1404 | 583331 | 868 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 34720 | 35.4804 | -120.6711 | 2 S/OF 2547 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0099266 | OH | Sus | 31471726 | No | 2019 | SEP | Yes | Line to Ground | 1470150 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE | 2675 | 20190916 | 1523 | 585380 | 367 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 13919 | 35.5438 | -120.8258 | MTR# 1009892852 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0099883 | OH | Sus | 31471961 | yes | 2019 | SEP | Yes | Line to Ground | 1470471 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | SANTA YNEZ-1101 | 182721101 | FUSE | 1621 | 20190921 | 57 | 599959 | 898 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 11102 | 34.5631 | -119.9348 | MTR 1010074081 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0102050 | OH | Sus | 0 | No | 2019 | SEP | Yes | Line to Line | 1471672 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | SAN LUIS OBISPO-1104 | 182631104 | TRIP-SAVER | 2293 | 20190922 | 238 | 603245 | 3332 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 47 | 128154 | 35.1919 | -120.4565 | 3 P/LD SIDE OF 9815 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0102206 | OH | Sus | 0 | No | 2019 | SEP | Yes | Line to Line | 1471874 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | BUELLTON-1102 | 183041102 | FUSE | 1031 | 20190930 | 1355 | 632533 | 240 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 17 | 4080 | 34.6126 | -120.1785 | Woodyard- Chase / 408-502-4061: 560 MCMURRAY RD | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0105582 | OH | Sus | 0 | No | 2019 | SEP | Yes | Multi-Fault | 1474228 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2111 | 183052111 | RECLOSER | A66 | 20191001 | 352 | 633516 | 673 | Distribution Circuit | Vegetation | Tree - branch fell on line | 969 | 134567 | 35.5213 | -120.7126 | at 4443 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0105739 | OH | Sus | 31473747 | No | 2019 | OCT | Yes | Three Phase Fault | 1474291 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1103 | 182541103 | FUSE | 30325 | 20191008 | 1758 | 647697 | 664 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 664 | 35.2993 | -120.4898 | 2P E/ OF 30325 at EOL | Clear-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0109036 | OH | Sus | 0 | No | 2019 | OCT | Yes | Line to Ground | 1476287 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PASO ROBLES-1103 | 182611103 | RECLOSER | N54 | 20191105 | 1350 | 700188 | 291 | Distribution Circuit | 3rd Party | Gun Shot | 1998 | 251130 | 35.6544 | -120.7258 | 1 SPAN S/OF 31887 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0121471 | OH | Sus | 44091088 | No | 2019 | NOV | Yes | Line to Ground | 1489394 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2113 | 183052113 | RECLOSER | A08 | 20191205 | 755 | 730265 | 428 | Distribution Circuit | Vegetation | Tree - fell into line | 925 | 31347 | 35.4621 | -120.6221 | TX 512204872002 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0133721 | OH | Sus | 0 | No | 2019 | DEC | Yes | Line to Line | 1497792 | CAW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | FUSE | 4747 | 20191215 | 1630 | 740363 | 354 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 17978 | 35.5503 | -121.0856 | CORNER OF AMHERST PI AND FERN DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0136664 | OH | Sus | 44122916 | No | 2019 | DEC | Yes | Line to Ground | 1500796 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1104 | 183101104 | FUSE | 6085 | 20200102 | 1150 | 753753 | 784 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 784 | 34.574 | -120.5173 | ELDER- John/5512/805-680-8334: 18 SPANS FROM END OF TAP | Clear-32-90 F | Insulator | Broken, wire on ground | 20-0004565 | OH | Sus | 44143176 | No | 2020 | JAN | Yes | Line to Line | 1503834 | INS | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ZACA-1102 | 182681102 | FUSE | 452469 | 20200109 | 544 | 757594 | 576 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 4539 | 34.666 | -120.0279 | AT MTR #1009904197 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0006648 | OH | Sus | 44146963 | No | 2020 | JAN | Yes | Line to Ground | 1505112 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CAMBRIA-1102 | 182771102 | OTHER | WIRE DOWN AT CGC # 510770576683 | 20200127 | 651 | 770541 | 372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 630 | 232961 | 35.568 | -121.1046 | AT CGC # 510770576683 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0013818 | OH | Sus | 31487762 | No | 2020 | JAN | Yes | Open Circuit | 1509353 | CO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1102 | 182601102 | FUSE | 14029 | 20200221 | 906 | 797759 | 423 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 2610 | 35.0851 | -120.5798 | 2P SOURCE SIDE OF MTR# 1006269038 | Overcast-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0024644 | OH | Sus | 44204928 | No | 2020 | FEB | Yes | Line to Ground | 1516893 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | BUELLTON-1101 | 183041101 | FUSE | 6997 | 20200229 | 142 | 819945 | 1094 | Distribution Circuit | Equipment Failure/Involved | Overhead | 177 | 193638 | 34.5983 | -120.1927 | MTR#1008675853 ON MAIN LINE | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 20-0027277 | OH | Sus | 0 | No | 2020 | FEB | Yes | Three Phase Fault | 1518557 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CAMBRIA-1102 | 182771102 | FUSE | 3865 | 20200229 | 2018 | 820396 | 792 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 65736 | 35.5742 | -121.1038 | 6460 Buckley | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0027460 | OH | Sus | 0 | No | 2020 | FEB | Yes | Three Phase Fault | 1518685 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SANTA YNEZ-1101 | 182721101 | RECLOSER | Y52 | 20200317 | 653 | 856249 | 345 | Distribution Circuit | Equipment Failure/Involved | Overhead | 190 | 53310 | 34.5981 | -120.0296 | SOURCE SIDE OF LR 980192 | Partly Cloudy-Fog-Drizzle-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0033135 | OH | Sus | 44263062 | yes | 2020 | MAR | Yes | Line to Line | 1522280 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1105 | 182601105 | OCB | 1105/2 | 20200320 | 1433 | 859844 | 307 | Distribution Circuit | 3rd Party | Metallic Balloon | 6514 | 258870 | 35.101 | -120.581 | AT CGC #512193560249 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0034744 | OH | Sus | 0 | No | 2020 | MAR | Yes | Line to Ground | 1523290 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 10895 | 20200327 | 825 | 868014 | 339 | Distribution Circuit | Animal | Bird found | 193 | 65427 | 35.1945 | -120.7141 | 1515 SEA CANYON RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0036590 | OH | Sus | 44275833 | No | 2020 | MAR | Yes | Line to Line | 1524200 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ZACA-1101 | 182681101 | OCB | 1101/2 | 20200420 | 1018 | 898093 | 340 | Distribution Circuit | 3rd Party | Vehicle | 163 | 10120 | 34.6968 | -120.1518 | 1 N/OF CGC# 513448644762 | Overcast-32-90 F | Anchor or Guy | Broken, wire on ground | 20-0042828 | OH | Sus | 44298880 | No | 2020 | APR | Yes | Line to Ground | 1528088 | ANC | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2108 | 183052108 | RECLOSER | A56 | 20200424 | 1530 | 900800 | 272 | Distribution Circuit | Vegetation | Tree - fell into line | 998 | 75682 | 35.5032 | -120.6933 | AT MTR #1007988812 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0044419 | OH | Sus | 44303661 | No | 2020 | APR | Yes | Line to Ground | 1528935 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V14 | 20200425 | 1050 | 901360 | 707 | Distribution Circuit | Vegetation | Tree - fell into line | 528 | 115066 | 35.1791 | -120.6181 | 2 SPANS SOUTH OF 15243 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0044535 | OH | Sus | 31501179 | No | 2020 | APR | Yes | Line to Line | 1529027 | CAW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PASO ROBLES-1103 | 182611103 | RECLOSER | N52 | 20200511 | 11 | 910845 | 764 | Distribution Circuit | 3rd Party | Vehicle | 1754 | 210170 | 35.6886 | -120.7649 | 92206 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 20-0048940 | OH | Sus | 0 | yes | 2020 | MAY | Yes | Line to Line | 1531835 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ZACA-1102 | 182681102 | JUMPER | WIRE DOWN JUST W/OF CGC# 513645942661 | 20200531 | 1936 | 926954 | 279 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1062 | 34.6538 | -120.1146 | JUST W/OF CGC# 513645942661 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0056086 | OH | Sus | 0 | No | 2020 | MAY | Yes | Line to Ground | 1535949 | CSO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | FUSE | 4563 | 20200615 | 1727 | 939837 | 1623 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 4869 | 35.18 | -120.6976 | ADORNI- JUSTIN: mattie rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0061593 | OH | Sus | 31506161 | No | 2020 | JUN | Yes | Three Phase Fault | 1539947 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1102 | 182601102 | FUSE | 14259 | 20200711 | 1252 | 962314 | 395 | Distribution Circuit | Vegetation | Tree - branch fell on line | 32 | 12640 | 35.078 | -120.5493 | 388 STANTON | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0070829 | OH | Sus | 44387985 | yes | 2020 | JUL | Yes | Line to Ground | 1545912 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE | 2797 | 20200827 | 439 | 1033495 | 462 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 29631 | 35.4782 | -120.709 | 11770 CENEGAL RD | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 20-0090541 | OH | Sus | 31512359 | No | 2020 | AUG | Yes | Line to Ground | 1559199 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | OTHER | 91825 | 20200930 | 1511 | 1102415 | 394 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 1855 | 35.2351 | -120.6757 | 1 POLE S/S OF MTR# 1008906960 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0103581 | OH | Sus | 44484339 | No | 2020 | SEP | Yes | Line to Ground | 1567484 | CO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2113 | 183052113 | RECLOSER | A70 | 20201001 | 801 | 1103153 | 432 | Distribution Circuit | 3rd Party | Vehicle | 1696 | 130331 | 35.5024 | -120.649 | SBCO 2941 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0103791 | OH | Sus | 0 | yes | 2020 | OCT | Yes | Multi-Fault | 1567568 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PURISIMA-1101 | 182971101 | RECLOSER | 49394 | 20201024 | 51 | 1124390 | 481 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2095 | 305349 | 34.7035 | -120.461 | SIRIUS & CONSTELLATION | Clear-32-90F | Insulator | Broken, wire on ground | 20-0112619 | OH | Sus | 44505225 | No | 2020 | OCT | Yes | Line to Ground | 1573043 | INS | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1101 | 182541101 | RECLOSER | A02 | 20201029 | 705 | 1131218 | 315 | Distribution Circuit | Vegetation | Tree - branch fell on line | 497 | 48315 | 35.4838 | -120.6842 | N/OF CGC# 511989973135 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0114616 | OH | Sus | 44509273 | No | 2020 | OCT | Yes | Line to Ground | 1575362 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | SANTA MARIA-1108 | 182671108 | RECLOSER | M80 | 20201122 | 619 | 1152635 | 435 | Distribution Circuit | Equipment Failure/Involved | Overhead | 385 | 167475 | 35.0164 | -120.3591 | 1P N/OF M80 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 20-0123906 | OH | Sus | 0 | No | 2020 | NOV | Yes | Line to Line | 1581923 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1103 | 182541103 | RECLOSER | A16 | 20201130 | 923 | 1156235 | 484 | Distribution Circuit | 3rd Party | Vehicle | 224 | 33232 | 35.392 | -120.5975 | 2/OFMTR# 1008836147 | Clear-32-90F | Anchor or Guy | Broken, wire on ground | 20-0125857 | OH | Sus | 31519529 | No | 2020 | NOV | Yes | Line to Line | 1583001 | ANC | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 4939 | 20201207 | 1450 | 1169527 | 426 | Distribution Circuit | Vegetation | Tree - branch fell on line | 63 | 8176 | 35.1547 | -120.528 | 3W OF 4939 ON SOUTH BUCK LINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0128663 | OH | Sus | 44579036 | No | 2020 | DEC | Yes | Three Phase Fault | 1585195 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2111 | 183052111 | FUSE | 7581 | 20210111 | 2359 | 1208635 | 721 | Distribution Circuit | 3rd Party | Vehicle | 170 | 121151 | 35.499 | -120.7022 | 3P N/OF 31015 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0007546 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1592405 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | PERRY-1101 | 183071101 | FUSE | 3057 | 20210114 | 548 | 1210162 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1728 | 35.5645 | -120.9071 | CGC 511353576274 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0008489 | OH | Sus | 31527247 | No | 2021 | JAN | Yes | Line to Ground | 1592956 | CO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | BUELLTON-1101 | 183041101 | FUSE | 20149 | 20210216 | 56 | 1255469 | 433 | Distribution Circuit | Equipment Failure/Involved | Overhead | 36 | 15580 | 34.5313 | -120.2913 | SPAN S/OF MTR # 1010195074 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 21-0025762 | OH | Sus | 44653168 | No | 2021 | FEB | Yes | Line to Ground | 1605326 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | GOLDTREE-1105 | 182581105 | OTHER | WIRE DOWN BET 4319 & 3087 | 20210404 | 11 | 1306573 | 347 | Distribution Circuit | Animal | Other | 2494 | 28688 | 35.2924 | -120.6653 | BET 4319 & 3087 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 21-0044508 | OH | Sus | 44720663 | No | 2021 | APR | Yes | Line to Ground | 1617436 | CO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1106 | 182601106 | OTHER | WIRE DOWN | 20210424 | 1241 | 1332516 | 351 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 351 | 35.0929 | -120.5804 | 1P W/OF CGC# 512287458920 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0052768 | OH | Sus | 31536922 | No | 2021 | APR | Yes | Line to Ground | 1622840 | CO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2110 | 183052110 | FUSE | 5581 | 20210503 | 114 | 1339410 | 510 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 52298 | 35.5552 | -120.8377 | 5581 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0055947 | OH | Sus | 0 | No | 2021 | MAY | Yes | Line to Ground | 1624966 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ZACA-1102 | 182681102 | RECLOSER | Y54 | 20210504 | 1026 | 1340622 | 305 | Distribution Circuit | Equipment Failure/Involved | Overhead | 543 | 74762 | 34.6532 | -120.0715 | SOURCE SIDE OF 7723 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0056596 | OH | Sus | 44772627 | No | 2021 | MAY | Yes | Line to Ground | 1625500 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1101 | 182631101 | RECLOSER | V12 | 20210516 | 558 | 1350729 | 562 | Distribution Circuit | 3rd Party | Vehicle | 202 | 63331 | 35.2947 | -120.636 | ADORNI- JUSTIN: highway 101 up grade nb lane sap 101845222 | Clear-32-90 F | Pole-Wood | Broken, wire on object | 21-0061968 | OH | Sus | 0 | No | 2021 | MAY | Yes | Multi-Fault | 1629154 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PALMER-1101 | 183031101 | RECLOSER | M82 | 20210715 | 450 | 1405060 | 174 | Distribution Circuit | Vegetation | Tree - fell into line | 745 | 92566 | 34.7368 | -120.2589 | 1 P LD SIDE OF 45193 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0089908 | OH | Sus | 31546370 | No | 2021 | JUL | Yes | Line to Ground | 1648456 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1101 | 182541101 | RECLOSER | A02 | 20210807 | 1455 | 1436592 | 440 | Distribution Circuit | Vegetation | Tree - branch fell on line | 498 | 134708 | 35.4838 | -120.6845 | MTR # 1007998681 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0101548 | OH | Sus | 31548897 | No | 2021 | AUG | Yes | Line to Ground | 1655482 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 14019 | 20210928 | 1303 | 1482720 | 422 | Distribution Circuit | 3rd Party | Vehicle | 18 | 2828 | 35.1593 | -120.5579 | 1 SPAN W/ OF FUCO 14019 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0123392 | OH | Sus | 0 | No | 2021 | SEP | Yes | Line to Ground | 1669426 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CAMBRIA-1102 | 182771102 | JUMPER | WIRE DOWN 1 SPAN W/OF CGC# 510920078634 | 20211022 | 44 | 1505399 | 849 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 849 | 35.6232 | -121.0574 | SAN SIMEON CRK RD | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0134991 | OH | Sus | 45019151 | No | 2021 | OCT | Yes | Line to Ground | 1676694 | CSO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2113 | 183052113 | RECLOSER | A12 | 20211026 | 112 | 1520665 | 936 | Distribution Circuit | Vegetation | Tree - branch fell on line | 132 | 84575 | 35.3806 | -120.4438 | 2 SS OF CGC 513032666955 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0137939 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1679183 | CAW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2113 | 183052113 | FUSE | 7099 | 20211107 | 754 | 1536706 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 7580 | 35.4951 | -120.6439 | 1 LD SIDE OF 7099 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0143118 | OH | Sus | 31577942 | No | 2021 | NOV | Yes | Three Phase Fault | 1682400 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ZACA-1101 | 182681101 | OTHER | 98478 | 20211114 | 1857 | 1544024 | 573 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 18197 | 34.7405 | -120.2261 | LANDEROS- MARIO / 805-680-5498: deadend pole 12 poles load side of recloser 98478 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0145466 | OH | Sus | 45066142 | No | 2021 | NOV | Yes | Line to Ground | 1684244 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SISQUOC-1103 | 182811103 | OTHER | WIRE DOWN ON GROUND 17 POLE LD SIDE OF 606751 | 20211124 | 246 | 1553986 | 583 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 12014 | 34.9185 | -120.2936 | 17 POLES LD SIDE OF 606751 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0150600 | OH | Sus | 45074910 | No | 2021 | NOV | Yes | Line to Ground | 1687758 | CO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1102 | 182601102 | OTHER | WIRE DOWN @ CGC 512263357529 | 20211216 | 1231 | 1574834 | 168 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2058 | 105273 | 35.0538 | -120.5851 | SIGHTS- JUSTIN / 805-550-0985: 511 Winterhaven | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158902 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1695937 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | V74 | 20211223 | 1110 | 1579860 | 316 | Distribution Circuit | Vegetation | Tree - fell into line | 382 | 31944 | 35.5459 | -121.0678 | 1 SS OF 9211- 1608 BRADFORD RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160273 | OH | Sus | 45100598 | No | 2021 | DEC | Yes | Line to Line | 1697713 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | MESA-1101 | 182821101 | JUMPER | WIRE DOWN 1P W/OF CGC #512420358365 | 20220108 | 219 | 1597936 | 654 | Distribution Circuit | 3rd Party | Vehicle | 10 | 6540 | 35.0779 | -120.5339 | 1P W/OF CGC #512420358365 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0007553 | OH | Sus | 31589815 | No | 2022 | JAN | Yes | Line to Ground | 1701558 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V18 | 20220217 | 701 | 1629610 | 906 | Distribution Circuit | 3rd Party | Vehicle | 2728 | 376646 | 35.1831 | -120.7038 | 1 SE/OF 4309 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0023320 | OH | Sus | 35328991 | No | 2022 | FEB | Yes | Three Phase Fault | 1710725 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1103 | 183101103 | FUSE | 1699 | 20220310 | 1556 | 1646395 | 589 | Distribution Circuit | Equipment Failure/Involved | Overhead | 61 | 35929 | 34.6195 | -120.4201 | ELDER- JOHN / 805-680-8334: 2240 SANTA ROSA RD | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 22-0032566 | OH | Sus | 45209120 | No | 2022 | MAR | Yes | Line to Ground | 1716287 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | TEMPLETON-2113 | 183052113 | RECLOSER | A12 | 20220411 | 1501 | 1669235 | 558 | Distribution Circuit | Equipment Failure/Involved | Overhead | 133 | 38306 | 35.3806 | -120.4438 | MTR# 1010609126 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0045755 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Line | 1724759 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2113 | 183052113 | OTHER | WIRE DOWN BET 32243 & 32241 | 20220420 | 1457 | -1677610 | 281 | Distribution Circuit | Animal | Bird found | 1706 | 109796 | 35.5112 | -120.6325 | BET 32243 & 32241- CLOSE TO FCO 32243 ON HWY 41 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0052123 | OH | Sus | 31601449 | No | 2022 | APR | Yes | Line to Ground | 1729712 | CO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | OTHER | WIRE DOWN 1 E/OF C603 | 20220430 | 1644 | 1685394 | 419 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1256 | 520126 | 35.1885 | -120.7176 | 1 POLES E/O C603 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0056477 | OH | Sus | 45273155 | No | 2022 | APR | Yes | Line to Ground | 1732522 | CO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1104 | 182631104 | OTHER | WIRE DOWN 5 W/OF 5185 | 20220602 | 1106 | 1716564 | 276 | Distribution Circuit | Equipment Failure/Involved | Overhead | 640 | 85902 | 35.1812 | -120.6166 | 5 W/OF 5185- ORMANDE OIL FIELDS GATE 8 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0069278 | OH | Sus | 45326462 | No | 2022 | JUN | Yes | Line to Ground | 1741205 | CO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ZACA-1101 | 182681101 | RECLOSER | M82 | 20220606 | 354 | 1719838 | 442 | Distribution Circuit | Equipment Failure/Involved | Overhead | 750 | 139703 | 34.7368 | -120.2589 | 8090 CAT CANYON RD | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 22-0070409 | OH | Sus | 0 | No | 2022 | JUN | Yes | Line to Ground | 1741953 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | SAN LUIS OBISPO-1104 | 182631104 | FUSE | 9201 | 20220614 | 1955 | 1731566 | 506 | Distribution Circuit | 3rd Party | Vehicle | 10 | 5060 | 35.2375 | -120.4731 | 13 SPANS FROM EOL | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0074382 | OH | Sus | 31606306 | No | 2022 | JUN | Yes | Line to Ground | 1744721 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1105 | 182631105 | FUSE | 3043 | 20220709 | 818 | 1752034 | 536 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 19911 | 35.2878 | -120.6501 | AT 10025 - 2046 SAN LUIS DR SAP101928659 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0083497 | OH | Sus | 0 | No | 2022 | JUL | Yes | Line to Ground | 1750837 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | RECLOSER | 891294 | 20220722 | 840 | 1763013 | 295 | Distribution Circuit | Vegetation | Tree - branch fell on line | 870 | 62863 | 35.1342 | -120.5702 | HARD TAP 1 POLE SOUTH OF 10795 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0088574 | OH | Sus | 31609586 | No | 2022 | JUL | Yes | Line to Ground | 1754256 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | BUELLTON-1101 | 183041101 | JUMPER | WIRE DOWN | 20220728 | 956 | 1767352 | 251 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 337 | 34.6351 | -120.1993 | 1 SPAN W/OF CGC#513391042031 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 22-0090823 | OH | Sus | 45393683 | No | 2022 | JUL | Yes | None | 1755793 | CSO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1103 | 183101103 | OTHER | HOT WIRE DOWN 1/S/LS OF 6741 | 20220730 | 2212 | 1769308 | 957 | Distribution Circuit | Equipment Failure/Involved | Overhead | 275 | 39534 | 34.6159 | -120.3732 | JUST LD SIDE OF 6741 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 22-0091754 | OH | Sus | 45399340 | No | 2022 | JUL | Yes | Line to Ground | 1756311 | CSO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | FOOTHILL SUB | 18295 | RECLOSER | TEMP LR 1101/2 | 20220803 | 1119 | 1772053 | 409 | Distribution Circuit | Equipment Failure/Involved | Overhead | 380 | 36233 | 35.2865 | -120.7064 | 12 SPANS LOADSIDE OF FUSES 3561 - 799 OCONNER RD | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 22-0093115 | OH | Sus | 45401637 | No | 2022 | AUG | Yes | Line to Ground | 1757265 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1102 | 182601102 | OTHER | HOT WIRE DOWN 1 S/LS OF 15327 | 20220920 | 801 | 1817189 | 374 | Distribution Circuit | Equipment Failure/Involved | Overhead | 437 | 2923 | 35.0758 | -120.5422 | 1 LD SIDE OF 15327 - 1688 QUIET OAKS | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 22-0112525 | OH | Sus | 45456282 | No | 2022 | SEP | Yes | Line to Ground | 1770355 | CSO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1107 | 182631107 | RECLOSER | V58 | 20221031 | 812 | 1848960 | 296 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2556 | 152851 | 35.247 | -120.6494 | CGC# 511984962711 | Clear-32-90 F | Insulator | Broken, wire on ground | 22-0126082 | OH | Sus | 31619742 | No | 2022 | OCT | Yes | Line to Ground | 1780171 | INS | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1102 | 182601102 | RECLOSER | 749231 | 20221128 | 2307 | 1870771 | 334 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2059 | 140818 | 35.0944 | -120.5735 | S/OF CGC 512241557590 - 2560 CALLENDER RD SAP 103345427 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 22-0134620 | OH | Sus | 45575975 | No | 2022 | NOV | Yes | Line to Ground | 1785940 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CAMBRIA-1101 | 182771101 | RECLOSER | 175422 | 20221130 | 101 | 1871680 | 386 | Distribution Circuit | Equipment Failure/Involved | Overhead | 62 | 22492 | 35.6473 | -121.191 | JUST S/OF C696 - PIEDRAS BLANCAS LIGHT HOUSE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0134995 | OH | Sus | 45576801 | No | 2022 | NOV | Yes | Line to Ground | 1786248 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | FOOTHILL SUB | 18295 | RECLOSER | TEMP LR 1101/2 | 20221204 | 1212 | 1875883 | 674 | Distribution Circuit | 3rd Party | Vehicle | 380 | 51320 | 35.2865 | -120.7064 | BET 9081 & C642 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0136453 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1787406 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OILFIELDS-1103 | 182391103 | RECLOSER | N48 | 20221212 | 306 | 1886639 | 662 | Distribution Circuit | Equipment Failure/Involved | Overhead | 279 | 160830 | 35.7984 | -120.9741 | INTERLAKE RD 2 SPANS E/O PLEYTO CEMETARY RD | Clear-32-90F | Insulator | Broken, wire on ground | 22-0139124 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1789939 | INS | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1104 | 183101104 | FUSE | 6345 | 20230101 | 0 | 1907547 | 1062 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 13022 | 34.6409 | -120.5021 | 3 LD SIDE OF 658059 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0004232 | OH | Sus | 0 | No | 2023 | JAN | Yes | Three Phase Fault | 1794824 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | OCEANO-1104 | 182601104 | FUSE | 9421 | 20230113 | 811 | 1951659 | 649 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1947 | 35.1295 | -120.5089 | 5 SPANS LD SIDE OF 9421 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015184 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1804217 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SISQUOC-1102 | 182811102 | FUSE | M54 | 20230113 | 518 | 1951306 | 316 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 21206 | 34.7773 | -120.1558 | 2 SPANS LOAD SIDE OF TAP FEEDING CGC 513561347551 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015058 | OH | Sus | 0 | No | 2023 | JAN | Yes | Three Phase Fault | 1804166 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1104 | 182601104 | FUSE | 3211 | 20230117 | 1954 | 1960319 | 351 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 28431 | 35.1497 | -120.6001 | BETWEEN 646469 & 1 POLE LD SIDE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0017904 | OH | Sus | 31634691 | No | 2023 | JAN | Yes | Line to Line | 1806316 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2113 | 183052113 | RECLOSER | A08 | 20230215 | 2352 | 1986537 | 381 | Distribution Circuit | 3rd Party | Vehicle | 930 | 293087 | 35.4622 | -120.6221 | 6 SPANS E OF 31261 | Clear-32-90 F | Anchor or Guy | Broken, wire on ground | 23-0029501 | OH | Sus | 31636889 | No | 2023 | FEB | Yes | Line to Line | 1813618 | ANC | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1104 | 183101104 | FUSE | 6091 | 20230301 | 1027 | 2018027 | 855 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3420 | 34.5858 | -120.5241 | 1 LD SIDE OF 6091 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0038160 | OH | Sus | 0 | No | 2023 | MAR | Yes | Three Phase Fault | 1820393 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | SANTA MARIA-1108 | 182671108 | FUSE | 45241 | 20230301 | 30 | 2017293 | 835 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 52605 | 35.0671 | -120.3919 | 1 LD SIDE OF CGC# 512831857966 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0037908 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1820243 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CAMBRIA-1102 | 182771102 | FUSE | 306275 | 20230310 | 1121 | 2030796 | 313 | Distribution Circuit | Vegetation | Tree - fell into line | 149 | 46637 | 35.5721 | -121.1068 | 1 SPAN SS OF 3865 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0043082 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1823726 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | SWITCH | 618168 | 20230310 | 39 | 2029805 | 791 | Distribution Circuit | Vegetation | Tree - fell into line | 151 | 45041 | 35.5454 | -121.076 | 2 SPANS LD SIDE OF 618 168 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 23-0042684 | OH | Sus | 31639699 | No | 2023 | MAR | Yes | Line to Line | 1823492 | PW | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | TEMPLETON-2110 | 183052110 | FUSE | 7513 | 20230313 | 900 | 2034286 | 243 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 243 | 35.5921 | -120.7957 | LD SIDE OF 7513 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0044055 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1824505 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1103 | 182541103 | FUSE | 30017 | 20230323 | 1119 | 2064546 | 243 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 243 | 35.2993 | -120.4896 | LD SIDE OF 30017 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0051328 | OH | Sus | 0 | No | 2023 | MAR | Yes | Three Phase Fault | 1829610 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 3 | ATASCADERO-1103 | 182541103 | FUSE | 5927 | 20230406 | 1133 | 2081749 | 412 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 9979 | 35.4604 | -120.7525 | MTR# 41614R | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0058080 | OH | Sus | 45717765 | No | 2023 | APR | Yes | Line to Ground | 1833837 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | PERRY-1101 | 183071101 | RECLOSER | V74 | 20230430 | 233 | 2100357 | 625 | Distribution Circuit | Equipment Failure/Involved | Overhead | 382 | 55000 | 35.5459 | -121.0678 | 1 P/W OF 14845 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0066370 | OH | Sus | 45745363 | No | 2023 | APR | Yes | Line to Ground | 1839589 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | BUELLTON-1101 | 183041101 | FUSE | 6997 | 20230511 | 1817 | 2110637 | 376 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 182 | 68416 | 34.5987 | -120.1926 | BEYOND 1413 | Clear-32-90 F | Conductor, Overhead | On Ground | 23-0071114 | OH | Sus | 45760075 | No | 2023 | MAY | Yes | Line to Ground | 1842648 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1103 | 183101103 | FUSE | 7195 | 20230524 | 1607 | 2120562 | 392 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1568 | 34.6084 | -120.3652 | 9 POLES LD SIDE OF 7195 | Overcast-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 23-0075257 | OH | Sus | 45773929 | No | 2023 | MAY | Yes | Force Out | 1845694 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | ATASCADERO-1103 | 182541103 | RECLOSER | A16 | 20230709 | 522 | 2157569 | 691 | Distribution Circuit | Vegetation | Tree - fell into line | 225 | 37805 | 35.392 | -120.5975 | 2 SPANS SOURCE SIDE OF 4063 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0090193 | OH | Sus | 31654902 | No | 2023 | JUL | Yes | Line to Line | 1855935 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SAN LUIS OBISPO-1104 | 182631104 | RECLOSER | V46 | 20230715 | 755 | 2163249 | 520 | Distribution Circuit | Vegetation | Tree - fell into line | 217 | 51470 | 35.1757 | -120.5255 | 1 SPAN SOURCE SIDE OF 14347 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0092542 | OH | Sus | 45887992 | No | 2023 | JUL | Yes | Line to Ground | 1857612 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1102 | 182601102 | OTHER | WIRE DWN BET 1477 & 14251 | 20230807 | 645 | 2184035 | 255 | Distribution Circuit | Equipment Failure/Involved | Overhead | 544 | 115822 | 35.0745 | -120.5774 | BET 1477 & 14251 | Overcast-Fog-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 23-0101119 | OH | Sus | 45915434 | No | 2023 | AUG | Yes | Line to Ground | 1863514 | CSO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | SANTA YNEZ-1101 | 182721101 | RECLOSER | Y52 | 20230815 | 1349 | 2191764 | 198 | Distribution Circuit | Vegetation | Tree - fell into line | 191 | 37818 | 34.5979 | -120.0297 | CGC 514194339317 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0104635 | OH | Sus | 0 | No | 2023 | AUG | Yes | Line to Line | 1865937 | CO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | CABRILLO-1103 | 183101103 | JUMPER | WIRE DOWN 3 S/S OF CGC#512851641940 | 20230918 | 840 | 2221413 | 266 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 266 | 34.6277 | -120.3784 | 3 S/S OF CGC#512851641940 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 23-0117685 | OH | Sus | 0 | No | 2023 | SEP | Yes | Line to Ground | 1874811 | CSO | OH | No | No
LOS PADRES | FIELD OPS SOUTH | Tier 2 | OCEANO-1102 | 182601102 | OTHER | 3815 | 20231115 | 1704 | 2270258 | 405 | Distribution Circuit | Vegetation | Tree - branch fell on line | 80 | 32400 | 35.088 | -120.5641 | 1 SPAN S/S OF 10081 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0139624 | OH | Sus | 31676533 | No | 2023 | NOV | Yes | Line to Ground | 1890903 | CO | OH | No | Yes
LOS PADRES | FIELD OPS SOUTH | Tier 2 | BUELLTON-1101 | 183041101 | FUSE | 20149 | 20231230 | 733 | 2302468 | 430 | Distribution Circuit | Equipment Failure/Involved | Overhead | 37 | 10198 | 34.5309 | -120.2908 | 7P W/OF 22063 | Overcast-Fog-Drizzle-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 23-0149343 | OH | Sus | 46118640 | No | 2023 | DEC | Yes | Line to Ground | 1900652 | CSO | OH | No | Yes
MISSION | FIELD OPS CENTRAL | Tier 3 | CASTRO VALLEY-1108 | 14091108 | SECTIONALIZER | 7672 | 20130622 | 833 | ODB-9927 | 679 | Distribution Circuit | 3rd Party | Vehicle | 0 | 98363 | 37.6953 | -122.024 | PALOMARES ROAD- CASTRO VALLEY | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0041705 | OH | Sus | 0 | No | 2013 | JUN | Yes |  | 99275051 | PW | OH | No
MISSION | FIELD OPS CENTRAL | Tier 2 | CAYETANO-2109 | 14422109 | SWITCH | 74154 | 20130628 | 1100 | 819313 | 25 | Distribution Circuit | 3rd Party | Vehicle | 3 | 75 | 37.7658 | -121.8109 | SAME | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0043387 | OH | Sus | 0 | yes | 2013 | JUN | Yes | None | 99277364 | CO | OH | No
MISSION | FIELD OPS CENTRAL | Tier 2 | CAYETANO-2109 | 14422109 | FUSE | 9273 | 20140312 | 221 | 982875 | 674 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 7030 | 37.7711 | -121.8105 | 7000 COLLIER CANYON | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0017414 | OH | Sus | 31062475 | yes | 2014 | MAR | Yes | Line to Ground | 99235354 | CO | OH | No
MISSION | FIELD OPS CENTRAL | Tier 2 | CASTRO VALLEY-1106 | 14091106 | FUSE | 8101 | 20140619 | 750 | 1036503 | 787 | Distribution Circuit | 3rd Party | Vehicle | 444 | 31654 | 37.717 | -122.0734 | GARBAGE TRUCK HIT POLE WITH CUTOUTS 12707 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0039247 | OH | Sus | 31083471 | No | 2014 | JUN | Yes | Line to Ground | 99220290 | PW | OH | No
MISSION | FIELD OPS CENTRAL | Tier 2 | NORTH DUBLIN-2101 | 14052101 | OCB | OCB | 20141024 | 1333 | 1101746 | 345 | Distribution Circuit | Equipment Failure/Involved | Other | 3435 | 224689 | 37.7448 | -121.8576 | AT POLE WITH MR167 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0065789 | OH | Sus | 42215742 | No | 2014 | OCT | Yes | Line to Ground | 99202266 | CO | OH | No
MISSION | FIELD OPS CENTRAL | Tier 2 | NORTH DUBLIN-2103 | 14052103 | FUSE | 74751 | 20141215 | 54 | 1140743 | 1691 | Distribution Circuit | 3rd Party | Vehicle | 174 | 27680 | 37.7521 | -121.8716 | TOBAR/3185: TASSAJARA RD | Rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0076928 | OH | Sus | 31121149 | yes | 2014 | DEC | Yes | Multi-Fault | 99193056 | PW | OH | No
MISSION | FIELD OPS CENTRAL | Tier 3 | RADUM-1105 | 13151105 | FUSE | 72826 | 20141215 | 1803 | 1141616 | 852 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 30171 | 37.6377 | -121.8967 | 38 GOLF RD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077106 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Multi-Fault | 99192856 | CO | OH | No
MISSION | FIELD OPS CENTRAL | Tier 2 | VINEYARD-2110 | 14502110 | FUSE | 9553 | 20150419 | 49 | 1221527 | 581 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 18011 | 37.7048 | -121.8233 | 9/N OF FUSE 9553 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0027634 | OH | Sus | 42371110 | No | 2015 | APR | Yes | Line to Ground | 99172956 | CO | OH | No
MISSION | FIELD OPS CENTRAL | Tier 3 | TASSAJARA-2113 | 14662113 | FUSE | 14246 | 20151120 | 753 | 1345725 | 350 | Distribution Circuit | 3rd Party | Vehicle | 8 | 2800 | 37.7535 | -122.0074 | NORRIS CANYON AND CROW CANYON | Clear-32-90 F | Pole-Wood | Broken, wire on object | 15-0079471 | OH | Sus | 31202243 | No | 2015 | NOV | Yes | Line to Ground | 1169633 | PW | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 3 | CASTRO VALLEY-1108 | 14091108 | FUSE | 12851 | 20160129 | 608 | 1393789 | 849 | Distribution Circuit | 3rd Party | Vehicle | 120 | 91968 | 37.6755 | -122.0126 | WASSON- PHILLIP: 31111 PALOMARES RD | Overcast-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 16-0009084 | OH | Sus | 0 | No | 2016 | JAN | Yes | Line to Ground | 1183234 | PW | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 3 | CASTRO VALLEY-1108 | 14091108 | FUSE | 10315 | 20160413 | 113 | 1449741 | 602 | Distribution Circuit | Equipment Failure/Involved | Overhead | 66 | 31802 | 37.6517 | -121.9818 | 7.8 MILE MARKER ON PALOMARES RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0028188 | OH | Sus | 0 | No | 2016 | APR | Yes | Line to Ground | 1197669 | CO | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 3 | SUNOL-1101 | 14241101 | OTHER | WIRE DOWN 10 POLES N/O 12787 | 20160515 | 1007 | 1469932 | 939 | Distribution Circuit | Vegetation | Tree - fell into line | 205 | 109398 | 37.6168 | -121.903 | 10 POLES N/O 12787 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0036103 | OH | Sus | 31238683 | No | 2016 | MAY | Yes | Line to Ground | 1203535 | CO | OH | No | Yes
MISSION | FIELD OPS CENTRAL | Tier 3 | CASTRO VALLEY-1108 | 14091108 | FUSE | 10315 | 20161005 | 930 | 1553351 | 707 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 67 | 34673 | 37.6517 | -121.9818 | FRANCO/5125: 34700 Palomares Rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0069831 | OH | Sus | 42805274 | No | 2016 | OCT | Yes | Line to Line | 1227558 | CO | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 2 | SAN LEANDRO-1114 | 13111114 | FUSE | 487577 | 20161013 | 1814 | 1557738 | 162 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 15066 | 37.7312 | -122.1356 | 1/P/S/O FUCO 6034 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0071763 | OH | Sus | 31277696 | yes | 2016 | OCT | Yes | Line to Line | 1228937 | CO | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 3 | CASTRO VALLEY-1108 | 14091108 | RECLOSER | MR243 | 20170125 | 1755 | 1667364 | 571 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 3932 | 37.7022 | -122.0452 | at 479403 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0014861 | OH | Sus | 42932760 | yes | 2017 | JAN | Yes | Line to Line | 1253434 | CO | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 2 | SAN LEANDRO-1114 | 13111114 | FUSE | 487577 | 20170206 | 1321 | 1676739 | 121 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 11253 | 37.7316 | -122.1347 | ON MAINLINE BETWEEN 8918 & 6034 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017851 | OH | Sus | 31304207 | yes | 2017 | FEB | Yes | Line to Ground | 1255734 | CO | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 3 | CASTRO VALLEY-1106 | 14091106 | FUSE | 12704 | 20170208 | 824 | 1681530 | 660 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1980 | 37.7269 | -122.0795 | 10 SPANS N/O 12704 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018890 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256620 | CO | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 2 | CASTRO VALLEY-1106 | 14091106 | FUSE | 51776 | 20170305 | 622 | 1719728 | 1303 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 56690 | 37.7176 | -122.0736 | 6/S/N/OF 51776 | Heavy Rain-Rain-32-90 F | Pole-Wood | Broken, wire on object | 17-0028424 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Three Phase Fault | 1264782 | PW | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 2 | NORTH DUBLIN-2103 | 14052103 | FUSE | 15953 | 20170322 | 958 | 1732736 | 148 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 1184 | 37.7625 | -121.8671 | DOUGLAS/129: SAME | Overcast-Drizzle-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0032709 | OH | Sus | 42974637 | yes | 2017 | MAR | Yes | Line to Line | 1268017 | CSO | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 2 | NORTH DUBLIN-2101 | 14052101 | OTHER | 37954 | 20170710 | 2136 | 1828676 | 656 | Distribution Circuit | 3rd Party | Vehicle | 63 | 41328 | 37.787 | -121.8591 | wire down 1 span e/o 37954 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0061912 | OH | Sus | 43057431 | No | 2017 | JUL | Yes | Line to Ground | 1290024 | PW | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 3 | VINEYARD-2108 | 14502108 | FUSE | 13159 | 20170902 | 1201 | 1866220 | 447 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 7152 | 37.6657 | -121.9176 | DOUGLAS/129: SAME | Clear-Heat Wave-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0075132 | OH | Sus | 0 | yes | 2017 | SEP | Yes | Line to Ground | 1299425 | CO | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 2 | NORTH DUBLIN-2103 | 14052103 | OTHER | WIRE DOWN NW/OF 21004 | 20171006 | 1514 | 1892122 | 1429 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 4225 | 37.7255 | -121.8736 | CAMPIOTTI/104: 5868 TASSAJARA RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0084814 | OH | Sus | 43160934 | No | 2017 | OCT | Yes | Line to Ground | 1306252 | CO | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 3 | CAYETANO-2109 | 14422109 | FUSE | 71424 | 20171116 | 1031 | 1923768 | 1019 | Distribution Circuit | Equipment Failure/Involved | Overhead | 64 | 29897 | 37.8183 | -121.7792 | 10695 MORGAN TERRITORY RD & 1 N/O 73217 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0095602 | OH | Sus | 0 | yes | 2017 | NOV | Yes | Line to Ground | 1314418 | CO | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 3 | CASTRO VALLEY-1108 | 14091108 | FUSE | 14394 | 20171209 | 122 | 1939361 | 729 | Distribution Circuit | 3rd Party | Vehicle | 57 | 41553 | 37.715 | -122.0397 | HA-CUONG `SONNY`: car hit | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0100905 | OH | Sus | 0 | No | 2017 | DEC | Yes | Line to Ground | 1318542 | PW | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 2 | SAN LEANDRO-1114 | 13111114 | JUMPER | WIRE DOWN | 20180609 | 713 | 104994 | 532 | Distribution Circuit | Equipment Failure/Involved | Overhead | 481 | 8372 | 37.7078 | -122.1093 | 15935 GRAMERCY DR | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0049192 | OH | Sus | 0 | yes | 2018 | JUN | Yes | Line to Ground | 1355194 | CO | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 3 | SAN RAMON-2107 | 14232107 | FUSE | 76044 | 20180609 | 541 | 104922 | 359 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 6462 | 37.7031 | -122.0019 | AT 29672 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 18-0049184 | OH | Sus | 31395159 | yes | 2018 | JUN | Yes | Line to Ground | 1355176 | CAW | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 2 | NORTH DUBLIN-2101 | 14052101 | OCB | 2101/2/NORM | 20180718 | 1236 | 134820 | 505 | Distribution Circuit | Animal | Bird found | 5789 | 335365 | 37.7448 | -121.8576 | SS 15801 7990 CAMINO TASSAJARA RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0061099 | OH | Sus | 43409364 | yes | 2018 | JUL | Yes | Line to Ground | 1364803 | CO | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 2 | CAYETANO-2109 | 14422109 | FUSE | 13345 | 20181222 | 458 | 245452 | 1016 | Distribution Circuit | 3rd Party | Vehicle | 179 | 69215 | 37.7523 | -121.7699 | 6 POLES W/O MORGAN TERRITORY RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0110315 | OH | Sus | 0 | No | 2018 | DEC | Yes | Line to Ground | 1401339 | PW | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 3 | SAN RAMON-2108 | 14232108 | FUSE | 13115 | 20190422 | 1911 | 365798 | 644 | Distribution Circuit | 3rd Party | Vehicle | 1852 | 107575 | 37.7705 | -122.0038 | 11567 CROW CANYON RD 1/P/W | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0045029 | OH | Sus | 0 | No | 2019 | APR | Yes | Line to Ground | 1432102 | CO | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 2 | CAYETANO-2109 | 14422109 | FUSE | 11775 | 20190515 | 1234 | 380943 | 305 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 6710 | 37.7685 | -121.7987 | 2000 VICTORINE | Overcast-Drizzle-32-90 F | PGs, Kearneys | Broken, wire on ground | 19-0052159 | OH | Sus | 43781828 | yes | 2019 | MAY | Yes | Line to Ground | 1436879 | PGK | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 2 | SUNOL-1101 | 14241101 | TRIP-SAVER | 8721 | 20200101 | 349 | 753228 | 499 | Distribution Circuit | 3rd Party | Vehicle | 24 | 11976 | 37.5663 | -121.8832 | 7500 SHERIDAN | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 20-0004212 | OH | Sus | 0 | No | 2020 | JAN | Yes | Line to Ground | 1503693 | PW | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 3 | SAN RAMON-2108 | 14232108 | FUSE | 13115 | 20200304 | 2218 | 831200 | 368 | Distribution Circuit | 3rd Party | Vehicle | 99 | 25430 | 37.7705 | -122.0038 | 2 N/OF 14221 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0028890 | OH | Sus | 0 | No | 2020 | MAR | Yes | Line to Line | 1519514 | PW | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 3 | CASTRO VALLEY-1110 | 14091110 | OTHER | WIRE DOWN ENERGIZED 6P E/O FUCO 11543 | 20211005 | 2105 | 1487973 | 486 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 486 | 37.7277 | -122.0329 | 6P E/O FUCO 11543 at EOL SPAN | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0126367 | OH | Sus | 45000286 | No | 2021 | OCT | Yes | Line to Ground | 1671205 | CSO | OH | No | Yes
MISSION | FIELD OPS CENTRAL | Tier 2 | CAYETANO-2109 | 14422109 | FUSE | 745511 | 20220121 | 2321 | 1607960 | 632 | Distribution Circuit | Vegetation | Tree - fell into line | 117 | 73944 | 37.7526 | -121.7791 | 1 POLE N/OF 73807 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0012847 | OH | Sus | 31590829 | No | 2022 | JAN | Yes | Line to Ground | 1704171 | CO | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 3 | CASTRO VALLEY-1110 | 14091110 | TRIP-SAVER | 10315 | 20220422 | 1244 | 1679378 | 235 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 17390 | 37.6519 | -121.9824 | 32684 PALOMARES RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0053418 | OH | Sus | 31601623 | No | 2022 | APR | Yes | Line to Ground | 1730352 | CO | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 2 | CASTRO VALLEY-1110 | 14091110 | RECLOSER | MR273 | 20220616 | 2233 | 1733509 | 761 | Distribution Circuit | Vegetation | Tree - branch fell on line | 208 | 158288 | 37.6978 | -122.0277 | 10440 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0075381 | OH | Sus | 0 | No | 2022 | JUN | Yes | Line to Line | 1745369 | CO | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 3 | SAN RAMON-2108 | 14232108 | RECLOSER | 53732 | 20230830 | 1009 | 2205841 | 658 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 50860 | 37.7758 | -121.9974 | 18219-18235 BOLLINGER CANYON RD. at CGC#315575347732 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0110669 | OH | Sus | 31666263 | No | 2023 | AUG | Yes | Line to Line | 1870190 | CO | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 2 | RADUM-1105 | 13151105 | FUSE | 8343 | 20231025 | 2001 | 2251947 | 510 | Distribution Circuit | 3rd Party | Vehicle | 8 | 4080 | 37.6383 | -121.8868 | HAPPY VALLEY RD & OSTRICH FEATHER | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0132621 | OH | Sus | 31674162 | No | 2023 | OCT | Yes | Line to Line | 1885047 | CO | OH | No | No
MISSION | FIELD OPS CENTRAL | Tier 2 | NORTH DUBLIN-2103 | 14052103 | OCB | 716168 | 20231106 | 12 | 2260877 | 780 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5000 | 395377 | 37.7448 | -121.8576 | 1 SPAN LOAD SIDE LR727584 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0136083 | OH | Sus | 31675429 | No | 2023 | NOV | Yes | Line to Ground | 1887964 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 311 | 20130108 | 1140 | 727093 | 160 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 1100 | 38.3493 | -122.379 | 1483 MT VEEDER RD. NAPA | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0002774 | OH | Sus | 0 | No | 2013 | JAN | Yes | Line to Line | 99305382 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | GREENBRAE-1103 | 43091103 | FUSE | 2371 | 20130114 | 1137 | 729789 | 948 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 54012 | 37.931 | -122.536 | 301 W. BALTIMORE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0004038 | OH | Sus | 30971117 | No | 2013 | JAN | Yes | Line to Line | 99304639 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE | 35665 | 20130126 | 1200 | 734836 | 416 | Distribution Circuit | Equipment Failure/Involved | Other | 7 | 2912 | 38.443 | -122.1995 | 5 SPANS LD SIDE OF FUCO 35665 ( NEAR 5633 MONTICELLO RD.) | Rain-32 - 90 F | Conductor, Overhead | On Ground | 13-0006341 | OH | Sus | 41845878 | No | 2013 | JAN | Yes | Line to Line | 99303229 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | STAFFORD-1102 | 43201102 | RECLOSER | 1202 | 20130227 | 707 | 748029 | 606 | Distribution Circuit | 3rd Party | Vehicle | 55 | 21280 | 38.122 | -122.6222 | 3835 NOVATO BLVD- NOVATO | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0012724 | OH | Sus | 30979866 | No | 2013 | FEB | Yes | Three Phase Fault | 99298980 | PW | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE | 1589 | 20130304 | 1324 | 751328 | 380 | Distribution Circuit | 3rd Party | Vehicle | 176 | 66880 | 38.4069 | -122.2056 | 17 SUNNYHILL RD | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 13-0013946 | OH | Sus | 41861476 | No | 2013 | MAR | Yes |  | 99298210 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | SWITCH | 523 | 20130305 | 2355 | 752323 | 815 | Distribution Circuit | Vegetation | Tree - fell into line | 167 | 136105 | 38.5664 | -122.6296 | 2 POLES LD SIDE OF SBCO 523 at 4940 MOUNTAIN HOME RANCH RD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0014455 | OH | Sus | 41862214 | yes | 2013 | MAR | Yes | Open Circuit | 99297867 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-2103 | 43292103 | RECLOSER | 678 | 20130322 | 737 | 760176 | 631 | Distribution Circuit | 3rd Party | Vehicle | 346 | 59194 | 38.3153 | -122.3426 | 3200 REDWOOD RD. | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0018356 | OH | Sus | 30984863 | No | 2013 | MAR | Yes | Multi-Fault | 99295249 | PW | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 6825 | 20130401 | 309 | 764714 | 501 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3507 | 38.5546 | -122.4888 | 3P LD SIDE OF 6825 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0020470 | OH | Sus | 30986612 | yes | 2013 | APR | Yes | Line to Ground | 99293602 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 5843 | 20130407 | 2308 | 767980 | 1944 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 15552 | 38.0149 | -122.6831 | 61 ROMONA AVE. FOREST KNOLLS | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0022103 | OH | Sus | 30987928 | yes | 2013 | APR | Yes |  | 99291798 | PW | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 1247 | 20130410 | 1542 | 772551 | 848 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 27136 | 37.9737 | -122.6127 | 46 BUENA VISTA AVE UPPER- FAIRFAX | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0023479 | OH | Sus | 41880968 | No | 2013 | APR | Yes | Line to Ground | 99291258 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 5559 | 20130414 | 2116 | 774716 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4896 | 38.3337 | -122.3719 | 3661 REDWOOD RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0024347 | OH | Sus | 41882498 | No | 2013 | APR | Yes | Line to Ground | 99290615 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 7467 | 20130415 | 1708 | 775601 | 476 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3332 | 38.0997 | -122.8766 | 8 SPANS LD SIDE OF 7467 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0024719 | OH | Sus | 0 | yes | 2013 | APR | Yes | Line to Line | 99290387 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER | 602 | 20130419 | 2346 | 778522 | 853 | Distribution Circuit | Equipment Failure/Involved | Other | 158 | 103337 | 38.1093 | -122.87 | Asay/411: 3 SPANS LOAD SIDE OF DISC. 1245 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0025946 | OH | Sus | 0 | No | 2013 | APR | Yes | Line to Ground | 99289451 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | CALISTOGA-1101 | 42711101 | FUSE | 8339 | 20130423 | 125 | 779863 | 725 | Distribution Circuit | Vegetation | Tree - branch fell on line | 62 | 44950 | 38.6326 | -122.6744 | MILE MARKER 20.80 AT FOOTE CREEK BRIDGE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0026458 | OH | Sus | 41887054 | yes | 2013 | APR | Yes | Line to Line | 99289069 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | OTHER |  | 20130423 | 741 | 780117 | 574 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1576 | 38.6415 | -122.5977 | 4 SPANS ON THE LOAD-SIDE OF LCO 6393- at THE SOURCE SIDE OF THE TRANSFORMER AT COORDINATES 2182955 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0026537 | OH | Sus | 41887403 | yes | 2013 | APR | Yes | Line to Ground | 99288989 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | CALISTOGA-1101 | 42711101 | FUSE | 9541 | 20130423 | 1353 | 780350 | 837 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 2547 | 38.6216 | -122.6795 | Bock/2425: RIGHT at THE LOAD-SIDE OF SOLID BLADE CUTOUTS 5249- at 10500 FRANZ VALLEY RD IN CALIS | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0026728 | OH | Sus | 41887681 | yes | 2013 | APR | Yes | Three Phase Fault | 99288856 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 665 | 20130424 | 708 | 780701 | 908 | Distribution Circuit | Equipment Failure/Involved | Other | 14 | 4715 | 38.6516 | -122.7351 | ON SINGLE PHASE HARD TAP 4 SPANS BEYOND 665 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0026849 | OH | Sus | 41887954 | No | 2013 | APR | Yes | Line to Ground | 99288797 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | OTHER |  | 20130424 | 1020 | 780999 | 345 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 345 | 38.6482 | -122.594 | 4485 LAKE COUNTY HWY | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0026879 | OH | Sus | 0 | No | 2013 | APR | Yes |  | 99288753 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | RECLOSER | 734 | 20130501 | 118 | 784669 | 2198 | Distribution Circuit | Vegetation | Tree - fell into line | 361 | 145508 | 38.5894 | -122.6077 | 3 SPANS LD SIDE OF 1843 TWD SW 4879 & AT SBCO 6639 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0028481 | OH | Sus | 0 | yes | 2013 | MAY | Yes | Multi-Fault | 99287300 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-1105 | 43291105 | FUSE | 1961 | 20130501 | 1948 | 785480 | 2858 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 5716 | 38.3779 | -122.2806 | 6 SPANS LD SIDE 0F 1961 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0028762 | OH | Sus | 0 | yes | 2013 | MAY | Yes | Line to Ground | 99287066 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 5847 | 20130506 | 254 | 788340 | 797 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 4916 | 38.0104 | -122.6888 | 5 SPANS LD SIDE OF 5847 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0029755 | OH | Sus | 30994579 | yes | 2013 | MAY | Yes | Line to Ground | 99286524 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | ALTO-1125 | 42031125 | FUSE | 2243 | 20130521 | 2051 | 796314 | 378 | Distribution Circuit | Vegetation | Tree - fell into line | 358 | 135324 | 37.8792 | -122.5388 | 534 NORTHERN AVE | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0033462 | OH | Sus | 0 | yes | 2013 | MAY | Yes | Three Phase Fault | 99284003 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 2629 | 20130521 | 2158 | 796371 | 757 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 48448 | 38.0103 | -122.7019 | VARIOUS LOCATIONS IN THE AREA OF 32 SPRING RD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0033478 | OH | Sus | 0 | yes | 2013 | MAY | Yes | Line to Line | 99283955 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | WOODACRE-1102 | 43021102 | RECLOSER | 1280 | 20130521 | 1724 | 796157 | 897 | Distribution Circuit | Vegetation | Tree - branch fell on line | 927 | 346974 | 37.996 | -122.5958 | Hlebakos/431: r/o 55 green valley ct. AND 2 SPANS LD SIDE OF 2145 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0033428 | OH | Sus | 0 | yes | 2013 | MAY | Yes | Line to Ground | 99283959 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 1087 | 20130610 | 602 | 807543 | 419 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 12696 | 38.584 | -122.6719 | 9000 FRANZ VALLEY SCHOOL RD | Lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0038099 | OH | Sus | 41909573 | yes | 2013 | JUN | Yes |  | 99280834 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1977 | 20130710 | 1827 | 829408 | 373 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2984 | 38.0857 | -122.839 | 11 REDWOOD AVE | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 13-0046535 | OH | Sus | 41924873 | No | 2013 | JUL | Yes | Line to Line | 99274870 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-1105 | 43291105 | FUSE | 1961 | 20130723 | 1834 | 837331 | 506 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1012 | 38.3779 | -122.2806 | 3 SPANS LD SIDE OF 1990 SODA CANYON RD. | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0049582 | OH | Sus | 41931891 | No | 2013 | JUL | Yes | Line to Ground | 99272704 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 421 | 20130814 | 1306 | 848306 | 285 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1140 | 38.5729 | -122.4417 | 2 SPANS LD SIDE OF FUCO 421 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0054558 | OH | Sus | 41943503 | No | 2013 | AUG | Yes | Line to Ground | 99269358 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | OTHER |  | 20130816 | 1748 | 849913 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 14746 | 38.1212 | -122.8828 | PIERCE POINT RD at 5 SPANS ON THE LOAD-SIDE OF RISER CUTOUTS 7295 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0055267 | OH | Sus | 31015435 | No | 2013 | AUG | Yes | Open Circuit | 99268928 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | RECLOSER | 1210 | 20130819 | 2332 | 852304 | 495 | Distribution Circuit | Vegetation | Tree - branch fell on line | 518 | 63945 | 37.9626 | -122.5689 | 49 GLENWOOD AVE- ROSS | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0055895 | OH | Sus | 31015891 | yes | 2013 | AUG | Yes |  | 99268287 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 3551 | 20130830 | 1310 | 858258 | 257 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 605 | 38.6063 | -122.6493 | 1 SPAN LOAD SIDE OF FUCO 3551 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0058835 | OH | Sus | 41949559 | No | 2013 | AUG | Yes | Line to Ground | 99266330 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | FUSE | 2147 | 20130914 | 1639 | 866175 | 524 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 33012 | 37.906 | -122.5521 | CASCADE AND MOLINO | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0062057 | OH | Sus | 31021379 | No | 2013 | SEP | Yes |  | 99263968 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | BOLINAS-1101 | 42261101 | FUSE | 98855 | 20130918 | 1156 | 868068 | 384 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1152 | 37.9289 | -122.6969 | 1 span ld side of fuco98855 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0062856 | OH | Sus | 0 | No | 2013 | SEP | Yes |  | 99263350 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1209 | 20130921 | 1323 | 870289 | 609 | Distribution Circuit | Vegetation | Tree - fell into line | 104 | 51592 | 38.0632 | -122.8208 | 36 BALBOA | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0063737 | OH | Sus | 31023264 | yes | 2013 | SEP | Yes |  | 99262773 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 2493 | 20130922 | 716 | 871000 | 604 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 7248 | 38.0969 | -122.859 | 3 SPANS LD SIDE OF 2493 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0063869 | OH | Sus | 41962821 | No | 2013 | SEP | Yes | Line to Ground | 99262605 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SAN RAFAEL-1104 | 42011104 | OTHER |  | 20130924 | 1838 | 872686 | 614 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 3530 | 37.9997 | -122.5811 | SAME AS ABOVE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0064598 | OH | Sus | 41963877 | No | 2013 | SEP | Yes | Line to Ground | 99262038 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 2625 | 20130924 | 1229 | 872387 | 229 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 2748 | 38.0129 | -122.6997 | SFD AND MT. VIEW | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0064460 | OH | Sus | 0 | No | 2013 | SEP | Yes | Three Phase Fault | 99262093 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-1105 | 43291105 | FUSE | 57813 | 20131003 | 741 | 876849 | 559 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 22165 | 38.4 | -122.2922 | 2367 SODA CANYON RD. NAPA | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0066713 | OH | Sus | 31025824 | yes | 2013 | OCT | Yes |  | 99260617 | PW | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5469 | 20131015 | 1619 | 885318 | 646 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 16556 | 38.0647 | -122.8251 | 78 DRAKE SUMMIT DR | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0069804 | OH | Sus | 0 | No | 2013 | OCT | Yes | Line to Ground | 99258245 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | WOODACRE-1101 | 43021101 | OTHER |  | 20131019 | 1225 | 887132 | 681 | Distribution Circuit | Animal | Bird found | 11 | 6441 | 38.0159 | -122.6741 | 1/W SS OF FUCO 2029 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0070783 | OH | Sus | 0 | No | 2013 | OCT | Yes | None | 99257585 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | BOLINAS-1101 | 42261101 | FUSE | 2165 | 20131020 | 633 | 887260 | 907 | Distribution Circuit | Equipment Failure/Involved | Other | 5 | 4535 | 37.954 | -122.7103 | ON THE SOURCE-SIDE OF THE TRANSFORMER at COORDINATES 3136197 53668 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0070821 | OH | Sus | 0 | No | 2013 | OCT | Yes | Line to Ground | 99257532 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SAN RAFAEL-1107 | 42011107 | FUSE | 4189 | 20131028 | 1145 | 892549 | 330 | Distribution Circuit | Vegetation | Tree - branch fell on line | 129 | 32516 | 37.9521 | -122.5589 | 3 TREE TOP LN | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0072818 | OH | Sus | 31031816 | yes | 2013 | OCT | Yes | Line to Ground | 99256111 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE | 8249 | 20131215 | 616 | 927832 | 515 | Distribution Circuit | 3rd Party | Vehicle | 4 | 2060 | 38.4787 | -122.2364 | CAPELL VALLEY CT at 6 POLES ON THE LOAD-SIDE OF LCO 8249 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0082397 | OH | Sus | 0 | No | 2013 | DEC | Yes | Line to Line | 99247717 | PW | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3585 | 20131218 | 2144 | 929791 | 856 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 15659 | 38.1033 | -122.8633 | BET: 325 AND 425 VISION | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0082818 | OH | Sus | 42048647 | No | 2013 | DEC | Yes | Line to Ground | 99247118 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 1087 | 20131219 | 2242 | 930778 | 427 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 12442 | 38.584 | -122.6719 | ON A BUCK LINE at 1 SPAN ON THE LOAD-SIDE OF LCO 1087 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0082982 | OH | Sus | 42049030 | yes | 2013 | DEC | Yes | Line to Ground | 99246872 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 2897 | 20131220 | 924 | 930983 | 426 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2130 | 38.5843 | -122.6817 | 2P LD SIDE OF CUTOUTS 2897 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0083036 | OH | Sus | 42049370 | No | 2013 | DEC | Yes | Line to Line | 99246769 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | TULUCAY-1101 | 42301101 | FUSE | 3025 | 20131221 | 1115 | 931497 | 325 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 7 | 2275 | 38.2107 | -122.2086 | Boydston/2486: 4901 jamison cyn.rd. | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0083136 | OH | Sus | 42049622 | No | 2013 | DEC | Yes |  | 99246620 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 1089 | 20140116 | 402 | 942530 | 644 | Distribution Circuit | Vegetation | Tree - fell into line | 225 | 96464 | 38.01 | -122.6402 | 15 MAPLE - REAR | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0004465 | OH | Sus | 42060230 | No | 2014 | JAN | Yes | Line to Ground | 99244093 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE | 3423 | 20140131 | 353 | 954989 | 465 | Distribution Circuit | Equipment Failure/Involved | Other | 20 | 15280 | 38.6796 | -122.2605 | Kent/2426: 5 spans load side of LCO 3423-Gamble Ranch | Drizzle-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0007827 | OH | Sus | 42068524 | No | 2014 | JAN | Yes |  | 99241982 | CSO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER | 1252 | 20140207 | 1444 | 961517 | 614 | Distribution Circuit | Vegetation | Tree - branch fell on line | 126 | 56572 | 38.0779 | -122.8333 | 45 DRAKES VIEW | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0009660 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Line | 99240970 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | FUSE | 835 | 20140208 | 36 | 962665 | 2104 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 216203 | 38.5074 | -122.4926 | 4401 SPRING MTN RD | Rain-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0009803 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Line | 99240579 | CAW | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER | 602 | 20140209 | 1931 | 964579 | 1314 | Distribution Circuit | Vegetation | Tree - fell into line | 155 | 44302 | 38.1093 | -122.87 | 8 SPANS LD SIDE OF FUCO 3393 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0010194 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Multi-Fault | 99240374 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1117 | 20140209 | 454 | 964447 | 221 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 11687 | 38.3726 | -122.4169 | 1250 LOKOYA RD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0010101 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Ground | 99240531 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | OTHER |  | 20140222 | 629 | 970773 | 451 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1353 | 38.3755 | -122.427 | AT FUCO 3035 (SAME P AS FUCO 2027) | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0012712 | OH | Sus | 42081838 | No | 2014 | FEB | Yes |  | 99238662 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | SWITCH | 743 | 20140225 | 830 | 971978 | 548 | Distribution Circuit | Animal | Squirrel | 527 | 277739 | 38.5932 | -122.439 | AT SW 743 AND BROKEN INSULATOR AT RISER 6715 | Partly cloudy-32 - 90 F | Insulator | Broken, wire on object | 14-0013179 | OH | Sus | 42082950 | No | 2014 | FEB | Yes | Open Circuit | 99238316 | INS | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | OTHER |  | 20140226 | 1901 | 972991 | 1079 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1079 | 38.0986 | -122.884 | Herries: 2 mt vision rd | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0013697 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Open Circuit | 99238002 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 2677 | 20140226 | 1947 | 973046 | 1280 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 136960 | 37.984 | -122.5919 | 71 FRUSTRUCK AVE | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0013627 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Multi-Fault | 99238016 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 757 | 20140227 | 648 | 973498 | 446 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 10861 | 38.0728 | -122.8278 | Hlebakos/431: 240 laurel st(last span of primary from c/o 757) | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0013781 | OH | Sus | 0 | yes | 2014 | FEB | Yes |  | 99237958 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 4535 | 20140228 | 1550 | 975535 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2240 | 38.0069 | -122.6987 | JENSEN- WILLIAM: 160 lagunitas rd | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0014577 | OH | Sus | 31059928 | yes | 2014 | FEB | Yes | Line to Ground | 99237450 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | OTHER |  | 20140303 | 1557 | 977758 | 81 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 28 | 2218 | 37.9169 | -122.5565 | 168 RALSTON AVE- MILL VALLEY | Drizzle-32 - 90 F | Insulator | Broken, wire on object | 14-0015165 | OH | Sus | 0 | No | 2014 | MAR | Yes | Line to Ground | 99236901 | INS | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE | 7353 | 20140312 | 956 | 983394 | 244 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 244 | 38.3325 | -122.1306 | 2 SPANS LD SIDE OF FUCO'S 7353 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0017517 | OH | Sus | 0 | yes | 2014 | MAR | Yes | Line to Line | 99235263 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2102 | 43292102 | FUSE | 407 | 20140312 | 347 | 982896 | 703 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 36556 | 38.4095 | -122.4656 | HEARN- TODD: 4420 trinity rd | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0017432 | OH | Sus | 42091325 | yes | 2014 | MAR | Yes |  | 99235341 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | FUSE | 4753 | 20140317 | 745 | 985525 | 400 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1600 | 38.5206 | -122.5381 | 4001 SPRING MTN. RD. | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0018473 | OH | Sus | 42093993 | No | 2014 | MAR | Yes | Line to Ground | 99234573 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 2227 | 20140319 | 817 | 986716 | 359 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 4308 | 37.896 | -122.6011 | 15 SP PAST FUCO 2227 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0019071 | OH | Sus | 42095567 | No | 2014 | MAR | Yes | Line to Ground | 99234198 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1119 | 20140402 | 907 | 994067 | 769 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4198 | 38.3822 | -122.4315 | 3410 MT VEEDER | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0022475 | OH | Sus | 31066938 | yes | 2014 | APR | Yes | Line to Ground | 99231830 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | OTHER |  | 20140404 | 1336 | 995275 | 1464 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1464 | 38.345 | -122.129 | TERRILL-RICH/4151/707-315-2058: 6699 gordon vly rd | Rain-32 - 90 F | Pole-Wood | Broken, wire on object | 14-0023121 | OH | Sus | 31067532 | No | 2014 | APR | Yes | Multi-Fault | 99231446 | PW | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1143 | 20140405 | 238 | 995461 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 17310 | 38.3461 | -122.3998 | 4715 REDWOOD RD | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0023188 | OH | Sus | 42102415 | No | 2014 | APR | Yes | Line to Ground | 99231439 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE | 5921 | 20140417 | 1446 | 1000868 | 899 | Distribution Circuit | Equipment Failure/Involved | Other | 31 | 20749 | 38.6062 | -122.2807 | Bock/2425: pole to pole Mile marker 7.18 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0025815 | OH | Sus | 42110058 | No | 2014 | APR | Yes | Line to Line | 99229730 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE | 2821 | 20140419 | 153 | 1001462 | 592 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4144 | 38.3321 | -122.1357 | SCHERER JR- MARK: 50 Hidden Springs Rd | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0025987 | OH | Sus | 42110639 | No | 2014 | APR | Yes | Line to Line | 99229616 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 1165 | 20140422 | 717 | 1002711 | 348 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1044 | 38.5549 | -122.4727 | Bock/2425: 1044 Deer Park Rd | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0026384 | OH | Sus | 42111686 | No | 2014 | APR | Yes |  | 99229304 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | ALTO-1125 | 42031125 | FUSE | 935 | 20140426 | 641 | 1004981 | 441 | Distribution Circuit | Equipment Failure/Involved | Other | 360 | 194620 | 37.8792 | -122.5384 | MARIN AVE- 5P LD SIDE OF FUCO'S 935 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0027487 | OH | Sus | 42113726 | yes | 2014 | APR | Yes | Line to Ground | 99228569 | CSO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5407 | 20140502 | 1909 | 1009397 | 442 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 5746 | 38.0694 | -122.8269 | 6 SPANS LD SIDE OF 5407 NEAR 220 VALLEJO ST. | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0029020 | OH | Sus | 31073528 | No | 2014 | MAY | Yes | Line to Ground | 99227534 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 2383 | 20140503 | 1805 | 1009733 | 588 | Distribution Circuit | 3rd Party | Vehicle | 25 | 14700 | 38.5817 | -122.6737 | ON FRANZ VALLEY SCHOOL RD AT COR/OF FRANZ VALLEY RD- 4 SPANS LD SIDE OF FUCO 2383 | Partly cloudy-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0029100 | OH | Sus | 31073544 | No | 2014 | MAY | Yes | Line to Line | 99227454 | CAW | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | FUSE | 2147 | 20140505 | 1955 | 1010661 | 537 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 33831 | 37.906 | -122.5521 | 36 CASCADE WAY- MILL VALLEY | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0029452 | OH | Sus | 42117622 | yes | 2014 | MAY | Yes | Line to Line | 99227198 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | FUSE | 835 | 20140505 | 1508 | 1010538 | 874 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 42918 | 38.5074 | -122.4926 | 3100 SPRING MTN RD | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0029435 | OH | Sus | 0 | yes | 2014 | MAY | Yes | Line to Line | 99227214 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER | 1252 | 20140506 | 1617 | 1011182 | 668 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 82832 | 38.0779 | -122.8333 | 2 SPANS W/OF LR-1252 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0029774 | OH | Sus | 42118083 | yes | 2014 | MAY | Yes |  | 99227015 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1885 | 20140510 | 919 | 1012871 | 601 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 34495 | 38.0983 | -122.8592 | 1 POLE WEST OF 22 CAMERON ST | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0030741 | OH | Sus | 42119713 | yes | 2014 | MAY | Yes | Line to Ground | 99226439 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | SWITCH | 743 | 20140514 | 2159 | 1015871 | 1088 | Distribution Circuit | Vegetation | Tree - fell into line | 527 | 441076 | 38.5932 | -122.439 | SAME SPAN LD SIDE OF 743. | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0031913 | OH | Sus | 42123551 | yes | 2014 | MAY | Yes |  | 99225607 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 6667 | 20140522 | 1206 | 1022504 | 650 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 21786 | 37.9789 | -122.592 | 110 WOOD LN | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0033761 | OH | Sus | 31077881 | No | 2014 | MAY | Yes | Line to Line | 99224327 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE | 4909 | 20140525 | 1906 | 1023977 | 598 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 7865 | 38.3389 | -122.1174 | 14 VALLA VISTA DR | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0034236 | OH | Sus | 31078318 | No | 2014 | MAY | Yes |  | 99223997 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 311 | 20140612 | 630 | 1033358 | 653 | Distribution Circuit | Equipment Failure/Involved | Other | 20 | 7720 | 38.0437 | -122.7462 | 4 SPANS FROM 333 TWD 3357 | Overcast-32 - 90 F | Crossarm, Wood | Broken, wire on object | 14-0037920 | OH | Sus | 31082324 | No | 2014 | JUN | Yes | Line to Ground | 99221433 | CAW | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-1104 | 43291104 | FUSE | 1029 | 20140621 | 1436 | 1037718 | 801 | Distribution Circuit | 3rd Party | Vehicle | 20 | 16020 | 38.3644 | -122.2626 | 2245 ATLAS PEAK RD | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0039764 | OH | Sus | 31084011 | No | 2014 | JUN | Yes | Line to Line | 99220068 | PW | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 6523 | 20140630 | 325 | 1041749 | 891 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 14935 | 37.9421 | -122.5601 | 101 IDLEWOOD RD. KENTFIELD | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0041333 | OH | Sus | 31085783 | No | 2014 | JUN | Yes | Three Phase Fault | 99218868 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 3807 | 20140701 | 643 | 1042493 | 1837 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9185 | 38.5471 | -122.5824 | 7P LD SIDE OF CUTOUTS 3807 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0041629 | OH | Sus | 31086167 | yes | 2014 | JUL | Yes | Line to Line | 99218483 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 49257 | 20140714 | 1632 | 1049314 | 758 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5306 | 38.1057 | -122.8619 | 2 SPANS FROM SIR FRANCIS DRAKE BLVD AT WOODHAVEN- INVERNESS | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0044429 | OH | Sus | 31088874 | yes | 2014 | JUL | Yes | Line to Line | 99216742 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 3045 | 20140722 | 1245 | 1053386 | 765 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1530 | 38.3874 | -122.4326 | 3525 MT VEETER RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0046155 | OH | Sus | 42158201 | yes | 2014 | JUL | Yes | Open Circuit | 99215571 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-1104 | 43291104 | FUSE | 1091 | 20140731 | 1609 | 1058982 | 873 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 13968 | 38.4406 | -122.246 | SS OF 3889 FUCO 4500 ATLAS PEAK | Partly cloudy-Above 90 F | Conductor, Overhead | Broken, wire on ground | 14-0048433 | OH | Sus | 42161931 | yes | 2014 | JUL | Yes | None | 99213950 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 851 | 20140731 | 2055 | 1059129 | 431 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 46696 | 38.0056 | -122.638 | 289 REDWOOD - WOODACRE - 11 SPANS LD SIDE | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0048462 | OH | Sus | 42162000 | yes | 2014 | JUL | Yes | Line to Ground | 99213983 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 2021 | 20140805 | 1605 | 1061504 | 598 | Distribution Circuit | Equipment Failure/Involved | Other | 4 | 2392 | 38.3619 | -122.3737 | 4613 DRY CREEK RD- NAPA | Overcast-32 - 90 F | Crossarm, Wood | Broken, wire on object | 14-0049297 | OH | Sus | 31093296 | No | 2014 | AUG | Yes | None | 99213338 | CAW | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2102 | 43432102 | RECLOSER | 34959 | 20140812 | 312 | 1065199 | 820 | Distribution Circuit | Vegetation | Tree - branch fell on line | 203 | 87857 | 38.5071 | -122.3741 | 2910 LOWER CHILES VALLEY RD- ST HELENA | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0050446 | OH | Sus | 31094547 | No | 2014 | AUG | Yes |  | 99212464 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2102 | 43292102 | FUSE | 3121 | 20140902 | 432 | 1075928 | 471 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 23550 | 38.4083 | -122.4301 | 5373 DRY CREEK RD. | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0054463 | OH | Sus | 42179578 | No | 2014 | SEP | Yes | Line to Ground | 99209603 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 6325 | 20140905 | 1058 | 1077678 | 492 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 19 | 2598 | 37.9779 | -122.5799 | 557 PHOENIX DR. | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0055353 | OH | Sus | 42181901 | No | 2014 | SEP | Yes | Line to Ground | 99209073 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | FUSE | 4595 | 20141006 | 103 | 1093344 | 708 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 18714 | 37.9154 | -122.5576 | 3 SPANS LD SIDE OF 6873 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0061531 | OH | Sus | 31105622 | No | 2014 | OCT | Yes | Line to Ground | 99204806 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SILVERADO-2104 | 43432104 | SECTIONALIZER | 7917 | 20141008 | 1418 | 1094734 | 682 | Distribution Circuit | Vegetation | Tree - fell into line | 223 | 142096 | 38.6632 | -122.4482 | 1965 SNELL CANYON | Clear-Above 90 F | Conductor, Overhead | Broken, wire on ground | 14-0062368 | OH | Sus | 42203561 | No | 2014 | OCT | Yes | Line to Ground | 99204363 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | RECLOSER | 736 | 20141015 | 1509 | 1097987 | 726 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 405 | 148512 | 38.5803 | -122.5978 | 5055 MOUNTAIN HOME RANCH RD IN CALISTOGA | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0063917 | OH | Sus | 31107610 | yes | 2014 | OCT | Yes | Line to Line | 99203359 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 2761 | 20141015 | 503 | ODB-9920 | 657 | Distribution Circuit | Equipment Failure/Involved | Other | 17 | 11169 | 38.0671 | -122.7264 | 1 SPAN LD SIDE OF FUCO 2761 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0063692 | OH | Sus | 0 | yes | 2014 | OCT | Yes |  | 99203494 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5407 | 20141026 | 333 | 1102999 | 642 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 8346 | 38.0694 | -122.8269 | 350 VALLEJO AVE- INVERNESS (6P LD SIDE OF 5407) | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0066159 | OH | Sus | 42215943 | No | 2014 | OCT | Yes | Line to Line | 99201933 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 2565 | 20141103 | 1318 | 1108630 | 426 | Distribution Circuit | Vegetation | Tree - fell into line | 160 | 30900 | 37.9594 | -122.5348 | 121 CYPRESS | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0067972 | OH | Sus | 0 | No | 2014 | NOV | Yes | Line to Line | 99200598 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-1104 | 43291104 | FUSE | 1091 | 20141105 | 834 | 1109200 | 288 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 4608 | 38.4406 | -122.246 | GREENE- JOSEPH: 4578 Atlas peak rd | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0068314 | OH | Sus | 42223685 | No | 2014 | NOV | Yes | None | 99200407 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | OTHER |  | 20141117 | 1715 | 1114332 | 1350 | Distribution Circuit | Equipment Failure/Involved | Other | 12 | 7950 | 38.0444 | -122.86 | 1 SPAN LD SIDE OF FUCO 6803 | Lightning-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0070559 | OH | Sus | 31115741 | No | 2014 | NOV | Yes | Line to Ground | 99198913 | CAW | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE | 2683 | 20141120 | 856 | 1115552 | 398 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2388 | 38.5638 | -122.5615 | 7 SPANS LOAD SIDE OF 2683 | Lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0071082 | OH | Sus | 42278555 | No | 2014 | NOV | Yes | Line to Ground | 99198568 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1107 | 42011107 | OTHER |  | 20141120 | 1611 | 1115828 | 950 | Distribution Circuit | Vegetation | Tree - bark fell into line | 38 | 2503 | 37.9653 | -122.5524 | LABO: 1 SPAN N/OF 10 SKYVIEW WY | Lightning-32 - 90 F | Conductor, Overhead | On Ground | 14-0071278 | OH | Sus | 31117017 | No | 2014 | NOV | Yes | Line to Ground | 99198439 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 4365 | 20141201 | 704 | 1119940 | 1102 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 39310 | 38.5825 | -122.4592 | 4365 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0072563 | OH | Sus | 31118133 | No | 2014 | DEC | Yes | Three Phase Fault | 99197401 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER | 1252 | 20141202 | 2015 | 1121472 | 402 | Distribution Circuit | Vegetation | Tree - fell into line | 126 | 50146 | 38.0779 | -122.8333 | JENSEN- WILLIAM: 30 drakes view dr | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073079 | OH | Sus | 31118818 | yes | 2014 | DEC | Yes | Line to Ground | 99197092 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | FUSE | 2147 | 20141205 | 2141 | 1125614 | 904 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 56952 | 37.9059 | -122.5522 | 26 CASCADE | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074100 | OH | Sus | 31119758 | No | 2014 | DEC | Yes | Line to Ground | 99196147 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | RECLOSER | 1238 | 20141206 | 613 | 1125777 | 718 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 39433 | 38.0108 | -122.7023 | JENSEN- WILLIAM: 2 spans loadside 333 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074132 | OH | Sus | 42291785 | No | 2014 | DEC | Yes | Multi-Fault | 99196112 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 1089 | 20141206 | 915 | 1125807 | 705 | Distribution Circuit | Vegetation | Tree - fell into line | 226 | 16789 | 38.01 | -122.6402 | 29 MADRONE | Fog-32 - 90 F | Conductor, Overhead | On Ground | 14-0074148 | OH | Sus | 42291789 | No | 2014 | DEC | Yes |  | 99196089 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1869 | 20141213 | 951 | 1139642 | 279 | Distribution Circuit | Equipment Failure/Involved | Other | 5 | 1395 | 38.039 | -122.7852 | I SPANS LD SIDE OF FUCO 1869 | Fog-32 - 90 F | Conductor, Overhead | On Ground | 14-0076708 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193380 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | CALISTOGA-1101 | 42711101 | FUSE | 8339 | 20141216 | 636 | 1141886 | 694 | Distribution Circuit | 3rd Party | Vehicle | 77 | 53438 | 38.6326 | -122.6744 | 7411 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0077166 | OH | Sus | 31121407 | yes | 2014 | DEC | Yes | Line to Line | 99192833 | PW | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2102 | 43432102 | FUSE | 3091 | 20141216 | 1747 | 1142460 | 671 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 31518 | 38.5125 | -122.4556 | 1 POLE LOAD SIDE OF MTR#1006223756 TWD 375 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077318 | OH | Sus | 42299366 | yes | 2014 | DEC | Yes | Line to Ground | 99192646 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | ALTO-1120 | 42031120 | FUSE | 6445 | 20141217 | 646 | 1142697 | 429 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 7293 | 37.8776 | -122.5334 | MTR#1008132281 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077368 | OH | Sus | 31121622 | No | 2014 | DEC | Yes | Line to Ground | 99192625 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | FUSE | 2129 | 20141217 | 406 | 1142657 | 1244 | Distribution Circuit | Vegetation | Tree - fell into line | 679 | 21980 | 37.9213 | -122.5556 | MTR#1008777941- # 545 W. BLITHEDALE | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0077360 | OH | Sus | 31121599 | No | 2014 | DEC | Yes | Line to Line | 99192629 | PW | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 1085 | 20141217 | 1020 | 1142861 | 890 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 24030 | 38.5718 | -122.6495 | MTR#1005992096 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0077396 | OH | Sus | 31121637 | No | 2014 | DEC | Yes | None | 99192581 | PW | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 1089 | 20141217 | 1627 | 1143196 | 653 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 50934 | 38.5774 | -122.4544 | 4SP LD SIDE OF FUSE 1089 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077482 | OH | Sus | 0 | No | 2014 | DEC | Yes | Line to Line | 99192518 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | CALISTOGA-1101 | 42711101 | FUSE | 8355 | 20141218 | 2143 | 1144022 | 1037 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 17799 | 38.622 | -122.6787 | 2 SPANS LD SIDE OF SBCO 1161 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077633 | OH | Sus | 31122189 | No | 2014 | DEC | Yes | Three Phase Fault | 99192277 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2102 | 43292102 | FUSE | 7619 | 20141218 | 1716 | 1143954 | 275 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 275 | 38.4016 | -122.4715 | SPAN LD SIDE OF FUCO 7619 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077620 | OH | Sus | 31122137 | No | 2014 | DEC | Yes | Line to Ground | 99192318 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 141 | 20141219 | 753 | 1144177 | 573 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 4164 | 38.5785 | -122.4422 | MTR#1009812013 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077685 | OH | Sus | 42301307 | No | 2014 | DEC | Yes | Line to Ground | 99192227 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | WOODACRE-1101 | 43021101 | RECLOSER | OCB | 20141219 | 1140 | 1144378 | 1678 | Distribution Circuit | Vegetation | Tree - fell into line | 1281 | 0 | 38.0193 | -122.6628 | 5720 NICASIO VALLEY RD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077701 | OH | Sus | 42301458 | No | 2014 | DEC | Yes |  | 99192143 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 605 | 20141221 | 1935 | 1145704 | 455 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 22295 | 38.1105 | -122.8717 | 570 VIA DELA VISTA | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077922 | OH | Sus | 31122455 | No | 2014 | DEC | Yes | Line to Line | 99191965 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1101 | 42011101 | FUSE | 101895 | 20141221 | 845 | 1145416 | 1798 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7192 | 37.9606 | -122.5132 | 1SP LD SIDE OF FUCO 101895 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077908 | OH | Sus | 31122449 | No | 2014 | DEC | Yes | Line to Ground | 99191942 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 141 | 20141223 | 522 | 1146386 | 389 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1079 | 38.5785 | -122.4422 | 400 HOWELL MOUNTAIN RD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078081 | OH | Sus | 31122816 | No | 2014 | DEC | Yes | Line to Ground | 99191757 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | GREENBRAE-1102 | 43091102 | FUSE | 2379 | 20141224 | 1343 | 1147462 | 1325 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 51675 | 37.9535 | -122.5352 | MTR#18P896 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078268 | OH | Sus | 42302870 | yes | 2014 | DEC | Yes | Line to Ground | 99191398 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | LAS GALLINAS A-1105 | 42991105 | RECLOSER | 99904 | 20141224 | 1442 | 1147557 | 2339 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 136407 | 38.0443 | -122.6162 | LABO MICHAEL: 5055 LUCAS VALLEY RD | Rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0078264 | OH | Sus | 31123302 | yes | 2014 | DEC | Yes | Line to Line | 99191264 | PW | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER | 722 | 20141226 | 1116 | 1148715 | 578 | Distribution Circuit | Vegetation | Tree - fell into line | 522 | 47611 | 38.545 | -122.4758 | 1108 DEER PARK RD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078547 | OH | Sus | 31123405 | No | 2014 | DEC | Yes | Line to Ground | 99191217 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5467 | 20150107 | 747 | 1160404 | 635 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1270 | 38.1088 | -122.8954 | 3 SPANS PAST FUCO 5467 | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 15-0003032 | OH | Sus | 42308821 | No | 2015 | JAN | Yes | Line to Ground | 99188915 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | FUSE | 4135 | 20150114 | 1007 | 1163629 | 397 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 794 | 38.516 | -122.518 | 3443 SPRING MTN RD - AT END OF LINE | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on object | 15-0004507 | OH | Sus | 31128203 | No | 2015 | JAN | Yes | Line to Ground | 99188088 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-2103 | 43292103 | FUSE | 9295 | 20150131 | 915 | 1170589 | 1019 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 27513 | 38.3135 | -122.3593 | GREER- JEFF: 1660 Partrick | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 15-0008481 | OH | Sus | 42325329 | No | 2015 | JAN | Yes | Line to Ground | 99186107 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | OTHER |  | 20150209 | 1054 | 1186349 | 910 | Distribution Circuit | Vegetation | Tree - fell into line | 217 | 197470 | 38.6021 | -122.632 | LD SIDE OF SBCO 3539 TWD 8321/18907 HWY 128 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012121 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183162 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE | 4909 | 20150209 | 1021 | 1186233 | 859 | Distribution Circuit | Equipment Failure/Involved | Other | 22 | 7763 | 38.3389 | -122.1174 | 8 SPANS LD SIDE OF FUCO 4909 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0012160 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183137 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER | 632 | 20150209 | 315 | 1185628 | 833 | Distribution Circuit | Equipment Failure/Involved | Other | 744 | 386844 | 38.5741 | -122.4439 | HUNKINS- DARIN: 1400 howell mnt | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011999 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183237 | PW | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | SWITCH | 7927 | 20150216 | 339 | 1190790 | 844 | Distribution Circuit | Equipment Failure/Involved | Other | 440 | 124760 | 38.34 | -122.3935 | Griffith/2483: 1 pole past 2113 wire down across cyn | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0013492 | OH | Sus | 31134930 | No | 2015 | FEB | Yes | Line to Line | 99181880 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 1449 | 20150217 | 1403 | 1191680 | 762 | Distribution Circuit | Vegetation | Tree - fell into line | 244 | 185928 | 38.5379 | -122.4761 | 623 SUNNYSIDE RDE | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0013764 | OH | Sus | 31135073 | No | 2015 | FEB | Yes | Line to Ground | 99181667 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1122 | 42031122 | OTHER |  | 20150226 | 2109 | 1196445 | 401 | Distribution Circuit | Vegetation | Tree - fell into line | 1765 | 65220 | 37.9208 | -122.5262 | BET: 158 AND 161 STETSON AVE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 15-0016051 | OH | Sus | 0 | No | 2015 | FEB | Yes | Line to Ground | 99180258 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | OTHER |  | 20150322 | 2119 | 1206703 | 876 | Distribution Circuit | Vegetation | Tree - branch fell on line | 32 | 25127 | 38.6552 | -122.5967 | 45.50 MILE MARKER OF HWY 29 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0021245 | OH | Sus | 42354934 | No | 2015 | MAR | Yes | Line to Ground | 99177195 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2102 | 43292102 | FUSE | 3121 | 20150328 | 2220 | 1209338 | 747 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 29620 | 38.4083 | -122.4301 | 6700 DRY CREEK RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0022775 | OH | Sus | 31144380 | No | 2015 | MAR | Yes | Line to Ground | 99176388 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | OTHER |  | 20150331 | 1909 | 1210901 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 7936 | 37.9922 | -122.5961 | 2P LD SIDE OF FUCOS 2657 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0023387 | OH | Sus | 31145005 | No | 2015 | MAR | Yes | None | 99176017 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SILVERADO-2102 | 43432102 | FUSE | 3531 | 20150407 | 1313 | 1215066 | 557 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 1114 | 38.5059 | -122.4076 | END OF TAP AT THE LAST TRANSFORMER | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0025021 | OH | Sus | 0 | yes | 2015 | APR | Yes | Line to Ground | 99174913 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 7311 | 20150407 | 1835 | 1215538 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 15059 | 38.5194 | -122.4623 | 3 SPANS LD SIDE OF 7311 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0025144 | OH | Sus | 0 | yes | 2015 | APR | Yes | Three Phase Fault | 99174829 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1641 | 20150409 | 614 | 1216270 | 408 | Distribution Circuit | Equipment Failure/Involved | Other | 62 | 9825 | 38.1329 | -122.9085 | RT.OF L RANCH RD-OFF PIERCE PT. RD.INVERNESS | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0025461 | OH | Sus | 31146964 | No | 2015 | APR | Yes | Line to Ground | 99174465 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | FUSE | 641 | 20150413 | 1454 | 1218742 | 2051 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 7091 | 38.5135 | -122.5097 | SPAN ON SOURCE SIDE OF RISER C/OUT 3809 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0026361 | OH | Sus | 0 | yes | 2015 | APR | Yes | Line to Ground | 99173750 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | SWITCH | 7927 | 20150415 | 127 | 1219842 | 810 | Distribution Circuit | Equipment Failure/Involved | Other | 343 | 97410 | 38.34 | -122.3935 | 4550 REDWOOD RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0026739 | OH | Sus | 0 | No | 2015 | APR | Yes | Line to Ground | 99173540 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | WOODACRE-1102 | 43021102 | OTHER |  | 20150428 | 2020 | 1226604 | 425 | Distribution Circuit | Vegetation | Tree - branch fell on line | 155 | 13868 | 38.0062 | -122.5758 | 35 GREEN VALLEY CT | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0030294 | OH | Sus | 42377924 | No | 2015 | APR | Yes | Line to Ground | 99171270 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 3343 | 20150502 | 2131 | 1228528 | 1774 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 43790 | 38.3612 | -122.3717 | N/OF 4598 DRY CREEK RD | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0031297 | OH | Sus | 31152523 | No | 2015 | MAY | Yes | Line to Ground | 99170636 | PW | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE | 1985 | 20150514 | 1350 | 1234533 | 1381 | Distribution Circuit | Environmental/External | Lightning | 37 | 16745 | 38.4835 | -122.1489 | LOAD SIDE OF 9667 TWD 7481 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0034193 | OH | Sus | 31154986 | yes | 2015 | MAY | Yes | Line to Line | 99168542 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | RECLOSER | 37384 | 20150525 | 1632 | 1239278 | 189 | Distribution Circuit | Vegetation | Tree - fell into line | 509 | 61927 | 38.4451 | -122.1965 | AT SBCO 8393 ON LINE SIDE | Clear-32 - 90 F | Conductor, Overhead | On Ground | 15-0036310 | OH | Sus | 42394749 | No | 2015 | MAY | Yes | Multi-Fault | 99167105 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 1247 | 20150602 | 1501 | 1242785 | 685 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 22605 | 37.9735 | -122.6126 | 2 SPANS LD SIDE OF FUCO 1247 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0038006 | OH | Sus | 31158683 | No | 2015 | JUN | Yes | Line to Line | 99165942 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1143 | 20150605 | 125 | 1243883 | 786 | Distribution Circuit | Vegetation | Tree - fell into line | 342 | 53842 | 38.3461 | -122.3998 | 4870 REDWOOD RD | Overcast-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0038607 | OH | Sus | 42401314 | yes | 2015 | JUN | Yes | Line to Ground | 99165529 | PW | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | SECTIONALIZER | 3925 | 20150609 | 1524 | s1139984 | 971 | Distribution Circuit | Vegetation | Tree - fell into line | 1442 | 651298 | 38.5446 | -122.4782 | WIRE DOWN 2 POLES LD SIDE OF 2987. OPEN JUMPER IN MAIN LINE ON SORURCE SIDE OF 7699 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0039825 | OH | Sus | 42402674 | yes | 2015 | JUN | Yes | Multi-Fault | 99164355 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2102 | 43292102 | OTHER |  | 20150627 | 1329 | 1257842 | 710 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1420 | 38.4071 | -122.4625 | 6493 DRY CREEK RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0043769 | OH | Sus | 31164674 | No | 2015 | JUN | Yes | Line to Ground | 99161615 | CO | OH | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SILVERADO-2105 | 43432105 | OTHER | 3475 ST HELENA HWY | 20150730 | 1914 | 1280464 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1028 | 38.5457 | -122.5105 | 3475 ST HELENA HWY | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0051793 | OH | Sus | 42440248 | No | 2015 | JUL | Yes | Open Circuit | 1148390 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | FUSE | 3119 | 20150803 | 633 | 1281753 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 22040 | 37.9075 | -122.5546 | 192 LAVELLE | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 15-0052198 | OH | Sus | 42441745 | No | 2015 | AUG | Yes | Line to Line | 1148707 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | RECLOSER | 1250 | 20150815 | 1341 | 1288785 | 281 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 4936 | 37.9607 | -122.5709 | N/E OF METER # 20P449 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0055217 | OH | Sus | 0 | No | 2015 | AUG | Yes | Line to Line | 1150840 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | WOODACRE-1101 | 43021101 | OTHER | WIRE DOWN BET 2603 AND 6579 | 20150815 | 225 | 1288584 | 1101 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 33910 | 38.0865 | -122.695 | 1200 OLD RANCHERIA RD IN NICASIO | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0055178 | OH | Sus | 0 | No | 2015 | AUG | Yes | Line to Line | 1150801 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SAN RAFAEL-1105 | 42011105 | FUSE | 5753 | 20150829 | 2131 | 1296996 | 734 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 4736 | 37.9798 | -122.4964 | IFO 320 MARGARITA DRIVE IN SAN RAFAEL | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on object | 15-0058225 | OH | Sus | 0 | yes | 2015 | AUG | Yes | Open Circuit | 1152934 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 6325 | 20150829 | 323 | 1296576 | 972 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 18468 | 37.9779 | -122.58 | JENSEN- WILLIAM: . | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0058128 | OH | Sus | 0 | yes | 2015 | AUG | Yes | Force Out | 1152831 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER | 806 | 20150829 | 1925 | 1296951 | 495 | Distribution Circuit | Equipment Failure/Involved | Overhead | 142 | 34590 | 38.6172 | -122.4244 | 1P LD SIDE OF LR 806 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0058213 | OH | Sus | 42460481 | yes | 2015 | AUG | Yes | Line to Ground | 1152919 | CSO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 2627 | 20150830 | 1603 | 1297305 | 675 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 41817 | 38.0122 | -122.702 | FUCO 5857 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0058269 | OH | Sus | 31180523 | No | 2015 | AUG | Yes |  | 1152979 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 3963 | 20150909 | 1905 | 1302835 | 523 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 15690 | 37.9028 | -122.5614 | Donahue/439: / | Clear-Heat Wave-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0060298 | OH | Sus | 31182797 | yes | 2015 | SEP | Yes | Line to Ground | 1154436 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2102 | 43432102 | OTHER | WIRE DOWN SOURCE SIDE OF REG 8365 | 20150910 | 1624 | 1303666 | 986 | Distribution Circuit | Equipment Failure/Involved | Overhead | 198 | 130124 | 38.5057 | -122.3547 | COUPLE OF SPANS SS OF REGS 8365 - NEED MAIN LINE CLEARED | Clear-Heat Wave-Above 90 | Conductor, Overhead | Broken, wire on ground | 15-0060610 | OH | Sus | 31183209 | yes | 2015 | SEP | Yes | Open Circuit | 1154657 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER | 602 | 20150911 | 815 | 1303890 | 497 | Distribution Circuit | Equipment Failure/Involved | Overhead | 155 | 32419 | 38.1094 | -122.87 | LD SIDE C/OUTS 1641 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0060698 | OH | Sus | 31183428 | yes | 2015 | SEP | Yes | Line to Ground | 1154720 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | OTHER | WIRE DOWN 2 W/OF FUCO 4753 | 20150913 | 426 | 1304997 | 1416 | Distribution Circuit | Vegetation | Tree - fell into line | 143 | 82390 | 38.5199 | -122.5405 | 4100 SPRING MTN RD. | Clear-32-90 F | Conductor, Overhead | On Ground | 15-0061096 | OH | Sus | 42470144 | No | 2015 | SEP | Yes | Line to Ground | 1154985 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 1089 | 20150916 | 1811 | 1307079 | 402 | Distribution Circuit | Vegetation | Tree - fell into line | 224 | 31585 | 38.0101 | -122.6402 | 12 SYLAN WY | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0061783 | OH | Sus | 42475124 | No | 2015 | SEP | Yes | Line to Ground | 1155498 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 5461 | 20150928 | 2019 | 1313341 | 531 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 3186 | 38.6072 | -122.651 | 18775 FOSS HILL RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0066190 | OH | Sus | 0 | No | 2015 | SEP | Yes | Line to Ground | 1159345 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5407 | 20151003 | 1700 | 1315996 | 867 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 12138 | 38.0694 | -122.8269 | 1P LD SIDE OF FUCO'S 5407 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0067611 | OH | Sus | 31188372 | yes | 2015 | OCT | Yes | Line to Line | 1160370 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 9169 | 20151004 | 46 | 1316631 | 994 | Distribution Circuit | 3rd Party | Vehicle | 18 | 10532 | 38.5721 | -122.5927 | 100 KORTUM CANYON RD | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 15-0067786 | OH | Sus | 0 | yes | 2015 | OCT | Yes | Line to Ground | 1160557 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2102 | 43292102 | JUMPER | WIRE DOWN 17 VINEYARD VIEW DR | 20151106 | 2012 | 1336832 | 1048 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2096 | 38.3847 | -122.3663 | 17 VINEYARD VIEW DR. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0076289 | OH | Sus | 42563409 | No | 2015 | NOV | Yes | Line to Ground | 1167035 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | BOLINAS-1101 | 42261101 | OTHER | WIRE DOWN | 20151109 | 708 | 1337675 | 2020 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 20852 | 37.9425 | -122.702 | SS OF FUCO 4913-1ST SPAN FROM 4/0AR MAILINE TWD 4913 | Overcast-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0076664 | OH | Sus | 42564202 | yes | 2015 | NOV | Yes | Line to Ground | 1167376 | CSO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 6333 | 20151116 | 206 | 1342745 | 487 | Distribution Circuit | Vegetation | Tree - branch fell on line | 93 | 13546 | 37.9024 | -122.557 | 506 PARK | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 15-0078082 | OH | Sus | 0 | yes | 2015 | NOV | Yes | Line to Ground | 1168568 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1101 | 42011101 | JUMPER | OJ SOURCE SIDE METER 1007926027 | 20151124 | 1351 | 1348129 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1848 | 37.962 | -122.5256 | SOURCE SIDE OF METER 1007926027 | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 15-0080640 | OH | Sus | 0 | yes | 2015 | NOV | Yes | Force Out | 1170581 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 6831 | 20151124 | 1438 | 1348090 | 853 | Distribution Circuit | 3rd Party | Vehicle | 94 | 51532 | 38.5716 | -122.4479 | 6831 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 15-0080664 | OH | Sus | 0 | yes | 2015 | NOV | Yes | Force Out | 1170587 | PW | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 479 | 20151130 | 1058 | 1350587 | 760 | Distribution Circuit | Animal | Squirrel | 265 | 172228 | 38.576 | -122.4446 | MTR 1006219255 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0081706 | OH | Sus | 42580058 | No | 2015 | NOV | Yes | Line to Ground | 1171528 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE | 35663 | 20151206 | 335 | 1354555 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 5420 | 38.4049 | -122.2054 | 174 COUNTRY CLUB LN | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on object | 15-0083014 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Line | 1172617 | CAW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 3417 | 20151206 | 1943 | 1354836 | 443 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 16834 | 37.9642 | -122.5505 | 2 SPANS SS OF NORMAL OPEN SW 5049 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083072 | OH | Sus | 31204428 | No | 2015 | DEC | Yes | Line to Line | 1172690 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER | 1252 | 20151209 | 1802 | 1356493 | 486 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 53802 | 38.0779 | -122.8329 | Hlebakos/431: 3 spans load side of c/o 5357 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083657 | OH | Sus | 42585973 | yes | 2015 | DEC | Yes | Line to Ground | 1173293 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 311 | 20151210 | 841 | 1357413 | 387 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 5757 | 38.0439 | -122.7468 | 2 POLES N/OF 3357 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0083930 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Three Phase Fault | 1173574 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2102 | 43432102 | FUSE | 1605 | 20151210 | 1227 | 1357869 | 756 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 65016 | 38.5038 | -122.3529 | AT LOAD SIDE OF 1605 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 15-0084000 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Three Phase Fault | 1173633 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 479 | 20151210 | 500 | 1357307 | 523 | Distribution Circuit | Vegetation | Tree - branch fell on line | 266 | 89520 | 38.576 | -122.4446 | 315 CLARK WY | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 15-0083868 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1173511 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 2859 | 20151218 | 2104 | 1366389 | 881 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 6167 | 38.5899 | -122.6086 | 3141 HWY 128 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | On Ground | 15-0086142 | OH | Sus | 31207517 | No | 2015 | DEC | Yes | Line to Ground | 1176073 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE | 1589 | 20151220 | 550 | 1366974 | 451 | Distribution Circuit | Vegetation | Tree - fell into line | 176 | 66979 | 38.4069 | -122.2056 | 450 COUNTRY CLUB LANE- NAPA | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086273 | OH | Sus | 31207684 | No | 2015 | DEC | Yes | Line to Line | 1176227 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | RECLOSER | 902 | 20151222 | 502 | 1368601 | 2159 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 23686 | 37.8892 | -122.5553 | Hlebakos/431: between LR 902 & Muir Woods | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086625 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1176621 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE | 9193 | 20151222 | 346 | 1368642 | 579 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 3107 | 38.5646 | -122.5585 | 4377 SCOTT WY | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 15-0086632 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1176628 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 7467 | 20151222 | 741 | 1368982 | 609 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4263 | 38.0998 | -122.8763 | 8 SPANS LD SIDE C/OUTS 7467 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086738 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1176754 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3585 | 20151222 | 1201 | 1369454 | 349 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 6631 | 38.1033 | -122.8632 | 525 VISION | Overcast-32-90 F | Conductor, Overhead | On Ground | 15-0086775 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1176797 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 3583 | 20151222 | 1032 | 1369334 | 462 | Distribution Circuit | Equipment Failure/Involved | Overhead | 96 | 13628 | 38.3745 | -122.4204 | 2 SPANS LOAD SIDE OF 861 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086741 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1176756 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 4967 | 20151222 | 627 | 1368718 | 306 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 8262 | 37.9473 | -122.5609 | 90 IDLEWOOD RD. | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | On Ground | 15-0086654 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1176651 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 2693 | 20151222 | 1012 | 1369327 | 486 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3402 | 37.973 | -122.6075 | 781 BOLINAS AVE. | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086762 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1176780 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | STAFFORD-1102 | 43201102 | FUSE | 1943 | 20151222 | 317 | 1368590 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 37522 | 38.097 | -122.588 | 501 CANYON RD | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 15-0086658 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1176655 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | WOODACRE-1101 | 43021101 | FUSE | 5639 | 20151222 | 740 | 1368979 | 798 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 4788 | 38.0766 | -122.6744 | 1650 RANCHARIA | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086765 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1176783 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 5839 | 20151222 | 544 | 1368819 | 2543 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 25430 | 38.013 | -122.6796 | 46 JUNIPER | Overcast-Fog-Drizzle-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 15-0086790 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1176812 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 2659 | 20151222 | 6 | 1368367 | 1167 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 28046 | 37.9902 | -122.5961 | 220 SCENIC | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086563 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1176557 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 3603 | 20151222 | 510 | 1368769 | 470 | Distribution Circuit | Equipment Failure/Involved | Overhead | 48 | 22560 | 38.0103 | -122.6399 | VENZON- FERNANDO: high wind | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086700 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1176704 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 1023 | 20151226 | 901 | 1372005 | 460 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 1840 | 38.6736 | -122.5746 | 3 SPANS LINE SIDE OF FUCO 2911 | Clear-32-90 F | Conductor, Overhead | On Ground | 15-0087420 | OH | Sus | 42597860 | No | 2015 | DEC | Yes | Line to Line | 1177500 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | OTHER | 7603 | 20151226 | 856 | 1371984 | 899 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 4718 | 38.4834 | -122.2408 | 1987 CAPELL VALLEY RD- NAPA | Clear-32-90 F | Conductor, Overhead | On Ground | 15-0087419 | OH | Sus | 42597863 | No | 2015 | DEC | Yes | Line to Ground | 1177499 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1101 | 42011101 | JUMPER | TAP LINE TO 112 COURTRIGHT | 20151228 | 707 | 1373168 | 518 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2590 | 37.9632 | -122.5287 | 112 COURTRIGHT RD- SAN RAFAEL | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087614 | OH | Sus | 31208975 | No | 2015 | DEC | Yes | None | 1177705 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | FUSE | 2147 | 20151230 | 1400 | 1374840 | 292 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 18396 | 37.906 | -122.552 | 37 CASCADE WAY | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087866 | OH | Sus | 31209508 | No | 2015 | DEC | Yes | Line to Ground | 1178163 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | BOLINAS-1101 | 42261101 | OTHER | WIRE DOWN BET 95983 & 88665 | 20151230 | 937 | 1374637 | 433 | Distribution Circuit | Equipment Failure/Involved | Overhead | 821 | 107501 | 37.9095 | -122.6498 | Hlebakos/431: between C/Os 95983 & 88665 | Partly Cloudy-Fog-Drizzle-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0087837 | OH | Sus | 42599140 | No | 2015 | DEC | Yes | Open Circuit | 1178111 | CSO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | OTHER | WIRE DOWN 1 SPAN LD SIDE OF FUCO 1247 | 20160104 | 1129 | 1376566 | 388 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 11474 | 37.9728 | -122.6131 | 1 SPAN LD SIDE OF FUCO 1247 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0002721 | OH | Sus | 42600566 | No | 2016 | JAN | Yes | None | 1178582 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | STAFFORD-1102 | 43201102 | OCB | 1102/2 | 20160105 | 1224 | 1377335 | 269 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5116 | 384136 | 38.12 | -122.6139 | 1 span ld side of lr 42542 | Partly Cloudy-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0003033 | OH | Sus | 31210539 | yes | 2016 | JAN | Yes | Line to Ground | 1178753 | CSO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | IGNACIO-1104 | 42481104 | FUSE | 2447 | 20160106 | 234 | 1377952 | 491 | Distribution Circuit | Vegetation | Tree - branch fell on line | 80 | 13144 | 38.1151 | -122.5136 | CREST RD & SCHOOL RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003256 | OH | Sus | 42601532 | yes | 2016 | JAN | Yes | Line to Ground | 1178874 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 7467 | 20160113 | 924 | 1382733 | 641 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4487 | 38.0998 | -122.8763 | 980 VISION RD- INVERNESS | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0005057 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1180308 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | WOODACRE-1101 | 43021101 | RECLOSER | 96844 | 20160114 | 2211 | 1384244 | 499 | Distribution Circuit | Equipment Failure/Involved | Overhead | 265 | 24715 | 38.0192 | -122.6631 | 1 SPAN LD SIDE OF LR 96844 | Overcast-Fog-32-90 F | Anchor or Guy | Broken, wire on ground | 16-0005492 | OH | Sus | 0 | No | 2016 | JAN | Yes | Line to Ground | 1180575 | ANC | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 7467 | 20160116 | 2133 | 1385277 | 1097 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 7679 | 38.0998 | -122.8763 | 8 SPANS LOAD SIDE OF 7467 (1000 VISION RD) | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0005854 | OH | Sus | 31213401 | No | 2016 | JAN | Yes | Line to Line | 1180822 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER | 726 | 20160117 | 1225 | 1385482 | 458 | Distribution Circuit | Equipment Failure/Involved | Overhead | 345 | 146420 | 38.6151 | -122.4295 | 7165 OLD POPE VALLEY RD- POPE VALLEY | Overcast-Fog-32-90 F | Insulator | Broken, wire on ground | 16-0005895 | OH | Sus | 42612964 | yes | 2016 | JAN | Yes | Line to Ground | 1180866 | INS | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 2761 | 20160119 | 831 | 1387013 | 629 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 10064 | 38.0672 | -122.7264 | 1 SPAN PAST FUCO 2761 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006216 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1181296 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 4967 | 20160119 | 1444 | 1387813 | 396 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 10692 | 37.9473 | -122.5609 | 60 IDLEWOOD ROAD- KENTFIELD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 16-0006523 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1181362 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SAUSALITO-1102 | 42491102 | FUSE | 1453 | 20160129 | 1451 | 1394131 | 780 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 6919 | 37.8306 | -122.5258 | 2 SPANS LD SIDE OF MTR# 1009126501 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009208 | OH | Sus | 31215827 | No | 2016 | JAN | Yes | Line to Ground | 1183294 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 1235 | 20160211 | 209 | 1401689 | 586 | Distribution Circuit | 3rd Party | Vehicle | 1 | 586 | 38.5524 | -122.4558 | 1 POLE LD SIDE OF FUCO 1235 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0011942 | OH | Sus | 0 | No | 2016 | FEB | Yes | Line to Ground | 1185353 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | STAFFORD-1102 | 43201102 | JUMPER | WIRE DOWN LD SIDE 3600 NOVATO BLVD | 20160220 | 1838 | 1409880 | 1140 | Distribution Circuit | Animal | Bird found | 55 | 6098 | 38.1156 | -122.6518 | 3600 NOVATO BLVD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0014517 | OH | Sus | 42634260 | No | 2016 | FEB | Yes | Line to Ground | 1187310 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 473 | 20160226 | 1543 | 1412732 | 599 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 8386 | 38.6737 | -122.5872 | HUNKINS- DARIN: approx 1/4 mile past 473 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0015927 | OH | Sus | 42641878 | No | 2016 | FEB | Yes | Multi-Fault | 1188304 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 4473 | 20160228 | 1814 | 1413376 | 1059 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 14877 | 38.5577 | -122.4547 | 534 LA TIERRA DR. | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on object | 16-0016114 | OH | Sus | 0 | No | 2016 | FEB | Yes | Line to Ground | 1188490 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | RECLOSER | 311 | 20160304 | 1658 | 1416029 | 1183 | Distribution Circuit | Vegetation | Tree - fell into line | 116 | 25408 | 38.0111 | -122.7023 | AT SW 333- TAYLOR PARK RD (ON RR RIGHT OF WAY OFF SF DRAKE BLVD- JEWELL) | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0017319 | OH | Sus | 31223131 | No | 2016 | MAR | Yes | Three Phase Fault | 1189224 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | FUSE | 6873 | 20160306 | 728 | 1421337 | 387 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 9288 | 37.9149 | -122.5579 | 4 SPANS LD SIDE OF 6873 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018444 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190280 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | BOLINAS-1101 | 42261101 | FUSE | 88665 | 20160306 | 2253 | 1422878 | 157 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 157 | 37.9094 | -122.6494 |  | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018608 | OH | Sus | 0 | yes | 2016 | MAR | Yes | None | 1190451 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE | 6143 | 20160306 | 800 | 1421419 | 1086 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 8134 | 38.5489 | -122.531 | BOOTHE STATE PARK 3200` W/O HWY. 29 (W/E VG) ST.HELENA | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018528 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190366 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1147 | 20160306 | 53 | 1420858 | 938 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5628 | 38.089 | -122.8428 | 1 SPAN LD SIDE 1147 | Overcast-Drizzle-32-90 F | Conductor, Overhead | On Ground | 16-0018091 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1189963 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 7467 | 20160306 | 855 | 1421589 | 1676 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 11732 | 38.0998 | -122.8763 | 10 SPANS LOAD SIDE OF 7467 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0018540 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190378 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1579 | 20160306 | 1919 | 1422652 | 1409 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 16908 | 38.0924 | -122.8586 | 4TH POLE LOAD SIDE OF FUCO 1579 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018566 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190407 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1145 | 20160306 | 1019 | 1421854 | 1691 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 26173 | 38.3344 | -122.373 | 1201 MT VEEDER RD. | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018466 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190304 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE | 9193 | 20160307 | 7 | 1422915 | 713 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 3115 | 38.5646 | -122.5585 | 4281 SCOTT WAY- CALISTOGA | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018640 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190485 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 311 | 20160307 | 121 | 1422985 | 861 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 8930 | 38.0439 | -122.7468 | 2 SPAN FROM SW 333 TWD 3357 | Overcast-Drizzle-32-90 F | Conductor, Overhead | On Ground | 16-0018630 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190476 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SILVERADO-2102 | 43432102 | RECLOSER | 714 | 20160308 | 333 | 1424837 | 775 | Distribution Circuit | Vegetation | Tree - fell into line | 700 | 99439 | 38.5063 | -122.4411 | 2 SPANS S/E OF 4335 per line item time 0614 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0019130 | OH | Sus | 42648209 | yes | 2016 | MAR | Yes | Multi-Fault | 1190901 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 7153 | 20160310 | 1346 | 1426720 | 750 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 9954 | 38.1231 | -122.8838 | 450 SHALLOW BCH | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020054 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1191579 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 2167 | 20160311 | 708 | 1427115 | 614 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 9723 | 37.9009 | -122.5499 | JENSEN- WILLIAM: 109 ON TAP at CORNER3 SPANS FROM INTERSECTION OF MOLINO & FLORENCE AVENUE ON TA | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020206 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1191726 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | ALTO-1125 | 42031125 | FUSE | 5189 | 20160311 | 727 | 1427127 | 389 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 6613 | 37.8783 | -122.5367 | 2 SPANS LOAD SIDE OF 5189 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020218 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1191736 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1683 | 20160311 | 1533 | 1428257 | 522 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2610 | 38.0723 | -122.8413 | 2 SPANS LD SIDE OF 1683 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020568 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1191945 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | SWITCH | 507 | 20160312 | 1414 | 1429577 | 967 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 24175 | 38.3839 | -122.4021 | GREER- JEFF: 5700 Dry creek rd | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0020803 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192184 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | CALISTOGA-1101 | 42711101 | FUSE | 773 | 20160313 | 801 | 1429895 | 602 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 15652 | 38.5992 | -122.6196 | 1200 BENNET LANE- CALISTOGA | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020887 | OH | Sus | 42655851 | yes | 2016 | MAR | Yes | Line to Line | 1192275 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE | 2683 | 20160313 | 1858 | 1430570 | 705 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4230 | 38.5641 | -122.5621 | BEYOND 4449 SAINT HELENA HWY CALISTOGA | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021046 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1192414 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | OTHER | WIRE DOWN @ 18555 HWY 1 | 20160313 | 1015 | 1430075 | 71 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 2500 | 38.1434 | -122.8789 | 18555 HWY 1 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 16-0020796 | OH | Sus | 31224618 | yes | 2016 | MAR | Yes | Line to Ground | 1192292 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | WOODACRE-1101 | 43021101 | RECLOSER | 91900 | 20160326 | 2353 | 1439261 | 404 | Distribution Circuit | Vegetation | Tree - fell into line | 113 | 19672 | 38.0551 | -122.6933 | 5500 NICASIO VALLEY ROAD | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0024217 | OH | Sus | 42663585 | No | 2016 | MAR | Yes | Line to Ground | 1194775 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 757 | 20160327 | 2058 | 1439532 | 617 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 16557 | 38.073 | -122.8278 | 145 LAUREL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0024289 | OH | Sus | 0 | No | 2016 | MAR | Yes | Line to Line | 1194858 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | FUSE | 4595 | 20160328 | 421 | 1439554 | 467 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 12979 | 37.9155 | -122.5577 | 67 MYRTLE | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0024297 | OH | Sus | 42663656 | yes | 2016 | MAR | Yes | Line to Ground | 1194866 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 2395 | 20160414 | 1614 | 1450882 | 559 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 8134 | 37.8943 | -122.557 | SEQOUIA VLY RD 3 POLES W/O EDGEWOOD MILL VALLEY | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0028732 | OH | Sus | 42679201 | No | 2016 | APR | Yes | Line to Ground | 1198013 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE | 2683 | 20160422 | 858 | 1455561 | 357 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1407 | 38.5641 | -122.5621 | 1 SPAN LD SIDE OF FUCO 609 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 16-0030539 | OH | Sus | 0 | yes | 2016 | APR | Yes | Line to Line | 1199325 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | OTHER | WIRE DOWN 4 SP LD SIDE OF 427 | 20160423 | 320 | 1456509 | 1165 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 10207 | 38.602 | -122.4411 | 4 SPAN LD SIDE OF FUCO 427 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0030890 | OH | Sus | 0 | No | 2016 | APR | Yes | Line to Ground | 1199550 | PW | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5469 | 20160424 | 1554 | 1457167 | 668 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 45424 | 38.0646 | -122.8251 | 14 DRAKES SUMMIT RD | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 16-0031045 | OH | Sus | 31233854 | yes | 2016 | APR | Yes | Line to Line | 1199722 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 605 | 20160424 | 1702 | 1457247 | 768 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 6996 | 38.1106 | -122.8716 | 555 VIA DE LA VISTA | Clear-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 16-0031056 | OH | Sus | 31233982 | yes | 2016 | APR | Yes | Line to Ground | 1199733 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | OTHER | WIRE DOWN 1 N/O MTR 1005143256 | 20160428 | 1514 | 1461070 | 620 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 3587 | 38.5639 | -122.5516 | 1 N/O MTR 1005143256 (4325 AZALEA SPRINGS WAY) | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0032488 | OH | Sus | 42687038 | No | 2016 | APR | Yes | Line to Ground | 1200814 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3261 | 20160429 | 1851 | 1461815 | 556 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3336 | 38.0735 | -122.8282 | 4 SPANS LOAD SIDE OF 3261 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0032756 | OH | Sus | 31235532 | yes | 2016 | APR | Yes | Line to Line | 1201018 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | RECLOSER | 37384 | 20160430 | 316 | 1461908 | 949 | Distribution Circuit | Vegetation | Tree - branch fell on line | 416 | 394784 | 38.4453 | -122.1966 | 2SP SS OF SBCO 8393 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0032793 | OH | Sus | 42687881 | yes | 2016 | APR | Yes | Multi-Fault | 1201058 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 7103 | 20160502 | 1418 | 1463373 | 550 | Distribution Circuit | 3rd Party | Vehicle | 3 | 1650 | 38.0136 | -122.6425 | 4260 Sir Francis Drake Blvd- Woodacre- California 94973 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0033281 | OH | Sus | 0 | No | 2016 | MAY | Yes | Line to Ground | 1201517 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 415 | 20160509 | 338 | 1466856 | 542 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 6504 | 38.5568 | -122.4932 | 801 N FORK CRYSTAL SPRINGS RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0034772 | OH | Sus | 42692387 | No | 2016 | MAY | Yes | Line to Line | 1202626 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | STAFFORD-1102 | 43201102 | FUSE | 4241 | 20160514 | 602 | 1469575 | 413 | Distribution Circuit | Animal | Bird found | 16 | 6608 | 38.1018 | -122.6296 | 10 MEADOW LANE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0036003 | OH | Sus | 42700730 | No | 2016 | MAY | Yes | Line to Ground | 1203424 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 9291 | 20160521 | 2040 | 1474566 | 1130 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 73450 | 38.5839 | -122.6709 | Bock/2425: one span from 9291 | Clear-32-90 F | Conductor, Overhead | On Ground | 16-0037640 | OH | Sus | 0 | No | 2016 | MAY | Yes | Line to Line | 1204693 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | WOODACRE-1102 | 43021102 | RECLOSER | 1280 | 20160524 | 544 | 1475640 | 343 | Distribution Circuit | Equipment Failure/Involved | Overhead | 933 | 80065 | 37.9962 | -122.5956 | 26 MARTLING DR. | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0037945 | OH | Sus | 31241827 | No | 2016 | MAY | Yes | Line to Line | 1204959 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | IGNACIO-1104 | 42481104 | FUSE | 2447 | 20160525 | 1158 | 1476484 | 283 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 79 | 22357 | 38.1151 | -122.5136 | 2 SPANS LOAD SIDE OF 2447 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0038362 | OH | Sus | 42706842 | No | 2016 | MAY | Yes | Line to Ground | 1205236 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 6381 | 20160601 | 1730 | 1481004 | 1181 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2362 | 38.5768 | -122.6205 | 170 PETRIFIED FOREST RD | Clear-32-90 F | Conductor, Overhead | On Ground | 16-0040347 | OH | Sus | 31243562 | yes | 2016 | JUN | Yes | Line to Line | 1206784 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-2103 | 43292103 | OTHER | 3SP LD SIDE OF LR 678 | 20160606 | 645 | 1483658 | 402 | Distribution Circuit | Vegetation | Tree - fell into line | 344 | 46180 | 38.3162 | -122.3432 | 3SP LD SIDE OF LR 678 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0041237 | OH | Sus | 31245789 | No | 2016 | JUN | Yes | Line to Ground | 1207518 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | SAN RAFAEL-1109 | 42011109 | FUSE | 2495 | 20160607 | 718 | 1484407 | 791 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 4908 | 37.9772 | -122.5059 | IRO 80 FAIRWAY DR. SAN RAFAEL | Overcast-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0041569 | OH | Sus | 0 | No | 2016 | JUN | Yes | Line to Line | 1207740 | CAW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | OTHER | WIRE DOWN 7 SPANS LOAD SIDE OF 9193 | 20160626 | 1503 | 1496142 | 677 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 3 | 2031 | 38.5627 | -122.5508 | 4319 AZALEA SPRINGS WAY | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 16-0045859 | OH | Sus | 42731593 | No | 2016 | JUN | Yes | Line to Ground | 1210943 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | CALISTOGA-1101 | 42711101 | OCB | 1101/2 | 20160628 | 1657 | 1497805 | 784 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 1676 | 341756 | 38.5924 | -122.5786 | 1299 TUBBS LANE | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 16-0046424 | OH | Sus | 0 | yes | 2016 | JUN | Yes | Line to Line | 1211356 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | RECLOSER | 734 | 20160701 | 1607 | 1499723 | 499 | Distribution Circuit | Vegetation | Tree - fell into line | 362 | 112390 | 38.5894 | -122.6078 | GREENE- JOSEPH: Foss Hill rd 2 spans line side of 87347 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0047463 | OH | Sus | 31250692 | yes | 2016 | JUL | Yes | Line to Ground | 1212015 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE | 2659 | 20160708 | 1049 | 1502825 | 941 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 19469 | 38.3373 | -122.1211 | 2 SPANS N/OF 2659 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0048647 | OH | Sus | 0 | No | 2016 | JUL | Yes | Line to Ground | 1212927 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1147 | 20160714 | 2029 | 1510272 | 566 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3396 | 38.089 | -122.8428 | 2/W/OF 1147 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0050032 | OH | Sus | 31257416 | yes | 2016 | JUL | Yes | Line to Ground | 1213936 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | FUSE | 5155 | 20160715 | 2026 | 1510938 | 1324 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 10 | 13240 | 38.4944 | -122.4944 | 3042 SULPHUR SPRING ROAD- ST HELENA | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0050320 | OH | Sus | 0 | No | 2016 | JUL | Yes | Open Circuit | 1214126 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 7467 | 20160719 | 1831 | 1512720 | 658 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4606 | 38.0998 | -122.8763 | 3W/of 1000 Vision Rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0051039 | OH | Sus | 31258116 | No | 2016 | JUL | Yes | Line to Line | 1214679 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | RECLOSER | 736-G | 20160729 | 1816 | 1518698 | 507 | Distribution Circuit | Vegetation | Tree - fell into line | 406 | 177834 | 38.5803 | -122.5979 | 159 PETRIFIED FOREST ROAD. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0053726 | OH | Sus | 31260423 | No | 2016 | JUL | Yes | Line to Ground | 1216455 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-1104 | 43291104 | FUSE | 1091 | 20160821 | 1302 | 1529743 | 852 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 15 | 12780 | 38.4411 | -122.2464 | Donahue/439: 4500 atles peak rd | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 16-0058847 | OH | Sus | 31264574 | No | 2016 | AUG | Yes | Line to Line | 1219918 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | OTHER | WIRE DOWN @ 2987 | 20160825 | 1158 | 1532089 | 937 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 530 | 393470 | 38.6134 | -122.4283 | HOWELL MT RD. 800' S/O POPE VALLEY STORE ST HELENA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0059980 | OH | Sus | 42775861 | No | 2016 | AUG | Yes | Line to Ground | 1220666 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 7467 | 20160902 | 2223 | 1536150 | 787 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5509 | 38.0998 | -122.8763 | 1000 VISION RD. | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0062190 | OH | Sus | 31269026 | No | 2016 | SEP | Yes | Line to Line | 1222132 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 605 | 20160910 | 1827 | 1539406 | 1343 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 64502 | 38.1106 | -122.8716 | JENSEN- WILLIAM: 300 via de la vista | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0063727 | OH | Sus | 31270735 | No | 2016 | SEP | Yes | Line to Line | 1223124 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | MIDDLETOWN-1101 | 43141101 | FUSE | 1023 | 20160919 | 1531 | 1544251 | 1315 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5260 | 38.6736 | -122.5746 | 2 SPAN S OF 1023 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 16-0065772 | OH | Sus | 0 | yes | 2016 | SEP | Yes | Line to Ground | 1224538 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SILVERADO-2102 | 43432102 | FUSE | 1601 | 20161006 | 2141 | 1554344 | 468 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 4362 | 38.5077 | -122.4067 | 1 span load side of 9151 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0070257 | OH | Sus | 42806355 | No | 2016 | OCT | Yes | Line to Ground | 1227856 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2102 | 43432102 | RECLOSER | 34959 | 20161015 | 32 | 1560542 | 1818 | Distribution Circuit | Equipment Failure/Involved | Overhead | 173 | 314514 | 38.508 | -122.3749 | LD side of REG 8365 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072402 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Line | 1229464 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SILVERADO-2102 | 43432102 | OTHER | WIRE DOWN @ 99 POPE ST | 20161019 | 1042 | 1565916 | 693 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 693 | 38.5105 | -122.4523 | 99 POPE ST. SAINT HELENA- CA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0073955 | OH | Sus | 42820761 | No | 2016 | OCT | Yes | Open Circuit | 1230800 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | JUMPER | O/J 1/S OF 540 MUND RD | 20161022 | 556 | 1567405 | 553 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 8848 | 38.5334 | -122.4698 | 2/S OF 540 MUND RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0074734 | OH | Sus | 31279572 | No | 2016 | OCT | Yes | Line to Ground | 1231344 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 3343 | 20161025 | 449 | 1569216 | 450 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 10156 | 38.3614 | -122.3713 | 18 POLES N/OF FUCO 2021 | Clear-32-90 F | Conductor, Overhead | On Ground | 16-0075235 | OH | Sus | 31280236 | No | 2016 | OCT | Yes | Line to Line | 1231808 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | RECLOSER | 634 | 20161028 | 903 | 1571647 | 717 | Distribution Circuit | 3rd Party | Vehicle | 457 | 32293 | 38.5859 | -122.5715 | BOCK- MIKE 707-695-8997 #1484: south of 4292 SILVERADO TRL | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0076288 | OH | Sus | 31281047 | yes | 2016 | OCT | Yes | Line to Line | 1232544 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | RECLOSER | 1210 | 20161029 | 1153 | 1572626 | 86 | Distribution Circuit | Vegetation | Tree - fell into line | 545 | 46786 | 37.9627 | -122.569 | 1 SPAN N/O 45619 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076657 | OH | Sus | 31281224 | No | 2016 | OCT | Yes | Line to Ground | 1232760 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2103 | 43432103 | FUSE | 3721 | 20161029 | 848 | 1572479 | 1392 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 7317 | 38.4639 | -122.4624 | RUPP- DONOVAN: 5/S down stream of SBCO 7479 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076641 | OH | Sus | 42869522 | No | 2016 | OCT | Yes | Line to Ground | 1232745 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 141 | 20161029 | 2215 | 1572894 | 765 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1910 | 38.5785 | -122.4424 | 229 HOWELL MOUNTAIN RD | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076722 | OH | Sus | 0 | No | 2016 | OCT | Yes | Line to Line | 1232827 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 3125 | 20161030 | 1604 | 1573362 | 2113 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 29582 | 38.3964 | -122.4494 | 5 SPANS LOAD SIDE OF 3125 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 16-0076828 | OH | Sus | 0 | No | 2016 | OCT | Yes | Line to Line | 1232929 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2102 | 43432102 | RECLOSER | 34959 | 20161101 | 1804 | 1574949 | 787 | Distribution Circuit | Equipment Failure/Involved | Overhead | 173 | 136151 | 38.508 | -122.3749 | WIRE DOWN 1 SPAN FROM LR-34959 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0077363 | OH | Sus | 42871290 | No | 2016 | NOV | Yes | Line to Ground | 1233367 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | JUMPER | WIRE DOWN 1 PHASE LD SIDE OF FUCO-7505 | 20161111 | 839 | 1579676 | 481 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 2 | 962 | 38.4927 | -122.5145 | wire down 1 phase 1 span LD side of FUCO-7505 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0079347 | OH | Sus | 42879043 | No | 2016 | NOV | Yes | None | 1234821 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1104 | 42011104 | OTHER | WIRE DOWN MTR# 1008086276 | 20161119 | 1528 | 1585229 | 623 | Distribution Circuit | Equipment Failure/Involved | Overhead | 48 | 27708 | 37.9818 | -122.5723 | 72 ALDER BACKYARD | Overcast-Drizzle-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0081148 | OH | Sus | 42882735 | yes | 2016 | NOV | Yes | Line to Ground | 1236167 | CSO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | OTHER | WIRE DOWN 2 SPANS LD SIDE OF 5849 | 20161124 | 730 | 1588146 | 531 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 4419 | 38.0126 | -122.6982 | 2 SPANS LD SIDE OF 5849 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0082103 | OH | Sus | 42884189 | No | 2016 | NOV | Yes | Line to Ground | 1236861 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 2685 | 20161126 | 329 | 1588898 | 628 | Distribution Circuit | Vegetation | Tree - branch fell on line | 149 | 93572 | 37.9786 | -122.5984 | 3 SPANS LD SIDE OF 2685 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0082242 | OH | Sus | 42884781 | yes | 2016 | NOV | Yes | Line to Ground | 1237003 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE | 2683 | 20161210 | 726 | 1598311 | 726 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4356 | 38.5641 | -122.5621 | 3 SPANS S/OF 609 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084918 | OH | Sus | 42894399 | yes | 2016 | DEC | Yes | Line to Ground | 1239462 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SAN RAFAEL-1109 | 42011109 | FUSE | 6997 | 20161212 | 1817 | 1600634 | 1343 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 6804 | 37.9789 | -122.508 | 340 HIGHLAND | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0085280 | OH | Sus | 0 | No | 2016 | DEC | Yes | Line to Line | 1239875 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1122 | 42031122 | FUSE | 2347 | 20161215 | 1530 | 1603004 | 961 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 78802 | 37.9209 | -122.527 | 399 chapman Dr corte madera 2 spans loadside of fuses 2347 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085783 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Three Phase Fault | 1240452 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 3499 | 20161215 | 240 | 1602238 | 825 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 5535 | 37.8999 | -122.5628 | PINTANE- BRANDON: 80 monte cimas Ave. mill valley | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085643 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1240300 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | ALTO-1125 | 42031125 | FUSE | 5189 | 20161215 | 311 | 1602248 | 672 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 11424 | 37.8783 | -122.5367 | JENSEN- WILLIAM: 454 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085646 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1240307 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 2155 | 20161215 | 1640 | 1602995 | 1078 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 15092 | 37.9001 | -122.5584 | 25 CASTLE ROCK DR. | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085805 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Line | 1240473 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER | 1252 | 20161215 | 239 | 1602239 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 126 | 64436 | 38.0779 | -122.8329 | DOYLE- TRAVIS: drakes veiw rd | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085634 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1240290 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SAN RAFAEL-1104 | 42011104 | FUSE | 2653 | 20161215 | 838 | 1602417 | 230 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 3220 | 38.0002 | -122.5781 | DOYLE- TRAVIS: 41 oak knoll | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085670 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1240346 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | OTHER | WIRE DOWN1 POLE S/W 3297 | 20161215 | 2134 | 1603785 | 1251 | Distribution Circuit | Vegetation | Tree - fell into line | 672 | 367562 | 37.9745 | -122.5665 | 1 POLE S/W OF 3297 | Partly Cloudy-Fog-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085900 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1240565 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 7449 | 20161215 | 1345 | 1602806 | 445 | Distribution Circuit | Vegetation | Tree - fell into line | 228 | 30294 | 38.0076 | -122.6447 | 1 SS OF 2931 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 16-0085750 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1240420 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | FUSE | 2151 | 20161216 | 213 | 1604071 | 792 | Distribution Circuit | Vegetation | Tree - branch fell on line | 118 | 93456 | 37.9115 | -122.5486 | 144 W00DBINE DR. & 150 ELDRIDGE | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085955 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Line | 1240622 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 3583 | 20170104 | 27 | 1617372 | 1048 | Distribution Circuit | Equipment Failure/Involved | Overhead | 93 | 57320 | 38.3745 | -122.4204 | E/of 3125 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003402 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243588 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | OCB | 1101/2 | 20170107 | 1618 | 1622006 | 1358 | Distribution Circuit | Vegetation | Tree - fell into line | 1214 | 167284 | 38.0125 | -122.654 | 6900 NICASIO VALLEY | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0004745 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244552 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | FUSE | 5439 | 20170112 | 624 | 1640991 | 776 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3880 | 38.5279 | -122.5574 | E/O PVT RD OFF OF SPRING MTN | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008331 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247755 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 5935 | 20170112 | 442 | 1640949 | 408 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4896 | 38.0062 | -122.6418 | 1 SPANS LOAD SIDE OF 5935 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008281 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1247721 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 6381 | 20170114 | 1223 | 1643424 | 787 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1574 | 38.5768 | -122.6205 | 1/N OF 6381 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0009130 | OH | Sus | 31296504 | No | 2017 | JAN | Yes | Line to Ground | 1248397 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE | 7603 | 20170116 | 756 | 1644336 | 1026 | Distribution Circuit | 3rd Party | Vehicle | 10 | 10260 | 38.4834 | -122.2408 | Line & buck 4-5 spans N/of FUCO-7603 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0009364 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Line | 1248628 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 805 | 20170124 | 1446 | 1665775 | 11 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 385 | 38.5526 | -122.6052 | HEIDE RD 1/E/OF FUCO 3807 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0014444 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1253139 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 186957 | 20170202 | 1935 | 1673339 | 547 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1094 | 38.0343 | -122.6759 | 1355 NICASIO VALLEY RD- NICASIO | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017039 | OH | Sus | 0 | No | 2017 | FEB | Yes | Line to Line | 1255131 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | SECTIONALIZER | 6053 | 20170203 | 30 | 1673421 | 773 | Distribution Circuit | Vegetation | Tree - fell into line | 742 | 124008 | 38.0957 | -122.8511 | 1 SOURCE SIDE OF 1739 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017065 | OH | Sus | 31303495 | yes | 2017 | FEB | Yes | Line to Line | 1255159 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 2627 | 20170203 | 627 | 1673523 | 434 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 14865 | 38.0122 | -122.702 | Centura Ave N/of 1/2 span N/of FUCO-5857 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017093 | OH | Sus | 31303550 | yes | 2017 | FEB | Yes | Line to Line | 1255183 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE | 1589 | 20170204 | 1336 | 1674879 | 553 | Distribution Circuit | Equipment Failure/Involved | Overhead | 175 | 23925 | 38.4069 | -122.2056 | 317 CIRCLE OAKS | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017464 | OH | Sus | 42939086 | No | 2017 | FEB | Yes | Line to Ground | 1255437 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 3149 | 20170204 | 129 | 1674548 | 1367 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 32808 | 38.5367 | -122.4638 | RUPP- DONOVAN: END OF MUND LN | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0017412 | OH | Sus | 42939009 | No | 2017 | FEB | Yes | Line to Line | 1255373 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3393 | 20170205 | 2145 | 1675644 | 5566 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 83490 | 38.1297 | -122.899 | 11 P/E/OF 3393 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017615 | OH | Sus | 0 | No | 2017 | FEB | Yes | Line to Ground | 1255580 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 4965 | 20170205 | 2247 | 1675749 | 1013 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 6232 | 37.9461 | -122.5564 | 6 SPANS LOAD SIDE | Overcast-Fog-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017642 | OH | Sus | 42939190 | No | 2017 | FEB | Yes | Line to Ground | 1255606 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 6323 | 20170205 | 2221 | 1675668 | 377 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 19227 | 37.9749 | -122.5686 | 93 HILLSIDE | Overcast-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0017628 | OH | Sus | 42939187 | No | 2017 | FEB | Yes | Line to Ground | 1255593 | CSO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER | 75686 | 20170206 | 55 | 1675796 | 683 | Distribution Circuit | Vegetation | Tree - branch fell on line | 129 | 31778 | 38.0487 | -122.7435 | Hlebakos/1277: 5600 Nicasio Valley Rd | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017650 | OH | Sus | 42939194 | yes | 2017 | FEB | Yes | Line to Ground | 1255614 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | FUSE | 427 | 20170208 | 523 | 1681313 | 851 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 7659 | 38.6015 | -122.4407 | BOCK- MIKE 707-695-8997 #1484: 2 spans from 427 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018870 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Force Out | 1256609 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | WOODACRE-1101 | 43021101 | RECLOSER | 96844 | 20170208 | 1455 | 1682173 | 1733 | Distribution Circuit | Vegetation | Tree - fell into line | 177 | 132477 | 38.0192 | -122.6631 | SPANS SOURCE SIDE OF FUCO-673545 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019096 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1256715 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | WOODACRE-1102 | 43021102 | SWITCH | 2145 | 20170208 | 1240 | 1681844 | 1416 | Distribution Circuit | Vegetation | Tree - fell into line | 599 | 105684 | 38.0059 | -122.5856 | 117 Legend | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019017 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Force Out | 1256678 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | LAS GALLINAS A-1106 | 42991106 | FUSE | 3221 | 20170210 | 1036 | 1684931 | 493 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2465 | 38.0406 | -122.6056 | 2500 LUCAS VLY RD- 60 KV CROSSING- SAN RAFAEL | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019875 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1257300 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2102 | 43292102 | FUSE | 3121 | 20170210 | 1336 | 1685232 | 222 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 21534 | 38.4078 | -122.4298 | 1 SPAN NORTH OF FUCO 675827 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019972 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1257358 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SAN RAFAEL-1107 | 42011107 | FUSE | 2821 | 20170210 | 900 | 1684757 | 721 | Distribution Circuit | Equipment Failure/Involved | Overhead | 463 | 36568 | 37.946 | -122.5461 | 2 SPANS WIRE DOWN FERN AND MURRAY | Heavy Rain-Strong Winds-Combination-Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019845 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1257286 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SILVERADO-2104 | 43432104 | FUSE | 95817 | 20170212 | 1545 | 1686967 | 588 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 588 | 38.6897 | -122.3717 | 2 SPANS LD SIDE OF 95817 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0020489 | OH | Sus | 0 | No | 2017 | FEB | Yes | Line to Ground | 1257857 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2102 | 43292102 | FUSE | 3121 | 20170214 | 1219 | 1688429 | 859 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 37387 | 38.4078 | -122.4298 | GREENE- JOSEPH: 4900 Drycreek rd. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021033 | OH | Sus | 42948902 | No | 2017 | FEB | Yes | Line to Ground | 1258318 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER | 806 | 20170215 | 1728 | 1689547 | 569 | Distribution Circuit | Equipment Failure/Involved | Overhead | 143 | 25751 | 38.6169 | -122.4244 | 4128 CHILES & POPE VALLEY VALLEY RD. | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021388 | OH | Sus | 31306135 | No | 2017 | FEB | Yes | Line to Ground | 1258589 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | FUSE | 4065 | 20170216 | 321 | 1689869 | 773 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5411 | 38.5203 | -122.5276 | 2 SPANS NORTH OF 3551 MAINTREE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021465 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1258675 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE | 65047 | 20170301 | 1541 | 1716945 | 654 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1308 | 38.4085 | -122.2055 | 4831 MONTICELLO RD- NAPA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0027696 | OH | Sus | 42956429 | No | 2017 | MAR | Yes | Line to Line | 1264193 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 4535 | 20170308 | 924 | 1722363 | 431 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3448 | 38.007 | -122.6989 | Hlebakos/1277: first span from C/O 4535 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0029346 | OH | Sus | 31311201 | No | 2017 | MAR | Yes | Line to Ground | 1265495 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-1104 | 43291104 | RECLOSER | 1304 | 20170314 | 909 | 1726744 | 967 | Distribution Circuit | Vegetation | Tree - fell into line | 156 | 100761 | 38.3634 | -122.2651 | 2670 ATLAS PEAK RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0030636 | OH | Sus | 0 | No | 2017 | MAR | Yes | Line to Ground | 1266493 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 311 | 20170321 | 1817 | 1732453 | 778 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 9400 | 38.0439 | -122.7468 | 8888 SIR FRANCIS DRAKE BLVD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0032550 | OH | Sus | 42974447 | yes | 2017 | MAR | Yes | Line to Ground | 1267882 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | CALISTOGA-1101 | 42711101 | FUSE | 8339 | 20170323 | 949 | 1733907 | 1095 | Distribution Circuit | Equipment Failure/Involved | Overhead | 76 | 74134 | 38.6327 | -122.6744 | 6/spans/LD side of 8339 | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 17-0033215 | OH | Sus | 42976234 | No | 2017 | MAR | Yes | Line to Ground | 1268308 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE | 1589 | 20170329 | 2317 | 1738775 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 175 | 31250 | 38.4069 | -122.2056 | 335 COUNTRY CLUB LN | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0034895 | OH | Sus | 42979755 | No | 2017 | MAR | Yes | Line to Ground | 1269609 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SAN RAFAEL-1109 | 42011109 | FUSE | 2495 | 20170330 | 844 | 1739019 | 825 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 14850 | 37.9772 | -122.5059 | 3 SPANS LD SIDE OF 2495 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0034981 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Ground | 1269721 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER | 75686 | 20170408 | 916 | 1752483 | 621 | Distribution Circuit | Equipment Failure/Involved | Overhead | 129 | 80004 | 38.0487 | -122.7435 | WIRE DOWN TWDS FUCO 2761 1 ? DOWN. | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038242 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1272302 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 2027 | 20170411 | 1902 | 1755632 | 888 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2664 | 38.3755 | -122.4268 | LD SIDE OF 2027 FUCO | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0039327 | OH | Sus | 31319143 | No | 2017 | APR | Yes | Line to Ground | 1273212 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2102 | 43292102 | FUSE | 3123 | 20170413 | 751 | 1756748 | 471 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 38622 | 38.4069 | -122.4422 | 6500 Dry Creek Rd | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0039884 | OH | Sus | 42993685 | yes | 2017 | APR | Yes | Line to Ground | 1273594 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | FUSE | 7505 | 20170413 | 1100 | 1756950 | 372 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 744 | 38.493 | -122.5153 | BOCK- MIKE 707-695-8997 #1484: last span on tap | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0039989 | OH | Sus | 42993846 | yes | 2017 | APR | Yes | Line to Ground | 1273648 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 3583 | 20170423 | 1440 | 1765392 | 2136 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 55894 | 38.3745 | -122.4204 | 6 SPANS LD SIDE OF 869 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0042225 | OH | Sus | 0 | No | 2017 | APR | Yes | Line to Ground | 1275389 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | BOLINAS-1101 | 42261101 | FUSE | 46819 | 20170426 | 1847 | 1767929 | 543 | Distribution Circuit | 3rd Party | Vehicle | 1 | 543 | 37.9382 | -122.703 | Hlebakos/1277: HWY 1- 730' S/E HORSESHOE HILL RD.- BOLINAS | Partly Cloudy-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0043182 | OH | Sus | 0 | No | 2017 | APR | Yes | Line to Ground | 1275962 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | JUMPER | WIRE DOWN SS OF 902 | 20170427 | 1852 | 1768964 | 100 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1164 | 25637 | 37.8892 | -122.5551 | SS OF LR902 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0043500 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1276184 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-1105 | 43291105 | FUSE | 6379 | 20170427 | 2058 | 1769048 | 1141 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 27855 | 38.4262 | -122.3002 | 3090 Soda Canyon | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0043533 | OH | Sus | 31322276 | yes | 2017 | APR | Yes | Line to Line | 1276214 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | BOLINAS-1101 | 42261101 | SWITCH | 1469 | 20170428 | 1218 | 1769532 | 37 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 666 | 37.8881 | -122.5687 | SS OF 902 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0043500 | OH | Sus | 0 | yes | 2017 | APR | Yes | None | 1276330 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | JUMPER | WIRE DOWN | 20170505 | 1726 | 1775762 | 715 | Distribution Circuit | Vegetation | Tree - branch fell on line | 237 | 134967 | 38.0982 | -122.8591 | 115 FORRES WAY | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0045701 | OH | Sus | 43007980 | No | 2017 | MAY | Yes | Line to Ground | 1277811 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | SAN RAFAEL-1107 | 42011107 | OTHER | 2323 | 20170509 | 2 | 1778209 | 369 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 12205 | 37.9454 | -122.5496 | 42 BRIAR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0046378 | OH | Sus | 43008982 | No | 2017 | MAY | Yes | Line to Ground | 1278436 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2102 | 43292102 | FUSE | 407 | 20170511 | 219 | 1779728 | 603 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 30753 | 38.4095 | -122.4654 | 265 WALL RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0047090 | OH | Sus | 31325160 | No | 2017 | MAY | Yes | Line to Ground | 1278970 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | JUMPER | WIRE DOWN | 20170512 | 1728 | 1781049 | 1764 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 41844 | 38.0344 | -122.7431 | 3107 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0047653 | OH | Sus | 0 | No | 2017 | MAY | Yes | Open Circuit | 1279308 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | SAUSALITO-1101 | 42491101 | FUSE | 5437 | 20170522 | 1619 | 1787943 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 49045 | 37.8452 | -122.4813 | 93 MARION | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0049769 | OH | Sus | 43021586 | yes | 2017 | MAY | Yes | Line to Ground | 1280912 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | ALTO-1120 | 42031120 | FUSE | 941 | 20170609 | 542 | 1800186 | 481 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1924 | 37.8696 | -122.5277 | 3 SPANS LD SIDE OF 941 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0053872 | OH | Sus | 43030604 | No | 2017 | JUN | Yes | Line to Ground | 1283882 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 4535 | 20170626 | 1908 | 1818677 | 387 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3096 | 38.007 | -122.6989 | MNT. VIEW AVE.- & SPRING AVE.-LAGUNITAS | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0058760 | OH | Sus | 43045460 | No | 2017 | JUN | Yes | Line to Ground | 1287794 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | BOLINAS-1101 | 42261101 | RECLOSER | 806 | 20170627 | 923 | 1818982 | 685 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 3920 | 37.9559 | -122.6176 | 2P E/OF LR-806 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0058882 | OH | Sus | 31334205 | No | 2017 | JUN | Yes | Line to Line | 1287935 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1117 | 20170630 | 510 | 1821135 | 520 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 10586 | 38.3727 | -122.417 | SOURCE SIDE OF 7597 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0059675 | OH | Sus | 31334632 | No | 2017 | JUN | Yes | Line to Ground | 1288481 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | ALTO-1120 | 42031120 | RECLOSER | 1214 | 20170703 | 938 | 1822723 | 166 | Distribution Circuit | 3rd Party | Vehicle | 594 | 98604 | 37.8784 | -122.5342 | JENSEN- Bill: 314 marin ave | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0060175 | OH | Sus | 43048248 | No | 2017 | JUL | Yes | Line to Ground | 1288842 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | RECLOSER | 734 | 20170703 | 720 | 1822623 | 580 | Distribution Circuit | Vegetation | Tree - fell into line | 362 | 143996 | 38.5894 | -122.6078 | 2/E/O 87347 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0060147 | OH | Sus | 43048250 | No | 2017 | JUL | Yes | Line to Ground | 1288815 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | BOLINAS-1101 | 42261101 | RECLOSER | 806 | 20170715 | 1029 | 1832092 | 891 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 2221 | 37.9559 | -122.6176 | 3 SPANS LD SIDE OF 806 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0063108 | OH | Sus | 31337236 | No | 2017 | JUL | Yes | Line to Ground | 1290920 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | FUSE | 6927 | 20170725 | 313 | 1839287 | 1227 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 7362 | 38.538 | -122.4864 | PHASE DOWN (FIELD SIDE) at 280 GLASS MOUNTAIN RD ST. HELENA | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0065194 | OH | Sus | 0 | No | 2017 | JUL | Yes | Line to Ground | 1292470 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | JUMPER | WIRE DOWN | 20170814 | 419 | 1851899 | 961 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 2662 | 38.6111 | -122.4543 | 1414 INK GRADE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0070014 | OH | Sus | 31342264 | No | 2017 | AUG | Yes | Force Out | 1295826 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 3343 | 20170822 | 1941 | 1857276 | 515 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 11138 | 38.3614 | -122.3713 | 4880 DRY CREEK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0072149 | OH | Sus | 31344152 | No | 2017 | AUG | Yes | Line to Ground | 1297279 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 1165 | 20170904 | 316 | 1869570 | 854 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2562 | 38.5547 | -122.4725 | LABO- MICHAEL: 1060 DEER PARK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0075772 | OH | Sus | 0 | yes | 2017 | SEP | Yes | Line to Ground | 1300048 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3261 | 20170918 | 1901 | 1881328 | 464 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 2784 | 38.0735 | -122.8282 | 2 SPANS LD SIDE OF FUCO 3261 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0079828 | OH | Sus | 43113421 | No | 2017 | SEP | Yes | Line to Ground | 1303071 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5445 | 20170918 | 1832 | 1881312 | 650 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5200 | 38.0599 | -122.821 | 14 SPANS LD SIDE- BROKE CROSS ARM AND WIRE DOWN | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0079832 | OH | Sus | 31351798 | No | 2017 | SEP | Yes | Line to Ground | 1303074 | CAW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | NAPA-1112 | 42021112 | FUSE | 2701 | 20171010 | 1700 | 1897862 | 10060 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 40240 | 38.3221 | -122.1913 | 3E/ FUCO-2701 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086136 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1307301 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1117 | 20171010 | 2014 | 1901453 | 17156 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 29 | 497524 | 38.3727 | -122.417 | MT VEEDER RD | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087584 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1308561 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 3651 | 20171010 | 1511 | 1898318 | 1355 | Distribution Circuit | Equipment Failure/Involved | Overhead | 99 | 134145 | 38.5379 | -122.4716 | 600' E/OF 3651 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086335 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Line | 1307486 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 4505 | 20171010 | 1615 | 1897824 | 1500 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 25500 | 38.5823 | -122.4592 | LD SIDE OF 4505 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086408 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1307509 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | FUSE | 585 | 20171010 | 1657 | 1897907 | 1434 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 7170 | 38.563 | -122.5456 | 4 SPANS LD SIDE OF FUCO 585 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086152 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1307315 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 683 | 20171011 | 2027 | 1900289 | 4130 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 25 | 103250 | 38.5925 | -122.6118 | HWY 128 W/BENTLEY DRIVE CALISTOGA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087197 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1308186 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | SWITCH | 3573 | 20171011 | 45 | 1898220 | 16885 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 523435 | 38.3656 | -122.407 | 2 N/OF 3573 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086282 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1307446 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-2103 | 43292103 | FUSE | 9295 | 20171011 | 23 | 1898059 | 8299 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 182578 | 38.3136 | -122.3592 | BRANDT- 4179 / 831-212-2088: cust reported seeing tree hit the line behind Fontana winnery | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086365 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1307498 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | CALISTOGA-1101 | 42711101 | OCB | 1101/2 | 20171012 | 858 | 1898937 | 3459 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 839 | 1570947 | 38.5924 | -122.5786 | 3485 OLD TOLL RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086662 | OH | Sus | 0 | No | 2017 | OCT | Yes | Force Out | 1307756 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | RECLOSER | 734 | 20171012 | 858 | 1900159 | 3379 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 44 | 148676 | 38.5894 | -122.6078 | BOCK- MIKE 707-695-8997 #1484: unknown | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087141 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1308143 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 2637 | 20171012 | 858 | 1900263 | 3379 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 1 | 3379 | 38.5908 | -122.6095 | HWY #128 N/O TUBBS LN. CALISTOGA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087180 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1308172 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | NAPA-1112 | 42021112 | FUSE | 349 | 20171012 | 1118 | 1899433 | 8722 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 6 | 51978 | 38.269 | -122.2053 | SB 1573 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086784 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1307843 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | BOLINAS-1101 | 42261101 | OCB | 1101/2 | 20171018 | 1018 | 1903217 | 1202 | Distribution Circuit | Vegetation | Tree - fell into line | 1615 | 388856 | 37.9407 | -122.7071 | 1 SPAN LD SIDE OF LR1064 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0088262 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1309011 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | BOLINAS-1101 | 42261101 | RECLOSER | 504 | 20171019 | 2238 | 1904680 | 1019 | Distribution Circuit | Equipment Failure/Involved | Overhead | 825 | 216655 | 37.9343 | -122.6968 | REGS 3639- 2 SPANS OF WIRE DOWN LINE SIDE | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0088772 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Line | 1309344 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | CALISTOGA-1101 | 42711101 | FUSE | 7623 | 20171022 | 1801 | 1907355 | 1312 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 6560 | 38.6274 | -122.6778 | LOAD SIDE OF 7623 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0089521 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1309980 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SILVERADO-2102 | 43432102 | FUSE | 3531 | 20171107 | 659 | 1917539 | 1151 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2302 | 38.5058 | -122.4072 | 3 SPANS W OF 3531 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0093255 | OH | Sus | 43208340 | No | 2017 | NOV | Yes | Line to Ground | 1312691 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 3149 | 20171118 | 123 | 1925453 | 716 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 17184 | 38.5367 | -122.4638 | 3 spans LD side of FUCO-3149 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0096151 | OH | Sus | 43217240 | No | 2017 | NOV | Yes | Line to Ground | 1314793 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | JUMPER | VERTICAL JUMPERS S/E/OF 4719 | 20171120 | 1741 | 1926857 | 2571 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 7569 | 38.3493 | -122.1583 | FROM MAINLINE TO THE SOUTH TWD MTR# 1006604663 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0096686 | OH | Sus | 31366537 | No | 2017 | NOV | Yes | Line to Ground | 1315241 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1115 | 20171121 | 900 | 1927122 | 1665 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 16650 | 38.3672 | -122.4102 | 1155 LOKOYA RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0096829 | OH | Sus | 43219348 | No | 2017 | NOV | Yes | Line to Ground | 1315328 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2103 | 43432103 | TRIP-SAVER | 3721 | 20171126 | 1259 | 1929401 | 583 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 8162 | 38.4639 | -122.4624 | LABO- MICHAEL: 1780 WHITEHALL LN. - ST HELENA | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0097606 | OH | Sus | 31366973 | No | 2017 | NOV | Yes | Line to Line | 1315831 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | RECLOSER | 736-G | 20171127 | 1546 | 1930516 | 690 | Distribution Circuit | Vegetation | Tree - branch fell on line | 408 | 139957 | 38.5803 | -122.5979 | 5055 MOUNTIAN HOME RANCH RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0097943 | OH | Sus | 31367195 | yes | 2017 | NOV | Yes | Line to Line | 1316103 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SAN RAFAEL-1109 | 42011109 | RECLOSER | 48472 | 20171203 | 1859 | 1934372 | 388 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2391 | 266940 | 37.9881 | -122.4895 | Robinhood & Knight | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0099378 | OH | Sus | 31368065 | No | 2017 | DEC | Yes | Line to Ground | 1317236 | CSO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER | 806 | 20171210 | 408 | 1939822 | 601 | Distribution Circuit | Equipment Failure/Involved | Overhead | 144 | 41526 | 38.6169 | -122.4244 | LABO- MICHAEL: 6 SPANS S/S 972477 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0100979 | OH | Sus | 31369121 | No | 2017 | DEC | Yes | Line to Ground | 1318658 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | JUMPER | 1117 | 20171219 | 656 | 1947418 | 393 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 10178 | 38.3712 | -122.4232 | 1144 Lokoya rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102528 | OH | Sus | 43238012 | No | 2017 | DEC | Yes | Line to Ground | 1320647 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 4497 | 20171221 | 2000 | 1949885 | 569 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 8994 | 37.9654 | -122.5514 | 4S/of SBCO-5787 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102986 | OH | Sus | 43239840 | No | 2017 | DEC | Yes | Line to Ground | 1321517 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | JUMPER | 1889 | 20180109 | 910 | 4822 | 1035 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 4329 | 38.0959 | -122.8558 | JOHNSTON-ANDREW: 11 glen way | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0004696 | OH | Sus | 0 | yes | 2018 | JAN | Yes | Line to Ground | 1323866 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | RECLOSER | 734 | 20180110 | 1126 | 5953 | 893 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 361 | 202748 | 38.5894 | -122.6078 | DOEDING- DUSTY: 18907 hwy 128 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0005026 | OH | Sus | 0 | No | 2018 | JAN | Yes | Line to Ground | 1324097 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2101 | 43292101 | FUSE | 1117 | 20180121 | 1139 | 11573 | 381 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 11430 | 38.3727 | -122.417 | 4 SPANS LD SIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0007669 | OH | Sus | 43258360 | No | 2018 | JAN | Yes | Line to Line | 1325778 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2101 | 43292101 | FUSE | 3125 | 20180128 | 1942 | 15576 | 1848 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 13668 | 38.3964 | -122.4494 | 2/P LD SIDE OF FUCO 3125- FIRST LINE & BUCK | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0009698 | OH | Sus | 43262692 | No | 2018 | JAN | Yes | Line to Ground | 1327004 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | OTHER | WIRE DOWN 1 SPANS SOURCE SIDE OF 743 #1?? | 20180129 | 1627 | 16071 | 526 | Distribution Circuit | Equipment Failure/Involved | Overhead | 744 | 243756 | 38.5928 | -122.4389 | 1 SPANS SOURCE SIDE OF 743 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0009959 | OH | Sus | 43263322 | No | 2018 | JAN | Yes | Line to Ground | 1327157 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | FUSE | 3755 | 20180221 | 1040 | 28657 | 186 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 13950 | 37.9152 | -122.5516 | 1S/NE/O 3755 | Partly Cloudy-32-90 F | Insulator | Broken, wire on object | 18-0015943 | OH | Sus | 31380150 | No | 2018 | FEB | Yes | Line to Ground | 1331243 | INS | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | SWITCH | 523 | 20180225 | 2013 | 31322 | 314 | Distribution Circuit | Equipment Failure/Involved | Overhead | 170 | 53380 | 38.5667 | -122.6299 | 4222 MOUNTAIN HOME RANCH RD | Partly Cloudy-32-90 F | Insulator | Broken, wire on object | 18-0017085 | OH | Sus | 0 | No | 2018 | FEB | Yes | Force Out | 1332022 | INS | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | ALTO-1125 | 42031125 | FUSE | 5191 | 20180226 | 1721 | 32208 | 371 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 12663 | 37.8827 | -122.5459 | Eucalyptus Way W/of Glenwood Ave | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0017522 | OH | Sus | 31381506 | yes | 2018 | FEB | Yes | Line to Ground | 1332257 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | RECLOSER | 658898 | 20180227 | 514 | 32489 | 809 | Distribution Circuit | Equipment Failure/Involved | Overhead | 145 | 96379 | 38.5072 | -122.4911 | A PHASE WIRE DOWN 2 SPANS N/OF 4773 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0017589 | OH | Sus | 43285847 | yes | 2018 | FEB | Yes | Line to Ground | 1332327 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 5369 | 20180301 | 1943 | 35648 | 547 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 22427 | 38.52 | -122.4692 | 3 SPANS LD SIDE OF 5369 | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0018914 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333271 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | OTHER | 7533 | 20180301 | 1004 | 34403 | 952 | Distribution Circuit | Equipment Failure/Involved | Overhead | 116 | 96144 | 38.5198 | -122.5269 | 4 SPANS SS 4065 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0018437 | OH | Sus | 43286582 | yes | 2018 | MAR | Yes | Line to Ground | 1332949 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 415 | 20180310 | 2101 | 41781 | 1166 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 15379 | 38.5568 | -122.4932 | at FUCO-415 & at 230 CRYSTAL SPRINGS RD | Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0021627 | OH | Sus | 31383600 | No | 2018 | MAR | Yes | Line to Ground | 1335183 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | RECLOSER | 322 | 20180312 | 1928 | 42781 | 474 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3094 | 395612 | 37.9774 | -122.5654 | 2 SPAN E/OF 3205 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0022019 | OH | Sus | 43299652 | No | 2018 | MAR | Yes | Line to Ground | 1335480 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-1105 | 43291105 | OTHER | WIRE DOWN OPEN @1174 LOMA VISTA DR. | 20180318 | 712 | 47374 | 1168 | Distribution Circuit | Equipment Failure/Involved | Overhead | 288 | 205888 | 38.3796 | -122.2893 | 1174 LOMA VISTA DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023894 | OH | Sus | 43303126 | No | 2018 | MAR | Yes | Line to Ground | 1336701 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | OTHER | WIRE DOWN 3 SPANS N/OF 8393 SBCO | 20180320 | 1954 | 48992 | 968 | Distribution Circuit | Equipment Failure/Involved | Overhead | 390 | 120468 | 38.4309 | -122.2073 | 3 SPANS N/OF 8393 SBCO | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0024618 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1337171 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | JUMPER | TEMP SOLID BLADES AT BEGINNING OF TAP | 20180322 | 1119 | 50626 | 875 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2625 | 38.097 | -122.8556 | JOHNSTON-ANDREW #1471: 4 Glen way | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025496 | OH | Sus | 31385497 | yes | 2018 | MAR | Yes | Line to Ground | 1337598 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2101 | 43292101 | TRIP-SAVER | 3583 | 20180322 | 2124 | 51373 | 1121 | Distribution Circuit | Equipment Failure/Involved | Overhead | 97 | 46977 | 38.3745 | -122.4203 | 2 SPANS LD SIDE OF FUCO 2027 ON THE MAIN LINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025834 | OH | Sus | 43306691 | yes | 2018 | MAR | Yes | Line to Line | 1337770 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | STAFFORD-1102 | 43201102 | RECLOSER | 1202 | 20180402 | 1956 | 58321 | 399 | Distribution Circuit | Animal | Bird found | 53 | 21147 | 38.1221 | -122.6224 | 3600 NOVATO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0028650 | OH | Sus | 43313566 | No | 2018 | APR | Yes | Line to Ground | 1340015 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | CALISTOGA-1101 | 42711101 | RECLOSER | 89150 | 20180406 | 2317 | 61408 | 1168 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 98902 | 38.6092 | -122.5912 | wire down 5S/of LR35588 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0030163 | OH | Sus | 43317007 | yes | 2018 | APR | Yes | Line to Ground | 1341034 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | OTHER | WIRE DOWN 5 SP/N/OF 4063 | 20180407 | 211 | 61575 | 549 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 10233 | 37.9089 | -122.5427 | 5 SP/N/OF FUCO 4063 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0030180 | OH | Sus | 43316771 | yes | 2018 | APR | Yes | Line to Ground | 1341050 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | RECLOSER | 432 | 20180407 | 630 | 61675 | 592 | Distribution Circuit | Vegetation | Tree - fell into line | 673 | 178985 | 37.9088 | -122.5475 | at FUCO-5773 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0030193 | OH | Sus | 31387696 | yes | 2018 | APR | Yes | Line to Ground | 1341065 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 2629 | 20180411 | 1801 | 64943 | 952 | Distribution Circuit | Vegetation | Tree - branch fell on line | 65 | 61880 | 38.0104 | -122.702 | 70 SPRING RD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0031439 | OH | Sus | 31388353 | yes | 2018 | APR | Yes | Line to Ground | 1342071 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 5605 | 20180417 | 1121 | 68861 | 540 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2700 | 38.0494 | -122.6783 | 1 SPAN LD SIDE OF 5605 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0033092 | OH | Sus | 31389032 | No | 2018 | APR | Yes | Line to Ground | 1343350 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-1105 | 43291105 | FUSE | 2793 | 20180506 | 1204 | 80284 | 1493 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 14930 | 38.4321 | -122.3005 | 1SPAN LD SIDE OF 2793 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0038635 | OH | Sus | 0 | No | 2018 | MAY | Yes | Line to Ground | 1347098 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5465 | 20180508 | 1440 | 81793 | 288 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 288 | 38.1099 | -122.8856 | 2 S/S OF | Partly Cloudy-32-90 F | Anchor or Guy | Broken, wire on object | 18-0039311 | OH | Sus | 0 | No | 2018 | MAY | Yes | Line to Line | 1347581 | ANC | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | ALTO-1125 | 42031125 | TRIP-SAVER | 2243 | 20180510 | 602 | 82776 | 326 | Distribution Circuit | Equipment Failure/Involved | Overhead | 959 | 236704 | 37.8804 | -122.5384 | HLEBAKOS- FRANK 415-306-6297: 552 Northern ave | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0039734 | OH | Sus | 43339917 | No | 2018 | MAY | Yes | Line to Ground | 1347907 | CSO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | OTHER | WIRE DOWN 1 W/OF 935 | 20180512 | 2205 | 85125 | 1194 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1145 | 1023078 | 38.4952 | -122.1999 | BURNED OPEN JUMPER 1 W/OF 935 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0040583 | OH | Sus | 43346620 | No | 2018 | MAY | Yes | Line to Ground | 1348649 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1147 | 20180519 | 1322 | 89773 | 758 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2032 | 38.089 | -122.8428 | 118 S DREAM FARM | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0042544 | OH | Sus | 43351601 | No | 2018 | MAY | Yes | Line to Ground | 1350126 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3585 | 20180526 | 2350 | 94678 | 820 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 14907 | 38.1033 | -122.8632 | 475 VISION RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0044695 | OH | Sus | 43356382 | No | 2018 | MAY | Yes | Line to Line | 1351779 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | BOLINAS-1101 | 42261101 | FUSE | 46819 | 20180609 | 934 | 105089 | 371 | Distribution Circuit | Vegetation | Tree - bark fell into line | 1 | 371 | 37.9382 | -122.703 | 2 SPANS LD SID OF 46819 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0049219 | OH | Sus | 43366609 | yes | 2018 | JUN | Yes | Line to Ground | 1355250 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 3345 | 20180609 | 1258 | 105199 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 8054 | 38.5515 | -122.4845 | MAINLINE AT 6827 FUCO | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0049248 | OH | Sus | 31395392 | yes | 2018 | JUN | Yes | Line to Ground | 1355285 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 4245 | 20180620 | 1150 | 113733 | 845 | Distribution Circuit | Equipment Failure/Involved | Overhead | 99 | 83655 | 38.5824 | -122.6581 | BOCK- MIKE 707-695-8997 #1484: 4245.. 8540 FRANZ VALLEY SCHOOL | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0052856 | OH | Sus | 43378096 | No | 2018 | JUN | Yes | Line to Ground | 1358106 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 1763 | 20180620 | 1622 | 114036 | 592 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4736 | 38.5931 | -122.4408 | 1250 HOWELL MT. RD. | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0052956 | OH | Sus | 43378647 | No | 2018 | JUN | Yes | Line to Ground | 1358150 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 4245 | 20180621 | 1307 | 114542 | 987 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 10493 | 38.5824 | -122.6581 | 8655 FRANZ VALLETY SCHOOL RD. | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 18-0053212 | OH | Sus | 43379540 | No | 2018 | JUN | Yes | Line to Line | 1358430 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | OTHER | WIRE DOWN 1 E/O 8321 | 20180623 | 1753 | 116494 | 330 | Distribution Circuit | Vegetation | Tree - fell into line | 218 | 71376 | 38.6033 | -122.6437 | 1 SPAN E/OF 8321 FUCO | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 18-0053919 | OH | Sus | 0 | yes | 2018 | JUN | Yes | Open Circuit | 1358943 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | WOODACRE-1102 | 43021102 | OTHER | 1 PHASE OPEN TWD SW815 | 20180629 | 2229 | 121490 | 484 | Distribution Circuit | Vegetation | Tree - fell into line | 444 | 57509 | 38.0085 | -122.5835 | 1/S/E/OF 815 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0055837 | OH | Sus | 43386456 | No | 2018 | JUN | Yes | Open Circuit | 1360650 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | ALTO-1120 | 42031120 | RECLOSER | 1120/2 | 20180723 | 816 | 137922 | 276 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1642 | 227058 | 37.8784 | -122.5342 | JOHNSTON-ANDREW #1474: 321 marin ave | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0062600 | OH | Sus | 31400879 | No | 2018 | JUL | Yes | Line to Line | 1365855 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | RECLOSER | 322 | 20180725 | 1729 | 140327 | 350 | Distribution Circuit | Vegetation | Tree - fell into line | 3094 | 158990 | 37.9774 | -122.5654 | JENSEN- BILL 415-450-7703: center & forrest ave | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0063755 | OH | Sus | 31401216 | No | 2018 | JUL | Yes | Line to Ground | 1366664 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SILVERADO-2102 | 43432102 | RECLOSER | 58626 | 20180725 | 1549 | 140217 | 653 | Distribution Circuit | Vegetation | Tree - fell into line | 337 | 108205 | 38.5071 | -122.4061 | DOEDING- DUSTY 707-888-1341: 1220 CONN VALLEY RD. | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0063707 | OH | Sus | 31401217 | No | 2018 | JUL | Yes | Line to Line | 1366634 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER | 806 | 20180727 | 549 | 141441 | 384 | Distribution Circuit | Vegetation | Tree - branch fell on line | 148 | 32064 | 38.6169 | -122.4244 | DOEDING- DUSTY 707-888-1341: 3928 CHILES POPE VALLEY RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0064251 | OH | Sus | 43420157 | No | 2018 | JUL | Yes | Line to Ground | 1367025 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | OTHER | WIRE DOWN | 20180804 | 2241 | 149153 | 979 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 27228 | 38.3454 | -122.4013 | 2 SPANS LD SIDE OF 1143 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0066824 | OH | Sus | 31402141 | No | 2018 | AUG | Yes | Line to Ground | 1369146 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | JUMPER | WIRE DOWN @4 GREENFIELD CT | 20180804 | 722 | 148731 | 626 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 6260 | 37.9756 | -122.5537 | 4 GREENFIELD CT | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0066666 | OH | Sus | 31401917 | No | 2018 | AUG | Yes | Line to Ground | 1368997 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 311 | 20180910 | 2037 | 171925 | 2655 | Distribution Circuit | Equipment Failure/Involved | Overhead | 148 | 219903 | 38.0439 | -122.7468 | BET Fuse 311 and SW 333 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0078359 | OH | Sus | 0 | No | 2018 | SEP | Yes | Line to Line | 1376979 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | OTHER | WIRE DOWN 2P E/OF 96903 | 20180921 | 2302 | 179155 | 778 | Distribution Circuit | Equipment Failure/Involved | Overhead | 159 | 9470 | 38.6428 | -122.7453 | 2P E/OF 96903 FUCO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0082304 | OH | Sus | 31406493 | No | 2018 | SEP | Yes | Line to Ground | 1379870 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | STAFFORD-1102 | 43201102 | RECLOSER | 1202 | 20181004 | 739 | 188017 | 321 | Distribution Circuit | Animal | Bird found | 53 | 10565 | 38.1221 | -122.6224 | Pederson- Ryley 707-494-1396: 3549 Novato Blvd | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0086585 | OH | Sus | 43496358 | yes | 2018 | OCT | Yes | Line to Line | 1382955 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 141 | 20181007 | 1337 | 190256 | 851 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 5106 | 38.5785 | -122.4424 | 400 HOWELL MOUNTAIN RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0087957 | OH | Sus | 0 | yes | 2018 | OCT | Yes | Three Phase Fault | 1383874 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 9251 | 20181016 | 1014 | 196309 | 376 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 752 | 38.5835 | -122.6597 | 8799 FRANZ VALLEY SCHOOL RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0090829 | OH | Sus | 0 | No | 2018 | OCT | Yes | Line to Ground | 1386027 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | WOODACRE-1101 | 43021101 | RECLOSER | 1456 | 20181016 | 2044 | 196932 | 736 | Distribution Circuit | Equipment Failure/Involved | Overhead | 77 | 56672 | 38.0541 | -122.6917 | HLEBAKOS- FRANK 415-306-6297: CAMINO MARGARITA at EL MIRADOR | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0091146 | OH | Sus | 43508718 | No | 2018 | OCT | Yes | Line to Ground | 1386194 | CSO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | RECLOSER | 736 | 20181031 | 1111 | 206297 | 899 | Distribution Circuit | Vegetation | Tree - fell into line | 354 | 249775 | 38.5803 | -122.5979 | BOCK- MIKE 707-695-8997 #1484: 347 Shaw Williams | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0095897 | OH | Sus | 43521877 | No | 2018 | OCT | Yes | Line to Line | 1389562 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | RECLOSER | 634 | 20181118 | 1707 | 217837 | 957 | Distribution Circuit | 3rd Party | Vehicle | 597 | 305965 | 38.5859 | -122.5715 | 1060 DUAAWEAL LN | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 18-0100821 | OH | Sus | 0 | No | 2018 | NOV | Yes | Line to Ground | 1393378 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | CALISTOGA-1102 | 42711102 | OCB | 1102/2 | 20181122 | 139 | 221445 | 581 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2148 | 150585 | 38.5924 | -122.5785 | LABO- MICHAEL: 1103 LARKMEAD LN | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102217 | OH | Sus | 31416641 | yes | 2018 | NOV | Yes | Line to Ground | 1394353 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | WOODACRE-1101 | 43021101 | RECLOSER | 91900 | 20181122 | 1646 | 222271 | 1573 | Distribution Circuit | Equipment Failure/Involved | Overhead | 115 | 91057 | 38.0551 | -122.6933 | 3 E OF 6573/ 1 W OF 2603 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102389 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1394541 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | OTHER | WIRE DOWN 2 SPANS S/O 4307 | 20181130 | 44 | 229791 | 1062 | Distribution Circuit | Equipment Failure/Involved | Overhead | 94 | 20962 | 38.005 | -122.7063 | WALTER- RYAN: 2 spans s/o sw4307 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105491 | OH | Sus | 31417311 | yes | 2018 | NOV | Yes | Line to Ground | 1396510 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | BOLINAS-1101 | 42261101 | FUSE | 1303 | 20181204 | 738 | 233243 | 472 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2832 | 37.9367 | -122.7033 | TURMEL- JOEL: tree fell at 660 horeshoe hill rd | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0106718 | OH | Sus | 31417545 | yes | 2018 | DEC | Yes | Line to Line | 1397475 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | OTHER | WIRE DOWN 255 PETRIFIED FOREST | 20181204 | 708 | 233258 | 323 | Distribution Circuit | Equipment Failure/Involved | Overhead | 358 | 97172 | 38.5798 | -122.6134 | BOCK- MIKE 707-695-8997 #1484: 255 petrified forest | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0106705 | OH | Sus | 43605722 | yes | 2018 | DEC | Yes | Line to Ground | 1397463 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | STAFFORD-1102 | 43201102 | FUSE | 2591 | 20181204 | 917 | 233357 | 248 | Distribution Circuit | Equipment Failure/Involved | Overhead | 87 | 21576 | 38.1026 | -122.6227 | ANDREWS- KYLE: 2560 VINEYARD RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0106752 | OH | Sus | 43605726 | yes | 2018 | DEC | Yes | Line to Line | 1397527 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5445 | 20181215 | 1355 | 241019 | 765 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 6120 | 38.0599 | -122.821 | 201 SILVER HILLS RD | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0109380 | OH | Sus | 31418626 | No | 2018 | DEC | Yes | Line to Ground | 1399951 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | FUSE | 2133 | 20181216 | 2301 | 241894 | 250 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 5250 | 37.9205 | -122.5543 | 1/S/E/OF 2133 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0109573 | OH | Sus | 43616028 | yes | 2018 | DEC | Yes | Line to Ground | 1400205 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5147 | 20181224 | 1458 | 246442 | 820 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 22960 | 38.0682 | -122.8252 | 1 SPAN LD SIDE OF 5147 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110495 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Ground | 1401573 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5469 | 20181225 | 313 | 246960 | 534 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 36312 | 38.0646 | -122.8251 | 30 DRAKE SUMMIT- INVERNESS | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110620 | OH | Sus | 0 | No | 2018 | DEC | Yes | Line to Ground | 1401701 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | RECLOSER | 734 | 20190101 | 732 | 251314 | 570 | Distribution Circuit | Vegetation | Tree - fell into line | 336 | 129640 | 38.5894 | -122.6078 | 1N/of FUCO-5074 4 spans primary down (mainline) | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0003401 | OH | Sus | 43624048 | No | 2019 | JAN | Yes | Line to Line | 1402607 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1101 | 42011101 | OTHER | WIRE DOWN ON GROUND AT 10 FIRE RD | 20190108 | 1010 | 260363 | 308 | Distribution Circuit | Vegetation | Tree - fell into line | 1321 | 17204 | 37.9615 | -122.5289 | 10 MEYER RD | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0006235 | OH | Sus | 31421297 | yes | 2019 | JAN | Yes | Line to Ground | 1404479 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3513 | 20190109 | 20 | 261137 | 565 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 13560 | 38.0752 | -122.8411 | 60 SUNNYSIDE- INVERNESS | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0006635 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1404718 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | WOODACRE-1101 | 43021101 | RECLOSER | 91900 | 20190109 | 6 | 261129 | 885 | Distribution Circuit | Equipment Failure/Involved | Overhead | 115 | 52051 | 38.0551 | -122.6933 | 3 SPANS SOURCE SIDE OF 6573 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0006610 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1404691 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 911 | 20190111 | 2240 | 263636 | 462 | Distribution Circuit | Equipment Failure/Involved | Overhead | 76 | 35112 | 37.9006 | -122.5642 | 34 MADERA WAY | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0008179 | OH | Sus | 31421790 | No | 2019 | JAN | Yes | Line to Ground | 1405704 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 2493 | 20190115 | 1930 | 266276 | 359 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 4667 | 38.0967 | -122.8591 | 160 LAUREL AVE | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009301 | OH | Sus | 43636017 | yes | 2019 | JAN | Yes | Line to Ground | 1406429 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1101 | 42011101 | FUSE | 331 | 20190207 | 2201 | 295819 | 581 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 23821 | 37.9725 | -122.5595 | JENSEN- BILL 415-450-7703: 7 sturdivant ave | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0019807 | OH | Sus | 31424999 | yes | 2019 | FEB | Yes | Line to Ground | 1413590 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 54471 | 20190220 | 508 | 319328 | 412 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 4120 | 37.8997 | -122.542 | 1/N of 54471 | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026314 | OH | Sus | 43682281 | yes | 2019 | FEB | Yes | Line to Ground | 1419145 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | FUSE | 4753 | 20190223 | 422 | 321753 | 2293 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 9172 | 38.5212 | -122.537 | 2 SPANS WEST OF 4753 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0027450 | OH | Sus | 0 | No | 2019 | FEB | Yes | Line to Ground | 1419738 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SILVERADO-2102 | 43432102 | RECLOSER | 58626 | 20190224 | 354 | 322315 | 669 | Distribution Circuit | Equipment Failure/Involved | Overhead | 431 | 121342 | 38.5071 | -122.4061 | E/O 81437 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0027550 | OH | Sus | 0 | No | 2019 | FEB | Yes | Line to Line | 1419834 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | JUMPER | CAR POLE @ 3185 | 20190225 | 254 | 322633 | 1034 | Distribution Circuit | 3rd Party | Vehicle | 33 | 32474 | 38.5283 | -122.4849 | 1 W/O 2974 SILVERADO TRAIL- NAPA | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0027653 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1419931 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 5827 | 20190225 | 1919 | 323527 | 652 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 15648 | 38.0224 | -122.7012 | 65 BARRANCA RD | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0027990 | OH | Sus | 43685371 | yes | 2019 | FEB | Yes | Line to Ground | 1420099 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER | 1200 | 20190305 | 2144 | 331982 | 616 | Distribution Circuit | Vegetation | Tree - branch fell on line | 238 | 146540 | 38.0971 | -122.8526 | 2 SP/SS OF FUCO 1885 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031020 | OH | Sus | 31427631 | yes | 2019 | MAR | Yes | Line to Line | 1422131 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 3393 | 20190306 | 112 | 332094 | 990 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 14850 | 38.1297 | -122.899 | 1 ld side of 3393 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031067 | OH | Sus | 43690690 | yes | 2019 | MAR | Yes | Line to Ground | 1422177 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 5343 | 20190306 | 2040 | 333295 | 333 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 4059 | 37.9759 | -122.5771 | 444 REDWOOD RD | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031496 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1422428 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | BOLINAS-1101 | 42261101 | TRIP-SAVER | 1247 | 20190307 | 1539 | 333889 | 641 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 18589 | 37.9737 | -122.6127 | 85 BOSQUE | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031823 | OH | Sus | 31427855 | No | 2019 | MAR | Yes | Line to Ground | 1422637 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | FUSE | 2487 | 20190310 | 718 | 335372 | 477 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 13356 | 37.9094 | -122.5567 | 225 TAMALPAIS AV | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0032389 | OH | Sus | 43698568 | No | 2019 | MAR | Yes | Line to Ground | 1423065 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | FUSE | 5769 | 20190310 | 1547 | 335600 | 642 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 11651 | 38.5979 | -122.4582 | 1P N/OF 5769 FUCO | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0032424 | OH | Sus | 0 | No | 2019 | MAR | Yes | None | 1423107 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | STAFFORD-1102 | 43201102 | FUSE | 4241 | 20190310 | 728 | 335376 | 680 | Distribution Circuit | Animal | Bird found | 16 | 10880 | 38.1018 | -122.6296 | 2 SP LINE SIDE OF 6773 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0032396 | OH | Sus | 43698570 | No | 2019 | MAR | Yes | Line to Line | 1423081 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | FUSE | 7505 | 20190311 | 849 | 335966 | 446 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 892 | 38.493 | -122.5153 | BOCK- MIKE 707-695-8997 #1484: 7505 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0032588 | OH | Sus | 43700026 | No | 2019 | MAR | Yes | Line to Ground | 1423270 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE | 9193 | 20190313 | 500 | 338128 | 410 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 3014 | 38.5646 | -122.5585 | 4319 azalea springs way.- calistoga | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033294 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1423756 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 6487 | 20190314 | 1006 | 339275 | 900 | Distribution Circuit | 3rd Party | Vehicle | 213 | 41014 | 37.9482 | -122.5589 | 214 EVERGREEN DR | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0033813 | OH | Sus | 31429048 | No | 2019 | MAR | Yes | Three Phase Fault | 1424139 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER | 632 | 20190317 | 1514 | 341496 | 674 | Distribution Circuit | Vegetation | Tree - bark fell into line | 753 | 302073 | 38.574 | -122.4444 | BOCK- MIKE 707-695-8997 #1484: 1400 howell mnt | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0034490 | OH | Sus | 43709133 | No | 2019 | MAR | Yes | Line to Ground | 1424678 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 7449 | 20190327 | 327 | 348142 | 458 | Distribution Circuit | Vegetation | Tree - branch fell on line | 43 | 19694 | 38.0076 | -122.6447 | 1 SP LD SIDE OF 7449 | Overcast-Fog-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0037285 | OH | Sus | 43718308 | yes | 2019 | MAR | Yes | Line to Ground | 1426563 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE | 9191 | 20190328 | 1208 | 349458 | 641 | Distribution Circuit | Vegetation | Tree - fell into line | 169 | 42406 | 38.5651 | -122.5582 | BETWEEN SW-693 AND 3755 FUCO | Partly Cloudy-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0037958 | OH | Sus | 43720896 | yes | 2019 | MAR | Yes | Line to Ground | 1426995 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 3343 | 20190331 | 430 | 351060 | 363 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 9801 | 38.3614 | -122.3713 | 4870 DRY CREEK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0038541 | OH | Sus | 31431921 | No | 2019 | MAR | Yes | Line to Ground | 1427431 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | OTHER | WIRE DOWN 1 SOURCE SIDE OF 630 | 20190410 | 625 | 357669 | 398 | Distribution Circuit | Equipment Failure/Involved | Overhead | 220 | 60650 | 38.5723 | -122.2432 | 1 SOURCE SIDE OF 630 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0041208 | OH | Sus | 43734959 | yes | 2019 | APR | Yes | Line to Ground | 1429298 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 6397 | 20190411 | 944 | 358737 | 1318 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 9226 | 38.6071 | -122.4594 | 3 SPANS LD SIDE OF 6397 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0041615 | OH | Sus | 31433788 | yes | 2019 | APR | Yes | Line to Ground | 1429676 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | CALISTOGA-1101 | 42711101 | OCB | 1101/2 | 20190416 | 645 | 361531 | 295 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1616 | 180426 | 38.5924 | -122.5786 | Jensen.Bill 415-450-7703: c/o 2307 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0042748 | OH | Sus | 31434363 | No | 2019 | APR | Yes | Line to Ground | 1430415 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | JUMPER | O/J 2 MT VISION RD LINE AND BUCK | 20190427 | 1748 | 369333 | 1324 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1324 | 38.099 | -122.8846 | MIDSPAN BETWEEN LINE AND BUCK AND EOL POT | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0046780 | OH | Sus | 43754442 | No | 2019 | APR | Yes | Line to Ground | 1433172 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | OTHER | 2387 | 20190515 | 1357 | 381010 | 508 | Distribution Circuit | Vegetation | Tree - fell into line | 2146 | 71882 | 37.9875 | -122.5995 | 463 SCENIC RD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0052211 | OH | Sus | 43782282 | yes | 2019 | MAY | Yes | Open Circuit | 1436897 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | JUMPER | WIRE DOWN 7 SPANS LD SIDE OF 4719 | 20190518 | 1907 | 384533 | 790 | Distribution Circuit | Vegetation | Tree - fell into line | 169 | 29092 | 38.3495 | -122.1589 | WIRE DOWN 7 SPANS LD SIDE OF 4719 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053715 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Line | 1437936 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | STAFFORD-1102 | 43201102 | OTHER | WIRE DOWN 1926 INDIAN VALLEY RD | 20190521 | 1816 | 387394 | 368 | Distribution Circuit | Equipment Failure/Involved | Overhead | 232 | 3980 | 38.0941 | -122.5981 | E /OF 5471 ON INDIAN VALLEY | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0055064 | OH | Sus | 43792146 | yes | 2019 | MAY | Yes | Line to Ground | 1438893 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1119 | 20190526 | 346 | 390570 | 769 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 6152 | 38.3825 | -122.4312 | BET THE 2ND & 3RD POLE LD SIDE | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0057767 | OH | Sus | 0 | No | 2019 | MAY | Yes | Line to Ground | 1441277 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 1089 | 20190529 | 1647 | 392908 | 388 | Distribution Circuit | Vegetation | Tree - fell into line | 397 | 85636 | 38.0101 | -122.6401 | 28 Elm Ave | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0059225 | OH | Sus | 43802159 | yes | 2019 | MAY | Yes | Three Phase Fault | 1442487 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 3881 | 20190604 | 1704 | 397714 | 896 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 896 | 37.8906 | -122.5649 | TURMEL- JOEL 415-299-4832: C/Os 3881 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0062730 | OH | Sus | 31451331 | yes | 2019 | JUN | Yes | Line to Ground | 1445290 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE | 174453 | 20190604 | 2049 | 398027 | 838 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 16667 | 38.5642 | -122.5804 | 1P LD SIDE OF 174453 FUCO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0062818 | OH | Sus | 43822592 | yes | 2019 | JUN | Yes | Line to Ground | 1445361 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | SILVERADO-2102 | 43432102 | FUSE | 7607 | 20190607 | 1123 | 400656 | 294 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 882 | 38.4874 | -122.3999 | 2 SPANS LD SIDE OF 7607 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0064281 | OH | Sus | 0 | yes | 2019 | JUN | Yes | None | 1446487 | CSO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1122 | 42031122 | FUSE | 2347 | 20190615 | 2328 | 415553 | 1479 | Distribution Circuit | Equipment Failure/Involved | Overhead | 78 | 60719 | 37.9209 | -122.527 | 1 SPANS SOURCE SIDE OF 2134 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0068198 | OH | Sus | 0 | No | 2019 | JUN | Yes | Line to Ground | 1449600 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | RECLOSER | 654 | 20190617 | 1023 | 417406 | 1403 | Distribution Circuit | Vegetation | Tree - branch fell on line | 220 | 306900 | 38.5116 | -122.2134 | TERRILL-RICH/4151/707-315-2058: 1710 knoxville rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0068579 | OH | Sus | 43845341 | No | 2019 | JUN | Yes | Line to Ground | 1449952 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 7467 | 20190617 | 1804 | 418035 | 496 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 3472 | 38.0998 | -122.8763 | 1000 VISON RD- INVERNESS | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0068786 | OH | Sus | 31454440 | No | 2019 | JUN | Yes | Line to Ground | 1450036 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 5377 | 20190618 | 2001 | 420660 | 514 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 10280 | 37.9762 | -122.577 | 248 REDWOOD RD- SAN ANSELMO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0069407 | OH | Sus | 43847433 | No | 2019 | JUN | Yes | Line to Ground | 1450464 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SILVERADO-2104 | 43432104 | OTHER | WIRE DOWN SSD 6711 | 20190626 | 1342 | 429863 | 1845 | Distribution Circuit | Vegetation | Tree - fell into line | 3228 | 21207 | 38.5149 | -122.459 | KNIFFIN- ANDREW 415-720-2131: FUSES 6711 ON SILVERADO TRAIL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0072340 | OH | Sus | 31455527 | No | 2019 | JUN | Yes | Line to Ground | 1452898 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SILVERADO-2102 | 43432102 | JUMPER | WIRE DOWN E/OF 6685 ACROSS CONN CREEK | 20190706 | 955 | 441784 | 361 | Distribution Circuit | Equipment Failure/Involved | Overhead | 337 | 50108 | 38.5056 | -122.3953 | ACROSS CONN CREEK | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0074934 | OH | Sus | 43869067 | No | 2019 | JUL | Yes | Line to Ground | 1454518 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | WOODACRE-1102 | 43021102 | FUSE | 1421 | 20190711 | 2000 | 445533 | 555 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 7940 | 37.9981 | -122.594 | 51 PEPER LN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0076573 | OH | Sus | 0 | No | 2019 | JUL | Yes | Line to Ground | 1455579 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | JUMPER | O/J 1 S/OF 6039 | 20190802 | 2001 | 479202 | 1154 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4616 | 38.596 | -122.4513 | 9839 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0083975 | OH | Sus | 0 | No | 2019 | AUG | Yes | Line to Ground | 1460484 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | CALISTOGA-1101 | 42711101 | OCB | 1101/2 | 20190816 | 1358 | 518459 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 1599 | 96615 | 38.5924 | -122.5786 | 689 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0088871 | OH | Sus | 31462823 | yes | 2019 | AUG | Yes | Line to Line | 1463683 | CAW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2102 | 43292102 | FUSE | 3123 | 20190817 | 1735 | 521393 | 697 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 26733 | 38.4069 | -122.4422 | 6495 DRY CREEK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0089123 | OH | Sus | 31462886 | No | 2019 | AUG | Yes | Line to Ground | 1463914 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | OTHER | WIRE DOWN 2 SPANS LD SIDE 2883 | 20190817 | 816 | 519146 | 337 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1454 | 176577 | 38.5722 | -122.4434 | 2 SPANS LD SIDE 2883 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0089040 | OH | Sus | 31462882 | No | 2019 | AUG | Yes | Line to Line | 1463812 | CSO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | GREENBRAE-1102 | 43091102 | FUSE | 699 | 20190819 | 1616 | 523858 | 630 | Distribution Circuit | Equipment Failure/Involved | Overhead | 76 | 16618 | 37.9524 | -122.5264 | 1 ? DOWN FROM 328 N ALMENAR DR TO 348 N ALEMENAR DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0089629 | OH | Sus | 43930480 | No | 2019 | AUG | Yes | Line to Line | 1464328 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SAUSALITO-1102 | 42491102 | FUSE | 1453 | 20190821 | 1915 | 529764 | 524 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 8384 | 37.8306 | -122.5258 | 10 spans LD side of FUCO-1453 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0090692 | OH | Sus | 31464840 | No | 2019 | AUG | Yes | Line to Line | 1464900 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | STAFFORD-1102 | 43201102 | FUSE | 6773 | 20190915 | 1249 | 583312 | 817 | Distribution Circuit | Vegetation | Tree - fell into line | 1565 | 21038 | 38.1059 | -122.6448 | 3035 NOVATO BLVD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0099253 | OH | Sus | 0 | No | 2019 | SEP | Yes | Force Out | 1470137 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | OTHER | WIRE DOWN @ MTR#1006107439 | 20190922 | 1036 | 603381 | 25 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 374 | 9200 | 38.5807 | -122.6099 | MTR#1006107439. | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on object | 19-0102219 | OH | Sus | 0 | No | 2019 | SEP | Yes | Line to Ground | 1471893 | CSO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | JUMPER | WIRE DOWN @ MTR#1010353000 | 20190928 | 1457 | 627723 | 723 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 5166 | 38.0565 | -122.8258 | 201 SILVER HILLS DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0105007 | OH | Sus | 43973740 | yes | 2019 | SEP | Yes | Line to Ground | 1473782 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | FUSE | 7281 | 20191028 | 1043 | 691633 | 6097 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 12194 | 38.333 | -122.1161 | TERRILL-RICH/4151/707-315-2058: 6355 gordon valley rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0118033 | OH | Sus | 0 | yes | 2019 | OCT | Yes | Line to Ground | 1487050 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 6829 | 20191103 | 1852 | 698855 | 437 | Distribution Circuit | Vegetation | Tree - fell into line | 478 | 140834 | 38.5713 | -122.4536 | LABO- Mike 415 238-4971: 424 COLLEGE AVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0120574 | OH | Sus | 31477164 | No | 2019 | NOV | Yes | Line to Ground | 1488989 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | STAFFORD-1101 | 43201101 | OCB | 1101/2 | 20191117 | 1509 | 708760 | 560 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4941 | 609582 | 38.12 | -122.6138 | RPTS WIRE DOWN SOURCE SIDE OF 4469 | Clear-32-90 F | Insulator | Broken, wire on ground | 19-0125503 | OH | Sus | 44101613 | No | 2019 | NOV | Yes | Line to Line | 1491948 | INS | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 4307 | 20191124 | 859 | 713773 | 496 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 4960 | 38.5917 | -122.4463 | 885 WHITE COTTAGE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0128093 | OH | Sus | 0 | No | 2019 | NOV | Yes | Line to Ground | 1493734 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5147 | 20191201 | 14 | 725405 | 941 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 26348 | 38.0682 | -122.8252 | WALTER- RYAN 510-965-3246: 21 Carmencita Rd | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0131787 | OH | Sus | 0 | No | 2019 | DEC | Yes | Line to Ground | 1496483 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 9291 | 20191211 | 2328 | 737043 | 301 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 20769 | 38.5841 | -122.6692 | 6 SPANS LOAD SIDE | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0136060 | OH | Sus | 44120848 | No | 2019 | DEC | Yes | Multi-Fault | 1499922 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 3677 | 20200210 | 1031 | 787318 | 472 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2360 | 38.6029 | -122.6282 | SINGLE PHASE TAP OFF OF 3677 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0019956 | OH | Sus | 0 | yes | 2020 | FEB | Yes | Line to Ground | 1513924 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 7673 | 20200210 | 909 | 787831 | 717 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 717 | 38.3695 | -122.4227 | 1133 LOKOYA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0020198 | OH | Sus | 0 | yes | 2020 | FEB | Yes | Line to Ground | 1514034 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | TRIP-SAVER | 1087 | 20200211 | 751 | 788324 | 553 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 11613 | 38.5846 | -122.6722 | 8445 FRANZ VALLEY SCHOOL RD- CALISTOGA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0020562 | OH | Sus | 31490334 | yes | 2020 | FEB | Yes | Line to Ground | 1514293 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE | 1013 | 20200217 | 528 | 792360 | 803 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 55247 | 38.5649 | -122.5583 | QUAIL MTN. LN. 200'W/O HWY 29- CALISTOGA | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 20-0022722 | OH | Sus | 31491432 | No | 2020 | FEB | Yes | Line to Ground | 1515742 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE | 6143 | 20200225 | 127 | 805463 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3726 | 38.548 | -122.529 | 3331 ST HELENA HWY-ST HELENA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0025438 | OH | Sus | 44211194 | No | 2020 | FEB | Yes | Line to Ground | 1517488 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | OTHER | HOT WIRE DWN 2 SP LD SIDE OF 1117 | 20200404 | 1538 | 882426 | 277 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 7202 | 38.3717 | -122.4183 | 2 SP LD SIDE OF 1117 | Overcast-Fog-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0038432 | OH | Sus | 0 | No | 2020 | APR | Yes | Line to Ground | 1525266 | CSO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 5857 | 20200405 | 849 | 882759 | 282 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 7050 | 38.0159 | -122.7031 | 2 SPANS L/S OF 5857 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0038528 | OH | Sus | 44281631 | yes | 2020 | APR | Yes | Line to Ground | 1525362 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | OTHER | JUMPER/WIRE BROKEN 5 - 6 SPANS E/O SW 5029 | 20200407 | 411 | 886993 | 639 | Distribution Circuit | Vegetation | Tree - branch fell on line | 205 | 21934 | 37.8959 | -122.5916 | 5 - 6 SPANS E/O SW 5029. S/O PANORAMIC HWY | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0039179 | OH | Sus | 44283885 | No | 2020 | APR | Yes | Line to Ground | 1525823 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 7467 | 20200501 | 140 | 904935 | 649 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4543 | 38.0998 | -122.8763 | 1055 VISION RD- 10 SPANS LD SIDE OF 7467 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0046127 | OH | Sus | 31501706 | No | 2020 | MAY | Yes | Line to Ground | 1530137 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | SAUSALITO-1101 | 42491101 | FUSE | 5437 | 20200509 | 4 | 910001 | 374 | Distribution Circuit | Equipment Failure/Involved | Overhead | 41 | 15334 | 37.8452 | -122.4813 | 2 sp ld side of 5437 | Overcast-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0048721 | OH | Sus | 44315305 | No | 2020 | MAY | Yes | Line to Ground | 1531646 | CSO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | BOLINAS-1101 | 42261101 | FUSE | 2455 | 20200512 | 953 | 912023 | 593 | Distribution Circuit | Vegetation | Tree - grew into line | 4 | 2372 | 37.9225 | -122.721 | LAST SPAN TO EOL NO STREET | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0049436 | OH | Sus | 31502693 | yes | 2020 | MAY | Yes | Line to Ground | 1532119 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | STAFFORD-1102 | 43201102 | RECLOSER | 1202 | 20200513 | 2027 | 913397 | 445 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 14589 | 38.1221 | -122.6224 | 9 SPANS LD SIDE OF 1347 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0050001 | OH | Sus | 31502877 | No | 2020 | MAY | Yes | Line to Line | 1532398 | CAW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | JUMPER | WIRE DOWN @ 313770157771 | 20200525 | 1351 | 920902 | 324 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 324 | 38.0672 | -122.6665 | 313770157771 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 20-0053818 | OH | Sus | 44331364 | yes | 2020 | MAY | Yes | Line to Ground | 1534431 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | NOVATO-1104 | 42211104 | FUSE | 183215 | 20200605 | 1537 | 932334 | 979 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1958 | 38.1374 | -122.5795 | LABO- Mike 415 238-4971: 7 POLE FROM C/O 183218 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0058325 | OH | Sus | 31505220 | yes | 2020 | JUN | Yes | Line to Line | 1537569 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SILVERADO-2105 | 43432105 | OTHER | WIRE DWN BET 3403 & 4479 | 20200613 | 606 | 938318 | 671 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 12024 | 38.5335 | -122.5049 | BET 3403 & 4479 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0060910 | OH | Sus | 31505899 | No | 2020 | JUN | Yes | Line to Ground | 1539488 | CSO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 5561 | 20200628 | 424 | 949198 | 467 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2802 | 38.3355 | -122.3864 | 4310 REDWOOD RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0065779 | OH | Sus | 0 | No | 2020 | JUN | Yes | Line to Ground | 1543005 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1875 | 20200818 | 652 | 1018747 | 403 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 806 | 38.0018 | -122.7588 | 2 SPANS LD SIDE OF 1875 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0086613 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Ground | 1556638 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 7341 | 20200824 | 1544 | 1028721 | 166 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 2490 | 38.5818 | -122.4423 | GRAMMER- MASON: 445 Lloyd ln. Angwin | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0089488 | OH | Sus | 44445348 | yes | 2020 | AUG | Yes | Line to Ground | 1558507 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1145 | 20201015 | 2138 | 1118959 | 1188 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 20196 | 38.3346 | -122.373 | 1 SPAN SS OF 311///MT VEEDER RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0109461 | OH | Sus | 0 | yes | 2020 | OCT | Yes | Line to Line | 1571240 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER | 37632 | 20201020 | 1126 | 1121608 | 546 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 421 | 229056 | 38.5349 | -122.4754 | 1 NORTH OF 1447 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0110751 | OH | Sus | 0 | No | 2020 | OCT | Yes | Line to Line | 1572123 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SILVERADO-2104 | 43432104 | FUSE | 7339 | 20201030 | 1023 | 1132198 | 322 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 3 | 966 | 38.698 | -122.4042 | 3 SPANS S/O 7339 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0115448 | OH | Sus | 0 | No | 2020 | OCT | Yes | Line to Line | 1575855 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER | 602 | 20201106 | 108 | 1137024 | 984 | Distribution Circuit | Equipment Failure/Involved | Overhead | 139 | 93388 | 38.1094 | -122.8698 | LD OF 3393 | Clear-32-90F | Conductor, Overhead | Broken, wire on object | 20-0117605 | OH | Sus | 0 | No | 2020 | NOV | Yes | Line to Ground | 1577374 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SAN RAFAEL-1105 | 42011105 | RECLOSER | 534 | 20201113 | 1510 | 1144027 | 247 | Distribution Circuit | Equipment Failure/Involved | Overhead | 78 | 7566 | 37.9763 | -122.4968 | ANDREWS- KYLE: 315 margarita dr | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0120767 | OH | Sus | 0 | No | 2020 | NOV | Yes | Line to Ground | 1579594 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1117 | 20201231 | 310 | 1201669 | 487 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 8606 | 38.3727 | -122.4171 | S/OF 7597 ON ML | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0132338 | OH | Sus | 31522715 | No | 2020 | DEC | Yes | Line to Ground | 1590261 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SAUSALITO-1102 | 42491102 | JUMPER | HOT WIRE DWN | 20210221 | 1228 | 1258960 | 429 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 21687 | 37.8453 | -122.487 | 1 SP E/OF 7407 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0027852 | OH | Sus | 31530905 | No | 2021 | FEB | Yes | Line to Ground | 1606657 | CSO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 6905 | 20210307 | 1449 | 1272928 | 541 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 5717 | 38.5252 | -122.4781 | IFO 264 VIA MONTE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0033219 | OH | Sus | 44672091 | No | 2021 | MAR | Yes | Line to Ground | 1610239 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-1104 | 43291104 | OTHER | HOT WIRE DWN @ 4375 ATLAS PEAK RD | 20210317 | 408 | 1285631 | 341 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 8624 | 38.4374 | -122.2453 | 4375 ATLAS PEAK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0037396 | OH | Sus | 44686279 | No | 2021 | MAR | Yes | Line to Ground | 1612731 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | RECLOSER | 1238 | 20210322 | 1308 | 1292298 | 407 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 11695 | 38.011 | -122.7023 | LABO- Mike 415 238-4971: C/O 1455 SIRFRANCISCO DRAKE BLVD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0039425 | OH | Sus | 44698685 | No | 2021 | MAR | Yes | Line to Line | 1613984 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | CALISTOGA-1101 | 42711101 | RECLOSER | 122350 | 20210412 | 1824 | 1313886 | 616 | Distribution Circuit | Equipment Failure/Involved | Overhead | 124 | 44930 | 38.6088 | -122.591 | SPAN AT 677 GOING NORTH ON THE 3 PHASE | Clear-32-90 F | Insulator | Broken, wire on object | 21-0047694 | OH | Sus | 31535849 | No | 2021 | APR | Yes | Line to Line | 1619566 | INS | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | STAFFORD-1102 | 43201102 | RECLOSER | 1048 | 20210415 | 609 | 1317277 | 307 | Distribution Circuit | Animal | Bird found | 234 | 45372 | 38.0957 | -122.6021 | 1780 INDIAN VALLEY RD- NAVATO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0048789 | OH | Sus | 44743924 | No | 2021 | APR | Yes | Line to Line | 1620294 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | LAS GALLINAS A-1105 | 42991105 | RECLOSER | 99904 | 20210516 | 2244 | 1351048 | 1029 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 63592 | 38.0443 | -122.6155 | POLE 6 SP/LD SD OF 5621 & 3/SP/SS OF 5203 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0062074 | OH | Sus | 44805693 | No | 2021 | MAY | Yes | Line to Ground | 1629237 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 7103 | 20210527 | 1202 | 1359984 | 213 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 639 | 38.0137 | -122.6424 | 9 SPANS LD SIDE OF 7103 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0066922 | OH | Sus | 44819932 | No | 2021 | MAY | Yes | Line to Line | 1632702 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 2565 | 20210529 | 17 | 1361041 | 640 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 23410 | 37.9595 | -122.5348 | 75 POPLAR DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0067649 | OH | Sus | 31541531 | No | 2021 | MAY | Yes | Three Phase Fault | 1633034 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 2383 | 20210603 | 727 | 1364581 | 764 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 23 | 8398 | 38.5822 | -122.674 | 4130 SLYVESTER LN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0069278 | OH | Sus | 31541961 | No | 2021 | JUN | Yes | Line to Ground | 1634109 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | IGNACIO-1101 | 42481101 | OTHER | WIRE DOWN 1/W 3065 | 20210619 | 2129 | 1379974 | 772 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2557 | 276259 | 38.0754 | -122.5626 | 1/W 3065 | Clear-Clear-Above 90 | Connector or Splice (OH) | Broken, wire on ground | 21-0076705 | OH | Sus | 44868668 | No | 2021 | JUN | Yes | Line to Ground | 1638982 | CSO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1869 | 20210711 | 1342 | 1399459 | 317 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 1500 | 38.0389 | -122.7853 | BOLINAS-OLEMA RD. 6 POLES S/O & 1 POLE W/O SFD BLVD-9799 HWY 1-OLEMA | Clear-32-90F | Conductor, Overhead | On Ground | 21-0087723 | OH | Sus | 44904107 | No | 2021 | JUL | Yes | Line to Ground | 1647178 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 605 | 20210725 | 926 | 1413965 | 583 | Distribution Circuit | Vegetation | Tree - fell into line | 720 | 42550 | 38.0972 | -122.852 | 580 VILLA DE LA VISTA- INVERNESS | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0094617 | OH | Sus | 44919813 | No | 2021 | JUL | Yes | Line to Ground | 1651500 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | RECLOSER | 322 | 20210815 | 918 | 1443229 | 715 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3095 | 1148978 | 37.9773 | -122.5655 | 1356 SAN ANSELMO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0104752 | OH | Sus | 31549661 | No | 2021 | AUG | Yes | Line to Ground | 1657714 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SAN RAFAEL-1109 | 42011109 | FUSE | 5397 | 20210827 | 927 | 1455320 | 322 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 29 | 9338 | 37.9781 | -122.5077 | 2 SPANS S/W OF 687 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0110139 | OH | Sus | 31550590 | No | 2021 | AUG | Yes | Line to Ground | 1661518 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | JUMPER | WIRE DOWN 2 SP LD SIDE FUCO 3807 @ A?? | 20210909 | 1116 | 1466167 | 460 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1274 | 38.5423 | -122.5847 | WIRE DOWN 2 SP LD FUCO 3807 at A? | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0115409 | OH | Sus | 0 | No | 2021 | SEP | Yes | Line to Ground | 1664462 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5147 | 20211020 | 105 | 1502550 | 353 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 4172 | 38.0682 | -122.8253 | 3RD SPAN W/O 5147 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0133424 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1675857 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 5469 | 20211021 | 23 | 1503903 | 1001 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 39457 | 38.0646 | -122.8251 | 75 DRAKE SUMMIT RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0134164 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Line | 1676252 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | RECLOSER | 322 | 20211104 | 309 | 1534300 | 833 | Distribution Circuit | Vegetation | Tree - fell into line | 3093 | 807689 | 37.9773 | -122.5655 | CENTER BLVD & MADRONE AVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0142020 | OH | Sus | 31573888 | No | 2021 | NOV | Yes | Line to Ground | 1681617 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1102 | 42711102 | FUSE | 6143 | 20211118 | 1113 | 1549070 | 560 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 6 | 3360 | 38.5477 | -122.5293 | 3 SPANS LD SIDE OF 6143 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0147870 | OH | Sus | 45070705 | No | 2021 | NOV | Yes | Line to Ground | 1686160 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2102 | 43292102 | OTHER | BROKEN NEUT LD SIDE OF CGC 218870526030 | 20211119 | 1708 | 1550472 | 482 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 6936 | 38.3795 | -122.396 | LD SIDE OF CGC 218870526030 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0148860 | OH | Sus | 0 | No | 2021 | NOV | Yes | Open Circuit | 1686751 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2102 | 43292102 | FUSE | 407 | 20211124 | 535 | 1553912 | 356 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 14596 | 38.4099 | -122.4651 | DYDO- GREG 415-589-0425: 215 Wall Rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0150460 | OH | Sus | 31579021 | No | 2021 | NOV | Yes | Line to Ground | 1687738 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 3485 | 20211129 | 1313 | 1555769 | 458 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 34 | 15572 | 38.5596 | -122.4241 | 10 SPANS LD SIDE OF 3485 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0152602 | OH | Sus | 31579258 | No | 2021 | NOV | Yes | Three Phase Fault | 1689503 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | OTHER | WIRE DOWN 2 SPANS LD SIDE 87347 | 20211130 | 1618 | 1556686 | 376 | Distribution Circuit | Vegetation | Tree - fell into line | 350 | 79144 | 38.609 | -122.6552 | 2 SPANS LD SIDE OF 87347 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0153224 | OH | Sus | 31579342 | No | 2021 | NOV | Yes | Line to Ground | 1690046 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 6549 | 20211201 | 839 | 1556953 | 345 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 9 | 3105 | 38.6116 | -122.6578 | GRAMMER- MASON: 18302 hwy 128. calistoga | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0153506 | OH | Sus | 31579213 | No | 2021 | DEC | Yes | Line to Line | 1690350 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | MONTICELLO-1101 | 43051101 | RECLOSER | 37384 | 20211205 | 114 | 1559463 | 398 | Distribution Circuit | Equipment Failure/Involved | Overhead | 505 | 210729 | 38.4456 | -122.196 | POLE TO POLE NEAR 65047 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0155000 | OH | Sus | 31579722 | No | 2021 | DEC | Yes | Line to Ground | 1691476 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | BOLINAS-1101 | 42261101 | FUSE | 1303 | 20211216 | 654 | 1574382 | 853 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5118 | 37.9367 | -122.7033 | 3 SPANS LD SIDE OF 1303 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0158967 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1696011 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 605 | 20211217 | 2128 | 1576497 | 977 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 48850 | 38.1107 | -122.8716 | 555 VIA DELA VISTA | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0159509 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1696651 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | OTHER | 3431 | 20211219 | 931 | 1577308 | 173 | Distribution Circuit | Equipment Failure/Involved | Overhead | 336 | 57360 | 37.9762 | -122.6011 | S SPANS S/S OF FUCO 3619 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0159717 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1696921 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | RECLOSER | 257964 | 20211222 | 721 | 1578986 | 255 | Distribution Circuit | Equipment Failure/Involved | Overhead | 351 | 89505 | 38.5894 | -122.6078 | 5 SPANS LD SIDE OF 257964 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160098 | OH | Sus | 45099649 | No | 2021 | DEC | Yes | Line to Ground | 1697490 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 5429 | 20211223 | 1746 | 1580162 | 285 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 3705 | 37.9587 | -122.5584 | ACROSS FROM 44 CHESTNUT AVE | Clear-32-90 F | Other | Broken, wire on object | 21-0160334 | OH | Sus | 45100780 | No | 2021 | DEC | Yes | Force Out | 1697774 | NON | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | RECLOSER | 902 | 20220109 | 2107 | 1598983 | 1179 | Distribution Circuit | Vegetation | Tree - fell into line | 204 | 188161 | 37.8893 | -122.5549 | 5 SPANS LD SIDE OF 943 FUCO | Clear-32-90 F | Conductor, Overhead | On Ground | 22-0007828 | OH | Sus | 45118734 | No | 2022 | JAN | Yes | Line to Ground | 1701773 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | BOLINAS-1101 | 42261101 | FUSE | 1551 | 20220321 | 1626 | 1652924 | 521 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 6980 | 37.9443 | -122.7033 | 5 SPANS S/OF 1551 ( 5925 HWY1 ) | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 22-0036580 | OH | Sus | 31597917 | No | 2022 | MAR | Yes | Line to Ground | 1718792 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER | 726 | 20220411 | 1337 | 1668900 | 350 | Distribution Circuit | Vegetation | Tree - fell into line | 346 | 38678 | 38.6152 | -122.4292 | 2 SPANS E/O 218937337378 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0045544 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Ground | 1724621 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 4267 | 20220414 | 520 | 1672109 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3645 | 38.5841 | -122.6696 | 2 P LD SIDE OF 4267 FUCO ON BUCK GOING EAST | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0047876 | OH | Sus | 31601020 | No | 2022 | APR | Yes | Three Phase Fault | 1726457 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | OTHER | 3 PHASES WIRE DOWN 2 SPANS LD SIDE OF 87347 | 20220605 | 1644 | 1719696 | 507 | Distribution Circuit | Vegetation | Tree - fell into line | 354 | 106058 | 38.609 | -122.6552 | 2ND SPAN LD SIDE OF 87347 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0070354 | OH | Sus | 31605362 | No | 2022 | JUN | Yes | Line to Ground | 1741906 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 1117 | 20220617 | 106 | 1733556 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 14742 | 38.3727 | -122.4171 | 16 SPANS & 19 SPANS LD SIDE OF 1117 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0075392 | OH | Sus | 31606350 | No | 2022 | JUN | Yes | Line to Ground | 1745381 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 7341 | 20221005 | 1414 | 1829630 | 156 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 2340 | 38.5819 | -122.4422 | GRAMMER- MASON: 500 eastern ave. Angwin | Clear-32-90F | Conductor, Overhead | On Ground | 22-0118246 | OH | Sus | 45475529 | No | 2022 | OCT | Yes | Force Out | 1774345 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | BOLINAS-1101 | 42261101 | FUSE | 46819 | 20221114 | 1128 | 1862311 | 507 | Distribution Circuit | 3rd Party | Vehicle | 1 | 507 | 37.9382 | -122.7029 | 1 SOPAN LD SIDE OF C/OUTS 46819 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0130893 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Ground | 1783647 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | OLEMA-1101 | 42291101 | FUSE | 4235 | 20221227 | 252 | 1898098 | 706 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3530 | 38.0079 | -122.7054 | ANDREWS- KYLE: 7438 sir Francis drake blvd | Strong Winds-Heavy Rain-Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0141535 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1793211 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 1655 | 20221227 | 157 | 1897988 | 511 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 5621 | 38.0592 | -122.8378 | 1655 FUSES TO FIRST POLE LD SIDE | Strong Winds-Heavy Rain-Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 22-0141556 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793233 | CSO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1101 | 43021101 | FUSE | 2627 | 20221227 | 923 | 1898905 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 49760 | 38.0123 | -122.702 | DYDO- GREG 415-589-0425: C/O 5855 | Strong Winds-Heavy Rain-Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 22-0141634 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793317 | CAW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | FUSE | 1023 | 20230112 | 931 | 1949890 | 581 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1162 | 38.6733 | -122.5745 | 5 SPANS LD SIDE OF 1023 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0014404 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1803708 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 1763 | 20230123 | 115 | 1965248 | 535 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 4815 | 38.5929 | -122.4401 | at CGC 218738233925 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0019987 | OH | Sus | 31634983 | No | 2023 | JAN | Yes | Line to Ground | 1807420 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2102 | 43432102 | OTHER | WIRE DOWN 1 W/OF 856273 | 20230130 | 902 | 1971702 | 433 | Distribution Circuit | Equipment Failure/Involved | Overhead | 880 | 247492 | 38.5088 | -122.3421 | 63 HENNESSEY RIDGE RD- ST HELENA | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0022882 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1809152 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 1763 | 20230209 | 1140 | 1980920 | 600 | Distribution Circuit | 3rd Party | Vehicle | 9 | 5400 | 38.5929 | -122.4401 | 8 SPAN LD SIDE OF 1763 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0027136 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1811940 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | STAFFORD-1102 | 43201102 | RECLOSER | 1202 | 20230213 | 1044 | 1983567 | 279 | Distribution Circuit | Animal | Bird found | 53 | 9327 | 38.1221 | -122.6221 | WALTER- RYAN 510-965-3246: 3549 Novato Blvd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0028112 | OH | Sus | 31636709 | No | 2023 | FEB | Yes | Line to Line | 1812764 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2105 | 43432105 | FUSE | 5159 | 20230301 | 1344 | 2018390 | 321 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1926 | 38.5227 | -122.5465 | GRAMMER- MASON: 4013 spring mountain rd. Saint Helena | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0038287 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1820494 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | ALTO-1125 | 42031125 | JUMPER | HOT WIRE DWN @ 701 VIEW POINT RD | 20230305 | 111 | 2023088 | 602 | Distribution Circuit | Vegetation | Tree - fell into line | 959 | 50408 | 37.8778 | -122.5419 | at 701 VIEW POINT RD | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 23-0040197 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1821945 | CSO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1125 | 42031125 | FUSE | 915 | 20230310 | 200 | 2029900 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 64960 | 37.9041 | -122.5692 | 599 EDGEWOOD AVE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0042875 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1823633 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SAN RAFAEL-1107 | 42011107 | SWITCH | 327509 | 20230310 | 852 | 2030463 | 630 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6300 | 37.9547 | -122.557 | 1 SPAN LD SIDE OF SW 327509- TREE at 85 ROCK RD. | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0042839 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1823610 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | SILVERADO-2102 | 43432102 | RECLOSER | 636 | 20230316 | 641 | 2047670 | 84 | Distribution Circuit | 3rd Party | Vehicle | 131 | 7961 | 38.5089 | -122.4472 | 2/SPAN/S/OF/ SBCO 3089 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0046872 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1826476 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | BOLINAS-1101 | 42261101 | FUSE | 1551 | 20230328 | 813 | 2069689 | 825 | Distribution Circuit | 3rd Party | Vehicle | 12 | 9900 | 37.947 | -122.7059 | 2/P/LD SIDE OF 1551 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 23-0053391 | OH | Sus | 0 | No | 2023 | MAR | Yes | Multi-Fault | 1831081 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | FUSE | 1085 | 20230328 | 845 | 2069802 | 658 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 7238 | 37.9719 | -122.5758 | 5/SPANS LD SIDE OF 1085FUCO ON OAK AVE. | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0053362 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1831065 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER | 633600 | 20230408 | 451 | 2083014 | 866 | Distribution Circuit | 3rd Party | Vehicle | 346 | 210092 | 38.6152 | -122.4293 | 2491 HARNESS DR- POPE VALLEY | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0058729 | OH | Sus | 31641664 | No | 2023 | APR | Yes | Three Phase Fault | 1834168 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2103 | 43432103 | RECLOSER | 34959 | 20230411 | 956 | 2085320 | 600 | Distribution Circuit | Company Initiated | Contact with High Voltage- company | 209 | 71940 | 38.5068 | -122.374 | REG 8365 2 SPANS WEST & 1 SPAN EAST | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0059497 | OH | Sus | 0 | No | 2023 | APR | Yes | Line to Line | 1834846 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | PUEBLO-2103 | 43292103 | FUSE | 3343 | 20230604 | 804 | 2128338 | 330 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 9570 | 38.3613 | -122.371 | 4921 DRY CREEK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0078689 | OH | Sus | 0 | No | 2023 | JUN | Yes | Line to Ground | 1847800 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 857 | 20230606 | 1239 | 2130613 | 341 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 4774 | 38.0129 | -122.6455 | 4/SPAN/E/OF FUCO 857 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0079378 | OH | Sus | 0 | No | 2023 | JUN | Yes | Open Circuit | 1848400 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-2103 | 43292103 | FUSE | 1325 | 20230613 | 745 | 2135865 | 303 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 71 | 21513 | 38.3473 | -122.3554 | N/O 1325 FUCO DRY CREEK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0081792 | OH | Sus | 45846064 | No | 2023 | JUN | Yes | Line to Ground | 1850209 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1108 | 42011108 | OTHER | WIRE DOWN SS OF 314000654752 | 20230617 | 1056 | 2139280 | 527 | Distribution Circuit | Animal | Bird found | 3096 | 165152 | 37.9856 | -122.5829 | 60 PASTORI AVE.- FAIRFAX | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0083370 | OH | Sus | 45851647 | No | 2023 | JUN | Yes | Line to Ground | 1851326 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 2 | SILVERADO-2102 | 43432102 | RECLOSER | 58626 | 20230617 | 1308 | 2139324 | 637 | Distribution Circuit | Vegetation | Tree - fell into line | 345 | 91218 | 38.5072 | -122.4059 | 2350 LOWER CHILES VALLEY RD- ST HELENA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0083380 | OH | Sus | 31652615 | No | 2023 | JUN | Yes | Line to Ground | 1851334 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | WOODACRE-1101 | 43021101 | RECLOSER | 91900 | 20230626 | 1206 | 2146068 | 664 | Distribution Circuit | Equipment Failure/Involved | Overhead | 113 | 39961 | 38.055 | -122.6933 | 5730 NICASIO VALLEY RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0085627 | OH | Sus | 31653490 | No | 2023 | JUN | Yes | Line to Ground | 1853208 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | ALTO-1124 | 42031124 | OTHER | WIRE DOWN 209 CASCADE DR | 20230716 | 1444 | 2164324 | 227 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 2951 | 37.9079 | -122.5594 | 209 CASCADE DR.- MILL VALLEY | Partly Cloudy-Above 90 | Conductor, Overhead | Broken, wire on ground | 23-0092839 | OH | Sus | 45888828 | No | 2023 | JUL | Yes | Line to Ground | 1857873 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | RECLOSER | 806500 | 20230802 | 1028 | 2180509 | 540 | Distribution Circuit | Vegetation | Tree - fell into line | 1298 | 234377 | 38.574 | -122.4444 | 1 SP FROM CGC# 218968732422 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0099526 | OH | Sus | 45217866 | No | 2023 | AUG | Yes | Line to Ground | 1862453 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | CALISTOGA-1101 | 42711101 | RECLOSER | 257964 | 20230906 | 150 | 2210527 | 659 | Distribution Circuit | 3rd Party | Vehicle | 360 | 180756 | 38.5894 | -122.6078 | 3535 HWY 128 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0112881 | OH | Sus | 0 | No | 2023 | SEP | Yes | Line to Line | 1871426 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | JUMPER | WIRE DOWN LS OF 1739 FUCO | 20230923 | 903 | 2225327 | 584 | Distribution Circuit | Vegetation | Tree - fell into line | 795 | 49560 | 38.1033 | -122.8588 | WIRE DOWN LS OF 1739 FUCO | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0120035 | OH | Sus | 0 | No | 2023 | SEP | Yes | Line to Ground | 1876213 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | PUEBLO-1105 | 43291105 | RECLOSER | 696 | 20230930 | 251 | 2231183 | 915 | Distribution Circuit | 3rd Party | Vehicle | 282 | 147648 | 38.3705 | -122.3006 | CGC# 219183025565 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 23-0122816 | OH | Sus | 31670788 | No | 2023 | SEP | Yes | Line to Ground | 1878051 | PW | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | ALTO-1120 | 42031120 | RECLOSER | 1214 | 20231003 | 1257 | 2233795 | 33 | Distribution Circuit | Equipment Failure/Involved | Overhead | 578 | 19074 | 37.8784 | -122.5341 | 355 MARIN AVE- MILL VALLEY | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 23-0123858 | OH | Sus | 0 | No | 2023 | OCT | Yes | Line to Ground | 1878960 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SILVERADO-2104 | 43432104 | FUSE | 4569 | 20231120 | 821 | 2273937 | 579 | Distribution Circuit | 3rd Party | Vehicle | 2 | 1158 | 38.61 | -122.4306 | 1740 HOWELL MTN. RD. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0141244 | OH | Sus | 0 | No | 2023 | NOV | Yes | Open Circuit | 1891898 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 2 | SAN RAFAEL-1109 | 42011109 | FUSE | 5397 | 20231218 | 2244 | 2295214 | 243 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 7047 | 37.9781 | -122.5077 | 1 SP LD SIDE OF 687 TWD WEST | Overcast-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 23-0148018 | OH | Sus | 46095422 | No | 2023 | DEC | Yes | Line to Ground | 1898834 | CSO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | GREENBRAE-1102 | 43091102 | FUSE | 1802 | 20231219 | 329 | 2295271 | 699 | Distribution Circuit | Vegetation | Tree - fell into line | 252 | 54040 | 37.9528 | -122.5377 | 393 LOS CERROS DR | Overcast-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 23-0148033 | OH | Sus | 31679814 | No | 2023 | DEC | Yes | Line to Ground | 1898850 | CSO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | GREENBRAE-1102 | 43091102 | FUSE | 3157 | 20231220 | 623 | 2296186 | 293 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 27249 | 37.952 | -122.5352 | JANCA- MARK 831-333-6009: Rear of 115 Corte Anita | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0148205 | OH | Sus | 31679946 | No | 2023 | DEC | Yes | Line to Ground | 1899076 | CO | OH | No | No
NORTH BAY | FIELD OPS NORTH | Tier 3 | SAN RAFAEL-1107 | 42011107 | FUSE | 2565 | 20231220 | 1558 | 2296814 | 349 | Distribution Circuit | Vegetation | Tree - branch fell on line | 157 | 28393 | 37.9595 | -122.5348 | PRIM WIRE 2 SPANS SOURCE SIDE OF FUCO 4475 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0148304 | OH | Sus | 46097847 | No | 2023 | DEC | Yes | Line to Ground | 1899241 | CO | OH | No | Yes
NORTH BAY | FIELD OPS NORTH | Tier 3 | WOODACRE-1102 | 43021102 | FUSE | 2647 | 20231228 | 13 | 2301003 | 840 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 81480 | 37.9958 | -122.5988 | 1 SPAN PAST 2647 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0149077 | OH | Sus | 46102449 | No | 2023 | DEC | Yes | Line to Ground | 1900256 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1102 | 103521102 | RECLOSER | 49144 | 20130101 | 1302 | 724095 | 513 | Distribution Circuit | Vegetation | Tree - fell into line | 554 | 31202 | 40.6598 | -122.3418 | 1 W/OF MTR 1006191288 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0001550 | OH | Sus | 30968710 | No | 2013 | JAN | Yes |  | 99306207 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 1-1101 | 103721101 | RECLOSER | 9702 | 20130113 | 738 | 729291 | 250 | Distribution Circuit | Equipment Failure/Involved | Other | 205 | 37688 | 41.0047 | -121.4471 | ON MAIN LINE SS OF MTR 1008049116 | Combination wind/rain/lightning-32 - 90 F | PGs, Kearneys | Broken, wire on ground | 13-0003877 | OH | Sus | 0 | No | 2013 | JAN | Yes | Line to Line | 99304758 | PGK | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1102 | 102541102 | RECLOSER | 1502 | 20130114 | 643 | 729579 | 261 | Distribution Circuit | Vegetation | Tree - fell into line | 1480 | 371575 | 40.4946 | -121.8729 | GERRARD/1324: s/s of fco 7683 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0003932 | OH | Sus | 41840261 | No | 2013 | JAN | Yes |  | 99304694 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ORO FINO-1102 | 103031102 | FUSE | 3369 | 20130119 | 1323 | 731870 | 1372 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4116 | 39.9351 | -121.6464 | MTR#86K899 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0005186 | OH | Sus | 41842671 | No | 2013 | JAN | Yes |  | 99303973 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 850239 | 20130123 | 1820 | 733416 | 195 | Distribution Circuit | Environmental/External | Ice or snow | 35 | 6825 | 40.3481 | -121.5961 | MASON/1373: broken side post insolator | Rain-32 - 90 F | Insulator | Broken, wire on object | 13-0005787 | OH | Sus | 30972760 | No | 2013 | JAN | Yes | None | 99303594 | INS | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1104 | 103521104 | OCB | OCB | 20130124 | 707 | 733689 | 359 | Distribution Circuit | 3rd Party | Vehicle | 2457 | 199143 | 40.619 | -122.3224 | 1S W/OF FUCO 9595 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0005808 | OH | Sus | 41844196 | No | 2013 | JAN | Yes | Multi-Fault | 99303564 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | FUSE | 2935 | 20130129 | 911 | 735973 | 549 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3294 | 40.1325 | -120.9563 | 8 SPANS LD SIDE OF TAP TO MTR 1003173629 | Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0006751 | OH | Sus | 0 | No | 2013 | JAN | Yes | Three Phase Fault | 99302884 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WILDWOOD-1101 | 103611101 | FUSE | 6051 | 20130129 | 649 | 735848 | 1166 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5668 | 40.3676 | -122.9711 | AT EOL PAST LCO 6051 | Rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0006764 | OH | Sus | 30974037 | No | 2013 | JAN | Yes | Line to Line | 99302880 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1105 | 102911105 | FUSE | 1461 | 20130213 | 1435 | 741789 | 397 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 22232 | 39.6487 | -121.4094 | 3 P PAST LCO 1461 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0009889 | OH | Sus | 30977226 | No | 2013 | FEB | Yes | Line to Ground | 99301001 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 1935 | 20130227 | 1011 | 748365 | 1161 | Distribution Circuit | Vegetation | Tree - fell into line | 742 | 196616 | 40.3484 | -121.6304 | 1ST SPAN LD SIDE FUCO 1935 | Overcast-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0012918 | OH | Sus | 30980025 | No | 2013 | FEB | Yes | Line to Ground | 99298800 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1105 | 102911105 | FUSE | 2715 | 20130305 | 2348 | 752120 | 821 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 37766 | 39.7836 | -121.5056 | .25 MI LD SIDE OF FUCO 2715 ON HOFFMAN RD | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0014424 | OH | Sus | 0 | yes | 2013 | MAR | Yes | Line to Line | 99297882 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER | 2476 | 20130306 | 530 | 752411 | 1018 | Distribution Circuit | Vegetation | Tree - fell into line | 1355 | 531417 | 40.1713 | -121.0879 | at MTR 1008574510 & at POLE 15/13 | Snow-Below 32 F | Conductor, Overhead | Broken, wire on object | 13-0014481 | OH | Sus | 0 | yes | 2013 | MAR | Yes |  | 99297848 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | OTHER |  | 20130306 | 124 | 752199 | 1036 | Distribution Circuit | Vegetation | Tree - fell into line | 741 | 282910 | 40.3486 | -121.6288 | MTR# 1009363641 AND 1 SPAN N/0F 850251 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0014446 | OH | Sus | 0 | yes | 2013 | MAR | Yes | Line to Ground | 99297871 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE | 5427 | 20130306 | 619 | 752416 | 289 | Distribution Circuit | Equipment Failure/Involved | Other | 20 | 5780 | 39.5932 | -121.445 | 1 P PAST LCO | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0014488 | OH | Sus | 0 | yes | 2013 | MAR | Yes | Line to Ground | 99297844 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1105 | 102911105 | FUSE | 1497 | 20130320 | 902 | 759282 | 550 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 3845 | 39.6553 | -121.4599 | 1/2 WAY BETWEEN 1497 AND EOL | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0017958 | OH | Sus | 30984387 | No | 2013 | MAR | Yes |  | 99295530 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | OCB | OCB | 20130326 | 648 | 761684 | 285 | Distribution Circuit | Animal | Bird found | 2410 | 320333 | 39.3877 | -121.4031 | AT FUCO 13511 ON MAIN LINE | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 13-0019091 | OH | Sus | 41873370 | No | 2013 | MAR | Yes | Line to Line | 99294692 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | OTHER |  | 20130328 | 1704 | 763039 | 163 | Distribution Circuit | Equipment Failure/Involved | Other | 753 | 94955 | 39.3899 | -121.4042 | MTR# 1009396915 | Overcast-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0019855 | OH | Sus | 0 | No | 2013 | MAR | Yes |  | 99294185 | CSO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1103 | 102911103 | RECLOSER | 1504 | 20130413 | 1745 | 774268 | 537 | Distribution Circuit | Equipment Failure/Involved | Other | 1670 | 53670 | 39.5045 | -121.4985 | 1 SPAN NORTH OF MTR#1009395523 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0024228 | OH | Sus | 0 | No | 2013 | APR | Yes |  | 99290776 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WHITMORE-1101 | 103601101 | RECLOSER | 1598 | 20130421 | 1509 | 779006 | 769 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 174 | 83010 | 40.6205 | -121.9334 | 1 WEST & 1 NORTH OF 7655 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0026112 | OH | Sus | 30990934 | No | 2013 | APR | Yes |  | 99289300 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | SYCAMORE CREEK-1111 | 102971111 | RECLOSER | 2014 | 20130430 | 712 | 783806 | 321 | Distribution Circuit | Equipment Failure/Involved | Other | 540 | 145254 | 39.8315 | -121.8441 | 2ND SPAN LD SIDE OF 16859 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0028155 | OH | Sus | 41890796 | yes | 2013 | APR | Yes |  | 99287822 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1105 | 102911105 | RECLOSER | 1972 | 20130430 | 2114 | 784489 | 322 | Distribution Circuit | Vegetation | Tree - fell into line | 264 | 85008 | 39.6446 | -121.4314 | WOODMANSEE/1206: tree top broke pole-10381 oro quincy hwy | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0028455 | OH | Sus | 0 | yes | 2013 | APR | Yes | Multi-Fault | 99287624 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1101 | 103401101 | FUSE | 9409 | 20130501 | 1028 | 785054 | 473 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 3844 | 40.5211 | -122.478 | MTR# 5M0570 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0028615 | OH | Sus | 30993625 | yes | 2013 | MAY | Yes | Line to Ground | 99287450 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2600 | 20130501 | 1933 | 785465 | 406 | Distribution Circuit | Equipment Failure/Involved | Other | 380 | 58497 | 39.8871 | -121.6657 | HOWARD/2603: mtr. 1009068357 nopel and hwy 32 | Clear-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 13-0028760 | OH | Sus | 30993772 | yes | 2013 | MAY | Yes |  | 99287372 | CAW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 5713 | 20130501 | 803 | 784864 | 737 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 19162 | 40.3518 | -121.5822 | 1 SPAN LD SIDE OF FUCO 5713 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0028618 | OH | Sus | 30993620 | yes | 2013 | MAY | Yes |  | 99287447 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1101 | 103401101 | FUSE | 9409 | 20130504 | 1808 | 787013 | 629 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 7052 | 40.5211 | -122.478 | MTR 5M0570 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0029509 | OH | Sus | 0 | yes | 2013 | MAY | Yes | Open Circuit | 99286765 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 17245 | 20130520 | 650 | 795161 | 790 | Distribution Circuit | Vegetation | Tree - fell into line | 122 | 90209 | 39.7575 | -121.5822 | 2 SPANS S/OF 17237 at FUSE POLE 17235 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0032895 | OH | Sus | 30997441 | No | 2013 | MAY | Yes | Line to Line | 99284331 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1101 | 103401101 | RECLOSER | 1330 | 20130522 | 232 | 796422 | 466 | Distribution Circuit | Vegetation | Tree - fell into line | 418 | 76830 | 40.5176 | -122.5056 | 2 SPANS W/OF TAP LINE FEEDING MTR 57B179 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0033485 | OH | Sus | 30997775 | No | 2013 | MAY | Yes | Open Circuit | 99283954 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 27099 | 20130602 | 645 | 802439 | 488 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 488 | 39.7405 | -121.6074 | 1ST SPAN LD SIDE OF 27099 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0035917 | OH | Sus | 31000252 | No | 2013 | JUN | Yes |  | 99282266 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 1571 | 20130608 | 225 | 806038 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 10860 | 39.7523 | -121.6008 | MTR 1007887494 | Heat wave-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0037665 | OH | Sus | 31001477 | yes | 2013 | JUN | Yes | Line to Ground | 99281276 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 5185 | 20130625 | 1222 | 816980 | 568 | Distribution Circuit | Vegetation | Tree - branch fell on line | 90 | 38708 | 39.7777 | -121.5957 | CHRISTENSEN/2698: on herman/pri tech has info | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0042535 | OH | Sus | 31005230 | yes | 2013 | JUN | Yes | Line to Line | 99277975 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1101 | 103351101 | RECLOSER | 1380 | 20130706 | 519 | 826719 | 662 | Distribution Circuit | 3rd Party | Vehicle | 584 | 227416 | 40.5608 | -122.1889 | FUCO POLE 2861 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0045509 | OH | Sus | 31007079 | No | 2013 | JUL | Yes |  | 99275576 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1101 | 103401101 | FUSE | 6355 | 20130717 | 524 | 832794 | 292 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 4964 | 40.5305 | -122.4751 | 8426 Rockland Way- Redding | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0047915 | OH | Sus | 31009132 | No | 2013 | JUL | Yes |  | 99273861 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | RECLOSER | 9072 | 20130720 | 755 | 835282 | 497 | Distribution Circuit | 3rd Party | Vehicle | 281 | 107518 | 40.3378 | -122.3718 | 1 S/OF 1355 | Clear-32 - 90 F | Pole-Wood | Broken, wire on object | 13-0048818 | OH | Sus | 0 | No | 2013 | JUL | Yes | Multi-Fault | 99273252 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1101 | 103031101 | FUSE | 27225 | 20130813 | 1153 | 847717 | 377 | Distribution Circuit | Equipment Failure/Involved | Other | 48 | 18096 | 39.8568 | -121.6072 | MTR# 1007694869 | Clear-32 - 90 F | Other | Broken, wire on object | 13-0054293 | OH | Sus | 41942806 | No | 2013 | AUG | Yes | Line to Ground | 99269563 | NON | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 11151 | 20130814 | 301 | 848002 | 424 | Distribution Circuit | 3rd Party | Vehicle | 47 | 12800 | 40.564 | -122.2884 | FUCO 11575 FUSE POLE- WIRE DOWN ON TOP OF VEHICLE - 1 SPAN N/OF FUCO 11575 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0054433 | OH | Sus | 31014681 | No | 2013 | AUG | Yes | Line to Ground | 99269483 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CORNING-1102 | 103331102 | RECLOSER | 53184 | 20130820 | 1347 | 852798 | 771 | Distribution Circuit | Vegetation | Tree - branch fell on line | 216 | 58180 | 39.9134 | -122.4298 | LD SIDE SBCO 850217 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0056167 | OH | Sus | 0 | yes | 2013 | AUG | Yes |  | 99268093 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1101 | 103351101 | RECLOSER | 1654 | 20130825 | 1604 | 855422 | 465 | Distribution Circuit | Vegetation | Tree - fell into line | 178 | 43312 | 40.5018 | -122.0408 | 27108 DERSCH RD- SHINGLETOWN- CA | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0057347 | OH | Sus | 31017055 | No | 2013 | AUG | Yes | Line to Line | 99267208 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ANTLER-1101 | 103271101 | FUSE | 5137 | 20130902 | 1016 | 859324 | 270 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 6 | 2334 | 40.8599 | -122.3482 | Just to the north side of Trail IN RV Park and Store (on edge of part) | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0059126 | OH | Sus | 41949750 | yes | 2013 | SEP | Yes | Line to Ground | 99266082 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 1599 | 20130902 | 1341 | 859484 | 352 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 15303 | 39.7377 | -121.5951 | on hard tap 1 SP W/OF 1599 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0059147 | OH | Sus | 31018628 | yes | 2013 | SEP | Yes | Line to Line | 99266063 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1106 | 102831106 | FUSE | 17967 | 20130903 | 1737 | 860224 | 617 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 9255 | 39.8003 | -121.6019 | LOC 1) MTR# 1007905150 LOC2) MTR# 1008143938 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0059528 | OH | Sus | 31018966 | No | 2013 | SEP | Yes | Line to Line | 99265825 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1109 | 102911109 | FUSE | 13941 | 20130903 | 150 | 859778 | 432 | Distribution Circuit | 3rd Party | Vehicle | 130 | 5984 | 39.458 | -121.5085 | FUCO POLE 13481 | Overcast-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0059228 | OH | Sus | 31018537 | No | 2013 | SEP | Yes | Three Phase Fault | 99265967 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE | 3177 | 20130908 | 1632 | 862809 | 1444 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 46 | 59584 | 40.6665 | -122.4015 | 6 POLES BEYOND FUSES 3177 | Clear-Above 90 F | Pole-Wood | Broken, wire on ground | 13-0060552 | OH | Sus | 31019814 | No | 2013 | SEP | Yes | Line to Ground | 99264990 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1104 | 103351104 | FUSE | 3719 | 20130912 | 11 | 864864 | 301 | Distribution Circuit | Vegetation | Tree - branch fell on line | 160 | 38850 | 40.5188 | -122.2385 | 2 N/OF MTR 39L429 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0061429 | OH | Sus | 41954694 | No | 2013 | SEP | Yes | Line to Ground | 99264394 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1102 | 103561102 | FUSE | 53979 | 20130925 | 1619 | 873204 | 277 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 2770 | 40.6815 | -122.3412 | 3 SPANS N/OF FUCO 63979 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0064828 | OH | Sus | 41964345 | No | 2013 | SEP | Yes | Line to Line | 99261856 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 79226 | 20130928 | 1010 | 874782 | 293 | Distribution Circuit | Equipment Failure/Involved | Other | 1122 | 294256 | 39.5151 | -121.2642 | MTR #1007885936 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0065536 | OH | Sus | 41965529 | No | 2013 | SEP | Yes | Line to Ground | 99261326 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 1283 | 20130929 | 1345 | 875175 | 657 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 50597 | 39.7667 | -121.6267 | 2 SPANS LD SIDE OF MTR #1008801919 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0065643 | OH | Sus | 31024953 | No | 2013 | SEP | Yes | Line to Ground | 99261221 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | FUSE | 3307 | 20131008 | 1059 | 881231 | 350 | Distribution Circuit | 3rd Party | Customer Equipment | 77 | 10086 | 40.7163 | -122.3318 | 1 SPAN E/OF MTR 65B539 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0068068 | OH | Sus | 0 | No | 2013 | OCT | Yes | Line to Ground | 99259529 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 1943 | 20131015 | 1406 | 885193 | 361 | Distribution Circuit | Equipment Failure/Involved | Other | 75 | 25611 | 39.5156 | -121.2642 | SPAN FROM 689 TWD 1943- MTR 1007486069 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0069777 | OH | Sus | 41973774 | No | 2013 | OCT | Yes | Line to Ground | 99258259 | CSO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RISING RIVER-1101 | 103551101 | RECLOSER | 1530 | 20131027 | 1452 | 890906 | 695 | Distribution Circuit | Vegetation | Tree - fell into line | 535 | 286989 | 40.8719 | -121.5543 | DOTY RD AND LONQUIST- 5 P PAST SBCO 705 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0072402 | OH | Sus | 31031551 | yes | 2013 | OCT | Yes | Multi-Fault | 99256458 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 1851 | 20131119 | 421 | 904296 | 546 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 14742 | 39.419 | -121.3686 | 194 DARBY RD- MTR 1008144064 | Rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0076888 | OH | Sus | 31036819 | yes | 2013 | NOV | Yes | Line to Line | 99252852 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WHITMORE-1101 | 103601101 | OTHER |  | 20131203 | 1425 | 918699 | 640 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 11350 | 40.6807 | -121.8828 | 1 SPAN SS OF TRANSF FEEDING MTR# 1009768749 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0080393 | OH | Sus | 42039135 | yes | 2013 | DEC | Yes | Line to Ground | 99249760 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANDERSON-1103 | 103261103 | OTHER |  | 20131206 | 2327 | 921447 | 353 | Distribution Circuit | Equipment Failure/Involved | Other | 30 | 4424 | 40.4776 | -122.2629 | 21318 VERONA | Fog-32 - 90 F | Connector or Splice (OH) | Broken, wire on object | 13-0081099 | OH | Sus | 42042384 | yes | 2013 | DEC | Yes |  | 99249138 | CSO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1103 | 102831103 | RECLOSER | 2488 | 20131209 | 642 | 923980 | 1150 | Distribution Circuit | Vegetation | Tree - fell into line | 905 | 163548 | 39.7411 | -121.6275 | MTR# 1007693730 / FUCO 1549 / 1 W/OF 2488 | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 13-0081514 | OH | Sus | 31041294 | No | 2013 | DEC | Yes | Three Phase Fault | 99248664 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | OTHER |  | 20140101 | 218 | 936141 | 724 | Distribution Circuit | Vegetation | Tree - fell into line | 1077 | 287559 | 39.8706 | -121.623 | approximately 15 spans load side of 2236 | Partly cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 14-0001756 | OH | Sus | 42052094 | No | 2014 | JAN | Yes | Line to Ground | 99245632 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | NOTRE DAME-1104 | 102041104 | RECLOSER | 2028 | 20140123 | 1104 | 945954 | 464 | Distribution Circuit | Vegetation | Tree - fell into line | 130 | 12188 | 39.8401 | -121.7023 | 1 SPAN N/O R 52 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0005837 | OH | Sus | 0 | yes | 2014 | JAN | Yes | Line to Ground | 99243208 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2236 | 20140123 | 1332 | 946130 | 228 | Distribution Circuit | Vegetation | Tree - fell into line | 1077 | 104224 | 39.8719 | -121.6118 | MAIOCCO- MARTY: AT METER NUMBER 1007696273 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 14-0005932 | OH | Sus | 42064648 | yes | 2014 | JAN | Yes | Line to Ground | 99243160 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1103 | 102831103 | FUSE | 17447 | 20140123 | 624 | 945720 | 687 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 12366 | 39.7657 | -121.6263 | 3 SPANS LD SIDE OF 17447 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0005753 | OH | Sus | 31051288 | yes | 2014 | JAN | Yes | Line to Ground | 99243284 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1102 | 103441102 | FUSE | 10235 | 20140125 | 2342 | 948011 | 473 | Distribution Circuit | 3rd Party | Vehicle | 1402 | 27938 | 40.4401 | -122.3405 | LCO 10235 POLE | Clear-32 - 90 F | Pole-Wood | Broken, wire on object | 14-0006429 | OH | Sus | 31052262 | No | 2014 | JAN | Yes | Line to Ground | 99242738 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 11585 | 20140207 | 2120 | 962259 | 950 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 6650 | 40.5632 | -122.2809 | S/OF OLD 44 DRIVE - MTR 1006234807 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on object | 14-0009780 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Ground | 99240814 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | RECLOSER | 2268 | 20140207 | 1412 | 961473 | 300 | Distribution Circuit | Vegetation | Tree - fell into line | 301 | 23024 | 39.9034 | -121.742 | CORNER OF COHASSET & ECUA MISSION LN | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0009654 | OH | Sus | 42073068 | yes | 2014 | FEB | Yes | Line to Ground | 99240972 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1103 | 102831103 | FUSE | 17667 | 20140210 | 1037 | 965010 | 278 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 3892 | 39.7507 | -121.6266 | 4 SPANS LD SIDE OF FUCO 17667 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0010345 | OH | Sus | 31055818 | yes | 2014 | FEB | Yes | Line to Ground | 99240295 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1102 | 102831102 | FUSE | 1239 | 20140211 | 1207 | 965917 | 804 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 6796 | 39.7654 | -121.5745 | 1 SP W/OF METER#1008143534 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0010667 | OH | Sus | 31056160 | No | 2014 | FEB | Yes | Line to Ground | 99239985 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1105 | 102911105 | FUSE | 1461 | 20140211 | 1046 | 965842 | 500 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 28000 | 39.6487 | -121.4093 | MTR 1007695314 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0010654 | OH | Sus | 42076041 | No | 2014 | FEB | Yes |  | 99240067 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | RECLOSER | 1804 | 20140302 | 1025 | 976909 | 323 | Distribution Circuit | 3rd Party | Vehicle | 425 | 87563 | 39.3899 | -121.4042 | MAIN LINE 1 LD SIDE OF 705 | Drizzle-32 - 90 F | Pole-Wood | Broken, wire on object | 14-0014887 | OH | Sus | 42085014 | No | 2014 | MAR | Yes | Line to Ground | 99237081 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1105 | 102911105 | FUSE | 13575 | 20140304 | 1036 | 978374 | 318 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 6472 | 39.6483 | -121.4027 | MAYS- SEAN: TREE FELL INTO AWAC AND PHONE PUTTING STRESS ON POLE AND BREAKING #6 COPPER | Partly cloudy-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0015353 | OH | Sus | 42086699 | No | 2014 | MAR | Yes | Line to Ground | 99236759 | CSO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CEDAR CREEK-1101 | 103321101 | OTHER |  | 20140306 | 1226 | 980028 | 298 | Distribution Circuit | Environmental/External | Lightning | 474 | 122518 | 40.8485 | -121.91 | 1 W/OF MTR #5000101432 ON MAIN LINE | Lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0016224 | OH | Sus | 0 | yes | 2014 | MAR | Yes | Line to Ground | 99236235 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | EAST QUINCY-1101 | 102551101 | OTHER | 52664 | 20140309 | 307 | 981065 | 411 | Distribution Circuit | Equipment Failure/Involved | Other | 2254 | 156487 | 39.9347 | -120.9257 | 3 SPANS E/OF CAP BK 462 | Overcast-32 - 90 F | Jumper | Broken, wire on ground | 14-0016732 | OH | Sus | 42088888 | No | 2014 | MAR | Yes | Line to Ground | 99235858 | JMP | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 1847 | 20140312 | 240 | 982880 | 234 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 4592 | 39.3901 | -121.4098 | 12 SPANS LD SIDE OF 23185 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0017407 | OH | Sus | 42091066 | yes | 2014 | MAR | Yes | Line to Line | 99235358 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | FRENCH GULCH-1102 | 103381102 | FUSE | 3055 | 20140317 | 358 | 985497 | 547 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4376 | 40.653 | -122.5574 | 13 POLES NORTH OF FUCO 3055 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0018456 | OH | Sus | 31063385 | No | 2014 | MAR | Yes | Line to Ground | 99234580 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 7043 | 20140320 | 1452 | 987470 | 366 | Distribution Circuit | Equipment Failure/Involved | Other | 18 | 6588 | 40.6216 | -122.2695 | MTR# 1006284270 | Clear-32 - 90 F | Insulator | Broken, wire on ground | 14-0019512 | OH | Sus | 31064442 | No | 2014 | MAR | Yes | Line to Ground | 99233947 | INS | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1103 | 102831103 | FUSE | 7007 | 20140326 | 530 | 989798 | 287 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 5166 | 39.7372 | -121.6429 | 1ST SPAN LD SIDE FUCO 7007 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0020508 | OH | Sus | 42098074 | yes | 2014 | MAR | Yes | Line to Ground | 99233198 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1103 | 102831103 | FUSE | 17681 | 20140329 | 1212 | 991373 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4400 | 39.7327 | -121.6364 | L&B 4 SPANS E/OF FUCO 17681 | Drizzle-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0021406 | OH | Sus | 31066070 | yes | 2014 | MAR | Yes | Line to Line | 99232643 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1101 | 103351101 | RECLOSER | 1380 | 20140331 | 1552 | 992710 | 391 | Distribution Circuit | 3rd Party | Vehicle | 582 | 156859 | 40.5608 | -122.1889 | MTR 5000016513- 23827 OLD 44- MILLVILLE | Rain-32 - 90 F | Pole-Wood | Broken, wire on object | 14-0021901 | OH | Sus | 31066482 | yes | 2014 | MAR | Yes | Line to Line | 99232183 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1101 | 103401101 | RECLOSER | 9732 | 20140331 | 358 | 992145 | 487 | Distribution Circuit | 3rd Party | Vehicle | 494 | 66174 | 40.521 | -122.4784 | 1 POLE SS OF C/OUT 4371 | Fog-32 - 90 F | Pole-Wood | Broken, wire on object | 14-0021608 | OH | Sus | 31066233 | yes | 2014 | MAR | Yes | Line to Line | 99232403 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1105 | 102911105 | RECLOSER | 1702 | 20140331 | 1628 | 992751 | 429 | Distribution Circuit | Equipment Failure/Involved | Other | 301 | 118147 | 39.7405 | -121.4961 | 1 W/OF MTR #100910642 | Lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0021926 | OH | Sus | 42100392 | yes | 2014 | MAR | Yes | Line to Ground | 99232254 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 1151 | 20140426 | 110 | 1004925 | 420 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2520 | 39.7776 | -121.6192 | MTR 1009291981 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0027467 | OH | Sus | 31071821 | yes | 2014 | APR | Yes | Line to Ground | 99228587 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1102 | 102931102 | FUSE | 5997 | 20140428 | 1310 | 1005834 | 230 | Distribution Circuit | 3rd Party | Vehicle | 31 | 1040 | 40.388 | -122.4589 | LYTLE/1959: 3306 WESTHO TRL CTWD | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on object | 14-0027797 | OH | Sus | 31072162 | No | 2014 | APR | Yes | None | 99228252 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 547 | 20140518 | 711 | 1020264 | 809 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3236 | 39.4408 | -121.3418 | MTR 1007888632 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0032675 | OH | Sus | 31077010 | No | 2014 | MAY | Yes |  | 99225096 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 547 | 20140519 | 1607 | 1021001 | 643 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 4 | 2572 | 39.4408 | -121.3418 | IN FIRST 2 SPANS LD SIDE OF FUCO 547 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0032987 | OH | Sus | 31077286 | yes | 2014 | MAY | Yes |  | 99224857 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER | 2260 | 20140520 | 825 | 1021343 | 487 | Distribution Circuit | 3rd Party | Vehicle | 958 | 61946 | 40.156 | -120.9429 | TRANSFORMER POLE MTR# 1008300854 | Overcast-Below 32 F | Pole-Wood | Broken, wire on ground | 14-0033102 | OH | Sus | 31077334 | No | 2014 | MAY | Yes | Line to Ground | 99224738 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CEDAR CREEK-1101 | 103321101 | FUSE | 5855 | 20140530 | 446 | 1026202 | 506 | Distribution Circuit | 3rd Party | Vehicle | 22 | 8902 | 40.7523 | -121.9561 | 18 POLES LD SIDE OF FUCO 5855 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0035141 | OH | Sus | 31079271 | No | 2014 | MAY | Yes | Line to Ground | 99223368 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1102 | 102931102 | FUSE | 2625 | 20140605 | 1247 | 1029043 | 254 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 594 | 40.3981 | -122.522 | 1 SPAN LD SIDE OF MTR 1009792312 | Clear-Above 90 F | Conductor, Overhead | Broken, wire on ground | 14-0036391 | OH | Sus | 42134545 | No | 2014 | JUN | Yes | Line to Ground | 99222469 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 13011 | 20140615 | 2220 | 1035041 | 574 | Distribution Circuit | 3rd Party | Vehicle | 23 | 2994 | 39.3849 | -121.4668 | 6 POLES SOURCE SIDE OF TRANSF FEEDING MTR# 1007772374 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on object | 14-0038503 | OH | Sus | 31082769 | No | 2014 | JUN | Yes | Line to Ground | 99220908 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER | 5460 | 20140704 | 1316 | 1044466 | 636 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 448 | 284928 | 39.5446 | -121.1476 | 1 W/OF MTR# 1007923734 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0042545 | OH | Sus | 31086949 | No | 2014 | JUL | Yes | Line to Line | 99218068 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 17343 | 20140705 | 2317 | 1045061 | 376 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 33840 | 39.8292 | -121.6207 | 6 POLES S/OF FUCO 7095 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0042693 | OH | Sus | 31087005 | No | 2014 | JUL | Yes | Line to Ground | 99217975 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CEDAR CREEK-1101 | 103321101 | OTHER |  | 20140712 | 1952 | 1048421 | 1150 | Distribution Circuit | Vegetation | Tree - fell into line | 203 | 53440 | 40.7786 | -121.9943 | 6 SPANS E/OF MTR 5000068877 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0044102 | OH | Sus | 42153522 | No | 2014 | JUL | Yes |  | 99216955 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1105 | 102831105 | FUSE | 1293 | 20140713 | 1218 | 1048594 | 248 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 1984 | 39.7952 | -121.5791 | 1 SPAN LD SIDE OF FUSES | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0044136 | OH | Sus | 42153545 | No | 2014 | JUL | Yes | Line to Line | 99216918 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 1305 | 20140720 | 1037 | 1052330 | 303 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 5577 | 39.7702 | -121.6208 | MTR# 1008909388 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0045658 | OH | Sus | 31089897 | yes | 2014 | JUL | Yes | Line to Ground | 99215885 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RISING RIVER-1101 | 103551101 | RECLOSER | 9032 | 20140801 | 2000 | 1059734 | 4357 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 553 | 479529 | 40.7802 | -121.5028 | HWY 89 & WILCOX ROAD/ MULTIPLE ON TAP S/OF LR 1530 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0048674 | OH | Sus | 31092553 | yes | 2014 | AUG | Yes | Line to Ground | 99213466 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KESWICK-1101 | 103451101 | OTHER |  | 20140802 | 1320 | 1060002 | 670 | Distribution Circuit | Vegetation | Tree - fell into line | 783 | 31650 | 40.6184 | -122.4797 | AT HARD TAP FEEDING MTR 1009638101 | Clear-Above 90 F | Conductor, Overhead | Broken, wire on ground | 14-0048745 | OH | Sus | 31092613 | No | 2014 | AUG | Yes | Line to Ground | 99213734 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1101 | 102931101 | RECLOSER | 68190 | 20140815 | 2233 | 1067161 | 705 | Distribution Circuit | Vegetation | Tree - fell into line | 467 | 147050 | 40.3648 | -122.4062 | 8 SPANS LD SIDE OF SBCO 2347 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0051310 | OH | Sus | 31095253 | No | 2014 | AUG | Yes | Line to Line | 99211878 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 1571 | 20140901 | 2249 | 1075859 | 285 | Distribution Circuit | Vegetation | Tree - fell into line | 103 | 27710 | 39.7523 | -121.6008 | BETWEEN 4527 AND METER # 1007909326 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0054449 | OH | Sus | 31098286 | No | 2014 | SEP | Yes |  | 99209630 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 1355 | 20140914 | 121 | 1080984 | 550 | Distribution Circuit | Vegetation | Tree - branch fell on line | 45 | 24750 | 39.7776 | -121.6229 | MTR 1007886826 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0056823 | OH | Sus | 31101083 | No | 2014 | SEP | Yes | Line to Line | 99208059 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 1355 | 20140925 | 839 | 1087614 | 397 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 11385 | 39.7776 | -121.6229 | MTR# 1009723532- 17139 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0059245 | OH | Sus | 0 | yes | 2014 | SEP | Yes | Line to Line | 99206362 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 1849 | 20140929 | 2316 | 1090496 | 374 | Distribution Circuit | 3rd Party | Vehicle | 148 | 55352 | 39.3847 | -121.4089 | 8TH POLE S/OF 1849 | Clear-32 - 90 F | Pole-Wood | Broken, wire on object | 14-0060342 | OH | Sus | 0 | No | 2014 | SEP | Yes | None | 99205624 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1102 | 102831102 | FUSE | 2755 | 20140930 | 1030 | 1090707 | 213 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 56 | 3348 | 39.7585 | -121.5738 | HARD TAP AT TRANSF FEEDING MTR# 1007771609 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0060424 | OH | Sus | 0 | No | 2014 | SEP | Yes | None | 99205525 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CENTERVILLE-1101 | 102021101 | FUSE | 6389 | 20141015 | 215 | 1097439 | 645 | Distribution Circuit | 3rd Party | Vehicle | 27 | 17415 | 39.7611 | -121.6773 | 12738 CENTERVILLE RD | Overcast-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0063686 | OH | Sus | 0 | yes | 2014 | OCT | Yes | Three Phase Fault | 99203506 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER | 2510 | 20141025 | 201 | 1102044 | 859 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2067 | 40.2105 | -121.1643 | 11 SPANS N/OF 18175 SBCO | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0065899 | OH | Sus | 0 | yes | 2014 | OCT | Yes | Three Phase Fault | 99202178 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1102 | 103521102 | RECLOSER | 1382 | 20141025 | 1435 | 1102703 | 235 | Distribution Circuit | Vegetation | Tree - fell into line | 242 | 32387 | 40.6539 | -122.3335 | 1 SP E/OF 7157 SBCO PORTERO & PASO ROBLES. | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0066054 | OH | Sus | 0 | yes | 2014 | OCT | Yes | Three Phase Fault | 99202042 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 3-2101 | 103732101 | RECLOSER | 1482 | 20141025 | 634 | 1102073 | 191 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 2505 | 40.9988 | -121.7478 | 1 SPAN SS OF SBCO 4445 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0065914 | OH | Sus | 0 | yes | 2014 | OCT | Yes | Line to Line | 99202169 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1102 | 103561102 | FUSE | 2587 | 20141025 | 1335 | 1102645 | 920 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1262 | 40.6866 | -122.3162 | BET 4&5 POLES BEYOND 2751 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0066056 | OH | Sus | 0 | yes | 2014 | OCT | Yes |  | 99202041 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1102 | 103561102 | FUSE | 6133 | 20141025 | 1657 | 1102971 | 563 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5067 | 40.6853 | -122.3097 | 3 POLES S/OF FUCO 6133 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0066146 | OH | Sus | 0 | yes | 2014 | OCT | Yes | Line to Line | 99201976 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PARADISE-1103 | 102831103 | FUSE | 7013 | 20141122 | 1258 | 1116795 | 272 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 3264 | 39.7295 | -121.6533 | MTR # E81858 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0071609 | OH | Sus | 31117261 | No | 2014 | NOV | Yes |  | 99198217 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 3-2101 | 103732101 | OTHER |  | 20141125 | 856 | 1117959 | 840 | Distribution Circuit | 3rd Party | Vehicle | 129 | 9251 | 41.0275 | -121.6768 | 3 P W/OF SBCO 7907 | Fog-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0071962 | OH | Sus | 31117598 | No | 2014 | NOV | Yes | Line to Ground | 99197794 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | FUSE | 5925 | 20141204 | 852 | 1124523 | 397 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 15086 | 39.7018 | -120.9665 | MTR 1008573977 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0073790 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99196458 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANTLER-1101 | 103271101 | FUSE | 3333 | 20141205 | 2148 | 1125618 | 418 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7076 | 40.8116 | -122.3195 | 2 POLES SS OF MTR 5000052244 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074105 | OH | Sus | 31119766 | No | 2014 | DEC | Yes |  | 99196142 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | FRENCH GULCH-1102 | 103381102 | FUSE | 2909 | 20141205 | 2251 | 1125772 | 894 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3576 | 40.6584 | -122.6235 | MTR #5000003337 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074124 | OH | Sus | 31119783 | No | 2014 | DEC | Yes | Line to Line | 99196128 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GRAYS FLAT-0401 | 102530401 | FUSE | 3079 | 20141214 | 1545 | 1140572 | 365 | Distribution Circuit | Equipment Failure/Involved | Other | 39 | 7464 | 40.0214 | -121.0633 | MTR 1008682484 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0076882 | OH | Sus | 0 | No | 2014 | DEC | Yes | Open Circuit | 99193150 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER | 5460 | 20141215 | 2057 | 1141728 | 399 | Distribution Circuit | Equipment Failure/Involved | Other | 453 | 156674 | 39.5446 | -121.1476 | 22 SPANS SS OF LR 98174 | Overcast-32 - 90 F | Insulator | Broken, wire on ground | 14-0077133 | OH | Sus | 42298093 | yes | 2014 | DEC | Yes |  | 99192913 | INS | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 85234 | 20141215 | 2244 | 1141792 | 444 | Distribution Circuit | Equipment Failure/Involved | Other | 539 | 169301 | 40.3484 | -121.6214 | MTR 1008682063 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077136 | OH | Sus | 42298089 | yes | 2014 | DEC | Yes | Line to Ground | 99192850 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CENTERVILLE-1101 | 102021101 | FUSE | 6383 | 20141220 | 1355 | 1145150 | 800 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 23200 | 39.7329 | -121.6978 | MTR# 5000069374 | Drizzle-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0077818 | OH | Sus | 0 | No | 2014 | DEC | Yes | Line to Line | 99192078 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1102 | 103401102 | OTHER |  | 20141222 | 930 | 1145989 | 252 | Distribution Circuit | 3rd Party | Vandalism | 773 | 54671 | 40.6058 | -122.4627 | GERRARD/1786: 10863 IRON MNT RD | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0075582 | OH | Sus | 30853610 | No | 2014 | DEC | Yes | Line to Ground | 99191857 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | OTHER |  | 20141227 | 40 | 1149016 | 755 | Distribution Circuit | 3rd Party | Vehicle | 1 | 755 | 39.9048 | -121.7419 | ROBBINS- JAMES: 9265 COHASSET RD | Clear-32 - 90 F | Pole-Wood | Broken, wire on object | 14-0078616 | OH | Sus | 0 | No | 2014 | DEC | Yes | None | 99191132 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1102 | 103521102 | RECLOSER | 49144 | 20141229 | 448 | 1149718 | 490 | Distribution Circuit | 3rd Party | Vehicle | 527 | 95577 | 40.6598 | -122.3418 | 18730 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0078763 | OH | Sus | 31123640 | No | 2014 | DEC | Yes | Line to Ground | 99190948 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1105 | 102911105 | RECLOSER | 1702 | 20141231 | 2230 | 1157657 | 397 | Distribution Circuit | Vegetation | Tree - branch fell on line | 305 | 110165 | 39.7405 | -121.4961 | MAIN LINE AT FUCO 1721 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079818 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99189919 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BURNEY-1101 | 103311101 | RECLOSER | 45984 | 20150101 | 1417 | 1157994 | 385 | Distribution Circuit | 3rd Party | Gun Shot | 932 | 125638 | 40.8793 | -121.6742 | C/OUT POLE 10059 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0002105 | OH | Sus | 42305850 | No | 2015 | JAN | Yes | Line to Ground | 99189618 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 1943 | 20150105 | 1018 | 1159456 | 305 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 74 | 22570 | 39.5156 | -121.2642 | SS MTR 1007906735 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0002488 | OH | Sus | 0 | No | 2015 | JAN | Yes | Line to Ground | 99189236 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BUCKS CREEK-1103 | 102211103 | FUSE | 1815 | 20150129 | 1236 | 1170056 | 334 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 334 | 39.8988 | -121.2119 | 1ST SPAN LD SIDE OF 1815 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0008117 | OH | Sus | 0 | No | 2015 | JAN | Yes | Line to Ground | 99186324 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RISING RIVER-1101 | 103551101 | RECLOSER | 9032 | 20150205 | 2331 | 1173039 | 6921 | Distribution Circuit | Vegetation | Tree - fell into line | 316 | 491696 | 40.7802 | -121.5028 | BOONE/1960: beyond address | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0009769 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182901 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 80454 | 20150205 | 813 | 1172510 | 567 | Distribution Circuit | Equipment Failure/Involved | Other | 241 | 39717 | 40.4341 | -121.8715 | at MTR 1008765111 | Overcast-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0009450 | OH | Sus | 31132973 | yes | 2015 | FEB | Yes | Line to Line | 99185548 | CSO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1101 | 103401101 | FUSE | 6355 | 20150209 | 824 | 1186318 | 626 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 6042 | 40.5305 | -122.4751 | MTR 1003728399 | Drizzle-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0012063 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183165 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1102 | 103441102 | RECLOSER | 1550 | 20150209 | 28 | 1185333 | 639 | Distribution Circuit | Vegetation | Tree - fell into line | 1399 | 189794 | 40.4471 | -122.3189 | 4 SP LD SIDE OF 2379 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011888 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182340 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KESWICK-1101 | 103451101 | FUSE | 7107 | 20150209 | 4 | 1185304 | 1201 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 25221 | 40.6104 | -122.4901 | BROKEN POLES AT MTR# 1006231301 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0011974 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183249 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1101 | 103031101 | FUSE | 1267 | 20150209 | 151 | 1185552 | 583 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 54802 | 39.8159 | -121.5809 | 1ST AND 2ND SPAN S/OF 16187 AND 1 SPAN LD SIDE OF 16187 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0011960 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99183254 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PANORAMA-1102 | 103461102 | RECLOSER | 1632 | 20150209 | 1842 | 1187113 | 1289 | Distribution Circuit | Equipment Failure/Involved | Other | 11 | 10763 | 40.4044 | -122.1222 | 26 POLES LOAD SIDE OF 5463 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012322 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99182514 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 3-2101 | 103732101 | OTHER |  | 20150211 | 730 | 1188323 | 281 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 2972 | 41.0081 | -121.6561 | 1 POLE LD/S OF 3681 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0012671 | OH | Sus | 31133933 | No | 2015 | FEB | Yes | Line to Ground | 99182448 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BOGARD-1101 | 103301101 | OTHER |  | 20150212 | 1445 | 1189390 | 383 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 766 | 40.5874 | -121.0918 | TAP MTR 5000003379 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0013058 | OH | Sus | 0 | No | 2015 | FEB | Yes | Line to Ground | 99182225 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1101 | 103031101 | OCB | OCB | 20150222 | 349 | 1193781 | 990 | Distribution Circuit | Vegetation | Tree - fell into line | 4506 | 597979 | 39.8717 | -121.6109 | 7155- 27221 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0014795 | OH | Sus | 0 | No | 2015 | FEB | Yes | Line to Line | 99181036 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1102 | 102831102 | FUSE | 2755 | 20150222 | 556 | 1193793 | 722 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 17328 | 39.7585 | -121.5738 | MTR 1007456177 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0014809 | OH | Sus | 0 | No | 2015 | FEB | Yes | Line to Line | 99181025 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 2871 | 20150222 | 1254 | 1194015 | 831 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 7479 | 40.428 | -121.8339 | 3 POLES SS OF MTR 1008259321 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0014872 | OH | Sus | 0 | No | 2015 | FEB | Yes | Line to Line | 99180966 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1103 | 102911103 | RECLOSER | 1508 | 20150222 | 1030 | 1193939 | 460 | Distribution Circuit | Vegetation | Tree - fell into line | 792 | 197440 | 39.5046 | -121.4523 | SPARKS- MARTY: 1230 Bald Rock Rd AT MTR# 1007884888 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0014822 | OH | Sus | 0 | No | 2015 | FEB | Yes | Three Phase Fault | 99181005 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CENTERVILLE-1101 | 102021101 | RECLOSER | 2592 | 20150223 | 505 | 1194323 | 623 | Distribution Circuit | Vegetation | Tree - fell into line | 411 | 133173 | 39.7885 | -121.6575 | FUCO 6389- MTR 1007905437- MTR 1008909381 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0014935 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99180889 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 17635 | 20150223 | 633 | 1194341 | 519 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 6420 | 39.7706 | -121.63 | 2 SPANS LD SIDE OF MTR 1007639641 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0014956 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99180880 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1103 | 102831103 | FUSE | 4665 | 20150223 | 512 | 1194325 | 806 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 58838 | 39.7626 | -121.6287 | MTR# 1007694427 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0014918 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99180895 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1103 | 102831103 | FUSE | 17711 | 20150223 | 507 | 1194329 | 382 | Distribution Circuit | Vegetation | Tree - fell into line | 174 | 63190 | 39.7401 | -121.6363 | MTR 1007905243 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0014934 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99180891 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1102 | 102541102 | FUSE | 7689 | 20150223 | 435 | 1194316 | 423 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 7191 | 40.5 | -121.8322 | MTR# 1006772068 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0014919 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99180894 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | RECLOSER | 1976 | 20150223 | 1022 | 1194593 | 219 | Distribution Circuit | Vegetation | Tree - fell into line | 246 | 53874 | 39.6347 | -121.3917 | 1 P PAST LR 1976 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0015036 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Multi-Fault | 99180830 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1101 | 103351101 | FUSE | 2593 | 20150305 | 600 | 1199509 | 380 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 14198 | 40.6871 | -122.0432 | MTR 5000018352 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0017399 | OH | Sus | 31138841 | No | 2015 | MAR | Yes | Line to Ground | 99179358 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 17811 | 20150312 | 2139 | 1202916 | 436 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 1691 | 39.7644 | -121.6124 | MTR 1007640763 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0019306 | OH | Sus | 42349114 | No | 2015 | MAR | Yes | Line to Ground | 99178340 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1102 | 102541102 | RECLOSER | 37350 | 20150312 | 1720 | 1202846 | 577 | Distribution Circuit | 3rd Party | Vehicle | 348 | 71181 | 40.5092 | -121.9583 | CLEVENGER/1788: 44 & shingke creek ln | Overcast-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0019280 | OH | Sus | 31141009 | No | 2015 | MAR | Yes | Three Phase Fault | 99178352 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1107 | 102911107 | RECLOSER | 1510 | 20150321 | 1559 | 1206401 | 76 | Distribution Circuit | 3rd Party | Vehicle | 444 | 18189 | 39.4969 | -121.4452 | ON HARD TAP 1 W/OF MTR 1007919256 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0021150 | OH | Sus | 31142694 | No | 2015 | MAR | Yes | Multi-Fault | 99177302 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 5462 | 20150325 | 1551 | 1208061 | 499 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 459 | 59581 | 39.483 | -121.2464 | TAP TO MTR 1007063415 | Overcast-32 - 90 F | Conductor, Overhead | On Ground | 15-0022133 | OH | Sus | 42357655 | No | 2015 | MAR | Yes | Multi-Fault | 99176785 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1106 | 102831106 | OTHER |  | 20150328 | 2038 | 1209321 | 357 | Distribution Circuit | Vegetation | Tree - branch fell on line | 734 | 20342 | 39.8146 | -121.6085 | MTR 1008113495 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on object | 15-0022774 | OH | Sus | 42358801 | No | 2015 | MAR | Yes | Line to Ground | 99176403 | CSO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | RECLOSER | 1804 | 20150407 | 831 | 1214616 | 181 | Distribution Circuit | Vegetation | Tree - fell into line | 425 | 47054 | 39.3898 | -121.4043 | SS MTR 1008144717 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0024724 | OH | Sus | 0 | yes | 2015 | APR | Yes | Line to Ground | 99175053 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1105 | 102911105 | RECLOSER | 1702 | 20150407 | 933 | 1214714 | 352 | Distribution Circuit | Vegetation | Tree - fell into line | 305 | 42762 | 39.7405 | -121.4961 | METER #1007367928 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0024826 | OH | Sus | 0 | yes | 2015 | APR | Yes | Line to Ground | 99175003 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1101 | 102931101 | RECLOSER | 1610 | 20150413 | 2211 | 1218975 | 430 | Distribution Circuit | Vegetation | Tree - fell into line | 220 | 94600 | 40.3262 | -122.4253 | PRIMARY AT MTR# 1008053699 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0026426 | OH | Sus | 42368134 | yes | 2015 | APR | Yes | Line to Ground | 99173779 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1102 | 103401102 | RECLOSER | 9012 | 20150413 | 2220 | 1218982 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 330 | 47490 | 40.5803 | -122.428 | 1ST AND 2ND POLE E/OF FUCO 11355 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0026427 | OH | Sus | 31148047 | yes | 2015 | APR | Yes | Line to Ground | 99173745 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1102 | 103401102 | FUSE | 6921 | 20150413 | 2231 | 1218985 | 958 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 7507 | 40.5595 | -122.435 | MTR 1006234741 & MTR 5000016563 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0026432 | OH | Sus | 31148045 | yes | 2015 | APR | Yes | Line to Line | 99173743 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1102 | 103441102 | RECLOSER | 1550 | 20150413 | 2107 | 1218938 | 218 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1398 | 140654 | 40.4471 | -122.3189 | ANDRADE- SHAWN: XST FROM 5507 HAPPY VALLEY RD(PALM & HAPPY VALLEY) | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0026418 | OH | Sus | 31148042 | yes | 2015 | APR | Yes | Line to Line | 99173746 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 5-1101 | 101321101 | OTHER |  | 20150422 | 1320 | 1223211 | 185 | Distribution Circuit | Environmental/External | Lightning | 53 | 1571 | 41.0294 | -121.9259 | 7/P/N/OF 10687 | Lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0028620 | OH | Sus | 0 | No | 2015 | APR | Yes | Line to Ground | 99172378 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 17285 | 20150509 | 1002 | 1231967 | 381 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 12 | 4572 | 39.7414 | -121.5938 | 1 SPAN W/OF TRANSFORMER FEEDING MTR# 1007692577 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0033073 | OH | Sus | 31153873 | No | 2015 | MAY | Yes | Line to Line | 99169446 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1109 | 102911109 | FUSE | 13499 | 20150513 | 1308 | 1233839 | 501 | Distribution Circuit | 3rd Party | Vehicle | 28 | 14028 | 39.438 | -121.4791 | 1 P SS OF TRANSFORMER FEEDING MTR# 1007887475 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0033860 | OH | Sus | 31154670 | No | 2015 | MAY | Yes | Line to Line | 99168850 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 1555 | 20150520 | 101 | 1237202 | 413 | Distribution Circuit | Equipment Failure/Involved | Overhead | 77 | 31801 | 40.4391 | -121.8492 | 1 P LD SIDE OF MTR 1008260052 | Overcast-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0035311 | OH | Sus | 42391915 | No | 2015 | MAY | Yes | Line to Ground | 99167773 | CSO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1103 | 102831103 | FUSE | 17453 | 20150605 | 1557 | 1244335 | 618 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1854 | 39.7644 | -121.6358 | 5925 RONSUE | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0038908 | OH | Sus | 42401434 | yes | 2015 | JUN | Yes | Line to Ground | 99165392 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 1516 | 20150609 | 1837 | 1247977 | 878 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 56739 | 40.3455 | -121.8925 | MTR# 1008222900- MTR# 1005833859 | Partly cloudy-Above 90 F | Conductor, Overhead | Broken, wire on ground | 15-0039862 | OH | Sus | 0 | yes | 2015 | JUN | Yes | Line to Ground | 99164492 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1105 | 102911105 | FUSE | 13575 | 20150615 | 1106 | 1251206 | 476 | Distribution Circuit | 3rd Party | Customer Equipment | 28 | 13328 | 39.6483 | -121.4027 | 244 LAKESIDE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0041163 | OH | Sus | 42408994 | No | 2015 | JUN | Yes | Line to Ground | 99163541 | CO | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CLARK ROAD-1102 | 103091102 | FUSE | 5057 | 20150616 | 1115 | 1251645 | 531 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 8426 | 39.6422 | -121.6601 | MTR# 1007546909 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0041343 | OH | Sus | 31161678 | No | 2015 | JUN | Yes | Line to Line | 99163388 | PW | OH | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1105 | 102911105 | JUMPER | WIRE DOWN 2 SPANS LD SIDE OF 1702 | 20150628 | 2107 | 1258381 | 418 | Distribution Circuit | Equipment Failure/Involved | Overhead | 306 | 45683 | 39.7405 | -121.4969 | 2 SPANS LD SIDE OF 1702 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0043869 | OH | Sus | 31164814 | No | 2015 | JUN | Yes | Line to Ground | 99161483 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1107 | 102911107 | FUSE | 13057 | 20150701 | 914 | 1260236 | 269 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 4962 | 39.4829 | -121.4822 | 162 ARTS LN | Clear-Heat Wave-Above 90 | Conductor, Overhead | On Ground | 15-0044544 | OH | Sus | 42418231 | yes | 2015 | JUL | Yes | Line to Ground | 1143207 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER | 2246 | 20150703 | 1640 | 1262546 | 1040 | Distribution Circuit | Vegetation | Tree - fell into line | 588 | 579273 | 40.211 | -121.1646 | MTR# 1008299744 & 18709 SS POLE- TRANSF at MTR 1008303036- MAINLINE at FUCO 18713- CABLE BET T20 | Partly Cloudy-Drizzle-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0045408 | UG | Sus | 31166007 | yes | 2015 | JUL | Yes | Three Phase Fault | 1143772 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KESWICK-1101 | 103451101 | FUSE | 2609 | 20150708 | 1744 | 1265093 | 339 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1017 | 40.5952 | -122.5365 | 7 SPANS LD SIDE OF FUCO 2609 | Strong Winds-Overcast-Rain-Lightning-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0046397 | OH | Sus | 31167227 | yes | 2015 | JUL | Yes | Line to Ground | 1144437 | CSO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 5462 | 20150721 | 1125 | 1274610 | 426 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 459 | 62567 | 39.483 | -121.2464 | MTR 1007886386 & 2 spans LD SIDE OF 13623 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0049508 | OH | Sus | 42432197 | yes | 2015 | JUL | Yes | Line to Line | 1146899 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 711 | 20150729 | 2101 | 1279816 | 638 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 9570 | 39.4438 | -121.2653 | MTR 1007884523 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0051486 | OH | Sus | 0 | yes | 2015 | JUL | Yes | Line to Line | 1148198 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | RECLOSER | 35002 | 20150731 | 1204 | 1280804 | 456 | Distribution Circuit | 3rd Party | Vehicle | 1100 | 57317 | 40.6242 | -122.3037 | TRANSFORMER FEEDING MTR# 1006192067 | Partly Cloudy-Above 90 | Pole-Wood | Broken, wire on ground | 15-0051918 | OH | Sus | 0 | No | 2015 | JUL | Yes | Line to Line | 1148471 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 711 | 20150806 | 1817 | 1283762 | 489 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 5263 | 39.4438 | -121.2653 | SS OF MTR# 1007918991 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0053347 | OH | Sus | 42444014 | yes | 2015 | AUG | Yes | Line to Line | 1149367 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CLARK ROAD-1102 | 103091102 | FUSE | 7063 | 20150808 | 2258 | 1285411 | 529 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 3582 | 39.6709 | -121.6273 | MTR# 1009122010 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 15-0053884 | OH | Sus | 42446281 | yes | 2015 | AUG | Yes | Line to Ground | 1149894 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | OCB | OCB | 20150810 | 1552 | 1286118 | 267 | Distribution Circuit | Equipment Failure/Involved | Overhead | 698 | 163106 | 39.4856 | -121.2204 | 1 SPANS LD SIDE OF MTR #1009119918 | Clear-32-90 F | Insulator | Broken, wire on object | 15-0054157 | OH | Sus | 0 | No | 2015 | AUG | Yes | Line to Line | 1150071 | INS | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 3-2101 | 103732101 | RECLOSER | 1482 | 20150814 | 1509 | 1288450 | 1265 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 3072 | 40.9989 | -121.7478 | BET POLES 10 & 11 LD SIDE OF 1733 | Clear-Drizzle-32-90 F | Conductor, Overhead | On Ground | 15-0055136 | OH | Sus | 0 | No | 2015 | AUG | Yes | Line to Line | 1150763 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1106 | 102831106 | FUSE | 17907 | 20150829 | 2323 | 1297028 | 438 | Distribution Circuit | Vegetation | Tree - branch fell on line | 96 | 42048 | 39.8203 | -121.6016 | MTR 1007237387 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0058228 | OH | Sus | 42460484 | yes | 2015 | AUG | Yes | Three Phase Fault | 1152936 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1105 | 102911105 | RECLOSER | 1702 | 20150913 | 1452 | 1305033 | 475 | Distribution Circuit | Equipment Failure/Involved | Overhead | 306 | 132570 | 39.7405 | -121.4961 | MAINLINE 5 SPANS E/OF FUCO 17271 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0061101 | OH | Sus | 42470147 | No | 2015 | SEP | Yes | Line to Ground | 1154991 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE | 9647 | 20150920 | 529 | 1308795 | 469 | Distribution Circuit | 3rd Party | Vehicle | 101 | 17326 | 40.3637 | -122.219 | 3/P/N/OF MTR 1008365065 | Clear-32-90 F | Pole-Wood | Broken, wire on object | 15-0062344 | OH | Sus | 0 | No | 2015 | SEP | Yes | Line to Line | 1155953 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1104 | 103351104 | FUSE | 3719 | 20150922 | 634 | 1309901 | 206 | Distribution Circuit | Vegetation | Tree - fell into line | 161 | 14518 | 40.5188 | -122.2385 | 2 S/OF MTR 1007306007 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0062628 | OH | Sus | 42481308 | No | 2015 | SEP | Yes | Multi-Fault | 1156192 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CENTERVILLE-1101 | 102021101 | FUSE | 16015 | 20151003 | 2111 | 1316255 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 157 | 10499 | 39.7363 | -121.6852 | IN SPAN IMMEDIATLY LD SIDE OF 16015 | Strong Winds-Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0067708 | OH | Sus | 0 | yes | 2015 | OCT | Yes | Line to Ground | 1160476 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1103 | 102831103 | RECLOSER | 2488 | 20151003 | 2103 | 1316247 | 623 | Distribution Circuit | Vegetation | Tree - fell into line | 777 | 81846 | 39.7411 | -121.6275 | 1 SPAND LD SIDE OF LR 2488/ MTR#1007550769 | Strong Winds-Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0067677 | OH | Sus | 0 | yes | 2015 | OCT | Yes | Line to Ground | 1160440 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 5181 | 20151004 | 13 | 1316382 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 44372 | 39.7774 | -121.5994 | METER #1007768714 | Strong Winds-Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0067707 | OH | Sus | 0 | yes | 2015 | OCT | Yes | Line to Ground | 1160474 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1105 | 102831105 | FUSE | 27157 | 20151004 | 56 | 1316439 | 899 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2697 | 39.7925 | -121.5798 | 1 SPAN LD SIDE OF 27157 | Strong Winds-Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0067711 | OH | Sus | 0 | yes | 2015 | OCT | Yes | Line to Ground | 1160480 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WHITMORE-1101 | 103601101 | FUSE | 1429 | 20151020 | 1455 | 1326821 | 713 | Distribution Circuit | 3rd Party | Vehicle | 10 | 7130 | 40.6148 | -121.8745 | 27 POLES LD SIDE OF 1429 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0072279 | OH | Sus | 0 | No | 2015 | OCT | Yes | Line to Ground | 1163720 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CORNING-1101 | 103331101 | RECLOSER | 85152 | 20151103 | 1919 | 1334907 | 518 | Distribution Circuit | 3rd Party | Vehicle | 479 | 189067 | 40.0156 | -122.4004 | REGINATO/1820: 16245 RANCHO TEHAMA RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0075389 | OH | Sus | 0 | yes | 2015 | NOV | Yes | Line to Line | 1166278 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1102 | 103521102 | JUMPER | OJ LINE & BUCK FEEDING MTR 1008130176 | 20151104 | 2003 | 1335659 | 490 | Distribution Circuit | Vegetation | Tree - branch fell on line | 76 | 13791 | 40.7162 | -122.3323 | MTR 1008730176 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0075703 | OH | Sus | 42561641 | No | 2015 | NOV | Yes | Line to Ground | 1166549 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 5713 | 20151109 | 2341 | 1338539 | 705 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 19035 | 40.3518 | -121.5823 | SPAN FEEDING TRANSFORMER MTR# 1008757854 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 15-0076897 | OH | Sus | 31199283 | yes | 2015 | NOV | Yes | Line to Line | 1167519 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANTLER-1101 | 103271101 | FUSE | 2305 | 20151110 | 159 | 1338559 | 800 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 17480 | 40.9061 | -122.3833 | 1 SPAN N/OF MTR# 1006280863 | Overcast-Fog-Snow-Below 32 F | Transformer (OH) | Broken, wire on ground | 15-0076900 | OH | Sus | 0 | No | 2015 | NOV | Yes | Three Phase Fault | 1167522 | TXO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CORNING-1101 | 103331101 | FUSE | 85211 | 20151115 | 1621 | 1342368 | 697 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 10199 | 40.0187 | -122.4113 | 1 SPAN SS OF MTR# 1007858701 | Partly Cloudy-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 15-0077987 | OH | Sus | 0 | yes | 2015 | NOV | Yes | Line to Line | 1168473 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 1969 | 20151124 | 1059 | 1347726 | 119 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 3808 | 39.4943 | -121.3171 | 8226 CAROLYN LN | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 15-0080535 | OH | Sus | 0 | yes | 2015 | NOV | Yes | None | 1170521 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CHESTER-1102 | 103181102 | RECLOSER | 2564 | 20151203 | 1911 | 1353395 | 208 | Distribution Circuit | Equipment Failure/Involved | Overhead | 80 | 16297 | 40.294 | -121.2428 | 1 SPAN SW/OF 18605 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082624 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1172284 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CLARK ROAD-1102 | 103091102 | RECLOSER | 47006 | 20151203 | 1428 | 1353041 | 149 | Distribution Circuit | 3rd Party | Vehicle | 316 | 47084 | 39.6988 | -121.5743 | 'PENTZ RD 1 POLE E/O FUCO 17747' | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082354 | OH | Sus | 0 | yes | 2015 | DEC | Yes | None | 1172229 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | FUSE | 3513 | 20151203 | 1016 | 1352723 | 527 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 8959 | 40.2943 | -121.05 | 5 SPANS LD SIDE OF 3513 | Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082460 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Multi-Fault | 1172162 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 1905 | 20151203 | 1217 | 1352818 | 377 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 32422 | 39.5171 | -121.2747 | MTR 1008865703 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082490 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1172185 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | SPANISH CREEK-4401 | 103104401 | OCB | OCB | 20151203 | 1210 | 1352805 | 730 | Distribution Circuit | Vegetation | Tree - fell into line | 928 | 196854 | 40.027 | -120.9631 | 5 SPANS LD SIDE OF SUB | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082505 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1172200 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | FRENCH GULCH-1101 | 103381101 | FUSE | 2905 | 20151207 | 2109 | 1355387 | 486 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 28519 | 40.7197 | -122.6294 | 11735 DRUNKEN GULCH LN | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083309 | OH | Sus | 31204714 | No | 2015 | DEC | Yes | Line to Ground | 1172916 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BUCKS CREEK-1103 | 102211103 | FUSE | 3085 | 20151210 | 1304 | 1357890 | 246 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 12300 | 39.8754 | -121.1743 | 4 POLES E/OF 3085 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083995 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1173626 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BUCKS CREEK-1103 | 102211103 | FUSE | 18103 | 20151210 | 1625 | 1358082 | 1063 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1063 | 39.8956 | -121.2793 | BEYOND 18103 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084049 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Three Phase Fault | 1173663 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 3-2101 | 103732101 | OCB | OCB | 20151214 | 1705 | 1363741 | 8 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 192 | 40.9982 | -121.748 | 20 SPANS N/OF SW 354683 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0085232 | OH | Sus | 31206126 | yes | 2015 | DEC | Yes | Line to Ground | 1175045 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 85234 | 20151219 | 149 | 1366425 | 390 | Distribution Circuit | Equipment Failure/Involved | Overhead | 539 | 122442 | 40.3483 | -121.6211 | 2 POLES SS TO 1 POLE LD SIDE OF 1175 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 15-0086148 | OH | Sus | 31207519 | No | 2015 | DEC | Yes | Line to Ground | 1176079 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER | 98174 | 20151220 | 1442 | 1367134 | 651 | Distribution Circuit | Equipment Failure/Involved | Overhead | 355 | 227578 | 39.6083 | -121.0754 | 24 SPANS N/OF 88575 | Overcast-Snow-32-90 F | Insulator | Broken, wire on object | 15-0086313 | OH | Sus | 42595367 | No | 2015 | DEC | Yes | Line to Line | 1176275 | INS | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | JUMPER | WIRE DOWN | 20151220 | 1153 | 1367346 | 1341 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 225248 | 40.3496 | -121.5546 | 30 SPANS LD SIDE OF LR 1640 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 15-0086362 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Line | 1176328 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | FRENCH GULCH-1101 | 103381101 | FUSE | 2905 | 20151222 | 2031 | 1369990 | 924 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 71070 | 40.7197 | -122.6294 | MTR 500049410 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086909 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1176938 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1101 | 103031101 | FUSE | 7173 | 20151223 | 1401 | 1370436 | 666 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 15792 | 39.849 | -121.6044 | CHRISTENSEN/2698/530-966-0403: at #1007456145 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086992 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Line | 1177057 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | JUMPER | WIRE DOWN 4 S/OF MTR# 1008942251 | 20160101 | 107 | 1375521 | 617 | Distribution Circuit | Equipment Failure/Involved | Overhead | 677 | 403459 | 40.3483 | -121.6211 | 4 SPANS LD SIDE OF MTR# 1008942251 | Strong Winds-Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 16-0002401 | OH | Sus | 0 | No | 2016 | JAN | Yes | Line to Ground | 1178320 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 5217 | 20160101 | 107 | 1375551 | 876 | Distribution Circuit | Equipment Failure/Involved | Overhead | 104 | 67184 | 40.3468 | -121.7671 | METER 1009287791 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0002414 | OH | Sus | 0 | No | 2016 | JAN | Yes | Line to Ground | 1178333 | PW | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 721 | 20160104 | 947 | 1376495 | 365 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 4 | 1460 | 39.4535 | -121.2535 | 2 P PAST LCO 721 | Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0002690 | OH | Sus | 42600562 | No | 2016 | JAN | Yes | Line to Line | 1178569 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GANSNER-1101 | 103021101 | JUMPER | OJ LINE AND BUCK TWD 2919 TO EOL | 20160114 | 1642 | 1384214 | 528 | Distribution Circuit | 3rd Party | Vehicle | 1 | 528 | 39.9462 | -120.9567 | HWY 70 OPP GANSER PARK | Overcast-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 16-0005483 | OH | Sus | 0 | No | 2016 | JAN | Yes | None | 1180565 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | RECLOSER | 48950 | 20160118 | 2237 | 1386626 | 727 | Distribution Circuit | Vegetation | Tree - fell into line | 253 | 36070 | 40.7039 | -122.3364 | 14257 OLD OREGON TR | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0006161 | OH | Sus | 31213543 | yes | 2016 | JAN | Yes | Three Phase Fault | 1181119 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1101 | 102931101 | RECLOSER | 68190 | 20160122 | 2138 | 1390392 | 450 | Distribution Circuit | Vegetation | Tree - fell into line | 470 | 122636 | 40.3649 | -122.4062 | MTR#1008363857 | Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007658 | OH | Sus | 42616340 | yes | 2016 | JAN | Yes | Line to Ground | 1182147 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1103 | 102911103 | RECLOSER | 1508 | 20160122 | 1950 | 1390349 | 519 | Distribution Circuit | Equipment Failure/Involved | Overhead | 793 | 59083 | 39.5046 | -121.4527 | MTR# 1009068741 | Drizzle-Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007571 | OH | Sus | 42616318 | yes | 2016 | JAN | Yes | Line to Ground | 1182053 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CENTERVILLE-1101 | 102021101 | FUSE | 27015 | 20160130 | 740 | 1394388 | 230 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 690 | 39.7895 | -121.6565 | 13 POLES W/OF 96997 COMBOS | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009272 | OH | Sus | 42621047 | No | 2016 | JAN | Yes | Three Phase Fault | 1183366 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | RECLOSER | 35002 | 20160131 | 1412 | 1394926 | 857 | Distribution Circuit | Vegetation | Tree - fell into line | 1116 | 147605 | 40.6243 | -122.3039 | MTR 1009791561 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009414 | OH | Sus | 31216097 | yes | 2016 | JAN | Yes | Line to Line | 1183490 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CORNING-1101 | 103331101 | FUSE | 4281 | 20160205 | 2050 | 1399247 | 588 | Distribution Circuit | 3rd Party | Vehicle | 95 | 11424 | 40.0156 | -122.4333 | 2 SPANS S/S OF MTR 1008366584 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0011034 | OH | Sus | 0 | No | 2016 | FEB | Yes | Line to Ground | 1184702 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CORNING-1101 | 103331101 | FUSE | 85213 | 20160206 | 2209 | 1399642 | 899 | Distribution Circuit | 3rd Party | Vehicle | 55 | 9801 | 40.0062 | -122.4318 | 1 N/W OF MTR #1008365795 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0011121 | OH | Sus | 0 | No | 2016 | FEB | Yes | Line to Ground | 1184788 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1103 | 102831103 | FUSE | 1549 | 20160208 | 26 | 1399904 | 635 | Distribution Circuit | Vegetation | Tree - fell into line | 130 | 63246 | 39.7411 | -121.6261 | MTR # 1007635685 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0011196 | OH | Sus | 0 | No | 2016 | FEB | Yes | Line to Ground | 1184861 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1105 | 102911105 | RECLOSER | 1702 | 20160208 | 355 | 1399914 | 422 | Distribution Circuit | Vegetation | Tree - fell into line | 308 | 87046 | 39.7403 | -121.4967 | MID SPAN ON LD SIDE OF 5039 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0011201 | OH | Sus | 42625616 | No | 2016 | FEB | Yes | Line to Ground | 1184866 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | KANAKA-1101 | 103221101 | FUSE | 1875 | 20160306 | 645 | 1421242 | 1973 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 78920 | 39.4363 | -121.326 | BROKEN CROSSARM LA PORTE RD 2P/S/OF 1875- WIRE DOWN MULTIPLE LOCATIONS: LA PORTE RD 3SP S/OF 1875 AN | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0018467 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190305 | CAW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 1941 | 20160306 | 443 | 1421084 | 1250 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5000 | 39.5088 | -121.2762 | 1 PHASE 2 SPANS SS OF MTR 1008139381 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018542 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190381 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | JUMPER | BURNED OPEN WIRE | 20160306 | 2024 | 1422756 | 1050 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3150 | 39.4696 | -121.2431 | 2 POLES E/OF LINE AND BUCK MTR 1007888007 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018606 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190448 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1103 | 102831103 | FUSE | 17709 | 20160306 | 308 | 1420919 | 373 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 7091 | 39.7408 | -121.627 | 462 NEVERNEVER LN | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018192 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190061 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 85567 | 20160306 | 849 | 1421555 | 1293 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 9051 | 40.3558 | -121.8935 | LD SIDE OF MTR 1008361389 | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0018398 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190247 | CAW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1107 | 102911107 | FUSE | 23101 | 20160306 | 152 | 1420666 | 368 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 7728 | 39.4871 | -121.4481 | 153 WAKEFIELD DRIVE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018143 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190014 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GANSNER-1101 | 103021101 | FUSE | 1795 | 20160307 | 526 | 1423194 | 460 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2300 | 39.9838 | -120.9465 | 3 SPANS LD SIDE OF 1975 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 16-0018762 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190592 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 1967 | 20160307 | 232 | 1423026 | 958 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 7664 | 39.506 | -121.2051 | Mays- Sean/2497: tree fell through line | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 16-0018795 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190617 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | KANAKA-1101 | 103221101 | FUSE | 5825 | 20160307 | 758 | 1423426 | 1054 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 15810 | 39.4411 | -121.3422 | WIRE DOWN AT TRANSF MTR# 1007907733 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018998 | OH | Sus | 0 | yes | 2016 | MAR | Yes | None | 1190750 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 5185 | 20160307 | 1004 | 1423669 | 445 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 39160 | 39.7778 | -121.5961 | 2 & 3 SPANS N/OF FUCO 5185 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018827 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190637 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1102 | 102541102 | FUSE | 7573 | 20160307 | 700 | 1423337 | 343 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1715 | 40.5088 | -121.9339 | 7278 MILLER RANCH RD | Overcast-Fog-Drizzle-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0018753 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190588 | CSO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1102 | 103521102 | JUMPER | WIRE DOWN | 20160310 | 1826 | 1426820 | 186 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 372 | 40.6617 | -122.4012 | 1 N/OF MTR 1009205613 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020082 | OH | Sus | 31224270 | yes | 2016 | MAR | Yes | Line to Ground | 1191596 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RISING RIVER-1101 | 103551101 | RECLOSER | 1530 | 20160310 | 213 | 1426198 | 446 | Distribution Circuit | Vegetation | Tree - fell into line | 527 | 85216 | 40.8713 | -121.5539 | 1839 FUSES | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0019826 | OH | Sus | 31224018 | yes | 2016 | MAR | Yes | Line to Line | 1191450 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER | 13026 | 20160312 | 2044 | 1429769 | 1555 | Distribution Circuit | Vegetation | Tree - fell into line | 167 | 204044 | 39.6844 | -120.9829 | MTR#1008048892 AND MTR#108865779 | Overcast-Fog-Strong Winds-Below 32 F | Conductor, Overhead | Broken, wire on ground | 16-0020858 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Multi-Fault | 1192247 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 9751 | 20160312 | 1423 | 1429503 | 385 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 1533 | 39.5036 | -121.2776 | 18561 INDIAN ROCK CT | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020798 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1192178 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | FUSE | 94967 | 20160312 | 2017 | 1429747 | 695 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 15985 | 40.6836 | -122.3455 | 4 POLES LD SIDE OF FUCO 94967 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020848 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1192237 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 5462 | 20160313 | 1759 | 1430465 | 662 | Distribution Circuit | Vegetation | Tree - fell into line | 458 | 30037 | 39.483 | -121.2464 | HARD TAP FEEDING MTR #1009120641 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021020 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192393 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 1437 | 20160313 | 1821 | 1430492 | 335 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 7035 | 40.6424 | -122.2305 | 2 SPANS N/OF 1437 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0021032 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192404 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 1299 | 20160313 | 552 | 1429918 | 321 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 4815 | 39.7687 | -121.6265 | TRANSF FEEDING MTR# 1007905806 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020877 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192267 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RISING RIVER-1101 | 103551101 | RECLOSER | 9032 | 20160313 | 1001 | 1430023 | 483 | Distribution Circuit | Vegetation | Tree - fell into line | 318 | 153594 | 40.7801 | -121.5032 | Knaup- George/1787: broken pole 3 spans s/o LR 9032 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0020911 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192294 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GIRVAN-1101 | 103401101 | FUSE | 1833 | 20160314 | 533 | 1430834 | 335 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 16112 | 40.4739 | -122.6207 | 2 NE/OF MTR 5000049397 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021140 | OH | Sus | 31224912 | yes | 2016 | MAR | Yes | Line to Ground | 1192507 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1102 | 102541102 | RECLOSER | 9742 | 20160315 | 1624 | 1432134 | 316 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 473 | 39958 | 40.518 | -121.7552 | MTR# 1008968888 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021734 | OH | Sus | 31225276 | No | 2016 | MAR | Yes | Line to Ground | 1192936 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KESWICK-1101 | 103451101 | RECLOSER | 9712 | 20160319 | 1119 | 1434203 | 517 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 435 | 77060 | 40.6166 | -122.4955 | Lytle/1785: 15805 HIGHWAY 299 WEST OLD SHASTA | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0022667 | OH | Sus | 31226033 | No | 2016 | MAR | Yes | Line to Ground | 1193625 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | TYLER-1105 | 103571105 | FUSE | 1947 | 20160320 | 234 | 1434485 | 613 | Distribution Circuit | 3rd Party | Vehicle | 50 | 22932 | 40.1595 | -122.338 | 1 E/OF MTR #1008046501 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 16-0022721 | OH | Sus | 0 | No | 2016 | MAR | Yes | Line to Ground | 1193679 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE | 1411 | 20160322 | 1407 | 1436233 | 398 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 9886 | 39.6362 | -121.4178 | MTR 1005566463 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0023324 | OH | Sus | 42661492 | No | 2016 | MAR | Yes | Line to Ground | 1194098 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 17637 | 20160329 | 422 | 1440525 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 14650 | 39.7724 | -121.6263 | MTR# 1008145270 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0024636 | OH | Sus | 0 | No | 2016 | MAR | Yes | Line to Line | 1195100 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1107 | 102911107 | RECLOSER | 37472 | 20160330 | 11 | 1441373 | 65 | Distribution Circuit | 3rd Party | Vandalism | 461 | 29965 | 39.4824 | -121.5036 | 1 WEST & 1 SOUTH OF 13489 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0024900 | OH | Sus | 0 | No | 2016 | MAR | Yes | Line to Line | 1195287 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 17635 | 20160406 | 21 | 1445163 | 719 | Distribution Circuit | Vegetation | Tree - fell into line | 160 | 88200 | 39.7705 | -121.6279 | AT C/OUT POLE 17635 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0026385 | OH | Sus | 0 | yes | 2016 | APR | Yes | Line to Ground | 1196344 | PW | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1102 | 103401102 | FUSE | 11343 | 20160413 | 2149 | 1450343 | 511 | Distribution Circuit | Vegetation | Tree - branch fell on line | 131 | 11015 | 40.5836 | -122.4696 | 11343 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0028461 | OH | Sus | 31231079 | No | 2016 | APR | Yes | Line to Line | 1197869 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANDERSON-1101 | 103261101 | FUSE | 2051 | 20160421 | 2255 | 1455381 | 692 | Distribution Circuit | Equipment Failure/Involved | Overhead | 84 | 26632 | 40.4188 | -122.2867 | Colgate- Calem/1959: MTR #1008767139 | Partly Cloudy-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0030414 | OH | Sus | 0 | No | 2016 | APR | Yes | Line to Line | 1199250 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 23129 | 20160517 | 846 | 1471033 | 404 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 1974 | 39.5037 | -121.3367 | 5 POLES SS OF MTR# 1008973335 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0036469 | OH | Sus | 42702725 | No | 2016 | MAY | Yes | Line to Line | 1203828 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 6149 | 20160528 | 1801 | 1478599 | 303 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 3939 | 40.6255 | -122.4138 | Lytle/1785: 2931 KESWICK DAM RD REDDING | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0039528 | OH | Sus | 42708500 | No | 2016 | MAY | Yes | Line to Line | 1206159 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1102 | 103401102 | FUSE | 9515 | 20160529 | 1419 | 1478900 | 386 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3860 | 40.5789 | -122.4673 | Lytle/1785: CINDEE LN 1/P/W/O VICTORIA DR REDDING | Clear-32-90 F | Conductor, Overhead | On Ground | 16-0039619 | OH | Sus | 31242864 | No | 2016 | MAY | Yes | Force Out | 1206245 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | JUMPER | WIRE DOWN | 20160606 | 1201 | 1483835 | 105 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 105 | 39.4463 | -121.3838 | 1 SPAN LD SIDE MTR 1008654330 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0041365 | OH | Sus | 42713056 | No | 2016 | JUN | Yes | Line to Ground | 1207606 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 1939 | 20160610 | 1742 | 1486866 | 996 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 44 | 19228 | 39.4503 | -121.1972 | 17211 OREGON HILL RD- CHALLENGE mtr 1007886779 | Clear-32-90 F | Conductor, Overhead | On Ground | 16-0042517 | OH | Sus | 42723156 | No | 2016 | JUN | Yes | Line to Line | 1208408 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1101 | 103351101 | FUSE | 5401 | 20160626 | 1106 | 1496075 | 736 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 15520 | 40.4962 | -122.0466 | 3 POLES LD SIDE OF MTR# 5000026162 & THE FOLLOWING 3 POLES | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0045846 | OH | Sus | 31249643 | No | 2016 | JUN | Yes | Line to Line | 1210929 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CORNING-1102 | 103331102 | FUSE | 2029 | 20160630 | 1714 | 1499124 | 725 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4520 | 40.0147 | -122.5714 | MTR 10099499679 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 16-0047210 | OH | Sus | 0 | No | 2016 | JUN | Yes | Line to Line | 1211875 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1102 | 102831102 | FUSE | 2755 | 20160630 | 141 | 1498699 | 327 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 4134 | 39.7584 | -121.5739 | MTR #1007456174 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0046769 | OH | Sus | 0 | No | 2016 | JUN | Yes | Line to Ground | 1211578 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1102 | 103561102 | RECLOSER | 1644 | 20160711 | 204 | 1507929 | 665 | Distribution Circuit | Vegetation | Tree - fell into line | 745 | 138837 | 40.6905 | -122.2786 | 21895 ELK TRAIL WEST | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0048929 | OH | Sus | 31256574 | No | 2016 | JUL | Yes | Line to Line | 1213173 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 76008 | 20160717 | 1223 | 1511469 | 477 | Distribution Circuit | Vegetation | Tree - fell into line | 379 | 55452 | 39.8877 | -121.6655 | 1 SPAN E/OF MTR 1009122776 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0050460 | OH | Sus | 31257662 | No | 2016 | JUL | Yes | Line to Ground | 1214279 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 1435 | 20160721 | 1649 | 1513860 | 442 | Distribution Circuit | 3rd Party | Vehicle | 65 | 10530 | 40.6403 | -122.2403 | 1 P/N/OF 12926 DRY CREEK RD | Clear-Above 90 | Pole-Wood | Broken, wire on ground | 16-0051672 | OH | Sus | 0 | No | 2016 | JUL | Yes | Line to Ground | 1215006 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1104 | 103521104 | OCB | 1104/2 | 20160727 | 2109 | 1517471 | 529 | Distribution Circuit | 3rd Party | Vehicle | 1195 | 65637 | 40.619 | -122.3227 | MTR#1006233184 | Clear-Above 90 | Pole-Wood | Broken, wire on ground | 16-0053085 | OH | Sus | 31259817 | yes | 2016 | JUL | Yes | Multi-Fault | 1216074 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1103 | 102831103 | JUMPER | WIRE DOWN TO HARDTAP 1 SPAN LOAD SIDE OF 2855 | 20160727 | 1230 | 1517129 | 183 | Distribution Circuit | Vegetation | Tree - fell into line | 582 | 3402 | 39.7569 | -121.6439 | 225 PARKWOOD DR | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 16-0052955 | OH | Sus | 42754213 | yes | 2016 | JUL | Yes | Open Circuit | 1216005 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | MC ARTHUR-1101 | 103491101 | RECLOSER | 37344 | 20160810 | 1349 | 1524364 | 641 | Distribution Circuit | 3rd Party | Vehicle | 233 | 69953 | 41.1203 | -121.1465 | CARPOLE at LINE AND BUCK 1 POLE SOUTHWEST OF MTR#5000002288 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0056320 | OH | Sus | 31262484 | No | 2016 | AUG | Yes | Line to Ground | 1218146 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 17293 | 20160819 | 511 | 1528777 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2008 | 39.7372 | -121.5938 | 2 SPANS LD SIDE OF FUCO 17293 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0058419 | OH | Sus | 0 | No | 2016 | AUG | Yes | Line to Line | 1219623 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CLARK ROAD-1102 | 103091102 | RECLOSER | 2070 | 20160904 | 535 | 1536484 | 465 | Distribution Circuit | Equipment Failure/Involved | Overhead | 404 | 48239 | 39.6565 | -121.5762 | 1/N/OF 2070 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0062294 | OH | Sus | 42781128 | No | 2016 | SEP | Yes | Line to Line | 1222234 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1101 | 103751101 | SWITCH | 26463 | 20160908 | 1635 | 1538608 | 31 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 62 | 39.6925 | -121.5331 | NONE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0062398 | OH | Sus | 0 | No | 2016 | SEP | Yes | Force Out | 1222883 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1103 | 102911103 | RECLOSER | 1504 | 20160911 | 34 | 1539461 | 655 | Distribution Circuit | 3rd Party | Vehicle | 1693 | 136364 | 39.5045 | -121.4987 | RISER POLE 6403 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0063744 | OH | Sus | 0 | No | 2016 | SEP | Yes | Three Phase Fault | 1223145 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | NOTRE DAME-1104 | 102041104 | RECLOSER | 2028 | 20160916 | 2056 | 1542958 | 918 | Distribution Circuit | Vegetation | Tree - fell into line | 1209 | 314427 | 39.8387 | -121.7023 | BET 7TH & 8TH POLE LD SIDE OF 585517 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0065273 | OH | Sus | 0 | No | 2016 | SEP | Yes | Line to Ground | 1224144 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RED BLUFF-1101 | 103541101 | FUSE | 85837 | 20160922 | 1353 | 1546178 | 86 | Distribution Circuit | Animal | Bird found | 171 | 14706 | 40.224 | -122.3417 | W/OF FU 85837 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0066692 | OH | Sus | 42796411 | No | 2016 | SEP | Yes | Line to Ground | 1225259 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | OCB | 1101/2 | 20161002 | 1822 | 1551643 | 964 | Distribution Circuit | Vegetation | Tree - fell into line | 702 | 501438 | 39.4857 | -121.2201 | 11708 LA PORTE RD ------- 2ND CASE- ON MAIN LINE 1 SPAN LS OF 79777 TAP----- #3 JUST LOAD SIDE OF 59 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0069063 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1226982 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | OTHER | WIRE DOWN | 20161002 | 1807 | 1551783 | 545 | Distribution Circuit | Environmental/External | Lightning | 195 | 92535 | 39.5734 | -121.3168 | WIRE DOWN AT LR 1406 BOTH SOURCE AND LOAD SIDE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0069110 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1227024 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2560 | 20161002 | 1641 | 1551502 | 849 | Distribution Circuit | Vegetation | Tree - fell into line | 1077 | 339550 | 39.8888 | -121.6648 | POLE # 153- LOAD SIDE OF 1423/ POLE 49 POLE 73 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0069050 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1226969 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | JUMPER | WIRE DOWN | 20161002 | 1823 | 1551630 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 247 | 39475 | 39.6358 | -121.3759 | 12 SPANS LD OF 1481 | Partly Cloudy-Drizzle-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0069079 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1226997 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | JUMPER | HOT WIRE DOWN 8 LD SIDE OF 1406 | 20161003 | 746 | 1551874 | 352 | Distribution Circuit | Environmental/External | Lightning | 123 | 33875 | 39.5714 | -121.321 | 8 SPANS LD SIDE OF 1406 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0069269 | OH | Sus | 0 | No | 2016 | OCT | Yes | Line to Ground | 1227152 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ANTLER-1101 | 103271101 | FUSE | 3353 | 20161015 | 1452 | 1561304 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 17577 | 40.8396 | -122.3601 | MTR# 1006235618 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072579 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1229627 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | SWITCH | 5933 | 20161015 | 1658 | 1561852 | 372 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 7440 | 39.7109 | -120.9853 | 1 SPAN LD SIDE OF SB 5933 | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072640 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1229681 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 5-1101 | 101321101 | RECLOSER | 1606 | 20161016 | 1212 | 1562943 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 17850 | 41.0191 | -121.9095 | Lytle/1785: 6/N/O S/B1763 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072915 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1229947 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WHITMORE-1101 | 103601101 | FUSE | 2211 | 20161017 | 2019 | 1564845 | 1223 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 50679 | 40.607 | -121.9558 | 8 SPANS LD SIDE OF 6699 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0073457 | OH | Sus | 31278305 | yes | 2016 | OCT | Yes | Line to Ground | 1230383 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | FRENCH GULCH-1102 | 103381102 | FUSE | 3055 | 20161024 | 1816 | 1569064 | 848 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 6784 | 40.6532 | -122.5575 | SOUTH OF MTR#5000022184 TWD 3055 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0075215 | OH | Sus | 42862591 | yes | 2016 | OCT | Yes | Line to Line | 1231785 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 75744 | 20161027 | 1638 | 1570992 | 519 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 16055 | 39.4965 | -121.3223 | 3400 FORBESTOWN RD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076084 | OH | Sus | 42868801 | yes | 2016 | OCT | Yes | Line to Line | 1232349 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 27211 | 20161028 | 1045 | 1571780 | 187 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1122 | 39.7562 | -121.585 | LD SIDE OF 27211 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076378 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1232585 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1102 | 103561102 | FUSE | 1965 | 20161030 | 1640 | 1573382 | 296 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 9512 | 40.7184 | -122.2416 | MTR# 1006233884 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076816 | OH | Sus | 31281298 | No | 2016 | OCT | Yes | Line to Line | 1232917 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 3-2101 | 103732101 | RECLOSER | 1482 | 20161119 | 300 | 1584648 | 1025 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 6558 | 40.9986 | -121.7471 | APPROX 30 SPANS LD SIDE OF 1733 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081046 | OH | Sus | 0 | yes | 2016 | NOV | Yes | Line to Ground | 1236072 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1102 | 102541102 | FUSE | 529177 | 20161119 | 44 | 1584550 | 527 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2635 | 40.5556 | -121.7268 | 2/P/LD OF 529177 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081037 | OH | Sus | 0 | yes | 2016 | NOV | Yes | Line to Line | 1236064 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CLARK ROAD-1102 | 103091102 | RECLOSER | 2068 | 20161130 | 114 | 1591675 | 1027 | Distribution Circuit | Vegetation | Tree - fell into line | 271 | 94684 | 39.6983 | -121.571 | JESSEN- MIKE/1776: 3247 TREVOR RD. | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0083055 | OH | Sus | 0 | No | 2016 | NOV | Yes | Line to Ground | 1237672 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANTLER-1101 | 103271101 | RECLOSER | 1376 | 20161208 | 235 | 1596646 | 514 | Distribution Circuit | Vegetation | Tree - branch fell on line | 67 | 34438 | 40.8524 | -122.3324 | 20236 GILMAN RD LAKEHEAD | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 16-0084479 | OH | Sus | 42893052 | yes | 2016 | DEC | Yes | Line to Line | 1239041 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CORNING-1102 | 103331102 | FUSE | 8105 | 20161208 | 1200 | 1596971 | 295 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1180 | 39.8492 | -122.6192 | 5/P/W OF 6038 ROUND VALLEY | Snow-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084630 | OH | Sus | 31288393 | yes | 2016 | DEC | Yes | None | 1239152 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ROUND MOUNTAIN-1101 | 109001101 | FUSE | 3943 | 20161208 | 720 | 1596726 | 246 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 4674 | 40.7415 | -121.9936 | BUZZARD ROOST RD at WILD ROSE LN 4/P/LD SICE | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084533 | OH | Sus | 42892913 | yes | 2016 | DEC | Yes | Line to Ground | 1239096 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ROUND MOUNTAIN-1101 | 109001101 | FUSE | 1639 | 20161208 | 255 | 1596655 | 642 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 13952 | 40.7533 | -122.0234 | 1/P/W/OF CGC 119872051630 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 16-0084534 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1239097 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 5-1101 | 101321101 | RECLOSER | 1618 | 20161210 | 642 | 1598441 | 3369 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 3369 | 40.9885 | -121.9742 | SS OF 9315 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084923 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Three Phase Fault | 1239470 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1107 | 102911107 | FUSE | 829 | 20161210 | 613 | 1598278 | 436 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 5273 | 39.5029 | -121.4031 | 1 SPAN W/OF CORNER OF MATHER AND ROMELT | Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084908 | OH | Sus | 42894398 | yes | 2016 | DEC | Yes | Line to Ground | 1239446 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1101 | 103751101 | FUSE | 17271 | 20161215 | 1709 | 1603357 | 565 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1695 | 39.7667 | -121.51 | JESSEN- MIKE/1776: 3856 JEFFREY PINE LN | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085857 | OH | Sus | 42900388 | yes | 2016 | DEC | Yes | Line to Ground | 1240524 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1102 | 103441102 | FUSE | 10245 | 20161215 | 630 | 1602298 | 353 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 3600 | 40.4344 | -122.4074 | 3 S/OF MTR 1008952755 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085656 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Line | 1240319 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 1151 | 20161215 | 1802 | 1603445 | 390 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2340 | 39.7776 | -121.6193 | Robbins- James/1934: 6638 VEIW ACRES | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085837 | OH | Sus | 31289845 | yes | 2016 | DEC | Yes | Line to Ground | 1240504 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ELK CREEK-1101 | 102781101 | FUSE | 2009 | 20161217 | 1253 | 1605592 | 735 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1470 | 39.4273 | -122.5054 | 3 SPANS N/O MTR 1006489611 | Clear-32-90 F | Insulator | Broken, wire on ground | 16-0086172 | OH | Sus | 31290110 | No | 2016 | DEC | Yes | Line to Ground | 1240943 | INS | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1105 | 102831105 | FUSE | 1291 | 20161218 | 641 | 1605961 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 4858 | 39.7999 | -121.585 | at MTR 1004506827 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 16-0086225 | OH | Sus | 0 | No | 2016 | DEC | Yes | Line to Line | 1241030 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1101 | 102541101 | OCB | 1101/2 | 20161218 | 1347 | 1606199 | 697 | Distribution Circuit | Vegetation | Tree - fell into line | 1341 | 99088 | 40.459 | -121.8679 | MTR 1008790287 & 3 SPANS SS OF REG 863397 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0086241 | OH | Sus | 42902236 | No | 2016 | DEC | Yes | Line to Ground | 1241051 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | KESWICK-1101 | 103451101 | FUSE | 2443 | 20161223 | 956 | 1609631 | 503 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6036 | 40.5974 | -122.5439 | 6 SPANS LOADSIDE OF FUCO 2443 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0086794 | OH | Sus | 31291446 | No | 2016 | DEC | Yes | Line to Line | 1241978 | CAW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 5-1101 | 101321101 | OTHER | 1618 | 20161224 | 936 | 1610238 | 196 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 196 | 40.9885 | -121.9742 | 1ST SPAN SS OF 9315 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 16-0086897 | OH | Sus | 0 | No | 2016 | DEC | Yes | Line to Ground | 1242085 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 17799 | 20161228 | 1414 | 1612296 | 278 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 7784 | 39.777 | -121.6031 | 1ST SPAN LD SIDE OF 17799 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0087245 | OH | Sus | 31291917 | No | 2016 | DEC | Yes | Line to Line | 1242577 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BURNEY-1101 | 103311101 | RECLOSER | 1322 | 20170104 | 1051 | 1618257 | 871 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 31897 | 40.913 | -121.6469 | Andrade- Shawn/1838: 5 LOADSIDE OF 1442- 5 SPANS LD SIDE OF 1442- 9 SPANS LD SIDE OF MTR # 100957568 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0003661 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1243759 | CAW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | MC ARTHUR-1101 | 103491101 | FUSE | 4233 | 20170104 | 2307 | 1619026 | 866 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 17320 | 41.1071 | -121.326 | 641-725 CIRCLE OAKS DR | Partly Cloudy-Below 32 F | Insulator | Broken, wire on ground | 17-0003831 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1243870 | INS | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1101 | 102931101 | RECLOSER | 1610 | 20170105 | 1614 | 1619639 | 301 | Distribution Circuit | Vegetation | Tree - fell into line | 221 | 8601 | 40.3261 | -122.4253 | HARD TAP TO EAST 2 SPANS E/OF 9563 | Clear-32-90 F | Insulator | Broken, wire on object | 17-0004087 | OH | Sus | 31293814 | No | 2017 | JAN | Yes | Force Out | 1244022 | INS | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1104 | 103351104 | FUSE | 6611 | 20170105 | 56 | 1619044 | 512 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 9728 | 40.5911 | -122.2468 | MTR#5000026150 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0003842 | OH | Sus | 0 | No | 2017 | JAN | Yes | Multi-Fault | 1243885 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANTLER-1101 | 103271101 | FUSE | 3319 | 20170107 | 1242 | 1621849 | 1554 | Distribution Circuit | Vegetation | Tree - fell into line | 103 | 68694 | 40.8129 | -122.3204 | 1 SPAN SS OF MTR#D46973 | Overcast-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 17-0004743 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244550 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | OTHER | HOT WIRE DOWN FEEDING MTR#1009365517 | 20170107 | 1125 | 1621550 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 1776 | 31749 | 40.3352 | -122.4125 | LINE & BUCK FEEDING MTR#1008365517 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004700 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1244513 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ELK CREEK-1101 | 102781101 | FUSE | 2009 | 20170107 | 1101 | 1621501 | 369 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 738 | 39.4273 | -122.5054 | 12 SPANS LD SIDE OF FUSE 2009 | Overcast-Drizzle-32-90 F | Insulator | Broken, wire on object | 17-0004703 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244518 | INS | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | FRENCH GULCH-1101 | 103381101 | FUSE | 2905 | 20170107 | 921 | 1621122 | 446 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 41032 | 40.7199 | -122.6295 | 31 POLES LD SIDE OF 2905- 45 POLES LD SIDE OF 2905 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0004622 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244446 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1102 | 103521102 | JUMPER | WIRE DOWN | 20170107 | 1139 | 1621632 | 422 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 844 | 40.662 | -122.4012 | 1 SPAN S/OF LINE AND BUCK AT CORNER OF WALKER MINE RD AND TERRA ROSA RD | Overcast-Drizzle-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0004756 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244560 | CSO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | JUMPER | ENERGIZED WIRE DOWN | 20170107 | 916 | 1621766 | 434 | Distribution Circuit | Equipment Failure/Involved | Overhead | 87 | 16380 | 40.4287 | -121.9228 | 1 SPAN S/OF 7465 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004696 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244510 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 1125 | 20170114 | 1815 | 1643783 | 313 | Distribution Circuit | Vegetation | Tree - bark fell into line | 10 | 3130 | 39.7776 | -121.6204 | 1/P/LS/OF 1125 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0009231 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Ground | 1248499 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE | 1635 | 20170124 | 1622 | 1666102 | 1136 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 18315 | 40.908 | -121.9112 | HENERY RPTS TREE MTR 11338R | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0014522 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1253193 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 5-1101 | 101321101 | FUSE | 1715 | 20170124 | 1000 | 1665529 | 167 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 668 | 41.011 | -121.8981 | 3 SPANS LD SIDE OF FUCO 1715 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0014306 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1253050 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE | 6843 | 20170202 | 1641 | 1673204 | 559 | Distribution Circuit | Equipment Failure/Involved | Overhead | 43 | 7077 | 40.3494 | -122.3265 | MTR#1008693627 | Overcast-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 17-0017028 | OH | Sus | 0 | No | 2017 | FEB | Yes | Line to Line | 1255120 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BUCKS CREEK-1102 | 102211102 | OCB | 1102/2 | 20170203 | 446 | 1673582 | 17697 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 53638 | 39.9131 | -121.3271 | TRANSMISSION POLE 20/16 TO POLE 20/20 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0017095 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1255186 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | RECLOSER | 1804 | 20170205 | 1558 | 1675453 | 601 | Distribution Circuit | 3rd Party | Vehicle | 433 | 35307 | 39.39 | -121.4043 | MTR 1007909106 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0017560 | OH | Sus | 0 | No | 2017 | FEB | Yes | Multi-Fault | 1255527 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1102 | 103561102 | FUSE | 6689 | 20170206 | 54 | 1675790 | 344 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 6536 | 40.6868 | -122.286 | Colgate- Calem/1959: 13764 BEAR CUB CT | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017654 | OH | Sus | 31303970 | yes | 2017 | FEB | Yes | Three Phase Fault | 1255619 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1102 | 103751102 | FUSE | 1449 | 20170215 | 1131 | 1689233 | 296 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 29008 | 39.6527 | -121.4451 | 3 SPANS LD SIDE OF 1449 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021273 | OH | Sus | 42949458 | No | 2017 | FEB | Yes | Line to Ground | 1258540 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | FUSE | 3121 | 20170216 | 126 | 1689782 | 784 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 21908 | 40.2085 | -121.1602 | 2 SPANS LD SIDE FU 3121 | Clear-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0021594 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1258787 | CAW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 27087 | 20170216 | 636 | 1690095 | 264 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 792 | 39.7487 | -121.5857 | 2ND SPAN LD SIDE OF FUCO 27087 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021518 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1258716 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | SPANISH CREEK-4401 | 103104401 | OCB | 72 | 20170216 | 311 | 1689879 | 3914 | Distribution Circuit | Vegetation | Tree - fell into line | 1848 | 757705 | 40.0274 | -120.9628 | Branch- Scott/1770: 1 pole n/o 43/20 on highway 70 near trestle bridge/SBCO 18121 | Clear-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 17-0021473 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1258682 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 80454 | 20170216 | 315 | 1689873 | 592 | Distribution Circuit | Vegetation | Tree - fell into line | 241 | 44392 | 40.4341 | -121.8714 | 2 LD SIDE OF 1571 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021446 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1258655 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1102 | 102541102 | FUSE | 7595 | 20170216 | 650 | 1690102 | 185 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 2590 | 40.4978 | -121.9956 | 15 SPANS LD SIDE OF 7595 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021532 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1258726 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE | 1173 | 20170225 | 329 | 1713619 | 906 | Distribution Circuit | Environmental/External | Ice or snow | 37 | 28814 | 40.7523 | -122.0231 | 26 POLES LD SIDE OF 1173 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 17-0026682 | OH | Sus | 31307785 | No | 2017 | FEB | Yes | Line to Ground | 1263346 | CAW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | JUMPER | WIRE DOWN 2 SP S/SIDE OF 1320 | 20170225 | 1319 | 1713896 | 102 | Distribution Circuit | Equipment Failure/Involved | Overhead | 675 | 44059 | 40.6952 | -122.3432 | 2 SPANS SOURCE SIDE OF 1320 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0026715 | OH | Sus | 42953887 | No | 2017 | FEB | Yes | Line to Ground | 1263407 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RED BLUFF-1105 | 103541105 | FUSE | 1699 | 20170321 | 1626 | 1732309 | 250 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 9185 | 40.2103 | -122.2112 | 3 & 4 SPANS LD SIDE OF 9367 | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0032503 | OH | Sus | 31313853 | yes | 2017 | MAR | Yes | Line to Line | 1267839 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BURNEY-1101 | 103311101 | RECLOSER | 45984 | 20170330 | 1829 | 1740212 | 183 | Distribution Circuit | Equipment Failure/Involved | Overhead | 933 | 91931 | 40.8795 | -121.6742 | Knaup- George/1787: wire dowin Tamarack and Fir St. Burney | Overcast-Snow-32-90 F | Conductor, Overhead | On Ground | 17-0035270 | OH | Sus | 31315962 | yes | 2017 | MAR | Yes | Line to Ground | 1269901 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1101 | 102541101 | OCB | 1101/2 | 20170331 | 1227 | 1741248 | 993 | Distribution Circuit | Vegetation | Tree - fell into line | 241 | 146251 | 40.459 | -121.8679 | 2 SPANS SS OF 1523- 4 SPANS SS OF 1563- 7 POLES SS OF SBCO 1571- 1 SPAN SS OF 1563 TREE IN LINE BROK | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0035578 | OH | Sus | 31316104 | yes | 2017 | MAR | Yes | Multi-Fault | 1270161 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 6149 | 20170408 | 124 | 1752265 | 530 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 6890 | 40.6255 | -122.4138 | 5/s/ld s of 6149 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038212 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1272268 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | FUSE | 1953 | 20170409 | 1354 | 1753388 | 426 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1278 | 39.5767 | -121.1007 | 6 SPANS LD SIDE FU 1953 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0038462 | OH | Sus | 42986960 | No | 2017 | APR | Yes | Line to Ground | 1272515 | CSO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 683 | 20170409 | 1600 | 1753659 | 665 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 4655 | 39.5189 | -121.2738 | LD SIDE FU 683 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038479 | OH | Sus | 31318607 | No | 2017 | APR | Yes | Line to Ground | 1272532 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 5185 | 20170412 | 1246 | 1756193 | 446 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 38802 | 39.7778 | -121.5961 | MTR 1008809952 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0039578 | OH | Sus | 0 | No | 2017 | APR | Yes | Multi-Fault | 1273398 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RISING RIVER-1101 | 103551101 | FUSE | 5983 | 20170413 | 1003 | 1756906 | 249 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 882 | 40.7542 | -121.4844 | 2 P/SS OF MTR# 1005450815 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0039930 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Line | 1273620 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WHITMORE-1101 | 103601101 | RECLOSER | 1598 | 20170414 | 510 | 1757604 | 452 | Distribution Circuit | Vegetation | Tree - fell into line | 173 | 31631 | 40.6208 | -121.9332 | 1 POLE W/OF 9495 | Partly Cloudy-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 17-0040192 | OH | Sus | 0 | No | 2017 | APR | Yes | Line to Line | 1273801 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 1555 | 20170416 | 1921 | 1759027 | 479 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 14533 | 40.4391 | -121.8503 | 31980 FORWARD RD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0040636 | OH | Sus | 42996109 | No | 2017 | APR | Yes | Line to Line | 1274121 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 5-1101 | 101321101 | OTHER | WIRE DOWN @ MTR#1008668826 | 20170418 | 1148 | 1760333 | 267 | Distribution Circuit | Vegetation | Tree - branch fell on line | 133 | 21200 | 41.0151 | -121.9058 | at MTR#1008668826 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0041169 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1274534 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 547 | 20170426 | 1918 | 1767942 | 470 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 4 | 1880 | 39.4407 | -121.3418 | 1/P/PAST MTR#1007906650 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0043192 | OH | Sus | 43001614 | No | 2017 | APR | Yes | Line to Ground | 1275969 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1101 | 103441101 | FUSE | 11241 | 20170504 | 2354 | 1775111 | 303 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 1837 | 40.4781 | -122.4104 | 1/S/S/OF MTR#1006194456 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0045439 | OH | Sus | 31324020 | yes | 2017 | MAY | Yes | Line to Ground | 1277664 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1102 | 103401102 | FUSE | 4407 | 20170505 | 2047 | 1775889 | 583 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7579 | 40.5869 | -122.4663 | 1/S/LD/S OF 4407 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0045726 | OH | Sus | 31324212 | No | 2017 | MAY | Yes | Line to Line | 1277838 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WILDWOOD-1101 | 103611101 | JUMPER | WIRE DOWN 6 SPANS LOADSIDE S/B C/O'S 1681 | 20170505 | 1729 | 1775854 | 629 | Distribution Circuit | Equipment Failure/Involved | Overhead | 92 | 56893 | 40.3779 | -123.0015 | Laughlin- Ronald/1016: 6 SPANS LOADSIDE S/B C/O'S 1681 & FLOATER at N40.37869- W123.00520 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0045707 | OH | Sus | 0 | No | 2017 | MAY | Yes | Line to Ground | 1277816 | CSO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1102 | 102541102 | FUSE | 1531 | 20170507 | 801 | 1776880 | 446 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 22746 | 40.5228 | -121.6813 | 20 LD SIDE OF 7107 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0045984 | OH | Sus | 43008160 | yes | 2017 | MAY | Yes | Line to Ground | 1278114 | CAW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1102 | 102541102 | RECLOSER | 1650 | 20170508 | 444 | 1777348 | 521 | Distribution Circuit | Vegetation | Tree - fell into line | 239 | 26994 | 40.517 | -121.7462 | 36940 VIOLA DRIVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0046089 | OH | Sus | 31324427 | yes | 2017 | MAY | Yes | Multi-Fault | 1278216 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BUCKS CREEK-1102 | 102211102 | RECLOSER | 1102/2 | 20170511 | 1554 | 1780244 | 1432 | Distribution Circuit | Vegetation | Tree - fell into line | 159 | 41113 | 39.9117 | -121.3266 | 1/2 MILE NORTHEAST OF CARIBOU CANYON | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0047375 | OH | Sus | 0 | No | 2017 | MAY | Yes | Three Phase Fault | 1279123 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1102 | 103401102 | RECLOSER | 9012 | 20170516 | 2128 | 1783627 | 270 | Distribution Circuit | Vegetation | Tree - fell into line | 335 | 49213 | 40.5805 | -122.4282 | 1 N OF MTR # 1006195534 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0048427 | OH | Sus | 31325743 | No | 2017 | MAY | Yes | Line to Ground | 1279975 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ELK CREEK-1101 | 102781101 | RECLOSER | 2004 | 20170518 | 1627 | 1785030 | 533 | Distribution Circuit | Equipment Failure/Involved | Overhead | 171 | 79023 | 39.6105 | -122.5319 | MTR # 1008569152 | Clear-32-90 F | Insulator | Broken, wire on object | 17-0048979 | OH | Sus | 31326740 | No | 2017 | MAY | Yes | Line to Ground | 1280351 | INS | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 1595 | 20170521 | 1710 | 1786852 | 250 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 2850 | 39.744 | -121.5938 | 2ND SPAN W/OF MTR 1007887411 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0049472 | OH | Sus | 43020445 | No | 2017 | MAY | Yes | Line to Line | 1280735 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 65606 | 20170526 | 1527 | 1791435 | 60 | Distribution Circuit | 3rd Party | Vehicle | 458 | 27249 | 39.5291 | -121.2838 | 3 SPANS SS OF SBCO 99163 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0051061 | OH | Sus | 0 | No | 2017 | MAY | Yes | Three Phase Fault | 1281775 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER | 2016 | 20170529 | 1518 | 1792673 | 535 | Distribution Circuit | Vegetation | Tree - fell into line | 613 | 125150 | 40.2098 | -121.1605 | 1214 PENNINSULA DR | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0051306 | OH | Sus | 31328482 | No | 2017 | MAY | Yes | Multi-Fault | 1282009 | CAW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE | 1411 | 20170615 | 945 | 1804974 | 560 | Distribution Circuit | 3rd Party | Vehicle | 47 | 12600 | 39.6362 | -121.4178 | RIP VAN WAY & PINE TREE LN MTR#1007241164 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0055459 | OH | Sus | 0 | No | 2017 | JUN | Yes | Line to Ground | 1285079 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 1151 | 20170619 | 409 | 1809944 | 425 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2550 | 39.7776 | -121.6193 | 4 SPANS LD SIDE OF FUCO 1151 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0056446 | OH | Sus | 0 | yes | 2017 | JUN | Yes | Line to Line | 1285941 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 1516 | 20170627 | 737 | 1818877 | 420 | Distribution Circuit | Vegetation | Tree - fell into line | 136 | 57120 | 40.3456 | -121.8925 | Laughlin- Ronald/1016: 30409 PAYNES CRK LOOP | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0058820 | OH | Sus | 31334206 | No | 2017 | JUN | Yes | Line to Line | 1287864 | CAW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1102 | 103751102 | FUSE | 1449 | 20170629 | 1542 | 1820799 | 561 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 99 | 30028 | 39.6527 | -121.4451 | 2 SPANS SS OF MTR#1009916362 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0059592 | OH | Sus | 43047269 | No | 2017 | JUN | Yes | Line to Line | 1288402 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | RECLOSER | 9072 | 20170708 | 1849 | 1826992 | 1513 | Distribution Circuit | Vegetation | Tree - fell into line | 288 | 157484 | 40.3378 | -122.3717 | FUCO 10173 / 16915 PRENTICE RD | Clear-Above 90 | Crossarm, Wood | Broken, wire on ground | 17-0061469 | OH | Sus | 31335983 | yes | 2017 | JUL | Yes | Line to Ground | 1289677 | CAW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1102 | 103561102 | FUSE | 6689 | 20170711 | 1147 | 1829036 | 312 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 5928 | 40.6868 | -122.286 | O Haire- Sean/1788: c/o6689 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0062052 | OH | Sus | 31336498 | No | 2017 | JUL | Yes | Line to Ground | 1290167 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CLARK ROAD-1102 | 103091102 | RECLOSER | 2070 | 20170715 | 1432 | 1832213 | 302 | Distribution Circuit | Vegetation | Tree - fell into line | 405 | 54372 | 39.6565 | -121.5762 | Bischel- Jason/1773: 3401 cherokee rd | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0063126 | OH | Sus | 43060253 | No | 2017 | JUL | Yes | Line to Ground | 1290935 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | RECLOSER | 35002 | 20170723 | 913 | 1838018 | 387 | Distribution Circuit | Animal | Bird found | 1115 | 184712 | 40.6243 | -122.3039 | 1 E/OF 1437 ON MAIN LINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0064801 | OH | Sus | 43065072 | No | 2017 | JUL | Yes | Line to Ground | 1292177 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | OTHER | 1 OF 3 HOT WIRES DOWN AT MTR#1009863922 | 20170725 | 1905 | 1839822 | 297 | Distribution Circuit | Equipment Failure/Involved | Overhead | 805 | 64105 | 39.5964 | -121.4445 | MTR# 1009863922 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0065453 | OH | Sus | 43067430 | No | 2017 | JUL | Yes | Line to Ground | 1292623 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 1355 | 20170727 | 1002 | 1840795 | 613 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 15995 | 39.7776 | -121.6229 | MTR 1007488830 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0065894 | OH | Sus | 31339504 | No | 2017 | JUL | Yes | Line to Ground | 1292914 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 5-1101 | 101321101 | OTHER | WIRE DOWN | 20170728 | 1402 | 1841709 | 381 | Distribution Circuit | Equipment Failure/Involved | Overhead | 129 | 46581 | 40.9997 | -121.9586 | 5 SPANS E/OF SW 4829 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0066367 | OH | Sus | 0 | No | 2017 | JUL | Yes | Line to Ground | 1293148 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1107 | 102911107 | RECLOSER | 37472 | 20170729 | 1324 | 1842174 | 1153 | Distribution Circuit | 3rd Party | Vehicle | 464 | 148419 | 39.4824 | -121.5036 | 2 POLES S/OF SW 6611 POLE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0066455 | OH | Sus | 0 | No | 2017 | JUL | Yes | Line to Ground | 1293235 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 1435 | 20170807 | 2257 | 1848210 | 277 | Distribution Circuit | Vegetation | Tree - branch fell on line | 65 | 18005 | 40.6403 | -122.2403 | 1/S/LOADSIDE OF MTR1009768686 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0068638 | OH | Sus | 31341292 | No | 2017 | AUG | Yes | Line to Line | 1294823 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1102 | 102831102 | FUSE | 27131 | 20170814 | 1919 | 1852555 | 321 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 5136 | 39.7634 | -121.6043 | MTR# 1007771722 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0070260 | OH | Sus | 31342492 | No | 2017 | AUG | Yes | Line to Line | 1295972 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1102 | 102541102 | OTHER | WIRE DOWN | 20170825 | 756 | 1858968 | 194 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1172 | 209208 | 40.4932 | -121.878 | at 7541 ON THE MAIN LINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0072757 | OH | Sus | 43094081 | No | 2017 | AUG | Yes | Line to Ground | 1297733 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | JUMPER | HOT WIRE DOWN AT MTR 1007544787 | 20170827 | 1601 | 1860588 | 414 | Distribution Circuit | Vegetation | Tree - branch fell on line | 67 | 17883 | 39.7518 | -121.5844 | 5691 WOODGLEN DR | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0073182 | OH | Sus | 31345533 | yes | 2017 | AUG | Yes | Line to Ground | 1298053 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 1153 | 20170828 | 24 | 1860967 | 540 | Distribution Circuit | Vegetation | Tree - branch fell on line | 50 | 27000 | 39.7771 | -121.6171 | MTR#1009203266- 6359 LUCKY JOHN RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0073266 | OH | Sus | 31345427 | yes | 2017 | AUG | Yes | Line to Line | 1298141 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1103 | 102911103 | RECLOSER | 75052 | 20170829 | 1335 | 1862601 | 7424 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 274 | 39045 | 39.5436 | -121.4343 | SOUTH AND EAST OF KANAKA SUB | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0073847 | OH | Sus | 31347938 | No | 2017 | AUG | Yes | Multi-Fault | 1298520 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | RECLOSER | 35002 | 20170830 | 1743 | 1863565 | 262 | Distribution Circuit | Vegetation | Tree - fell into line | 1117 | 76344 | 40.6243 | -122.3039 | 11764 STILLWATER WAY | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0074287 | OH | Sus | 0 | No | 2017 | AUG | Yes | Line to Ground | 1298776 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1101 | 103351101 | SWITCH | 5953 | 20170901 | 1405 | 1864900 | 218 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 68 | 8056 | 40.7009 | -122.0398 | 4 SPANS N/OF 4699 | Clear-Heat Wave-Above 90 | Pole-Wood | Broken, wire on ground | 17-0074816 | OH | Sus | 0 | yes | 2017 | SEP | Yes | Force Out | 1299142 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | SYCAMORE CREEK-1111 | 102971111 | OTHER | WIRE DOWN | 20170904 | 339 | 1869480 | 425 | Distribution Circuit | Equipment Failure/Involved | Overhead | 538 | 214974 | 39.8473 | -121.8265 | BET DIST POLE #'S 39 & 41 - 200 YDS N/E OF NICALOG RD S/OF COHASSET RD | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0075723 | OH | Sus | 0 | yes | 2017 | SEP | Yes | Line to Ground | 1300003 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ANTLER-1101 | 103271101 | FUSE | 2417 | 20170906 | 1926 | 1871913 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 23830 | 40.847 | -122.3315 | HARD TAP 1 SS OF FU 3353 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0076501 | OH | Sus | 43100665 | No | 2017 | SEP | Yes | Line to Ground | 1300562 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1101 | 103751101 | FUSE | 1715 | 20170915 | 1423 | 1879696 | 631 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 14 | 8834 | 39.7409 | -121.4958 | 1/P/W/OF MTR 1007696516 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0079388 | OH | Sus | 31351291 | No | 2017 | SEP | Yes | Line to Ground | 1302689 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1102 | 103401102 | FUSE | 9513 | 20170921 | 2102 | 1883684 | 652 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6520 | 40.5801 | -122.4676 | Gerrard- Randy/1786: 3 POLES LOAD SIDE 9513 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0080854 | OH | Sus | 31352388 | yes | 2017 | SEP | Yes | Line to Line | 1303757 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 1640 | 20170921 | 1011 | 1883206 | 1018 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 168 | 35916 | 40.3543 | -121.5766 | MTR# 1009435453 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0080582 | OH | Sus | 43115529 | yes | 2017 | SEP | Yes | Line to Ground | 1303623 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | RECLOSER | 35002 | 20170923 | 1417 | 1884647 | 468 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1117 | 98820 | 40.6243 | -122.3039 | 20507 PORTERO DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0081216 | OH | Sus | 43116611 | No | 2017 | SEP | Yes | Line to Ground | 1304019 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CLARK ROAD-1102 | 103091102 | OTHER | WIRE DOWN 2 N/O 59123 | 20170925 | 1547 | 1885579 | 303 | Distribution Circuit | Equipment Failure/Involved | Overhead | 203 | 47360 | 39.7136 | -121.5214 | AT FUCO 68381 ON MAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0076714 | OH | Sus | 31171820 | No | 2017 | SEP | Yes | Line to Ground | 1304281 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1102 | 103441102 | FUSE | 10277 | 20170930 | 1122 | 1888561 | 471 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1884 | 40.4706 | -122.3984 | MTR # 1006183436 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0083034 | OH | Sus | 0 | No | 2017 | SEP | Yes | Line to Ground | 1305121 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1105 | 102831105 | JUMPER | HOT WIRE DOWN ON HARD TAP FEEDING 5293 | 20171005 | 1035 | 1891413 | 337 | Distribution Circuit | Animal | Squirrel | 1290 | 39768 | 39.7908 | -121.5857 | SQUIRREL AT 5293- WIRE DOWN 1 POLE E/O 5293 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0084445 | OH | Sus | 31354875 | No | 2017 | OCT | Yes | Line to Ground | 1306043 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1102 | 102831102 | FUSE | 1261 | 20171006 | 817 | 1891798 | 348 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 14616 | 39.7612 | -121.6063 | MTR 1007692270 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0084652 | OH | Sus | 31354811 | No | 2017 | OCT | Yes | Line to Ground | 1306190 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 7031 | 20171023 | 1650 | 1908136 | 483 | Distribution Circuit | Equipment Failure/Involved | Overhead | 66 | 3276 | 40.6218 | -122.2766 | AT MTR 1008668445 | Clear-Above 90 | Pole-Wood | Broken, wire on object | 17-0089798 | OH | Sus | 0 | No | 2017 | OCT | Yes | Force Out | 1310184 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 9653 | 20171031 | 817 | 1912782 | 292 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1232 | 174696 | 39.483 | -121.2465 | 2 SPANS SS OF 85780 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0091455 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Line | 1311362 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER | 98174 | 20171115 | 2016 | 1923308 | 651 | Distribution Circuit | Vegetation | Tree - fell into line | 358 | 228978 | 39.6081 | -121.0754 | 1 LD SIDE OF MTR 1008298320 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0095347 | OH | Sus | 0 | yes | 2017 | NOV | Yes | Line to Ground | 1314242 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 1415 | 20171115 | 1550 | 1923216 | 418 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1254 | 39.8287 | -121.6239 | 2 SP LD SIDE OF FUCO 1415 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0095318 | OH | Sus | 0 | yes | 2017 | NOV | Yes | Line to Ground | 1314225 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 1271 | 20171207 | 143 | 1937852 | 649 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 72958 | 39.7709 | -121.6266 | 1 S/OF FUCO 17639- 6296 OLIVER RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0100406 | OH | Sus | 0 | No | 2017 | DEC | Yes | Line to Ground | 1318070 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BURNEY-1101 | 103311101 | RECLOSER | 1340 | 20171218 | 2109 | 1947249 | 107 | Distribution Circuit | Vegetation | Tree - branch fell on line | 539 | 121697 | 40.9126 | -121.6455 | 9 SPANS LD SIDE OF LR 1340 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102499 | OH | Sus | 0 | No | 2017 | DEC | Yes | Line to Ground | 1320569 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1102 | 102541102 | FUSE | 1539 | 20171218 | 2045 | 1947242 | 517 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 5893 | 40.5226 | -121.6835 | MTR#1006191604 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102501 | OH | Sus | 0 | No | 2017 | DEC | Yes | Line to Ground | 1320571 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1107 | 102911107 | RECLOSER | 1510 | 20171229 | 1440 | 1953065 | 188 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 444 | 27211 | 39.497 | -121.4452 | MTR#1008257249 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0103601 | OH | Sus | 43242581 | No | 2017 | DEC | Yes | Line to Ground | 1322406 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 1845 | 20180102 | 711 | 309 | 230 | Distribution Circuit | Equipment Failure/Involved | Overhead | 74 | 17020 | 39.3963 | -121.4134 | 2 W/OF MTR 1009396901 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0002913 | OH | Sus | 0 | No | 2018 | JAN | Yes | Line to Line | 1322664 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | RECLOSER | 80670 | 20180102 | 2039 | 839 | 498 | Distribution Circuit | 3rd Party | Vehicle | 168 | 20579 | 39.3883 | -121.4056 | NEAR LA PORT AND KINGS RANCH RD | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 18-0003097 | OH | Sus | 0 | No | 2018 | JAN | Yes | Line to Line | 1322787 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CLARK ROAD-1102 | 103091102 | RECLOSER | 2068 | 20180108 | 40 | 3571 | 860 | Distribution Circuit | Equipment Failure/Involved | Overhead | 270 | 54881 | 39.6983 | -121.571 | Maiocco- Marty/1672: broke crossarm and pole at 10846 NELSON BAR RD | Overcast-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0004152 | OH | Sus | 31372684 | yes | 2018 | JAN | Yes | Line to Ground | 1323575 | CAW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 17327 | 20180119 | 22 | 10551 | 836 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5016 | 39.7297 | -121.5742 | 1 POLE W/OF EOL AT LINE & BUCK- 5038 ARDED WAY | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 18-0007218 | OH | Sus | 31374551 | No | 2018 | JAN | Yes | Line to Line | 1325462 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 83288 | 20180125 | 600 | 13581 | 304 | Distribution Circuit | Vegetation | Tree - branch fell on line | 215 | 56640 | 39.5275 | -121.2862 | 5 SPANS LD SIDE OF 1997 ON MAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0008761 | OH | Sus | 43261103 | No | 2018 | JAN | Yes | Line to Ground | 1326390 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | FUSE | 7135 | 20180126 | 851 | 14456 | 129 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 387 | 40.7207 | -122.329 | MTR 1008790298 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0009276 | OH | Sus | 0 | No | 2018 | JAN | Yes | Multi-Fault | 1326683 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 1596 | 20180126 | 1103 | 14576 | 339 | Distribution Circuit | Equipment Failure/Involved | Overhead | 747 | 206502 | 40.3514 | -121.7815 | 16 POLES SS OF SW 7747 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0009312 | OH | Sus | 31375774 | No | 2018 | JAN | Yes | Force Out | 1326707 | CAW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1101 | 103751101 | FUSE | 1725 | 20180206 | 924 | 20031 | 374 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4114 | 39.744 | -121.525 | 6 SPANS LD SIDE OF 1725 | Clear-32-90 F | Conductor, Overhead | On Ground | 18-0011821 | OH | Sus | 31377511 | No | 2018 | FEB | Yes | Multi-Fault | 1328456 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KESWICK-1101 | 103451101 | JUMPER | WIRE DOWN AT MTR# 5000003570 | 20180207 | 544 | 20595 | 495 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 9610 | 40.6542 | -122.5191 | MTR#5000003570 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0012073 | OH | Sus | 31377410 | No | 2018 | FEB | Yes | Line to Ground | 1328606 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | JUMPER | WIRE DOWN 15 SPANS LD SIDE LR 2040 | 20180212 | 2010 | 23612 | 473 | Distribution Circuit | Equipment Failure/Involved | Overhead | 316 | 149212 | 39.9437 | -121.651 | 7 SPANS LD SIDE LR 2040 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0013604 | OH | Sus | 31378806 | No | 2018 | FEB | Yes | Line to Ground | 1329692 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | RECLOSER | 37436 | 20180301 | 1446 | 35102 | 1399 | Distribution Circuit | Vegetation | Tree - fell into line | 1766 | 1135129 | 40.1713 | -121.0871 | 14 S/SS/OF 3193 AND 3/S/SS/OF 724955 | Overcast-Snow-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0018661 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Multi-Fault | 1333068 | CAW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | FUSE | 1967 | 20180301 | 459 | 33900 | 2420 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 24200 | 39.506 | -121.2051 | Sparks- Marty/3864: 15 spans load side of C/O 1967 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0018426 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1332942 | CAW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | OTHER | 1508 | 20180301 | 358 | 33851 | 454 | Distribution Circuit | Equipment Failure/Involved | Overhead | 806 | 274677 | 39.5605 | -121.4292 | 3 SPANS LD SIDE OF 43601 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0018293 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1332825 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE | 4929 | 20180302 | 1850 | 36681 | 932 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 932 | 40.8264 | -121.9415 | 1 POLE SS OF MTR1008043574 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0019282 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333483 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | RECLOSER | 2510 | 20180303 | 1203 | 37423 | 309 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 927 | 40.2105 | -121.1644 | 4 POLES SS OF SW 4729 | Overcast-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0019416 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333616 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 83288 | 20180304 | 757 | 37910 | 873 | Distribution Circuit | Equipment Failure/Involved | Overhead | 215 | 88587 | 39.5275 | -121.2862 | 2 SPANS LD SIDE OF MTR# 1005378545 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019582 | OH | Sus | 0 | No | 2018 | MAR | Yes | Line to Ground | 1333778 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 1413 | 20180304 | 1153 | 37914 | 1507 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 6456 | 39.5926 | -121.2679 | 19 SPANS LD SIDE OF FUCO 1413 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019598 | OH | Sus | 0 | No | 2018 | MAR | Yes | Line to Ground | 1333792 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BUCKS CREEK-1103 | 102211103 | RECLOSER | 1103/2 | 20180315 | 1444 | 44829 | 1061 | Distribution Circuit | Equipment Failure/Involved | Overhead | 321 | 318425 | 39.9117 | -121.3266 | 1 SPAN LD SIDE 18661 | Overcast-Snow-Below 32 F | Insulator | Broken, wire on object | 18-0023120 | OH | Sus | 0 | No | 2018 | MAR | Yes | Line to Ground | 1336061 | INS | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 1937 | 20180319 | 1926 | 48232 | 359 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 359 | 39.4725 | -121.2151 | 3 SPANS LOADSIDE OF 1937 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0024220 | OH | Sus | 43303599 | No | 2018 | MAR | Yes | Line to Ground | 1336926 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 1413 | 20180322 | 602 | 50184 | 713 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 30659 | 39.7486 | -121.5718 | 3 POLES LD SIDE OF 1413 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0025280 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1337492 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WILDWOOD-1101 | 103611101 | FUSE | 1671 | 20180411 | 1444 | 64718 | 815 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 18632 | 40.389 | -123.0596 | MTR # 1008299108 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0031453 | OH | Sus | 31388358 | yes | 2018 | APR | Yes | Multi-Fault | 1342084 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1103 | 102911103 | FUSE | 16821 | 20180415 | 2038 | 67481 | 386 | Distribution Circuit | 3rd Party | Vehicle | 1 | 386 | 39.5362 | -121.4346 | 1 POLE LD SIDE OF FUCO 16821- HWY 162 1 MILE NORTH OF LOAFER CRK TURN OFF | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0032437 | OH | Sus | 0 | yes | 2018 | APR | Yes | Line to Line | 1342929 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CRESCENT MILLS-2101 | 103132101 | FUSE | 18127 | 20180419 | 1320 | 70131 | 180 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 3780 | 40.1501 | -120.789 | MTR# 1008300581 | Partly Cloudy-32-90 F | Insulator | Broken, wire on object | 18-0033768 | OH | Sus | 43328121 | No | 2018 | APR | Yes | Force Out | 1343774 | INS | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1107 | 102911107 | RECLOSER | 37472 | 20180419 | 1317 | 70188 | 751 | Distribution Circuit | 3rd Party | Vehicle | 466 | 36940 | 39.4824 | -121.5036 | 3986 FOOTHILL BLVD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0033766 | OH | Sus | 0 | No | 2018 | APR | Yes | Line to Line | 1343772 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1102 | 102541102 | RECLOSER | 1646 | 20180502 | 2133 | 78557 | 379 | Distribution Circuit | 3rd Party | Vehicle | 543 | 101203 | 40.5007 | -121.9162 | 1ST L&B SS OF MTR# 1006189602 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0037860 | OH | Sus | 43335634 | No | 2018 | MAY | Yes | Line to Ground | 1346466 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1104 | 103521104 | FUSE | 11591 | 20180510 | 2124 | 83447 | 204 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 408 | 40.554 | -122.2886 | 2 LD SIDE OF 11591 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0040023 | OH | Sus | 43344428 | No | 2018 | MAY | Yes | Line to Ground | 1348156 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | OTHER | WIRE DOWN | 20180511 | 951 | 83911 | 326 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 23342 | 39.8183 | -121.6261 | at MTR#1008115181- 13846 NIMSHEW RD | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0040235 | OH | Sus | 0 | yes | 2018 | MAY | Yes | Open Circuit | 1348329 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 1557 | 20180511 | 915 | 83766 | 458 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 458 | 40.4433 | -121.7762 | 4 SPANS SS OF MTR#1009197865 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0040261 | OH | Sus | 0 | yes | 2018 | MAY | Yes | Line to Line | 1348353 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 1905 | 20180512 | 1409 | 84938 | 455 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 86 | 21574 | 39.5172 | -121.2747 | Woodmansee- Matt/1751: wire down at 18826 new york flat rd | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on object | 18-0040536 | OH | Sus | 0 | No | 2018 | MAY | Yes | Line to Line | 1348596 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 9751 | 20180515 | 120 | 86231 | 261 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 3915 | 39.5036 | -121.2776 | MTR#1008144973 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0041048 | OH | Sus | 43347383 | No | 2018 | MAY | Yes | Line to Line | 1349019 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RED BLUFF-1104 | 103541104 | OTHER | WIRE DOWN 1 P/SS OF MTR#1008951490 | 20180519 | 1944 | 89875 | 373 | Distribution Circuit | 3rd Party | Vehicle | 360 | 31980 | 40.2666 | -122.2726 | 1 P/SS OF MTR# 1008951490 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0042559 | OH | Sus | 0 | No | 2018 | MAY | Yes | Line to Ground | 1350143 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | RECLOSER | 9072 | 20180606 | 1554 | 103087 | 710 | Distribution Circuit | 3rd Party | Vehicle | 289 | 205190 | 40.3378 | -122.3717 | 1 SPAN SOUTH OF SBCO 1355 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0048104 | OH | Sus | 31395045 | No | 2018 | JUN | Yes | Line to Line | 1354447 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2560 | 20180608 | 1340 | 104463 | 486 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 566 | 253126 | 39.8888 | -121.6648 | 2 SPANS N/OF CGC# 220975081973 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0048951 | OH | Sus | 31395195 | No | 2018 | JUN | Yes | Line to Ground | 1355069 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | NOTRE DAME-1104 | 102041104 | JUMPER | OJ'S ON HARD TAP FEEDING MTR#1007237258 | 20180616 | 2215 | 111168 | 775 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 3100 | 39.857 | -121.6907 | 15056 BLACK OAK TERR | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0051737 | OH | Sus | 43375777 | yes | 2018 | JUN | Yes | Line to Ground | 1357184 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | FRENCH GULCH-1102 | 103381102 | OTHER | WIRE DOWN S/SIDE OF MTR#5000003304 | 20180622 | 725 | 115164 | 324 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 4236 | 40.6487 | -122.5585 | SS TO MTR#5000003304 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0053474 | OH | Sus | 31397135 | No | 2018 | JUN | Yes | Line to Ground | 1358543 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 7835 | 20180703 | 844 | 123601 | 1766 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7064 | 40.7119 | -122.0865 | 2 S/LD SIDE OF 7835 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0056681 | OH | Sus | 31398822 | No | 2018 | JUL | Yes | Line to Ground | 1361311 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CLARK ROAD-1102 | 103091102 | OTHER | 92622 | 20180707 | 1618 | 126147 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 264 | 4872 | 39.6565 | -121.5745 | Woodmansee- Matt/1751: 2490 cherokee rd | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0057685 | OH | Sus | 31399050 | No | 2018 | JUL | Yes | Line to Ground | 1361982 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1102 | 103401102 | FUSE | 2843 | 20180713 | 1403 | 130873 | 501 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 5535 | 40.5527 | -122.4452 | MTR#1006194068- 9143 CHAPPARREL DR | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0059579 | OH | Sus | 0 | No | 2018 | JUL | Yes | Line to Line | 1363508 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CORNING-1101 | 103331101 | FUSE | 4281 | 20180714 | 1955 | 131931 | 438 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 97 | 3237 | 40.0156 | -122.4333 | 1 SS OF MTR 1008055238 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0059873 | OH | Sus | 0 | No | 2018 | JUL | Yes | Line to Ground | 1363814 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 4523 | 20180716 | 1514 | 133052 | 352 | Distribution Circuit | 3rd Party | Vehicle | 125 | 16896 | 39.7345 | -121.6128 | 2 SS MTR 1003912096 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0060326 | OH | Sus | 0 | No | 2018 | JUL | Yes | Line to Ground | 1364197 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 1311 | 20180718 | 1629 | 134995 | 567 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 19 | 6373 | 40.3542 | -121.579 | HARD TAP FEEDING MTR#1008046483 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0061227 | OH | Sus | 31400333 | yes | 2018 | JUL | Yes | Line to Line | 1364842 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1104 | 103351104 | FUSE | 6615 | 20180720 | 1435 | 136569 | 771 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 3654 | 40.5931 | -122.2516 | MTR#1006231541 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0062118 | OH | Sus | 31400536 | No | 2018 | JUL | Yes | Line to Line | 1365407 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CLARK ROAD-1102 | 103091102 | RECLOSER | 2070 | 20180723 | 1727 | 138513 | 613 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1058 | 183629 | 39.6569 | -121.576 | CORNER OF PENTZ RD & LIME SADDLE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0062874 | OH | Sus | 0 | No | 2018 | JUL | Yes | Line to Ground | 1366056 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1101 | 102831101 | FUSE | 4593 | 20180725 | 42 | 139623 | 493 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 6742 | 39.7778 | -121.6132 | at MTR 1007918484 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0063320 | OH | Sus | 0 | No | 2018 | JUL | Yes | Line to Ground | 1366406 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1101 | 103401101 | SWITCH | 3665 | 20180726 | 1830 | 145466 | 9679 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 42 | 126 | 40.5433 | -122.474 | LD SIDE SW 3665 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0065168 | OH | Sus | 0 | No | 2018 | JUL | Yes | Open Circuit | 1367858 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1102 | 103401102 | JUMPER | OJ 7 SPANS LD SIDE OF 3875 | 20180726 | 1759 | 145314 | 9806 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 8 | 24015 | 40.5669 | -122.4377 | OJ 7 SPANS LD SIDE OF 3875 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0065129 | OH | Sus | 0 | No | 2018 | JUL | Yes | Open Circuit | 1367821 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KESWICK-1101 | 103451101 | FUSE | 2427 | 20180726 | 404 | 143576 | 17989 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 10 | 410 | 40.6111 | -122.4594 | LD SIDE OF 2427 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0063814 | OH | Sus | 31401029 | No | 2018 | JUL | Yes | Line to Ground | 1367515 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 1997 | 20180727 | 1108 | 141768 | 363 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2904 | 39.524 | -121.2954 | MTR#1008707822 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0064384 | OH | Sus | 0 | No | 2018 | JUL | Yes | Line to Line | 1367174 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 7041 | 20180803 | 1631 | 148487 | 274 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 1732 | 40.6221 | -122.2638 | MTR# 1008046355 | Clear-32-90F | Pole-Wood | Broken, wire on object | 18-0066590 | OH | Sus | 0 | No | 2018 | AUG | Yes | Line to Line | 1368920 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1102 | 103521102 | FUSE | 653 | 20180806 | 537 | 149595 | 800 | Distribution Circuit | 3rd Party | Vehicle | 5 | 4000 | 40.6479 | -122.3597 | 1 SPAN FROM L&B TO 10813 TWD 4461 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0066960 | OH | Sus | 0 | No | 2018 | AUG | Yes | Three Phase Fault | 1369260 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE | 6367 | 20180817 | 938 | 157013 | 235 | Distribution Circuit | 3rd Party | Vehicle | 66 | 15510 | 40.2997 | -122.3322 | 2 SPANS LD SIDE FU 6367 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0071042 | OH | Sus | 0 | No | 2018 | AUG | Yes | Line to Ground | 1371498 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PANORAMA-1102 | 103461102 | FUSE | 2005 | 20180818 | 719 | 157476 | 301 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 903 | 40.3859 | -122.177 | MTR# 1009027903 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0071324 | OH | Sus | 0 | No | 2018 | AUG | Yes | Line to Line | 1371693 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | FRENCH GULCH-1101 | 103381101 | TRIP-SAVER | 2905 | 20180820 | 1137 | 158692 | 333 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 92 | 24686 | 40.7199 | -122.6295 | MTR#5000075394 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0071727 | OH | Sus | 31403691 | No | 2018 | AUG | Yes | Three Phase Fault | 1372129 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1105 | 102831105 | RECLOSER | 2438 | 20180820 | 934 | 158521 | 557 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 4299 | 394259 | 39.8142 | -121.58 | 9289 SKYWAY | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0071596 | OH | Sus | 31403686 | No | 2018 | AUG | Yes | Force Out | 1372045 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1101 | 103441101 | RECLOSER | 41356 | 20180831 | 1302 | 166356 | 425 | Distribution Circuit | Vegetation | Tree - fell into line | 351 | 18300 | 40.4772 | -122.4548 | LAST SPAN ON HARD TAP LD SIDE OF CGC118660241679 | Clear-32-90 F | Conductor, Overhead | On Ground | 18-0075616 | OH | Sus | 0 | No | 2018 | AUG | Yes | Multi-Fault | 1375081 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | NOTRE DAME-1104 | 102041104 | FUSE | 26501 | 20180831 | 545 | 166076 | 435 | Distribution Circuit | Animal | Other | 44 | 19140 | 39.843 | -121.6941 | 2 SPANS SOURCE SIDE OF 94725- MTR1007242019 | Clear-32-90 F | Conductor, Overhead | On Ground | 18-0075414 | OH | Sus | 43452052 | No | 2018 | AUG | Yes | Line to Ground | 1374956 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 17423 | 20180914 | 1457 | 174502 | 646 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4522 | 39.9048 | -121.5288 | 1 SPAN EAST OF FUCO 17423 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0079898 | OH | Sus | 0 | No | 2018 | SEP | Yes | Line to Line | 1378080 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1106 | 102831106 | RECLOSER | 762292 | 20180922 | 1459 | 179462 | 688 | Distribution Circuit | 3rd Party | Vehicle | 412 | 44065 | 39.7878 | -121.5975 | 2511 FUCO | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 18-0082429 | OH | Sus | 0 | No | 2018 | SEP | Yes | Multi-Fault | 1379991 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1103 | 102831103 | RECLOSER | 2488 | 20180929 | 1417 | 184053 | 860 | Distribution Circuit | 3rd Party | Vehicle | 785 | 121128 | 39.7411 | -121.6278 | MTR 1007918099 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 18-0084855 | OH | Sus | 0 | No | 2018 | SEP | Yes | Line to Ground | 1381634 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CLARK ROAD-1102 | 103091102 | RECLOSER | 92622 | 20181004 | 1633 | 188566 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 264 | 34646 | 39.6565 | -121.5745 | 3 SPANS SS OF MTR#1007637147 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0087069 | OH | Sus | 43496977 | yes | 2018 | OCT | Yes | Line to Ground | 1383182 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1106 | 102831106 | FUSE | 16189 | 20181004 | 721 | 187999 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 489 | 39.7895 | -121.6576 | 3RD SPAN LD SIDE OF 16189 | Overcast-Drizzle-32-90 F | Conductor, Overhead | On Ground | 18-0086782 | OH | Sus | 43496803 | yes | 2018 | OCT | Yes | Line to Ground | 1383095 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1106 | 102831106 | FUSE | 6383 | 20181007 | 617 | 190013 | 337 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 3845 | 39.7331 | -121.698 | MTR1007459616 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0087825 | OH | Sus | 43498365 | yes | 2018 | OCT | Yes | Line to Ground | 1383802 | CSO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | TYLER-1105 | 103571105 | FUSE | 9163 | 20181026 | 2055 | 203191 | 401 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4812 | 40.1544 | -122.3574 | 18120 JOHNSON RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0094702 | OH | Sus | 43518292 | No | 2018 | OCT | Yes | Line to Line | 1388505 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | SYCAMORE CREEK-1111 | 102971111 | FUSE | 953 | 20181109 | 449 | 212052 | 340 | Distribution Circuit | Animal | Bird found | 35 | 11900 | 39.82 | -121.8433 | 8 SPANS LD SIDE OF FU 953 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0098482 | OH | Sus | 0 | No | 2018 | NOV | Yes | Line to Ground | 1391568 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1102 | 102541102 | RECLOSER | 1502 | 20181122 | 1339 | 222084 | 507 | Distribution Circuit | Vegetation | Tree - fell into line | 1456 | 696298 | 40.4948 | -121.873 | WIRE DOWN LD SIDE/O MTR 1009197853 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102365 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1394512 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 651 | 20181124 | 1127 | 223652 | 1403 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 60329 | 39.446 | -121.3756 | 145 OBERT ROAD | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102802 | OH | Sus | 0 | No | 2018 | NOV | Yes | Line to Ground | 1394878 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KESWICK-1101 | 103451101 | RECLOSER | 1586 | 20181205 | 923 | 234121 | 420 | Distribution Circuit | 3rd Party | Gun Shot | 39 | 10905 | 40.6253 | -122.4632 | WALLER- KEN: BEHIND 14642 IRON MOUNTAIN RD- KESWICK | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0107223 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Force Out | 1397728 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE | 7321 | 20181208 | 257 | 236092 | 630 | Distribution Circuit | 3rd Party | Vehicle | 17 | 10710 | 40.8341 | -121.9247 | BOONE- STAN/1435: 12 spans ld side 7321 fuses | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 18-0108016 | OH | Sus | 0 | No | 2018 | DEC | Yes | Line to Ground | 1398355 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RISING RIVER-1101 | 103551101 | JUMPER | WIRE DOWN | 20181214 | 1230 | 240459 | 752 | Distribution Circuit | Vegetation | Tree - fell into line | 738 | 486567 | 40.9191 | -121.5533 | 1 LD SIDE OF 7709 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0109237 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Open Circuit | 1399744 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CLARK ROAD-1102 | 103091102 | FUSE | 17273 | 20181220 | 741 | 244329 | 424 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 6 | 2544 | 39.7761 | -121.5079 | 2 SPANS LD SIDE OF 17273 | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 18-0110112 | OH | Sus | 0 | No | 2018 | DEC | Yes | Multi-Fault | 1401004 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CLARK ROAD-1102 | 103091102 | FUSE | 68381 | 20181224 | 852 | 246064 | 503 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 10060 | 39.7142 | -121.5214 | 1ST SPAN N/OF MTR#1007696513 | Overcast-Fog-Drizzle-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0110450 | OH | Sus | 43621576 | yes | 2018 | DEC | Yes | Line to Line | 1401529 | CSO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PANORAMA-1102 | 103461102 | RECLOSER | 1632 | 20181225 | 220 | 246879 | 799 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 7990 | 40.4045 | -122.1217 | POLE SAP ID #101510023 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0110617 | OH | Sus | 43621728 | No | 2018 | DEC | Yes | Line to Ground | 1401698 | CSO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1109 | 102911109 | TRIP-SAVER | 5607 | 20181225 | 1642 | 247191 | 161 | Distribution Circuit | Equipment Failure/Involved | Overhead | 95 | 10525 | 39.458 | -121.5132 | 1 SPAN SOURCE SIDE OF FUCO 13723 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110668 | OH | Sus | 43621738 | No | 2018 | DEC | Yes | Line to Ground | 1401752 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1101 | 103031101 | FUSE | 1267 | 20190102 | 1114 | 251987 | 446 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 47 | 5078 | 39.8162 | -121.5813 | 14351 WINCHESTER | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0003648 | OH | Sus | 0 | No | 2019 | JAN | Yes | Line to Ground | 1402763 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BUTTE-1105 | 103081105 | OTHER | HOT WIRE DOWN AT 2637 | 20190105 | 1806 | 254727 | 145 | Distribution Circuit | Vegetation | Tree - fell into line | 1243 | 40486 | 39.7384 | -121.6806 | 5133 OAK HAVEN LN- MAIN LINE FEEDING 2637 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0004913 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403444 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GANSNER-1101 | 103021101 | JUMPER | OJ 4 LD SIDE OF 1797 | 20190107 | 816 | 258822 | 484 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1936 | 40.0039 | -120.9699 | 1 N/OF MTR#1008298345 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005834 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1404202 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CLARK ROAD-1102 | 103091102 | OTHER | WIRE DOWN | 20190109 | 506 | 261330 | 461 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 1229 | 39.7854 | -121.5236 | Sherrod- 1784: COVELO CT ONE SPAND SS OF EOL POLE | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0006686 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1404752 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE | 5435 | 20190109 | 747 | 261319 | 223 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 12198 | 39.6312 | -121.4039 | MTR# 1008143719 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0006728 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1404791 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 11135 | 20190113 | 1218 | 264270 | 235 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 23 | 5405 | 40.6423 | -122.3973 | LD SIDE OF 11135 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0008372 | OH | Sus | 0 | No | 2019 | JAN | Yes | Line to Ground | 1405944 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | RECLOSER | 43008 | 20190211 | 1554 | 300105 | 547 | Distribution Circuit | 3rd Party | Vehicle | 357 | 61084 | 39.7371 | -121.6481 | BRANCH/1770: 3125 neal | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021177 | OH | Sus | 31425364 | yes | 2019 | FEB | Yes | Line to Line | 1414782 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANTLER-1101 | 103271101 | RECLOSER | 1378 | 20190218 | 1733 | 318156 | 4179 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 47527 | 40.8486 | -122.3311 | 3 E/OF 5881- MTR# 1010059218- CGC 119138552620 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025739 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1418783 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | JUMPER | 10895 SS JUMPERS | 20190218 | 938 | 317383 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 464 | 40.331 | -122.4064 | EOL SINGLE PHASE OH SS RCO 10895 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025571 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418620 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | JUMPER | OJ RAINBOW CANYON DR & BOWMAN DR | 20190218 | 1134 | 317678 | 431 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2586 | 40.3312 | -122.394 | 2 P/S/OF RAINBOW CANYON DR & BOWMAN RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025635 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418685 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KESWICK-1101 | 103451101 | OTHER | HOT WIRE DOWN | 20190218 | 1410 | 317765 | 1268 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 24092 | 40.6639 | -122.4995 | 1 POLE LD SIDE OF FUCO 2407 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025709 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418755 | PW | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1101 | 103031101 | FUSE | 17119 | 20190218 | 1530 | 317976 | 288 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 44 | 12672 | 39.8183 | -121.5952 | MTR#1010516783 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025722 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418768 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PANORAMA-1102 | 103461102 | FUSE | 2005 | 20190218 | 928 | 317372 | 3203 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 9609 | 40.3859 | -122.177 | MTR 1009027903 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025567 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418614 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WHITMORE-1101 | 103601101 | FUSE | 7653 | 20190218 | 1314 | 317692 | 3044 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 8298 | 40.7083 | -121.9335 | MTR# 1008771047 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025680 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418725 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1107 | 102911107 | OTHER | WIRE DOWN 2 SS 13231 | 20190218 | 831 | 317327 | 524 | Distribution Circuit | Vegetation | Tree - branch fell on line | 522 | 75415 | 39.498 | -121.389 | MENZEL- KILE/T1778: / 2 SPANS SOURCE SIDE OF 13231 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025562 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1418608 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | JUMPER | OJ'S/1/P/N/1/S/W OF 6587 | 20190219 | 1138 | 318968 | 357 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2142 | 40.3312 | -122.405 | 2 SPANS LD SIDE OF LINE AND BUCK TREE THROUGH LINE | Clear-32-90 F | Conductor, Overhead | On Ground | 19-0026130 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1419008 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KESWICK-1101 | 103451101 | SWITCH | 2735SW | 20190219 | 820 | 318432 | 280 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 280 | 40.6663 | -122.5006 | LD SIDE OF 2735SW | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025881 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1418902 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 1365 | 20190219 | 1404 | 318938 | 546 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3276 | 39.7486 | -121.5751 | 5 SPANS LD SIDE OF 1365 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026115 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1419000 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | JUMPER | OJ'S 1 N/OF 44653 | 20190219 | 840 | 318468 | 630 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 630 | 40.6989 | -122.3211 | LAST POLE ON HARD TAP FEEDING MTR# 1006235667 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0025899 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418908 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1104 | 103351104 | FUSE | 4557 | 20190220 | 1505 | 319618 | 209 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1463 | 40.5087 | -122.2243 | 3 SPANS SS OF MTR#1009936821***40.50871-122.22432 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0026565 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1419243 | CSO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1103 | 103441103 | JUMPER | WIRE DOWN LD SIDE OF 9893 | 20190220 | 1440 | 319841 | 176 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 176 | 40.481 | -122.2994 | 3 LD SIDE OF 9893 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026546 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1419240 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PANORAMA-1102 | 103461102 | OTHER | WIRE DOWN 13 SPANS SS OF 5463 | 20190220 | 816 | 319397 | 488 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 4700 | 40.4011 | -122.1215 | 4 P/S/OF TRANSMISSION POLE 1/18 13 SPANS SS OF 5463 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026435 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1419215 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1106 | 102831106 | FUSE | 1361 | 20190222 | 936 | 321207 | 232 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 41 | 9048 | 39.7752 | -121.6095 | 4 LD SIDE OF FUCO 1361 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0027222 | OH | Sus | 0 | No | 2019 | FEB | Yes | Line to Ground | 1419632 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1102 | 102931102 | RECLOSER | 9026 | 20190225 | 1338 | 323149 | 186 | Distribution Circuit | Equipment Failure/Involved | Overhead | 698 | 120699 | 40.3895 | -122.3431 | 1 SPAN LD SIDE OF REG 3669 | Overcast-Drizzle-Strong Winds-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0027854 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1420040 | CSO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 80454 | 20190225 | 1540 | 323291 | 671 | Distribution Circuit | Vegetation | Tree - fell into line | 242 | 74062 | 40.4341 | -121.8714 | FUCO 56633 | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0027936 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1420062 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | EAST QUINCY-1101 | 102551101 | FUSE | 1749 | 20190228 | 1354 | 328195 | 1571 | Distribution Circuit | Environmental/External | Ice or snow | 3 | 4713 | 39.9266 | -121.0664 | 10 SPANS LD SIDE OF FU 1749 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0029457 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1421105 | PW | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | FUSE | 993 | 20190228 | 1424 | 328202 | 654 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4235 | 39.9594 | -121.7141 | RCO 9655 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029559 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1421125 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 27213 | 20190301 | 1816 | 329235 | 1365 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4095 | 39.7559 | -121.5844 | BRANCH/1770: s/e corner of woddglenn road and nunneley road- paradise | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029873 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1421360 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1105 | 102831105 | OTHER | WIRE DOWN 1437 MAYHEW LN | 20190301 | 859 | 328754 | 202 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 3362 | 39.7822 | -121.5919 | MAYHEW LANE - POLE AT EOL | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029701 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1421271 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | OTHER | WIRE DOWN BET MTR#1008301612 & HARD TAP TO MT | 20190302 | 1348 | 329678 | 712 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 12526 | 40.3524 | -121.5787 | BET MTR#1008301612 & HARD TAP TO MTR#1008046483 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0030117 | OH | Sus | 43689050 | yes | 2019 | MAR | Yes | Line to Ground | 1421573 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 83288 | 20190307 | 335 | 333385 | 623 | Distribution Circuit | Vegetation | Tree - fell into line | 135 | 19123 | 39.5275 | -121.2862 | Sparks- Marty/3864: 4 poles SS/O 1997 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031553 | OH | Sus | 0 | No | 2019 | MAR | Yes | Line to Ground | 1422488 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1106 | 102831106 | FUSE | 17803 | 20190307 | 1524 | 333881 | 715 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 40755 | 39.7777 | -121.5983 | 4 LD SIDE OF 17803 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0031826 | OH | Sus | 0 | No | 2019 | MAR | Yes | Line to Ground | 1422638 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CORNING-1102 | 103331102 | FUSE | 1913 | 20190313 | 1607 | 338768 | 540 | Distribution Circuit | Animal | Bird found | 94 | 21012 | 39.8869 | -122.5411 | 11 SPANS LD SIDE OF 8101 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033617 | OH | Sus | 31428913 | yes | 2019 | MAR | Yes | Line to Ground | 1423960 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1102 | 103441102 | FUSE | 10257 | 20190316 | 1623 | 340932 | 385 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1925 | 40.4516 | -122.4556 | 3 SPANS LD SIDE OF 10257 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0034410 | OH | Sus | 43708968 | No | 2019 | MAR | Yes | Line to Ground | 1424583 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | FUSE | 3133 | 20190319 | 1150 | 342931 | 260 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 2 | 520 | 40.1558 | -120.9423 | 317 COUNTRY RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0035069 | OH | Sus | 0 | No | 2019 | MAR | Yes | Line to Ground | 1425114 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ANTLER-1101 | 103271101 | FUSE | 2417 | 20190321 | 1629 | 344921 | 337 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 25275 | 40.847 | -122.3315 | MTR 1006235610 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0035907 | OH | Sus | 0 | No | 2019 | MAR | Yes | Line to Ground | 1425587 | CAW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ELK CREEK-1101 | 102781101 | FUSE | 3965 | 20190323 | 1647 | 346063 | 318 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 12402 | 39.6138 | -122.5193 | 1 P/E/OF 14703 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0036364 | OH | Sus | 43714791 | No | 2019 | MAR | Yes | Line to Line | 1425916 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ELK CREEK-1101 | 102781101 | FUSE | 3965 | 20190324 | 149 | 346155 | 929 | Distribution Circuit | Environmental/External | Lightning | 39 | 36231 | 39.6138 | -122.5193 | 1 LD SIDE OF FUSES | Partly Cloudy-32-90 F | Transformer (OH) | Broken, wire on ground | 19-0036429 | OH | Sus | 31430503 | No | 2019 | MAR | Yes | Line to Ground | 1425977 | TXO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1104 | 103351104 | FUSE | 4303 | 20190409 | 731 | 356265 | 202 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 9292 | 40.5703 | -122.272 | 1ST SPAN LD SIDE OF 4303 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0040746 | OH | Sus | 31433281 | yes | 2019 | APR | Yes | Line to Line | 1428948 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 1475 | 20190416 | 156 | 361439 | 408 | Distribution Circuit | Vegetation | Tree - branch fell on line | 237 | 31098 | 40.686 | -122.141 | 1 SPAN SOURCE SIDE TO 7249 HARD TAP TO SOUTH | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0042721 | OH | Sus | 0 | No | 2019 | APR | Yes | Line to Line | 1430398 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 1406 | 20190419 | 952 | 363703 | 1096 | Distribution Circuit | 3rd Party | Vehicle | 178 | 64056 | 39.5731 | -121.3176 | 4 POLES LD SIDE OF 793 ON MAINLINE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0044334 | OH | Sus | 0 | No | 2019 | APR | Yes | Line to Line | 1431567 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CLARK ROAD-1102 | 103091102 | RECLOSER | 2070 | 20190428 | 1236 | 369637 | 389 | Distribution Circuit | Equipment Failure/Involved | Overhead | 400 | 79810 | 39.6565 | -121.5762 | JUST S/OF MTR#1007919112 ON MAINLINE- PENTZ ROAD S/O LIME SADDLE- TRANS POLE 1/12 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0046853 | OH | Sus | 43754474 | No | 2019 | APR | Yes | Line to Ground | 1433256 | CSO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 85143 | 20190501 | 1050 | 371641 | 919 | Distribution Circuit | 3rd Party | Aircraft | 8 | 7352 | 40.3619 | -121.5123 | MULTIPLE LOCATIONS LD SIDE OF 85143 FUSES | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0047921 | OH | Sus | 31437577 | No | 2019 | MAY | Yes | Multi-Fault | 1433975 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | FUSE | 3313 | 20190515 | 2030 | 381368 | 322 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 10948 | 40.73 | -122.3239 | MTR 1006191212 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052322 | OH | Sus | 43783209 | yes | 2019 | MAY | Yes | Line to Ground | 1436965 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 1064 | 20190516 | 2023 | 383079 | 290 | Distribution Circuit | Vegetation | Tree - fell into line | 202 | 23930 | 39.482 | -121.2419 | 16850 SESAME ST | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053024 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Multi-Fault | 1437412 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | RECLOSER | 1804 | 20190518 | 1702 | 384396 | 549 | Distribution Circuit | Vegetation | Tree - fell into line | 885 | 120033 | 39.39 | -121.4043 | MTR 1007888649 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0053696 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Three Phase Fault | 1437915 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1102 | 102931102 | RECLOSER | 9026 | 20190527 | 430 | 391067 | 626 | Distribution Circuit | 3rd Party | Vehicle | 698 | 200193 | 40.3895 | -122.3431 | 1 W/O 17736 GAS POINT RD | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0057923 | OH | Sus | 0 | No | 2019 | MAY | Yes | Multi-Fault | 1441440 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1107 | 102911107 | FUSE | 23101 | 20190530 | 1822 | 393889 | 396 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 8316 | 39.4871 | -121.4481 | 156 WAKEFIELD | Overcast-Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0060313 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Line | 1443357 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | OTHER | WIRE DOWN 4 SP LD SD SB 87953 | 20190531 | 1523 | 394676 | 772 | Distribution Circuit | Equipment Failure/Involved | Overhead | 242 | 55546 | 40.4456 | -121.816 | 4 LD SIDE OF SBCO 87953 | Partly Cloudy-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0060901 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Open Circuit | 1443797 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 85567 | 20190601 | 1911 | 395403 | 1239 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 8673 | 40.3558 | -121.8935 | BELL- J/1836: 18P E/O FUCO 85567 | Partly Cloudy-Drizzle-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0061447 | OH | Sus | 31450148 | yes | 2019 | JUN | Yes | Line to Ground | 1444302 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1101 | 103031101 | FUSE | 17203 | 20190603 | 802 | 396208 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 4396 | 39.8531 | -121.5951 | 15060 TRAILS END RD- S/E CORNER OF TRAILS END ROAD AND CROSSROADS RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0061813 | OH | Sus | 31450223 | yes | 2019 | JUN | Yes | Line to Line | 1444654 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | OTHER | WIRE DOWN 3 SP LD SD 43601 | 20190604 | 2002 | 397982 | 475 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1192 | 554069 | 39.5614 | -121.4282 | 3 LD SIDE OF SBCO 43601 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0062777 | OH | Sus | 43822598 | yes | 2019 | JUN | Yes | Open Circuit | 1445315 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | SYCAMORE CREEK-1111 | 102971111 | FUSE | 943 | 20190609 | 1602 | 402690 | 225 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 8082 | 39.8995 | -121.7407 | 99 HARVEY RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0064881 | OH | Sus | 0 | yes | 2019 | JUN | Yes | Line to Line | 1447197 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1101 | 103751101 | RECLOSER | 641808 | 20190623 | 736 | 426691 | 492 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 168 | 75808 | 39.7404 | -121.4965 | ROGERS- JIM/ 559-240-4392: 1 SPAN W/O C/O2757 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0071198 | OH | Sus | 43854847 | No | 2019 | JUN | Yes | Line to Ground | 1452026 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 23519 | 20190623 | 1202 | 426819 | 703 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2109 | 39.4183 | -121.2923 | SPARKS- MARTY/3864: 10 spans L/O/S of c/o's23519 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0071257 | OH | Sus | 43854811 | No | 2019 | JUN | Yes | Line to Ground | 1452082 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | OTHER | WIRE DOWN @ MTR 1009068741 | 20190624 | 411 | 427275 | 438 | Distribution Circuit | Equipment Failure/Involved | Overhead | 806 | 288388 | 39.6255 | -121.4348 | B & C Guild Hall- MTR#1009068741 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0071340 | OH | Sus | 43855284 | No | 2019 | JUN | Yes | Line to Ground | 1452164 | CSO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1107 | 102911107 | FUSE | 13187 | 20190630 | 2321 | 438364 | 351 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1053 | 39.4724 | -121.4903 | JUST LD SIDE OF 13187 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0073497 | OH | Sus | 43862384 | No | 2019 | JUN | Yes | Line to Ground | 1453766 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RED BLUFF-1103 | 103541103 | FUSE | 85399 | 20190716 | 1729 | 454788 | 271 | Distribution Circuit | Vegetation | Tree - fell into line | 175 | 45533 | 40.1648 | -122.2896 | 19720 PINE CREEK RD. | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 19-0078094 | OH | Sus | 31457644 | No | 2019 | JUL | Yes | Three Phase Fault | 1456650 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | TRIP-SAVER | 18205 | 20190725 | 1500 | 471840 | 1220 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 12000 | 40.2961 | -121.1335 | 541 CATFISH BEACH RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0081291 | OH | Sus | 0 | No | 2019 | JUL | Yes | Three Phase Fault | 1458719 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 1555 | 20190725 | 1104 | 471273 | 533 | Distribution Circuit | Equipment Failure/Involved | Overhead | 77 | 41041 | 40.4391 | -121.8503 | 5 P/W/O MTR 1008260052 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0081162 | OH | Sus | 43898296 | No | 2019 | JUL | Yes | Line to Line | 1458692 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PANORAMA-1102 | 103461102 | FUSE | 2005 | 20190727 | 822 | 473039 | 152 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 456 | 40.3859 | -122.177 | MTR#1009027903 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0081756 | OH | Sus | 0 | No | 2019 | JUL | Yes | Line to Line | 1459046 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RED BLUFF-1104 | 103541104 | SWITCH | 113623 | 20190824 | 825 | 535136 | 212 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 718 | 40.3295 | -122.1899 | OD BANK SS/OF SW 2887 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0091736 | OH | Sus | 31467267 | No | 2019 | AUG | Yes | Force Out | 1465503 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | OTHER | WIRE DOWN @ 707 FUCO | 20190826 | 1259 | 539798 | 636 | Distribution Circuit | 3rd Party | Vehicle | 460 | 45047 | 39.4509 | -121.2825 | AT 707 FUCO POLE | Clear-32-90 F | Pole-Wood | Broken, wire on object | 19-0092264 | OH | Sus | 0 | No | 2019 | AUG | Yes | Open Circuit | 1465930 | PW | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 1811 | 20190827 | 2042 | 543098 | 350 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 7630 | 39.4456 | -121.2771 | MTR 1005545248 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0092810 | OH | Sus | 43939470 | No | 2019 | AUG | Yes | Line to Line | 1466214 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1101 | 103351101 | OTHER | 1380 | 20190829 | 106 | 545959 | 260 | Distribution Circuit | Equipment Failure/Involved | Overhead | 583 | 125057 | 40.5607 | -122.1889 | WIRE DOWN 1 S/OF AND 1 E/OF 10763 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0093318 | OH | Sus | 31469884 | No | 2019 | AUG | Yes | Line to Ground | 1466489 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ELK CREEK-1101 | 102781101 | FUSE | 14381 | 20190831 | 133 | 549294 | 787 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 8657 | 39.3113 | -122.4791 | MTR 1009904172 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0094287 | OH | Sus | 0 | No | 2019 | AUG | Yes | Line to Ground | 1466955 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 80454 | 20190908 | 709 | 562391 | 768 | Distribution Circuit | Equipment Failure/Involved | Overhead | 242 | 59774 | 40.4341 | -121.8714 | 8 SPANS W/OF 5493 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0096539 | OH | Sus | 31471043 | No | 2019 | SEP | Yes | Line to Ground | 1468449 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE | 5561 | 20190914 | 1552 | 582776 | 424 | Distribution Circuit | 3rd Party | Vehicle | 13 | 4052 | 40.2987 | -122.3952 | NEAR 17020 PRENTICE RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0099167 | OH | Sus | 0 | No | 2019 | SEP | Yes | Line to Line | 1470052 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1107 | 102911107 | JUMPER | OJ'S 3 SPAN SS OF MTR#1008115362 | 20190927 | 1954 | 624039 | 359 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 359 | 39.4523 | -121.4632 | at MTR#1008115362 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0104821 | OH | Sus | 43973474 | No | 2019 | SEP | Yes | Line to Ground | 1473575 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | OTHER | WIRE DOWN | 20191021 | 710 | 676077 | 580 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 9714 | 39.3698 | -121.4308 | 3 SPANS SS OF MTR 1009395787 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0114002 | OH | Sus | 0 | No | 2019 | OCT | Yes | Line to Ground | 1481561 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CLARK ROAD-1102 | 103091102 | RECLOSER | 47006 | 20191111 | 2151 | 704639 | 966 | Distribution Circuit | 3rd Party | Vehicle | 124 | 50112 | 39.6987 | -121.5742 | 17133 RISER CUTOUTS PARADISE | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0123664 | OH | Sus | 0 | No | 2019 | NOV | Yes | Three Phase Fault | 1490540 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1103 | 102931103 | FUSE | 10447 | 20191214 | 2015 | 739918 | 620 | Distribution Circuit | Environmental/External | Lightning | 1 | 620 | 40.348 | -122.2203 | EOL AT TRANSF#119406136855 | Overcast-32-90 F | Transformer (OH) | Broken, wire on ground | 19-0136599 | OH | Sus | 0 | No | 2019 | DEC | Yes | Three Phase Fault | 1500706 | TXO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PANORAMA-1101 | 103461101 | RECLOSER | 713592 | 20191214 | 1756 | 739879 | 674 | Distribution Circuit | Environmental/External | Lightning | 785 | 67522 | 40.3776 | -122.2114 | ON HARD TAP FEEDING MTR#1008365283 | Overcast-Lightning-32-90 F | Transformer (OH) | Broken, wire on ground | 19-0136590 | OH | Sus | 0 | No | 2019 | DEC | Yes | Line to Line | 1500698 | TXO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1102 | 102541102 | RECLOSER | 93418 | 20191216 | 749 | 740962 | 514 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 731 | 119126 | 40.5138 | -121.7868 | LD SIDE OF FUSES 1531(HWY 44 N/O VIOLA CONE AT ROAD) | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0136714 | OH | Sus | 31481636 | No | 2019 | DEC | Yes | Multi-Fault | 1500900 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1102 | 102541102 | FUSE | 1531 | 20191217 | 1313 | 744735 | 356 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 51 | 18156 | 40.5228 | -121.6813 | 6 SPANS SOURCE SIDE OF 7707 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0136993 | OH | Sus | 31482803 | yes | 2019 | DEC | Yes | Line to Line | 1501478 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RED BLUFF-1105 | 103541105 | FUSE | 85631 | 20200123 | 2232 | 769057 | 148 | Distribution Circuit | 3rd Party | Vehicle | 180 | 26640 | 40.2025 | -122.2266 | MTR 1009872674 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 20-0013053 | OH | Sus | 0 | No | 2020 | JAN | Yes | Multi-Fault | 1508821 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 3-2101 | 103732101 | RECLOSER | 1386 | 20200128 | 1606 | 772054 | 92 | Distribution Circuit | Equipment Failure/Involved | Overhead | 63 | 4592 | 41.0214 | -121.6772 | 1/SP/LD SIDE OF 7229 | Partly Cloudy-32-90 F | Insulator | Broken, wire on object | 20-0014706 | OH | Sus | 0 | No | 2020 | JAN | Yes | Force Out | 1509903 | INS | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RED BLUFF-1101 | 103541101 | FUSE | 85365 | 20200205 | 1628 | 778782 | 646 | Distribution Circuit | 3rd Party | Vehicle | 15 | 9690 | 40.2212 | -122.3583 | 3 SPANS LD SIDE OF 85365 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0017894 | OH | Sus | 0 | No | 2020 | FEB | Yes | Line to Ground | 1512207 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CEDAR CREEK-1101 | 103321101 | OCB | 1101/2 | 20200308 | 2205 | 838783 | 584 | Distribution Circuit | Equipment Failure/Involved | Overhead | 791 | 311872 | 40.7909 | -121.9381 | 1 SPAN LD SIDE OF 882937 & 10 SPANS LD SIDE OF 4131 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0029931 | OH | Sus | 44232384 | No | 2020 | MAR | Yes | Line to Line | 1520181 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1101 | 103751101 | FUSE | 7149 | 20200309 | 1352 | 840755 | 238 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 952 | 39.6898 | -121.458 | 4 SP SS OF EOL at LINE & BUCK | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0030184 | OH | Sus | 31494619 | No | 2020 | MAR | Yes | Line to Ground | 1520328 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RISING RIVER-1101 | 103551101 | RECLOSER | 9032 | 20200314 | 304 | 851068 | 526 | Distribution Circuit | Vegetation | Tree - fell into line | 319 | 90392 | 40.7801 | -121.5032 | 5 SPANS SS OF 721 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0032028 | OH | Sus | 31496902 | yes | 2020 | MAR | Yes | Line to Ground | 1521359 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | OTHER | WIRE DOWN SAP ID 103144868 | 20200317 | 447 | 856213 | 604 | Distribution Circuit | Vegetation | Tree - branch fell on line | 444 | 228015 | 39.5993 | -121.0749 | SAP ID 103144868 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0033131 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Ground | 1522278 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | OTHER | WIRE DOWN MTR#1008256607 | 20200317 | 505 | 856207 | 706 | Distribution Circuit | Equipment Failure/Involved | Overhead | 242 | 88925 | 40.4403 | -121.8501 | MTR# 1008256607 | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0033129 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Ground | 1522277 | CAW | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | OTHER | 3/P/E/OF 2605 BALD ROCK RD | 20200317 | 753 | 856522 | 595 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 21471 | 39.6362 | -121.3475 | 3/P/E/OF 2605 BALD ROCK RD | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0033281 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Ground | 1522363 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | FUSE | 1821 | 20200318 | 931 | 857682 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 20475 | 40.2588 | -121.1364 | 7/SP/LD SIDE OF 1821 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 20-0033744 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Line | 1522686 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | OTHER | WIRE DOWN 2 SPANS LD SIDE OF 48813 | 20200318 | 717 | 857732 | 605 | Distribution Circuit | Equipment Failure/Involved | Overhead | 543 | 185969 | 40.3449 | -121.6141 | 2 SPANS LD SIDEOF FUCO 48813 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0033752 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Force Out | 1522694 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1101 | 103401101 | FUSE | 4139 | 20200326 | 1023 | 866593 | 516 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 3300 | 40.5182 | -122.5036 | MTR 1006196155 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0036360 | OH | Sus | 0 | No | 2020 | MAR | Yes | Line to Ground | 1524079 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | OTHER | 88575 | 20200406 | 744 | 884998 | 445 | Distribution Circuit | Vegetation | Tree - fell into line | 184 | 81880 | 39.6544 | -121.0216 | 8 SPANS LD SIDE OF CGC 222821573301 | Overcast-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0038864 | OH | Sus | 0 | yes | 2020 | APR | Yes | Line to Ground | 1525655 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 1415 | 20200411 | 612 | 893776 | 676 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2028 | 39.8287 | -121.6239 | at CGC# 221062378866 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0040561 | OH | Sus | 0 | No | 2020 | APR | Yes | Line to Line | 1526649 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | FUSE | 3419 | 20200415 | 1249 | 895943 | 500 | Distribution Circuit | 3rd Party | Vehicle | 47 | 10365 | 40.1519 | -120.9553 | 3 SPANS LD SIDE OF 3419 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0041634 | OH | Sus | 0 | No | 2020 | APR | Yes | Line to Ground | 1527358 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | RECLOSER | 1974 | 20200421 | 117 | 898497 | 623 | Distribution Circuit | 3rd Party | Vehicle | 625 | 374495 | 39.6394 | -121.4297 | 6/SP/LD SIDE OF MTR # 1008984343 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0043090 | OH | Sus | 0 | No | 2020 | APR | Yes | Line to Line | 1528182 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1107 | 102911107 | FUSE | 13513 | 20200423 | 1439 | 900175 | 329 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3290 | 39.4307 | -121.4303 | 2 LD SIDE OF FUCO 13513 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0044152 | OH | Sus | 31501136 | No | 2020 | APR | Yes | Multi-Fault | 1528745 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CLARK ROAD-1102 | 103091102 | FUSE | 1501 | 20200429 | 1533 | 903942 | 448 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 26 | 11648 | 39.5723 | -121.5191 | 3 SPANS SS OF MTR 1008116457 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0045697 | OH | Sus | 44306087 | No | 2020 | APR | Yes | Force Out | 1529873 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CORNING-1102 | 103331102 | FUSE | 850211 | 20200511 | 1151 | 911206 | 506 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2018 | 39.915 | -122.4311 | CGC# 118740721130 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0049215 | OH | Sus | 31502764 | yes | 2020 | MAY | Yes | Line to Line | 1531981 | CAW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | RECLOSER | 1974 | 20200607 | 1040 | 933447 | 383 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 625 | 53995 | 39.6394 | -121.4297 | CAMPBELL- SCOTT/1671: tree thru pri | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0058595 | OH | Sus | 31505311 | yes | 2020 | JUN | Yes | Line to Ground | 1537826 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GIRVAN-1101 | 103401101 | FUSE | 5017 | 20200623 | 1619 | 945538 | 276 | Distribution Circuit | Equipment Failure/Involved | Overhead | 33 | 8339 | 40.5007 | -122.5429 | MTR 1009717391 | Clear-Above 90 | Conductor, Overhead | Broken, wire on object | 20-0064146 | OH | Sus | 44363875 | yes | 2020 | JUN | Yes | Line to Ground | 1541888 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | NOTRE DAME-1104 | 102041104 | OTHER | WIRE DOWN 1/S/SS OF CGC 220866579257 | 20200710 | 139 | 961346 | 608 | Distribution Circuit | Vegetation | Tree - fell into line | 138 | 23888 | 39.8419 | -121.693 | 1/S/LD SIDE AND 1/S/SS OF CGC 220866579257 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0070340 | OH | Sus | 31508159 | No | 2020 | JUL | Yes | Open Circuit | 1545572 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1103 | 102911103 | FUSE | 13747 | 20200715 | 1121 | 965336 | 335 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 27 | 5485 | 39.6253 | -121.3921 | MENZEL- KILE/T1778: 259 hidden springs rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0072240 | OH | Sus | 44391579 | yes | 2020 | JUL | Yes | Line to Ground | 1546900 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CORNING-1101 | 103331101 | RECLOSER | 85162 | 20200717 | 1149 | 966676 | 444 | Distribution Circuit | 3rd Party | Vehicle | 883 | 347078 | 39.9385 | -122.4044 | 1 W/OF 85035 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0073067 | OH | Sus | 0 | No | 2020 | JUL | Yes | Line to Line | 1547380 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CORNING-1102 | 103331102 | RECLOSER | 53184 | 20200804 | 1158 | 978619 | 260 | Distribution Circuit | Animal | Bird found | 216 | 29250 | 39.9132 | -122.4295 | PASKENTA RD & CORNING RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0079535 | OH | Sus | 31510529 | No | 2020 | AUG | Yes | Line to Ground | 1551646 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 1939 | 20200805 | 1241 | 979432 | 348 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 15312 | 39.4498 | -121.1976 | MAYS- S / 2497: tree knocked down wire | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0080060 | OH | Sus | 44410642 | yes | 2020 | AUG | Yes | Line to Line | 1551990 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | FUSE | 1967 | 20200811 | 615 | 991130 | 968 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 6679 | 39.506 | -121.2051 | MTR 1010466728 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0081926 | OH | Sus | 0 | No | 2020 | AUG | Yes | Line to Ground | 1553165 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1104 | 103351104 | FUSE | 6609 | 20200821 | 1131 | 1026377 | 566 | Distribution Circuit | 3rd Party | Vehicle | 34 | 3868 | 40.5922 | -122.2448 | MTR 5000101356 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0088530 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Multi-Fault | 1557849 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ELK CREEK-1101 | 102781101 | OCB | 1101/2 | 20200827 | 432 | 1033493 | 757 | Distribution Circuit | Equipment Failure/Involved | Overhead | 903 | 460057 | 39.5933 | -122.5435 | FUCO 65167 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0090534 | OH | Sus | 0 | No | 2020 | AUG | Yes | Three Phase Fault | 1559194 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 23519 | 20200901 | 1015 | 1046213 | 703 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2109 | 39.4181 | -121.2926 | 10 POLES LD SIDE OF 23519 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0092191 | OH | Sus | 0 | No | 2020 | SEP | Yes | Line to Ground | 1560265 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1102 | 103751102 | RECLOSER | 1102/2 | 20200928 | 1545 | 1096947 | 369 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 9 | 3321 | 39.6769 | -121.4916 | 2ND & 3RD POLES W/OF 5403 | Clear-Above 90 | Crossarm, Wood | Broken, wire on ground | 20-0102526 | OH | Sus | 0 | yes | 2020 | SEP | Yes | Line to Line | 1566932 | CAW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1105 | 102831105 | RECLOSER | 829194 | 20200928 | 2151 | 1097261 | 538 | Distribution Circuit | Vegetation | Tree - fell into line | 345 | 33623 | 39.8256 | -121.5976 | C/OUT 17979 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0102640 | OH | Sus | 0 | yes | 2020 | SEP | Yes | Line to Ground | 1566973 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 6533 | 20201001 | 2157 | 1105944 | 969 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 17442 | 39.8952 | -121.6629 | 5085 PINE WAY - SAP 100437944 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0104258 | OH | Sus | 0 | yes | 2020 | OCT | Yes | Line to Ground | 1567848 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1101 | 102931101 | JUMPER | WIRE DOWN @ SAP ID 101511399 | 20201015 | 702 | 1118349 | 646 | Distribution Circuit | 3rd Party | Vehicle | 221 | 131766 | 40.3237 | -122.4294 | SAP ID 101511399 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0109022 | OH | Sus | 0 | yes | 2020 | OCT | Yes | Open Circuit | 1571046 | PW | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1101 | 102931101 | FUSE | 1375 | 20201015 | 1356 | 1118585 | 265 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 8480 | 40.3635 | -122.3465 | 19560 EIGHMY RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0109282 | OH | Sus | 0 | yes | 2020 | OCT | Yes | Force Out | 1571144 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CORNING-1101 | 103331101 | JUMPER | OJ 1/P/W/OF MTR 5000064526 | 20201106 | 728 | 1137181 | 492 | Distribution Circuit | 3rd Party | Vehicle | 6 | 2952 | 40.0197 | -122.4479 | LAUGHLIN- RONALD /4251: SUTTER CT -- JI2I: MTR 5000064526 | Clear-32-90 F | Pole-Wood | Broken, wire on object | 20-0117659 | OH | Sus | 0 | No | 2020 | NOV | Yes | Force Out | 1577412 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1105 | 102831105 | JUMPER | WIRE DOWN | 20201108 | 2013 | 1139806 | 694 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 11 | 7380 | 39.8097 | -121.604 | BETWEEN 13773 & 13769 FERGUSON DR | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0118592 | OH | Sus | 0 | No | 2020 | NOV | Yes | Open Circuit | 1578209 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1105 | 102831105 | FUSE | 17403 | 20201206 | 2133 | 1167236 | 651 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 15624 | 39.8228 | -121.5948 | MTR 1007883611 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0128353 | OH | Sus | 0 | No | 2020 | DEC | Yes | Line to Line | 1584922 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | OCB | 1101/2 | 20201207 | 30 | 1167244 | 1018 | Distribution Circuit | Vegetation | Tree - fell into line | 702 | 714124 | 39.4857 | -121.2201 | 8/LD SIDE OF 1913 | Clear-32-90 F | Conductor, Overhead | On Ground | 20-0128355 | OH | Sus | 0 | No | 2020 | DEC | Yes | Three Phase Fault | 1584923 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 1139 | 20201207 | 148 | 1168133 | 869 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5214 | 39.9027 | -121.5274 | SAP ID# 100361113 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0128462 | OH | Sus | 0 | No | 2020 | DEC | Yes | Force Out | 1585067 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1105 | 102831105 | JUMPER | UNMAPPED FUSES 270331 | 20201207 | 47 | 1168429 | 1084 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1084 | 39.7863 | -121.5891 | 2 POLES LD SIDE OF 270331 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0128488 | OH | Sus | 0 | No | 2020 | DEC | Yes | Force Out | 1585092 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | RECLOSER | 80670 | 20201229 | 546 | 1200562 | 302 | Distribution Circuit | Vegetation | Tree - fell into line | 169 | 48374 | 39.3882 | -121.4056 | 5125 LA PORTE RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0132138 | OH | Sus | 44597654 | No | 2020 | DEC | Yes | Line to Line | 1589920 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1104 | 102831104 | FUSE | 4533 | 20210104 | 1132 | 1203677 | 359 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 2739 | 39.7409 | -121.5937 | 1 POLE SS/OF MTR# 1007692508 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0004719 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1590724 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GIRVAN-1101 | 103401101 | FUSE | 3489 | 20210114 | 823 | 1210211 | 301 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 10 | 3010 | 40.5055 | -122.5471 | 2 N/OF 7741 ZOGG MINE RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0008596 | OH | Sus | 44624980 | No | 2021 | JAN | Yes | Force Out | 1593064 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ORO FINO-1102 | 103031102 | FUSE | 16659 | 20210120 | 1021 | 1218946 | 354 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 18184 | 40.1127 | -121.4675 | SAP ID # 100342797 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0011591 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1595147 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | MC ARTHUR-1101 | 103491101 | FUSE | 2459 | 20210123 | 1046 | 1221758 | 339 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 22866 | 41.1188 | -121.3322 | 44900 OLD BROWN RANCH RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013276 | OH | Sus | 44633167 | No | 2021 | JAN | Yes | Line to Ground | 1596229 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANTLER-1101 | 103271101 | FUSE | 8285 | 20210129 | 1559 | 1242134 | 158 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 2212 | 40.8776 | -122.3622 | 18950 CLAUS LN | Snow- | Conductor, Overhead | Broken, wire on ground | 21-0018578 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1600463 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | GIRVAN-1101 | 103401101 | RECLOSER | 1330 | 20210129 | 1254 | 1241896 | 7 | Distribution Circuit | Equipment Failure/Involved | Overhead | 364 | 2548 | 40.5176 | -122.5057 | TAP TWD CGC 118565543624 | Snow- | Conductor, Overhead | Broken, wire on ground | 21-0018419 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1600352 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1101 | 103561101 | FUSE | 3313 | 20210129 | 1904 | 1242579 | 129 | Distribution Circuit | Environmental/External | Ice or snow | 34 | 4386 | 40.73 | -122.3239 | REGINATO- A/1820: SAME | Snow- | Conductor, Overhead | Broken, wire on ground | 21-0018691 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1600550 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CORNING-1102 | 103331102 | FUSE | 2029 | 20210130 | 2016 | 1243586 | 1349 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 10792 | 40.0146 | -122.5712 | 1/SP/SS/OF MTR# 1009949674 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0019928 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1601778 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RISING RIVER-1101 | 103551101 | JUMPER | WIRE DOWN 29 SPANS LD SIDE OF 7711 | 20210202 | 332 | 1245641 | 554 | Distribution Circuit | Equipment Failure/Involved | Overhead | 551 | 297458 | 40.8791 | -121.556 | 29 SPANS LD SIDE OF 7711 -- CENTER PHASE | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 21-0020691 | OH | Sus | 0 | No | 2021 | FEB | Yes | Open Circuit | 1602336 | CSO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GANSNER-1101 | 103021101 | FUSE | 1379 | 20210211 | 1029 | 1253013 | 149 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 149 | 40.0408 | -120.9702 | 7 SPANS LD SIDE OF 1379 | Clear-32-90F | Conductor, Overhead | On Ground | 21-0024464 | OH | Sus | 44650917 | No | 2021 | FEB | Yes | Line to Ground | 1604562 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1102 | 103441102 | FUSE | 6379 | 20210212 | 53 | 1253457 | 618 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 1806 | 40.4308 | -122.4314 | MTR 5000072957 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 21-0024829 | OH | Sus | 0 | No | 2021 | FEB | Yes | Line to Ground | 1604702 | CAW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 1064 | 20210222 | 1316 | 1259542 | 304 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 200 | 48662 | 39.4819 | -121.2418 | 1 SPAN LD SIDE OF SAP ID 100406956 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0028165 | OH | Sus | 31531120 | No | 2021 | FEB | Yes | Line to Ground | 1606901 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | FUSE | 1683 | 20210306 | 18 | 1270885 | 641 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 71792 | 40.2946 | -121.0529 | MTR# 108570506 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0032936 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1609999 | CAW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1101 | 103751101 | FUSE | 1715 | 20210310 | 1120 | 1277567 | 538 | Distribution Circuit | Environmental/External | Ice or snow | 7 | 3766 | 39.7413 | -121.4954 | BETWEEN THE 3RD & 4TH POLE LD SIDE OF 1715 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0034823 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1611076 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1102 | 103751102 | RECLOSER | 1102/2 | 20210310 | 1010 | 1277213 | 532 | Distribution Circuit | Vegetation | Tree - fell into line | 303 | 157117 | 39.6769 | -121.4916 | 2 SPANS LD SIDE OF CGC# 221595972359 ON THE MAIN LINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0034537 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1610981 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 717 | 20210310 | 344 | 1276618 | 304 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3040 | 39.4554 | -121.2472 | 4 SPANS LD SIDE OF FU 717 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0034308 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1610843 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 1811 | 20210310 | 900 | 1277105 | 382 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 19482 | 39.4448 | -121.2767 | SPARKS- MARTY/3864: 9060 Seven Spring Trl | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0034579 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Line | 1610999 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | RECLOSER | 83288 | 20210310 | 1000 | 1277192 | 276 | Distribution Circuit | Vegetation | Tree - fell into line | 137 | 29276 | 39.5275 | -121.2861 | 6 SPANS N/OF FUCO 23377 ON MAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0034529 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Line | 1610977 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1107 | 102911107 | SWITCH | 1929 | 20210310 | 1453 | 1277592 | 7 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 679 | 39.4963 | -121.3221 | 6 SPANS SS OF 23377 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0034529 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1611082 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 648743 | 20210311 | 1035 | 1278695 | 458 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 5954 | 39.5184 | -121.2575 | 4 SPANS LD SIDE OF 648743 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0035323 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1611411 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 80454 | 20210315 | 401 | 1282447 | 732 | Distribution Circuit | Vegetation | Tree - fell into line | 242 | 159655 | 40.4341 | -121.8715 | 4 SPANS LD SIDE OF FUCO 56503 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0036350 | OH | Sus | 0 | No | 2021 | MAR | Yes | Three Phase Fault | 1612051 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 85567 | 20210315 | 950 | 1282868 | 427 | Distribution Circuit | Environmental/External | Ice or snow | 6 | 2562 | 40.3559 | -121.8936 | 2 SPANS W/ MTR# 1010425652 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0036637 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1612277 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1101 | 102931101 | FUSE | 10757 | 20210327 | 647 | 1300144 | 590 | Distribution Circuit | 3rd Party | Vehicle | 6 | 1380 | 40.3452 | -122.4608 | WALLER- KEN 1372: S/W CORNER OF EVERGREEN AND LUCE &GRISWOLD RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0041728 | OH | Sus | 35239655 | No | 2021 | MAR | Yes | Line to Ground | 1615467 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | OTHER | WIRE DOWN 7 SPANS LD SIDE 5923 | 20210405 | 1225 | 1307186 | 351 | Distribution Circuit | Equipment Failure/Involved | Overhead | 453 | 135253 | 39.5911 | -121.0765 | MAYS- S / 2497: wire has bad spots in it and it fell // 7 SPANS LD SIDE 5923 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0044805 | OH | Sus | 31535316 | No | 2021 | APR | Yes | Open Circuit | 1617735 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1102 | 102541102 | FUSE | 1489 | 20210417 | 230 | 1320498 | 816 | Distribution Circuit | 3rd Party | Vehicle | 65 | 21288 | 40.52 | -121.9328 | at LINE AND BUCK POLE FEEDING MTR#1009768656 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0049851 | OH | Sus | 0 | No | 2021 | APR | Yes | Line to Ground | 1620861 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1101 | 103751101 | JUMPER | WIRE DOWN | 20210418 | 538 | 1321713 | 462 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1848 | 39.6854 | -121.4555 | 4 SPANS LD SIDE OF 7149 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0050012 | OH | Sus | 0 | No | 2021 | APR | Yes | Line to Ground | 1621021 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | RECLOSER | 31502 | 20210421 | 1546 | 1327412 | 327 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1670 | 165445 | 39.3862 | -121.4014 | 13498 DIXON HILL RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0051546 | OH | Sus | 0 | No | 2021 | APR | Yes | Line to Ground | 1622104 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1102 | 103751102 | OTHER | WIRE DOWN | 20210427 | 1009 | 1335464 | 285 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 349 | 39.6439 | -121.4306 | MTR# 1007241152 TWDS LINE AND BUCK | Clear-32-90 F | Conductor, Overhead | On Ground | 21-0053855 | OH | Sus | 0 | No | 2021 | APR | Yes | Line to Ground | 1623660 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 27019 | 20210510 | 433 | 1344613 | 705 | Distribution Circuit | 3rd Party | Vehicle | 165 | 116325 | 39.849 | -121.6166 | 1 POLE LD SIDE OF MTR# 1007456154 | Strong Winds- | Pole-Wood | Broken, wire on ground | 21-0059046 | OH | Sus | 0 | No | 2021 | MAY | Yes | Line to Ground | 1627034 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1105 | 102831105 | FUSE | 969683 | 20210510 | 714 | 1344652 | 508 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 7112 | 39.8091 | -121.5795 | 1 SPAN SS OF MTR 100000048163 | Strong Winds- | Conductor, Overhead | On Ground | 21-0059075 | OH | Sus | 0 | No | 2021 | MAY | Yes | Line to Ground | 1627064 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | FRENCH GULCH-1102 | 103381102 | RECLOSER | 2902 | 20210524 | 2250 | 1357924 | 1255 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 6985 | 40.6669 | -122.6336 | AT FUCO 2931 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0065459 | OH | Sus | 31541215 | No | 2021 | MAY | Yes | Line to Line | 1631792 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BURNEY-1101 | 103311101 | RECLOSER | 1322 | 20210626 | 248 | 1385421 | 515 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 20369 | 40.9132 | -121.6469 | 5 SPANS LD SIDE OF FUCO 74753 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0080221 | OH | Sus | 31544744 | No | 2021 | JUN | Yes | Line to Ground | 1641847 | CSO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WHITMORE-1101 | 103601101 | FUSE | 4725 | 20210627 | 2119 | 1386334 | 1337 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 25187 | 40.7232 | -121.9182 | MTR# 1010028397 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0080660 | OH | Sus | 0 | No | 2021 | JUN | Yes | Line to Line | 1642315 | CAW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CLARK ROAD-1102 | 103091102 | FUSE | 91881 | 20210701 | 1127 | 1389920 | 320 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 2 | 640 | 39.7291 | -121.5745 | LD SIDE OF CGC# 221199975125 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0083491 | OH | Sus | 0 | No | 2021 | JUL | Yes | Line to Line | 1644476 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1105 | 102831105 | FUSE | 1291 | 20210714 | 1448 | 1404752 | 482 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 1446 | 39.7997 | -121.5849 | 3 SPANS SS/OF CGC 221167477962 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0089718 | OH | Sus | 31546406 | No | 2021 | JUL | Yes | Line to Ground | 1648359 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | WYANDOTTE-1107 | 102911107 | OTHER | WIRE DOWN N/OF 23373 | 20210816 | 2003 | 1444404 | 488 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 137 | 23287 | 39.5081 | -121.3082 | SPAN N/OF 23373 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0105286 | OH | Sus | 0 | No | 2021 | AUG | Yes | Line to Ground | 1658117 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | STILLWATER-1102 | 103561102 | FUSE | 6685 | 20210819 | 1704 | 1447867 | 300 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 4400 | 40.6881 | -122.2816 | CGC 119222349662 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0107071 | OH | Sus | 0 | No | 2021 | AUG | Yes | Line to Ground | 1659226 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CLARK ROAD-1102 | 103091102 | FUSE | 2701 | 20210901 | 638 | 1459635 | 612 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 4696 | 39.665 | -121.626 | 3P LD SIDE OF CGC#221117473047 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0111939 | OH | Sus | 0 | No | 2021 | SEP | Yes | Line to Line | 1662641 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RISING RIVER-1101 | 103551101 | RECLOSER | 9032 | 20210906 | 1314 | 1463058 | 567 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 320 | 103258 | 40.78 | -121.5028 | LOMMEN- TONY 530-941-7476: 9 SP/LD/SD/O SW 7719 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0113874 | OH | Sus | 0 | No | 2021 | SEP | Yes | Line to Line | 1663674 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1101 | 103031101 | RECLOSER | 2022 | 20210913 | 1028 | 1470608 | 404 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1045 | 422180 | 39.8542 | -121.6059 | 1 S/OF CGC# 221142879456 | Clear-32-90 F | Insulator | Broken, wire on object | 21-0116778 | OH | Sus | 0 | No | 2021 | SEP | Yes | Line to Ground | 1665362 | INS | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | RECLOSER | 1448 | 20211005 | 2022 | 1487932 | 352 | Distribution Circuit | 3rd Party | Vehicle | 241 | 84832 | 40.6478 | -122.222 | MAIN LINE at LINE & BUCK THAT FEEDS CGC# 119405448141 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0126355 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1671202 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 1064 | 20211014 | 1058 | 1497550 | 375 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 200 | 54735 | 39.4819 | -121.2418 | 9594 FORSYTHE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0131045 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1674203 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE | 1611 | 20211019 | 1438 | 1502130 | 300 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 13800 | 40.8231 | -121.9399 | 1 SPAN SS OF METER#60810J | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0133245 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Line | 1675760 | CAW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | RED BLUFF-1104 | 103541104 | RECLOSER | 51238 | 20211103 | 2215 | 1534221 | 476 | Distribution Circuit | Equipment Failure/Involved | Overhead | 358 | 127415 | 40.2389 | -122.2594 | LAUGHLIN- RONALD /4251: TRANS POLE 9/183 | Clear-32-90 F | Insulator | Broken, wire on ground | 21-0142005 | OH | Sus | 0 | No | 2021 | NOV | Yes | Multi-Fault | 1681598 | INS | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | KESWICK-1101 | 103451101 | FUSE | 2443 | 20211109 | 840 | 1538536 | 586 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 5860 | 40.5975 | -122.5436 | MTR 1009717942 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0143800 | OH | Sus | 0 | No | 2021 | NOV | Yes | Line to Line | 1682995 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 1640 | 20211109 | 13 | 1538224 | 545 | Distribution Circuit | Vegetation | Tree - fell into line | 166 | 139554 | 40.3543 | -121.5767 | 5 POLES LD SIDE OF 2195 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0143648 | OH | Sus | 0 | No | 2021 | NOV | Yes | Line to Ground | 1682885 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 65764 | 20211117 | 1031 | 1547762 | 176 | Distribution Circuit | Vegetation | Tree - fell into line | 147 | 14489 | 40.4014 | -121.8773 | CERRO- RICHARD: 3 WEST OF SB 5593 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0146903 | OH | Sus | 45069645 | No | 2021 | NOV | Yes | Line to Line | 1685554 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 713 | 20211120 | 2034 | 1552216 | 527 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3162 | 39.4464 | -121.2602 | 3 SPANS LD SIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0149130 | OH | Sus | 31578861 | No | 2021 | NOV | Yes | Line to Line | 1687069 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | FUSE | 17169 | 20211120 | 2150 | 1552272 | 900 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 23400 | 39.8636 | -121.5764 | CGC 221195479947 & 221194379961 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 21-0149141 | OH | Sus | 0 | No | 2021 | NOV | Yes | Line to Ground | 1687078 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | RECLOSER | 80670 | 20211202 | 817 | 1557684 | 665 | Distribution Circuit | 3rd Party | Vehicle | 168 | 104592 | 39.3882 | -121.4056 | Woodmansee- Matt/1751: carpole accident-6spans loadside of 1849 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0154045 | OH | Sus | 0 | No | 2021 | DEC | Yes | Multi-Fault | 1690724 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CEDAR CREEK-1101 | 103321101 | OTHER | WIRE DOWN 14 SPANS LD SIDE OF 1635 | 20211212 | 432 | 1564987 | 954 | Distribution Circuit | Vegetation | Tree - fell into line | 228 | 61640 | 40.9079 | -121.9248 | 14 SPANS LD SIDE OF 1635 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0156764 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1693627 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1102 | 102541102 | OTHER | WIRE DOWN 1/S/SS 3793 | 20211216 | 30 | 1574135 | 688 | Distribution Circuit | Vegetation | Tree - fell into line | 212 | 144752 | 40.5167 | -121.7941 | 1/S/SS 3793 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158758 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1695762 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1102 | 102541102 | FUSE | 164929 | 20211216 | 500 | 1574340 | 689 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1378 | 40.5036 | -121.8321 | 2 SP LD SIDE OF FUCO 164929 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0158791 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1695801 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | JUMPER | OJ ON SINGLE PHASE TAP 2 NORTH OF 1683 | 20211218 | 1140 | 1576779 | 262 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 2882 | 40.295 | -121.0531 | 1 SPAN WEST OF LINE AND BUCK THAT IS 2 SPANS NORTH OF 1683 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0159540 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1696713 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | RECLOSER | 542442 | 20211219 | 817 | 1577256 | 566 | Distribution Circuit | 3rd Party | Vehicle | 32 | 18112 | 39.3899 | -121.41 | MENZEL- KILE/T1778: bangor park& bangor trl | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0159712 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1696913 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | NOTRE DAME-1104 | 102041104 | RECLOSER | 2028 | 20211219 | 1649 | 1577519 | 315 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1540 | 451458 | 39.839 | -121.7019 | THORNE-ALLAN: at FUSES 16055 ON MAINLINE TWRD LOADSIDEQ | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0159749 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1696962 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | NOTRE DAME-1104 | 102041104 | RECLOSER | 2028 | 20211219 | 2207 | 1577676 | 366 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1595 | 535591 | 39.839 | -121.7019 | 1 S/OF CGC 220910980489 | Strong Winds-Snow-Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0159810 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1697022 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | OTHER | WIRE DOWN 5/E/OF FUCO 2103 | 20211223 | 1033 | 1579845 | 492 | Distribution Circuit | Vegetation | Tree - fell into line | 167 | 81820 | 40.3473 | -121.5382 | 5 SPANS EAST OF FUCO 2103 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 21-0160272 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1697712 | CAW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 1902 | 20211228 | 946 | 1586655 | 10276 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 36288 | 39.484 | -121.2453 | 2 SPANS LD SIDE OF 1957- 4 SPANS LD SIDE 691 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0161318 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1698945 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 1915 | 20211228 | 754 | 1586532 | 516 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 9288 | 39.4827 | -121.2195 | 5 SS OF 1939 - 11843 MORAN | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0161342 | OH | Sus | 0 | No | 2021 | DEC | Yes | Multi-Fault | 1698982 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 23411 | 20211228 | 917 | 1586612 | 376 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 4512 | 39.4855 | -121.2223 | 3 SPANS LD SIDE OF FUCO 32411 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0161346 | OH | Sus | 0 | No | 2021 | DEC | Yes | Multi-Fault | 1698990 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | JUMPER | OJ 2 SS/OF CGC 222581069957 | 20220104 | 803 | 1594633 | 267 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 267 | 39.5843 | -121.0858 | CGC OJ 2 SS/OF CGC 222581069957 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0005834 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Ground | 1700858 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1101 | 103751101 | RECLOSER | 1101/2 | 20220116 | 1228 | 1603593 | 578 | Distribution Circuit | Vegetation | Tree - fell into line | 300 | 44072 | 39.6769 | -121.4915 | 7086 BUNKER HILL MINE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0010360 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Ground | 1702928 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | FUSE | 3513 | 20220119 | 1353 | 1605322 | 446 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 18 | 8028 | 40.2941 | -121.0498 | BETWEEN 4-7 SPANS LD SIDE FUCO 3513 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0011441 | OH | Sus | 45128176 | No | 2022 | JAN | Yes | Line to Line | 1703519 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GIRVAN-1101 | 103401101 | OTHER | 2 PHASE DOWN AT MTR E79156 | 20220214 | 2013 | 1627462 | 735 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 15408 | 40.5404 | -122.5689 | LYTLE/2454: 8616 ZOGG MINE RD IGO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0022246 | OH | Sus | 31595515 | No | 2022 | FEB | Yes | Line to Ground | 1710017 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | HAMILTON BRANCH-1101 | 102361101 | RECLOSER | 90334 | 20220222 | 1630 | 1634120 | 223 | Distribution Circuit | Equipment Failure/Involved | Overhead | 302 | 65904 | 40.2684 | -121.0876 | 2 POLES NORTH OF 18421 ON MAINLINE | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 22-0025241 | OH | Sus | 0 | No | 2022 | FEB | Yes | Line to Ground | 1711971 | CSO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | CEDAR CREEK-1101 | 103321101 | FUSE | 6449 | 20220223 | 808 | 1634448 | 706 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 7060 | 40.8446 | -121.9225 | 30022 JACKSON LN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0025473 | OH | Sus | 35329983 | No | 2022 | FEB | Yes | Line to Line | 1712153 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | OTHER | WIRE DOWN MAINLINE N/OF 8267 LA PORTE RD | 20220303 | 1015 | 1641239 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 622 | 154753 | 39.4532 | -121.2995 | 8267 LA PORTE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0029132 | OH | Sus | 0 | No | 2022 | MAR | Yes | Line to Ground | 1714294 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1102 | 103751102 | RECLOSER | 1102/2 | 20220322 | 2130 | 1653896 | 917 | Distribution Circuit | Equipment Failure/Involved | Overhead | 396 | 111087 | 39.6769 | -121.4916 | 7 SS OF C218 | Lightning-Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0037151 | OH | Sus | 45225412 | No | 2022 | MAR | Yes | Line to Ground | 1719181 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1103 | 102911103 | RECLOSER | 1508 | 20220322 | 1559 | 1653742 | 572 | Distribution Circuit | Equipment Failure/Involved | Overhead | 284 | 24901 | 39.5048 | -121.4524 | 10 SPANS S/OF 714105 | Lightning-Strong Winds-Clear-32-90 F | Other | Broken, wire on object | 22-0037056 | OH | Sus | 0 | No | 2022 | MAR | Yes | Force Out | 1719144 | NON | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 11137 | 20220328 | 142 | 1657434 | 649 | Distribution Circuit | 3rd Party | Vehicle | 631 | 160045 | 40.6121 | -122.3838 | AT FUCO 11137 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0039120 | OH | Sus | 0 | No | 2022 | MAR | Yes | Multi-Fault | 1720461 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1107 | 102911107 | RECLOSER | 83288 | 20220414 | 316 | 1672101 | 329 | Distribution Circuit | Equipment Failure/Involved | Overhead | 655 | 87599 | 39.4971 | -121.4451 | MTR 1008112037 | Rain-Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0047850 | OH | Sus | 0 | No | 2022 | APR | Yes | Three Phase Fault | 1726441 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | JESSUP-1101 | 103441101 | RECLOSER | 41356 | 20220507 | 1235 | 1690715 | 432 | Distribution Circuit | 3rd Party | Vehicle | 353 | 42831 | 40.4772 | -122.4548 | 1 E/OF 872879 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0059301 | OH | Sus | 0 | No | 2022 | MAY | Yes | Line to Ground | 1734442 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BURNEY-1101 | 103311101 | FUSE | 74753 | 20220513 | 1105 | 1695443 | 325 | Distribution Circuit | 3rd Party | Aircraft | 6 | 525 | 40.9299 | -121.7254 | 3 POLES SS OF MTR# 1008843601 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0061741 | OH | Sus | 0 | No | 2022 | MAY | Yes | Three Phase Fault | 1736097 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GANSNER-1101 | 103021101 | FUSE | 18737 | 20220604 | 736 | 1718817 | 922 | Distribution Circuit | Equipment Failure/Involved | Overhead | 326 | 42182 | 39.9234 | -121.075 | 3/S/OF 18737 | Clear-32-90 F | Pole-Wood | Broken, wire on object | 22-0070096 | OH | Sus | 0 | No | 2022 | JUN | Yes | Line to Ground | 1741696 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1102 | 102931102 | RECLOSER | 9026 | 20220607 | 1123 | 1721450 | 762 | Distribution Circuit | Vegetation | Tree - branch fell on line | 989 | 97559 | 40.3893 | -122.3432 | CGC 119006238093 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0071037 | OH | Sus | 0 | No | 2022 | JUN | Yes | Line to Ground | 1742532 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WYANDOTTE-1109 | 102911109 | JUMPER | OJ'S 1 SPAN N/OF METER# 1008802543 | 20220610 | 308 | 1726913 | 639 | Distribution Circuit | Vegetation | Tree - grew into line | 1 | 639 | 39.4485 | -121.5472 | METER# 1008802543 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0072523 | OH | Sus | 0 | No | 2022 | JUN | Yes | Line to Ground | 1743333 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 3-2101 | 103732101 | OCB | 2101/2 | 20220621 | 2327 | 1737536 | 868 | Distribution Circuit | Equipment Failure/Involved | Overhead | 152 | 45375 | 40.9981 | -121.7476 | 5 SPANS LD SIDE OF 354683 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0076763 | OH | Sus | 31606758 | No | 2022 | JUN | Yes | Line to Line | 1746529 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BUTTE-1105 | 103081105 | RECLOSER | 135519 | 20220626 | 2350 | 1742899 | 825 | Distribution Circuit | Vegetation | Tree - fell into line | 368 | 44865 | 39.7117 | -121.7738 | 1 SPAN LD SIDE OF FUCO 16999 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0078825 | OH | Sus | 0 | No | 2022 | JUN | Yes | Line to Line | 1748143 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | SYCAMORE CREEK-1111 | 102971111 | RECLOSER | 2014 | 20220809 | 1322 | 1776995 | 746 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 534 | 94648 | 39.8317 | -121.8444 | BISCHEL /2498: 355 Hollow Oak Dr | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0095399 | OH | Sus | 31612544 | No | 2022 | AUG | Yes | Line to Ground | 1758845 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 3-2101 | 103732101 | RECLOSER | 1480 | 20220818 | 1441 | 1784595 | 678 | Distribution Circuit | 3rd Party | Vehicle | 129 | 22158 | 41.0219 | -121.6801 | 3 SPANS SS OF FUCO 9975 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0099382 | OH | Sus | 0 | No | 2022 | AUG | Yes | Line to Line | 1761394 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER | 5460 | 20220908 | 1057 | 1805752 | 528 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 458 | 65932 | 39.5443 | -121.1479 | METER 1010573792 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0107899 | OH | Sus | 0 | No | 2022 | SEP | Yes | Line to Ground | 1767082 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA SUB | 10322 | RECLOSER | LR1101/2 | 20221101 | 1256 | 1850148 | 296 | Distribution Circuit | Vegetation | Tree - fell into line | 548 | 31355 | 39.575 | -121.3064 | CARRELL- ROBERT/1776: 18172 Wetmore way- SAP#100422509 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0126504 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Ground | 1780543 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1101 | 103751101 | FUSE | 17489 | 20221107 | 522 | 1855715 | 431 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 2004 | 39.6983 | -121.4593 | METER# 1007766054 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0128413 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Line | 1781843 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | GANSNER-1101 | 103021101 | FUSE | 18599 | 20221108 | 1009 | 1857083 | 448 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 2464 | 39.9795 | -120.9398 | 2 SPANS SS OF CGC 122981923501 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0129104 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Ground | 1782219 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | FUSE | 13629 | 20221108 | 1043 | 1857149 | 264 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 792 | 39.5267 | -121.2845 | 3 SPANS LD SIDE OF 13629 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0129052 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Ground | 1782193 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1102 | 102541102 | RECLOSER | 1650 | 20221109 | 347 | 1858627 | 700 | Distribution Circuit | Vegetation | Tree - fell into line | 1073 | 154251 | 40.517 | -121.7462 | 3 SPANS SS/OF C165 | Snow-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0129424 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Ground | 1782462 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | VOLTA-1102 | 102541102 | OTHER | WIRE DOWN 1 SPAN LD SIDE OF 90047 | 20221109 | 608 | 1858797 | 328 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2624 | 40.5178 | -121.7976 | 1 SPAN LD SIDE OF 90047 | Snow-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0129465 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Ground | 1782487 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1105 | 102831105 | RECLOSER | 121988 | 20221115 | 2116 | 1863579 | 479 | Distribution Circuit | Vegetation | Tree - fell into line | 209 | 15877 | 39.8118 | -121.5914 | CORNER OF SOUTH PARK AND SCRIPPS- MTR# 1007884791. | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0131431 | OH | Sus | 31625526 | No | 2022 | NOV | Yes | Line to Ground | 1783967 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | MC ARTHUR-1101 | 103491101 | RECLOSER | 1544 | 20221201 | 928 | 1872949 | 377 | Distribution Circuit | Environmental/External | Ice or snow | 354 | 126135 | 41.0573 | -121.279 | KNAUP- GEORGE/1787: at fco 5651 CENTER PHASE DOWN | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0135490 | OH | Sus | 0 | No | 2022 | DEC | Yes | Multi-Fault | 1786674 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1105 | 102831105 | RECLOSER | 121988 | 20221201 | 701 | 1872734 | 638 | Distribution Circuit | Vegetation | Tree - fell into line | 209 | 22037 | 39.8118 | -121.5914 | LAST POLE LD SIDE OF FUCO 17963 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0135413 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1786614 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | NOTRE DAME-1104 | 102041104 | RECLOSER | 38698 | 20221205 | 547 | 1876183 | 427 | Distribution Circuit | Equipment Failure/Involved | Overhead | 311 | 132017 | 40.0372 | -121.6183 | GARRETSON- GREG/3650: 6 STR SS HARD TAP FEEDING MTR 1009069174 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0136576 | OH | Sus | 31629487 | No | 2022 | DEC | Yes | Line to Ground | 1787511 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | FUSE | 5925 | 20221218 | 1501 | 1892370 | 743 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 28234 | 39.7019 | -120.9664 | CGC 222916874357 | Clear-32-90F | Conductor, Overhead | On Ground | 22-0140586 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1791749 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1101 | 103351101 | RECLOSER | 1380 | 20221227 | 253 | 1898031 | 1009 | Distribution Circuit | Vegetation | Tree - fell into line | 588 | 241901 | 40.5607 | -122.189 | FUCO 9865 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0141449 | OH | Sus | 0 | No | 2022 | DEC | Yes | Three Phase Fault | 1793125 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | PARADISE-1105 | 102831105 | FUSE | 4515 | 20221227 | 235 | 1898073 | 628 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 6908 | 39.8063 | -121.5961 | CAMPBELL-SCOTT/1671: Cond | Clear-32-90F | Conductor, Overhead | On Ground | 22-0141499 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793176 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 850229 | 20221227 | 319 | 1898175 | 751 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 4506 | 40.4421 | -121.8336 | 3 SPANS LD SIDE OF 850229 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0141658 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793343 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 914816 | 20221230 | 605 | 1901789 | 816 | Distribution Circuit | 3rd Party | Vehicle | 213 | 151258 | 40.4342 | -121.8692 | MTR# 1008050690 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0142156 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1793928 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2560 | 20230103 | 506 | 1910950 | 427 | Distribution Circuit | Vegetation | Tree - fell into line | 573 | 141651 | 39.8889 | -121.6646 | 2/P/LD SIDE OF 2040 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0004954 | OH | Sus | 31634224 | No | 2023 | JAN | Yes | Line to Ground | 1795562 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1101 | 103201101 | RECLOSER | 13026 | 20230111 | 235 | 1946923 | 745 | Distribution Circuit | Vegetation | Tree - fell into line | 172 | 101540 | 39.6842 | -120.9829 | LOAD SIDE OF 5933 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0013337 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1802888 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KANAKA-1101 | 103221101 | OTHER | WIRE DOWN HOT | 20230118 | 2140 | 1961535 | 1228 | Distribution Circuit | Equipment Failure/Involved | Overhead | 541 | 24346 | 39.5463 | -121.2833 | 1 SPAN LD SIDE OF 78815 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0018628 | OH | Sus | 0 | No | 2023 | JAN | Yes | Force Out | 1806684 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | SYCAMORE CREEK-1111 | 102971111 | RECLOSER | 2014 | 20230119 | 536 | 1961802 | 442 | Distribution Circuit | Equipment Failure/Involved | Overhead | 533 | 180516 | 39.8317 | -121.8444 | PALADE-WES/1934: 4 spans load side of sbco 16859 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0018658 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1806723 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 1-1101 | 103721101 | RECLOSER | 1552 | 20230122 | 500 | 1964434 | 523 | Distribution Circuit | Equipment Failure/Involved | Overhead | 355 | 48514 | 41.0151 | -121.4689 | WIRE DOWN SS OF CGC 121423761971 ON MAIN LINE | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0019817 | OH | Sus | 45647023 | No | 2023 | JAN | Yes | Multi-Fault | 1807277 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 7825 | 20230123 | 807 | 1965421 | 763 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 20601 | 40.6918 | -122.1129 | 1 SS/OF SBCO 1573 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0020070 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1807501 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1101 | 103751101 | RECLOSER | 641808 | 20230129 | 2313 | 1971276 | 1074 | Distribution Circuit | Vegetation | Tree - fell into line | 148 | 144802 | 39.7407 | -121.4962 | ON MAINLINE AT FUCO 17273 AND LD SIDE OF FUCO 17273 | Clear-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 23-0022788 | OH | Sus | 31635982 | No | 2023 | JAN | Yes | Line to Ground | 1808989 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CLARK ROAD-1102 | 103091102 | FUSE | 7105 | 20230303 | 903 | 2020954 | 286 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 2860 | 39.6857 | -121.5343 | 471 RICH GULCH RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0039363 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1821242 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | FUSE | 1915 | 20230305 | 932 | 2023528 | 302 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 17159 | 39.4827 | -121.2195 | STORM VARIOUS | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0040313 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1822046 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 5-1101 | 101321101 | RECLOSER | 1618 | 20230305 | 1311 | 2023766 | 386 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 386 | 40.9885 | -121.9754 | 8 POLES FROM EOL LD SIDE OF 1618 SAP ID 101518716 | Overcast-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 23-0040354 | OH | Sus | 0 | No | 2023 | MAR | Yes | Force Out | 1822080 | CSO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 1-1101 | 103721101 | RECLOSER | 1552 | 20230308 | 616 | 2026230 | 506 | Distribution Circuit | Environmental/External | Ice or snow | 352 | 78915 | 41.0151 | -121.4689 | 2 SS OF CGC 121356363222 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0041473 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1822800 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | COTTONWOOD-1102 | 102931102 | FUSE | 2625 | 20230310 | 1809 | 2031539 | 187 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 561 | 40.3982 | -122.5216 | 1 SPAN LD SIDE OF FUCO 2625 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0043306 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1823892 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | OREGON TRAIL-1103 | 103521103 | FUSE | 3175 | 20230310 | 708 | 2030401 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 28850 | 40.664 | -122.4009 | CGC 118837048349 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0042827 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1823605 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | ANTLER-1101 | 103271101 | RECLOSER | 1520 | 20230328 | 1038 | 2070209 | 269 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 21672 | 40.8995 | -122.3862 | 1 SOUTH OF CGC 118942557450 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | On Ground | 23-0053427 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1831097 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | BIG BEND-1101 | 103751101 | FUSE | 17491 | 20230328 | 944 | 2070027 | 321 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1284 | 39.6877 | -121.4593 | 39.686432 -121.460843 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 23-0053473 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1831128 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WILDWOOD-1101 | 103611101 | FUSE | 6051 | 20230328 | 703 | 2070833 | 1080 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5400 | 40.368 | -122.9715 | 3 SPANS LD SIDE | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0053698 | OH | Sus | 0 | No | 2023 | MAR | Yes | Open Circuit | 1831265 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 2560 | 20230329 | 1405 | 2073228 | 283 | Distribution Circuit | Vegetation | Tree - fell into line | 255 | 33575 | 39.8889 | -121.6646 | 4 SPANS LD SIDE OF FUCO 1475 ON MAINLINE | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0054476 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1831671 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | OTHER | WIRE DOWN 3 SP LD SIDE OF 17419 | 20230329 | 1131 | 2072900 | 393 | Distribution Circuit | Equipment Failure/Involved | Overhead | 183 | 71208 | 39.9008 | -121.5308 | PALADE-WES/1934: 3 spans load side of c/o 17419 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0054370 | OH | Sus | 0 | No | 2023 | MAR | Yes | Open Circuit | 1831632 | CO | OH | No | Yes
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 5-1101 | 101321101 | RECLOSER | 1660 | 20230401 | 219 | 2076441 | 536 | Distribution Circuit | Equipment Failure/Involved | Overhead | 128 | 47728 | 40.9964 | -121.9198 | SPAN SS/OF CGC 120252961395 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0055791 | OH | Sus | 0 | No | 2023 | APR | Yes | Line to Ground | 1832393 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | KESWICK-1101 | 103451101 | RECLOSER | 9712 | 20230411 | 2338 | 2086081 | 1202 | Distribution Circuit | Vegetation | Tree - fell into line | 286 | 157724 | 40.6166 | -122.4958 | LYTLE-JOHN/2454: 11045 Sugar Pine Ln Shasta | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0059843 | OH | Sus | 45726954 | No | 2023 | APR | Yes | Three Phase Fault | 1835006 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PANORAMA-1101 | 103461101 | RECLOSER | 713592 | 20230412 | 2228 | 2087157 | 455 | Distribution Circuit | 3rd Party | Vehicle | 806 | 129269 | 40.3776 | -122.2114 | 1 W/OF 11213 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0060430 | OH | Sus | 0 | No | 2023 | APR | Yes | Three Phase Fault | 1835339 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CLARK ROAD-1102 | 103091102 | RECLOSER | 90548 | 20230413 | 241 | 2087185 | 787 | Distribution Circuit | Vegetation | Tree - fell into line | 160 | 25925 | 39.6945 | -121.5248 | 2 N/OF 262745 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0060445 | OH | Sus | 45727839 | No | 2023 | APR | Yes | Line to Line | 1835352 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | OTHER | WIRE DOWN 7 LD SIDE 3813 | 20230420 | 715 | 2092920 | 349 | Distribution Circuit | Equipment Failure/Involved | Overhead | 547 | 190133 | 40.3453 | -121.6704 | 7 SPANS LD SIDE OF 3813 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0062800 | OH | Sus | 0 | No | 2023 | APR | Yes | Open Circuit | 1837141 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1101 | 103351101 | RECLOSER | 1652 | 20230522 | 2325 | 2119226 | 710 | Distribution Circuit | 3rd Party | Vehicle | 324 | 45220 | 40.5336 | -122.1437 | 7 SPANS E/OF SW-7417 at BOOSTER B118 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 23-0074436 | OH | Sus | 0 | No | 2023 | MAY | Yes | Multi-Fault | 1845163 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | FUSE | 2561 | 20230531 | 1630 | 2124987 | 6 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 6 | 40.3659 | -121.5115 | CGC 121352838190 | Partly Cloudy-32-90 F | Cutout, fuse holder | Broken, wire on ground | 23-0077422 | OH | Sus | 0 | No | 2023 | MAY | Yes | None | 1847083 | CFH | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 1064 | 20230715 | 1353 | 2163487 | 298 | Distribution Circuit | Equipment Failure/Involved | Overhead | 198 | 35154 | 39.4819 | -121.2418 | MEINBERG- BRAD: 17582 New York house rd | Clear-Above 90 | Connector or Splice (OH) | Broken, wire on ground | 23-0092632 | OH | Sus | 45887916 | No | 2023 | JUL | Yes | Line to Line | 1857687 | CSO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | PIT NO 5-1101 | 101321101 | RECLOSER | 1658 | 20230805 | 626 | 2182844 | 717 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 115 | 39960 | 40.9921 | -121.9718 | 9 SPANS LD SIDE OF CGC 120229561519 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0100840 | OH | Sus | 31661928 | No | 2023 | AUG | Yes | Line to Line | 1863223 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | ORO FINO-1102 | 103031102 | RECLOSER | 65932 | 20230809 | 344 | 2186226 | 751 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1093 | 109926 | 39.8705 | -121.6503 | METER# 1007238993 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0101980 | OH | Sus | 0 | No | 2023 | AUG | Yes | Line to Ground | 1864140 | PW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | VOLTA-1101 | 102541101 | RECLOSER | 65764 | 20230824 | 639 | 2200860 | 501 | Distribution Circuit | Vegetation | Tree - fell into line | 146 | 26098 | 40.4014 | -121.8773 | CGC 120214236454 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0108418 | OH | Sus | 31664654 | No | 2023 | AUG | Yes | Line to Ground | 1868501 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | DESCHUTES-1101 | 103351101 | RECLOSER | 1502 | 20231008 | 145 | 2238085 | 931 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2055 | 359846 | 40.5607 | -122.189 | WIRE DOWN BET CGC 119619543711 AND CGC 119615443716 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0125830 | OH | Sus | 31671941 | No | 2023 | OCT | Yes | Line to Ground | 1880289 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 3 | CHALLENGE-1102 | 103201102 | RECLOSER | 5462 | 20231211 | 802 | 2288628 | 447 | Distribution Circuit | Equipment Failure/Involved | Overhead | 462 | 94624 | 39.483 | -121.2466 | WIRE DOWN at CGC 222108766114 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0146834 | OH | Sus | 0 | No | 2023 | DEC | Yes | Three Phase Fault | 1896697 | CO | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | WHITMORE-1101 | 103601101 | OCB | 1101/2 | 20231219 | 1214 | 2295705 | 340 | Distribution Circuit | Vegetation | Tree - fell into line | 545 | 50609 | 40.6293 | -121.9156 | 2 N/OF 4231 | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0148102 | OH | Sus | 31679904 | No | 2023 | DEC | Yes | Line to Ground | 1898964 | CAW | OH | No | No
NORTH VALLEY | FIELD OPS NORTH | Tier 2 | BIG MEADOWS-2101 | 102812101 | FUSE | 18131 | 20231220 | 151 | 2296240 | 843 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 2 | 1686 | 40.068 | -120.6815 | EOL LD SIDE OF FU 18131 | Overcast-Fog-32-90 F | Pole-Wood | Broken, wire on object | 23-0148229 | OH | Sus | 0 | No | 2023 | DEC | Yes | Line to Ground | 1899149 | PW | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 13213 | 20130119 | 1350 | 731880 | 340 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 1700 | 37.1703 | -122.2999 | CLARK/ 1076: 240 Daffodil lane | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0005188 | OH | Sus | 41842672 | No | 2013 | JAN | Yes | Line to Ground | 99304003 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | SWITCH | 14513 | 20130228 | 1250 | 748802 | 448 | Distribution Circuit | Vegetation | Tree - fell into line | 2006 | 44578 | 37.3126 | -122.2883 | 314824530015 | Partly cloudy-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0013218 | OH | Sus | 41860139 | No | 2013 | FEB | Yes | Open Circuit | 99298671 | CSO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | SWITCH | 14513 | 20130301 | 1016 | 749136 | 102 | Distribution Circuit | Equipment Failure/Involved | Other | 40 | 4080 | 37.3126 | -122.2883 | N/A | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0013393 | OH | Sus | 0 | No | 2013 | MAR | Yes | None | 99298563 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | RALSTON-1101 | 24141101 | FUSE | 1633 | 20130305 | 2213 | 752036 | 249 | Distribution Circuit | Vegetation | Tree - branch fell on line | 143 | 37961 | 37.5186 | -122.3357 | 314693137566 | Rain-32 - 90 F | Connector or Splice (OH) | Broken, wire on object | 13-0014377 | OH | Sus | 41862078 | yes | 2013 | MAR | Yes |  | 99297963 | CSO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 11437 | 20130404 | 856 | 766436 | 345 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4531 | 37.3942 | -122.2606 | 314895533094 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0021401 | OH | Sus | 30987369 | No | 2013 | APR | Yes | Line to Ground | 99292910 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 11585 | 20130415 | 223 | 774786 | 637 | Distribution Circuit | Equipment Failure/Involved | Other | 10 | 6370 | 37.2806 | -122.1485 | 315212328763 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0024362 | OH | Sus | 41882502 | yes | 2013 | APR | Yes | Line to Line | 99290612 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | OTHER |  | 20130416 | 819 | 776131 | 401 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 401 | 37.2692 | -122.2112 | 315024628464 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0024886 | OH | Sus | 0 | yes | 2013 | APR | Yes | Open Circuit | 99290225 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | SAN CARLOS-1104 | 24181104 | FUSE | 5319 | 20130429 | 1306 | 783432 | 882 | Distribution Circuit | 3rd Party | Vehicle | 72 | 6487 | 37.4878 | -122.2737 | 314857636417 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0027993 | OH | Sus | 30993098 | No | 2013 | APR | Yes |  | 99287920 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER |  | 20130505 | 140 | 787298 | 510 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 26937 | 37.3875 | -122.2691 | 314861932804 | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 13-0029564 | OH | Sus | 41892952 | yes | 2013 | MAY | Yes | Line to Ground | 99286740 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 3211 | 20130505 | 906 | 787532 | 814 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4884 | 37.4188 | -122.3316 | 314660334125 | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 13-0029642 | OH | Sus | 41892968 | yes | 2013 | MAY | Yes | Open Circuit | 99286659 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 8541 | 20130530 | 2016 | 801056 | 1089 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 15246 | 37.2623 | -122.2131 | 315013428146 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0035541 | OH | Sus | 0 | No | 2013 | MAY | Yes | Line to Ground | 99282547 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER |  | 20130613 | 2045 | 810154 | 609 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3446 | 37.3792 | -122.2717 | 314854932500 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0039551 | OH | Sus | 31002738 | No | 2013 | JUN | Yes | Open Circuit | 99279924 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 9067 | 20130629 | 715 | 820404 | 465 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 465 | 37.2531 | -122.3714 | 314558327971 | Partly cloudy-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0043697 | OH | Sus | 0 | yes | 2013 | JUN | Yes | Line to Ground | 99277130 | CSO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4737 | 20130722 | 143 | 836250 | 661 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 11944 | 37.4022 | -122.3361 | 314652233244 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0048984 | OH | Sus | 41930405 | No | 2013 | JUL | Yes | Line to Ground | 99273060 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 7439 | 20130729 | 948 | 840079 | 431 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3017 | 37.4203 | -122.3268 | 314694934056 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0050776 | OH | Sus | 41934015 | No | 2013 | JUL | Yes | None | 99271835 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER |  | 20130730 | 2039 | 841025 | 476 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 7528 | 37.2406 | -122.3185 | 314709927497 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0051310 | OH | Sus | 41935357 | No | 2013 | JUL | Yes | Open Circuit | 99271600 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 1721 | 20130801 | 717 | 841598 | 383 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 19150 | 37.3179 | -122.191 | 315123430033 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0051646 | OH | Sus | 41936324 | No | 2013 | AUG | Yes | Line to Ground | 99271376 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE | 10695 | 20130802 | 1440 | 842358 | 1370 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 6810 | 37.486 | -122.419 | VILLA/ 838 (1953): far end of digges cyn cross st hwy 92 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0052126 | OH | Sus | 41936458 | No | 2013 | AUG | Yes | Line to Ground | 99271111 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8974 | 20130916 | 421 | 866549 | 799 | Distribution Circuit | Vegetation | Tree - fell into line | 312 | 47408 | 37.3882 | -122.267 | 314892432623 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0062135 | OH | Sus | 31021563 | No | 2013 | SEP | Yes | Line to Ground | 99263859 | PW | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER |  | 20130921 | 818 | 869916 | 364 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 4597 | 37.3919 | -122.2676 | 314868532958 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0063623 | OH | Sus | 31023190 | yes | 2013 | SEP | Yes | Line to Ground | 99262871 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 6075 | 20130927 | 626 | 874063 | 424 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 10783 | 37.404 | -122.4128 | 314566134614 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0065178 | OH | Sus | 0 | No | 2013 | SEP | Yes |  | 99261579 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8983 | 20131004 | 206 | 878015 | 844 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 9324 | 37.3779 | -122.2619 | 314906232383 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0067139 | OH | Sus | 31026012 | yes | 2013 | OCT | Yes | Line to Ground | 99260293 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER |  | 20131004 | 1803 | 878981 | 1397 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 10042 | 37.3972 | -122.3496 | BET 10 DURHAM & 1445 NATIVE SONS | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0067480 | OH | Sus | 41968014 | yes | 2013 | OCT | Yes | Line to Ground | 99260014 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 5417 | 20131028 | 1 | 891972 | 486 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 29272 | 37.3891 | -122.2663 | 314860633029 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0072653 | OH | Sus | 0 | yes | 2013 | OCT | Yes |  | 99256229 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 8739 | 20131206 | 2158 | 921358 | 327 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 7871 | 37.4311 | -122.3841 | 314566134614 | Rain-32 - 90 F | Conductor, Overhead | On Ground | 13-0081081 | OH | Sus | 42042380 | yes | 2013 | DEC | Yes | Line to Ground | 99249152 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER |  | 20131207 | 7 | 921551 | 704 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2112 | 37.4028 | -122.2873 | 314808833374 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081185 | OH | Sus | 42042394 | yes | 2013 | DEC | Yes |  | 99249022 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER |  | 20131207 | 734 | 922054 | 456 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 2660 | 37.3735 | -122.2555 | 314902732280 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081235 | OH | Sus | 42042398 | yes | 2013 | DEC | Yes | Line to Ground | 99248968 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER |  | 20131207 | 730 | 922044 | 420 | Distribution Circuit | Equipment Failure/Involved | Other | 20 | 5930 | 37.392 | -122.3332 | 314675932973 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081255 | OH | Sus | 31041222 | yes | 2013 | DEC | Yes | Line to Ground | 99248949 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER |  | 20140124 | 1403 | 947073 | 522 | Distribution Circuit | Equipment Failure/Involved | Other | 16 | 4496 | 37.2552 | -122.3176 | 314711528035 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0006321 | OH | Sus | 42065233 | yes | 2014 | JAN | Yes | Open Circuit | 99242852 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 3217 | 20140202 | 1504 | 958613 | 636 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 10176 | 37.294 | -122.2411 | JUST LD SIDE 3217 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0008196 | OH | Sus | 42069014 | yes | 2014 | FEB | Yes | Open Circuit | 99241710 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1102 | 24101102 | FUSE | 5903 | 20140208 | 816 | 962660 | 479 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2842 | 37.5436 | -122.4985 | SINGLE PHASE WIRE FEEDING 771 RIVERA RD. | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0009863 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Ground | 99240758 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1104 | 24251104 | FUSE | 3585 | 20140209 | 600 | 963879 | 478 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 7648 | 37.424 | -122.2753 | IFO 3650 SUMMIT SPRINGS RD WD | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0010104 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Line | 99240528 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER |  | 20140210 | 343 | 964730 | 694 | Distribution Circuit | Vegetation | Tree - fell into line | 314 | 18241 | 37.3879 | -122.2627 | 1 POLE LINE SIDE OF 4133 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0010222 | OH | Sus | 42073829 | yes | 2014 | FEB | Yes | Open Circuit | 99240366 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER |  | 20140213 | 627 | 966750 | 983 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 30473 | 37.1708 | -122.3053 | 3015 whitehouse canyon rd | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0011016 | OH | Sus | 31056517 | No | 2014 | FEB | Yes | Open Circuit | 99239787 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | OTHER |  | 20140216 | 1129 | 968248 | 826 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 45292 | 37.2675 | -122.2108 | KUHLS/836 (1865): crew to put up 3 spans of wire loadside of 8982 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0011587 | OH | Sus | 31057069 | No | 2014 | FEB | Yes | Line to Ground | 99239418 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER |  | 20140216 | 212 | 968145 | 473 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 14952 | 37.3854 | -122.2587 | IRO 260 GRANDVIEW DR.- WOODSIDE | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0011558 | OH | Sus | 42079340 | No | 2014 | FEB | Yes | Open Circuit | 99239451 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4203 | 20140226 | 1645 | 972881 | 695 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 2780 | 37.1669 | -122.3609 | 1ST & 2ND SPAN LD SIDE OF C/OUTS 4203 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0013555 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Ground | 99238160 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER |  | 20140226 | 1954 | 973060 | 1151 | Distribution Circuit | Equipment Failure/Involved | Other | 30 | 28914 | 37.3835 | -122.2718 | FROM C/OUTS 7969 2 SPANS TO THE LINE SIDE | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0013649 | OH | Sus | 0 | yes | 2014 | FEB | Yes |  | 99235612 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | H80 | 20140303 | 2300 | 977919 | 1030 | Distribution Circuit | Equipment Failure/Involved | Other | 646 | 230242 | 37.3303 | -122.375 | LA HONDA RD .5 MI W/OF TROUTMERE- LH- ALSO WIRE DOWN LD SIDE OF 1811 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0015196 | OH | Sus | 31060297 | No | 2014 | MAR | Yes | Line to Ground | 99236851 | PW | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 1115 | 20140309 | 1117 | 981168 | 763 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 5341 | 37.2893 | -122.2321 | 2 SPANS LD SIDE OF FU 10987 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0016770 | OH | Sus | 0 | No | 2014 | MAR | Yes | Line to Ground | 99235822 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4133 | 20140415 | 1940 | 1000022 | 582 | Distribution Circuit | Equipment Failure/Involved | Other | 4 | 2328 | 37.3881 | -122.2632 | 4/S/E/O C/OUTS 4133 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0025318 | OH | Sus | 42108881 | No | 2014 | APR | Yes | Line to Ground | 99230046 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 13243 | 20140520 | 812 | 1021325 | 448 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5376 | 37.3795 | -122.2624 | ROBERTSON/839 (2486): 19 BIG TREE WAY | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0033137 | OH | Sus | 31077332 | No | 2014 | MAY | Yes | None | 99224712 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 8541 | 20140605 | 1555 | 1029145 | 462 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 9447 | 37.2623 | -122.2131 | 4 SPANS LD SIDE OF 8541 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0036484 | OH | Sus | 31080972 | No | 2014 | JUN | Yes | Line to Ground | 99222440 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | BERESFORD-0403 | 24040403 | OTHER |  | 20140722 | 1400 | 1053528 | 779 | Distribution Circuit | Vegetation | Tree - branch fell on line | 127 | 41201 | 37.557 | -122.3426 | SCHAPPERT/ 2589 (2268): tree branchfell and burned down wire | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0046259 | OH | Sus | 42158327 | yes | 2014 | JUL | Yes | Line to Ground | 99215541 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1621 | 20140729 | 1347 | 1057411 | 793 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 3 | 2379 | 37.32 | -122.3751 | VILLA/ 838 (1953): 888 Seaside School rd San Gregorio | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0047794 | OH | Sus | 0 | No | 2014 | JUL | Yes | Line to Ground | 99214400 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | RECLOSER | 8982 | 20140810 | 1801 | 1064043 | 702 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 38610 | 37.2681 | -122.211 | 1 SPAN LINE SIDE OF 8549 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0050165 | OH | Sus | 31094141 | No | 2014 | AUG | Yes | Line to Ground | 99212674 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1125 | 20140814 | 1333 | 1066460 | 281 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 11808 | 37.2607 | -122.3247 | DEARBORN PARK. | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0051066 | OH | Sus | 0 | No | 2014 | AUG | Yes |  | 99212071 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | SNEATH LANE-1102 | 22721102 | OTHER |  | 20140912 | 1311 | 1080433 | 393 | Distribution Circuit | Equipment Failure/Involved | Other | 3764 | 27120 | 37.6323 | -122.4537 | SW COR. SKYLINE BLVD. & BERKSHIRE DR.- SB | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0056646 | OH | Sus | 42189670 | No | 2014 | SEP | Yes | Line to Ground | 99208217 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | HALF MOON BAY-1101 | 24101101 | FUSE | 8607 | 20141127 | 2301 | 1118917 | 839 | Distribution Circuit | Equipment Failure/Involved | Other | 8 | 6712 | 37.4451 | -122.3314 | 13410 SKYLINE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0072329 | OH | Sus | 31117979 | No | 2014 | NOV | Yes | Line to Ground | 99197641 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER |  | 20141204 | 943 | 1124484 | 908 | Distribution Circuit | Equipment Failure/Involved | Other | 66 | 58108 | 37.2342 | -122.3234 | CLARK/ 1076 (2418): 354 madrone acroos crk to 58 fern pes | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073778 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Open Circuit | 99196469 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | OTHER |  | 20141204 | 832 | 1124311 | 1033 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 6956 | 37.2619 | -122.208 | KUHLS/836 (1865): crew to put up 1span 2 wire 100ft of 6sol tree wire | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073816 | OH | Sus | 31118268 | yes | 2014 | DEC | Yes |  | 99196444 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | SAN CARLOS-1104 | 24181104 | RECLOSER | 9052 | 20141204 | 2156 | 1124955 | 770 | Distribution Circuit | 3rd Party | Vehicle | 328 | 193360 | 37.4782 | -122.2613 | EDGEWOOD & WOODHUE | Drizzle-32 - 90 F | Pole-Wood | Broken, wire on object | 14-0073912 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99196301 | PW | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | WOODSIDE-1104 | 24251104 | OTHER |  | 20141208 | 1833 | 1127250 | 449 | Distribution Circuit | Equipment Failure/Involved | Other | 829 | 83885 | 37.4627 | -122.2599 | IFO 3810 E LAKE- RWC | Partly cloudy-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0074446 | OH | Sus | 31120270 | No | 2014 | DEC | Yes | Open Circuit | 99195769 | CSO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER |  | 20141215 | 1527 | 1141476 | 1328 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 2656 | 37.3244 | -122.3989 | 190 LA HONDA RD SAN GREGORIO | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077126 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99192853 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 7809 | 20141220 | 353 | 1144849 | 1044 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 7308 | 37.2692 | -122.2114 | SCHLOCKER/ 252 (2286): 1500 portola state pk road | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077782 | OH | Sus | 31122395 | No | 2014 | DEC | Yes | Line to Ground | 99192127 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | HALF MOON BAY-1101 | 24101101 | FUSE | 4147 | 20141227 | 1229 | 1149184 | 631 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4417 | 37.4922 | -122.4343 | KUHLS/836 (1865): crew to put up 1 span 600ft 6sol | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078668 | OH | Sus | 42303600 | No | 2014 | DEC | Yes | Line to Ground | 99191081 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 12185 | 20141227 | 1916 | 1149323 | 644 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 19274 | 37.3751 | -122.3773 | 3 POLE LD SIDE OF FU 6089 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078681 | OH | Sus | 42303615 | No | 2014 | DEC | Yes | Line to Ground | 99190957 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 8549 | 20141231 | 1549 | 1157384 | 1311 | Distribution Circuit | Equipment Failure/Involved | Other | 35 | 45885 | 37.2625 | -122.2118 | IRO 120 BACK RD- ALSO 180 BACK RD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079776 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99189696 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 7747 | 20150104 | 1633 | 1159170 | 1191 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3477 | 37.251 | -122.3542 | O`DRISCOLL/ 840 (1673): END OF WILLOW SPRINGS RD PESCADERO | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0002372 | OH | Sus | 42306895 | No | 2015 | JAN | Yes | Line to Ground | 99189155 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1517 | 20150128 | 1352 | 1169478 | 259 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 10101 | 37.4432 | -122.4029 | 2 SPANS LD SIDE OF 1517 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0007801 | OH | Sus | 0 | No | 2015 | JAN | Yes | Line to Line | 99186471 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1721 | 20150130 | 546 | 1170122 | 524 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 26200 | 37.3179 | -122.191 | EPPERSON-CHAD/832 (1674): skyline 2 mi south of page mill- alpine | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0008144 | OH | Sus | 31131610 | No | 2015 | JAN | Yes | Line to Ground | 99186275 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 14653 | 20150212 | 1023 | 1189088 | 629 | Distribution Circuit | Equipment Failure/Involved | Other | 9 | 5661 | 37.2402 | -122.3362 | 2/P LD SIDE OF 14653 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0012902 | OH | Sus | 31134266 | No | 2015 | FEB | Yes | Line to Ground | 99182276 | PW | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER |  | 20150223 | 1155 | 1194662 | 255 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 765 | 37.3257 | -122.279 | CLARK/ 1076 (2418): la honda and hilldebrand | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0015093 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Open Circuit | 99180080 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 7499 | 20150322 | 2342 | 1206770 | 918 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 4310 | 37.2884 | -122.2354 | SCHLOCKER- JEFF: 8700 Alpine Road La Honda | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0021293 | OH | Sus | 0 | No | 2015 | MAR | Yes | Line to Line | 99176458 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 5741 | 20150606 | 1113 | 1244750 | 947 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 25569 | 37.2628 | -122.2081 | SLATE CREEK RD AT 5747 WATER PLANT | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0039047 | OH | Sus | 42401524 | No | 2015 | JUN | Yes | Line to Ground | 99165232 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 5753 | 20150610 | 1905 | 1248575 | 382 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 382 | 37.3805 | -122.2542 | 25 UPENUF RD- WOODSIDE | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0040223 | OH | Sus | 42404645 | yes | 2015 | JUN | Yes | Open Circuit | 99164313 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1102 | 24131102 | FUSE | 12249 | 20150622 | 1617 | 1254799 | 628 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 16328 | 37.3531 | -122.2642 | 10707 LA HONDA RD WOODSIDE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0042606 | OH | Sus | 42413185 | No | 2015 | JUN | Yes | Line to Line | 99162489 | CO | OH | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4229 | 20150629 | 1534 | 1258849 | 626 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 626 | 37.2182 | -122.344 | SCHLOCKER- JEFF: near 1101 canyon | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0044086 | OH | Sus | 31164970 | No | 2015 | JUN | Yes | Line to Ground | 99161329 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | HALF MOON BAY-1101 | 24101101 | JUMPER | WIRE DOWN 5 SPANS N/OF 14409 | 20150713 | 802 | 1267140 | 1140 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 3420 | 37.5067 | -122.3723 | SCHLOCKER- JEFF: 4n of rco 14409 half moon bay | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 15-0047078 | OH | Sus | 42425902 | No | 2015 | JUL | Yes | Line to Ground | 1145021 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | SWITCH | 7481 | 20150727 | 1654 | 1278253 | 559 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 15623 | 37.3991 | -122.2935 | IFO 1040 BEAR GLUTCH RD- WDS | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0050810 | OH | Sus | 42437128 | No | 2015 | JUL | Yes | Line to Ground | 1147783 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER | DOWN WIRE ON LA HONDA RD 100FT E/ GRANDVIEW | 20150821 | 937 | 1292472 | 293 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 923 | 37.3899 | -122.2625 | 100FT E/GRANDVIEW ON LA HONDA RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0056574 | OH | Sus | 42455476 | No | 2015 | AUG | Yes | Open Circuit | 1151791 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | RALSTON-1101 | 24141101 | FUSE | 6341 | 20150914 | 28 | 1305188 | 719 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2517 | 118583 | 37.5143 | -122.3381 | C/OUT 7199 | Fog-Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 15-0061124 | OH | Sus | 31184116 | yes | 2015 | SEP | Yes | Line to Ground | 1155016 | CAW | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 8549 | 20151019 | 1045 | 1326067 | 378 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 11358 | 37.2626 | -122.2118 | 41 BACK RD | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0071898 | OH | Sus | 42530111 | No | 2015 | OCT | Yes | Line to Ground | 1163516 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1102 | 24131102 | OTHER | 2369 | 20151116 | 1005 | 1343144 | 315 | Distribution Circuit | Equipment Failure/Involved | Overhead | 60 | 17402 | 37.3599 | -122.2474 | EPPERSON-CHAD/832 (1674): 1 span load side of 2369- eisenberg tap | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0078332 | OH | Sus | 42569643 | yes | 2015 | NOV | Yes | Line to Ground | 1168807 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER | 4133 | 20151212 | 439 | 1359227 | 539 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2049 | 37.3882 | -122.2633 | AVALO- JORGE / 953: tree fell causing 3phases 1span of 6sol down need crew | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084361 | OH | Sus | 0 | No | 2015 | DEC | Yes | Open Circuit | 1173995 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | HALF MOON BAY-1101 | 24101101 | FUSE | 8607 | 20151219 | 1949 | 1366881 | 1078 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 8624 | 37.4451 | -122.3314 | OKRY- DONNIE/2413: tree fell into wire | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086254 | OH | Sus | 42595301 | No | 2015 | DEC | Yes | Line to Ground | 1176206 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | JUMPER | 12KV DOWN 2/P LD SIDE OF LR8982 | 20151219 | 759 | 1366498 | 512 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 27926 | 37.2674 | -122.2109 | 2 POLES LD SIDE OF LR8982 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086178 | OH | Sus | 42595188 | No | 2015 | DEC | Yes | Open Circuit | 1176120 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1102 | 24131102 | FUSE | 8347 | 20151221 | 1901 | 1368214 | 1185 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 14220 | 37.3469 | -122.2095 | 1976 SKYLINE BLVD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086546 | OH | Sus | 42595885 | yes | 2015 | DEC | Yes | Line to Ground | 1176540 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER | WIRE DOWN @ 5957 MAINLINE | 20151222 | 236 | 1368517 | 631 | Distribution Circuit | Vegetation | Tree - fell into line | 312 | 154954 | 37.386 | -122.2641 | POLE WITH FUSE 5957 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086609 | OH | Sus | 31208076 | yes | 2015 | DEC | Yes | Open Circuit | 1176605 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 7481 | 20151222 | 1328 | 1369688 | 794 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 25408 | 37.3991 | -122.2935 | LD SIDE OF 7481 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086801 | OH | Sus | 42595832 | yes | 2015 | DEC | Yes | Line to Line | 1176830 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER | 8329 | 20151225 | 1453 | 1371761 | 1198 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1198 | 37.3816 | -122.2553 | BRODERIUS/1504: 600 OLD LA HONDA RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087302 | OH | Sus | 42597672 | No | 2015 | DEC | Yes | Open Circuit | 1177384 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 11585 | 20151230 | 838 | 1374564 | 761 | Distribution Circuit | 3rd Party | Vehicle | 10 | 7610 | 37.2807 | -122.1486 | 7 spans load side of 11585 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0087838 | OH | Sus | 42599113 | No | 2015 | DEC | Yes | Line to Ground | 1178112 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | EMERALD LAKE-0402 | 24080402 | FUSE | 3501 | 20160106 | 1015 | 1378450 | 384 | Distribution Circuit | 3rd Party | Vehicle | 48 | 18432 | 37.4628 | -122.2643 | O`DRISCOLL/ 840 (1673): LAKEVIEW AND MIDLAND RWC | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003428 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1179006 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER | WIRE DOWN 1/S OF 7573 | 20160106 | 733 | 1378202 | 652 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 14244 | 37.3836 | -122.2889 | 1/S OF 7573 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003406 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1178991 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 4311 | 20160112 | 1100 | 1382043 | 825 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 12375 | 37.305 | -122.268 | 10 SPANS LOAD SIDE OF 4311 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0004740 | OH | Sus | 31212186 | yes | 2016 | JAN | Yes | Line to Ground | 1180100 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 1721 | 20160116 | 1409 | 1385156 | 710 | Distribution Circuit | 3rd Party | Vehicle | 50 | 35500 | 37.318 | -122.1911 | O`DRISCOLL/ 840 (1673): 22 POLES LD/SD/O CO 1721 I POLE N/O 1185 SKYLINE RWC/LA HONDA/SAN MATEO CTY | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0005805 | OH | Sus | 0 | No | 2016 | JAN | Yes | Three Phase Fault | 1180771 | PW | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER | WIRE DOWN AT 8089 | 20160118 | 605 | 1385933 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 105 | 51345 | 37.2193 | -122.3404 | 664 MADRONE AVE | Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006026 | OH | Sus | 42613069 | yes | 2016 | JAN | Yes | Line to Ground | 1180995 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | 8894 | 20160119 | 823 | 1386870 | 733 | Distribution Circuit | Vegetation | Tree - fell into line | 302 | 96160 | 37.25 | -122.3603 | SCHLOCKER- JEFF: 10 s plus minus of lr8894 pescadero | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006227 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1181167 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 5743 | 20160119 | 1502 | 1387749 | 666 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2664 | 37.2629 | -122.2075 | BUSS RD | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006567 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1181388 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4431 | 20160119 | 1804 | 1388051 | 537 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 17184 | 37.3856 | -122.2613 | SCHAPPERT/ 2589 (2268): 1span 6 sol down | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 16-0006625 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1181434 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 11769 | 20160122 | 732 | 1389724 | 371 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 9907 | 37.3142 | -122.2727 | SHELDON & REDWOOD DR | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007378 | OH | Sus | 42615753 | yes | 2016 | JAN | Yes | Line to Ground | 1181973 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | OTHER | WIRE DOWN | 20160123 | 1729 | 1390937 | 1199 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 19184 | 37.2947 | -122.2414 | SCHLOCKER- JEFF: near 9645 alpine road la honda | Partly Cloudy-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007793 | OH | Sus | 42616425 | yes | 2016 | JAN | Yes | Line to Ground | 1182289 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER | DOWN WIRE LINE SIDE OF 4431 | 20160131 | 2212 | 1395761 | 303 | Distribution Circuit | Vegetation | Tree - fell into line | 314 | 26342 | 37.3853 | -122.2613 | 1 SPAN LINE SIDE OF 4431 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009590 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Open Circuit | 1183671 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | 8894 | 20160218 | 1414 | 1408566 | 764 | Distribution Circuit | Vegetation | Tree - branch fell on line | 443 | 46264 | 37.25 | -122.3603 | 410 WURR RD- LOMA MAR | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013885 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Line | 1186873 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 41680 | 20160306 | 1412 | 1422444 | 2875 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 51350 | 37.2749 | -122.2122 | 2 SPANS LD SIDE OF 41680 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0018510 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Three Phase Fault | 1190348 | PW | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | RECLOSER | 8512 | 20160306 | 2113 | 1422805 | 1134 | Distribution Circuit | Vegetation | Tree - fell into line | 287 | 59241 | 37.2891 | -122.213 | 13450 PESCADERO RD | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018594 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190436 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER | WIRE DOWN 2P W/OF 8493 | 20160307 | 551 | 1423231 | 424 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 10161 | 37.3143 | -122.276 | LA HONDA RD AT MEMORY LANE 2P W/OF 8493 | Overcast-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018702 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190544 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | H82 | 20160310 | 905 | 1426347 | 1106 | Distribution Circuit | Vegetation | Tree - fell into line | 1861 | 235765 | 37.4176 | -122.4246 | S/O SW 6017 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 16-0019861 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1191489 | PW | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4227 | 20160311 | 1459 | 1428176 | 703 | Distribution Circuit | Vegetation | Tree - fell into line | 170 | 80940 | 37.2151 | -122.3473 | 1101 Canyon Rd | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020505 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1191892 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER | WIRE DOWN W/12039 | 20160311 | 1433 | 1428577 | 1331 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 99375 | 37.3852 | -122.2458 | ROBERTSON/839 (2486): 25 UPPER LAKE RD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020639 | OH | Sus | 31224348 | yes | 2016 | MAR | Yes | Line to Ground | 1192011 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER | WIRE DOWN @ MTR#1009055607 | 20160311 | 1823 | 1428669 | 477 | Distribution Circuit | Vegetation | Tree - branch fell on line | 68 | 29784 | 37.4202 | -122.3272 | S/O 252 SWETT RD | Strong Winds-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020640 | OH | Sus | 42655224 | yes | 2016 | MAR | Yes | Line to Ground | 1192012 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 3 | HALF MOON BAY-1101 | 24101101 | FUSE | 3665 | 20160312 | 1748 | 1429525 | 1179 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 9432 | 37.3966 | -122.3481 | FULLER- LLOYD / 2588: 10 DURHAM RD | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020818 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192201 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 5749 | 20160312 | 1621 | 1429607 | 4154 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 8308 | 37.263 | -122.2017 | LD SIDE 5749 | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 16-0021301 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192609 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8884 | 20160312 | 1117 | 1429325 | 1047 | Distribution Circuit | Vegetation | Tree - branch fell on line | 341 | 40373 | 37.3895 | -122.2687 | C/OUT 14645 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020766 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1192146 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1102 | 24131102 | RECLOSER | 8952 | 20160313 | 347 | 1429892 | 767 | Distribution Circuit | Vegetation | Tree - fell into line | 296 | 185071 | 37.3512 | -122.1983 | FOXWOOD RD - LOS TRANCOS X-St.: LOS TRANCOS | Overcast-Rain-32-90 F | Conductor, Overhead | On Ground | 16-0020869 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192259 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | JUMPER | DOWN WIRE 4 SPANS LD SIDE OF 3931 | 20160314 | 400 | 1430811 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 9369 | 37.3518 | -122.3342 | 8 SPANS LD SIDE OF 3931 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021135 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Open Circuit | 1192504 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | 8894 | 20160319 | 1152 | 1434217 | 1164 | Distribution Circuit | Vegetation | Tree - fell into line | 301 | 61020 | 37.25 | -122.3601 | CLARK/ 1076 (2418): between co 10459 and 10461 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0022658 | OH | Sus | 31226031 | No | 2016 | MAR | Yes | Line to Ground | 1193621 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4279 | 20160409 | 2208 | 1448017 | 589 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 25389 | 37.318 | -122.3008 | 2 SPAN E/O 7940 LA HONDA RD | Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0027542 | OH | Sus | 0 | yes | 2016 | APR | Yes | Line to Ground | 1197124 | PW | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 8541 | 20160415 | 1534 | 1451532 | 1267 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 19005 | 37.2623 | -122.2131 | SCHLOCKER- JEFF: portola st pk near camp 53 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0029029 | OH | Sus | 42680259 | yes | 2016 | APR | Yes | Line to Ground | 1198190 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER | WIRE DOWN ON NATIVE SONS RD, 1/4 MILE TO S/S | 20160424 | 1532 | 1457161 | 518 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 17012 | 37.2465 | -122.3386 | BROWN- SAMUEL (1558): On Native Sons Rd- 1/4 mile to s/s of bridge | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0031047 | OH | Sus | 42684729 | yes | 2016 | APR | Yes | Line to Ground | 1199724 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | EMERALD LAKE-0401 | 24080401 | JUMPER | WIRE DOWN @ EOL OF 5163 TAP | 20160504 | 1339 | 1464590 | 781 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 826 | 37.4702 | -122.3158 | SCHAPPERT/ 2589 (2268): open 5163 / cut taps then close 5163 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0033786 | OH | Sus | 42690445 | No | 2016 | MAY | Yes | Line to Ground | 1201936 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | OTHER | 8541 | 20160607 | 2153 | 1484963 | 907 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 13605 | 37.2626 | -122.2132 | ROBERTSON/839 (2486): 9000 PORTOLA STATE PARK | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0041797 | OH | Sus | 31246196 | No | 2016 | JUN | Yes | Line to Ground | 1207918 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 8089 | 20160614 | 308 | 1488416 | 619 | Distribution Circuit | Vegetation | Tree - fell into line | 107 | 66233 | 37.2193 | -122.3422 | 22 SPANS LD SIDE OF C/OUT 8089 | Clear-32-90 F | Conductor, Overhead | On Ground | 16-0043005 | OH | Sus | 31247267 | No | 2016 | JUN | Yes | Line to Ground | 1208874 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8319 | 20160712 | 1115 | 1508864 | 1183 | Distribution Circuit | 3rd Party | Vehicle | 33 | 37615 | 37.3833 | -122.2487 | OLD LA HONDA ROAD AND ORCHARD HILLS- WOODSIDE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0049334 | OH | Sus | 0 | No | 2016 | JUL | Yes | Line to Ground | 1213487 | PW | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | 8982 | 20160801 | 623 | 1519597 | 447 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 24585 | 37.2682 | -122.2113 | 3 SPAN LD SIDE OF 8982 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0054033 | OH | Sus | 42756884 | No | 2016 | AUG | Yes | Line to Ground | 1216748 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4431 | 20160807 | 1420 | 1522802 | 610 | Distribution Circuit | Vegetation | Tree - fell into line | 312 | 29869 | 37.3881 | -122.2669 | 277 GRANDVIEW WAY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0055597 | OH | Sus | 31261829 | No | 2016 | AUG | Yes | Line to Ground | 1217636 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE | 6125 | 20160912 | 1340 | 1540330 | 352 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 5632 | 37.4924 | -122.3853 | 78 PILARCITOS | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0064018 | OH | Sus | 0 | No | 2016 | SEP | Yes | Line to Ground | 1223369 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 7487 | 20161016 | 1304 | 1562841 | 805 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4830 | 37.3818 | -122.2647 | 11 starwood | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072886 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1229919 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER | 1551 | 20161030 | 838 | 1572980 | 349 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 349 | 37.3152 | -122.2909 | 3/S LOAD SIDE OF 1551 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076751 | OH | Sus | 42869646 | No | 2016 | OCT | Yes | Force Out | 1232858 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE | 10695 | 20161208 | 959 | 1596863 | 1705 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 8139 | 37.4861 | -122.4191 | 25 SPANS LD SIDE OF 10695 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084592 | OH | Sus | 42893501 | yes | 2016 | DEC | Yes | Line to Ground | 1239132 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | RECLOSER | 8512 | 20161209 | 1622 | 1597970 | 573 | Distribution Circuit | Vegetation | Tree - fell into line | 143 | 12362 | 37.2891 | -122.2132 | ALPINE & PESCADERO- LA HONDA | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084828 | OH | Sus | 31288616 | No | 2016 | DEC | Yes | Line to Ground | 1239354 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1102 | 24131102 | JUMPER | 1 SPAN 2PHASES WIRE DOWN S/OF 7851 | 20161210 | 2226 | 1599518 | 1084 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2168 | 37.2862 | -122.2277 | JUST S/OF FU 7851 ON SINGLE PHASE TAP LINE FEEDING 2 OH TRANSF | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085050 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Open Circuit | 1239604 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | HALF MOON BAY-1101 | 24101101 | FUSE | 1751 | 20161215 | 1715 | 1603365 | 555 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2775 | 37.443 | -122.3268 | 30 FOREST RD. WOODSIDE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085824 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1240492 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4427 | 20161215 | 1958 | 1603706 | 662 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 14564 | 37.3996 | -122.2505 | 2087 PORTOLA RD | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085902 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1240567 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 6115 | 20161216 | 8 | 1604326 | 2272 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 65888 | 37.3713 | -122.3432 | O`DRISCOLL/ 840 (1673): LOAD SIDE OF 6115 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0086051 | OH | Sus | 31289656 | yes | 2016 | DEC | Yes | Line to Line | 1240773 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 7983 | 20161216 | 1430 | 1605025 | 248 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 744 | 37.2067 | -122.3324 | OLMO FIRE ROAD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0086070 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1240799 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1102 | 24101102 | FUSE | 14497 | 20161226 | 708 | 1610914 | 427 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 427 | 37.5459 | -122.4947 | 2 spans south of co 14497 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0087029 | OH | Sus | 42905586 | No | 2016 | DEC | Yes | Line to Line | 1242220 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | PACIFICA-1102 | 22811102 | FUSE | 1849 | 20170106 | 940 | 1620255 | 1500 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 1500 | 37.6214 | -122.4808 | 3 SPANS LD SIDE OF 1849 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004258 | OH | Sus | 0 | No | 2017 | JAN | Yes | Three Phase Fault | 1244154 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER | WIRE DOWN 5/P/LD/SIDE 8601 | 20170107 | 1033 | 1621574 | 168 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 6936 | 37.4392 | -122.3249 | LD SIDE 8601 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004648 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244470 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8974 | 20170112 | 605 | 1640986 | 1172 | Distribution Circuit | Vegetation | Tree - fell into line | 279 | 62368 | 37.3881 | -122.2669 | 4 SP WEST OF FUSE 7487 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008282 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247722 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 7983 | 20170117 | 1048 | 1645306 | 972 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2916 | 37.2067 | -122.3324 | 10SPANS LD SIDE 7983. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0009612 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Line | 1248832 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4737 | 20170128 | 822 | 1669347 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 11252 | 37.4023 | -122.3361 | 3 PHASE WIRE DOWN at 1492 STAR HILL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0015801 | OH | Sus | 31300945 | No | 2017 | JAN | Yes | Line to Line | 1254234 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | HALF MOON BAY-1101 | 24101101 | SWITCH | 5295 | 20170204 | 1046 | 1674767 | 56 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 3656 | 37.3895 | -122.2658 | NONE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017209 | OH | Sus | 0 | No | 2017 | FEB | Yes | Force Out | 1255407 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | SNEATH LANE-1101 | 22721101 | FUSE | 10037 | 20170204 | 829 | 1674624 | 658 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 12502 | 37.6183 | -122.436 | IRO 2471 WHITMAN WAY | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017433 | OH | Sus | 42939001 | No | 2017 | FEB | Yes | Line to Line | 1255391 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 7813 | 20170205 | 2243 | 1675718 | 762 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 8382 | 37.3862 | -122.2933 | 200 ALLEN RD | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017632 | OH | Sus | 31304022 | No | 2017 | FEB | Yes | None | 1255597 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8974 | 20170206 | 951 | s1255722 | 386 | Distribution Circuit | Vegetation | Tree - bark fell into line | 11 | 3526 | 37.3881 | -122.2669 | 2 POLES S/O 4433 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017763 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1255722 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8615 | 20170206 | 2228 | 1677195 | 1049 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 14686 | 37.4248 | -122.3133 | 2 blue jay way | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018002 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1255854 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8974 | 20170208 | 615 | 1681340 | 1602 | Distribution Circuit | Equipment Failure/Involved | Overhead | 284 | 199793 | 37.3881 | -122.2669 | HWY 35 & HWY 84 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018854 | OH | Sus | 31304022 | yes | 2017 | FEB | Yes | Line to Ground | 1256600 | PW | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 8541 | 20170210 | 925 | 1684791 | 905 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 13575 | 37.2626 | -122.2132 | SPANS LD SIDE OF 8541 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019903 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1257317 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER | WIRE DOWN 9 SPANS LD SIDE OF 6187 | 20170210 | 134 | 1684458 | 1329 | Distribution Circuit | Vegetation | Tree - fell into line | 338 | 57036 | 37.3899 | -122.2749 | WIRE DOWN 9 SPANS LD SIDE OF 6187 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019745 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Open Circuit | 1257216 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1101 | 24101101 | OTHER | WIRE DOWN | 20170305 | 1623 | 1720330 | 1536 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 30136 | 37.4856 | -122.4186 | 90 DIGGES CANYON ROAD | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0028544 | OH | Sus | 42958978 | yes | 2017 | MAR | Yes | Line to Ground | 1264906 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1102 | 24101102 | FUSE | 12457 | 20170307 | 1040 | 1721732 | 1708 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1708 | 37.524 | -122.488 | MULTIPLE LOCATIONS LD SIDE OF 12457 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0029042 | OH | Sus | 0 | No | 2017 | MAR | Yes | Line to Ground | 1265281 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | JUMPER | 2 SP WIRE DOWN | 20170316 | 1558 | 1728715 | 634 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1268 | 37.2551 | -122.221 | 2 SPANS FROM EOL | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0031375 | OH | Sus | 0 | No | 2017 | MAR | Yes | Line to Line | 1266988 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4133 | 20170320 | 1044 | 1730667 | 391 | Distribution Circuit | 3rd Party | Customer Equipment | 5 | 1955 | 37.3881 | -122.2632 | 6 SPAN LD SIDE FUSE 4133 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0031967 | OH | Sus | 42973565 | yes | 2017 | MAR | Yes | Line to Ground | 1267529 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | HALF MOON BAY-1101 | 24101101 | FUSE | 1335 | 20170321 | 1331 | 1732372 | 1589 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1589 | 37.5097 | -122.3862 | LD SIDE OF 1335 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0032510 | OH | Sus | 42974397 | yes | 2017 | MAR | Yes | Line to Line | 1267843 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8884 | 20170321 | 658 | 1731577 | 620 | Distribution Circuit | Vegetation | Tree - branch fell on line | 341 | 12339 | 37.3895 | -122.2687 | 6 SPAN WEST OF 7867 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0032189 | OH | Sus | 42973876 | yes | 2017 | MAR | Yes | Line to Ground | 1267677 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER | WIRE DOWN 2/SP/LD SIDE 345 SWETT RD | 20170331 | 1003 | 1740992 | 347 | Distribution Circuit | Vegetation | Tree - branch fell on line | 68 | 17986 | 37.4185 | -122.3296 | 2/SP/LD/SIDE 345 SWETT RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0035513 | OH | Sus | 42981559 | yes | 2017 | MAR | Yes | Line to Ground | 1270147 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 5487 | 20170331 | 1200 | 1741189 | 500 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2500 | 37.3833 | -122.2345 | IRO 877 PORTOLA RD. PORTOLA VALLEY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0035639 | OH | Sus | 42981774 | yes | 2017 | MAR | Yes | Line to Ground | 1270193 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE | 9839 | 20170410 | 1405 | 1754567 | 251 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 502 | 37.5099 | -122.4059 | CLARK/ 1076 (2418): 6 spans load side 9839 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038933 | OH | Sus | 42991809 | No | 2017 | APR | Yes | Line to Ground | 1272929 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE | 10695 | 20170428 | 2308 | 1770101 | 667 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 11339 | 37.4861 | -122.4191 | 3 SPANS LD SIDE OF 10695 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0043840 | OH | Sus | 43003560 | yes | 2017 | APR | Yes | Line to Ground | 1276443 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 7673 | 20170501 | 1344 | 1771653 | 1384 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 8859 | 37.2978 | -122.2417 | SCHLOCKER- JEFF: 15 heritage la honda | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0044267 | OH | Sus | 0 | No | 2017 | MAY | Yes | Line to Ground | 1276814 | PW | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | HALF MOON BAY-1101 | 24101101 | FUSE | 4151 | 20170503 | 1516 | 1773632 | 1404 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1404 | 37.5234 | -122.4194 | 2 SPAN LOAD SIDE OF 4151 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0044971 | OH | Sus | 31323613 | yes | 2017 | MAY | Yes | Line to Ground | 1277328 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER | WIRE DOWN LINE SIDE 13269 | 20170505 | 2152 | 1775896 | 1131 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 46591 | 37.3759 | -122.2624 | KUHLS- STEVE: 4-5 man crew tree crew 100-200ft o 6sol tree wire | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0045727 | OH | Sus | 43007995 | No | 2017 | MAY | Yes | Open Circuit | 1277839 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 1229 | 20170506 | 814 | 1776053 | 550 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2200 | 37.3937 | -122.2618 | STILL CREEK RD- WS | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0045764 | OH | Sus | 0 | yes | 2017 | MAY | Yes | Line to Ground | 1277883 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 7481 | 20170506 | 653 | 1776017 | 1080 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 30635 | 37.399 | -122.2933 | BEAR GULCH RD- WS | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0045777 | OH | Sus | 0 | yes | 2017 | MAY | Yes | Line to Ground | 1277900 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | WOODSIDE-1104 | 24251104 | JUMPER | WIRE DOWN LD SIDE 52233 | 20170608 | 1926 | 1799995 | 450 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 900 | 37.4346 | -122.2815 | at 52233 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0053829 | OH | Sus | 0 | yes | 2017 | JUN | Yes | Open Circuit | 1283828 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | JUMPER | WIRE DOWN 3 SPANS LD SIDE OF LR 8982 | 20170625 | 822 | 1817527 | 591 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 32323 | 37.2677 | -122.2111 | 1800 PORTOLA STATE PARK RD 3 SPANS LD SIDE OF LR 8982 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0058432 | OH | Sus | 43044666 | No | 2017 | JUN | Yes | Line to Ground | 1287534 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 12185 | 20170630 | 1231 | 1821457 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 6339 | 37.3752 | -122.3773 | 3890 TUNITAS CREEK RD- HMB | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0059825 | OH | Sus | 31334637 | No | 2017 | JUN | Yes | Line to Ground | 1288557 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 5741 | 20170716 | 1515 | 1832770 | 654 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 17658 | 37.263 | -122.2086 | 1/POLE LINE SIDE OF 5747- SLATE CREEK RD- LH | Clear-Above 90 | Connector or Splice (OH) | Broken, wire on ground | 17-0063248 | OH | Sus | 43060364 | No | 2017 | JUL | Yes | Force Out | 1291053 | CSO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 3217 | 20170721 | 1050 | 1837014 | 426 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 6816 | 37.294 | -122.2409 | 3 SPANS LOAD SIDE OF 3217 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0064585 | OH | Sus | 43065178 | No | 2017 | JUL | Yes | Line to Ground | 1292005 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 5739 | 20170731 | 1627 | 1843362 | 573 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4011 | 37.2629 | -122.209 | LD SIDE AT FUCO 5739 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0066832 | OH | Sus | 43071693 | No | 2017 | JUL | Yes | Line to Line | 1293543 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1125 | 20170828 | 208 | 1860999 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 24381 | 37.2608 | -122.3247 | DEARBORN PARK RD E/OF PRUESS RD- PESCADERO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0073273 | OH | Sus | 43094670 | yes | 2017 | AUG | Yes | Line to Line | 1298150 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1102 | 24131102 | TRIP-SAVER | 1721 | 20170904 | 2034 | 1870150 | 442 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 22100 | 37.3152 | -122.1879 | SKYLINE 1/4 MI S/OF PAGE MILL -- 8/P E/OF 1721 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0075898 | OH | Sus | 31349122 | yes | 2017 | SEP | Yes | Line to Ground | 1300139 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1119 | 20170906 | 2008 | 1871967 | 1026 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4914 | 37.2819 | -122.2847 | BURNS VALLEY RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0076502 | OH | Sus | 43100667 | No | 2017 | SEP | Yes | Line to Ground | 1300563 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1125 | 20170920 | 206 | 1882150 | 851 | Distribution Circuit | 3rd Party | Vehicle | 43 | 36593 | 37.2608 | -122.3247 | DEERBORN PARK RD & KYNE RD- PESCADERO | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0080179 | OH | Sus | 31352021 | No | 2017 | SEP | Yes | Line to Ground | 1303297 | PW | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 6087 | 20171007 | 507 | 1892361 | 502 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 3010 | 37.3749 | -122.3779 | SOURCE SIDE OF 12563 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0084908 | OH | Sus | 43161017 | No | 2017 | OCT | Yes | Line to Ground | 1306343 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | 8898 | 20171011 | 332 | 1898084 | 1357 | Distribution Circuit | Vegetation | Tree - fell into line | 385 | 53673 | 37.3135 | -122.2756 | LA HONDA RD S/OF ENTRADA WAY | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086199 | OH | Sus | 43190478 | No | 2017 | OCT | Yes | Three Phase Fault | 1307375 | PW | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1102 | 24101102 | FUSE | 5521 | 20171015 | 1600 | 1901424 | 619 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 619 | 37.544 | -122.4993 | 1 SPAN LD SIDE OF 5521 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087574 | OH | Sus | 31361140 | No | 2017 | OCT | Yes | Line to Ground | 1308549 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 5485 | 20171023 | 2123 | 1908338 | 442 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1768 | 37.3716 | -122.3598 | CLARK/ 1076 (2418): 6 pole loadside co 5485 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0089820 | OH | Sus | 31362141 | No | 2017 | OCT | Yes | Line to Ground | 1310209 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | CAROLANDS-0404 | 24060404 | JUMPER | WIRE DOWN IFO 1220 CARDIGAN | 20171025 | 1042 | 1909406 | 483 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 13706 | 37.5517 | -122.3545 | IFO 1220 CARDIGAN | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0090327 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1310536 | CSO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 6075 | 20171031 | 1550 | 1913229 | 345 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 5785 | 37.4041 | -122.4128 | SCHLOCKER- JEFF: 2359 purissima creek road | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0091620 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1311483 | PW | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE | 10695 | 20171104 | 1408 | 1916064 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 3824 | 37.4861 | -122.4191 | 132 DIGGES CANYON RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0092661 | OH | Sus | 43207323 | No | 2017 | NOV | Yes | Line to Ground | 1312221 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1125 | 20171104 | 1403 | 1916072 | 425 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 6480 | 37.2608 | -122.3247 | LOWER DEARBORN PARK RD 5 SPANS PAST 11271- PESCADERO | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0092655 | OH | Sus | 31363938 | No | 2017 | NOV | Yes | Line to Ground | 1312215 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | 98440 | 20171112 | 712 | 1920803 | 164 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 24307 | 37.2667 | -122.3224 | 1 SPAN W/1015 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0094490 | OH | Sus | 43213117 | No | 2017 | NOV | Yes | Line to Ground | 1313522 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1102 | 24131102 | FUSE | 4995 | 20171116 | 2001 | 1924405 | 1599 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 35178 | 37.2876 | -122.2464 | CLARK/ 1076 (2418): 9111 Apline rd La honda | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0095828 | OH | Sus | 0 | yes | 2017 | NOV | Yes | Line to Line | 1314595 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER | WIRE DOWN | 20171116 | 1741 | 1924321 | 628 | Distribution Circuit | 3rd Party | Vehicle | 312 | 20249 | 37.3722 | -122.2641 | LA HONDA RD 1 MILE S/OF FU 7487 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0095730 | OH | Sus | 0 | yes | 2017 | NOV | Yes | Line to Line | 1314480 | PW | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1102 | 24131102 | JUMPER | OPEN JUMPERS 2/P/S/O 5739 | 20171118 | 818 | 1925529 | 3799 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 26593 | 37.2628 | -122.2087 | S/O OPEN JUMPERS 2/P/S/O 5739 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0096196 | OH | Sus | 0 | No | 2017 | NOV | Yes | Line to Ground | 1314857 | PW | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 8541 | 20171218 | 723 | 1946541 | 633 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 9495 | 37.2625 | -122.2131 | 12-13 SPANS SOUTH OF 8541 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102411 | OH | Sus | 43237790 | No | 2017 | DEC | Yes | Line to Ground | 1320413 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 12185 | 20171220 | 755 | 1948293 | 590 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 6602 | 37.3752 | -122.3773 | 3890 TUNITAS CREEK RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0102756 | OH | Sus | 43238631 | yes | 2017 | DEC | Yes | Line to Ground | 1321076 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1102 | 24131102 | FUSE | 13329 | 20180104 | 1027 | 1827 | 3042 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 8484 | 37.2535 | -122.2165 | 4/SP FROM EOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0003644 | OH | Sus | 43244681 | yes | 2018 | JAN | Yes | Line to Line | 1323182 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1127 | 20180108 | 1319 | 4048 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 17476 | 37.2549 | -122.3459 | 10 SPANS LD SIDE OF C/OUTS 1127 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0004393 | OH | Sus | 43246407 | yes | 2018 | JAN | Yes | Line to Ground | 1323658 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4279 | 20180108 | 1931 | 4260 | 117 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 10881 | 37.3176 | -122.3002 | at C/OUTS 14513 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0004461 | OH | Sus | 0 | yes | 2018 | JAN | Yes | Line to Ground | 1323693 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1102 | 24131102 | FUSE | 7809 | 20180109 | 1844 | 5439 | 529 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3703 | 37.2693 | -122.2115 | 1 SPAN DOWN 1 SPAN LD SIDE 7809 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0004886 | OH | Sus | 43247053 | yes | 2018 | JAN | Yes | Line to Ground | 1323972 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4279 | 20180129 | 855 | 15700 | 99 | Distribution Circuit | Animal | Bird found | 93 | 9207 | 37.3176 | -122.3002 | 2 SPAN SOURCE SIDE 10303 | Clear-32-90 F | Conductor, Overhead | On Ground | 18-0009802 | OH | Sus | 0 | No | 2018 | JAN | Yes | Open Circuit | 1327090 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE | 4141 | 20180226 | 628 | 31388 | 363 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 12516 | 37.4945 | -122.4539 | 590 MIRAMAR DR | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0017120 | OH | Sus | 43284749 | yes | 2018 | FEB | Yes | Line to Ground | 1332061 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER | WIRE DOWN LD SIDE C/OUTS 7813 | 20180302 | 1713 | 36756 | 1189 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 4986 | 37.3863 | -122.2935 | LD SIDE 7813 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019250 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333449 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | RECLOSER | 8512 | 20180414 | 314 | 66706 | 606 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 16419 | 37.2892 | -122.2132 | ALPINE RD 1P S/OF PESCADERO CR RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0032208 | OH | Sus | 31388701 | No | 2018 | APR | Yes | Line to Ground | 1342652 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8972 | 20180520 | 1834 | 90280 | 1153 | Distribution Circuit | Vegetation | Tree - bark fell into line | 68 | 78404 | 37.4185 | -122.3224 | 3 SPAN LD SIDE OF 8972 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0042653 | OH | Sus | 43351746 | No | 2018 | MAY | Yes | Line to Ground | 1350253 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 7809 | 20180603 | 1559 | 100245 | 2152 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4839 | 37.2677 | -122.2134 | 1652 PORTOLA STATE PARK RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0046777 | OH | Sus | 43361555 | No | 2018 | JUN | Yes | Line to Ground | 1353435 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | EMERALD LAKE-0402 | 24080402 | RECLOSER | 8872 | 20180609 | 2114 | 105508 | 687 | Distribution Circuit | 3rd Party | Vehicle | 665 | 93925 | 37.4638 | -122.2719 | S/O 10879 ON JEFFERSON AVE | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0049308 | OH | Sus | 31395500 | yes | 2018 | JUN | Yes | Line to Ground | 1355350 | PW | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | WOODSIDE-1101 | 24251101 | JUMPER | WIRE DOWN @ LOS TRANCOS | 20180618 | 2219 | 112410 | 474 | Distribution Circuit | Vegetation | Tree - fell into line | 298 | 139866 | 37.3497 | -122.199 | WIRE DOWN at 1044 LOS TRANCOS | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 18-0052108 | OH | Sus | 31396513 | No | 2018 | JUN | Yes | Line to Ground | 1357530 | CAW | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 5739 | 20180711 | 629 | 128749 | 551 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2171 | 37.2629 | -122.209 | MTR # 1010189704 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0058785 | OH | Sus | 31399516 | No | 2018 | JUL | Yes | Line to Ground | 1362862 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1102 | 24131102 | FUSE | 8347 | 20180718 | 1807 | 135066 | 3080 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 40040 | 37.3464 | -122.2101 | 5933 ALPINE RD | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0061250 | OH | Sus | 43410202 | yes | 2018 | JUL | Yes | Line to Ground | 1364858 | PW | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | 98440 | 20180808 | 1534 | 151600 | 646 | Distribution Circuit | Equipment Failure/Involved | Overhead | 808 | 54974 | 37.2667 | -122.3224 | 13366 PESCADERO RD N/O SW 6591 | Clear-32-90F | Conductor, Overhead | On Ground | 18-0058731 | OH | Sus | 35021876 | No | 2018 | AUG | Yes | Line to Ground | 1369922 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 12185 | 20181005 | 424 | 188800 | 606 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 5470 | 37.3752 | -122.3773 | CLARK/ 1076 (2418): 3949 Tunitus crk rd HMB | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0087154 | OH | Sus | 43497025 | No | 2018 | OCT | Yes | Line to Ground | 1383248 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | JUMPER | WIRE DOWN @ LAST SPAN MEMORY LANE | 20181007 | 1129 | 190282 | 393 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 3386 | 37.3152 | -122.2772 | APPROX 18 MEMORY LANE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0087934 | OH | Sus | 43498410 | yes | 2018 | OCT | Yes | None | 1383865 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 13833 | 20181017 | 1359 | 197479 | 502 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 11546 | 37.3229 | -122.2693 | 2/S LD SIDE 13833 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 18-0091453 | OH | Sus | 43510119 | No | 2018 | OCT | Yes | Line to Ground | 1386448 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | HALF MOON BAY-1101 | 24101101 | FUSE | 1745 | 20181029 | 240 | 203997 | 468 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 7020 | 37.4429 | -122.3289 | IFO 50 BIG PINE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0094996 | OH | Sus | 31414303 | No | 2018 | OCT | Yes | Line to Line | 1388820 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 6115 | 20181109 | 1412 | 212548 | 1503 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 42963 | 37.3713 | -122.3432 | 3215 bear gulch rd. | Clear-32-90 F | Conductor, Overhead | On Ground | 18-0098721 | OH | Sus | 43535730 | No | 2018 | NOV | Yes | Multi-Fault | 1391782 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | EMERALD LAKE-0401 | 24080401 | FUSE | 1669 | 20181123 | 1318 | 223081 | 5806 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 12251 | 37.4447 | -122.2882 | 8 SPANS SOURCE S/O 5477 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102667 | OH | Sus | 43585786 | yes | 2018 | NOV | Yes | Multi-Fault | 1394759 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4737 | 20181128 | 2207 | 227019 | 994 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 10028 | 37.4023 | -122.3361 | LD SIDE 3665 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104633 | OH | Sus | 31417032 | yes | 2018 | NOV | Yes | Line to Ground | 1395948 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | HALF MOON BAY-1101 | 24101101 | SWITCH | 6393 | 20181201 | 1025 | 230900 | 566 | Distribution Circuit | Vegetation | Tree - fell into line | 113 | 63958 | 37.4536 | -122.3406 | 120 WARE RD- WS | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105801 | OH | Sus | 31417402 | yes | 2018 | DEC | Yes | Multi-Fault | 1396766 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 5637 | 20181201 | 1016 | 230891 | 451 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4059 | 37.3844 | -122.235 | 158 WAYSIDE- WS | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0105830 | OH | Sus | 31417398 | yes | 2018 | DEC | Yes | Multi-Fault | 1396772 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1035 | 20181224 | 1607 | 246556 | 1240 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 3720 | 37.3257 | -122.2796 | LA HONDA & HILDEBRAND- LH | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110535 | OH | Sus | 43621703 | yes | 2018 | DEC | Yes | Line to Ground | 1401614 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER | WIRE DOWN @ 266 LAGUNA DR | 20190101 | 425 | 251288 | 578 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 2870 | 37.3126 | -122.2717 | SCHLOCKER- JEFF: 266 laguna la honda | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0003395 | OH | Sus | 43624047 | No | 2019 | JAN | Yes | Line to Ground | 1402601 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | EMERALD LAKE-0401 | 24080401 | FUSE | 1669 | 20190105 | 1533 | 254462 | 1948 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 7792 | 37.4447 | -122.2882 | KUHLS- STEVE: 100 ft of 4 str and sleeves end of toyon trail | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0004933 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403463 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER | WIRE DOWN | 20190105 | 956 | 253702 | 399 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 4885 | 37.3765 | -122.2551 | 2 MEDWAY RD WOODSIDE | Overcast-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0004695 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Open Circuit | 1403253 | CAW | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 5745 | 20190107 | 1255 | 259401 | 1837 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3674 | 37.2648 | -122.2065 | KUHLS- STEVE: 120ft of 1/0 alum- straighten pole and remove limb single buckets only ssd 5745 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005998 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Force Out | 1404303 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | JUMPER | WIRE DOWN | 20190108 | 1705 | 260916 | 2845 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 9134 | 37.2839 | -122.2129 | 225 PORTOLA STATE PARK | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0006488 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1404574 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 1097 | 20190108 | 2350 | 261125 | 1057 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 35837 | 37.383 | -122.2634 | 1/S 1097 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0006623 | OH | Sus | 43627999 | yes | 2019 | JAN | Yes | Force Out | 1404705 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 13353 | 20190109 | 1135 | 261751 | 633 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1266 | 37.3181 | -122.2589 | 2/P LINE SIDE OF FUSE 4157 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0006911 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Force Out | 1404872 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | OTHER | 5745 | 20190109 | 1924 | 262064 | 1191 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2382 | 37.2648 | -122.2065 | LD SIDE 5745 | Clear-32-90 F | Conductor, Overhead | On Ground | 19-0007311 | OH | Sus | 31421645 | yes | 2019 | JAN | Yes | Line to Ground | 1405147 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | RECLOSER | 8512 | 20190112 | 35 | 263649 | 768 | Distribution Circuit | Vegetation | Tree - fell into line | 281 | 90848 | 37.2892 | -122.2132 | 3 SPANS 2/N 4311 (19405 PESCADERO CREEK RD) | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0008183 | OH | Sus | 31421696 | No | 2019 | JAN | Yes | Line to Ground | 1405707 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 7573 | 20190113 | 750 | 264154 | 365 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1825 | 37.3849 | -122.2897 | KUHLS- STEVE: 3 man crew put up 200 ft of 4acsr tree wire first 2 spans from c/o7573 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0008345 | OH | Sus | 43633440 | No | 2019 | JAN | Yes | Line to Ground | 1405917 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4279 | 20190115 | 1941 | 266342 | 434 | Distribution Circuit | Vegetation | Tree - branch fell on line | 93 | 18938 | 37.3176 | -122.3002 | LA HONDA RD 900' E/OF BOOTS & SADDLES- LA HONDA | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009310 | OH | Sus | 43636018 | yes | 2019 | JAN | Yes | Line to Line | 1406431 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 13333 | 20190118 | 1233 | 275778 | 387 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 515 | 37.305 | -122.2574 | LD SIDE 4313 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011760 | OH | Sus | 43635440 | yes | 2019 | JAN | Yes | Line to Ground | 1408200 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 2683 | 20190118 | 841 | 275358 | 1469 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1469 | 37.315 | -122.195 | Alpine Rd 6P W/O Skyline Blvd. La Honda | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011578 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408102 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | PACIFICA-1103 | 22811103 | FUSE | 10501 | 20190120 | 1703 | 277465 | 537 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 8055 | 37.5832 | -122.498 | LOAD SIDE OF 10501 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012612 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408938 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8901 | 20190120 | 1831 | 277555 | 975 | Distribution Circuit | Vegetation | Tree - branch fell on line | 314 | 33260 | 37.3825 | -122.2869 | 2 SPANS E/OF 400 ALLEN RD- WOODSIDE | Partly Cloudy-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012631 | OH | Sus | 31422194 | yes | 2019 | JAN | Yes | Line to Ground | 1408960 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1101 | 24101101 | JUMPER | WIRE DOWN LD SIDE 6129 | 20190220 | 1705 | 320049 | 1150 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 2300 | 37.4742 | -122.4084 | LD SIDE 6129 at OD BK | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 19-0026611 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1419263 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER | WIRE DOWN & POLE LEANING | 20190305 | 2244 | 332040 | 993 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 26384 | 37.4029 | -122.2871 | 11393 | Overcast-32-90 F | Conductor, Overhead | On Ground | 19-0031042 | OH | Sus | 43690685 | yes | 2019 | MAR | Yes | Line to Ground | 1422153 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | 98440 | 20190307 | 2317 | 334014 | 134 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 16373 | 37.2667 | -122.3224 | PESCADERO CREEK RD 1/SPAN W/OF 81321 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031873 | OH | Sus | 0 | No | 2019 | MAR | Yes | Line to Ground | 1422682 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE | 4141 | 20190312 | 1623 | 337574 | 436 | Distribution Circuit | Vegetation | Tree - branch fell on line | 59 | 25331 | 37.4945 | -122.4539 | LOAD SIDE OF 4141 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033153 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1423620 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 12065 | 20190409 | 1821 | 357306 | 599 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 18569 | 37.1724 | -122.3131 | CLARK/ 1076 (2418): 3015 Whitehouse cyn rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0041149 | OH | Sus | 43731291 | yes | 2019 | APR | Yes | Line to Ground | 1429241 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4279 | 20190411 | 1619 | 359077 | 620 | Distribution Circuit | Vegetation | Tree - branch fell on line | 83 | 22624 | 37.3176 | -122.3002 | 1 W/O 6911 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0041770 | OH | Sus | 43737416 | yes | 2019 | APR | Yes | Line to Line | 1429746 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8615 | 20190417 | 1929 | 362768 | 1420 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 19880 | 37.4248 | -122.3133 | 2021-2025 KINGS MOUNTIAN RD // POLE 2 SPANS E/O 4909 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0043770 | OH | Sus | 31434610 | No | 2019 | APR | Yes | Line to Ground | 1431147 | PW | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER | WIRE DOWN | 20190423 | 919 | 366325 | 552 | Distribution Circuit | Equipment Failure/Involved | Overhead | 65 | 9755 | 37.377 | -122.2654 | 14850 LA HONDA RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0045232 | OH | Sus | 0 | yes | 2019 | APR | Yes | Open Circuit | 1432298 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 5703 | 20190617 | 1701 | 418054 | 581 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1743 | 37.2697 | -122.3158 | LD SIDE 5703 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0068781 | OH | Sus | 31454418 | No | 2019 | JUN | Yes | Line to Line | 1450031 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | OTHER | WIRE DOWN 2/P/N OF C0521 | 20190708 | 1925 | 443129 | 115 | Distribution Circuit | Vegetation | Tree - fell into line | 141 | 12603 | 37.2985 | -122.2662 | 2/P/N OF C-521 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0075416 | OH | Sus | 43870181 | No | 2019 | JUL | Yes | Line to Ground | 1454841 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 3 | HALF MOON BAY-1103 | 24101103 | OTHER | WIRE DOWN | 20190803 | 808 | 480233 | 340 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 2106 | 37.5384 | -122.4928 | 40 HERMOSA RD- MONTARA | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0084028 | OH | Sus | 43908065 | No | 2019 | AUG | Yes | Open Circuit | 1460578 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4199 | 20190807 | 520 | 487995 | 808 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 808 | 37.1423 | -122.3261 | CLARK/ 1076 (2418): Cabrillo Hwy at Cascade ranch co 4199 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0085095 | OH | Sus | 43910774 | No | 2019 | AUG | Yes | Line to Ground | 1461253 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | SWITCH | 587 | 20190814 | 2122 | 511309 | 943 | Distribution Circuit | Vegetation | Tree - fell into line | 288 | 82064 | 37.3182 | -122.1908 | 225 PORTOLA STATE PARK RD | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0088069 | OH | Sus | 0 | yes | 2019 | AUG | Yes | Force Out | 1463149 | CSO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | TRIP-SAVER | 8089 | 20190912 | 601 | 572870 | 730 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 77380 | 37.2191 | -122.3424 | CGC 314671526917 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0098066 | OH | Sus | 43953935 | No | 2019 | SEP | Yes | Line to Ground | 1469441 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | JUMPER | WIRE DOWN 3 SPANS LD SIDE OF 1721 | 20190912 | 1351 | 576157 | 1747 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 89097 | 37.3148 | -122.1874 | 3 SPANS LD SIDE 1721 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0098386 | OH | Sus | 0 | No | 2019 | SEP | Yes | Line to Ground | 1469606 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | WOODSIDE-1104 | 24251104 | TRIP-SAVER | 3583 | 20190926 | 48 | 615637 | 737 | Distribution Circuit | Vegetation | Tree - fell into line | 99 | 63147 | 37.4245 | -122.2736 | N/O SUMMIT SPRINGS & PATROL ON SUMMIT SPRINGS | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0103844 | OH | Sus | 31473328 | yes | 2019 | SEP | Yes | Three Phase Fault | 1473060 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 7983 | 20190928 | 1611 | 628139 | 1454 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4362 | 37.2067 | -122.3324 | 10 SPANS LOAD SIDE OF 7983 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0105015 | OH | Sus | 0 | yes | 2019 | SEP | Yes | Open Circuit | 1473790 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 7487 | 20190928 | 2039 | 628454 | 938 | Distribution Circuit | Vegetation | Tree - branch fell on line | 65 | 19089 | 37.3818 | -122.2647 | 22 STARWOOD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0105107 | OH | Sus | 0 | yes | 2019 | SEP | Yes | Line to Ground | 1473889 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1102 | 24131102 | JUMPER | TREE FELL WIRE DOWN BOTH SPANS | 20191020 | 402 | 674698 | 675 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1257 | 37.3432 | -122.216 | SOURCE SIDE OF FU 1433 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0113781 | OH | Sus | 44013220 | No | 2019 | OCT | Yes | Line to Ground | 1481283 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | BERESFORD-0403 | 24040403 | FUSE | 1581 | 20191101 | 918 | 697328 | 820 | Distribution Circuit | 3rd Party | Vehicle | 28 | 22960 | 37.5509 | -122.3413 | CRYSTAL SPRINGS S/OF MERNER HILLSBOROUGH | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0119871 | OH | Sus | 0 | No | 2019 | NOV | Yes | Multi-Fault | 1488665 | PW | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 3211 | 20191102 | 2209 | 698458 | 1163 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6978 | 37.4188 | -122.3316 | LD SIDE 3211- END OF SWETT RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0120493 | OH | Sus | 31477180 | No | 2019 | NOV | Yes | Line to Ground | 1488913 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE | 6129 | 20200102 | 825 | 753774 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 812 | 37.4754 | -122.4119 | LD SIDE OF 6129 & 11 SPANS FROM EOL | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0004490 | OH | Sus | 44143118 | No | 2020 | JAN | Yes | Line to Ground | 1503815 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 6973 | 20200102 | 858 | 753596 | 722 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 4 | 2888 | 37.3174 | -122.3331 | 1 SPAN LD SIDE OF 6973 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0004414 | OH | Sus | 31484775 | No | 2020 | JAN | Yes | Line to Ground | 1503798 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 6081 | 20200106 | 47 | 755207 | 954 | Distribution Circuit | Vegetation | Tree - fell into line | 117 | 66702 | 37.3591 | -122.3963 | KRUPENS-DOUG/ 559-908-8529: NEAR 1855 TUNITAS CREEK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0005325 | OH | Sus | 31485084 | No | 2020 | JAN | Yes | Line to Ground | 1504183 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER | WIRE DOWN 2 SP LD SIDE OF 4293 | 20200118 | 1331 | 765716 | 241 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 2773 | 37.3248 | -122.3849 | 2 SPANS LD SIDE OF 4293 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0011087 | OH | Sus | 44159232 | No | 2020 | JAN | Yes | Force Out | 1507596 | CSO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | OTHER | PRI DOWN LD SIDE CGC # ...7654 | 20200119 | 1153 | 766182 | 1612 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 20181 | 37.2472 | -122.2166 | LD SIDE CGC 315005227654 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0011195 | OH | Sus | 31486986 | No | 2020 | JAN | Yes | Open Circuit | 1507721 | CAW | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 8615 | 20200120 | 1204 | 766634 | 1951 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5097 | 37.4248 | -122.3133 | 2 BLUE JAY WAY & 100 LAUGHING COW RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0011369 | OH | Sus | 31486996 | No | 2020 | JAN | Yes | Line to Ground | 1507876 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 8549 | 20200210 | 1155 | 787534 | 75 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 2550 | 37.2628 | -122.2119 | Middleton Subdivision-Portola State Park | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0020039 | OH | Sus | 0 | yes | 2020 | FEB | Yes | Line to Ground | 1513978 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 7851 | 20200215 | 813 | 791648 | 663 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5304 | 37.2863 | -122.2277 | 4 SPANS LD SIDE OF 7851 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0022567 | OH | Sus | 44195011 | No | 2020 | FEB | Yes | Line to Ground | 1515597 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8884 | 20200217 | 2316 | 793053 | 936 | Distribution Circuit | Vegetation | Tree - fell into line | 344 | 58426 | 37.3895 | -122.2687 | 17001 SKYLINE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0022988 | OH | Sus | 31491493 | No | 2020 | FEB | Yes | Line to Ground | 1515852 | PW | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER | WIRE DOWN @ 137 SHELDON RD | 20200301 | 908 | 820606 | 648 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 4344 | 37.3124 | -122.2736 | 137 SHELDON RD- LA HONDA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0027486 | OH | Sus | 44226102 | No | 2020 | MAR | Yes | Line to Ground | 1518715 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | SAN CARLOS-1104 | 24181104 | RECLOSER | 36864 | 20200411 | 1802 | 893961 | 628 | Distribution Circuit | Vegetation | Tree - fell into line | 389 | 36721 | 37.48 | -122.26 | AVALO- JORGE / 650-333-4012: need crew to repair wire down | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0040603 | OH | Sus | 44292036 | No | 2020 | APR | Yes | Line to Ground | 1526692 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 5061 | 20200512 | 537 | 911817 | 842 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2526 | 37.2796 | -122.2116 | LD SIDE 5061 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0049421 | OH | Sus | 44321335 | yes | 2020 | MAY | Yes | Line to Ground | 1532110 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4211 | 20200526 | 1049 | 921539 | 576 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2304 | 37.2123 | -122.4051 | MTR# 314452826489 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on object | 20-0054031 | OH | Sus | 44331667 | yes | 2020 | MAY | Yes | Force Out | 1534621 | CSO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 3217 | 20200611 | 545 | 936485 | 599 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 9584 | 37.294 | -122.2409 | 3217 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0060097 | OH | Sus | 31505670 | No | 2020 | JUN | Yes | Line to Ground | 1538877 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | OTHER | WIRE DOWN 1 POLE S.O 8549 | 20200808 | 2238 | 987081 | 1104 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 57444 | 37.2627 | -122.2121 | 9000 PORTOLA STATE PARK RD- LA HONDA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0081302 | OH | Sus | 44415625 | No | 2020 | AUG | Yes | Line to Ground | 1552718 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE | 4149 | 20201013 | 857 | 1116358 | 446 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 892 | 37.4967 | -122.4298 | CLARK- DON / 650-867-3678: end of line co 4149 Frenchmans crk rd | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0107976 | OH | Sus | 31515937 | No | 2020 | OCT | Yes | Line to Ground | 1570377 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4737 | 20201218 | 637 | 1193192 | 509 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 10689 | 37.4021 | -122.3362 | 5/P/SO 4737 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0131062 | OH | Sus | 31522020 | No | 2020 | DEC | Yes | Line to Line | 1588421 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | JUMPER | OPEN TAPS | 20210105 | 1121 | 1204624 | 360 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 1800 | 37.2391 | -122.32 | FERN RD & REDWOOD AVE PASADERO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0005170 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1591014 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4431 | 20210120 | 747 | 1218334 | 738 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 22878 | 37.3857 | -122.2613 | 5 E/O 4431 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0011423 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1595076 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 10265 | 20210123 | 803 | 1221619 | 754 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2618 | 37.3845 | -122.2937 | 2150 BEAR GULCH | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0013268 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1596223 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1102 | 24101102 | FUSE | 5521 | 20211021 | 1246 | 1504750 | 584 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 584 | 37.5441 | -122.4994 | ELM & DRAKE | Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0134779 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1676514 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 7809 | 20211021 | 1138 | 1504444 | 487 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 3409 | 37.2688 | -122.2114 | 2/SPANS W/OF 7809- PORTOLA ST PK | Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0134469 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1676419 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | 623460 | 20211022 | 542 | 1505344 | 2317 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 23320 | 37.3638 | -122.32 | at CGC# 314706631899 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0134845 | OH | Sus | 0 | No | 2021 | OCT | Yes | Multi-Fault | 1676570 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1102 | 24101102 | FUSE | 8497 | 20211026 | 817 | 1520943 | 538 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3228 | 37.5334 | -122.4937 | LD SIDE OF 8497 | Strong Winds-Rain-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0137930 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Line | 1679178 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 1125 | 20220102 | 355 | 1592151 | 848 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 19484 | 37.2606 | -122.3245 | 210 LOWER DEARBORN PARK RD | Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0005174 | OH | Sus | 45105455 | No | 2022 | JAN | Yes | Line to Ground | 1700360 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1101 | 24101101 | FUSE | 10695 | 20220110 | 54 | 1599040 | 950 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 9402 | 37.4883 | -122.42 | DUMP AT END OF QUARRY RD- HMB | Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0007851 | OH | Sus | 31590304 | No | 2022 | JAN | Yes | Line to Ground | 1701793 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4737 | 20220202 | 731 | 1618868 | 364 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 7644 | 37.4021 | -122.3362 | NATIVE SON RD S/W OF STAR HILL RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0017431 | OH | Sus | 31591635 | No | 2022 | FEB | Yes | Line to Ground | 1706945 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | 6018 | 20220306 | 1943 | 1643597 | 404 | Distribution Circuit | Vegetation | Tree - fell into line | 1001 | 91609 | 37.3265 | -122.3877 | 3/P/NO 4299- 1380 STAGE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0030482 | OH | Sus | 31596760 | No | 2022 | MAR | Yes | Line to Ground | 1715025 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1104 | 24251104 | FUSE | 9173 | 20220309 | 1703 | 1645654 | 345 | Distribution Circuit | Vegetation | Tree - branch fell on line | 60 | 20700 | 37.4254 | -122.2786 | IFO 635 PATROL RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0031986 | OH | Sus | 31597183 | No | 2022 | MAR | Yes | Line to Ground | 1715976 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4279 | 20220419 | 848 | 1676320 | 724 | Distribution Circuit | Vegetation | Tree - fell into line | 93 | 43089 | 37.3178 | -122.3 | 7940 LA HONDA RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0051366 | OH | Sus | 31601211 | No | 2022 | APR | Yes | Line to Ground | 1729294 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 7851 | 20220524 | 1343 | 1709049 | 707 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3448 | 37.2872 | -122.2283 | 151 ALIPINE OAKS RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0065893 | OH | Sus | 31604448 | No | 2022 | MAY | Yes | Multi-Fault | 1739011 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1102 | 24101102 | OTHER | HOT WIRE DOWN 9 P/LS OF 13985 | 20220605 | 659 | 1719462 | 734 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 5008 | 37.5453 | -122.4965 | 9 POLES LOAD SIDE OF 13985 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0070303 | OH | Sus | 0 | No | 2022 | JUN | Yes | Line to Ground | 1741867 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | OTHER | WIRE DOWN & BROKEN POLE | 20220613 | 1745 | 1730592 | 683 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 37479 | 37.3741 | -122.2649 | 13994 LA HONDA RD- RWC | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0073857 | OH | Sus | 35355989 | No | 2022 | JUN | Yes | Open Circuit | 1744348 | PW | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4293 | 20220616 | 1246 | 1733147 | 323 | Distribution Circuit | Animal | Bird found | 13 | 4199 | 37.3251 | -122.3869 | FIVE POLES FROM CUT OUTS 4293 AT THE LINE AND BUCK | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0075194 | OH | Sus | 45345245 | No | 2022 | JUN | Yes | Line to Line | 1745282 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | H82 | 20220628 | 1139 | 1744458 | 491 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1947 | 436691 | 37.4177 | -122.4246 | CABRILLO HWY N/OF ANO NUEVO ST PK - 3 SPANS LS OF 1071 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0079519 | OH | Sus | 0 | No | 2022 | JUN | Yes | Line to Line | 1748678 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | JUMPER | A&B PHASE TREE WIRE DOWN | 20220920 | 1220 | 1817516 | 810 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 45162 | 37.2678 | -122.2111 | LD SIDE LR8982 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0112695 | OH | Sus | 31616453 | No | 2022 | SEP | Yes | Line to Ground | 1770489 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER | HOT WIRE DOWN 3 N/OF 4227 | 20221001 | 1231 | 1825706 | 394 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2066 | 174491 | 37.2161 | -122.3488 | 3 SPANS N/O SSD-4227 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0116929 | OH | Sus | 31617506 | No | 2022 | OCT | Yes | Line to Ground | 1773356 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | RECLOSER | 8884 | 20221122 | 1650 | 1868052 | 568 | Distribution Circuit | 3rd Party | Vehicle | 343 | 46098 | 37.3894 | -122.2686 | 1/4 MI S/OF SW 6333- WS - E/O 14865 SKYLINE BLVD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0133638 | OH | Sus | 35404659 | No | 2022 | NOV | Yes | Force Out | 1785218 | PW | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1102 | 24101102 | JUMPER | WIRE DOWN N/O R340 | 20221227 | 455 | 1898608 | 624 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 1911 | 37.5528 | -122.5088 | JONES- MICHAEL / 707-382-6904: One spin off Tap line which is one span north of R340 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0141569 | OH | Sus | 0 | No | 2022 | DEC | Yes | Open Circuit | 1793248 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | OTHER | 8982 | 20221227 | 759 | 1898682 | 1046 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 16976 | 37.2681 | -122.2112 | 100 YARD LD SIDE OF SAP #102351207 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0141585 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793265 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 4799 | 20221227 | 732 | 1898738 | 495 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2475 | 37.3941 | -122.2449 | LACY- CHRIS 510-435-9556 2185: 133 Home Rd- Woodside | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0141670 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793355 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | 29454 | 20230117 | 17 | 1959008 | 863 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 32794 | 37.4434 | -122.403 | NEAR 2165 HIGGINS CNYON RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0017444 | OH | Sus | 0 | No | 2023 | JAN | Yes | Multi-Fault | 1806112 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | OTHER | WIRE DOWN AT 11 RECREATION DR | 20230119 | 202 | 1961771 | 711 | Distribution Circuit | Vegetation | Tree - branch fell on line | 326 | 35344 | 37.3184 | -122.2679 | 11 RECREATION DR | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0018653 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1806717 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 43139 | 20230127 | 1133 | 1969891 | 1624 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3248 | 37.365 | -122.3086 | ROBERTS- RON / 209-986-6628: load side of 43139 end of line | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0022422 | OH | Sus | 31635761 | No | 2023 | JAN | Yes | Line to Ground | 1808699 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | RECLOSER | 8982 | 20230203 | 1226 | 1975895 | 305 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 17080 | 37.2681 | -122.2112 | 2 SPANS S/O LR 8982 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0024949 | OH | Sus | 31636256 | No | 2023 | FEB | Yes | Force Out | 1810340 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 4311 | 20230212 | 948 | 1982859 | 346 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 4844 | 37.305 | -122.268 | LD SIDE OF 4317 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0027915 | OH | Sus | 0 | No | 2023 | FEB | Yes | Force Out | 1812505 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | FUSE | 4279 | 20230310 | 254 | 2029965 | 1074 | Distribution Circuit | Vegetation | Tree - fell into line | 208 | 129342 | 37.3178 | -122.3 | 11 PSAN E/O 4279 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0042856 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1823619 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | TRIP-SAVER | 8601 | 20230310 | 809 | 2030396 | 347 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 14574 | 37.4387 | -122.3236 | 145 HENRICK IBSEN PARK RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0042937 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1823668 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 5637 | 20230310 | 812 | 2030404 | 623 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5607 | 37.3844 | -122.235 | 150 WAYSIDE RD- PV | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0043037 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1823708 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | FUSE | 10265 | 20230326 | 854 | 2067826 | 651 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1953 | 37.3845 | -122.2937 | 12 SPANS LD SIDE OF 1265 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0052693 | OH | Sus | 0 | No | 2023 | MAR | Yes | Force Out | 1830629 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 3 | WOODSIDE-1101 | 24251101 | JUMPER | 2 SPANS OF WIRE DOWN 1/P LOAD SIDE OF 4121 | 20230409 | 318 | 2083535 | 635 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 3175 | 37.3881 | -122.262 | 2 SPANS LOAD SIDE OF 4121 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0058844 | OH | Sus | 31641720 | No | 2023 | APR | Yes | Line to Ground | 1834294 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | OTHER | 1 PHASE, 1 SPAN DOWN | 20230515 | 1141 | 2113094 | 731 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 10131 | 37.2566 | -122.2154 | N/O 13331 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0071997 | OH | Sus | 31645498 | No | 2023 | MAY | Yes | Line to Ground | 1843373 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | EMERALD LAKE-0401 | 24080401 | OTHER | HOT WIRE DOWN @ 512 MAPLE WAY | 20230520 | 333 | 2117436 | 522 | Distribution Circuit | Vegetation | Tree - fell into line | 624 | 4979 | 37.4555 | -122.2765 | 512 Maple way Woodside | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0073785 | OH | Sus | 31645959 | No | 2023 | MAY | Yes | Open Circuit | 1844604 | CO | OH | No | Yes
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | FUSE | 7809 | 20230707 | 220 | 2155940 | 625 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4375 | 37.2688 | -122.2114 | 1680 PORTOLA STATE PARK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0089645 | OH | Sus | 0 | No | 2023 | JUL | Yes | Line to Line | 1855622 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | EMERALD LAKE SUB | 2408 | OCB | 401/2 | 20230730 | 1009 | 2177629 | 620 | Distribution Circuit | Vegetation | Tree - fell into line | 624 | 48566 | 37.4615 | -122.2773 | 10 POLES N/O FUSE 5163 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0098443 | OH | Sus | 31657501 | No | 2023 | JUL | Yes | Line to Ground | 1861589 | CO | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | HALF MOON BAY-1103 | 24101103 | RECLOSER | 880484 | 20231016 | 1422 | 2244651 | 34 | Distribution Circuit | Vegetation | Tree - fell into line | 1917 | 65178 | 37.4177 | -122.4246 | W/O 5585 | Overcast-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0128824 | OH | Sus | 0 | No | 2023 | OCT | Yes | Line to Line | 1882569 | CAW | OH | No | No
PENINSULA | FIELD OPS CENTRAL | Tier 2 | MENLO-1103 | 24131103 | RECLOSER | 8512 | 20231118 | 2129 | 2273326 | 1143 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 83918 | 37.2891 | -122.2132 | JONES- MICHAEL / 707-382-6904: 13940 Alpine Rd. | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0141022 | OH | Sus | 46061762 | No | 2023 | NOV | Yes | Line to Ground | 1891691 | CO | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | DOBBINS-1101 | 153741101 | FUSE | 5261 | 20130202 | 1200 | 737716 | 428 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 37 | 15836 | 39.3619 | -121.2237 | 2 SPANS SOUTH OF 5261 | Overcast-32 - 90 F | Conductor, Overhead | On Ground | 13-0007711 | OH | Sus | 30974976 | No | 2013 | FEB | Yes | Line to Ground | 99302348 | CO | OH | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | PUTAH CREEK-1102 | 63681102 | RECLOSER | A1W1 | 20130223 | 1301 | 746665 | 967 | Distribution Circuit | Vegetation | Tree - fell into line | 103 | 12187 | 38.4807 | -122.0272 | 8325 QUIAL CANYON WINTERS | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0012060 | OH | Sus | 30979165 | No | 2013 | FEB | Yes | Line to Ground | 99299541 | CO | OH | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 40133 | 20130316 | 2049 | 757836 | 336 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2411 | 31519 | 39.3193 | -121.3991 | at MTR # 1005534341/ 12697 MELROSE LN | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0017166 | OH | Sus | 41869542 | No | 2013 | MAR | Yes | Line to Ground | 99293653 | CO | OH | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | VACA DIXON-1105 | 63591105 | FUSE | 11365 | 20130629 | 1248 | 820410 | 248 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 11656 | 38.4176 | -121.9994 | 8 SPANS LOADSIDE OF 11365 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0043703 | OH | Sus | 0 | yes | 2013 | JUN | Yes |  | 99277122 | CO | OH | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | VACA DIXON-1105 | 63591105 | FUSE | 11365 | 20130713 | 2124 | 831012 | 1246 | Distribution Circuit | Vegetation | Tree - branch fell on line | 47 | 8162 | 38.4176 | -121.9994 | HARD TAP ACROSS FROM 4005 CANTELOW RD | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0047234 | OH | Sus | 31008483 | No | 2013 | JUL | Yes |  | 99274390 | PW | OH | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | VACAVILLE-1111 | 63601111 | RECLOSER | 13652 | 20140208 | 503 | 962522 | 598 | Distribution Circuit | Equipment Failure/Involved | Other | 131 | 21134 | 38.3802 | -121.9988 | FOX- ALBERT: 6813 Gibson Canyon | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0009821 | OH | Sus | 42073384 | yes | 2014 | FEB | Yes |  | 99240796 | CO | OH | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 9823 | 20140226 | 2145 | 973283 | 427 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5978 | 39.3522 | -121.2379 | 13233 DIXON HILL RD | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 14-0013675 | OH | Sus | 31059387 | yes | 2014 | FEB | Yes | Line to Ground | 99238076 | CO | OH | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 15797 | 20140430 | 2353 | 1008419 | 430 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 12470 | 39.3239 | -121.3573 | 7189 MARYSVILLE RD. MTR #1005450863 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0028470 | OH | Sus | 42115258 | yes | 2014 | APR | Yes | Line to Line | 99227816 | CO | OH | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | OTHER |  | 20140516 | 1926 | 1019738 | 255 | Distribution Circuit | Equipment Failure/Involved | Other | 995 | 79511 | 39.3236 | -121.3864 | 11961 LOMA RICA RD | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0032512 | OH | Sus | 42125603 | No | 2014 | MAY | Yes | Line to Ground | 99225271 | CO | OH | No
SACRAMENTO | FIELD OPS NORTH | Tier 3 | DOBBINS-1101 | 153741101 | FUSE | 1271 | 20140603 | 641 | 1027785 | 589 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 8681 | 39.3811 | -121.1441 | McBRIDE M / 1259/ 530-362-2433: mv | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0035760 | OH | Sus | 42133113 | No | 2014 | JUN | Yes | Line to Line | 99222895 | CO | OH | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | DOBBINS-1101 | 153741101 | RECLOSER | 1808 | 20140709 | 1722 | 1047057 | 798 | Distribution Circuit | 3rd Party | Vehicle | 167 | 81506 | 39.3741 | -121.2339 | 2 P W/O 39173 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0043560 | OH | Sus | 31087748 | No | 2014 | JUL | Yes | Line to Ground | 99217336 | PW | OH | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | SWITCH | 299913 | 20140730 | 1042 | 1057908 | 254 | Distribution Circuit | Equipment Failure/Involved | Other | 996 | 201761 | 39.3252 | -121.386 | 12698 SCOTT GRANT RD | Partly cloudy-Above 90 F | Conductor, Overhead | Broken, wire on ground | 14-0047985 | OH | Sus | 42161153 | yes | 2014 | JUL | Yes | Line to Line | 99214240 | CO | OH | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | JAMESON-1105 | 63801105 | FUSE | 11833 | 20141009 | 1318 | 1095149 | 239 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 239 | 38.3109 | -122.1292 | 1 SP LD SIDE OF C/OUT 11833 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0062629 | OH | Sus | 0 | No | 2014 | OCT | Yes | Line to Ground | 99204218 | CO | OH | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | NARROWS-2102 | 153132102 | OCB | OCB | 20141111 | 1126 | 1111545 | 1048 | Distribution Circuit | Equipment Failure/Involved | Other | 3910 | 636904 | 39.2352 | -121.2692 | 2 SPANS EAST OF 5251 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0069411 | OH | Sus | 0 | No | 2014 | NOV | Yes | Line to Ground | 99199665 | PW | OH | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | BROWNS VALLEY-1101 | 152921101 | RECLOSER | 36622 | 20141202 | 1347 | 1121127 | 396 | Distribution Circuit | Equipment Failure/Involved | Other | 20 | 6265 | 39.2251 | -121.4225 | 6 SPANS LD SIDE OF SBCO 7381 | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0073000 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99197134 | CO | OH | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | SMARTVILLE-1101 | 153791101 | FUSE | 1225 | 20150119 | 128 | 1165534 | 527 | Distribution Circuit | 3rd Party | Vehicle | 162 | 77074 | 39.2075 | -121.303 | 6 P/W/O 17317 SBCO | Fog-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0005506 | OH | Sus | 31129075 | No | 2015 | JAN | Yes | Line to Ground | 99187607 | PW | OH | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | DOBBINS-1101 | 153741101 | FUSE | 88093 | 20150223 | 809 | 1194438 | 536 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2144 | 39.3815 | -121.2225 | 3 EAST & 2 NORTH OF 88093 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0015038 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99180828 | CO | OH | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | DOBBINS-1101 | 153741101 | FUSE | 9813 | 20150223 | 746 | 1194415 | 531 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 11151 | 39.3676 | -121.2143 | LD SIDE OF 9813 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0015097 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99180808 | CO | OH | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | VACAVILLE-1108 | 63601108 | FUSE | 9897 | 20150620 | 1800 | 1253914 | 421 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 2526 | 38.3625 | -122.0234 | PAGAN-VICTOR/ 707-689-3441: FUSES 9897 TO 1 SPAN IN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0042304 | OH | Sus | 42412626 | No | 2015 | JUN | Yes | Line to Line | 99162750 | CO | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | RECLOSER | 7446 | 20150924 | 1356 | 1311414 | 397 | Distribution Circuit | 3rd Party | Vehicle | 525 | 51917 | 39.3517 | -121.3276 | 9692 RICES TEXAS HILL | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 15-0063159 | OH | Sus | 0 | No | 2015 | SEP | Yes | Three Phase Fault | 1156592 | PW | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | BROWNS VALLEY-1101 | 152921101 | FUSE | 18167 | 20151004 | 132 | 1316457 | 418 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 4021 | 39.229 | -121.386 | SAMANIEGO-S/626/530-906-3122: 6275 sandstone | Clear-32-90 F | Conductor, Overhead | On Ground | 15-0067743 | OH | Sus | 0 | yes | 2015 | OCT | Yes | Line to Ground | 1160512 | CO | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | SMARTVILLE-1101 | 153791101 | FUSE | 1225 | 20160117 | 1137 | 1385452 | 546 | Distribution Circuit | 3rd Party | Vehicle | 164 | 29241 | 39.2077 | -121.3031 | 2 POLES W/O 17119 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0005890 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1180861 | PW | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | NARROWS-2101 | 153132101 | FUSE | 15793 | 20160310 | 1806 | 1426806 | 478 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 7648 | 39.2967 | -121.3759 | BARKER-BILL/1256/530-362-2077: 1 SPAN E/O FC/O 15793 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020086 | OH | Sus | 31224272 | yes | 2016 | MAR | Yes | Line to Line | 1191602 | CO | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 39975 | 20160313 | 353 | 1429957 | 828 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3312 | 39.2905 | -121.3962 | 1 P LD SIDE OF 39975 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0020903 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1192288 | PW | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 7925 | 20160506 | 1358 | 1465982 | 382 | Distribution Circuit | 3rd Party | Vehicle | 42 | 14634 | 39.3641 | -121.3232 | 9237 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0034548 | OH | Sus | 0 | yes | 2016 | MAY | Yes | Line to Ground | 1202389 | PW | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | JAMESON-1103 | 63801103 | FUSE | 2577 | 20160521 | 1636 | s1204680 | 642 | Distribution Circuit | 3rd Party | Vehicle | 44 | 13054 | 38.2527 | -122.1763 | 2SP W/OF 94587 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0037626 | OH | Sus | 0 | No | 2016 | MAY | Yes | Line to Ground | 1204680 | PW | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | DOBBINS-1101 | 153741101 | FUSE | 5261 | 20160710 | 2108 | 1507878 | 492 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 5850 | 39.3621 | -121.2237 | WILKINS-ARMANDO/1589/913-5057: 13769 YUBA NEVADA RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0048918 | OH | Sus | 0 | No | 2016 | JUL | Yes | Line to Ground | 1213159 | PW | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | NARROWS-2102 | 153132102 | OCB | 2102/2 | 20170206 | 2142 | 1677158 | 1225 | Distribution Circuit | Vegetation | Tree - fell into line | 3381 | 862627 | 39.2354 | -121.2691 | SW 785 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018009 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1255861 | CO | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | VACA DIXON-1105 | 63591105 | FUSE | 11365 | 20170330 | 921 | 1739105 | 807 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 38736 | 38.4177 | -121.9996 | 9 POLES LD SIDE OF 11365 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0035008 | OH | Sus | 42980124 | yes | 2017 | MAR | Yes | Line to Ground | 1269737 | CO | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | VACAVILLE-1104 | 63601104 | FUSE | 771 | 20170423 | 2156 | 1765605 | 1207 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 22933 | 38.335 | -122.0303 | 2 W/O 771 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0042276 | OH | Sus | 0 | No | 2017 | APR | Yes | Line to Ground | 1275435 | CO | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | SMARTVILLE-1101 | 153791101 | FUSE | 1225 | 20170527 | 1946 | 1792083 | 591 | Distribution Circuit | 3rd Party | Vehicle | 165 | 88233 | 39.1965 | -121.3042 | 10 SPANS W/O 17317 | Clear-32-90 F | Pole-Wood | Broken, wire on object | 17-0051175 | OH | Sus | 31328480 | No | 2017 | MAY | Yes | Line to Ground | 1281876 | PW | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | SMARTVILLE-1101 | 153791101 | FUSE | 1225 | 20180123 | 847 | 12401 | 344 | Distribution Circuit | 3rd Party | Vehicle | 166 | 18303 | 39.2077 | -121.3031 | 2 POLES W/O FUCO 17119 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0008101 | OH | Sus | 0 | No | 2018 | JAN | Yes | Three Phase Fault | 1326071 | CO | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | VACAVILLE-1108 | 63601108 | FUSE | 76285 | 20180218 | 1924 | 26891 | 1136 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 10588 | 38.4228 | -122.0456 | THOMAS- ROBERT: ro 3490 cantelow rd vville | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0015285 | OH | Sus | 31379781 | yes | 2018 | FEB | Yes | Line to Line | 1330723 | PW | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | BROWNS VALLEY-1101 | 152921101 | RECLOSER | 36622 | 20180318 | 827 | 47233 | 346 | Distribution Circuit | 3rd Party | Aircraft | 16 | 5191 | 39.2251 | -121.4231 | RIVER CROSSING AT YUBA RIVER | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023875 | OH | Sus | 31384726 | No | 2018 | MAR | Yes | Line to Line | 1336677 | CO | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | DOBBINS-1101 | 153741101 | FUSE | 15881 | 20180719 | 1755 | 135846 | 605 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5445 | 39.3184 | -121.2415 | BARRIE-JESSE/1258/530-863-8433: 12206 RICES CROSSING RD- OREGON HOUSE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0061638 | OH | Sus | 43411320 | yes | 2018 | JUL | Yes | Three Phase Fault | 1365149 | CO | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | PEABODY-2106 | 63642106 | FUSE | 47447 | 20180810 | 1911 | 153259 | 1219 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 3 | 282 | 38.3052 | -121.9714 | MTR# 1003806726 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0068879 | OH | Sus | 0 | No | 2018 | AUG | Yes | Force Out | 1370303 | PW | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | DOBBINS-1101 | 153741101 | FUSE | 15899 | 20190430 | 852 | 370775 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3253 | 39.366 | -121.2474 | 9823 TEXAS HILL RD. | Overcast-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0047461 | OH | Sus | 0 | No | 2019 | APR | Yes | Line to Ground | 1433681 | CAW | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | VACAVILLE-1108 | 63601108 | OTHER | WIRE DOWN TWD MTR 1010193830 | 20190430 | 103 | 370603 | 746 | Distribution Circuit | Equipment Failure/Involved | Overhead | 392 | 13681 | 38.3586 | -122.0247 | SINGLE PHASE TAP P N/O 8021 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0047282 | OH | Sus | 31437127 | No | 2019 | APR | Yes | Open Circuit | 1433533 | CO | OH | No | Yes
SACRAMENTO | FIELD OPS NORTH | Tier 3 | DOBBINS-1101 | 153741101 | FUSE | 5203 | 20190605 | 1400 | 398780 | 382 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 9932 | 39.3912 | -121.2024 | KRZYMINSKI- WOODY: 14976 fountain house | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0063302 | OH | Sus | 43825018 | yes | 2019 | JUN | Yes | Line to Ground | 1445734 | CO | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | VACAVILLE-1111 | 63601111 | SWITCH | 17427 | 20190611 | 1221 | 405684 | 14 | Distribution Circuit | Company Initiated | Return Circuit Normal | 224 | 3136 | 38.3949 | -122.0001 | 40092 | Clear-Above 90 | Pole-Wood | Broken, wire on ground | 19-0065327 | OH | Sus | 0 | yes | 2019 | JUN | Yes | Line to Ground | 1448037 | PW | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 9237 | 20190816 | 957 | 516475 | 458 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4580 | 39.3684 | -121.3212 | WIRE DOWN 3 SPAN LD SIDE OF 9237 at LINE & BUCK | Clear-Above 90 | Crossarm, Wood | Broken, wire on ground | 19-0088805 | OH | Sus | 31462706 | yes | 2019 | AUG | Yes | Line to Line | 1463658 | CAW | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | SMARTVILLE-1101 | 153791101 | FUSE | 1225 | 20190916 | 1347 | 585345 | 758 | Distribution Circuit | 3rd Party | Vehicle | 171 | 18078 | 39.2077 | -121.3031 | 2 SPAN W/O 17119 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0099774 | OH | Sus | 0 | yes | 2019 | SEP | Yes | Line to Line | 1470446 | PW | OH | No | Yes
SACRAMENTO | FIELD OPS NORTH | Tier 2 | VACAVILLE-1111 | 63601111 | RECLOSER | 12342 | 20191021 | 802 | 675314 | 999 | Distribution Circuit | 3rd Party | Vehicle | 944 | 120913 | 38.3689 | -121.9938 | 4 POLES E/OF SW 7101 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0113907 | OH | Sus | 0 | No | 2019 | OCT | Yes | Line to Line | 1481414 | PW | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | PUTAH CREEK-1102 | 63681102 | RECLOSER | 67858 | 20191030 | 1301 | 695318 | 311 | Distribution Circuit | Vegetation | Tree - branch fell on line | 104 | 32344 | 38.4806 | -122.0272 | 1 SPAN LD SIDE OF B52 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0118985 | OH | Sus | 0 | yes | 2019 | OCT | Yes | Line to Ground | 1488029 | CO | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | VACAVILLE-1104 | 63601104 | RECLOSER | 6542 | 20200127 | 1407 | 771035 | 477 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1514 | 105749 | 38.3422 | -122.0077 | NELSON RD 2 P/W/O REGS R1022 | Clear-32-90 F | Insulator | Broken, wire on ground | 20-0014158 | OH | Sus | 44167021 | No | 2020 | JAN | Yes | Line to Ground | 1509581 | INS | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | PUTAH CREEK-1102 | 63681102 | FUSE | 11461 | 20200425 | 1237 | 901411 | 631 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 25240 | 38.4665 | -122.0497 | 8062 PLESANT VALLEY RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0044552 | OH | Sus | 0 | No | 2020 | APR | Yes | Three Phase Fault | 1529032 | CO | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | VACAVILLE-1108 | 63601108 | FUSE | 1475 | 20200530 | 717 | 926118 | 1033 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 6198 | 38.4093 | -122.0652 | 1 SPAN LD SIDE OF 1475 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0055946 | OH | Sus | 0 | yes | 2020 | MAY | Yes | Line to Ground | 1535822 | CO | OH | No | Yes
SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 39977 | 20200619 | 910 | 942513 | 357 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 714 | 39.2916 | -121.3988 | MIDSPAN FROM FU 39977 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0063011 | OH | Sus | 0 | No | 2020 | JUN | Yes | Line to Line | 1540986 | CO | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | PUTAH CREEK-1102 | 63681102 | OTHER | HOT WIRE DOWN @ CGC 219913029178 | 20200711 | 2157 | 962629 | 876 | Distribution Circuit | Equipment Failure/Involved | Overhead | 104 | 13367 | 38.4676 | -122.0314 | at CGC 219913029178 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0070907 | OH | Sus | 44388086 | yes | 2020 | JUL | Yes | Line to Ground | 1545969 | CO | OH | No | Yes
SACRAMENTO | FIELD OPS NORTH | Tier 2 | VACAVILLE-1104 | 63601104 | RECLOSER | 6542 | 20201120 | 49 | 1149850 | 873 | Distribution Circuit | 3rd Party | Vehicle | 156 | 40680 | 38.3423 | -122.0077 | 2 POLE E/OF 58263 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 20-0123134 | OH | Sus | 0 | No | 2020 | NOV | Yes | Three Phase Fault | 1581414 | PW | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 3 | DOBBINS-1101 | 153741101 | FUSE | 6187 | 20210309 | 745 | 1274984 | 359 | Distribution Circuit | 3rd Party | Vehicle | 7 | 2513 | 39.3812 | -121.145 | LD SIDE OF FU 6187 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0033787 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1610626 | PW | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | OTHER | WIRE DOWN BTWN 18645 & 15779 | 20210731 | 604 | 1424399 | 552 | Distribution Circuit | Equipment Failure/Involved | Overhead | 618 | 339372 | 39.3181 | -121.4014 | MARINO-TONY/6134/530-682-6418: 11596 LOMA RICA RD LOMA RICA | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0097860 | OH | Sus | 31547739 | No | 2021 | JUL | Yes | Line to Ground | 1653451 | CO | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | DOBBINS-1101 | 153741101 | RECLOSER | 1808 | 20211109 | 450 | 1538333 | 904 | Distribution Circuit | Vegetation | Tree - fell into line | 169 | 85060 | 39.3743 | -121.2341 | FINLEY- ALAN: c/o frenchtown & vavassuer rd - dobbins | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0143684 | OH | Sus | 0 | No | 2021 | NOV | Yes | Line to Line | 1682922 | CO | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | JAMESON-1102 | 63801102 | FUSE | 11633 | 20211130 | 1223 | 1556471 | 367 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 84 | 30828 | 38.2628 | -122.1643 | 1/S SOURCE SIDE TO CGC#219524321866 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0153095 | OH | Sus | 0 | No | 2021 | NOV | Yes | Line to Ground | 1690007 | CSO | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | FUSE | 5211 | 20220212 | 2131 | 1626361 | 754 | Distribution Circuit | 3rd Party | Vehicle | 35 | 20006 | 39.3638 | -121.3237 | 2/P/N/OF CGC#221879862137 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0021810 | OH | Sus | 0 | No | 2022 | FEB | Yes | Line to Ground | 1709625 | PW | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | DOBBINS-1101 | 153741101 | FUSE | 15901 | 20220902 | 1308 | 1797715 | 575 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 12075 | 39.3682 | -121.2457 | 3 SPANS LD SIDE OF 15901 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0105247 | OH | Sus | 45438734 | No | 2022 | SEP | Yes | Line to Ground | 1765326 | CO | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | DOBBINS-1101 | 153741101 | RECLOSER | 5202 | 20221012 | 1202 | 1835791 | 443 | Distribution Circuit | 3rd Party | Vehicle | 208 | 58809 | 39.3398 | -121.1945 | 12350 REGENT WAY | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0120639 | OH | Sus | 0 | No | 2022 | OCT | Yes | Line to Ground | 1775932 | PW | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | DOBBINS-1101 | 153741101 | FUSE | 9815 | 20230310 | 105 | 2029840 | 885 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3540 | 39.3648 | -121.2187 | 3 S/E OF 9815 | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0042869 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1823630 | CO | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | BANGOR-1101 | 103191101 | RECLOSER | 7446 | 20230328 | 834 | 2069735 | 580 | Distribution Circuit | Vegetation | Tree - fell into line | 532 | 69484 | 39.3516 | -121.3276 | HOWARD-JIMMY/530-712-7998: Yuba ranch way | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 23-0053296 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1831017 | PW | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | DOBBINS-1101 | 153741101 | FUSE | 15901 | 20230328 | 904 | 2069669 | 508 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 10668 | 39.3682 | -121.2457 | MTR # 1005656291 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 23-0053375 | OH | Sus | 31640507 | No | 2023 | MAR | Yes | Line to Ground | 1831075 | PW | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | NARROWS-2101 | 153132101 | RECLOSER | 1202 | 20230725 | 1608 | 2173730 | 696 | Distribution Circuit | 3rd Party | Vehicle | 501 | 127510 | 39.2105 | -121.3109 | FINLEY- ALAN 530-434-3718: Hwy 20 just e/o Stacey Anne rd | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 23-0096713 | OH | Sus | 0 | No | 2023 | JUL | Yes | Line to Line | 1860429 | CO | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | SMARTVILLE-1101 | 153791101 | OCB | 1101/2 | 20231211 | 1753 | 2289540 | 47 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1095 | 18735 | 39.2087 | -121.3026 | 5 SPANS E/O 467375 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0052792 | OH | Sus | 35314690 | No | 2023 | DEC | Yes | Line to Line | 1896936 | CO | OH | No | No
SACRAMENTO | FIELD OPS NORTH | Tier 2 | BROWNS VALLEY-1101 | 152921101 | FUSE | 6291 | 20231213 | 917 | 2290746 | 286 | Distribution Circuit | Equipment Failure/Involved | Overhead | 15 | 1269 | 39.2363 | -121.41 | at MTR# 1009123298 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0147220 | OH | Sus | 46089868 | No | 2023 | DEC | Yes | Line to Ground | 1897482 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2105 | 83242105 | RECLOSER | XR070 | 20130313 | 706 | 756054 | 439 | Distribution Circuit | Equipment Failure/Involved | Other | 165 | 46841 | 37.0426 | -121.6544 | 1 SPAN SOUTH OF 23073 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0016133 | OH | Sus | 41866656 | No | 2013 | MAR | Yes | Line to Ground | 99296706 | CO | OH | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2111 | 83242111 | RECLOSER | XR186 | 20130410 | 634 | 772115 | 425 | Distribution Circuit | Equipment Failure/Involved | Other | 417 | 27564 | 37.1455 | -121.6707 | END OF PALM AVE MORGAN HILL | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0023212 | OH | Sus | 41880513 | No | 2013 | APR | Yes | Line to Ground | 99291405 | CO | OH | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | PIERCY-2110 | 83912110 | FUSE | 43411 | 20130627 | 2111 | 818929 | 851 | Distribution Circuit | Vegetation | Tree - bark fell into line | 694 | 68534 | 37.2487 | -121.6841 | SAN FILIPE & METCALF RD | Clear-Above 90 F | Conductor, Overhead | Broken, wire on ground | 13-0043281 | OH | Sus | 31005827 | yes | 2013 | JUN | Yes | Line to Ground | 99277452 | CO | OH | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | PIERCY-2110 | 83912110 | FUSE | 43411 | 20130707 | 1622 | 827218 | 812 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 12992 | 37.2487 | -121.6841 | LD SIDE OF LCO 43411 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0045629 | OH | Sus | 31007192 | No | 2013 | JUL | Yes | Line to Ground | 99275426 | CO | OH | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2111 | 83242111 | FUSE | 3761 | 20130901 | 1805 | 859143 | 1155 | Distribution Circuit | 3rd Party | Vehicle | 125 | 14295 | 37.1084 | -121.7321 | 4980 CROY RD | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0059072 | OH | Sus | 31018550 | No | 2013 | SEP | Yes | Line to Ground | 99266117 | PW | OH | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MILPITAS-1109 | 82831109 | RECLOSER | XR082 | 20130929 | 1057 | 875126 | 489 | Distribution Circuit | Animal | Squirrel | 212 | 103668 | 37.4483 | -121.846 | CALAVERAS 4 SPANS W/O WELLER | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0065629 | OH | Sus | 41965605 | No | 2013 | SEP | Yes | Line to Ground | 99261178 | CO | OH | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MILPITAS-1109 | 82831109 | RECLOSER | XR082 | 20140313 | 1940 | 984305 | 445 | Distribution Circuit | Equipment Failure/Involved | Other | 212 | 72569 | 37.4483 | -121.846 | FELTER & MARSH | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0018019 | OH | Sus | 42092179 | No | 2014 | MAR | Yes | Line to Ground | 99235008 | CO | OH | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | SWIFT-2110 | 83392110 | FUSE | 15553 | 20140513 | 1731 | 1014799 | 169 | Distribution Circuit | Equipment Failure/Involved | Other | 17 | 2873 | 37.367 | -121.4849 | 4500 SA ANTONIO VALLEY | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0031541 | OH | Sus | 0 | yes | 2014 | MAY | Yes | None | 99225893 | CO | OH | No
SAN JOSE | FIELD OPS SOUTH | Tier 3 | MORGAN HILL-2111 | 83242111 | FUSE | 3695 | 20140914 | 1629 | 1081233 | 1261 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 13021 | 37.103 | -121.7252 | 1 SPAN S/E OF 3695 17410 UVAS | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0056885 | OH | Sus | 0 | No | 2014 | SEP | Yes | Line to Ground | 99207981 | CO | OH | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MILPITAS-1109 | 82831109 | FUSE | 25457 | 20150101 | 1522 | 1158024 | 373 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1492 | 37.4006 | -121.7642 | END OF CUST OWNED TAP LINE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0002124 | OH | Sus | 0 | No | 2015 | JAN | Yes | Line to Ground | 99189600 | CO | OH | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MILPITAS-1109 | 82831109 | RECLOSER | XR082 | 20150301 | 2027 | 1197865 | 498 | Distribution Circuit | 3rd Party | Vehicle | 211 | 83646 | 37.4483 | -121.846 | 316096134808 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0016520 | OH | Sus | 31137948 | No | 2015 | MAR | Yes | Line to Ground | 99179854 | CO | OH | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MILPITAS-1109 | 82831109 | FUSE | 14255 | 20150519 | 1753 | 1237124 | 1087 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1087 | 37.4777 | -121.8554 | S/OF MONUMENT PEAK W/OF LCO 14255 1 SPAN FROM EOL | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0035289 | OH | Sus | 42391899 | No | 2015 | MAY | Yes | Line to Ground | 99167777 | CO | OH | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2111 | 83242111 | RECLOSER | XR186 | 20150816 | 1248 | 1289149 | 782 | Distribution Circuit | 3rd Party | Vehicle | 395 | 26855 | 37.1456 | -121.6707 | HALE & PALM- MORGAN HILL | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0055309 | OH | Sus | 0 | yes | 2015 | AUG | Yes | Line to Line | 1150928 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 3 | HICKS-2101 | 83432101 | FUSE | 6813 | 20150830 | 1626 | 1297310 | 6909 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 23977 | 37.1564 | -121.8444 | Guillen/4644: EOL ALAMITOS RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0058275 | OH | Sus | 31180421 | No | 2015 | AUG | Yes | Line to Ground | 1152985 | PW | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MILPITAS-1109 | 82831109 | FUSE | 12465 | 20151222 | 710 | 1368931 | 420 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 5204 | 37.4313 | -121.8076 | 5555 SWEIGERT | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086693 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1176691 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | PIERCY-2110 | 83912110 | FUSE | 96883 | 20151222 | 1407 | 1369685 | 1588 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 19056 | 37.224 | -121.6586 | E/S SAN FELIPE RD E/OF METCALF RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086832 | OH | Sus | 31208369 | yes | 2015 | DEC | Yes | Line to Line | 1176864 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 3 | MORGAN HILL-2111 | 83242111 | FUSE | 4461 | 20160105 | 2123 | 1377888 | 514 | Distribution Circuit | Vegetation | Tree - branch fell on line | 63 | 32382 | 37.0838 | -121.7754 | Johnson/1055: SPAN AT FUSE 40771- CROY RD. | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003243 | OH | Sus | 31210740 | yes | 2016 | JAN | Yes | Line to Ground | 1178857 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 3 | MORGAN HILL-2111 | 83242111 | FUSE | 4463 | 20160218 | 1311 | 1408389 | 734 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 5138 | 37.0835 | -121.7684 | CROY RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013861 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186859 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2105 | 83242105 | FUSE | 3157 | 20160307 | 1015 | 1423691 | 317 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 6340 | 37.0609 | -121.6651 | Moyano/3707: tree fell on primary and burnt it down in park thousand trails | Overcast-Rain-32-90 F | Conductor, Overhead | On Ground | 16-0018867 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190669 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2111 | 83242111 | RECLOSER | XR398 | 20160310 | 612 | 1426239 | 325 | Distribution Circuit | Equipment Failure/Involved | Overhead | 392 | 32900 | 37.1263 | -121.7285 | Moyano/3707: on mkean rd 10 p s/o sw 10131 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | On Ground | 16-0019830 | OH | Sus | 42654564 | yes | 2016 | MAR | Yes | Line to Ground | 1191457 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2111 | 83242111 | FUSE | 15917 | 20160608 | 1733 | 1485488 | 166 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 664 | 37.1826 | -121.7605 | EOL | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0042029 | OH | Sus | 0 | No | 2016 | JUN | Yes | Three Phase Fault | 1208048 | PW | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2105 | 83242105 | FUSE | 28315 | 20160813 | 605 | 1525674 | 728 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 87 | 40024 | 37.0597 | -121.663 | BARGAS/1494: 13695 uvas rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0057070 | OH | Sus | 0 | No | 2016 | AUG | Yes | Line to Line | 1218663 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 3 | MORGAN HILL-2111 | 83242111 | FUSE | 14925 | 20160813 | 1248 | 1525817 | 616 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 5544 | 37.0824 | -121.7852 | BARGAS/1494: 3 spans load side of c/o's 14925 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0057106 | OH | Sus | 31263068 | No | 2016 | AUG | Yes | Line to Ground | 1218716 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | SWIFT-2110 | 83392110 | FUSE | 15525 | 20160910 | 1549 | 1539348 | 937 | Distribution Circuit | Vegetation | Tree - fell into line | 183 | 76251 | 37.3353 | -121.7714 | 2418 MOUNT PLEASANT ROAD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0063714 | OH | Sus | 31270731 | No | 2016 | SEP | Yes | Line to Ground | 1223110 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 3 | MORGAN HILL-2111 | 83242111 | FUSE | 2153 | 20161015 | 1702 | 1561578 | 1023 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 10852 | 37.0885 | -121.7564 | BARGAS/1494: 15 poles load side fuses 2153 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072615 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1229658 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2111 | 83242111 | FUSE | 3171 | 20161031 | 508 | 1573546 | 1230 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 18720 | 37.1294 | -121.6831 | 1160 LLAGAS RD | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 16-0076885 | OH | Sus | 0 | No | 2016 | OCT | Yes | Line to Ground | 1232991 | PW | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | SWIFT-2110 | 83392110 | RECLOSER | XR254 | 20161206 | 651 | 1595208 | 404 | Distribution Circuit | Animal | Bird found | 193 | 77972 | 37.334 | -121.7559 | 18405 MT HAMILTON RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084033 | OH | Sus | 42891271 | No | 2016 | DEC | Yes | Line to Ground | 1238631 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2111 | 83242111 | FUSE | 3761 | 20170328 | 1247 | 1737739 | 511 | Distribution Circuit | Vegetation | Tree - fell into line | 123 | 41073 | 37.1085 | -121.7322 | W/O 4461 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0034506 | OH | Sus | 42978865 | yes | 2017 | MAR | Yes | Line to Ground | 1269304 | CSO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 3 | MORGAN HILL-2111 | 83242111 | FUSE | 3695 | 20170331 | 1348 | 1741439 | 632 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 25976 | 37.103 | -121.7251 | SOUTH OF 28303 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0035637 | OH | Sus | 31316106 | yes | 2017 | MAR | Yes | Line to Line | 1270192 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MILPITAS-2112 | 82832112 | FUSE | 28429 | 20170418 | 836 | 1760030 | 834 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 17514 | 37.414 | -121.78 | Johnson/1055: 4974 SIERRA RD. | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0041149 | OH | Sus | 42997382 | yes | 2017 | APR | Yes | Line to Ground | 1274516 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2105 | 83242105 | RECLOSER | XR564 | 20170808 | 1119 | 1848507 | 411 | Distribution Circuit | Company Initiated | Personnel- company | 348 | 34192 | 37.0455 | -121.6522 | BARGAS/-GREG/1494: K965 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0068774 | OH | Sus | 0 | No | 2017 | AUG | Yes | Line to Ground | 1294955 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2110 | 83242110 | FUSE | 26057 | 20170902 | 231 | 1865940 | 789 | Distribution Circuit | 3rd Party | Vehicle | 65 | 51285 | 37.0875 | -121.6269 | COOLIDGE 200' N/O STEVENS CT | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0075073 | OH | Sus | 31348896 | yes | 2017 | SEP | Yes | Line to Ground | 1299373 | PW | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2111 | 83242111 | RECLOSER | XR186 | 20171122 | 1202 | 1928026 | 518 | Distribution Circuit | 3rd Party | Vehicle | 395 | 46285 | 37.1456 | -121.6707 | 2/P/E/OF HALE AVE ON LIVE OAKS AVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0097124 | OH | Sus | 43220643 | No | 2017 | NOV | Yes | Line to Ground | 1315476 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2111 | 83242111 | RECLOSER | XR398 | 20171124 | 1543 | 1928737 | 475 | Distribution Circuit | Equipment Failure/Involved | Overhead | 393 | 68853 | 37.1263 | -121.7285 | MEISTEN-JUSTIN: Mckean Rd SOUTH OF 41405 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0097397 | OH | Sus | 43221259 | No | 2017 | NOV | Yes | Line to Line | 1315654 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2105 | 83242105 | FUSE | 4685 | 20171208 | 1954 | 1939315 | 786 | Distribution Circuit | Animal | Other | 18 | 9498 | 37.0546 | -121.6608 | FUCO 5213 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0100894 | OH | Sus | 31369008 | No | 2017 | DEC | Yes | Line to Ground | 1318525 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | LLAGAS-2101 | 83182101 | FUSE | 3843 | 20171227 | 1150 | 1951967 | 870 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 12180 | 37.0696 | -121.5205 | 2 SPANS LD SIDE OF MTR# 1007453830 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0103412 | OH | Sus | 31371473 | No | 2017 | DEC | Yes | Line to Ground | 1322116 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2111 | 83242111 | RECLOSER | XR398 | 20180115 | 1750 | 8563 | 517 | Distribution Circuit | Equipment Failure/Involved | Overhead | 394 | 39430 | 37.1263 | -121.7285 | BET FUCO 83889 & 7869 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0006217 | OH | Sus | 43254247 | No | 2018 | JAN | Yes | Line to Ground | 1324911 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2111 | 83242111 | FUSE | 4329 | 20180514 | 1539 | 86061 | 1321 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 3134 | 37.0845 | -121.7133 | 15805 UVAS RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0040988 | OH | Sus | 31392126 | No | 2018 | MAY | Yes | Line to Ground | 1348954 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 3 | HICKS-2101 | 83432101 | FUSE | 6813 | 20181225 | 1327 | 247143 | 573 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 10314 | 37.1563 | -121.8443 | 5 SPANS SOUTH OF 6813 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110660 | OH | Sus | 43621736 | No | 2018 | DEC | Yes | Line to Ground | 1401743 | CO | OH | No | Yes
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2111 | 83242111 | FUSE | 3761 | 20190203 | 309 | 288383 | 1011 | Distribution Circuit | Vegetation | Tree - fell into line | 124 | 94682 | 37.1085 | -121.7322 | 2 SPANS SS OF 4461 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017479 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411894 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | SWIFT-2110 | 83392110 | FUSE | 15557 | 20190310 | 848 | 335402 | 6471 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 6471 | 37.3414 | -121.6411 | 7261 MOUNT HAMILTON RD | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0033827 | OH | Sus | 31428905 | No | 2019 | MAR | Yes | Line to Ground | 1424147 | CAW | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 3 | MORGAN HILL-2111 | 83242111 | FUSE | 4463 | 20190620 | 1315 | 424133 | 820 | Distribution Circuit | Vegetation | Tree - branch fell on line | 7 | 5740 | 37.0835 | -121.7684 | 11 SPANS LD SIDE OF 4463 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0070354 | OH | Sus | 43853074 | yes | 2019 | JUN | Yes | Line to Ground | 1451252 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | LLAGAS-2101 | 83182101 | FUSE | 3843 | 20190627 | 1515 | 432256 | 865 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 12110 | 37.0696 | -121.5205 | 10750 COYOTE RESERVOIR RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0072829 | OH | Sus | 31455586 | No | 2019 | JUN | Yes | Line to Ground | 1453218 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | SWIFT-2110 | 83392110 | FUSE | 15525 | 20191115 | 621 | 707242 | 319 | Distribution Circuit | Equipment Failure/Involved | Overhead | 182 | 19139 | 37.3353 | -121.7714 | 3/P/N/O 42477 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0125002 | OH | Sus | 44099419 | No | 2019 | NOV | Yes | Line to Ground | 1491451 | CSO | OH | No | Yes
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2111 | 83242111 | FUSE | 3761 | 20200517 | 830 | 915040 | 765 | Distribution Circuit | Vegetation | Tree - fell into line | 125 | 23085 | 37.1085 | -121.7322 | 8000 CROY RD.- MORGAN HILL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0050967 | OH | Sus | 44325933 | yes | 2020 | MAY | Yes | Line to Line | 1532907 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2111 | 83242111 | RECLOSER | 997000 | 20220211 | 830 | 1625401 | 860 | Distribution Circuit | 3rd Party | Vehicle | 299 | 38280 | 37.1446 | -121.6698 | SW 513 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0021202 | OH | Sus | 0 | No | 2022 | FEB | Yes | Line to Ground | 1709267 | PW | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MILPITAS-1109 | 82831109 | OTHER | WIRE DOWN 1/S/WO 40805 | 20220315 | 2026 | 1649487 | 523 | Distribution Circuit | Equipment Failure/Involved | Overhead | 209 | 104603 | 37.439 | -121.8306 | 1/S/WO 40805 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 22-0034336 | OH | Sus | 0 | No | 2022 | MAR | Yes | Line to Ground | 1717353 | CSO | OH | No | Yes
SAN JOSE | FIELD OPS SOUTH | Tier 3 | MORGAN HILL-2111 | 83242111 | FUSE | 4463 | 20220408 | 901 | 1665803 | 869 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 6083 | 37.0839 | -121.7682 | JOHNSON- JON / 408-209-5042: 14 POLES FROM 4463 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0044659 | OH | Sus | 45246530 | No | 2022 | APR | Yes | Line to Ground | 1723908 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2111 | 83242111 | RECLOSER | 997000 | 20220525 | 1015 | 1710007 | 937 | Distribution Circuit | Equipment Failure/Involved | Overhead | 397 | 119679 | 37.1446 | -121.6698 | NW OF RISER CUTOUT 25367 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0066191 | OH | Sus | 31604496 | No | 2022 | MAY | Yes | Line to Ground | 1739276 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2111 | 83242111 | RECLOSER | XR398 | 20220727 | 26 | 1766285 | 1497 | Distribution Circuit | 3rd Party | Vehicle | 400 | 233040 | 37.1263 | -121.7284 | AT 40191 POLE | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0090111 | OH | Sus | 0 | No | 2022 | JUL | Yes | Line to Ground | 1755337 | PW | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2111 | 83242111 | FUSE | 1685 | 20230117 | 540 | 1959085 | 606 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1212 | 37.1208 | -121.6868 | W/S LLAGAS RD. S/O WOODLAND AV. | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0017454 | OH | Sus | 0 | No | 2023 | JAN | Yes | Open Circuit | 1806124 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2111 | 83242111 | FUSE | 28347 | 20230202 | 1121 | 1974905 | 864 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 864 | 37.1321 | -121.7012 | 28347 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0024438 | OH | Sus | 0 | No | 2023 | FEB | Yes | Line to Ground | 1810050 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 3 | MORGAN HILL-2105 | 83242105 | FUSE | 4253 | 20230311 | 2004 | 2032880 | 1406 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7030 | 37.0457 | -121.7231 | CGC 316434520495 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0043702 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1824220 | CO | OH | No | No
SAN JOSE | FIELD OPS SOUTH | Tier 2 | MORGAN HILL-2111 | 83242111 | RECLOSER | XR398 | 20230322 | 402 | 2061559 | 9 | Distribution Circuit | Vegetation | Tree - fell into line | 276 | 2484 | 37.1263 | -121.7284 | LD SIDE & SS OF 43487 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0050314 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1828976 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 31403 | 20130102 | 1338 | 724538 | 845 | Distribution Circuit | 3rd Party | Vehicle | 47 | 19483 | 39.0089 | -121.0424 | IFO 2910 VOLLEY CIR | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0001758 | OH | Sus | 30968864 | No | 2013 | JAN | Yes | Line to Line | 99306080 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | DIAMOND SPRINGS-1107 | 152261107 | FUSE | 10725 | 20130108 | 1144 | 727098 | 121 | Distribution Circuit | Equipment Failure/Involved | Other | 186 | 18937 | 38.7112 | -120.8862 | MTR# 1007142566 | Overcast-32 - 90 F | Insulator | Broken, wire on ground | 13-0002798 | OH | Sus | 41835353 | No | 2013 | JAN | Yes | Line to Ground | 99305376 | INS | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 10002 | 20130112 | 1609 | 729118 | 898 | Distribution Circuit | 3rd Party | Vehicle | 1229 | 273813 | 38.5722 | -120.7337 | 2 SP S/O 21341 & MTR#100390925 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0003838 | OH | Sus | 41838832 | No | 2013 | JAN | Yes | Line to Line | 99304778 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2422 | 20130113 | 2241 | 729465 | 824 | Distribution Circuit | Vegetation | Tree - fell into line | 605 | 146475 | 38.8999 | -120.9074 | HATTRUP-JIM/1533/530-906-2888: Main line 6 spans beyond CO 5891 On Upper Manhattan Creek Rd | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0003922 | OH | Sus | 30970968 | No | 2013 | JAN | Yes | Line to Line | 99304700 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE | 6685 | 20130124 | 1437 | 734006 | 788 | Distribution Circuit | 3rd Party | Vehicle | 66 | 41145 | 39.2158 | -120.997 | 1 POLE LD SIDE OF FU 6687 ON MAIN LINE | Rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0005999 | OH | Sus | 30972991 | No | 2013 | JAN | Yes | Line to Ground | 99303460 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE | 6685 | 20130126 | 1049 | 734807 | 486 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 32076 | 39.2158 | -120.997 | 14375 GREENHORN RD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0006332 | OH | Sus | 41845875 | No | 2013 | JAN | Yes | Line to Ground | 99303237 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 30917 | 20130128 | 1353 | 735653 | 384 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 384 | 38.8982 | -120.9766 | RAND-DAN/530-913-6400: 2000 hwy 193 cool part of outage ois# 735594 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0006593 | OH | Sus | 0 | No | 2013 | JAN | Yes | Line to Ground | 99302990 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE | 33279 | 20130214 | 757 | 742035 | 489 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 12 | 5868 | 39.1679 | -120.9658 | MTR#1007742684 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0009994 | OH | Sus | 30977320 | No | 2013 | FEB | Yes | Line to Line | 99300894 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 5299 | 20130219 | 1626 | 744144 | 289 | Distribution Circuit | Equipment Failure/Involved | Other | 35 | 10115 | 38.676 | -120.6367 | 344 FOREST SPRINGS RD. RIGHT AT FUCO 21381 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0011015 | OH | Sus | 41856428 | yes | 2013 | FEB | Yes | Line to Ground | 99300291 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 8372 | 20130219 | 2214 | 744699 | 364 | Distribution Circuit | Environmental/External | Ice or snow | 701 | 128560 | 38.6093 | -120.7025 | STEELE-BRENT/624/530-906-3165: 7800 boondock trl somerset | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0011072 | OH | Sus | 41856540 | yes | 2013 | FEB | Yes |  | 99300253 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8113 | 20130219 | 1403 | 743928 | 777 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 32634 | 39.3809 | -120.9942 | 1 SPAN SS OF MTR#1005534276 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0010987 | OH | Sus | 30978304 | yes | 2013 | FEB | Yes | Three Phase Fault | 99300311 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 1299 | 20130219 | 1646 | 744160 | 369 | Distribution Circuit | Vegetation | Tree - branch fell on line | 69 | 25461 | 38.6924 | -120.7646 | 4580 CEDAR RAVINE | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0011035 | OH | Sus | 41856431 | yes | 2013 | FEB | Yes | Line to Ground | 99300277 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE | 4801 | 20130220 | 937 | 745043 | 297 | Distribution Circuit | Equipment Failure/Involved | Other | 210 | 75774 | 39.264 | -121.0216 | 1 SPAN E/OF 4801 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0011270 | OH | Sus | 41856733 | yes | 2013 | FEB | Yes | Line to Ground | 99299960 | CSO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | ECHO SUMMIT-1101 | 158031101 | FUSE | 2619 | 20130309 | 1740 | 754707 | 2600 | Distribution Circuit | Equipment Failure/Involved | Other | 62 | 104098 | 38.8252 | -120.0373 | 1/S/OF 2621 | Clear-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 13-0015439 | OH | Sus | 30982108 | No | 2013 | MAR | Yes | Line to Ground | 99297204 | CAW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 7742 | 20130319 | 1820 | 759021 | 771 | Distribution Circuit | Equipment Failure/Involved | Other | 749 | 116914 | 38.6612 | -120.911 | 1 SPAN S/O C2044 | Rain-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0017818 | OH | Sus | 41871083 | No | 2013 | MAR | Yes |  | 99295619 | CSO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 6852 | 20130321 | 557 | 759673 | 495 | Distribution Circuit | 3rd Party | Vehicle | 1992 | 201906 | 38.7611 | -120.5586 | DERYK-KEVIN/621/530-386-5111: sly park rd 3 P/N/O FUCO 20973 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0018095 | OH | Sus | 30984511 | No | 2013 | MAR | Yes | Multi-Fault | 99295458 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | LINCOLN-2108 | 153702108 | FUSE | 5393 | 20130321 | 1538 | 760014 | 237 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 14850 | 38.9464 | -121.2466 | 1 P/N/O FUCO 5393 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0018299 | OH | Sus | 41871932 | No | 2013 | MAR | Yes | Line to Ground | 99295309 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | OTHER |  | 20130330 | 2216 | 764000 | 587 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 13365 | 39.3214 | -120.8644 | at FUCO 31909 TWD 9819 | Lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0020252 | OH | Sus | 30986514 | No | 2013 | MAR | Yes | Line to Line | 99293828 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE | 59355 | 20130330 | 1659 | 763868 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 8957 | 39.1163 | -120.9515 | 2 E/O C/OUT 33571 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0020188 | OH | Sus | 30986476 | No | 2013 | MAR | Yes | Line to Line | 99293929 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER | 2130 | 20130416 | 1523 | 776564 | 437 | Distribution Circuit | Vegetation | Tree - fell into line | 198 | 21682 | 39.2741 | -120.97 | ON MAINLINE AT 34169. | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0024999 | OH | Sus | 30990017 | yes | 2013 | APR | Yes |  | 99290171 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 12635 | 20130425 | 1210 | 781616 | 175 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 21 | 3675 | 38.8057 | -120.7001 | 6150 PINE NEEDLE | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0027241 | OH | Sus | 41888918 | No | 2013 | APR | Yes | None | 99288546 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-1104 | 153651104 | OCB | OCB | 20130426 | 1644 | 782403 | 535 | Distribution Circuit | 3rd Party | Vehicle | 1257 | 70283 | 38.6594 | -120.9472 | DOLCINI-JOHN/627/530-906-3118: Rear of 4151 South shingle rd.- Shingle Springs | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0027595 | OH | Sus | 30992778 | No | 2013 | APR | Yes | Line to Ground | 99288247 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 61892 | 20130430 | 709 | 783804 | 358 | Distribution Circuit | Vegetation | Tree - fell into line | 391 | 29154 | 38.7122 | -120.9498 | DERYK-KEVIN/621/530-386-5111: 500 jurgens | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0028152 | OH | Sus | 30993304 | yes | 2013 | APR | Yes | Three Phase Fault | 99287825 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8133 | 20130501 | 137 | 784680 | 803 | Distribution Circuit | Vegetation | Tree - bark fell into line | 42 | 10917 | 39.3771 | -120.9844 | BENTLEY-S/1585/209-559-4666: 18191 Tyler Foote Rd Nevada City | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0028483 | OH | Sus | 30993478 | yes | 2013 | MAY | Yes |  | 99287570 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 18875 | 20130519 | 1424 | 794996 | 710 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 23210 | 38.822 | -120.8807 | HART-EMMETT/1506/530-906-2031: 6241 Mt Murphy Rd 4-spans load/s co c/o 18875 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0032849 | OH | Sus | 41900902 | No | 2013 | MAY | Yes | Line to Line | 99284390 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | OCB | OCB | 20130519 | 1133 | 794919 | 196 | Distribution Circuit | Vegetation | Tree - fell into line | 1605 | 226915 | 39.0357 | -120.9877 | RIGHT OUTSIDE SUB | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0032830 | OH | Sus | 30997310 | No | 2013 | MAY | Yes | Line to Ground | 99284409 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 30935 | 20130528 | 1342 | 799817 | 783 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1566 | 38.8967 | -120.8921 | JOHNSTON-M/1508/530-906-5563: 4644 hwy 193 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0034944 | OH | Sus | 30999173 | No | 2013 | MAY | Yes |  | 99282943 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | CLARKSVILLE-2103 | 153612103 | FUSE | 10695 | 20130601 | 1632 | 802003 | 662 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 110653 | 38.592 | -121.0134 | MTR#1009125782 | Clear-Above 90 F | Conductor, Overhead | On Ground | 13-0035858 | OH | Sus | 41906270 | No | 2013 | JUN | Yes |  | 99282302 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | BELL-1107 | 152701107 | FUSE | 4549 | 20130603 | 1606 | 803368 | 360 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 4656 | 38.9037 | -121.1173 | AT MTR # 1004773380 & 10400 BLUE LIGHT RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0036231 | OH | Sus | 0 | No | 2013 | JUN | Yes | Line to Ground | 99282041 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 4201 | 20130617 | 1328 | 811970 | 797 | Distribution Circuit | 3rd Party | Vehicle | 30 | 7488 | 39.1544 | -121.1894 | OAK MEADOW RD | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0040272 | OH | Sus | 0 | No | 2013 | JUN | Yes | Line to Ground | 99279420 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | FUSE | 7863 | 20130620 | 939 | 813545 | 805 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 9170 | 39.0916 | -121.1774 | mtr#1007518429 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0041189 | OH | Sus | 31004065 | No | 2013 | JUN | Yes | Line to Line | 99278880 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | FUSE | 3711 | 20130625 | 1254 | 817016 | 376 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 8328 | 38.9086 | -121.1639 | JOHNSTON-M/1508/530-906-5563: 6844 chili hill rd | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0042558 | OH | Sus | 31005228 | yes | 2013 | JUN | Yes |  | 99277966 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 7961 | 20130627 | 2157 | 818959 | 820 | Distribution Circuit | 3rd Party | Vehicle | 52 | 36190 | 38.7534 | -120.6198 | 2 POLES N/OF 1009706531 | Clear-32 - 90 F | Pole-Wood | Broken, wire on object | 13-0043283 | OH | Sus | 31005829 | yes | 2013 | JUN | Yes | Line to Line | 99277450 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE | 33113 | 20130627 | 1756 | 818753 | 679 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 20 | 5552 | 39.2523 | -121.0094 | MTR# 1007600281 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0043265 | OH | Sus | 31005811 | yes | 2013 | JUN | Yes | Line to Ground | 99277456 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE | 1513 | 20130629 | 1234 | 820386 | 1706 | Distribution Circuit | 3rd Party | Vehicle | 20 | 9592 | 38.7424 | -120.6943 | 2920 BARKELY | Heat wave-Above 90 F | Pole-Wood | Broken, wire on ground | 13-0043705 | OH | Sus | 31006168 | yes | 2013 | JUN | Yes | Line to Ground | 99276669 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 8372 | 20130629 | 1826 | 820880 | 1124 | Distribution Circuit | Equipment Failure/Involved | Other | 701 | 63285 | 38.6093 | -120.7025 | 3 SPANS SOUTH OF 1345 | Clear-Above 90 F | Conductor, Overhead | Broken, wire on ground | 13-0043792 | OH | Sus | 41920100 | yes | 2013 | JUN | Yes |  | 99276912 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1110 | 152691110 | FUSE | 4871 | 20130629 | 111 | 820046 | 443 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 14176 | 39.0615 | -121.0192 | JIMENEZ-AL/1586/530-913-7963: MAGNOLIA RD BTWN CLIFFORD RD & SPRING RANCH RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0043608 | OH | Sus | 31006082 | yes | 2013 | JUN | Yes |  | 99277204 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | RECLOSER | 594 | 20130702 | 1020 | 823677 | 425 | Distribution Circuit | Vegetation | Tree - bark fell into line | 247 | 13835 | 39.0349 | -121.0957 | TASSONE-LOUIS/1262/682-6302: 1 POLE LD SIDE C/O 5707 | Heat wave-Above 90 F | Conductor, Overhead | Broken, wire on ground | 13-0044574 | OH | Sus | 0 | yes | 2013 | JUL | Yes | Line to Ground | 99276355 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 3049 | 20130722 | 413 | 836258 | 407 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 4896 | 38.8194 | -120.8677 | MTR#1004755648 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0048992 | OH | Sus | 41930409 | No | 2013 | JUL | Yes | Line to Ground | 99273058 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | OTHER |  | 20130726 | 932 | 838845 | 434 | Distribution Circuit | Animal | Other | 2286 | 0 | 38.9709 | -121.0369 | HOT WIRE DOWN I SPAN SS OF 5767 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0050370 | OH | Sus | 41933512 | No | 2013 | JUL | Yes |  | 99272178 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1101 | 152201101 | RECLOSER | 1730 | 20130808 | 926 | 844984 | 782 | Distribution Circuit | Animal | Squirrel | 140 | 100772 | 39.452 | -121.0542 | MARYSVILLE RD AND SYCAMORE - CAMPTONVILLE | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 13-0053248 | OH | Sus | 41940015 | No | 2013 | AUG | Yes | Line to Ground | 99270335 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE | 7815 | 20130812 | 1807 | 847220 | 856 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 2 | 1712 | 39.146 | -121.1443 | MTR#1007535043 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0054100 | OH | Sus | 0 | No | 2013 | AUG | Yes | Multi-Fault | 99269688 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | FUSE | 5431 | 20130817 | 1213 | 850177 | 272 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 3848 | 38.9006 | -121.1452 | SATTERLEE-M/1531/530-320-4435: 2/2blwn at 5431-tree branch on 12kv-openO-J-awaiting crew | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0055377 | OH | Sus | 41944823 | No | 2013 | AUG | Yes | Line to Ground | 99268834 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 12617 | 20130820 | 1848 | 853066 | 464 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 7888 | 38.8068 | -120.7468 | AT MTR# 1007477721 | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 13-0056277 | OH | Sus | 0 | yes | 2013 | AUG | Yes | Line to Line | 99268056 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 4345 | 20130823 | 1639 | 854746 | 523 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 13348 | 39.2116 | -121.2012 | 19319 DONAVAN | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0057174 | OH | Sus | 41947106 | No | 2013 | AUG | Yes | Line to Ground | 99267396 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 3087 | 20130824 | 1452 | 855070 | 1738 | Distribution Circuit | Vegetation | Tree - fell into line | 2947 | 373302 | 38.905 | -120.84 | 16 SP S/O C/OUT 3078 | Partly cloudy-Above 90 F | Conductor, Overhead | Broken, wire on ground | 13-0057261 | OH | Sus | 0 | No | 2013 | AUG | Yes | Three Phase Fault | 99267272 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 11409 | 20130827 | 958 | 856346 | 499 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 64 | 11929 | 38.696 | -120.6071 | MTR# 1005202815 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0057801 | OH | Sus | 41948156 | No | 2013 | AUG | Yes |  | 99266826 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8035 | 20130902 | 2 | 859207 | 814 | Distribution Circuit | 3rd Party | Vehicle | 1131 | 108584 | 39.3445 | -121.077 | TASSONE-LOUIS/1262/682-6302: MURPHY & TYLER FOOTE RD | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on object | 13-0059091 | OH | Sus | 31018558 | yes | 2013 | SEP | Yes |  | 99266114 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 9729 | 20130906 | 1559 | 861895 | 599 | Distribution Circuit | Equipment Failure/Involved | Other | 1333 | 99634 | 39.109 | -121.0906 | MTR#1007522751 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on object | 13-0060339 | OH | Sus | 41951939 | No | 2013 | SEP | Yes | Line to Ground | 99265254 | CSO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE | 30899 | 20130923 | 1227 | 871732 | 847 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 24 | 11709 | 39.0206 | -120.8137 | RAND-DAN/530-913-6400: 2460 granite chief foresthill | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0064158 | OH | Sus | 31023592 | No | 2013 | SEP | Yes |  | 99262321 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 31097 | 20131003 | 2255 | 877831 | 957 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 7359 | 38.9331 | -120.7531 | 8771 WINTWORTH SPRINGS | Clear-32 - 90 F | Pole-Wood | Broken, wire on object | 13-0067117 | OH | Sus | 31026004 | yes | 2013 | OCT | Yes | Line to Ground | 99260306 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE | 3739 | 20131004 | 437 | 878071 | 503 | Distribution Circuit | Equipment Failure/Involved | Other | 74 | 37222 | 39.1917 | -121.0972 | 13160 MCCOURTNEY RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0067191 | OH | Sus | 41967679 | yes | 2013 | OCT | Yes | Line to Ground | 99260257 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 4065 | 20131009 | 322 | 881540 | 433 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 22949 | 38.8425 | -121.0289 | 10 SPANS LD SIDE OF 4065 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0068246 | OH | Sus | 41969196 | yes | 2013 | OCT | Yes | Three Phase Fault | 99259461 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2102 | 153132102 | FUSE | 32993 | 20131024 | 841 | 889498 | 532 | Distribution Circuit | 3rd Party | Vehicle | 84 | 44688 | 39.2527 | -121.1147 | 13631 EMPRESS RD. | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0071818 | OH | Sus | 31030963 | No | 2013 | OCT | Yes | Line to Ground | 99256772 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1106 | 152481106 | SECTIONALIZER | 2772 | 20131029 | 1900 | 893607 | 692 | Distribution Circuit | Vegetation | Tree - fell into line | 173 | 54700 | 39.149 | -121.0343 | 2 SPANS LOAD SIDE OF 6753 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0073177 | OH | Sus | 31032199 | No | 2013 | OCT | Yes | Line to Ground | 99255772 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1103 | 152561103 | FUSE | 5253 | 20131101 | 2107 | 895099 | 1283 | Distribution Circuit | 3rd Party | Aircraft | 55 | 37650 | 38.8342 | -121.1096 | FOLSOM LAKE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0073955 | OH | Sus | 41982618 | No | 2013 | NOV | Yes | Three Phase Fault | 99255267 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 9315 | 20131120 | 1324 | 905809 | 761 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 18626 | 38.9111 | -120.8246 | 3251 HANSON HOLLOW | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0077418 | OH | Sus | 31037493 | yes | 2013 | NOV | Yes | Line to Ground | 99252477 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 3915 | 20131123 | 1842 | 913250 | 296 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 8880 | 38.9178 | -120.8148 | 3261 CHIPMUNK TRAIL | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078970 | OH | Sus | 0 | yes | 2013 | NOV | Yes |  | 99251097 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | SPAULDING-1101 | 152251101 | OTHER |  | 20131124 | 1048 | 914361 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3024 | 39.2978 | -120.6406 | 476 N FORK PLACE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0079086 | OH | Sus | 0 | No | 2013 | NOV | Yes | Line to Ground | 99250855 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 1333 | 20131126 | 1209 | 915725 | 459 | Distribution Circuit | Equipment Failure/Involved | Other | 25 | 2763 | 38.6746 | -120.7235 | 2061 REISLING | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0079433 | OH | Sus | 31038906 | No | 2013 | NOV | Yes | None | 99250543 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 4713 | 20131206 | 2133 | 921340 | 1192 | Distribution Circuit | 3rd Party | Vehicle | 58 | 10825 | 39.1652 | -121.1579 | MTR#1007666312 | Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 13-0081093 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99249068 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | OCB | OCB | 20131206 | 2334 | 921491 | 741 | Distribution Circuit | Environmental/External | Ice or snow | 3492 | 541146 | 38.6594 | -120.9466 | SAMANIEGO-S/626/530-906-3122: 3661 ponderosa rd & 3471 PONDEROSA | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081089 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Multi-Fault | 99249069 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | BELL-1108 | 152701108 | OTHER |  | 20131207 | 1327 | 922942 | 213 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 920 | 38.99 | -121.0859 | WIRE DOWN E/OF TRANSF 222599248334 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081346 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Line | 99248878 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 1299 | 20131207 | 223 | 921780 | 693 | Distribution Circuit | Environmental/External | Ice or snow | 69 | 47817 | 38.6924 | -120.7646 | SAMANIEGO-S/626/530-906-3122: 4700 b mineral way | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0081206 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Multi-Fault | 99249002 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 5781 | 20131207 | 50 | 921979 | 621 | Distribution Circuit | Vegetation | Tree - fell into line | 172 | 104353 | 39.0177 | -121.0297 | 2721 HILLSIDE RD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081211 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99248999 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 5785 | 20131207 | 538 | 921951 | 557 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 5570 | 39.0045 | -121.0378 | SATTERLEE-M/1531/530-320-4435: 2/2 blwn at 5785-1span #4acsr down(800ft span) | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081268 | OH | Sus | 0 | yes | 2013 | DEC | Yes |  | 99248939 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | BELL-1108 | 152701108 | FUSE | 8537 | 20131209 | 2034 | 924585 | 326 | Distribution Circuit | Equipment Failure/Involved | Other | 202 | 36664 | 38.9818 | -121.0732 | 3557 MARY LN | Clear-32 - 90 F | Insulator | Broken, wire on object | 13-0081668 | OH | Sus | 0 | No | 2013 | DEC | Yes | Line to Ground | 99248540 | INS | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 34007 | 20131221 | 1004 | 931462 | 476 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 10 | 1385 | 39.0504 | -120.9667 | MTR#1004688955 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0083128 | OH | Sus | 31044452 | No | 2013 | DEC | Yes | Line to Line | 99246628 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | CLARKSVILLE-2104 | 153612104 | RECLOSER | 13352 | 20140102 | 653 | 936395 | 232 | Distribution Circuit | Equipment Failure/Involved | Other | 704 | 109471 | 38.6875 | -121.0135 | W/O C135- 6 SPANS E/O OF 2181 MARDEN DR- 6 SPANS E/O OF 2181 MARDEN DR | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0001811 | OH | Sus | 42052333 | No | 2014 | JAN | Yes | Line to Line | 99245487 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 19752 | 20140105 | 2302 | 937555 | 1168 | Distribution Circuit | 3rd Party | Vehicle | 1076 | 132808 | 38.7139 | -120.5836 | SW 13127 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0002262 | OH | Sus | 31046767 | No | 2014 | JAN | Yes | Line to Line | 99245269 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE | 1313 | 20140209 | 1227 | 964249 | 653 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 16325 | 38.7589 | -120.7201 | 3430 N. CANTON RD- CAMINO | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0010158 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Three Phase Fault | 99240467 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 2500 | 20140209 | 352 | 963780 | 2473 | Distribution Circuit | Vegetation | Tree - fell into line | 1321 | 506576 | 38.8234 | -120.0308 | STEELE-BRENT/624/530-906-3165: johnson pass rd and hwy 50 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0010085 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Line | 99240379 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1102 | 152591102 | SWITCH | 2305 | 20140209 | 616 | 963884 | 788 | Distribution Circuit | Environmental/External | Ice or snow | 292 | 18911 | 39.3094 | -120.3408 | 1 P/SOURCE SIDE OF 6841 FUCO- SATTERLEE-M/1531/530-320-4435: deenergized circuit to clear downed 12 | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0010071 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Ground | 99240539 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-1104 | 153651104 | OTHER |  | 20140210 | 930 | 964907 | 420 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1260 | 38.5923 | -120.967 | LIZARRAGA-A/620/530-906-3131: 6240 FERNWOOD | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0010335 | OH | Sus | 42075344 | yes | 2014 | FEB | Yes | Line to Ground | 99240175 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1102 | 152591102 | OTHER |  | 20140210 | 958 | 964957 | 319 | Distribution Circuit | Equipment Failure/Involved | Other | 10 | 2137 | 39.3165 | -120.3368 | 4 SPANS LOADSIDE OF 1359 | Drizzle-32 - 90 F | Conductor, Overhead | On Ground | 14-0010396 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Ground | 99240268 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1103 | 152561103 | FUSE | 8909 | 20140215 | 2014 | 968082 | 460 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 10260 | 38.8548 | -121.1077 | HARD TAP TO WEST at MTR# 1004894485 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0011537 | OH | Sus | 42079300 | No | 2014 | FEB | Yes | Line to Ground | 99239459 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 20881 | 20140216 | 2339 | 968384 | 1056 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4372 | 38.6552 | -120.7038 | MTR#1006523337 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0011614 | OH | Sus | 31057073 | No | 2014 | FEB | Yes | Line to Ground | 99239388 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | RECLOSER | 2054 | 20140220 | 1810 | 970115 | 354 | Distribution Circuit | Animal | Bird found | 209 | 39210 | 38.8964 | -121.1203 | 9405 CRATER HILL RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0012479 | OH | Sus | 42081282 | No | 2014 | FEB | Yes | Line to Ground | 99238870 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE | 8061 | 20140224 | 905 | 971394 | 971 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 112 | 90146 | 39.2624 | -121.0733 | TASSONE-LOUIS/1262/682-6302: NEWTOWN RD | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0012906 | OH | Sus | 31058297 | No | 2014 | FEB | Yes |  | 99238492 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1103 | 152561103 | FUSE | 8909 | 20140225 | 1337 | 972254 | 246 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 71 | 10998 | 38.8548 | -121.1077 | 2321 PERSIMMON LN | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0013263 | OH | Sus | 42082973 | No | 2014 | FEB | Yes | Line to Ground | 99238291 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | RECLOSER | 50486 | 20140226 | 48 | 972491 | 580 | Distribution Circuit | 3rd Party | Vehicle | 892 | 201790 | 38.9928 | -120.8827 | POLE 2 SPANS LD SIDE OF LR 50486 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0013329 | OH | Sus | 31058955 | yes | 2014 | FEB | Yes | Line to Line | 99238021 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 6935 | 20140226 | 2344 | 973381 | 1091 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 10910 | 38.8537 | -120.8285 | 4441 WINTUN CT - GARDEN VALLEY MTR#1007742638 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0013715 | OH | Sus | 31059421 | yes | 2014 | FEB | Yes | Line to Ground | 99237995 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE | 7073 | 20140227 | 113 | 973412 | 459 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 18360 | 39.164 | -120.9688 | MTR# 1007742638 | Heavy rain-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0013740 | OH | Sus | 42083765 | yes | 2014 | FEB | Yes | Line to Ground | 99237985 | CSO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 2061 | 20140227 | 612 | 973477 | 329 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2303 | 38.6817 | -120.8607 | 1 N/OF MTR#1007195826 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0013759 | OH | Sus | 42083767 | yes | 2014 | FEB | Yes | Line to Ground | 99237969 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 90730 | 20140228 | 1127 | 975113 | 402 | Distribution Circuit | Animal | Bird found | 92 | 25791 | 39.3424 | -121.1221 | JIMENEZ-AL/1586/530-913-7963: PLEASENT VALLEY at BIRCHVILLE RD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0014441 | OH | Sus | 31059838 | yes | 2014 | FEB | Yes | Line to Ground | 99237533 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER | 2204 | 20140302 | 1729 | 977129 | 410 | Distribution Circuit | Equipment Failure/Involved | Other | 1684 | 427122 | 39.2642 | -120.9857 | AT SWITCH 1473 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0014932 | OH | Sus | 0 | No | 2014 | MAR | Yes | Line to Ground | 99237041 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | RECLOSER | 697216 | 20140307 | 614 | 980296 | 399 | Distribution Circuit | Equipment Failure/Involved | Other | 204 | 34126 | 38.9364 | -121.1762 | RENFREE-SAM/1505/530-906-2110: MT V ERNON AND BUFFALO HILL RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0016350 | OH | Sus | 31061510 | No | 2014 | MAR | Yes | Line to Line | 99235963 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE | 8015 | 20140312 | 503 | 983063 | 767 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3835 | 38.7586 | -120.6791 | 2190 APPLE VISTA LANE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0017499 | OH | Sus | 0 | yes | 2014 | MAR | Yes | Line to Line | 99235284 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 6799 | 20140312 | 909 | 983300 | 491 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 9300 | 38.7601 | -120.5688 | LIZARRAGA-A/620/530-906-3131: 3354 sly park rd | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0017538 | OH | Sus | 0 | yes | 2014 | MAR | Yes |  | 99235255 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1102 | 152241102 | OTHER |  | 20140312 | 509 | 982939 | 333 | Distribution Circuit | Equipment Failure/Involved | Other | 23 | 5214 | 38.9478 | -121.0376 | 445 CHUBB RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0017459 | OH | Sus | 0 | yes | 2014 | MAR | Yes | Line to Line | 99235325 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 8145 | 20140313 | 1641 | 984254 | 299 | Distribution Circuit | Vegetation | Tree - fell into line | 184 | 19492 | 38.6978 | -120.9363 | 3 S/OF 53913 | Clear-32 - 90 F | Fuse | Broken, wire on ground | 14-0018006 | OH | Sus | 42092174 | No | 2014 | MAR | Yes | Line to Ground | 99235017 | FUS | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 2177 | 20140316 | 727 | 985255 | 557 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4456 | 38.6916 | -120.7371 | 4807 WOODLAND DR PLACERVILLE | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0018395 | OH | Sus | 42093924 | No | 2014 | MAR | Yes | Line to Ground | 99234651 | CSO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | ALLEGHANY-1101 | 152101101 | RECLOSER | 978 | 20140330 | 519 | 991837 | 12521 | Distribution Circuit | Equipment Failure/Involved | Other | 198 | 293703 | 39.6079 | -120.6067 | THREE LOCATIONS: LD SIDE OF 32519 AND SS OF 32519 AND LD SIDE OF 7933 | Snow-Below 32 F | Insulator | Broken, wire on ground | 14-0021536 | OH | Sus | 0 | yes | 2014 | MAR | Yes | Line to Ground | 99231305 | INS | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | OTHER |  | 20140331 | 722 | 992196 | 374 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 392 | 38.7522 | -120.5549 | FLECKLIN-PAUL/623/530-906-3142: SBCO 1211 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0021621 | OH | Sus | 42100069 | yes | 2014 | MAR | Yes |  | 99232392 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1110 | 153081110 | FUSE | 12989 | 20140401 | 336 | 993040 | 488 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 15616 | 38.7472 | -120.8209 | STEELE-BRENT/624/530-906-3165: 331 baker rd placerville | Drizzle-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0021992 | OH | Sus | 0 | yes | 2014 | APR | Yes | Line to Line | 99232172 | CAW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 33873 | 20140401 | 936 | 993195 | 294 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1764 | 39.0286 | -120.9799 | JUST LD SIDE OF 33873 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0022117 | OH | Sus | 42100612 | yes | 2014 | APR | Yes |  | 99232107 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1102 | 152241102 | FUSE | 8487 | 20140424 | 2000 | 1004197 | 374 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4488 | 38.9855 | -121.006 | 3 SPANS LD SIDE OF 8487 | Drizzle-32 - 90 F | Conductor, Overhead | On Ground | 14-0027102 | OH | Sus | 42113235 | No | 2014 | APR | Yes | Line to Line | 99228854 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | OTHER |  | 20140425 | 1826 | 1004783 | 703 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 0 | 38.6701 | -120.7737 | WIRE DOWN 1 SPAN E/0F 10587 | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0027416 | OH | Sus | 31071810 | yes | 2014 | APR | Yes |  | 99228606 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 31165 | 20140426 | 431 | 1004950 | 825 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4125 | 38.8402 | -120.8744 | 5520 HANCOCK CT | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0027477 | OH | Sus | 31071735 | yes | 2014 | APR | Yes | Line to Ground | 99228580 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8215 | 20140514 | 1928 | 1015672 | 488 | Distribution Circuit | Equipment Failure/Involved | Other | 23 | 11224 | 39.3815 | -120.9963 | MTR 1007605427 | Clear-32 - 90 F | Insulator | Broken, wire on object | 14-0031886 | OH | Sus | 31076297 | yes | 2014 | MAY | Yes |  | 99225657 | INS | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1110 | 152691110 | FUSE | 4871 | 20140518 | 1348 | 1020367 | 650 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 5538 | 39.0615 | -121.0192 | MTR 1007517407 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0032703 | OH | Sus | 31077017 | No | 2014 | MAY | Yes |  | 99225067 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1102 | 152241102 | OCB | OCB | 20140521 | 659 | 1021814 | 887 | Distribution Circuit | Vegetation | Tree - fell into line | 1993 | 126553 | 38.9566 | -121.0433 | 4 E/OF SW 511 | Fog-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0033392 | OH | Sus | 31077495 | No | 2014 | MAY | Yes |  | 99224598 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 18875 | 20140522 | 1254 | 1022529 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 12817 | 38.822 | -120.881 | 6340 JOHNSTOWN CREEK RD- COLOMA | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0033795 | OH | Sus | 31077892 | No | 2014 | MAY | Yes | Line to Ground | 99224318 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE | 6005 | 20140528 | 321 | 1024982 | 814 | Distribution Circuit | Vegetation | Tree - fell into line | 399 | 78112 | 39.019 | -120.8961 | 20635 FORREST HILL RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0034582 | OH | Sus | 42130178 | No | 2014 | MAY | Yes | Line to Ground | 99223729 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1103 | 152561103 | FUSE | 5259 | 20140529 | 1447 | 1025967 | 474 | Distribution Circuit | 3rd Party | Vehicle | 373 | 4228 | 38.8414 | -121.1163 | NORMAL OPEN SW 5203 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0035081 | OH | Sus | 31079317 | No | 2014 | MAY | Yes |  | 99223427 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | RECLOSER | 9432 | 20140609 | 1243 | 1031368 | 665 | Distribution Circuit | Vegetation | Tree - fell into line | 549 | 250999 | 38.731 | -120.8422 | MTR# 1009704587 | Clear-Above 90 F | Conductor, Overhead | Broken, wire on ground | 14-0037197 | OH | Sus | 0 | yes | 2014 | JUN | Yes | Line to Ground | 99221933 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1110 | 152691110 | RECLOSER | 2408 | 20140623 | 1745 | 1038496 | 757 | Distribution Circuit | Vegetation | Tree - fell into line | 443 | 104875 | 39.047 | -121.0489 | BET: MTR# 1007517420 & FUCO 7495 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0040061 | OH | Sus | 31084370 | No | 2014 | JUN | Yes | Three Phase Fault | 99219805 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE | 6005 | 20140625 | 853 | 1039409 | 316 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 289 | 80744 | 39.019 | -120.8961 | HATTRUP-JIM/1533/530-906-2888: Mian Line N/O buck to 20340 Spring Garden # 1004520726 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0040448 | OH | Sus | 31084757 | yes | 2014 | JUN | Yes | Line to Ground | 99219512 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1110 | 152691110 | OTHER |  | 20140702 | 1328 | 1043534 | 397 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 4367 | 39.0662 | -121.015 | 15330 MAGNOLIA RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0042116 | OH | Sus | 42148436 | No | 2014 | JUL | Yes | Line to Ground | 99218342 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 6721 | 20140708 | 2239 | 1046625 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 11451 | 39.0695 | -120.9792 | 22640 PLUMTREE RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0043331 | OH | Sus | 31087567 | No | 2014 | JUL | Yes | Line to Line | 99217532 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1102 | 152491102 | FUSE | 6101 | 20140708 | 1353 | 1046412 | 366 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 145 | 36494 | 39.0439 | -120.9969 | 21450 PLACER HILLS RD | Clear-Above 90 F | Conductor, Overhead | Broken, wire on ground | 14-0043254 | OH | Sus | 42150432 | No | 2014 | JUL | Yes | Three Phase Fault | 99217572 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 11469 | 20140714 | 956 | 1048943 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 8388 | 38.7955 | -120.8032 | MTR # 1007480904 | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0044299 | OH | Sus | 31088783 | yes | 2014 | JUL | Yes | Line to Line | 99216791 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1103 | 153661103 | OTHER |  | 20140721 | 340 | 1052649 | 427 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 1002 | 38.7505 | -120.7423 | 2245 FROSTY FIR DR - MTR# 1009239832 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0045725 | OH | Sus | 42157447 | No | 2014 | JUL | Yes | Line to Ground | 99215808 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | FUSE | 32877 | 20140724 | 1928 | 1054932 | 480 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 11520 | 39.0507 | -121.1684 | MUELLER-ANDY/1585/530-863-6807: 16243 TIERRS RD- GRASS VALLEY | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0046849 | OH | Sus | 31091019 | yes | 2014 | JUL | Yes | Line to Ground | 99215139 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 13789 | 20140726 | 1548 | 1055843 | 2748 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 44 | 3975 | 38.5963 | -120.8059 | 5 P LD SIDE OF 20985 | Partly cloudy-Above 90 F | Pole-Wood | Broken, wire on ground | 14-0047155 | OH | Sus | 0 | yes | 2014 | JUL | Yes | None | 99214695 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 2177 | 20140726 | 734 | 1055656 | 634 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5072 | 38.6916 | -120.7371 | DERYK-KEVIN/621/530-386-5111: 4807 woodland | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0047136 | OH | Sus | 31091324 | yes | 2014 | JUL | Yes | Line to Line | 99214885 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 31753 | 20140804 | 302 | 1060532 | 734 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5872 | 39.2356 | -120.9813 | 13100 BANNER LAVA CAP | Overcast-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0048853 | OH | Sus | 31092762 | No | 2014 | AUG | Yes | Line to Line | 99213604 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | FUSE | 5379 | 20140805 | 257 | 1061094 | 788 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 16179 | 38.9489 | -121.1625 | 7150 MEARS DR #A AUBURN | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0049069 | OH | Sus | 42164031 | No | 2014 | AUG | Yes | Line to Ground | 99213457 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 30323 | 20140806 | 646 | 1061704 | 346 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1108 | 39.2373 | -121.1425 | 10790 BONANZA WAY | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0049358 | OH | Sus | 42164704 | No | 2014 | AUG | Yes | Line to Ground | 99213288 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | DRUM-1101 | 152321101 | FUSE | 30595 | 20140811 | 1932 | 1065037 | 453 | Distribution Circuit | 3rd Party | Vehicle | 45 | 3669 | 39.2566 | -120.7214 | HATTRUP-JIM/1533/530-906-2888: Car Pole 1 span source side # 1005564131 | Lightning-32 - 90 F | Insulator | Broken, wire on object | 14-0050415 | OH | Sus | 42168736 | yes | 2014 | AUG | Yes | Line to Ground | 99212510 | INS | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | EL DORADO PH-2101 | 152762101 | RECLOSER | 13532 | 20140812 | 1538 | 1065603 | 452 | Distribution Circuit | Vegetation | Tree - fell into line | 765 | 28448 | 38.773 | -120.2936 | WEST SIDE OF SW 6161 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0050624 | OH | Sus | 42169451 | No | 2014 | AUG | Yes | Three Phase Fault | 99212357 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1107 | 152561107 | FUSE | 8599 | 20140816 | 1318 | 1067337 | 752 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 3022 | 38.8087 | -121.141 | RENFREE-SAM/1505/530-906-2110: 8754 TUDSBURY | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0051367 | OH | Sus | 31095350 | No | 2014 | AUG | Yes |  | 99211832 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1110 | 152691110 | RECLOSER | 2408 | 20140819 | 1732 | 1068998 | 1591 | Distribution Circuit | Vegetation | Tree - fell into line | 443 | 100880 | 39.047 | -121.0489 | 1007532607 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0051906 | OH | Sus | 31096010 | No | 2014 | AUG | Yes | Line to Ground | 99211399 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 9503 | 20140826 | 231 | 1072974 | 645 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 30315 | 39.0559 | -120.998 | 2 SP N/O C/OUT 9503 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0053185 | OH | Sus | 31096994 | No | 2014 | AUG | Yes | Line to Line | 99210477 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE | 7571 | 20140904 | 625 | 1077024 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 6450 | 38.9988 | -120.8687 | RENFREE-SAM/1505/530-906-2110: 21045 MELODY CRT | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0054981 | OH | Sus | 31099041 | No | 2014 | SEP | Yes | Line to Line | 99209293 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21315 | 20140908 | 208 | 1078313 | 702 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 22056 | 38.6192 | -120.7646 | DERYK-KEVIN/621/530-386-5111: sw of 2500 sand ridge. | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0055553 | OH | Sus | 31099656 | No | 2014 | SEP | Yes | Line to Ground | 99208911 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1102 | 152491102 | RECLOSER | 2038 | 20140912 | 1628 | 1080498 | 583 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 9999 | 39.0316 | -121.0046 | 18847 PLACER HILLS RD | Clear-Above 90 F | Conductor, Overhead | Broken, wire on ground | 14-0056687 | OH | Sus | 31100972 | No | 2014 | SEP | Yes | Line to Ground | 99208206 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | RECLOSER | 19752 | 20140918 | 2316 | 1084348 | 548 | Distribution Circuit | Vegetation | Tree - fell into line | 1631 | 197337 | 38.7139 | -120.5836 | BEHIND ADDRESS WITH MTR # 1007652266 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0057930 | OH | Sus | 0 | yes | 2014 | SEP | Yes | Line to Line | 99207329 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | OLETA-1102 | 163541102 | FUSE | 20987 | 20141006 | 2113 | 1093808 | 917 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 1661 | 38.5495 | -120.747 | 6276 DEAN RD | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0061790 | OH | Sus | 31105797 | No | 2014 | OCT | Yes | Line to Ground | 99204687 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 9783 | 20141010 | 107 | 1095375 | 581 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 10458 | 39.1544 | -121.0653 | 10195 KENWOOD DR | Lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0062716 | OH | Sus | 42204290 | No | 2014 | OCT | Yes | Line to Ground | 99204157 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 7293 | 20141015 | 524 | 1097521 | 697 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3485 | 39.2315 | -121.1099 | STEPHENSON /1588/ 530-913-1482: 12693 ROUGH AND READY RD | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0063831 | OH | Sus | 31107560 | yes | 2014 | OCT | Yes | Line to Ground | 99203417 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1103 | 152561103 | RECLOSER | 604 | 20141015 | 705 | 1097578 | 191 | Distribution Circuit | Vegetation | Tree - fell into line | 307 | 19858 | 38.8544 | -121.1507 | MTR#1005556380 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0063720 | OH | Sus | 42209672 | yes | 2014 | OCT | Yes | Line to Ground | 99203481 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1101 | 152201101 | RECLOSER | 1720 | 20141015 | 821 | 1097726 | 1453 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 43590 | 39.4552 | -121.0529 | JIMENEZ-AL/1586/530-913-7963: 14444 PENDOLA RD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0063879 | OH | Sus | 31107600 | yes | 2014 | OCT | Yes | Line to Ground | 99203360 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1112 | 153081112 | FUSE | 7023 | 20141015 | 1133 | 1097891 | 507 | Distribution Circuit | 3rd Party | Vehicle | 169 | 20972 | 38.7196 | -120.7702 | DERYK-KEVIN/621/530-386-5111: near 4040 cedar ravine rd | Drizzle-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0063835 | OH | Sus | 31107569 | yes | 2014 | OCT | Yes | Line to Line | 99203414 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | OTHER |  | 20141017 | 1900 | 1098912 | 502 | Distribution Circuit | Equipment Failure/Involved | Other | 1219 | 122448 | 38.6423 | -120.7024 | MAINLINE at FUSE POLE 21135 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0064447 | OH | Sus | 42212504 | No | 2014 | OCT | Yes | Line to Ground | 99203109 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1350 | 20141103 | 853 | 1108425 | 467 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 880 | 36775 | 38.8933 | -120.9965 | 15 SPANS E/O SW 1105 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0067859 | OH | Sus | 31112475 | No | 2014 | NOV | Yes | Three Phase Fault | 99200643 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20141103 | 1019 | 1108496 | 745 | Distribution Circuit | 3rd Party | Vehicle | 913 | 140591 | 38.816 | -120.8219 | 2 W/O SW 1135 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0067888 | OH | Sus | 31112524 | No | 2014 | NOV | Yes | Line to Line | 99200542 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | BELL-1108 | 152701108 | FUSE | 8537 | 20141112 | 757 | 1111850 | 330 | Distribution Circuit | Vegetation | Tree - branch fell on line | 203 | 45342 | 38.9818 | -121.0732 | 1 SPAN LOADSIDE OF 9527 - MARY LANE - AUBURN | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0069473 | OH | Sus | 0 | No | 2014 | NOV | Yes | Line to Ground | 99199595 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1101 | 152271101 | FUSE | 5299 | 20141118 | 730 | 1114371 | 491 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 6383 | 38.8861 | -121.1032 | 3 SPANS E/O 5299 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0070612 | OH | Sus | 42275732 | No | 2014 | NOV | Yes | Line to Ground | 99198867 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 8273 | 20141122 | 2200 | 1116982 | 486 | Distribution Circuit | Equipment Failure/Involved | Other | 132 | 45947 | 38.9704 | -121.0551 | 1425 SHADOWROCK DR. | Rain-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0071653 | OH | Sus | 42280242 | No | 2014 | NOV | Yes | Line to Line | 99198159 | CSO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1110 | 152691110 | FUSE | 7489 | 20141126 | 818 | 1118361 | 339 | Distribution Circuit | 3rd Party | Vehicle | 31 | 10509 | 39.0798 | -121.0127 | 2 P/S/O 17681 RIVER RANCH RD- GRASS VALLEY MET# 1007533891 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0072149 | OH | Sus | 31117822 | No | 2014 | NOV | Yes | Line to Ground | 99197762 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9235 | 20141202 | 1305 | 1121069 | 803 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 45771 | 38.9217 | -120.896 | 7 SPAN LD SIDE OF 9235 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0073028 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99197123 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE | 6303 | 20141204 | 1424 | 1124687 | 673 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 23039 | 39.0898 | -120.9654 | 1170 OLD COLONY LN | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0073852 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99196432 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | FORESTHILL-1102 | 152181102 | OTHER |  | 20141206 | 2 | 1125668 | 508 | Distribution Circuit | Equipment Failure/Involved | Other | 111 | 59998 | 38.9879 | -120.9311 | 19005 forest hill rd | Drizzle-32 - 90 F | Other | Broken, wire on ground | 14-0074111 | OH | Sus | 31119761 | No | 2014 | DEC | Yes |  | 99196138 | NON | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1102 | 152291102 | OTHER |  | 20141213 | 1721 | 1140091 | 594 | Distribution Circuit | Equipment Failure/Involved | Other | 22 | 11316 | 39.3192 | -120.6199 | 1 SS OF 6703 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076822 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193283 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 77546 | 20141215 | 1153 | 1141264 | 166 | Distribution Circuit | Vegetation | Tree - branch fell on line | 422 | 58937 | 38.57 | -120.7323 | MTR# 1008911986 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077012 | OH | Sus | 42297932 | yes | 2014 | DEC | Yes | Line to Ground | 99192992 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2101 | 153132101 | OCB | OCB | 20141216 | 1109 | 1142163 | 361 | Distribution Circuit | Vegetation | Tree - fell into line | 7587 | 476416 | 39.2351 | -121.2692 | WILKINS-ARMANDO/1589/913-5057: SW 983 1 SPAN TO EAST | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077218 | OH | Sus | 31121481 | yes | 2014 | DEC | Yes | Line to Ground | 99192779 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 7023 | 20141218 | 658 | 1143428 | 319 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 21054 | 39.1269 | -121.0553 | JIMENEZ-AL/1586/530-913-7963: TREE FRM 17124 ALIOTO FELL ON LAWRENCE DR 17169 ONTO LINES | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077533 | OH | Sus | 42300621 | No | 2014 | DEC | Yes | Line to Ground | 99192426 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 20255 | 20141219 | 1623 | 1144698 | 434 | Distribution Circuit | Equipment Failure/Involved | Other | 2471 | 71390 | 38.6208 | -120.849 | 7841 HWY 49 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077749 | OH | Sus | 31122355 | No | 2014 | DEC | Yes | Line to Ground | 99192176 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 9075 | 20141224 | 1616 | 1147761 | 599 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 29950 | 39.1858 | -120.9722 | 13970 DAY SPRINGS RD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0078308 | OH | Sus | 42302872 | yes | 2014 | DEC | Yes | Line to Ground | 99191498 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | OCB | OCB | 20141226 | 203 | 1148543 | 684 | Distribution Circuit | Equipment Failure/Involved | Other | 1130 | 206784 | 39.3313 | -121.1016 | SS OF MTR# 1005514208 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078513 | OH | Sus | 31123367 | No | 2014 | DEC | Yes | Line to Ground | 99191255 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1101 | 152591101 | RECLOSER | 2304 | 20141227 | 1722 | 1149283 | 587 | Distribution Circuit | Equipment Failure/Involved | Other | 815 | 173603 | 39.3125 | -120.3811 | RENFREE-SAM/1505/530-906-2110: 2 SPANS N OF 6641 MAIN LINE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078670 | OH | Sus | 42303609 | No | 2014 | DEC | Yes | Line to Ground | 99191077 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | EL DORADO PH-2101 | 152762101 | RECLOSER | 36764 | 20141231 | 532 | 1156141 | 2178 | Distribution Circuit | Vegetation | Tree - fell into line | 765 | 456794 | 38.787 | -120.2058 | 1 POLE W/O 13362 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079667 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99189707 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2102 | 153132102 | FUSE | 32925 | 20150109 | 1428 | 1161697 | 454 | Distribution Circuit | 3rd Party | Vehicle | 126 | 57204 | 39.2527 | -121.2076 | AT FUCO 32943 POLE | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0003657 | OH | Sus | 31126956 | No | 2015 | JAN | Yes | Line to Ground | 99188618 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 7742 | 20150117 | 819 | 1165063 | 641 | Distribution Circuit | 3rd Party | Vehicle | 692 | 71039 | 38.6612 | -120.911 | STEELE-BRENT/624/530-906-3165: french creek rd near brandon rd shinlge springs | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0005330 | OH | Sus | 31128987 | No | 2015 | JAN | Yes | Line to Ground | 99187711 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1110 | 152691110 | FUSE | 7489 | 20150124 | 2148 | 1168117 | 1017 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 7167 | 39.0798 | -121.0127 | 1 SP LOAD SIDE OF MTR # 1009742879 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 15-0006933 | OH | Sus | 0 | No | 2015 | JAN | Yes | Line to Ground | 99186937 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 6623 | 20150201 | 1310 | 1170884 | 268 | Distribution Circuit | Equipment Failure/Involved | Other | 13 | 3484 | 38.6877 | -120.6381 | mtr#1007651002 | Clear-32 - 90 F | Insulator | Broken, wire on object | 15-0008569 | OH | Sus | 42325405 | No | 2015 | FEB | Yes | None | 99186037 | INS | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1101 | 152271101 | OCB | OCB | 20150203 | 1520 | 1171765 | 576 | Distribution Circuit | 3rd Party | Vehicle | 918 | 152294 | 38.8896 | -121.0987 | 5/N/OF 2205- 60 KV POLE 2/48 ON PLACER-DEL MAR 60KV LINE | Clear-32 - 90 F | Pole-Wood | Broken, wire on object | 15-0009127 | OH | Sus | 31132580 | No | 2015 | FEB | Yes | Line to Ground | 99182397 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 9881 | 20150222 | 2217 | 1194225 | 725 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 13775 | 39.0886 | -121.0847 | 2 LD SIDE OF MTR # 1003918373 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0014908 | OH | Sus | 42337300 | No | 2015 | FEB | Yes | Line to Line | 99180902 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | RECLOSER | 50070 | 20150223 | 205 | 1194267 | 804 | Distribution Circuit | Vegetation | Tree - fell into line | 451 | 93279 | 39.2754 | -121.0221 | WILKINS-ARMANDO/1589/913-5057: 5 SPANS LS C/O 33607 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0014910 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99180901 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1103 | 152031103 | RECLOSER | 2180 | 20150223 | 312 | 1194304 | 1030 | Distribution Circuit | Vegetation | Tree - fell into line | 489 | 111152 | 39.1531 | -121.077 | TASSONE-LOUIS/1262/682-6302: 19068 MCCOURTNEY RD | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0014912 | OH | Sus | 31136268 | yes | 2015 | FEB | Yes | Line to Ground | 99180899 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 34401 | 20150223 | 721 | 1194370 | 1831 | Distribution Circuit | Environmental/External | Ice or snow | 23 | 42113 | 39.3039 | -120.4179 | 7 SPANS LOAD SIDE | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on object | 15-0015150 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99180710 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 8511 | 20150225 | 1535 | 1195904 | 446 | Distribution Circuit | Equipment Failure/Involved | Other | 43 | 8594 | 38.8652 | -121.0191 | MTR#1004190467 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0015785 | OH | Sus | 31137016 | No | 2015 | FEB | Yes | Line to Ground | 99180431 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 5779 | 20150307 | 450 | 1200344 | 1465 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 20510 | 39.0942 | -121.0402 | 3 SPANS LOADSIDE OF 5779 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0017960 | OH | Sus | 0 | No | 2015 | MAR | Yes | Line to Line | 99179054 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 18677 | 20150308 | 1648 | 1200800 | 567 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 6 | 3402 | 38.6303 | -120.8211 | 2 SPANS LD SIDE OF FUSE 18677 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0018106 | OH | Sus | 0 | No | 2015 | MAR | Yes | Line to Ground | 99178952 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1103 | 153661103 | OTHER |  | 20150309 | 936 | 1201075 | 359 | Distribution Circuit | Animal | Bird found | 592 | 35991 | 38.729 | -120.7593 | ON MAIN LINE LD SIDE OF DDE POLE 11069 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 15-0018212 | OH | Sus | 42345354 | No | 2015 | MAR | Yes | Line to Ground | 99178854 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE | 6001 | 20150311 | 2231 | 1202443 | 503 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 25653 | 39.019 | -120.8613 | ? | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0019007 | OH | Sus | 31140749 | No | 2015 | MAR | Yes | Line to Ground | 99178494 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1107 | 152691107 | FUSE | 3161 | 20150311 | 1301 | 1202240 | 284 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 2272 | 39.0269 | -121.0676 | 11903 COMBIE RD | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0018923 | OH | Sus | 42348482 | No | 2015 | MAR | Yes | Line to Ground | 99178550 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 9372 | 20150311 | 1007 | 1202113 | 233 | Distribution Circuit | Vegetation | Tree - fell into line | 2047 | 110717 | 38.7137 | -120.9392 | LIZARRAGA-A/620/530-906-3131: luneman e/o el largo | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0018818 | OH | Sus | 42348325 | No | 2015 | MAR | Yes | Line to Ground | 99178570 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20150327 | 802 | 1208722 | 338 | Distribution Circuit | Equipment Failure/Involved | Other | 915 | 79481 | 38.816 | -120.8219 | 5920 MOUNT MURPHY RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0022460 | OH | Sus | 42358452 | No | 2015 | MAR | Yes | Line to Ground | 99176566 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | OTHER |  | 20150330 | 710 | 1209636 | 402 | Distribution Circuit | Equipment Failure/Involved | Other | 692 | 103729 | 38.6339 | -120.9102 | STEELE-BRENT/624/530-906-3165: 5221 big canyon rd shingle springs | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0022846 | OH | Sus | 0 | No | 2015 | MAR | Yes | Line to Ground | 99176304 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1103 | 152561103 | RECLOSER | 2198 | 20150331 | 644 | 1210495 | 369 | Distribution Circuit | Animal | Bird found | 434 | 52246 | 38.8637 | -121.1285 | 2901 RATTLESNAKE BAR RD | Clear-32 - 90 F | Conductor, Overhead | On Ground | 15-0023124 | OH | Sus | 31144749 | No | 2015 | MAR | Yes | Line to Ground | 99176127 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | BELL-1108 | 152701108 | OTHER |  | 20150402 | 1320 | 1211607 | 160 | Distribution Circuit | Animal | Bird found | 5 | 800 | 38.9992 | -121.1075 | MTR#1004802396 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0023848 | OH | Sus | 42361541 | No | 2015 | APR | Yes | Line to Ground | 99175652 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | OTHER |  | 20150404 | 1739 | 1212694 | 365 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 25798 | 39.042 | -120.9631 | 1 span source side of FUCO 8335 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0024214 | OH | Sus | 42362492 | No | 2015 | APR | Yes | Line to Ground | 99175407 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21313 | 20150405 | 1737 | 1213011 | 610 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4880 | 38.6203 | -120.7647 | HYLAND- TRAVIS: 1/p/s 3148 yearling trl | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0024281 | OH | Sus | 31145830 | No | 2015 | APR | Yes | Line to Ground | 99175332 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER | 808 | 20150407 | 1223 | 1215015 | 228 | Distribution Circuit | Environmental/External | Ice or snow | 906 | 94239 | 39.4882 | -120.8572 | 2 POLES N/OF 805 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0024930 | OH | Sus | 0 | yes | 2015 | APR | Yes | Line to Ground | 99174954 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 9847 | 20150407 | 1205 | 1214965 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2560 | 39.2854 | -120.9451 | MUELLER-ANDY/1585/530-863-6807: 18881 HWY 20 & 19000 SCOTTS FLAT RD- NEVADA CITY | Snow-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 15-0024936 | OH | Sus | 0 | yes | 2015 | APR | Yes | Line to Line | 99174949 | CAW | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8103 | 20150407 | 1152 | 1214937 | 562 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 9554 | 39.3597 | -121.1202 | 1 & 2 SPANS LOAD SIDE OF C/OUT'S | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0024990 | OH | Sus | 0 | yes | 2015 | APR | Yes | Line to Line | 99174928 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE | 4211 | 20150407 | 1121 | 1214878 | 443 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1772 | 39.1306 | -120.9455 | 26445 BARBWIRE LN | Snow-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0024895 | OH | Sus | 0 | yes | 2015 | APR | Yes | Line to Line | 99174970 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 96011 | 20150412 | 1107 | 1217866 | 863 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 103560 | 38.8988 | -120.8591 | 1/S/OF 4103 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0026078 | OH | Sus | 31147656 | No | 2015 | APR | Yes | Line to Ground | 99173992 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 8143 | 20150424 | 759 | 1224114 | 244 | Distribution Circuit | Vegetation | Tree - branch fell on line | 128 | 15150 | 38.6793 | -120.8878 | TAP LINE TO MTR #1006545188 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0029152 | OH | Sus | 31150623 | yes | 2015 | APR | Yes | Line to Ground | 99172096 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 12945 | 20150427 | 1149 | 1225754 | 348 | Distribution Circuit | Vegetation | Tree - fell into line | 114 | 25922 | 38.7356 | -120.7865 | 2665 MORRENE DR.- PLACERVILLE | Clear-32 - 90 F | Pole-Wood | Broken, wire on object | 15-0029850 | OH | Sus | 31151146 | No | 2015 | APR | Yes | Line to Ground | 99171508 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | FUSE | 5359 | 20150430 | 917 | 1227308 | 228 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 6774 | 38.8843 | -121.1543 | 489 UNCLE JOES LN. | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0030738 | OH | Sus | 42378756 | No | 2015 | APR | Yes | Line to Ground | 99170969 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1107 | 152481107 | FUSE | 32613 | 20150507 | 339 | 1230259 | 446 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 15610 | 39.2262 | -121.0672 | WILKINS-ARMANDO/1589/913-5057: 11585 ALTA VISTA C/O 32613 | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 15-0032359 | OH | Sus | 42382590 | yes | 2015 | MAY | Yes | Line to Line | 99170037 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHADY GLEN-1101 | 152431101 | OCB | OCB | 20150507 | 1142 | 1230778 | 582 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1930 | 337351 | 39.1154 | -120.9534 | SOUTH WEST SIDE OF 6215 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0032524 | OH | Sus | 0 | yes | 2015 | MAY | Yes | Line to Line | 99169904 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | OCB | OCB | 20150509 | 1310 | 1232020 | 1051 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3926 | 382926 | 39.2355 | -121.2692 | TASSONE-LOUIS/1262/682-6302: BYOND 51580 | Lightning-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0033085 | OH | Sus | 31153882 | No | 2015 | MAY | Yes | Three Phase Fault | 99169400 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 9717 | 20150511 | 1631 | 1232873 | 704 | Distribution Circuit | 3rd Party | Vehicle | 11 | 7744 | 39.1977 | -121.0521 | MTR#1007521342 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0033421 | OH | Sus | 31154220 | No | 2015 | MAY | Yes | Three Phase Fault | 99169212 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE | 33279 | 20150527 | 2144 | 1240374 | 854 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 10828 | 39.1679 | -120.9658 | 1 POLE S/S OF MTR at 1009283757 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0036850 | OH | Sus | 31157512 | No | 2015 | MAY | Yes | Line to Ground | 99166567 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 21599 | 20150604 | 2000 | 1243842 | 580 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 55 | 9640 | 38.6916 | -120.8606 | 6050 GOLD MEADOW RD - PLACERVILLE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0038597 | OH | Sus | 31159231 | No | 2015 | JUN | Yes | Line to Ground | 99165562 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8233 | 20150606 | 1720 | 1244928 | 530 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 9420 | 39.3426 | -121.0616 | 22484 PURDON RD - MTR# 1007600986 | Lightning-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0039066 | OH | Sus | 0 | No | 2015 | JUN | Yes | Line to Line | 99165216 | PW | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 7899 | 20150615 | 935 | 1251087 | 284 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 6660 | 39.1218 | -121.054 | S1 SPAN LOADSIDE OF MTR#1007546161 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0041054 | OH | Sus | 31161388 | No | 2015 | JUN | Yes | Line to Ground | 99163571 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1102 | 152491102 | FUSE | 6175 | 20150618 | 103 | 1252567 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 23293 | 39.0361 | -121.0041 | HART-EMMETT/1506/530-906-2031: 1330 Pleasant Ridge Rd | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0041774 | OH | Sus | 31161971 | No | 2015 | JUN | Yes | Line to Line | 99163129 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | RECLOSER | 32120 | 20150622 | 1158 | 1254645 | 462 | Distribution Circuit | Vegetation | Tree - fell into line | 2040 | 148438 | 39.105 | -121.085 | FUCO 32721 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0042502 | OH | Sus | 31162887 | No | 2015 | JUN | Yes | Line to Ground | 99162530 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1112 | 153081112 | FUSE | 5277 | 20150623 | 2344 | 1255533 | 677 | Distribution Circuit | Vegetation | Tree - branch fell on line | 52 | 35204 | 38.7342 | -120.8189 | 2 P/NE/O 268 MIDDLETOWN RD- PLACERVILLE | Overcast-32 - 90 F | Crossarm, Wood | Broken, wire on object | 15-0042947 | OH | Sus | 31163614 | No | 2015 | JUN | Yes | Line to Line | 99162257 | CAW | OH | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1104 | 152481104 | FUSE | 7133 | 20150627 | 2115 | 1257927 | 421 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4210 | 39.2698 | -121.0431 | 1 SPAN N/O MTR # 1009283557 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0043789 | OH | Sus | 42416770 | No | 2015 | JUN | Yes | Line to Ground | 99161595 | CO | OH | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2102 | 153132102 | FUSE | 7251 | 20150629 | 2213 | 1259023 | 532 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 28500 | 39.2632 | -121.1989 | SATTERLEE-M/1531/530-320-4435: primary nuetral down crew to repair | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 15-0044120 | OH | Sus | 42417355 | No | 2015 | JUN | Yes | Line to Ground | 99161282 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 4489 | 20150630 | 710 | 1259102 | 455 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 18800 | 38.9142 | -120.9384 | 2643 CASCADE TRAIL | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0044177 | OH | Sus | 31165056 | yes | 2015 | JUN | Yes | Line to Ground | 99161240 | CSO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 5831 | 20150704 | 2203 | 1263026 | 589 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 30628 | 38.849 | -120.8684 | TWO SPANS DOWN LD SIDE OF 5831 | Partly Cloudy-Above 90 | Conductor, Overhead | On Ground | 15-0045531 | OH | Sus | 42420843 | No | 2015 | JUL | Yes | Line to Ground | 1143882 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | OTHER | HOT WIRE DOWN @ 16782 GEORGE WAY | 20150707 | 1042 | 1264245 | 280 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2686 | 46738 | 39.1139 | -121.0653 | 16782 GEORGE WAY | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0045985 | OH | Sus | 0 | yes | 2015 | JUL | Yes | Line to Ground | 1144194 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | RECLOSER | 97086 | 20150722 | 1421 | 1275603 | 842 | Distribution Circuit | Vegetation | Tree - fell into line | 443 | 149206 | 38.7654 | -120.704 | 1 P S/O 12641 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 15-0049908 | OH | Sus | 0 | yes | 2015 | JUL | Yes | Line to Line | 1147135 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 9547 | 20150728 | 2306 | 1279067 | 675 | Distribution Circuit | 3rd Party | Vehicle | 202 | 116750 | 39.1035 | -121.0438 | 18273 WOLFCREEK RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0051139 | OH | Sus | 31172396 | No | 2015 | JUL | Yes | Line to Line | 1147992 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 4667 | 20150816 | 1844 | 1289534 | 485 | Distribution Circuit | 3rd Party | Vehicle | 35 | 6382 | 38.6905 | -120.7431 | MTR# 1006709350 | Clear-Above 90 | Pole-Wood | Broken, wire on ground | 15-0055379 | OH | Sus | 0 | yes | 2015 | AUG | Yes | Line to Ground | 1150999 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 95765 | 20150817 | 1352 | 1290343 | 309 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2472 | 38.9896 | -121.0235 | 2 SPANS LOADSIDE OF 95765 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 15-0055600 | OH | Sus | 31176604 | yes | 2015 | AUG | Yes | Line to Ground | 1151173 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | JUMPER | WIRE DOWN SS OF 7257 | 20150821 | 1204 | 1292553 | 454 | Distribution Circuit | Vegetation | Tree - fell into line | 1015 | 85174 | 39.2107 | -121.1622 | SS OF FUSE 7257 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0056597 | OH | Sus | 31178066 | No | 2015 | AUG | Yes | Line to Ground | 1151801 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | SECTIONALIZER | 1762 | 20150822 | 33 | 1292835 | 1020 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 594 | 229498 | 39.0184 | -120.8293 | HATTRUP-JIM/1533/530-906-2888: arrestor appears to have put 12 kv to ground wire started butt on fir | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0056681 | OH | Sus | 31178213 | No | 2015 | AUG | Yes | Three Phase Fault | 1151852 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 7357 | 20150825 | 117 | 1294036 | 711 | Distribution Circuit | 3rd Party | Vehicle | 37 | 26307 | 39.2407 | -120.9823 | JIMENEZ-AL/1586/530-913-7963: 13000 REDWOOD PL | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0057086 | OH | Sus | 0 | No | 2015 | AUG | Yes | Line to Ground | 1152144 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-1104 | 153651104 | FUSE | 22311 | 20150906 | 2301 | 1301083 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4928 | 38.6061 | -120.9564 | 1 P E/O MTR#1007476559 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 15-0059622 | OH | Sus | 0 | No | 2015 | SEP | Yes | Line to Line | 1153988 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1105 | 152561105 | FUSE | 48359 | 20150909 | 1627 | 1302570 | 390 | Distribution Circuit | 3rd Party | Vehicle | 1 | 390 | 38.8796 | -121.1701 | 1 POLE LD SIDE OF 48359 | Clear-Above 90 | Pole-Wood | Broken, wire on ground | 15-0060267 | OH | Sus | 31182832 | yes | 2015 | SEP | Yes | Line to Ground | 1154405 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1101 | 152201101 | JUMPER | OJ 1 SPAN SS OF MTR # 1007742509 | 20150914 | 936 | 1305320 | 609 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 609 | 39.4598 | -121.0435 | 1 SPAN LD SIDE OF MTR # 1007742509 - | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0061234 | OH | Sus | 31184546 | yes | 2015 | SEP | Yes | Line to Ground | 1155099 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE | 5737 | 20150923 | 549 | 1310603 | 506 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2024 | 39.2595 | -121.0272 | TASSONE-LOUIS/1262/682-6302: 3 POLE ABOVE 3757 FUSE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0062836 | OH | Sus | 31186282 | No | 2015 | SEP | Yes | Three Phase Fault | 1156347 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 1499 | 20150930 | 1725 | 1314445 | 608 | Distribution Circuit | Vegetation | Tree - fell into line | 179 | 28912 | 38.5936 | -120.6608 | 1 N/OF & 1 W/OF MTR # 1007388276 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | On Ground | 15-0066934 | OH | Sus | 0 | No | 2015 | SEP | Yes | Line to Ground | 1159884 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | CLARKSVILLE-2104 | 153612104 | FUSE | 12147 | 20151001 | 445 | 1314604 | 574 | Distribution Circuit | 3rd Party | Vehicle | 55 | 13178 | 38.7523 | -121.0509 | 8 NE/OF 22671 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 15-0066997 | OH | Sus | 0 | yes | 2015 | OCT | Yes | Line to Line | 1159952 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 32333 | 20151003 | 2345 | 1316376 | 555 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1110 | 38.8566 | -120.8523 | 3661 BAY LEAF RD GARDEN VALLEY | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 15-0067714 | OH | Sus | 42489057 | yes | 2015 | OCT | Yes | Line to Ground | 1160484 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 4785 | 20151007 | 2038 | 1318525 | 633 | Distribution Circuit | 3rd Party | Vehicle | 70 | 40572 | 39.255 | -120.9511 | MTR#1009122990 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0068777 | OH | Sus | 31189269 | No | 2015 | OCT | Yes | Line to Line | 1161225 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | FORESTHILL-1102 | 152181102 | FUSE | 6047 | 20151007 | 1752 | 1318457 | 600 | Distribution Circuit | 3rd Party | Vehicle | 7 | 4200 | 38.9808 | -120.9403 | 5 SP S/W OF 35381 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0068767 | OH | Sus | 0 | No | 2015 | OCT | Yes | Line to Line | 1161217 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BELL-1107 | 152701107 | FUSE | 5751 | 20151009 | 1412 | 1319379 | 413 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1901 | 38.9555 | -121.1354 | MTR#1004246313 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 15-0069296 | OH | Sus | 31190209 | No | 2015 | OCT | Yes | Line to Ground | 1161545 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 99251 | 20151028 | 1013 | 1330337 | 367 | Distribution Circuit | Vegetation | Tree - branch fell on line | 290 | 7646 | 38.827 | -120.8449 | SATTERLEE-M/1531/530-320-4435: 2/2blwn at 99251-1 span#2 ACSR down&N.G. TX-tree branch | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0073837 | OH | Sus | 0 | No | 2015 | OCT | Yes | Line to Line | 1165000 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1103 | 152561103 | FUSE | 151597 | 20151029 | 714 | 1330817 | 330 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 330 | 38.8544 | -121.1433 | HART-EMMETT/1506/530-906-2031: 8695 Gilard Rd | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 15-0073992 | OH | Sus | 31196052 | No | 2015 | OCT | Yes | Line to Ground | 1165126 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 61892 | 20151102 | 1526 | 1333732 | 304 | Distribution Circuit | Equipment Failure/Involved | Overhead | 394 | 30542 | 38.7122 | -120.9498 | STEELE-BRENT/624/530-906-3165: 2893 jay hawk rescue | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0074999 | OH | Sus | 0 | yes | 2015 | NOV | Yes | Line to Ground | 1165948 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1103 | 152561103 | FUSE | 47871 | 20151115 | 1422 | 1342125 | 901 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3604 | 38.8332 | -121.1025 | RENFREE-SAM/1505/530-906-2110: 47871 | Partly Cloudy-Drizzle-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0077943 | OH | Sus | 0 | yes | 2015 | NOV | Yes | Line to Ground | 1168426 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | RECLOSER | 32120 | 20151116 | 1337 | 1343429 | 828 | Distribution Circuit | Vegetation | Tree - fell into line | 1337 | 215475 | 39.105 | -121.085 | 2 P/E/O 9737 FUCO | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0078391 | OH | Sus | 0 | yes | 2015 | NOV | Yes | Line to Ground | 1168847 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 7709 | 20151116 | 822 | 1342941 | 890 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 12290 | 39.0744 | -121.007 | 20341 GUN STOCK | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0078273 | OH | Sus | 0 | yes | 2015 | NOV | Yes | Line to Ground | 1168760 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 32419 | 20151203 | 1421 | 1353028 | 750 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 6000 | 38.8684 | -120.8541 | SATTERLEE-M/1531/530-320-4435: 2-2blwn at 32419-primary conductor down-crew to repair | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082573 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1172243 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1110 | 153081110 | FUSE | 11417 | 20151204 | 2114 | 1354121 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 42888 | 38.7419 | -120.8174 | FLECKLIN-PAUL/623/530-906-3142: 2577 BRYAN CRT | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082899 | OH | Sus | 42583437 | No | 2015 | DEC | Yes | Line to Ground | 1172482 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1112 | 153081112 | FUSE | 12721 | 20151204 | 839 | 1353628 | 264 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 1986 | 38.7179 | -120.754 | Texas Hill Rd 1mi E/Cedar Ravine Rd | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0082712 | OH | Sus | 42583071 | No | 2015 | DEC | Yes | Line to Ground | 1172364 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 34485 | 20151205 | 314 | 1354147 | 970 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 55715 | 39.1233 | -121.0613 | 6 SPANS LD SIDE OF C/OUT'S | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0082913 | OH | Sus | 31204368 | No | 2015 | DEC | Yes | Line to Line | 1172496 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1104 | 152481104 | RECLOSER | 1020 | 20151208 | 1414 | 1355773 | 311 | Distribution Circuit | Vegetation | Tree - fell into line | 457 | 76950 | 39.2471 | -121.0378 | 1 SPAN N/O 6283 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083434 | OH | Sus | 42585393 | No | 2015 | DEC | Yes | Line to Ground | 1173058 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 5171 | 20151210 | 650 | 1357183 | 671 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4026 | 39.2695 | -120.9922 | 11300 LITTLE VALLEY RD | Overcast-Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083948 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1173591 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | OCB | 2101/2 | 20151210 | 706 | 1357228 | 623 | Distribution Circuit | Vegetation | Tree - fell into line | 4604 | 196593 | 38.7934 | -120.62 | 6740 RIDGEWAY | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 15-0083843 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Multi-Fault | 1173483 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 4281 | 20151210 | 701 | 1357223 | 149 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 21048 | 39.0915 | -121.0564 | RENFREE-SAM/1505/530-906-2110: 13330 lodestar rd | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083862 | OH | Sus | 31205344 | yes | 2015 | DEC | Yes | Line to Ground | 1173501 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | JUMPER | HOT WIRE DOWN 5 SPANS LD SIDE OF 5247 | 20151210 | 514 | 1357202 | 747 | Distribution Circuit | Vegetation | Tree - fell into line | 3934 | 81522 | 39.2006 | -121.2327 | 4 SPANS S/O 5247 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083829 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1173469 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 5859 | 20151210 | 737 | 1357326 | 603 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 9045 | 38.8531 | -120.7892 | 2 SPANS SOUTH OF 6923 | Strong Winds-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 15-0083891 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1173534 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1104 | 152481104 | RECLOSER | 1020 | 20151221 | 2225 | 1368330 | 482 | Distribution Circuit | Equipment Failure/Involved | Overhead | 457 | 56825 | 39.2471 | -121.0378 | TASSONE-LOUIS/1262/682-6302: 406 OLD DOWNIEVILLE HWY ACCESS OFF MONROE ST | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 15-0086550 | OH | Sus | 31208102 | yes | 2015 | DEC | Yes | Three Phase Fault | 1176544 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2102 | 153132102 | RECLOSER | 48484 | 20151221 | 1508 | 1368025 | 958 | Distribution Circuit | Vegetation | Tree - fell into line | 596 | 175283 | 39.2544 | -121.1459 | 1 LD SIDE OF 51321 - MID SPAN | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086468 | OH | Sus | 31208061 | yes | 2015 | DEC | Yes | Three Phase Fault | 1176462 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 12613 | 20151221 | 1351 | 1367911 | 709 | Distribution Circuit | Vegetation | Tree - branch fell on line | 102 | 47295 | 38.7943 | -120.7332 | 2 P N/OF MTR# 1009727075 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086457 | OH | Sus | 0 | yes | 2015 | DEC | Yes | None | 1176451 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 3785 | 20151222 | 1929 | 1369968 | 1133 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5665 | 39.0049 | -121.0161 | 1155 WALGRA MEADOWS MEADOW VISTA | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 15-0086920 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1176950 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 3603 | 20151225 | 2350 | 1371913 | 829 | Distribution Circuit | 3rd Party | Vehicle | 9 | 7461 | 39.1953 | -121.0238 | 3 LD SIDE OF 3603 | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 15-0087403 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Line | 1177483 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 18979 | 20160107 | 706 | 1379287 | 665 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4431 | 38.6236 | -120.8498 | MTR 1007480690 | Overcast-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 16-0003712 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Multi-Fault | 1179193 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | DRUM-1101 | 152321101 | OTHER | 1611 | 20160107 | 1234 | 1379747 | 238 | Distribution Circuit | Equipment Failure/Involved | Overhead | 196 | 20128 | 39.257 | -120.7662 | 13 SPANS SS/OF 34807 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003863 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1179319 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 22391 | 20160113 | 453 | 1382537 | 537 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4296 | 38.7741 | -120.5923 | 1 SPAN SOUTH AND 2 SPANS WEST OF MTR 1005208499 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0004957 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1180236 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1101 | 152591101 | OTHER | WIRE DOWN | 20160113 | 513 | 1382837 | 597 | Distribution Circuit | Equipment Failure/Involved | Overhead | 287 | 103131 | 39.3191 | -120.4434 | 6 POLES WEST OF FUCO 6661 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0005045 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1180300 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11547 | 20160117 | 2358 | 1385822 | 962 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 5092 | 38.6779 | -120.9432 | 3840 WELKER LN | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0005984 | OH | Sus | 42612984 | yes | 2016 | JAN | Yes | Line to Ground | 1180951 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 7202 | 20160118 | 221 | 1385861 | 552 | Distribution Circuit | Vegetation | Tree - fell into line | 1218 | 183598 | 38.6426 | -120.7007 | BETWEEN 11655 & 22755 ON MAIN LINE | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0005989 | OH | Sus | 42613062 | yes | 2016 | JAN | Yes | Three Phase Fault | 1180957 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 18935 | 20160118 | 944 | 1386086 | 191 | Distribution Circuit | Vegetation | Tree - fell into line | 187 | 35717 | 38.6728 | -120.8939 | SAMANIEGO-S/626/530-906-3122: 5010 mother lode | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006048 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1181017 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 6875 | 20160118 | 625 | 1385929 | 855 | Distribution Circuit | Equipment Failure/Involved | Overhead | 262 | 35268 | 39.1046 | -121.0589 | TASSONE-LOUIS/1262/682-6302: ANAONA | Partly Cloudy-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006016 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1180985 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20160118 | 838 | 1386057 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 1014 | 74283 | 38.8155 | -120.8221 | HATTRUP-JIM/1533/530-906-2888: Main lline at CO 31113 & CO 31111 | Partly Cloudy-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006038 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1181007 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9387 | 20160119 | 928 | 1387003 | 808 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 47888 | 38.9237 | -120.9073 | 1 S SS OF 40369 | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006365 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1181257 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 4585 | 20160119 | 946 | 1387055 | 644 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 12880 | 39.1869 | -121.1866 | 11475 ELNORA DR | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006341 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1181241 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | CLARKSVILLE-2104 | 153612104 | FUSE | 63453 | 20160123 | 747 | 1390585 | 417 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 834 | 38.7444 | -121.0601 | 1061 SALMON FALLS RD- EL DORADO HILLS | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007726 | OH | Sus | 42616349 | yes | 2016 | JAN | Yes | Line to Ground | 1182224 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 18843 | 20160125 | 451 | 1391450 | 531 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 7434 | 38.5358 | -120.6969 | 2 poles s/o 3780 Bridgeport School Rd | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0007925 | OH | Sus | 0 | No | 2016 | JAN | Yes | Line to Line | 1182435 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | RECLOSER | 97086 | 20160211 | 1106 | 1401901 | 435 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 444 | 79673 | 38.7653 | -120.7047 | 3220 HIGH GATE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0012049 | OH | Sus | 42629716 | No | 2016 | FEB | Yes | Line to Ground | 1185459 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 10025 | 20160214 | 1327 | 1403167 | 575 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 7878 | 38.5352 | -120.6993 | SS OF MTR # 5000023067 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0012556 | OH | Sus | 0 | No | 2016 | FEB | Yes | Line to Ground | 1185765 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | FUSE | 4109 | 20160214 | 1358 | 1403197 | 579 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 16212 | 39.0838 | -121.1142 | TASSONE-LOUIS/1262/682-6302: VINLEE PL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0012560 | OH | Sus | 0 | No | 2016 | FEB | Yes | Line to Ground | 1185769 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 11661 | 20160215 | 1742 | 1403739 | 509 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 62 | 31558 | 38.5544 | -120.7286 | FLECKLIN-PAUL/623/530-906-3142: 8181 MT AUKUM RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0012670 | OH | Sus | 31219397 | No | 2016 | FEB | Yes | Line to Ground | 1185883 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 12025 | 20160218 | 151 | 1407710 | 1252 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 132712 | 38.6276 | -120.7439 | CONTRERAS- TEAGUE: 3346 sand ridge rd | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013641 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186718 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 18843 | 20160218 | 1331 | 1408531 | 680 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 9520 | 38.5358 | -120.6969 | MTR 1007197051 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013939 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186894 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 6779 | 20160218 | 942 | 1408154 | 558 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 558 | 39.315 | -120.9646 | FIRST SPAN LD SIDE OF 6779 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013826 | OH | Sus | 31219754 | yes | 2016 | FEB | Yes | Line to Ground | 1186841 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 22825 | 20160218 | 502 | 1408471 | 1194 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2388 | 38.6359 | -120.5257 | 1 SPAN LD SIDE OF C/OUTS | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013924 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186889 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1110 | 153081110 | OTHER | WIRE DOWN | 20160218 | 742 | 1407977 | 792 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 6336 | 38.7288 | -120.8041 | AT MET# 1007650620 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 16-0013792 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186822 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 18229 | 20160228 | 2219 | 1413408 | 457 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 6057 | 38.785 | -120.9558 | 1060 SPRING CREST CRT | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0016130 | OH | Sus | 42642320 | No | 2016 | FEB | Yes | Line to Line | 1188505 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 1053 | 20160306 | 332 | 1421421 | 908 | Distribution Circuit | Vegetation | Tree - fell into line | 71 | 38628 | 38.6532 | -120.6273 | MTR#1007197028 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018417 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190261 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7045 | 20160306 | 1612 | 1422404 | 1293 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2586 | 39.193 | -121.009 | 11731 STATE HIGHWAY 174 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018549 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190388 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 2500 | 20160306 | 731 | 1421362 | 1869 | Distribution Circuit | Vegetation | Tree - fell into line | 348 | 345421 | 38.8236 | -120.0305 | 1. WIRE ON ARM 16 S/E/OF 4563 2. 1 SPAN E/O 2609 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 16-0018305 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190167 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1105 | 152561105 | FUSE | 5557 | 20160306 | 205 | 1420955 | 492 | Distribution Circuit | Vegetation | Tree - branch fell on line | 74 | 36408 | 38.8595 | -121.1567 | SISLEY RD & ORANGE HILL LN | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018204 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190073 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1105 | 152561105 | FUSE | 69443 | 20160306 | 551 | 1421151 | 548 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 14888 | 38.8649 | -121.1526 | 1700 GOULART RANCH ROAD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018377 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190228 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER | 804 | 20160307 | 1119 | 1423871 | 3123 | Distribution Circuit | Equipment Failure/Involved | Overhead | 600 | 173413 | 39.5598 | -120.8239 | 2 P/E/O FUCO 31311 | Strong Winds-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 16-0018936 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190710 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1102 | 152301102 | JUMPER | WIRE DOWN NEAR MTR#1004891071 | 20160307 | 348 | 1423347 | 742 | Distribution Circuit | Equipment Failure/Involved | Other | 437 | 91840 | 39.2016 | -120.8178 | MAINLINE at MTR# 1004891071 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018790 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190614 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 30711 | 20160307 | 612 | 1423343 | 665 | Distribution Circuit | Vegetation | Tree - branch fell on line | 86 | 50879 | 39.2145 | -120.8088 | RAND-DAN/1508/530-913-6400: west of c/o 9593 alta | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 16-0018811 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190626 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE | 7161 | 20160307 | 413 | 1423171 | 784 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 54488 | 39.2082 | -120.998 | 1 P/LD SIDE OF MET# 1007534345 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018751 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190586 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE | 7005 | 20160307 | 545 | 1423224 | 311 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 12227 | 39.2131 | -121.0136 | SUSPECT BEYOND 7011/ RELATED TO OUTAGE 1423171/1 P/LD SIDE OF MET# 1007534345 | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 16-0018776 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190599 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7025 | 20160307 | 526 | 1423195 | 652 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 51508 | 39.1988 | -121.0104 | 12847 BURMA RD- 1 P/W/O 7061 FUCO | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 16-0018724 | OH | Sus | 31223007 | yes | 2016 | MAR | Yes | Line to Ground | 1190565 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1102 | 152201102 | OTHER | WIRE DOWN 7 P/S/OF 8801 | 20160307 | 942 | 1424432 | 923 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 24921 | 39.4866 | -120.995 | 7 P/S/O 8801 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0019027 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190775 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | RECLOSER | 2054 | 20160307 | 421 | 1423143 | 462 | Distribution Circuit | Vegetation | Tree - branch fell on line | 210 | 52874 | 38.8963 | -121.1201 | at 5597 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018684 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190527 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1102 | 152101102 | FUSE | 8021 | 20160310 | 1100 | 1426468 | 11718 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 105462 | 39.4628 | -120.8506 | KANATAN AT CREEK CROSSING/NEAR CREEK - ENTER at CUSTOMER GATE | Overcast-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0019970 | OH | Sus | 42654875 | yes | 2016 | MAR | Yes | Line to Ground | 1191543 | CSO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1110 | 152691110 | FUSE | 7489 | 20160311 | 1418 | 1427929 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 4152 | 39.0798 | -121.0125 | 2 E/O 18176 RIVER RD | Partly Cloudy-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 16-0020476 | OH | Sus | 31224540 | yes | 2016 | MAR | Yes | Line to Ground | 1191874 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | RECLOSER | 2058 | 20160312 | 448 | 1429035 | 562 | Distribution Circuit | Vegetation | Tree - fell into line | 403 | 54770 | 39.0444 | -120.9858 | HARD TAP 1 N/OF 34017 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020716 | OH | Sus | 31224603 | yes | 2016 | MAR | Yes | Line to Ground | 1192098 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | ALLEGHANY-1101 | 152101101 | RECLOSER | 978 | 20160313 | 1843 | 1430508 | 4489 | Distribution Circuit | Environmental/External | Ice or snow | 199 | 318324 | 39.608 | -120.6068 | FLOATER 3 SP/LD/SIDE OF SBCO 31923WIRE DOWN 2 SP/LD/SIDE OF 7925- WIRE DOWN 4 SP/LD/SIDE OF 7971- WI | Sleet or Ice-Snow-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021069 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192435 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 20869 | 20160313 | 929 | 1430000 | 450 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2250 | 38.7605 | -120.5091 | 1 AND 2 SPAND LD SIDE OF MTR # 1006624921 | Overcast-Fog-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0020923 | OH | Sus | 31224751 | yes | 2016 | MAR | Yes | Line to Line | 1192301 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SPAULDING-1101 | 152251101 | FUSE | 9221 | 20160313 | 1557 | 1430357 | 582 | Distribution Circuit | Environmental/External | Ice or snow | 40 | 23280 | 39.3009 | -120.661 | JOHNSTON-M/1508/530-906-5563: 12 spans n/o co 9221 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021019 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1192391 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6631 | 20160313 | 1007 | 1430039 | 849 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 50811 | 39.32 | -120.4408 | 6 S/OF & 2 E/OF 6631 - ON TAMARACK CRESENT | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 16-0020906 | OH | Sus | 42655928 | yes | 2016 | MAR | Yes | Three Phase Fault | 1192290 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 2057 | 20160314 | 11 | 1430791 | 954 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 43407 | 38.678 | -120.7615 | MTR 1008988808 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0021124 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Three Phase Fault | 1192493 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1103 | 152561103 | JUMPER | WIREDOWN | 20160314 | 2116 | 1431569 | 479 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 7178 | 38.8532 | -121.1528 | BET MAINLINE AND 5247 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021479 | OH | Sus | 31225124 | yes | 2016 | MAR | Yes | Line to Ground | 1192766 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 7319 | 20160314 | 935 | 1431033 | 467 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 15411 | 38.7111 | -120.944 | BETWEEN 1 & 2ND POLE LD SIDE OF 7319 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021207 | OH | Sus | 31225005 | yes | 2016 | MAR | Yes | Line to Line | 1192565 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2105 | 153652105 | FUSE | 10331 | 20160315 | 1430 | 1432042 | 216 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 6912 | 38.6738 | -120.9578 | SS C/OUT 10331 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021710 | OH | Sus | 0 | No | 2016 | MAR | Yes | Line to Line | 1192913 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 5793 | 20160316 | 701 | 1432352 | 355 | Distribution Circuit | Animal | Bird found | 79 | 28045 | 39.0048 | -121.0352 | 2181 HIDDEN ACRES | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021810 | OH | Sus | 42658464 | No | 2016 | MAR | Yes | Multi-Fault | 1193013 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | RECLOSER | 9712 | 20160321 | 1533 | 1435452 | 703 | Distribution Circuit | Vegetation | Tree - fell into line | 1506 | 55296 | 38.8326 | -120.8178 | 2 SPANS BEYOND FUCO 31155 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0023052 | OH | Sus | 31226571 | yes | 2016 | MAR | Yes | Line to Ground | 1193893 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 7742 | 20160325 | 641 | 1438325 | 339 | Distribution Circuit | Equipment Failure/Involved | Overhead | 694 | 138371 | 38.6615 | -120.9109 | SAMANIEGO-S/626/530-906-3122: 4-spans n/e of19930 off big canyon | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0023926 | OH | Sus | 42663085 | No | 2016 | MAR | Yes | Line to Ground | 1194549 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 44383 | 20160327 | 1447 | 1439418 | 599 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 599 | 38.8995 | -120.9151 | END OF LINE LD SIDE OF FU 44383 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0024243 | OH | Sus | 42663590 | No | 2016 | MAR | Yes | Line to Ground | 1194814 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2102 | 153132102 | FUSE | 7239 | 20160329 | 1450 | 1441093 | 346 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 30 | 10380 | 39.242 | -121.1116 | 2 SPANS LD SIDE OF 7239/ 10910 BITNEY SPRINGS RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0024854 | OH | Sus | 31227994 | No | 2016 | MAR | Yes | Line to Line | 1195244 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 7742 | 20160409 | 1152 | 1447725 | 447 | Distribution Circuit | Equipment Failure/Involved | Overhead | 694 | 139194 | 38.6615 | -120.9109 | SAMANIEGO-S/626/530-906-3122: 5221 big canyon | Overcast-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0027450 | OH | Sus | 31230231 | yes | 2016 | APR | Yes | Line to Ground | 1197038 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 20269 | 20160410 | 755 | 1448100 | 652 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 3020 | 38.589 | -120.8423 | JESSEE-BEN /620/ 916-826-8237: PRETTY PENNY LAND | Partly Cloudy-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0027571 | OH | Sus | 42675732 | No | 2016 | APR | Yes | Line to Ground | 1197155 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 41187 | 20160410 | 1202 | 1448240 | 242 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 35 | 3130 | 38.6787 | -120.7707 | SAMANIEGO-S/626/530-906-3122: 4800 oak hill | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0027593 | OH | Sus | 42675736 | No | 2016 | APR | Yes | Line to Ground | 1197180 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | LINCOLN-1101 | 153701101 | FUSE | 9181 | 20160410 | 220 | 1448055 | 546 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 7530 | 38.8961 | -121.2193 | 4680 UPSON DOWN RD. | Partly Cloudy-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0027557 | OH | Sus | 31230303 | No | 2016 | APR | Yes | Line to Ground | 1197140 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 18841 | 20160411 | 607 | 1448584 | 492 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 10044 | 38.5729 | -120.6568 | 5 S/OF MTR# 1007202904 | Partly Cloudy-Fog-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0027676 | OH | Sus | 31230456 | No | 2016 | APR | Yes | Line to Ground | 1197265 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1346 | 20160414 | 1940 | 1451010 | 500 | Distribution Circuit | 3rd Party | Vehicle | 133 | 54883 | 38.8931 | -120.9977 | 3 SP S/O 701293 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 16-0028767 | OH | Sus | 0 | No | 2016 | APR | Yes | Line to Ground | 1198027 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 7919 | 20160415 | 1234 | 1451407 | 321 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 8767 | 38.7504 | -120.6322 | MTR#1007386001 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0028959 | OH | Sus | 0 | yes | 2016 | APR | Yes | Line to Line | 1198161 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1110 | 152691110 | FUSE | 4879 | 20160422 | 1015 | 1455615 | 606 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 29694 | 39.0911 | -121.0014 | 1 SPAN SOURCE SIDE OF 31277 / 4 P LD SIDE OF 4879 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0030595 | OH | Sus | 31233523 | yes | 2016 | APR | Yes | Line to Ground | 1199339 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | OTHER | HOT WIRE DOWN E/O MTR 1008890867 | 20160510 | 659 | 1467417 | 428 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1374 | 175420 | 39.0804 | -120.9711 | 4 WAY CORNER S/E OF MTR 1008890867 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0035025 | OH | Sus | 0 | No | 2016 | MAY | Yes | Open Circuit | 1202781 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 10025 | 20160512 | 1052 | 1468613 | 638 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 24244 | 38.5352 | -120.6993 | BRIDGEPORT SCHOOL RD NG TRANSF at MTR 10073371916/WIRE DOWN AT MTR# 1007 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0035568 | OH | Sus | 31238321 | No | 2016 | MAY | Yes | Line to Ground | 1203197 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | CLARKSVILLE-2104 | 153612104 | FUSE | 18517 | 20160520 | 1859 | 1473931 | 358 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 5404 | 38.7226 | -121.0464 | 4 N/OF MTR # 1009667448 | Lightning-Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0037516 | OH | Sus | 0 | yes | 2016 | MAY | Yes | Line to Line | 1204551 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1103 | 152561103 | FUSE | 8903 | 20160524 | 1922 | 1476160 | 313 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 5008 | 38.8579 | -121.1156 | 9550 POWERHOUSE RD | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0038233 | OH | Sus | 42706460 | No | 2016 | MAY | Yes | Line to Line | 1205116 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 10687 | 20160602 | 453 | 1481159 | 455 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 9100 | 38.6842 | -120.6538 | 4560 BONITA VISTA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0040392 | OH | Sus | 31243569 | No | 2016 | JUN | Yes | Line to Line | 1206836 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | SWITCH | 52193 | 20160603 | 1216 | 1482041 | 449 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1705 | 98486 | 38.6092 | -120.7073 | 1/N/OF/20891 | Clear-32-90 F | Conductor, Overhead | On Ground | 16-0040808 | OH | Sus | 42712253 | yes | 2016 | JUN | Yes | Force Out | 1207129 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8103 | 20160604 | 609 | 1482665 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 6885 | 39.3593 | -121.1207 | TASSONE-LOUIS/1262/682-6302: 2 POLES LD SIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0041029 | OH | Sus | 42712304 | No | 2016 | JUN | Yes | Line to Line | 1207290 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BELL-1107 | 152701107 | JUMPER | OJ'S 1 SPAN S/S OF MTR # 1004689622 | 20160606 | 1948 | 1484281 | 322 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 2039 | 38.9126 | -121.1189 | 2290 Moran Ct. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0041497 | OH | Sus | 42713342 | No | 2016 | JUN | Yes | Line to Ground | 1207673 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE | 9779 | 20160610 | 1433 | 1486758 | 691 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 111 | 53405 | 39.2089 | -120.9467 | 3 SPANS E/O 4817 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0042496 | OH | Sus | 42723148 | No | 2016 | JUN | Yes | Three Phase Fault | 1208391 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1107 | 152561107 | OTHER | WIRE DOWN @ 32085 | 20160618 | 1532 | 1491917 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 2663 | 11216 | 38.8131 | -121.1639 | HIGH SIDE OF 32085 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 16-0044251 | OH | Sus | 31248158 | No | 2016 | JUN | Yes | Line to Ground | 1209711 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | JUMPER | 1 SPAN OF WIRE DOWN | 20160702 | 911 | 1500021 | 589 | Distribution Circuit | Vegetation | Tree - fell into line | 169 | 36126 | 38.5976 | -120.8054 | 2 N/OF 13791 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0047561 | OH | Sus | 0 | No | 2016 | JUL | Yes | Open Circuit | 1212102 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 30839 | 20160712 | 2106 | 1509120 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2195 | 38.8328 | -120.8181 | 8581 HWY 193 TWD THE END OF THE TAP | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0049479 | OH | Sus | 31257027 | No | 2016 | JUL | Yes | Line to Ground | 1213559 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 4255 | 20160714 | 428 | 1509739 | 747 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 22353 | 39.1008 | -121.0938 | 11185 LIME KILN RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0049719 | OH | Sus | 0 | yes | 2016 | JUL | Yes | Line to Ground | 1213764 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 12187 | 20160716 | 47 | 1510977 | 841 | Distribution Circuit | 3rd Party | Vehicle | 58 | 24808 | 38.7074 | -120.6802 | 11531 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0050337 | OH | Sus | 0 | No | 2016 | JUL | Yes | Line to Ground | 1214148 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21295 | 20160724 | 838 | 1515013 | 777 | Distribution Circuit | Vegetation | Tree - fell into line | 388 | 16907 | 38.6434 | -120.6989 | SANDRIDGE AND BREKS RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0052085 | OH | Sus | 0 | No | 2016 | JUL | Yes | Line to Ground | 1215349 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1105 | 152561105 | FUSE | 862969 | 20160731 | 1145 | 1519426 | 294 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 294 | 38.8686 | -121.1303 | at 862969 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0053947 | OH | Sus | 0 | No | 2016 | JUL | Yes | Line to Line | 1216670 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 6943 | 20160803 | 438 | 1520733 | 444 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 2751 | 38.8447 | -120.8224 | TREE THRU LINE BETWEEN 2ND & 3RD POLE ON TAP | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0054597 | OH | Sus | 42757862 | No | 2016 | AUG | Yes | Line to Ground | 1217066 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1102 | 152291102 | OTHER | WIRE DOWN AT T-POLE 10/127 | 20160803 | 1241 | 1521016 | 522 | Distribution Circuit | Equipment Failure/Involved | Overhead | 226 | 20554 | 39.3295 | -120.5976 | 10/127 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0054769 | OH | Sus | 0 | No | 2016 | AUG | Yes | Line to Ground | 1217172 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2422 | 20160806 | 1435 | 1522554 | 655 | Distribution Circuit | Vegetation | Tree - fell into line | 603 | 58527 | 38.9 | -120.9075 | 3 WIRES DOWN 2 POLES SOURCE SIDE OF 35007 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0055524 | OH | Sus | 42760253 | No | 2016 | AUG | Yes | Three Phase Fault | 1217579 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1103 | 153661103 | OCB | 1103/2 | 20160812 | 1847 | 1525606 | 721 | Distribution Circuit | 3rd Party | Vehicle | 1874 | 86438 | 38.7393 | -120.6773 | 1 P N/O 18329 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0057044 | OH | Sus | 0 | No | 2016 | AUG | Yes | Line to Ground | 1218634 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-1103 | 153651103 | OCB | 1103/2 | 20160812 | 755 | 1525226 | 365 | Distribution Circuit | Animal | Bird found | 1129 | 63295 | 38.6597 | -120.9473 | 1 S/OF 10075 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0056813 | OH | Sus | 42768134 | No | 2016 | AUG | Yes | Line to Ground | 1218520 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE | 7463 | 20160824 | 805 | 1531283 | 532 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 6980 | 39.165 | -120.9698 | 14243 TALKING PINES DR. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0059593 | OH | Sus | 0 | No | 2016 | AUG | Yes | Multi-Fault | 1220369 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE | 6335 | 20160902 | 1743 | 1536103 | 734 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 25 | 18350 | 39.1217 | -120.9539 | MTR# 1004703128 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0062150 | OH | Sus | 0 | No | 2016 | SEP | Yes | Line to Ground | 1222093 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 4599 | 20160907 | 2058 | 1538095 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 8910 | 39.1815 | -121.1962 | 1 SPAN LD SIDE OF 4599 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0063056 | OH | Sus | 0 | No | 2016 | SEP | Yes | Line to Ground | 1222729 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9387 | 20160908 | 1426 | 1538520 | 284 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 20440 | 38.9237 | -120.9073 | 1 POLE SOUTH OF RCO 40369 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0063278 | OH | Sus | 42783154 | No | 2016 | SEP | Yes | Line to Ground | 1222866 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2102 | 153132102 | RECLOSER | 48484 | 20160909 | 932 | 1538852 | 605 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 598 | 66952 | 39.2544 | -121.1459 | 12913 GOLDEN EAGLE WAY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0063425 | OH | Sus | 0 | No | 2016 | SEP | Yes | Multi-Fault | 1222982 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 1443 | 20160911 | 1832 | 1539785 | 619 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 54472 | 38.7977 | -120.8206 | 3 SPANS LD SIDE OF MTR 1009960979 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0063800 | OH | Sus | 31270784 | No | 2016 | SEP | Yes | Line to Ground | 1223197 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | SWITCH | 8105 | 20160923 | 1523 | 1546770 | 702 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 79 | 55458 | 39.3784 | -121.0923 | TASSONE-LOUIS/1262/682-6302: 30850 GOLD DUST WAY OFF HWY 49 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0067089 | OH | Sus | 31273203 | No | 2016 | SEP | Yes | Open Circuit | 1225462 | CAW | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8157 | 20160926 | 1758 | 1548073 | 742 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 8100 | 39.3685 | -121.0681 | 12199 BREM RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0067641 | OH | Sus | 0 | yes | 2016 | SEP | Yes | Line to Line | 1225905 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1102 | 152101102 | FUSE | 8007 | 20161001 | 1519 | 1551029 | 991 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 153 | 6157 | 39.4382 | -120.8159 | 1 LD SIDE OF 8007 & 1 LD SIDE OF 8007 ON MAIN LINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0068934 | OH | Sus | 0 | No | 2016 | OCT | Yes | Line to Line | 1226842 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 33765 | 20161001 | 1757 | 1551071 | 1166 | Distribution Circuit | 3rd Party | Vehicle | 27 | 31482 | 39.2028 | -121.011 | 4 LD SIDE OF FUSE 33765 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0068959 | OH | Sus | 0 | No | 2016 | OCT | Yes | Line to Line | 1226863 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | OTHER | 1104 | 20161001 | 857 | 1550910 | 479 | Distribution Circuit | 3rd Party | Vehicle | 649 | 214738 | 38.9124 | -120.8201 | MAIN LINE at C/OUTS 9349 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0068898 | OH | Sus | 31274469 | No | 2016 | OCT | Yes | Three Phase Fault | 1226819 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-1103 | 153651103 | OCB | 1103/2 | 20161009 | 1852 | 1555512 | 563 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1128 | 98361 | 38.6597 | -120.9473 | WIRE DOWN SS OF 8319 TWD MAIN LINE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0070676 | OH | Sus | 31275989 | No | 2016 | OCT | Yes | Line to Ground | 1228222 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 7319 | 20161010 | 559 | 1555612 | 332 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 10956 | 38.7111 | -120.944 | 1 SPAN LD SIDE OF MTR 1008898130 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0070716 | OH | Sus | 42810384 | No | 2016 | OCT | Yes | Line to Ground | 1228263 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | RECLOSER | 2408 | 20161013 | 2057 | 1557802 | 664 | Distribution Circuit | 3rd Party | Vehicle | 445 | 111148 | 39.0472 | -121.0489 | TROTTER RD AND MAGNOLIA | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0071792 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Three Phase Fault | 1228964 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8137 | 20161016 | 2058 | 1563724 | 1010 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 83794 | 39.3645 | -121.0833 | 4 SPANS LD SIDE OF SBCO 8105 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on object | 16-0073095 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1230119 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 21977 | 20161016 | 1948 | 1563651 | 434 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2604 | 38.7146 | -120.8798 | BETWEEN 2ND & 4TH POLE BEYOND C/OUT 21977 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0073014 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1230044 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | ECHO SUMMIT-1101 | 158031101 | RECLOSER | LR 2500 | 20161016 | 1934 | 1563630 | 1431 | Distribution Circuit | Equipment Failure/Involved | Overhead | 351 | 411102 | 38.8236 | -120.0305 | BTW 4563 & 7449 | Overcast-Heavy Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 16-0073003 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Three Phase Fault | 1230033 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 21529 | 20161016 | 1446 | 1563065 | 377 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 5711 | 38.753 | -120.5762 | WIRE DOWN BEYOND C/OUTS 18503 EOL | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072956 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Line | 1229987 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE | 83291 | 20161016 | 2046 | 1563691 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1317 | 39.1448 | -121.1438 | 3 POLES W/O 83291 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0073065 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1230092 | CAW | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 20679 | 20161016 | 1504 | 1563116 | 674 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5392 | 38.6039 | -120.9275 | FLECKLIN-PAUL/623/530-906-3142: 5700 SEMOR DR | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072958 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Line | 1229989 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-1104 | 153651104 | FUSE | 12085 | 20161017 | 446 | 1563975 | 861 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 15955 | 38.6086 | -120.9557 | 5720 HONEYCOME LN | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0073136 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1230166 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1110 | 152691110 | FUSE | 7487 | 20161027 | 2202 | 1571205 | 924 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 12980 | 39.0797 | -121.0131 | RICHARD- JP: 13360 KNOLL WOOD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076170 | OH | Sus | 31281002 | yes | 2016 | OCT | Yes | Line to Line | 1232441 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1102 | 152241102 | FUSE | 7795 | 20161028 | 1239 | 1571925 | 218 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 2288 | 39.0046 | -120.9954 | 3 WEST OF FUSE 7795 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076452 | OH | Sus | 31281121 | yes | 2016 | OCT | Yes | Line to Line | 1232616 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 30251 | 20161030 | 1305 | 1573235 | 1118 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 8234 | 39.1684 | -120.9375 | 8 P LD SIDE OF C/OUT 30251 | Overcast-Heavy Rain-Lightning-32-90 F | Pole-Wood | Broken, wire on ground | 16-0076808 | OH | Sus | 0 | No | 2016 | OCT | Yes | Line to Line | 1232909 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | RECLOSER | 50072 | 20161030 | 1150 | 1573151 | 440 | Distribution Circuit | Vegetation | Tree - fell into line | 621 | 103438 | 39.0757 | -121.1143 | 1 SS OF 7059 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076777 | OH | Sus | 0 | No | 2016 | OCT | Yes | Line to Ground | 1232884 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 4655 | 20161030 | 1944 | 1573450 | 548 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4384 | 39.4223 | -121.015 | JUST LD SIDE OF C/OUT 4655 #1-2 POLES | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076833 | OH | Sus | 0 | No | 2016 | OCT | Yes | Line to Line | 1232935 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 4975 | 20161031 | 758 | 1573559 | 412 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 721 | 39.2034 | -121.1913 | LD SIDE OF 54585 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076933 | OH | Sus | 42870102 | No | 2016 | OCT | Yes | Line to Ground | 1233036 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | CLARKSVILLE-2103 | 153612103 | FUSE | 11049 | 20161116 | 1523 | 1582354 | 477 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 9942 | 38.6063 | -121.0218 | CGC# 222857834585 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0080333 | OH | Sus | 42881606 | No | 2016 | NOV | Yes | Line to Ground | 1235615 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | CLARKSVILLE-2104 | 153612104 | FUSE | 18523 | 20161127 | 1728 | 1590083 | 822 | Distribution Circuit | Equipment Failure/Involved | Overhead | 74 | 54228 | 38.7479 | -121.0597 | RISER POLE 52265 | Partly Cloudy-32-90 F | Anchor or Guy | Broken, wire on ground | 16-0082492 | OH | Sus | 0 | yes | 2016 | NOV | Yes | Line to Ground | 1237229 | ANC | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | EL DORADO PH-2101 | 152762101 | RECLOSER | 52456 | 20161127 | 11 | 1589565 | 2596 | Distribution Circuit | Vegetation | Tree - fell into line | 190 | 153529 | 38.7754 | -120.4024 | FLECKLIN-PAUL/623/530-906-3142: 29 MILESTONE TRACT | Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 16-0082376 | OH | Sus | 0 | yes | 2016 | NOV | Yes | Line to Line | 1237132 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER | 804 | 20161202 | 721 | 1593318 | 1935 | Distribution Circuit | Vegetation | Tree - fell into line | 603 | 138434 | 39.5598 | -120.8239 | TASSONE-LOUIS/1262/682-6302: 5 POLE LD SIDE XING at LURE RESORT TWRDS CAL TRANS | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 16-0083574 | OH | Sus | 31286856 | No | 2016 | DEC | Yes | Three Phase Fault | 1238156 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8103 | 20161208 | 2204 | 1597406 | 948 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 16116 | 39.3593 | -121.1207 | MTR#1008892404 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084699 | OH | Sus | 31288452 | yes | 2016 | DEC | Yes | Multi-Fault | 1239215 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 31783 | 20161209 | 128 | 1597459 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 464 | 39.26 | -120.9474 | JIMENEZ-AL/1586/530-913-7963: 14040 BANNER QUAKER HILL XING | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084706 | OH | Sus | 42893579 | No | 2016 | DEC | Yes | Multi-Fault | 1239225 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 1333 | 20161210 | 2044 | 1599472 | 1103 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 27575 | 38.6747 | -120.7232 | FLECKLIN-PAUL/623/530-906-3142: 4925 BUCKS BAR RD | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085041 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1239592 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1102 | 152241102 | FUSE | 5739 | 20161210 | 1919 | 1599453 | 471 | Distribution Circuit | Vegetation | Tree - fell into line | 117 | 55107 | 38.9696 | -121.0157 | 524 CLIPPER GAP | Rain-Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085014 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Line | 1239562 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | RECLOSER | 594 | 20161210 | 910 | 1598423 | 482 | Distribution Circuit | Vegetation | Tree - fell into line | 253 | 45506 | 39.0351 | -121.0957 | 4757 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084934 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1239482 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE | 8677 | 20161215 | 2332 | 1603947 | 885 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 6319 | 39.1559 | -120.9798 | IRO 14119 JUDY LANE | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0085927 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Line | 1240593 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-1104 | 153651104 | FUSE | 12855 | 20161217 | 715 | 1605335 | 599 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3594 | 38.5986 | -120.9729 | LUNA- MARCOS: 4990 Cothrin Ranch Rd | Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 16-0086137 | OH | Sus | 0 | No | 2016 | DEC | Yes | Multi-Fault | 1240890 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 4159 | 20161218 | 1921 | 1606405 | 1045 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 6458 | 38.8451 | -120.8572 | 5211 OAK RD. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0086263 | OH | Sus | 42902261 | No | 2016 | DEC | Yes | Line to Ground | 1241080 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 2212 | 20170102 | 2148 | 1615207 | 1450 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 105850 | 39.3844 | -121.0318 | 3 POLES W/OF MTR# 397E99 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0002873 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Line | 1243193 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE | 6005 | 20170102 | 724 | 1614635 | 330 | Distribution Circuit | Equipment Failure/Involved | Overhead | 299 | 74097 | 39.0191 | -120.8972 | RENFREE-SAM/1505/530-906-2110: 20120 spring garden rd | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0002783 | OH | Sus | 42908153 | No | 2017 | JAN | Yes | Line to Ground | 1243098 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER | 806 | 20170104 | 12 | 1617325 | 5393 | Distribution Circuit | Equipment Failure/Involved | Overhead | 83 | 193709 | 39.4878 | -120.8572 | 2733 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003349 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243522 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE | 4801 | 20170104 | 310 | 1617551 | 1011 | Distribution Circuit | Vegetation | Tree - fell into line | 218 | 219996 | 39.2642 | -121.0216 | RCO 9357 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003411 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1243600 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | SECTIONALIZER | 878 | 20170104 | 553 | 1617919 | 812 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 215 | 174026 | 39.3044 | -120.9558 | 1 SP WIRE DWON 5 SP LD SIDE OF 2715 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003712 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243779 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1110 | 152481110 | RECLOSER | 2664 | 20170104 | 19 | 1617352 | 1150 | Distribution Circuit | Vegetation | Tree - fell into line | 1988 | 505816 | 39.235 | -121.0604 | MTR# 1007665551 RCO 6859 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0003357 | OH | Sus | 31292417 | yes | 2017 | JAN | Yes | Line to Ground | 1243532 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1101 | 152591101 | FUSE | 6627 | 20170104 | 1600 | 1618604 | 1612 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 48543 | 39.3246 | -120.3841 | 21664 DONNER PASS RD | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004053 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1244013 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6615 | 20170104 | 2237 | 1619314 | 3967 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 230865 | 39.3222 | -120.436 | 5 SPANS LD SIDE OF 6611 | Overcast-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0003982 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243988 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 8417 | 20170105 | 1430 | 1619619 | 1536 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 52224 | 39.4603 | -121.0316 | Kitchell / 2011 / 925-525-3751: c/o 38371 Norcrest rd. | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004116 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Line | 1244047 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1101 | 152591101 | JUMPER | WIREDOWN @ MTR# 1006721519 | 20170105 | 1658 | 1619729 | 403 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 2766 | 39.325 | -120.3709 | MTR# 1006721519 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0004094 | OH | Sus | 0 | No | 2017 | JAN | Yes | Open Circuit | 1244026 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6617 | 20170106 | 1452 | 1620483 | 1684 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 20568 | 39.3202 | -120.4334 | SS 6653 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0004355 | OH | Sus | 0 | No | 2017 | JAN | Yes | Force Out | 1244187 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 7755 | 20170107 | 436 | 1620787 | 592 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 9472 | 39.0779 | -121.0865 | METER# 1007600418 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004526 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244354 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE | 6303 | 20170107 | 1753 | 1622123 | 1345 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 64499 | 39.0896 | -120.9656 | SPAN W/O 34625 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004796 | OH | Sus | 31294367 | yes | 2017 | JAN | Yes | Line to Line | 1244597 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | DRUM-1101 | 152321101 | FUSE | 9221 | 20170112 | 1449 | 1641691 | 2867 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 70526 | 39.3011 | -120.6604 | MULTIPLE LD SIDE OF 9221 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008475 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247848 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1102 | 152201102 | FUSE | 30593 | 20170112 | 1703 | 1641872 | 1413 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 11304 | 39.5212 | -120.9976 | 2 SPANS LS SIDE 30593 / 1- 2 & 3 SPANS SS OF THREE PHASE TAP OFF TO FUCO 8315 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008515 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1247875 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6635 | 20170112 | 1823 | 1642848 | 2869 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 68856 | 39.3199 | -120.4337 | 1/E/OF 8085 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008850 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1248119 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 13785 | 20170113 | 1118 | 1642469 | 1432 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4296 | 38.5948 | -120.8235 | 3 SP LD SIDE OF 13785 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0009054 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1248324 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6637 | 20170113 | 1142 | 1642516 | 1565 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 15650 | 39.3144 | -120.4584 | LD SIDE OF 6637 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0008746 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1248055 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6619 | 20170113 | 1624 | 1642833 | 175 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 3325 | 39.318 | -120.4546 | 3 SP SS OF 6637 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0008851 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1248120 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | ALLEGHANY-1101 | 152101101 | FUSE | 30317 | 20170115 | 1138 | 1644118 | 1882 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1882 | 39.6179 | -120.593 | 2 SP LD SIDE OF 30317 | Partly Cloudy-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0009284 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Ground | 1248547 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BELL-1109 | 152701109 | FUSE | 4417 | 20170116 | 818 | 1644335 | 486 | Distribution Circuit | 3rd Party | Vehicle | 64 | 31104 | 38.9623 | -121.0679 | FIRST POLE LD SIDE OF FUCO | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on object | 17-0009360 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Ground | 1248624 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1101 | 152591101 | FUSE | 6629 | 20170117 | 1000 | 1645385 | 73593 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 34293 | 39.3124 | -120.4184 | SOURCE SIDE AND LOAD SIDE OF MTR 100933368 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0009642 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Ground | 1248840 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | ALLEGHANY-1101 | 152101101 | SECTIONALIZER | 2628 | 20170124 | 1635 | 1666148 | 3037 | Distribution Circuit | Environmental/External | Ice or snow | 100 | 95457 | 39.6103 | -120.6059 | LD SIDE OF 2628 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0014489 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Force Out | 1253170 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | JUMPER | OJ 10 SPANS LD SIDE 9843 | 20170124 | 922 | 1665446 | 398 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 398 | 38.7491 | -120.6494 | 2681 CRYSTAL SPRINGS RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0014283 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1253030 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | DRUM-1101 | 152321101 | FUSE | 31201 | 20170124 | 1753 | 1666204 | 1182 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 2787 | 39.2872 | -120.6948 | MULTIPLE LOCATIONS | Clear-Below 32 F | Conductor, Overhead | On Ground | 17-0013558 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1253181 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 26000 | 20170124 | 1539 | 1666028 | 4447 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 4447 | 38.7525 | -120.5549 | JESSEE-BEN /620/ 916-826-8237: MULTIPLE LOCATIONS BETWEEN LR 26000 AND 7575 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0014462 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1253156 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 20527 | 20170125 | 940 | 1666762 | 236 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 472 | 38.6557 | -120.602 | ACROSS THE RIVER SOURCE SIDE FROM THE TRANSFORMER AT THE END OF THE TAP. | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0014684 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1253345 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 2500 | 20170125 | 1058 | 1666613 | 343 | Distribution Circuit | Vegetation | Tree - fell into line | 759 | 259893 | 38.8236 | -120.0305 | BETWEEN 6193 & 12333 & 2 & 5 S/W/O 10435 | Overcast-Below 32 F | Conductor, Overhead | On Ground | 17-0014725 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1253363 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | OTHER | 6615 | 20170125 | 1335 | 1667084 | 1409 | Distribution Circuit | Equipment Failure/Involved | Overhead | 120 | 169080 | 39.3222 | -120.436 | AT KINGVALE - TAP TO PALISADES | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0014796 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Open Circuit | 1253404 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE | 7161 | 20170203 | 1020 | 1673803 | 322 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 34199 | 39.2082 | -120.998 | AT MTR 1007534345 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017206 | OH | Sus | 42938467 | yes | 2017 | FEB | Yes | Line to Ground | 1255253 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE | 33219 | 20170206 | 2118 | 1677120 | 1087 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 2174 | 39.2608 | -121.0156 | MTR# 1007691572 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 17-0017994 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1255846 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1107 | 152691107 | JUMPER | OJ'S @ MTR#1007545819 | 20170206 | 2055 | s1256152 | 2522 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2522 | 39.0087 | -121.066 | ... | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018316 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256152 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 4345 | 20170206 | 2142 | 1677128 | 488 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 22936 | 39.2115 | -121.2014 | MTR# 1009122537 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018008 | OH | Sus | 31304290 | yes | 2017 | FEB | Yes | Line to Ground | 1255860 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1107 | 152561107 | FUSE | 30471 | 20170206 | 2017 | 1677056 | 347 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 11244 | 38.8267 | -121.1242 | TREE IN LINE 2 SPANS EAST OF MTR# 1003913351 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017932 | OH | Sus | 42939818 | yes | 2017 | FEB | Yes | Line to Ground | 1255784 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACER-1103 | 152461103 | FUSE | 5405 | 20170206 | 825 | 1675989 | 352 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 14304 | 38.9096 | -121.088 | 1 P S/O 30659 & END OF TAP LAST POLE | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017732 | OH | Sus | 31304113 | yes | 2017 | FEB | Yes | Line to Line | 1255681 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 11655 | 20170208 | 1108 | 1681790 | 247 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 494 | 38.5878 | -120.7328 | JESSEE-BEN /620/ 916-826-8237: 4 SPANS LOAD SIDE C/OS 11655 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019018 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256680 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 8667 | 20170208 | 1234 | 1681863 | 249 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 12948 | 39.184 | -120.9995 | WILKINS-ARMANDO/1589/913-5057: 8 POLES LS OF C/O 8667 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019016 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256677 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 4487 | 20170208 | 1831 | 1682467 | 486 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 12608 | 38.9132 | -120.9627 | 2601 WILLOW CREEK PLACE | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019150 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256762 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 32969 | 20170208 | 1647 | 1682331 | 1188 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1461 | 39.2507 | -121.2185 | 13800 RIVER ROCK RD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019131 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256745 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1105 | 152561105 | FUSE | 862969 | 20170208 | 1212 | 1681911 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 489 | 38.8686 | -121.1303 | RENFREE-SAM/1505/530-906-2110: 1105 newcastle rd | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019027 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256686 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 21521 | 20170208 | 2241 | 1682628 | 1018 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 5090 | 38.7941 | -120.7333 | 2699 & 2704 RIFLE CT | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0019201 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256814 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1101 | 152101101 | FUSE | 8849 | 20170210 | 1506 | 1685372 | 1544 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 10808 | 39.472 | -120.8416 | MTR 100895067 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0020029 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1257394 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 51792 | 20170210 | 259 | 1684474 | 8027 | Distribution Circuit | Vegetation | Tree - fell into line | 853 | 86235 | 38.6435 | -120.6959 | DERYK-KEVIN/621/530-386-5111: s/o of s/b 1341 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019748 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1257219 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | EL DORADO PH-2101 | 152762101 | OTHER | WIRE DWN 6 POLES W/O LR 36764 | 20170210 | 1549 | 1685507 | 1581 | Distribution Circuit | Vegetation | Tree - fell into line | 457 | 666444 | 38.7867 | -120.2117 | 6 W/O 36764 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019977 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1257403 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1102 | 152591102 | FUSE | 6829 | 20170210 | 655 | 1684614 | 683 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2732 | 39.3175 | -120.3525 | LINE & BUCK POLE | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019923 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1257332 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1350 | 20170212 | 1421 | 1686809 | 798 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 518 | 37390 | 38.8931 | -120.9966 | MTR 1004703627 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0020473 | OH | Sus | 0 | No | 2017 | FEB | Yes | Line to Ground | 1257842 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8233 | 20170216 | 426 | 1689959 | 526 | Distribution Circuit | Vegetation | Tree - fell into line | 58 | 30508 | 39.3421 | -121.0616 | 2 SPANS SOURCE SIDE OF 6973 | Overcast-Rain-32-90 F | Insulator | Broken, wire on ground | 17-0021470 | OH | Sus | 42949789 | yes | 2017 | FEB | Yes | Line to Line | 1258680 | INS | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 2212 | 20170216 | 426 | 1689944 | 909 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 67266 | 39.3844 | -121.0318 | MTR#397E99 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021519 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1258717 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 26000 | 20170216 | 601 | 1690063 | 1924 | Distribution Circuit | Equipment Failure/Involved | Overhead | 650 | 300946 | 38.7525 | -120.5549 | N/O 4691 at MTR#1005202863 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021476 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1258685 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | ECHO SUMMIT-1101 | 158031101 | FUSE | 2619 | 20170224 | 1059 | 1713135 | 1591 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 98642 | 38.8253 | -120.037 | FLECKLIN-PAUL/623/530-906-3142: ECHO LAKE RD=1 MILE NORTH O/JOHNSON PASS RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0026491 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Force Out | 1263172 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 32389 | 20170224 | 1842 | 1713553 | 652 | Distribution Circuit | 3rd Party | Vehicle | 4 | 2608 | 38.8134 | -121.0211 | 2 LD SIDE OF FUSE 32389 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0026668 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1263330 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1102 | 152591102 | FUSE | 6841 | 20170224 | 1150 | 1713080 | 220 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1320 | 39.3106 | -120.3394 | 6841 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0026466 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1263161 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1103 | 153661103 | FUSE | 18211 | 20170227 | 635 | 1714784 | 482 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2410 | 38.7269 | -120.7138 | 2 SPANS LD SIDE OF 18211 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0026968 | OH | Sus | 0 | No | 2017 | FEB | Yes | Line to Line | 1263654 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 34401 | 20170302 | 1146 | 1717805 | 10127 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 121524 | 39.3038 | -120.4184 | 1 SPAN LD SIDE OF 34401 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0027851 | OH | Sus | 0 | No | 2017 | MAR | Yes | Force Out | 1264341 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 13247 | 20170303 | 247 | 1718244 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 2824 | 38.6982 | -120.6704 | MTR # 1005286246 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0028037 | OH | Sus | 0 | No | 2017 | MAR | Yes | Line to Line | 1264447 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7067 | 20170304 | 2203 | 1719573 | 816 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 25271 | 39.1732 | -120.9739 | MTR# N42503 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0028402 | OH | Sus | 31309301 | No | 2017 | MAR | Yes | Line to Line | 1264755 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 34553 | 20170305 | 727 | 1719762 | 668 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 7348 | 38.9152 | -120.7779 | 1 SPAN SOURCE SIDE OF MTR# 1010029347 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0028482 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Ground | 1264844 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | EL DORADO PH-2101 | 152762101 | RECLOSER | 13532 | 20170306 | 1301 | 1721071 | 4529 | Distribution Circuit | Vegetation | Tree - fell into line | 773 | 282325 | 38.7731 | -120.2934 | WIRE DOWN 6/E/OF 18157/LIMB ON LINE 1 1/2 SPANS E/OF 36764 | Drizzle-Snow-Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0028783 | OH | Sus | 31309643 | yes | 2017 | MAR | Yes | Line to Ground | 1265082 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 32801 | 20170307 | 39 | 1721466 | 752 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 10528 | 39.1339 | -121.0724 | TREE THROUGH LINE AT MTR# 1007666392 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0028942 | OH | Sus | 0 | No | 2017 | MAR | Yes | Line to Ground | 1265207 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 4317 | 20170309 | 2034 | 1723650 | 1002 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 7290 | 39.2317 | -121.1689 | TASSONE-LOUIS/1262/682-6302: 11536 MINERS WAY | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0029861 | OH | Sus | 31311594 | No | 2017 | MAR | Yes | Line to Ground | 1265853 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1101 | 152101101 | JUMPER | OJ'S N/O MTR 1007601173 | 20170311 | 1043 | 1724948 | 3137 | Distribution Circuit | Environmental/External | Ice or snow | 2 | 6274 | 39.4888 | -120.8543 | TASSONE-LOUIS/1262/682-6302: MTR 1007601173 FOREST CITY | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0030130 | OH | Sus | 0 | No | 2017 | MAR | Yes | Line to Ground | 1266058 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | CLARKSVILLE-2103 | 153612103 | FUSE | 1295 | 20170313 | 1653 | 1726203 | 308 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 32 | 9856 | 38.5705 | -120.9684 | 2990 WHITE THORN | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0030518 | OH | Sus | 42968987 | No | 2017 | MAR | Yes | Line to Ground | 1266374 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1101 | 152591101 | FUSE | 6629 | 20170316 | 708 | 1728167 | 196 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 4656 | 39.3124 | -120.4184 | LD SIDE OF 34401 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0031131 | OH | Sus | 0 | No | 2017 | MAR | Yes | Line to Ground | 1266831 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BELL-1108 | 152701108 | FUSE | 6853 | 20170318 | 1538 | 1729827 | 167 | Distribution Circuit | 3rd Party | Vehicle | 225 | 29858 | 38.9971 | -121.1168 | 10025 LONESTAR | Clear-32-90 F | Other | Broken, wire on object | 17-0031691 | OH | Sus | 0 | No | 2017 | MAR | Yes | Line to Ground | 1267281 | NON | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BELL-1108 | 152701108 | SWITCH | 8317 | 20170318 | 2105 | 1729967 | 63 | Distribution Circuit | 3rd Party | Vehicle | 143 | 9009 | 39.001 | -121.1318 | LD SIDE OF 8317 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on object | 17-0031691 | OH | Sus | 31312373 | No | 2017 | MAR | Yes | Line to Ground | 1267293 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE | 6005 | 20170319 | 1052 | 1730146 | 277 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 414 | 27686 | 39.019 | -120.8972 | AT CGC #223118448927 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0031763 | OH | Sus | 42973099 | No | 2017 | MAR | Yes | Line to Ground | 1267367 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 4587 | 20170324 | 1838 | 1734964 | 1316 | Distribution Circuit | 3rd Party | Vehicle | 10 | 13160 | 39.1864 | -121.1867 | 11291 SPENCEVILLE RD | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0033562 | OH | Sus | 31314711 | yes | 2017 | MAR | Yes | Line to Ground | 1268501 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE | 33233 | 20170327 | 1620 | 1736869 | 111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 333 | 39.1198 | -120.949 | ? | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on object | 17-0034204 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Force Out | 1269046 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 12959 | 20170328 | 650 | 1737175 | 772 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3860 | 38.6442 | -120.8734 | SAMANIEGO-S/626/530-906-3122: 3-spans s/co's 12959 on neilson ranch rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0034370 | OH | Sus | 42978521 | yes | 2017 | MAR | Yes | Line to Ground | 1269219 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9311 | 20170330 | 225 | 1738799 | 525 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 3624 | 38.8344 | -121.0144 | RENFREE-SAM/1505/530-906-2110: 4800 jackass mine rd | Overcast-Drizzle-32-90 F | Woodpin | Broken, wire on object | 17-0034900 | OH | Sus | 31315392 | yes | 2017 | MAR | Yes | Line to Ground | 1269616 | WP | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2108 | 153652108 | RECLOSER | 51474 | 20170330 | 1118 | 1739300 | 186 | Distribution Circuit | Vegetation | Tree - branch fell on line | 742 | 68852 | 38.657 | -120.9942 | 2497 MARYHCASE DR | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0035043 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Ground | 1269759 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER | 804 | 20170331 | 938 | 1740926 | 981 | Distribution Circuit | Vegetation | Tree - fell into line | 603 | 264018 | 39.5598 | -120.8239 | JIMENEZ-AL/1586/530-913-7963: 4 SPNS SSD OF FSCOS 32497 OFF HWY 49 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0035535 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Three Phase Fault | 1270136 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 1029 | 20170408 | 1720 | 1753045 | 442 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 11492 | 38.6519 | -120.7816 | 5610 ROCKY RIDGE | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038353 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1272406 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1103 | 152561103 | RECLOSER | 51658 | 20170408 | 103 | 1752253 | 780 | Distribution Circuit | Vegetation | Tree - fell into line | 634 | 181761 | 38.8547 | -121.1505 | HART-EMMETT/1506/530-906-2031: 2865 Rattlesnake rd | Partly Cloudy-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038187 | OH | Sus | 31318217 | yes | 2017 | APR | Yes | Three Phase Fault | 1272245 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | FUSE | 5401 | 20170408 | 129 | 1752268 | 837 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 25947 | 38.8988 | -121.096 | 7 SPANS LOAD SIDE OF 5401 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038267 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1272326 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 34485 | 20170412 | 1643 | 1756333 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 33066 | 39.1233 | -121.0615 | mtr# 1007668697- 17118 LANDIS | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0039667 | OH | Sus | 42993416 | No | 2017 | APR | Yes | Line to Ground | 1273417 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | EL DORADO PH-2101 | 152762101 | RECLOSER | 36764 | 20170413 | 1531 | 1757252 | 1554 | Distribution Circuit | Equipment Failure/Involved | Overhead | 686 | 201244 | 38.7871 | -120.2059 | TWO SETS OF TBL. WIRE DOWN at 35 MILE TRACT JUST LD SIDE OF 18157 & BURNED INSULATOR & CROSS ARM | Overcast-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0040054 | OH | Sus | 42995053 | yes | 2017 | APR | Yes | Line to Line | 1273679 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 9741 | 20170413 | 1927 | 1757460 | 447 | Distribution Circuit | Equipment Failure/Involved | Overhead | 126 | 56322 | 39.1039 | -121.0841 | 19653 valkenburg ln | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0040115 | OH | Sus | 0 | yes | 2017 | APR | Yes | Open Circuit | 1273728 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | ALLEGHANY-1101 | 152101101 | RECLOSER | 978 | 20170415 | 1415 | 1758528 | 17624 | Distribution Circuit | Vegetation | Tree - fell into line | 199 | 143632 | 39.608 | -120.6068 | 1 POLE S/S/32519 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0040504 | OH | Sus | 31320294 | No | 2017 | APR | Yes | Line to Ground | 1274020 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1350 | 20170415 | 2313 | 1758726 | 715 | Distribution Circuit | Animal | Bird found | 884 | 125742 | 38.8931 | -120.9966 | 3190 MAGIC MORGAN TRAIL - COOL MTR# 1005416002 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0040561 | OH | Sus | 42996120 | No | 2017 | APR | Yes | Line to Ground | 1274065 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | LINCOLN-1104 | 153701104 | FUSE | 2387 | 20170418 | 1032 | 1760321 | 510 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 9215 | 39.0275 | -121.2938 | 5 E/O 31735 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0041157 | OH | Sus | 42997395 | yes | 2017 | APR | Yes | Line to Ground | 1274521 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1102 | 20170418 | 11 | 1759861 | 891 | Distribution Circuit | Equipment Failure/Involved | Overhead | 780 | 105995 | 38.8698 | -121.0202 | MTR# 1008818832 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0040956 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1274366 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 9737 | 20170426 | 1007 | 1767410 | 391 | Distribution Circuit | Vegetation | Tree - fell into line | 72 | 13648 | 39.1108 | -121.0824 | AT MTR # 1007602769 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0043017 | OH | Sus | 43001244 | No | 2017 | APR | Yes | Line to Line | 1275896 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | OTHER | WIRE DOWN 1 SPAN SOURCE SIDE OF 8465 | 20170426 | 1746 | 1767858 | 354 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6292 | 719136 | 39.0383 | -120.9875 | 2 SPANS SOURCE SIDE OF 8465 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0043179 | OH | Sus | 43001610 | No | 2017 | APR | Yes | Line to Ground | 1275958 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 9372 | 20170428 | 1549 | 1769753 | 706 | Distribution Circuit | Vegetation | Tree - fell into line | 2069 | 82614 | 38.714 | -120.9394 | at MTR # 1007650072 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0043771 | OH | Sus | 31322588 | yes | 2017 | APR | Yes | Line to Ground | 1276370 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 68757 | 20170524 | 2149 | 1789967 | 726 | Distribution Circuit | Vegetation | Tree - fell into line | 518 | 120015 | 38.7058 | -120.5996 | 1 SPAN SOUTH OF MTR# 1007392124 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0050499 | OH | Sus | 43022689 | No | 2017 | MAY | Yes | Line to Line | 1281430 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1103 | 152561103 | FUSE | 5259 | 20170524 | 1619 | 1789788 | 98 | Distribution Circuit | 3rd Party | Vehicle | 33 | 3234 | 38.8416 | -121.1161 | MTR # 1004248600 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0050465 | OH | Sus | 0 | No | 2017 | MAY | Yes | Three Phase Fault | 1281391 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 4655 | 20170529 | 2217 | 1792824 | 370 | Distribution Circuit | Equipment Failure/Involved | Overhead | 32 | 11840 | 38.7689 | -120.9511 | 1452 BADGER HILL RD. PLACERVILLE | Clear-32-90 F | Insulator | Broken, wire on ground | 17-0051359 | OH | Sus | 31328485 | No | 2017 | MAY | Yes | Line to Ground | 1282063 | INS | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 31487 | 20170608 | 1612 | 1799887 | 228 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 5016 | 39.1978 | -121.2133 | at MTR# 1007693399 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0053807 | OH | Sus | 43030574 | yes | 2017 | JUN | Yes | Line to Ground | 1283815 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE | 1313 | 20170622 | 1724 | 1815332 | 355 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 25 | 8517 | 38.7588 | -120.7204 | 3427 N CANYON BACK OF HOUSE | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0057857 | OH | Sus | 0 | yes | 2017 | JUN | Yes | Line to Ground | 1287051 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1103 | 152561103 | RECLOSER | 51658 | 20170622 | 1500 | 1815079 | 164 | Distribution Circuit | Vegetation | Tree - fell into line | 634 | 41570 | 38.8547 | -121.1505 | 2525 RATTLESNAKE RD- NEWCASTLE- AT 37225 FUCO | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0057792 | OH | Sus | 0 | yes | 2017 | JUN | Yes | Line to Line | 1287015 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | OTHER | WIRE DOWN NORTH AT | 20170623 | 2014 | 1816872 | 500 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1615 | 280532 | 39.0693 | -121.1113 | AT 9751 SBCO- SPAN GOING NORTH IS ON GRD | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0058231 | OH | Sus | 43044584 | yes | 2017 | JUN | Yes | Line to Ground | 1287323 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | OTHER | WIRE DOWN 4 SP W/OF 5791 | 20170705 | 1004 | 1823815 | 243 | Distribution Circuit | Equipment Failure/Involved | Overhead | 56 | 13340 | 39.0075 | -121.0421 | 4 SPANS WEST OF 5791 WIRE DOWN | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0060566 | OH | Sus | 31335273 | No | 2017 | JUL | Yes | Line to Ground | 1289115 | CSO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 5267 | 20170705 | 1158 | 1823929 | 787 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 10231 | 39.2137 | -121.2311 | JP RICHARD: 4 SPANS LS OF C/O 5285 ON ML | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0060605 | OH | Sus | 43049436 | No | 2017 | JUL | Yes | Line to Line | 1289128 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9353 | 20170707 | 515 | 1825161 | 300 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 3900 | 38.9016 | -120.9036 | 2 SPANS S/O CGC# 223114045259 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0061068 | OH | Sus | 43050049 | yes | 2017 | JUL | Yes | Three Phase Fault | 1289404 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 7899 | 20170709 | 2227 | 1827704 | 451 | Distribution Circuit | Equipment Failure/Involved | Overhead | 54 | 10536 | 39.122 | -121.0541 | 17805 NORLENE WAY | Clear-32-90 F | Insulator | Broken, wire on object | 17-0061615 | OH | Sus | 31336085 | No | 2017 | JUL | Yes | Line to Ground | 1289831 | INS | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 18861 | 20170709 | 1417 | 1827439 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 12466 | 38.7948 | -120.8843 | 1 SPAN SOUTH OF MTR# 1007297629 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0061553 | OH | Sus | 0 | No | 2017 | JUL | Yes | Line to Line | 1289766 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE | 6005 | 20170710 | 217 | 1827747 | 434 | Distribution Circuit | Vegetation | Tree - fell into line | 300 | 77167 | 39.019 | -120.8972 | SS OF MTR# 1004247535 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0061622 | OH | Sus | 0 | No | 2017 | JUL | Yes | Line to Ground | 1289838 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE | 5907 | 20170727 | 1323 | 1840921 | 111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 6105 | 39.0543 | -120.7586 | LD SIDE OF 5907 | Clear-32-90 F | Crossarm, Wood | Broken, wire on object | 17-0065987 | OH | Sus | 0 | No | 2017 | JUL | Yes | Force Out | 1292936 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1107 | 152561107 | FUSE | 38445 | 20170731 | 1430 | 1843278 | 210 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 210 | 38.7965 | -121.1333 | Turney- Robert 530-205-6563: 1/2 sp L/S C/O's 38445 | Partly Cloudy-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0066797 | OH | Sus | 43071628 | No | 2017 | JUL | Yes | Line to Ground | 1293523 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 12723 | 20170804 | 113 | 1846096 | 699 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 13281 | 38.7341 | -120.5715 | HYLAND-TRAVIS/530-295-7076: co 12723 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0067861 | OH | Sus | 31340787 | No | 2017 | AUG | Yes | Line to Line | 1294263 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1101 | 152031101 | FUSE | 32721 | 20170807 | 2138 | 1848199 | 441 | Distribution Circuit | Vegetation | Tree - fell into line | 228 | 9244 | 39.1748 | -121.067 | 1/LD SIDE OF 32721 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0068626 | OH | Sus | 43076409 | No | 2017 | AUG | Yes | Line to Ground | 1294810 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | RECLOSER | 2748 | 20170809 | 1342 | 1849359 | 940 | Distribution Circuit | 3rd Party | Vehicle | 884 | 83048 | 39.2081 | -121.2033 | AT MTR # 1007693414 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0069146 | OH | Sus | 0 | No | 2017 | AUG | Yes | Three Phase Fault | 1295177 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 130889 | 20170812 | 1643 | 1851217 | 404 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2020 | 39.1069 | -121.0556 | 17259 RUTH CT GRASS VALLEY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0069861 | OH | Sus | 43083249 | No | 2017 | AUG | Yes | Line to Ground | 1295685 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | OTHER | WIRE DOWN | 20170817 | 1450 | 1854371 | 663 | Distribution Circuit | Animal | Other | 253 | 32850 | 39.3704 | -121.049 | 2 SPANS W/O 31657 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0071121 | OH | Sus | 43088068 | No | 2017 | AUG | Yes | Line to Ground | 1296527 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 2053 | 20170822 | 1805 | 1857226 | 676 | Distribution Circuit | 3rd Party | Vehicle | 170 | 19340 | 38.7199 | -120.9392 | GREEN VALLEY RD AND BORREGO RD 1 POLE W/O FUSE 9867 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0072140 | OH | Sus | 0 | No | 2017 | AUG | Yes | Line to Ground | 1297271 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER | 2210 | 20170825 | 1806 | 1859461 | 817 | Distribution Circuit | 3rd Party | Vehicle | 869 | 453761 | 39.261 | -120.9817 | MTR#1007517371 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0072940 | OH | Sus | 0 | No | 2017 | AUG | Yes | Line to Ground | 1297845 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | JUMPER | WIREDOWN @ CGC 222418545636 | 20170827 | 1943 | 1860902 | 905 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 905 | 38.9161 | -121.151 | CGC 222418545636 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0073228 | OH | Sus | 0 | yes | 2017 | AUG | Yes | Force Out | 1298103 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | JUMPER | WIRE DOWN 2 SPANS S/OF SAP# 100097971 | 20170828 | 1010 | 1861294 | 613 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 105 | 10077 | 39.0472 | -120.7859 | 2 SPANS S/OF SAP# 100097971 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0073379 | OH | Sus | 31345493 | yes | 2017 | AUG | Yes | Force Out | 1298230 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 4537 | 20170830 | 1621 | 1863676 | 5635 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 10 | 24513 | 39.3443 | -121.1205 | TASSONE-LOUIS/1262/682-6302: BYOND C/O 4537 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0074305 | OH | Sus | 0 | No | 2017 | AUG | Yes | Line to Line | 1298794 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1102 | 152241102 | OTHER | WIRE DOWN | 20170830 | 2234 | 1863721 | 375 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 3750 | 38.9995 | -120.9888 | 1 SPAN SOUTH OF 6225 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0074333 | OH | Sus | 43096804 | No | 2017 | AUG | Yes | Line to Ground | 1298826 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 1111 | 20170908 | 447 | 1873150 | 441 | Distribution Circuit | Vegetation | Tree - bark fell into line | 230 | 39736 | 38.7478 | -120.859 | 7 SPANS W/O 1111 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0076889 | OH | Sus | 43101926 | No | 2017 | SEP | Yes | Three Phase Fault | 1300892 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 20679 | 20170908 | 1721 | 1873635 | 1063 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 8504 | 38.6039 | -120.9275 | 1 SPAN SW/O 20679 (SAME SPAN) | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0077122 | OH | Sus | 31349947 | No | 2017 | SEP | Yes | Line to Ground | 1301014 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1102 | 152591102 | FUSE | 6829 | 20170908 | 1329 | 1873504 | 508 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 4 | 2032 | 39.3175 | -120.3525 | 2 P/N/O 6829 | Clear-32-90 F | Crossarm, Wood | Broken, wire on object | 17-0077096 | OH | Sus | 43102342 | No | 2017 | SEP | Yes | Line to Ground | 1301000 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2102 | 153132102 | OTHER | WIRE DOWN S/W OF MTR#1007667096 | 20170912 | 1904 | 1877786 | 533 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 14 | 6526 | 39.2805 | -121.1293 | 2 SPANS SW/O MET# 1007667096 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0078387 | OH | Sus | 43108873 | yes | 2017 | SEP | Yes | Line to Ground | 1302023 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 18497 | 20170920 | 2003 | 1882747 | 216 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 2376 | 38.7583 | -120.5764 | 3105 HAZEL ST | Overcast-Rain-32-90 F | Other | Broken, wire on object | 17-0080440 | OH | Sus | 43114562 | No | 2017 | SEP | Yes | Force Out | 1303482 | NON | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1102 | 152291102 | FUSE | 9221 | 20170921 | 1145 | 1883311 | 555 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 21645 | 39.3011 | -120.6604 | AT CGC # 223821159924 | Overcast-32-90 F | Crossarm, Wood | Broken, wire on object | 17-0080702 | OH | Sus | 31351996 | yes | 2017 | SEP | Yes | Force Out | 1303666 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 4655 | 20170930 | 1251 | 1888594 | 32 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 256 | 39.4223 | -121.015 | 1 span ld side of 4655 | Clear-32-90 F | Insulator | Broken, wire on object | 17-0083043 | OH | Sus | 0 | No | 2017 | SEP | Yes | Force Out | 1305127 | INS | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | RECLOSER | 97982 | 20171002 | 1719 | 1889629 | 765 | Distribution Circuit | 3rd Party | Vehicle | 104 | 21593 | 38.6216 | -120.5867 | 1/SW/OF 39671 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0083547 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Three Phase Fault | 1305454 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 2679 | 20171002 | 1633 | 1889608 | 204 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 4797 | 38.7077 | -120.9708 | 2200 PINE HILL RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0083539 | OH | Sus | 31354019 | yes | 2017 | OCT | Yes | Line to Ground | 1305448 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2102 | 153132102 | FUSE | 32993 | 20171010 | 1926 | 1898104 | 1330 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 74704 | 39.2528 | -121.115 | 13523 EMPRESS RD | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0086236 | OH | Sus | 31360492 | No | 2017 | OCT | Yes | Line to Ground | 1307399 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | ECHO SUMMIT-1101 | 158031101 | RECLOSER | 8922 | 20171019 | 2019 | 1904584 | 2628 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 17895 | 38.8228 | -120.0296 | 7 SPANS LOAD SIDE OF 10199 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0088717 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1309289 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1101 | 152591101 | OTHER | WIRE DOWN 3 W/OF 64185 | 20171109 | 2009 | 1919784 | 948 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 4779 | 39.3283 | -120.388 | RENFREE-SAM/1505/530-906-2110: sherrit ln by fire house end of road | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0094104 | OH | Sus | 43208518 | yes | 2017 | NOV | Yes | Line to Ground | 1313233 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 19612 | 20171110 | 1701 | 1920300 | 473 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1346 | 16709 | 38.7621 | -120.5586 | MTR # 1007652331 | Overcast-Drizzle-32-90 F | Insulator | Broken, wire on object | 17-0094334 | OH | Sus | 31364935 | No | 2017 | NOV | Yes | Force Out | 1313351 | INS | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 6877 | 20171112 | 2105 | 1921061 | 965 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 11261 | 39.2858 | -121.0264 | BARKER- BILL: 16200 AIRPORT RD. N. C. SAP POLE ID 100079658- | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0094579 | OH | Sus | 31365160 | No | 2017 | NOV | Yes | Line to Ground | 1313597 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1107 | 152561107 | JUMPER | O/J 3 W/OF MTR# 1004896265 | 20171114 | 1730 | 1922503 | 84 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 252 | 38.8296 | -121.1202 | MTR#1004896265 | Clear-32-90 F | Insulator | Broken, wire on object | 17-0095007 | OH | Sus | 0 | No | 2017 | NOV | Yes | Force Out | 1314015 | INS | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 5781 | 20171115 | 1819 | 1923228 | 452 | Distribution Circuit | Vegetation | Tree - fell into line | 176 | 79552 | 39.0178 | -121.0299 | MTR 1004689307 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0095331 | OH | Sus | 43215951 | yes | 2017 | NOV | Yes | Line to Ground | 1314228 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BELL-1108 | 152701108 | FUSE | 8537 | 20171116 | 753 | 1923564 | 490 | Distribution Circuit | Vegetation | Tree - fell into line | 206 | 47946 | 38.9819 | -121.0731 | JOHNSTON-M/1508/530-906-5563: 3840 ginger ct | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0095494 | OH | Sus | 0 | yes | 2017 | NOV | Yes | Line to Ground | 1314360 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1102 | 152241102 | FUSE | 6123 | 20171116 | 56 | 1923407 | 747 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 56025 | 38.9793 | -121.0077 | 16455 BASS LAKE RD. | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0095402 | OH | Sus | 0 | yes | 2017 | NOV | Yes | Line to Line | 1314284 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 22347 | 20171116 | 757 | 1923498 | 347 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 6246 | 38.6466 | -120.9198 | 45775 MILLWOOD DR. | Overcast-Heavy Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0095450 | OH | Sus | 0 | yes | 2017 | NOV | Yes | Line to Ground | 1314319 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1101 | 152101101 | SWITCH | 865 | 20171118 | 1250 | 1925726 | 39 | Distribution Circuit | Equipment Failure/Involved | Overhead | 48 | 1872 | 39.4659 | -120.8447 | 2 P/N/O C541 | Clear-32-90 F | Other | Broken, wire on object | 17-0096204 | OH | Sus | 0 | No | 2017 | NOV | Yes | Force Out | 1314860 | NON | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2105 | 153652105 | OCB | 2105/2 | 20171125 | 1905 | 1929108 | 680 | Distribution Circuit | 3rd Party | Vehicle | 3962 | 515506 | 38.6597 | -120.9472 | CORNER OF MANY OAKS LN & WILD CHAPARRAL DR | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 17-0097525 | OH | Sus | 0 | No | 2017 | NOV | Yes | Three Phase Fault | 1315756 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | JUMPER | WIRE DOWN @ 7595 SLY PARD RD | 20171129 | 1724 | 1932196 | 657 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3089 | 582825 | 38.6842 | -120.655 | 7595 SLY PARK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0098456 | OH | Sus | 43224390 | No | 2017 | NOV | Yes | Line to Ground | 1316585 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | SWITCH | 11123 | 20171130 | 2102 | 1933016 | 365 | Distribution Circuit | 3rd Party | Vehicle | 8 | 2920 | 38.6628 | -120.9477 | HWY 50 & MANY OAKS LANE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0097525 | OH | Sus | 0 | No | 2017 | NOV | Yes | Three Phase Fault | 1316858 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | FORESTHILL-1102 | 152181102 | FUSE | 6023 | 20171201 | 1510 | 1933422 | 159 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 8 | 607 | 38.9931 | -120.9239 | SPAN FROM MTR# 1004247533 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0099024 | OH | Sus | 31367946 | No | 2017 | DEC | Yes | Line to Ground | 1317003 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | DIAMOND SPRINGS-1105 | 152261105 | OTHER | WIRE DOWN IRO 5321 SPREADING OAK LN | 20171208 | 1406 | 1939171 | 183 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 2340 | 38.6709 | -120.8576 | HYLAND-TRAVIS/530-295-7076: 5321 spreading oak ln | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0100858 | OH | Sus | 31369001 | No | 2017 | DEC | Yes | Line to Ground | 1318495 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 8372 | 20171219 | 1903 | 1947936 | 430 | Distribution Circuit | Equipment Failure/Involved | Overhead | 711 | 65426 | 38.6092 | -120.7025 | FLECKLIN-PAUL/623/530-906-3142: 7001 PERRY CREEK RD | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0102584 | OH | Sus | 43238407 | No | 2017 | DEC | Yes | Line to Ground | 1320806 | CSO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE | 6331 | 20171219 | 1829 | 1947919 | 608 | Distribution Circuit | 3rd Party | Vehicle | 206 | 33662 | 39.1456 | -120.9054 | 34701 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0102586 | OH | Sus | 31370568 | No | 2017 | DEC | Yes | Three Phase Fault | 1320808 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | EL DORADO PH-2101 | 152762101 | RECLOSER | 13532 | 20180104 | 325 | 1551 | 243 | Distribution Circuit | Equipment Failure/Involved | Overhead | 772 | 92021 | 38.7731 | -120.2934 | 2 SPANS E/O METER #1009125279 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0003422 | OH | Sus | 43244316 | yes | 2018 | JAN | Yes | Line to Ground | 1323024 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 7291 | 20180104 | 1646 | 2172 | 619 | Distribution Circuit | 3rd Party | Vehicle | 41 | 9951 | 39.2327 | -121.1306 | at METER #1007667614 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0003705 | OH | Sus | 0 | yes | 2018 | JAN | Yes | Line to Line | 1323213 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 2422 | 20180109 | 1736 | 5397 | 1309 | Distribution Circuit | Vegetation | Tree - fell into line | 741 | 63647 | 38.9 | -120.9075 | Fator- Travis 530-217-7961: Hwy 193 Gabby ln Georgetown | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 18-0004854 | OH | Sus | 31373045 | yes | 2018 | JAN | Yes | Line to Line | 1323937 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8861 | 20180110 | 1159 | 5933 | 327 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 6867 | 39.3887 | -121.0935 | 14097 MOONSHINE RD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0005034 | OH | Sus | 0 | No | 2018 | JAN | Yes | Line to Ground | 1324110 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 31079 | 20180111 | 657 | 6364 | 260 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 7280 | 38.8231 | -121.0112 | 1/W/O MTR 1004691724 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0005217 | OH | Sus | 43251510 | No | 2018 | JAN | Yes | Line to Ground | 1324224 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BELL-1108 | 152701108 | FUSE | 9927 | 20180123 | 1724 | 12809 | 267 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 3111 | 38.9692 | -121.1046 | Fator- Travis 530-217-7961: 4555 Chris Ln Auburn | Clear-32-90 F | Crossarm, Wood | Broken, wire on object | 18-0008292 | OH | Sus | 31375609 | No | 2018 | JAN | Yes | Force Out | 1326144 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1101 | 152301101 | RECLOSER | 1101/2 | 20180125 | 2301 | 14194 | 432 | Distribution Circuit | Vegetation | Tree - fell into line | 513 | 138287 | 39.214 | -120.8098 | HART-EMMETT/1506/530-906-2031: 777 Sacramento St ( 1st span load side of fco 6377) | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 18-0009142 | OH | Sus | 31375941 | No | 2018 | JAN | Yes | Line to Line | 1326578 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | OTHER | WIRE DOWN 14420 YOU BET RD | 20180125 | 2111 | 14166 | 402 | Distribution Circuit | Vegetation | Tree - branch fell on line | 364 | 146100 | 39.1913 | -120.9715 | 14420 You Bet Rd. | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0009137 | OH | Sus | 43261471 | No | 2018 | JAN | Yes | Line to Ground | 1326571 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1103 | 153661103 | OCB | 1103/2 | 20180207 | 709 | 20581 | 432 | Distribution Circuit | 3rd Party | Vehicle | 1806 | 127560 | 38.7393 | -120.6773 | FLECKLIN-PAUL/623/530-906-3142: 2961 CARSON RD | Clear-32-90 F | Pole-Wood | Broken, wire on object | 18-0012068 | OH | Sus | 0 | No | 2018 | FEB | Yes | Line to Ground | 1328603 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1107 | 152561107 | FUSE | 34765 | 20180211 | 1239 | 22726 | 290 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 4060 | 38.8 | -121.1756 | 6835 BROOKS LN | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0013237 | OH | Sus | 31378763 | No | 2018 | FEB | Yes | Line to Ground | 1329409 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 1299 | 20180215 | 1152 | 25333 | 354 | Distribution Circuit | 3rd Party | Vehicle | 69 | 24426 | 38.6932 | -120.766 | LD SIDE 1299 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0014638 | OH | Sus | 31379318 | No | 2018 | FEB | Yes | Line to Ground | 1330293 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 18399 | 20180223 | 728 | 29809 | 400 | Distribution Circuit | Equipment Failure/Involved | Overhead | 19 | 7600 | 38.5933 | -120.6537 | HYLAND-TRAVIS/530-295-7076: 2 spans load side of cutout 18399 | Clear-Below 32 F | Connector or Splice (OH) | Broken, wire on ground | 18-0016679 | OH | Sus | 31380904 | No | 2018 | FEB | Yes | Line to Ground | 1331698 | CSO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 7502 | 20180226 | 1016 | 31788 | 380 | Distribution Circuit | Equipment Failure/Involved | Overhead | 367 | 76980 | 38.6828 | -120.6611 | MAINLINE at 22837 | Overcast-Fog-Snow-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0017243 | OH | Sus | 0 | yes | 2018 | FEB | Yes | Line to Ground | 1332143 | CSO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 7117 | 20180226 | 844 | 31579 | 447 | Distribution Circuit | Vegetation | Tree - fell into line | 155 | 69285 | 39.2846 | -121.022 | 14702 HOB NOB WY | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0017242 | OH | Sus | 0 | yes | 2018 | FEB | Yes | Multi-Fault | 1332141 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 9793 | 20180226 | 848 | 31608 | 246 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 6150 | 39.1904 | -120.9841 | 13618 PEARDALE RD. | Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0017176 | OH | Sus | 31381305 | yes | 2018 | FEB | Yes | Open Circuit | 1332101 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1110 | 152481110 | FUSE | 32301 | 20180226 | 848 | 31539 | 416 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 4576 | 39.2225 | -121.0854 | 4 SPANS S/OF 32301 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0017358 | OH | Sus | 0 | yes | 2018 | FEB | Yes | Line to Ground | 1332186 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 1104 | 20180226 | 900 | 31632 | 435 | Distribution Circuit | Environmental/External | Ice or snow | 651 | 125573 | 38.9124 | -120.8201 | HART-EMMETT/1506/530-906-2031: 4-spans load side of s/bcutouts 4743 on Fox Run | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0017192 | OH | Sus | 0 | yes | 2018 | FEB | Yes | Line to Ground | 1332115 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHADY GLEN-1102 | 152431102 | JUMPER | WIRE DOWN | 20180226 | 1336 | 31792 | 343 | Distribution Circuit | Equipment Failure/Involved | Overhead | 127 | 5561 | 39.1294 | -120.9103 | S/OF ANGLE POLE at END OF CAPE HORN | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on object | 18-0017467 | OH | Sus | 0 | yes | 2018 | FEB | Yes | Open Circuit | 1332221 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHADY GLEN-1102 | 152431102 | OTHER | 6343 | 20180226 | 940 | 31741 | 614 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 17192 | 39.1278 | -120.9388 | LD SIDE 6343 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0017468 | OH | Sus | 0 | yes | 2018 | FEB | Yes | Open Circuit | 1332222 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 4267 | 20180227 | 1005 | 32743 | 302 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 20364 | 39.097 | -121.0984 | MUELLER-ANDY/1585/530-863-6807: ABOVE 11743 TOM RAY DR GRASS VALLEY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0017701 | OH | Sus | 43285854 | yes | 2018 | FEB | Yes | Line to Line | 1332461 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE | 30263 | 20180301 | 1521 | 35170 | 1389 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 7848 | 39.2154 | -120.9322 | SOURCE SIDE OF MTR # 1007520813 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0018721 | OH | Sus | 31312028 | yes | 2018 | MAR | Yes | Line to Line | 1333103 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | EL DORADO PH-2101 | 152762101 | FUSE | 2429 | 20180301 | 2100 | 35784 | 884 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 5304 | 38.7746 | -120.4 | N/OF MTR# 1007479281 | Overcast-Fog-Snow-32-90 F | Crossarm, Wood | Broken, wire on object | 18-0018898 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Force Out | 1333254 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | RECLOSER | 1704 | 20180301 | 1205 | 34724 | 176 | Distribution Circuit | Vegetation | Tree - branch fell on line | 430 | 29780 | 38.9946 | -121.0261 | 1850 MEADOW VISTA RD & LAREDO | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0018588 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333036 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 5793 | 20180301 | 1513 | 35163 | 428 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 34240 | 39.0048 | -121.0352 | 2322 VAN GIESEN DR | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0018712 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333098 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1102 | 152201102 | JUMPER | WIRE DOWN 5/S/SIDE OF 8801 | 20180301 | 1652 | 35760 | 1454 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 39258 | 39.4883 | -120.9964 | 5/SS/OF 8801 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0018813 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333214 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 20481 | 20180301 | 1148 | 34670 | 1669 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 8102 | 38.7678 | -120.9511 | 4323 ROSSLER RD | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0018557 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333013 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE | 20837 | 20180302 | 2201 | 36903 | 2396 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 9584 | 38.7453 | -120.648 | JESSEE-BEN /620/ 916-826-8237: PONY EXPRESS AND MELODY LANE | Overcast-Fog-Drizzle-32-90 F | Insulator | Broken, wire on object | 18-0019427 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333625 | INS | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 31793 | 20180302 | 2007 | 36815 | 981 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 19554 | 39.2666 | -120.8999 | BARKER- BILL: 17123 BANNER QUAKER HILL RD NEV CITY. OR at SAP POLE ID 100099757 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0019284 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333485 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 19612 | 20180302 | 2317 | 36949 | 3540 | Distribution Circuit | Vegetation | Tree - fell into line | 1345 | 1973152 | 38.7621 | -120.5586 | BEHIND FOREST SERVICE CAMP. 7887 US HWY 50/ AT END OF ALDER CREEK TRACT/10 S/W/OF 13133 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 18-0019290 | OH | Sus | 31381891 | yes | 2018 | MAR | Yes | Line to Line | 1333491 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 18431 | 20180302 | 2351 | 36973 | 2207 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 18199 | 38.7558 | -120.5957 | MTR# 1006494480 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019440 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333632 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1102 | 152241102 | FUSE | 6147 | 20180302 | 20 | 35922 | 560 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 11012 | 38.9973 | -120.9802 | at MTR # 1004895883 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0018959 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333315 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 32741 | 20180302 | 47 | 35908 | 765 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 17148 | 39.1442 | -121.0627 | 10396 ALTA SIERRA DR | Overcast-Fog-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 18-0018954 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Three Phase Fault | 1333309 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 7899 | 20180302 | 2037 | 36837 | 938 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 15750 | 39.122 | -121.0541 | 17794 NORLENE WAY | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019280 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333480 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE | 1463 | 20180303 | 719 | 37185 | 625 | Distribution Circuit | Vegetation | Tree - fell into line | 245 | 105027 | 38.7471 | -120.6443 | JESSEE-BEN /620/ 916-826-8237: CORNER OF FERN AND CEDAR | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0019344 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333548 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 2051 | 20180303 | 457 | 37079 | 747 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 79182 | 38.7456 | -120.6284 | FULTON- ERIC: 2 poles north of fuse 2051 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0019348 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333552 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 3369 | 20180303 | 19 | 36976 | 2467 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 14802 | 38.7521 | -120.6285 | 3 SPAN LOAD SIDE 3369 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019415 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333615 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 9659 | 20180303 | 637 | 37422 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 7028 | 39.3111 | -120.9802 | LD SIDE OF 9659 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0019428 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333626 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 18415 | 20180303 | 608 | 37109 | 872 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 11336 | 38.7719 | -120.5758 | 2420 RANDOLPH CANYON RD | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0019464 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333656 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 12645 | 20180303 | 106 | 36989 | 2311 | Distribution Circuit | Vegetation | Tree - fell into line | 88 | 82525 | 38.7126 | -120.6007 | MTR1007392131 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0019476 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333663 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 18511 | 20180303 | 50 | 36983 | 1014 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 80626 | 38.7537 | -120.575 | 1/S/O 18511 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0019304 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333506 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | TRIP-SAVER | 6645 | 20180303 | 55 | 36986 | 2175 | Distribution Circuit | Vegetation | Tree - branch fell on line | 116 | 252300 | 38.7648 | -120.5895 | MTR#1009706355 & 5 span ld side of 18401 & 2 span e/o 18403 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0019318 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333524 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 1381 | 20180303 | 133 | 37002 | 1320 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 19800 | 38.7556 | -120.6011 | 4061 NATRUAL WAY | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0019405 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333607 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 3369 | 20180304 | 1821 | 38132 | 1709 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4938 | 38.7521 | -120.6285 | CGC # 223888539985 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019615 | OH | Sus | 0 | No | 2018 | MAR | Yes | Line to Ground | 1333807 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | SWITCH | 31765 | 20180304 | 2344 | 38190 | 276 | Distribution Circuit | Equipment Failure/Involved | Overhead | 21 | 3081 | 39.2388 | -120.9609 | 2 POLES NW ON METER#1007546193 | Clear-Below 32 F | Insulator | Broken, wire on object | 18-0019797 | OH | Sus | 43288801 | No | 2018 | MAR | Yes | Force Out | 1333988 | INS | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 12101 | 20180313 | 1316 | 43342 | 557 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 11697 | 38.8299 | -120.8157 | 8681 HWY 193 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0022371 | OH | Sus | 31383917 | yes | 2018 | MAR | Yes | Line to Line | 1335642 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 4169 | 20180314 | 154 | 43726 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 20054 | 39.11 | -121.0304 | MUELLER-ANDY/1585/530-863-6807: 19302 TIGER TAIL RD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0022503 | OH | Sus | 43300303 | yes | 2018 | MAR | Yes | Line to Line | 1335725 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE | 5907 | 20180315 | 2014 | 45085 | 1042 | Distribution Circuit | Vegetation | Tree - branch fell on line | 55 | 23290 | 39.0543 | -120.7586 | 3N & 5E/O 30397 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0023213 | OH | Sus | 43301933 | No | 2018 | MAR | Yes | Line to Ground | 1336114 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1107 | 152561107 | FUSE | 32061 | 20180315 | 1555 | 44878 | 275 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 4037 | 38.8315 | -121.1686 | 1 N/O 1004425859 | Overcast-Rain-32-90 F | Woodpin | Broken, wire on object | 18-0023160 | OH | Sus | 31384425 | No | 2018 | MAR | Yes | Line to Line | 1336072 | WP | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 7075 | 20180317 | 1558 | 46867 | 1030 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 21410 | 38.7525 | -120.6068 | 2/S/OF 7075 | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023864 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336658 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | JUMPER | WIRE DOWN 1/W/OF 31905 | 20180317 | 927 | 46626 | 420 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 31 | 12250 | 39.3237 | -120.8789 | 1/W/OF 31905 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023741 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Open Circuit | 1336533 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | RECLOSER | 19562 | 20180317 | 1559 | 46752 | 1283 | Distribution Circuit | Vegetation | Tree - fell into line | 414 | 217960 | 38.7604 | -120.5769 | 3480 Gold Ridge Trl Pollack pines/4046 OPAL TR. | Partly Cloudy-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023786 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336575 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 7079 | 20180318 | 249 | 47111 | 550 | Distribution Circuit | Equipment Failure/Involved | Overhead | 310 | 170500 | 38.7533 | -120.5967 | 6001 PONY EXPRESS TR | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0023865 | OH | Sus | 0 | No | 2018 | MAR | Yes | Multi-Fault | 1336659 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 95465 | 20180318 | 843 | 47252 | 558 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2232 | 38.7672 | -120.578 | THORNTON- ELLIS: CANYON EDGE RD AND FOREBAY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023908 | OH | Sus | 0 | No | 2018 | MAR | Yes | Line to Ground | 1336708 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | EL DORADO PH-2101 | 152762101 | OTHER | WIRE DOWN 1 N/OF MTR#1009663296 | 20180320 | 1019 | 48486 | 551 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5842 | 38.7659 | -120.436 | 1 SPAN N/O MTR# 1009663296 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0024394 | OH | Sus | 31385122 | yes | 2018 | MAR | Yes | Line to Ground | 1337071 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1107 | 152691107 | FUSE | 5727 | 20180321 | 1424 | 49583 | 485 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 14395 | 39.019 | -121.0518 | 1/W/MTR# 1007546603 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025074 | OH | Sus | 43304950 | yes | 2018 | MAR | Yes | Multi-Fault | 1337342 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1103 | 152561103 | FUSE | 5285 | 20180322 | 731 | 50327 | 581 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 12201 | 38.8087 | -121.0754 | 2 SPANS N/O 30161 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025423 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1337571 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1110 | 153081110 | RECLOSER | 19582 | 20180322 | 1416 | 50824 | 569 | Distribution Circuit | Equipment Failure/Involved | Overhead | 742 | 84076 | 38.7527 | -120.8225 | HYLAND-TRAVIS/530-295-7076: 3/s/s co 2641 | Partly Cloudy-Fog-Heavy Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025619 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1337635 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1111 | 153081111 | FUSE | 22381 | 20180322 | 757 | 50320 | 270 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2160 | 38.7236 | -120.8352 | DERYK-KEVIN/621/530-386-5111: 7080 helmrich rd | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025342 | OH | Sus | 31385410 | yes | 2018 | MAR | Yes | Line to Ground | 1337523 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHADY GLEN-1101 | 152431101 | OTHER | WIRE DOWN 3 SPAN E/O 7495 | 20180322 | 832 | 50432 | 537 | Distribution Circuit | Vegetation | Tree - fell into line | 227 | 80133 | 39.0639 | -121.0221 | 21475 SPRING RANCH RD | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025390 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1337555 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 20809 | 20180322 | 1602 | 51218 | 215 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1720 | 38.8105 | -120.9439 | JESSEE-BEN /620/ 916-826-8237: C/O POLE 80665 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025774 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1337711 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 1975 | 20180322 | 837 | 50380 | 372 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 4632 | 38.6669 | -120.9135 | 4310 CHILDHOOD LN | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025457 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1337580 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 26000 | 20180323 | 1620 | 52176 | 5348 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 5348 | 38.7525 | -120.5549 | S/OF LINE & BUCK FEEDING TO 2481 AND 4 SPANS N/O 7575 | Partly Cloudy-32-90 F | Insulator | Broken, wire on ground | 18-0026133 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1337983 | INS | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE | 31321 | 20180326 | 1508 | 53825 | 200 | Distribution Circuit | Equipment Failure/Involved | Overhead | 100 | 12356 | 39.2692 | -121.008 | 2/S/OF 31841 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0026785 | OH | Sus | 31385976 | No | 2018 | MAR | Yes | Line to Ground | 1338621 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | CLARKSVILLE-2105 | 153612105 | RECLOSER | 75884 | 20180401 | 2345 | 57613 | 894 | Distribution Circuit | Vegetation | Tree - branch fell on line | 919 | 117464 | 38.6553 | -121.0511 | LUNA- MARCOS: 4081 marble mountainMTR#1009649419 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0028316 | OH | Sus | 31387101 | No | 2018 | APR | Yes | Line to Ground | 1339814 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2108 | 153652108 | RECLOSER | 2695 | 20180404 | 221 | 59154 | 810 | Distribution Circuit | 3rd Party | Vehicle | 2400 | 255626 | 38.6569 | -120.9928 | 22291 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 18-0029047 | OH | Sus | 0 | No | 2018 | APR | Yes | Line to Line | 1340307 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1107 | 152691107 | JUMPER | WIRE DOWN @ MTR# 1003917864 | 20180410 | 1313 | 63996 | 240 | Distribution Circuit | Vegetation | Tree - fell into line | 1694 | 49287 | 39.0203 | -121.0681 | 25238 TABLE MEADOW RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0030949 | OH | Sus | 43322341 | No | 2018 | APR | Yes | Line to Ground | 1341755 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | RECLOSER | 842642 | 20180414 | 2132 | 67034 | 642 | Distribution Circuit | 3rd Party | Vehicle | 247 | 158574 | 39.1268 | -121.056 | ACROSS FROM 17594 LAWRENCE WAY | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0032303 | OH | Sus | 0 | No | 2018 | APR | Yes | Line to Line | 1342762 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20180416 | 1132 | 67901 | 275 | Distribution Circuit | Environmental/External | Lightning | 1025 | 133966 | 38.8155 | -120.8221 | at MTR 1004691944 | Overcast-Drizzle-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0032626 | OH | Sus | 0 | yes | 2018 | APR | Yes | Line to Line | 1343083 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | OTHER | WIRE DOWN 4 SE/O 36495 | 20180419 | 1156 | 70126 | 880 | Distribution Circuit | 3rd Party | Vehicle | 153 | 113094 | 39.0892 | -121.1728 | BARKER- BILL: 4 POLES S/E OF FC/O 36495 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 18-0033752 | OH | Sus | 0 | No | 2018 | APR | Yes | Line to Ground | 1343766 | PW | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21121 | 20180425 | 710 | 73379 | 428 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2568 | 38.6788 | -120.7208 | 2/S/O CGC 223657037240 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0035304 | OH | Sus | 0 | No | 2018 | APR | Yes | Line to Ground | 1344830 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1101 | 152301101 | RECLOSER | 86696 | 20180427 | 1248 | 75445 | 342 | Distribution Circuit | Vegetation | Tree - fell into line | 147 | 28650 | 39.1829 | -120.8565 | 2 SPANS W/O R281 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0036310 | OH | Sus | 43333077 | No | 2018 | APR | Yes | Line to Ground | 1345436 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | OTHER | WIRE DOWN 1 SP E/O MTR#1010249473 | 20180430 | 1225 | 76759 | 357 | Distribution Circuit | 3rd Party | Vehicle | 203 | 1511 | 39.2749 | -120.9342 | 1 SP E/O MTR#1010249473 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0036887 | OH | Sus | 43333752 | No | 2018 | APR | Yes | Line to Ground | 1345884 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 12619 | 20180511 | 1102 | 83902 | 452 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 17 | 7684 | 38.7998 | -120.7289 | 2919 SWANSBRO RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0040331 | OH | Sus | 31391804 | yes | 2018 | MAY | Yes | Line to Ground | 1348367 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 85766 | 20180511 | 1743 | 84335 | 525 | Distribution Circuit | Equipment Failure/Involved | Overhead | 260 | 53784 | 38.8026 | -120.9065 | 1 & 3 SPANS SE OF 22949 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0040415 | OH | Sus | 0 | yes | 2018 | MAY | Yes | Line to Ground | 1348424 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 6397 | 20180511 | 1750 | 84330 | 537 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 8592 | 39.0135 | -120.9813 | 7 POLES LD SIDE OF 6397 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0040427 | OH | Sus | 31391798 | yes | 2018 | MAY | Yes | Line to Line | 1348433 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE | 7005 | 20180512 | 1052 | 84796 | 310 | Distribution Circuit | Vegetation | Tree - fell into line | 567 | 29228 | 39.2131 | -121.0136 | TREE INTO THE LINE 1 SPAN S/O 39003 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0040494 | OH | Sus | 31391687 | No | 2018 | MAY | Yes | Multi-Fault | 1348559 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 12187 | 20180514 | 2253 | 86214 | 1006 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 41192 | 38.7074 | -120.6802 | 12187 SOMMER STAR | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0041074 | OH | Sus | 31392183 | No | 2018 | MAY | Yes | Line to Line | 1349053 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 22861 | 20180519 | 1613 | 89812 | 178 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 2 | 356 | 38.6972 | -120.6049 | UNK | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0042545 | OH | Sus | 43351608 | No | 2018 | MAY | Yes | Line to Ground | 1350128 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 1104 | 20180519 | 9 | 89501 | 782 | Distribution Circuit | Vegetation | Tree - fell into line | 652 | 342698 | 38.9124 | -120.8201 | 4 s/w of 40519 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0042471 | OH | Sus | 43351463 | No | 2018 | MAY | Yes | Line to Line | 1350009 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE | 3553 | 20180606 | 2344 | 103312 | 721 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 10815 | 39.1749 | -121.0948 | 4 P E/O MTR#1007517910 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0048188 | OH | Sus | 31395047 | No | 2018 | JUN | Yes | Line to Line | 1354548 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | AUBURN-1101 | 152161101 | FUSE | 8409 | 20180607 | 658 | 103374 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 6490 | 38.8936 | -121.0611 | 145 MARINA | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0048221 | OH | Sus | 31395096 | No | 2018 | JUN | Yes | Line to Line | 1354576 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | OCB | 2102/2 | 20180614 | 1419 | 109303 | 412 | Distribution Circuit | 3rd Party | Vehicle | 2655 | 256192 | 38.7394 | -120.6774 | 3923 PLEASANT VALLEY RD.- PLACERVILLE | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0051122 | OH | Sus | 0 | No | 2018 | JUN | Yes | Multi-Fault | 1356677 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2105 | 153652105 | FUSE | 22973 | 20180621 | 2045 | 114859 | 577 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 6924 | 38.6684 | -120.9799 | 301 SUDBURY RD | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0053349 | OH | Sus | 31397193 | No | 2018 | JUN | Yes | Line to Ground | 1358475 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | OCB | 1101/2 | 20180624 | 222 | 116822 | 636 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1143 | 629380 | 39.3313 | -121.1015 | RENFREE-SAM/1505/530-906-2110: 23837 pleasant valley rd | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0053992 | OH | Sus | 0 | No | 2018 | JUN | Yes | Line to Line | 1359023 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1107 | 152691107 | FUSE | 4641 | 20180626 | 2057 | 119086 | 508 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 2540 | 39.0104 | -121.0683 | 4/SE/O 4641 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0054868 | OH | Sus | 0 | No | 2018 | JUN | Yes | Line to Ground | 1359738 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | CLARKSVILLE-2103 | 153612103 | FUSE | 11421 | 20180628 | 1227 | 120300 | 483 | Distribution Circuit | 3rd Party | Vehicle | 91 | 24671 | 38.6033 | -121.02 | 1 P N/O 3664 COTHRANE RD EL DO HILLS | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0055479 | OH | Sus | 0 | No | 2018 | JUN | Yes | Three Phase Fault | 1360263 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8119 | 20180630 | 1114 | 121753 | 318 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 5724 | 39.3625 | -121.0844 | TASSONE- LOUIS: 5 POLE LD SIDE 8119 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0055945 | OH | Sus | 43386758 | No | 2018 | JUN | Yes | Line to Line | 1360778 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 9755 | 20180630 | 2236 | 122077 | 863 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 8004 | 39.113 | -121.0814 | 2 SPANS W/O MTR 1007548201 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0056039 | OH | Sus | 31398504 | No | 2018 | JUN | Yes | Line to Ground | 1360850 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 7853 | 20180702 | 424 | 122704 | 721 | Distribution Circuit | Vegetation | Tree - branch fell on line | 33 | 9653 | 39.242 | -120.9626 | MTR 1007521075 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0056180 | OH | Sus | 31398587 | No | 2018 | JUL | Yes | Line to Ground | 1360983 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | JUMPER | OJ 2 SPANS E/O CGC #223560042040 | 20180705 | 942 | 124818 | 302 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 1209 | 38.8141 | -120.7506 | 2 SPANS E/O CGC# 223560042040 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0057106 | OH | Sus | 31398925 | No | 2018 | JUL | Yes | Line to Ground | 1361617 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | RECLOSER | 2234 | 20180705 | 831 | 124728 | 343 | Distribution Circuit | Equipment Failure/Involved | Overhead | 258 | 33306 | 38.8955 | -121.1358 | 7370 RIDGE RD at MTR # 1004247505 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 18-0057076 | OH | Sus | 43389174 | No | 2018 | JUL | Yes | Line to Line | 1361600 | CSO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | LINCOLN-1104 | 153701104 | FUSE | 37455 | 20180714 | 1444 | 131699 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2430 | 38.952 | -121.2467 | 1 SPAN LD SIDE OF FUCO 37455 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0059847 | OH | Sus | 43401093 | No | 2018 | JUL | Yes | Line to Line | 1363787 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 20681 | 20180714 | 301 | 131365 | 543 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4887 | 38.7578 | -120.7646 | 2018 SHADOW RUN RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0059719 | OH | Sus | 31399831 | No | 2018 | JUL | Yes | Line to Line | 1363684 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2105 | 153652105 | FUSE | 11867 | 20180717 | 203 | 133397 | 493 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 13804 | 38.6813 | -120.9636 | 3434 MEDER RD. SHINGLE SPRINGS. | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0060399 | OH | Sus | 31400203 | yes | 2018 | JUL | Yes | Line to Ground | 1364279 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | OTHER | WIRE DOWN 1 S SW OF MTR# 1009669888 | 20180719 | 1105 | 135565 | 923 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11965 | 38.6845 | -120.7067 | 1 SPAN SW/O MTR 1009669888 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0061481 | OH | Sus | 0 | yes | 2018 | JUL | Yes | Line to Ground | 1365084 | PW | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 9503 | 20180720 | 911 | 136234 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 25186 | 39.056 | -120.9979 | 1 POLE E/O MTR 1004686667 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0061885 | OH | Sus | 43411966 | No | 2018 | JUL | Yes | Line to Line | 1365328 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 2117 | 20180721 | 23 | 136842 | 717 | Distribution Circuit | 3rd Party | Vehicle | 260 | 107552 | 38.6927 | -120.7921 | 1 P/W/O 20325 | Clear-32-90F | Pole-Wood | Broken, wire on object | 18-0062206 | OH | Sus | 0 | No | 2018 | JUL | Yes | Line to Ground | 1365489 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9387 | 20180724 | 646 | 138721 | 348 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 11100 | 38.9237 | -120.9073 | SYD RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0062963 | OH | Sus | 43415389 | yes | 2018 | JUL | Yes | Line to Ground | 1366151 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1101 | 152031101 | FUSE | 32729 | 20180726 | 1740 | 141209 | 605 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 12100 | 39.16 | -121.058 | 1 SPAN LD SIDE OF 32729 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 18-0064185 | OH | Sus | 31401407 | No | 2018 | JUL | Yes | Line to Ground | 1366952 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1102 | 152101102 | FUSE | 8003 | 20180807 | 1025 | 150415 | 3375 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 10125 | 39.4455 | -120.8236 | 5 P LD SIDE OF 8003 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 18-0067414 | OH | Sus | 31402447 | No | 2018 | AUG | Yes | Line to Line | 1369645 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 12615 | 20180810 | 1254 | 152960 | 396 | Distribution Circuit | 3rd Party | Vehicle | 67 | 26532 | 38.7995 | -120.7287 | S/E CORNER OF SWANSBORO AND SLUICE | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0068798 | OH | Sus | 0 | No | 2018 | AUG | Yes | Line to Line | 1370236 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 21039 | 20180810 | 1931 | 153204 | 391 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2737 | 38.6364 | -120.9106 | ACROSS FROM 5061 FRENCH CREEK RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0068883 | OH | Sus | 31402517 | No | 2018 | AUG | Yes | Line to Line | 1370273 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1112 | 153081112 | FUSE | 40501 | 20180819 | 57 | 157942 | 878 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 878 | 38.7276 | -120.8098 | at 40501 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0071403 | OH | Sus | 31403604 | No | 2018 | AUG | Yes | Line to Line | 1371813 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1107 | 152261107 | FUSE | 18637 | 20180821 | 1013 | 159351 | 363 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 4572 | 38.7033 | -120.8863 | 50FT E/OF MTR# 1009554344 |  | Conductor, Overhead | Broken, wire on ground | 18-0072055 | OH | Sus | 0 | No | 2018 | AUG | Yes | Line to Ground | 1372369 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7067 | 20180822 | 2106 | 160567 | 523 | Distribution Circuit | 3rd Party | Vehicle | 56 | 29288 | 39.1732 | -120.9739 | 1 P N/O MTR#1009804282 |  | Pole-Wood | Broken, wire on ground | 18-0072652 | OH | Sus | 31403893 | No | 2018 | AUG | Yes | Line to Line | 1372796 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 35424 | 20180826 | 1529 | 162711 | 492 | Distribution Circuit | Vegetation | Tree - fell into line | 240 | 36162 | 39.3432 | -121.1212 | MTR:1007742668 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0073601 | OH | Sus | 43448411 | No | 2018 | AUG | Yes | Line to Ground | 1373565 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHADY GLEN-1101 | 152431101 | FUSE | 6367 | 20180906 | 1619 | 169515 | 570 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 30780 | 39.0937 | -120.9486 | 24002 GRANDVIEW AVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0077280 | OH | Sus | 31405579 | No | 2018 | SEP | Yes | Line to Ground | 1376162 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 68757 | 20180912 | 108 | 172771 | 637 | Distribution Circuit | Vegetation | Tree - fell into line | 522 | 201054 | 38.7058 | -120.5996 | REAR OF 5215 SIERRA SPRINGS DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0078816 | OH | Sus | 31405955 | No | 2018 | SEP | Yes | Line to Line | 1377311 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 12847 | 20180917 | 1723 | 176131 | 580 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 8700 | 38.7469 | -120.8031 | 2621 BEDFORD AVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0080661 | OH | Sus | 31406618 | No | 2018 | SEP | Yes | Line to Line | 1378690 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1110 | 153081110 | RECLOSER | 19682 | 20180928 | 430 | 183102 | 726 | Distribution Circuit | Vegetation | Tree - fell into line | 337 | 72635 | 38.7642 | -120.8853 | HYLAND-TRAVIS/530-295-7076: 1300 los robles rd | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0084359 | OH | Sus | 0 | No | 2018 | SEP | Yes | Three Phase Fault | 1381294 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 10017 | 20181003 | 1328 | 187124 | 761 | Distribution Circuit | Vegetation | Tree - branch fell on line | 32 | 13534 | 38.5478 | -120.7355 | 3075 CEDAR CREEK RD | Partly Cloudy-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 18-0086198 | OH | Sus | 31410805 | yes | 2018 | OCT | Yes | Line to Ground | 1382721 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 39963 | 20181003 | 1815 | 187588 | 179 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 1611 | 39.1996 | -121.2674 | MTR# 1007547061 | Overcast-Heavy Rain-Lightning-32-90 F | Pole-Wood | Broken, wire on ground | 18-0086454 | OH | Sus | 0 | yes | 2018 | OCT | Yes | Line to Ground | 1382842 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 10559 | 20181003 | 1637 | 187443 | 657 | Distribution Circuit | Vegetation | Tree - fell into line | 83 | 54531 | 38.7899 | -120.9323 | 1181 ARROWBEE DR | Partly Cloudy-Heavy Rain-Lightning-32-90 F | Pole-Wood | Broken, wire on ground | 18-0086416 | OH | Sus | 0 | yes | 2018 | OCT | Yes | Line to Ground | 1382807 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | RECLOSER | 2234 | 20181003 | 1929 | 187698 | 734 | Distribution Circuit | Vegetation | Tree - fell into line | 258 | 78436 | 38.8955 | -121.1358 | 1 SPAN W/O C221 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0086427 | OH | Sus | 0 | yes | 2018 | OCT | Yes | Line to Ground | 1382817 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 19612 | 20181004 | 915 | 188141 | 366 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 899 | 291404 | 38.7621 | -120.5586 | 2 SPANS W/O 18507 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0086671 | OH | Sus | 0 | yes | 2018 | OCT | Yes | Line to Line | 1383030 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2108 | 153652108 | RECLOSER | 51474 | 20181004 | 720 | 187985 | 491 | Distribution Circuit | Equipment Failure/Involved | Overhead | 744 | 166014 | 38.657 | -120.9942 | DERYK-KEVIN/621/530-386-5111: cambridge rd between rco 18239 & rco 9369 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0086582 | OH | Sus | 0 | yes | 2018 | OCT | Yes | Line to Ground | 1382951 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 31467 | 20181005 | 1915 | 189383 | 455 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5460 | 39.1257 | -121.0845 | APPROX 2 SPANS TO THE SOUTH OF NORTH & SOUTH SPLIT | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0087527 | OH | Sus | 31411545 | No | 2018 | OCT | Yes | Line to Ground | 1383469 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | CLARKSVILLE-2104 | 153612104 | FUSE | 2043 | 20181019 | 1306 | 198660 | 684 | Distribution Circuit | 3rd Party | Vehicle | 12 | 2498 | 38.7091 | -121.0412 | 1880 GREEN VALLEY RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0092201 | OH | Sus | 0 | No | 2018 | OCT | Yes | Line to Ground | 1386897 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 20781 | 20181104 | 1351 | 208606 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 1459 | 38.6165 | -120.9278 | 1800 VIA ROSA LN | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0096946 | OH | Sus | 31415040 | No | 2018 | NOV | Yes | Line to Ground | 1390427 | CSO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | EL DORADO PH-2101 | 152762101 | RECLOSER | 52456 | 20181111 | 436 | 213229 | 829 | Distribution Circuit | Vegetation | Tree - fell into line | 1082 | 81114 | 38.7754 | -120.4024 | BET 22785 & 2447 ON MAIN LINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0098895 | OH | Sus | 43538398 | No | 2018 | NOV | Yes | Line to Ground | 1391973 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE | 1467 | 20181117 | 1720 | 217489 | 682 | Distribution Circuit | 3rd Party | Vehicle | 54 | 35749 | 38.7046 | -120.7072 | 4570 NEWTOWN RD- MTR# 1005220428 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0100697 | OH | Sus | 0 | No | 2018 | NOV | Yes | Line to Ground | 1393264 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7065 | 20181123 | 1724 | 223127 | 1241 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 62050 | 39.187 | -120.9556 | 14333 SONTAG RD GRASS VALLEY | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102650 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1394743 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 63823 | 20181123 | 2226 | 223269 | 1156 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 63580 | 38.8591 | -120.8471 | 5 SPANS S/O 9391 at .5 SPAN S/O 5803 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102719 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Line | 1394812 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2108 | 153652108 | FUSE | 10361 | 20181123 | 2204 | 223239 | 815 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 33586 | 38.658 | -120.9846 | 3875 RUSTIC RD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102721 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Line | 1394814 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 12187 | 20181124 | 954 | 223561 | 227 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 12939 | 38.7074 | -120.6802 | 1 S/OF CGC223770038006 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102775 | OH | Sus | 0 | No | 2018 | NOV | Yes | Line to Line | 1394857 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 18569 | 20181203 | 1357 | 232805 | 703 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2109 | 38.747 | -120.6238 | 223925839694 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 18-0106563 | OH | Sus | 31417523 | No | 2018 | DEC | Yes | Line to Line | 1397378 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1102 | 152481102 | FUSE | 33701 | 20181212 | 1954 | 238996 | 313 | Distribution Circuit | 3rd Party | Vehicle | 2 | 626 | 39.213 | -121.0175 | 8 S/OF 33701 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on object | 18-0108882 | OH | Sus | 0 | No | 2018 | DEC | Yes | Three Phase Fault | 1399268 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE | 7123 | 20181224 | 1657 | 246631 | 1468 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 15385 | 39.254 | -121.057 | 3 P/W/O & 1 P/N/O 7123 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0110553 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Ground | 1401633 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 34485 | 20181225 | 354 | 246976 | 583 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 16770 | 39.1233 | -121.0615 | 17235 BIVENS PLACE | Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110610 | OH | Sus | 31419572 | No | 2018 | DEC | Yes | Line to Line | 1401691 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE | 5939 | 20181227 | 820 | 247856 | 908 | Distribution Circuit | 3rd Party | Vehicle | 40 | 9970 | 39.0098 | -120.8444 | 2 SPANS E/OF 22830 FOREST HILL RD | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 18-0110808 | OH | Sus | 0 | No | 2018 | DEC | Yes | Line to Line | 1401934 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1102 | 152241102 | FUSE | 8487 | 20181229 | 1751 | 249470 | 270 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 13 | 3510 | 38.9855 | -121.0061 | 2 SPANS LD SIDE OF FUCO 8487 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0111067 | OH | Sus | 0 | No | 2018 | DEC | Yes | Force Out | 1402286 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 10321 | 20181231 | 734 | 249980 | 167 | Distribution Circuit | Equipment Failure/Involved | Overhead | 88 | 13500 | 38.8032 | -120.9305 | 1/W/OF MTR# 1007389443 | Clear-32-90 F | Insulator | Broken, wire on object | 18-0111175 | OH | Sus | 31420188 | yes | 2018 | DEC | Yes | Line to Ground | 1402404 | INS | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 35466 | 20190105 | 1321 | 254168 | 284 | Distribution Circuit | Vegetation | Tree - fell into line | 524 | 65739 | 38.9124 | -120.932 | 1681 SHELTER COVE DR- GREENWOOD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0004763 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Three Phase Fault | 1403314 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 7697 | 20190105 | 1325 | 254170 | 459 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 8481 | 38.863 | -120.8662 | CGC #223250543885 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0004890 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1403426 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | OTHER | WIRE DOWN N/O 91317 TWD 5381 | 20190105 | 943 | 253586 | 272 | Distribution Circuit | Equipment Failure/Involved | Overhead | 838 | 76218 | 38.9236 | -121.1772 | N/O 91317 TWD 5381 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0004666 | OH | Sus | 43626489 | yes | 2019 | JAN | Yes | Open Circuit | 1403227 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1101 | 152101101 | FUSE | 35275 | 20190107 | 1236 | 259368 | 1598 | Distribution Circuit | Environmental/External | Ice or snow | 8 | 12784 | 39.5525 | -120.7846 | POLE SAP ID# 100103531 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005957 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1404283 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 20481 | 20190108 | 229 | 260080 | 536 | Distribution Circuit | Equipment Failure/Involved | Overhead | 26 | 13936 | 38.7678 | -120.9511 | 2P S/O CGC #222999540175 | Overcast-32-90 F | Insulator | Broken, wire on ground | 19-0006079 | OH | Sus | 31421284 | yes | 2019 | JAN | Yes | Line to Ground | 1404394 | INS | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 7957 | 20190115 | 2127 | 266378 | 805 | Distribution Circuit | Vegetation | Tree - fell into line | 167 | 84150 | 38.707 | -120.6003 | CGC 223989638175 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0009348 | OH | Sus | 31421994 | yes | 2019 | JAN | Yes | Line to Ground | 1406468 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1111 | 153081111 | FUSE | 22381 | 20190115 | 2148 | 266384 | 818 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 6544 | 38.7236 | -120.8352 | 7141 HELMRICH LN- PLACERVILLE | Overcast-Fog-Drizzle-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 19-0009339 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1406459 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | FUSE | 4429 | 20190115 | 2037 | 266338 | 1015 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 5075 | 38.8833 | -121.1466 | 1/S/O 4429 | Partly Cloudy-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0009333 | OH | Sus | 31422310 | yes | 2019 | JAN | Yes | Line to Ground | 1406453 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6617 | 20190118 | 724 | 275239 | 1741 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 95755 | 39.3202 | -120.4334 | Turney- Robert 530-205-6563: 2 spans L/S 6617 | Overcast-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0011942 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Open Circuit | 1408276 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 8875 | 20190120 | 1112 | 277219 | 908 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1014 | 39.2123 | -121.2338 | TASSONE- LOUIS/530-682-6302: 20540 1S & 1/E OF 8875 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0012558 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408894 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE | 5681 | 20190121 | 927 | 278158 | 515 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1030 | 39.0094 | -120.8438 | 3/S/O 5681 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012885 | OH | Sus | 0 | No | 2019 | JAN | Yes | Line to Ground | 1409225 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8865 | 20190203 | 1450 | 288897 | 719 | Distribution Circuit | Vegetation | Tree - branch fell on line | 43 | 3917 | 39.3069 | -121.1523 | 1 SPAN LD SIDE OF CGC 222367959879 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017581 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411996 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 84629 | 20190203 | 1517 | 289080 | 353 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 15179 | 38.7531 | -120.7765 | 1 SPAN N OF 84629 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017602 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412016 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 21031 | 20190203 | 1137 | 288764 | 368 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2208 | 38.6551 | -120.9103 | 2/E/O 21031 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017538 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411947 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 22561 | 20190206 | 1518 | 294506 | 1469 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 4407 | 38.6913 | -120.6936 | Turney- Robert 530-205-6563: 4 poles L/S 22561 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0019270 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413227 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 18789 | 20190206 | 1647 | 294591 | 2708 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 56868 | 38.6816 | -120.719 | 3099 SPRINGER RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0019316 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413252 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 18795 | 20190206 | 1212 | 294291 | 1768 | Distribution Circuit | Environmental/External | Ice or snow | 30 | 53040 | 38.6778 | -120.7463 | MELLO- ADAM 530-401-5814/T5429: wire down at mtr1007387147 2387 tsi la gi rd- just off pleasant vall | Clear-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0019321 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413257 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 2591 | 20190206 | 1212 | 294292 | 1937 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 67795 | 38.6584 | -120.7816 | 7247 HORSESHOE LN | Clear-32-90 F | Insulator | Broken, wire on object | 19-0019339 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413273 | INS | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 1029 | 20190206 | 1211 | 294427 | 1941 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 50466 | 38.6519 | -120.7816 | 5610 ROCKY RIDGE RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0019353 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413286 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21511 | 20190207 | 2151 | 295892 | 2311 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 6933 | 38.6365 | -120.6464 | 7030 GRIZZLY FLAT | Overcast-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0019900 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413690 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 21385 | 20190207 | 819 | 295048 | 651 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 12369 | 38.6938 | -120.6192 | 4 SPANS E/O MTR #1007413725 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0019627 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413490 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 4105 | 20190207 | 1237 | 295387 | 524 | Distribution Circuit | Environmental/External | Ice or snow | 11 | 5764 | 38.9137 | -120.6793 | 4 SPAN LD SIDE OF4105 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on object | 19-0019701 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413524 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 18279 | 20190208 | 708 | 295926 | 1991 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 15928 | 38.6347 | -120.6076 | MTR 1007480279 | Partly Cloudy-Below 32 F | Crossarm, Wood | Broken, wire on ground | 19-0019955 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413722 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 11427 | 20190208 | 526 | 295897 | 1910 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 13224 | 38.6858 | -120.6419 | 2501 PARK HIL DR/MTR 1009125971 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0019980 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413746 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 10019 | 20190208 | 1341 | 296312 | 1571 | Distribution Circuit | Vegetation | Tree - branch fell on line | 88 | 138248 | 38.5706 | -120.6951 | Cramer- Chris: 5 spans S/O cutouts 10021 | Overcast-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0020069 | OH | Sus | 43666953 | yes | 2019 | FEB | Yes | Line to Ground | 1413786 | CSO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 18841 | 20190208 | 1352 | 296315 | 4385 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 153475 | 38.5729 | -120.6568 | 4757 COYOTEVILLE LN- 4040 CEDAR CREEK RD & CEDAR CREEK & COYOTEVILLE RD | Overcast-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0020093 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413800 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | ALLEGHANY-1101 | 152101101 | FUSE | 32493 | 20190211 | 1320 | 299971 | 196 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 392 | 39.5652 | -120.6373 | TASSONE- LOUIS/530-682-6302: H | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0021095 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414739 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 1381 | 20190211 | 1840 | 300252 | 1445 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 28900 | 38.7556 | -120.6011 | WIRE DOWN 9 SP LD SIDE 1381 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0021312 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414877 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 1309 | 20190211 | 619 | 299525 | 605 | Distribution Circuit | Equipment Failure/Involved | Overhead | 20 | 12100 | 38.7857 | -120.6076 | 4 LD SIDE OF 1309 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0020947 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1414636 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE | 18531 | 20190218 | 725 | 317224 | 1835 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 11010 | 38.7627 | -120.7059 | Bennett- Jeffrey: 3734 N Canyon Rd | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0025594 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Three Phase Fault | 1418641 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 3369 | 20190218 | 1619 | 318060 | 1490 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 10430 | 38.7521 | -120.6284 | 5 SPANS LD SIDE OF 3369 | Clear-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0025900 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1418909 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | EL DORADO PH-2101 | 152762101 | FUSE | 2435 | 20190219 | 2330 | 319522 | 1030 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 18540 | 38.7661 | -120.3781 | 1 SPAN LD SIDE OF CGC 224629640343 | Overcast-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0026385 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1419196 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | RECLOSER | 2054 | 20190224 | 1810 | 322546 | 773 | Distribution Circuit | 3rd Party | Vehicle | 213 | 36863 | 38.8963 | -121.1201 | 1720 BALD HILL RD | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0027594 | OH | Sus | 0 | No | 2019 | FEB | Yes | Line to Line | 1419877 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1103 | 152481103 | FUSE | 33109 | 20190225 | 2303 | 323665 | 799 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2397 | 39.2469 | -121.0159 | 3/S/O 33109 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028051 | OH | Sus | 31426368 | yes | 2019 | FEB | Yes | Line to Line | 1420161 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1105 | 152561105 | FUSE | 5557 | 20190225 | 2329 | 323707 | 1032 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 71742 | 38.8595 | -121.1567 | Turney- Robert 530-205-6563: 1 span L/S fuses 5557 | Partly Cloudy-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028080 | OH | Sus | 31426665 | yes | 2019 | FEB | Yes | Line to Ground | 1420191 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 22127 | 20190228 | 2046 | 328473 | 1032 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3096 | 38.7608 | -120.6129 | 2 SPANS LD SIDE OF 22127 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029621 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1421184 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | FUSE | 5775 | 20190228 | 402 | 327697 | 779 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 37392 | 39.0211 | -121.1003 | 10200 HIDDEN HILL | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029304 | OH | Sus | 31426712 | yes | 2019 | FEB | Yes | Line to Ground | 1421032 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 9637 | 20190301 | 855 | 328684 | 472 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 472 | 39.29 | -120.9849 | 12999 HOGUE RD. | Overcast-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 19-0029711 | OH | Sus | 31426712 | yes | 2019 | MAR | Yes | Line to Ground | 1421283 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SPAULDING-1101 | 152251101 | JUMPER | WIRE DOWN 2 SPANS FROM EOL | 20190301 | 1002 | 328777 | 1636 | Distribution Circuit | Environmental/External | Ice or snow | 2 | 3272 | 39.3167 | -120.6542 | JOHNSTON-M/1508/530-906-5563: co 9220 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0029710 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1421282 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SPAULDING-1101 | 152251101 | RECLOSER | 578852 | 20190302 | 2313 | 329931 | 1415 | Distribution Circuit | Equipment Failure/Involved | Overhead | 360 | 306346 | 39.3251 | -120.6428 | PASQUA-MARK: 4 spans load side 9201 laing rd. | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0030216 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1421671 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1102 | 152241102 | RECLOSER | 39104 | 20190304 | 1446 | 330910 | 406 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 892 | 69140 | 38.9734 | -121.014 | Turney- Robert 530-205-6563: 17855 Lake Arthur Rd | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0030554 | OH | Sus | 0 | No | 2019 | MAR | Yes | Line to Ground | 1421900 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1110 | 152481110 | RECLOSER | 1252 | 20190306 | 924 | 332534 | 784 | Distribution Circuit | Vegetation | Tree - fell into line | 882 | 119961 | 39.2321 | -121.1071 | CRAMER- CHRIS: 15289 Pleasant Valley rd | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031205 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Three Phase Fault | 1422269 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11545 | 20190306 | 1412 | 332932 | 391 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 13294 | 38.6758 | -120.9431 | 2 SPANS LD SIDE OF 11545 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031401 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1422361 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 7742 | 20190306 | 1121 | 332702 | 287 | Distribution Circuit | Vegetation | Tree - fell into line | 706 | 98067 | 38.6615 | -120.9109 | 1600 HIDDEN CIR SHINGLE SPRINGS | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031255 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1422297 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1102 | 152101102 | FUSE | 8021 | 20190308 | 1039 | 334336 | 3174 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 28566 | 39.4628 | -120.8506 | DOWN BY CREEK | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0032010 | OH | Sus | 31426711 | No | 2019 | MAR | Yes | Line to Ground | 1422797 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 4173 | 20190308 | 841 | 334177 | 426 | Distribution Circuit | Vegetation | Tree - fell into line | 95 | 40470 | 39.109 | -121.0301 | 19739 WOLFCREEK RD GRASS VALLEY | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031972 | OH | Sus | 31426712 | No | 2019 | MAR | Yes | Line to Line | 1422769 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9235 | 20190311 | 1957 | 336700 | 660 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 16480 | 38.9217 | -120.896 | CRAMER- CHRIS: between 8th and 9th span loadside of 6585 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0032804 | OH | Sus | 31428317 | No | 2019 | MAR | Yes | Line to Line | 1423368 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE | 6257 | 20190314 | 1350 | 339166 | 1355 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 1355 | 39.0662 | -120.769 | 31 SPANS LD SIDE OF 6257 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033911 | OH | Sus | 43706156 | No | 2019 | MAR | Yes | Force Out | 1424176 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 3377 | 20190316 | 1401 | 340838 | 409 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 172 | 27628 | 38.944 | -120.7213 | 3814 VOLCANOEVILLE RD- GEORGETOWN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0034396 | OH | Sus | 43708965 | No | 2019 | MAR | Yes | Line to Ground | 1424568 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | DRUM-1101 | 152321101 | FUSE | 9215 | 20190320 | 1536 | 344127 | 2547 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 45846 | 39.276 | -120.7173 | 5 SP LD SIDE OF C/OUTS | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0035559 | OH | Sus | 31430011 | yes | 2019 | MAR | Yes | Force Out | 1425358 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE | 1463 | 20190322 | 2200 | 345608 | 940 | Distribution Circuit | Equipment Failure/Involved | Overhead | 250 | 41105 | 38.7471 | -120.6443 | at MTR # 1007392440 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0036243 | OH | Sus | 31429931 | No | 2019 | MAR | Yes | Line to Line | 1425793 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 34035 | 20190327 | 2232 | 349073 | 883 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 23841 | 39.0574 | -121.0875 | 22307 CAMEO DR | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0037705 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Line | 1426813 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 9103 | 20190327 | 1416 | 348619 | 242 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 4893 | 38.8109 | -120.9108 | 7330 AMALOC LN | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0037562 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Line | 1426714 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1107 | 152561107 | FUSE | 32061 | 20190328 | 1454 | 349655 | 292 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 3181 | 38.8315 | -121.1686 | 3211 BOULDER CREEK PL | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0038063 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1427036 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2105 | 153652105 | FUSE | 11871 | 20190328 | 1415 | 349607 | 750 | Distribution Circuit | 3rd Party | Vehicle | 124 | 93000 | 38.6829 | -120.9697 | JESSEE-BEN /620/ 916-826-8237: MEDER RD AT COROUSEL LN | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0038011 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Three Phase Fault | 1427017 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | OTHER | WIRE DOWN @ CGC 222413555077 | 20190330 | 1905 | 350944 | 1225 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3675 | 39.1755 | -121.149 | CGC 222413555077 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0038532 | OH | Sus | 31431780 | No | 2019 | MAR | Yes | Open Circuit | 1427413 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 6852 | 20190409 | 1959 | 357541 | 549 | Distribution Circuit | Vegetation | Tree - fell into line | 2947 | 172128 | 38.7612 | -120.5582 | FLECKLIN-PAUL/623/530-906-3142: 1 SP SOUTH OF 669489 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0041137 | OH | Sus | 43731293 | yes | 2019 | APR | Yes | Line to Ground | 1429231 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 7201 | 20190409 | 1409 | 356726 | 1428 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 54 | 77112 | 39.1665 | -121.1996 | FUCO 36327 NORTH AND SOUTH OF THIS LOCATION | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0040985 | OH | Sus | 31433414 | yes | 2019 | APR | Yes | Line to Line | 1429104 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1102 | 152491102 | FUSE | 6399 | 20190414 | 1717 | 360622 | 709 | Distribution Circuit | Vegetation | Tree - fell into line | 223 | 63247 | 39.0372 | -121.0037 | 2 SPANS LD OF 6399 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0042338 | OH | Sus | 43738675 | No | 2019 | APR | Yes | Three Phase Fault | 1430172 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | JUMPER | WIRE DOWN 1 W/O CGC 223027237702 | 20190416 | 839 | 361657 | 461 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4922 | 38.697 | -120.9409 | WIRE DOWN 1 W/O CGC 223027237702 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0042829 | OH | Sus | 31434366 | No | 2019 | APR | Yes | Open Circuit | 1430502 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1110 | 152691110 | RECLOSER | 2408 | 20190418 | 1951 | 363414 | 508 | Distribution Circuit | Vegetation | Tree - branch fell on line | 448 | 112578 | 39.0472 | -121.0488 | MAINLINE at FUCO 7495 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0044192 | OH | Sus | 43745123 | No | 2019 | APR | Yes | Three Phase Fault | 1431433 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1102 | 152491102 | OTHER | WIRE DOWN 2 E/O CGC 222833550415 | 20190427 | 1818 | 369355 | 452 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 13040 | 39.047 | -121.0021 | 2 SPANS E/O CGC 222833550415 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0046776 | OH | Sus | 43754427 | No | 2019 | APR | Yes | Open Circuit | 1433168 | CSO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 130441 | 20190503 | 1614 | 373362 | 1113 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 3 | 3339 | 39.2056 | -120.7994 | 1ST SPAN FROM 130441 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0048789 | OH | Sus | 43763521 | No | 2019 | MAY | Yes | Line to Line | 1434457 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 20259 | 20190504 | 1753 | 373803 | 673 | Distribution Circuit | 3rd Party | Vehicle | 12 | 8076 | 38.6057 | -120.8451 | 13 P/N OF 20259- UNION MINE RD. AND RIVERFRONT TRL | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0048916 | OH | Sus | 0 | No | 2019 | MAY | Yes | Line to Line | 1434596 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 6893 | 20190516 | 51 | 381830 | 715 | Distribution Circuit | 3rd Party | Vehicle | 5 | 3575 | 39.1463 | -121.031 | 3 S/OF 6893 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 19-0052502 | OH | Sus | 31441073 | yes | 2019 | MAY | Yes | Multi-Fault | 1437148 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1107 | 152561107 | FUSE | 8649 | 20190516 | 1441 | 382638 | 316 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 9480 | 38.7937 | -121.1372 | S/O MTR 1004116303 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052973 | OH | Sus | 43784712 | yes | 2019 | MAY | Yes | Line to Ground | 1437373 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1107 | 152561107 | FUSE | 8655 | 20190517 | 1005 | 383488 | 286 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 2288 | 38.7903 | -121.1638 | MTR 1003844721 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053313 | OH | Sus | 31442244 | No | 2019 | MAY | Yes | Line to Ground | 1437654 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SPAULDING-1101 | 152251101 | FUSE | 5999 | 20190517 | 640 | 383277 | 309 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1545 | 39.3157 | -120.614 | 20 SPANS LD SIDE OF 5999 | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0053149 | OH | Sus | 31441698 | No | 2019 | MAY | Yes | Line to Ground | 1437537 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 51792 | 20190518 | 1049 | 384173 | 1517 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 854 | 39115 | 38.6435 | -120.6959 | FLECKLIN-PAUL/623/530-906-3142: 1 SPAN SOUTH OF RCO22921 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053633 | OH | Sus | 31442271 | yes | 2019 | MAY | Yes | Force Out | 1437878 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 41425 | 20190519 | 134 | 384963 | 946 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1892 | 39.128 | -121.0377 | 1 SP LD SD OF FUCO 41425 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0053919 | OH | Sus | 31442803 | yes | 2019 | MAY | Yes | Line to Line | 1438127 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 9235 | 20190519 | 421 | 384781 | 860 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 45202 | 38.9217 | -120.896 | 2 SP E/O 6585 C/OUTS | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053861 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1438074 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1112 | 153081112 | FUSE | 21087 | 20190519 | 1530 | 385460 | 658 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 20398 | 38.7368 | -120.8317 | FLECKLIN-PAUL/623/530-906-3142: 2580 ANDLER RD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053999 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Three Phase Fault | 1438206 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7041 | 20190521 | 421 | 386629 | 833 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 14236 | 39.1982 | -121.022 | AT 7041 | Overcast-Fog-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0054671 | OH | Sus | 31443609 | yes | 2019 | MAY | Yes | Line to Ground | 1438703 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 20190522 | 2214 | 388407 | 620 | Distribution Circuit | Vegetation | Tree - fell into line | 1519 | 164750 | 39.0996 | -121.05 | 18541 WOLF RD. | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0055774 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1439496 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | OCB | 2102/2 | 20190525 | 2201 | 390387 | 860 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 7493 | 761542 | 38.7394 | -120.6774 | LUNA- MARCOS: 1 W/O 18045 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0057690 | OH | Sus | 43798262 | yes | 2019 | MAY | Yes | Line to Ground | 1441196 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | CLARKSVILLE-2103 | 153612103 | FUSE | 12873 | 20190527 | 1424 | 391296 | 311 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 2451 | 38.6239 | -121.0232 | CGC: 222774234923 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0057985 | OH | Sus | 43798523 | No | 2019 | MAY | Yes | Line to Ground | 1441490 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 18745 | 20190530 | 1136 | 393560 | 669 | Distribution Circuit | 3rd Party | Vehicle | 2307 | 31959 | 38.6734 | -120.7226 | 7 POLES LD SIDE OF 18745 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0060037 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Force Out | 1443274 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 26000 | 20190531 | 1802 | 394759 | 216 | Distribution Circuit | Vegetation | Tree - fell into line | 640 | 44946 | 38.7525 | -120.5549 | 14 SPANS N/O 7575 | Partly Cloudy-Drizzle-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0060944 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1443810 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE | 32029 | 20190602 | 1454 | 395829 | 697 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 18819 | 38.9998 | -120.8892 | 20690 CEDAR VIEW RD | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0061526 | OH | Sus | 31450099 | yes | 2019 | JUN | Yes | Line to Line | 1444392 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 6765 | 20190611 | 1531 | 406057 | 1499 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 17988 | 39.4908 | -121.0863 | MTR 1010464282 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 19-0066225 | OH | Sus | 31453372 | yes | 2019 | JUN | Yes | Line to Ground | 1448158 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7053 | 20190612 | 1227 | 407668 | 652 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 13488 | 39.1909 | -120.9934 | 1324 DAY RD- GRASS VALLEY | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 19-0066713 | OH | Sus | 0 | yes | 2019 | JUN | Yes | Line to Line | 1448554 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 63823 | 20190621 | 145 | 425204 | 1233 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 23024 | 38.8591 | -120.8471 | REAR OF 4180 MT EATON RD AT FUCO POLE 40283 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0070502 | OH | Sus | 31454891 | yes | 2019 | JUN | Yes | Line to Ground | 1451411 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BELL-1107 | 152701107 | FUSE | 9919 | 20190622 | 256 | 425993 | 366 | Distribution Circuit | Vegetation | Tree - branch fell on line | 54 | 18289 | 38.9632 | -121.1358 | TURNEY- ROBERT 530-205-6563: 2 Poles E/O 9101 Hubbard Rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0070977 | OH | Sus | 31454899 | No | 2019 | JUN | Yes | Line to Ground | 1451786 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BELL-1108 | 152701108 | OTHER | WIRE DOWN @ MTR 1004700202 | 20190629 | 1236 | 436279 | 317 | Distribution Circuit | Vegetation | Tree - fell into line | 838 | 9896 | 38.9841 | -121.073 | 1004700202 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0073362 | OH | Sus | 43862162 | No | 2019 | JUN | Yes | Open Circuit | 1453636 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER | 1101/2 | 20190711 | 1506 | 445366 | 1667 | Distribution Circuit | Vegetation | Tree - fell into line | 1074 | 416401 | 39.4655 | -120.8444 | 2.5 SPANS LD SIDE OF CGC 223775069500 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0076481 | OH | Sus | 31457100 | No | 2019 | JUL | Yes | Line to Ground | 1455555 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BELL-1108 | 152701108 | TRIP-SAVER | 5703 | 20190717 | 2323 | 456965 | 358 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 30230 | 38.9965 | -121.1079 | 5700 WINDING WY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0078609 | OH | Sus | 0 | No | 2019 | JUL | Yes | Line to Line | 1456992 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1102 | 152241102 | FUSE | 6123 | 20190721 | 919 | 464982 | 438 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 32850 | 38.9793 | -121.0077 | SAP ID #100034283 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0079578 | OH | Sus | 31459401 | No | 2019 | JUL | Yes | Line to Ground | 1457689 | CSO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1101 | 152491101 | FUSE | 6189 | 20190725 | 7 | 470801 | 588 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 7845 | 39.0685 | -120.9796 | 750 MOUNT HOWELL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0080924 | OH | Sus | 31459905 | No | 2019 | JUL | Yes | Line to Ground | 1458539 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1103 | 152561103 | FUSE | 5211 | 20190726 | 1811 | 472836 | 493 | Distribution Circuit | Vegetation | Tree - branch fell on line | 89 | 22165 | 38.84 | -121.1387 | CGC 222483142986 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 19-0081702 | OH | Sus | 43899504 | No | 2019 | JUL | Yes | Line to Ground | 1458995 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 1443 | 20190726 | 1159 | 472538 | 185 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 16465 | 38.7977 | -120.8206 | 7801 BAYNE RD- KELSEY | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0081559 | OH | Sus | 31460039 | No | 2019 | JUL | Yes | Line to Ground | 1458944 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 34485 | 20190730 | 1513 | 475744 | 540 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 31302 | 39.1233 | -121.0615 | NORTH OF AND SOUTH OF THE MTR#1007664969 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0082713 | OH | Sus | 31460550 | No | 2019 | JUL | Yes | Line to Ground | 1459733 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1107 | 152691107 | FUSE | 7563 | 20190806 | 940 | 486513 | 436 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 27468 | 39.0202 | -121.0618 | 27289 TABLE MEADOW RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0084727 | OH | Sus | 31461213 | No | 2019 | AUG | Yes | Line to Ground | 1461111 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 1161 | 20190812 | 1734 | 504678 | 629 | Distribution Circuit | Vegetation | Tree - fell into line | 178 | 54604 | 38.6755 | -120.7512 | SAP ID 101404439 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0087080 | OH | Sus | 31462345 | No | 2019 | AUG | Yes | Line to Line | 1462514 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11551 | 20190825 | 318 | 537969 | 500 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 5500 | 38.6806 | -120.9397 | 4073 CACTUS RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0091864 | OH | Sus | 43937783 | No | 2019 | AUG | Yes | Line to Line | 1465624 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1102 | 152181102 | FUSE | 7781 | 20190828 | 1414 | 545474 | 689 | Distribution Circuit | 3rd Party | Vehicle | 37 | 5693 | 39.0181 | -120.8484 | MTR# 1004895119 | Partly Cloudy-Above 90 | Pole-Wood | Broken, wire on ground | 19-0093211 | OH | Sus | 0 | No | 2019 | AUG | Yes | Line to Line | 1466435 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 2224 | 20190829 | 1816 | 547563 | 520 | Distribution Circuit | Equipment Failure/Involved | Overhead | 997 | 419630 | 38.9052 | -120.8373 | NE/O 32343 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0093811 | OH | Sus | 43941620 | No | 2019 | AUG | Yes | Line to Line | 1466689 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 30295 | 20190831 | 2058 | 550194 | 927 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4047 | 39.1236 | -121.0362 | 5/E/O 30295 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0094402 | OH | Sus | 31470340 | No | 2019 | AUG | Yes | Line to Line | 1467040 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1103 | 152561103 | RECLOSER | 604 | 20190831 | 146 | 549295 | 783 | Distribution Circuit | 3rd Party | Vehicle | 323 | 103545 | 38.8543 | -121.1505 | 1/E/O 590165 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0094271 | OH | Sus | 31470227 | No | 2019 | AUG | Yes | Three Phase Fault | 1466939 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE | 7007 | 20190905 | 1052 | 555293 | 692 | Distribution Circuit | 3rd Party | Vehicle | 22 | 15224 | 39.2127 | -120.9876 | CORNER OF GREENHORN RD AND BACCARAT CT | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0095609 | OH | Sus | 0 | No | 2019 | SEP | Yes | Line to Line | 1467894 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 97061 | 20190907 | 1823 | 562195 | 798 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 31512 | 38.7478 | -120.7972 | 2161 BEAR ROCK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0096494 | OH | Sus | 0 | yes | 2019 | SEP | Yes | Line to Line | 1468399 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE | 44621 | 20190916 | 819 | 583915 | 295 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 8555 | 39.141 | -121.1644 | JENSEN- WILLIAMS: 17450 royal oaks pl | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0099421 | OH | Sus | 43957669 | yes | 2019 | SEP | Yes | Line to Line | 1470286 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1102 | 152241102 | TRIP-SAVER | 5739 | 20190916 | 1725 | 585562 | 1011 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 21742 | 38.9696 | -121.0157 | 2 SPANS LD SIDE OF TRIP SAVER 5739 | Overcast-Heavy Rain-Lightning-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0099929 | OH | Sus | 31471972 | yes | 2019 | SEP | Yes | Line to Ground | 1470487 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 3541 | 20190919 | 2111 | 595867 | 518 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1036 | 39.1044 | -121.0053 | CROOKS- MICHAEL: 13979 OWL HILL CT | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0101553 | OH | Sus | 31472702 | No | 2019 | SEP | Yes | Line to Line | 1471401 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1184 | 20190928 | 2029 | 628328 | 441 | Distribution Circuit | Vegetation | Tree - fell into line | 302 | 61552 | 38.8993 | -120.8546 | TOMASI-MIKE 916-747-0242: 2708 illinois canyon rd | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0105043 | OH | Sus | 0 | yes | 2019 | SEP | Yes | Line to Ground | 1473820 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 4257 | 20190929 | 46 | 628426 | 824 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 32960 | 39.1043 | -121.0917 | 18458 WATERFALL LANE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0105098 | OH | Sus | 0 | No | 2019 | SEP | Yes | Line to Line | 1473876 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | RECLOSER | 1006 | 20191015 | 724 | 658805 | 396 | Distribution Circuit | Animal | Bird found | 1519 | 79872 | 39.0996 | -121.05 | JENSEN- BILL: 16481 norlene way | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0111599 | OH | Sus | 43999653 | No | 2019 | OCT | Yes | Three Phase Fault | 1480039 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 63464 | 20191021 | 2039 | 676532 | 222 | Distribution Circuit | Vegetation | Tree - fell into line | 1156 | 21895 | 38.7607 | -120.5049 | 4 SPANS SS OF 2417 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0114251 | OH | Sus | 44047326 | No | 2019 | OCT | Yes | Line to Ground | 1481655 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20191101 | 801 | 697231 | 759 | Distribution Circuit | 3rd Party | Vehicle | 1029 | 142995 | 38.8155 | -120.8221 | 1 POLE E/O 4271 | Clear-32-90 F | Pole-Wood | Broken, wire on object | 19-0119824 | OH | Sus | 0 | No | 2019 | NOV | Yes | Force Out | 1488648 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | RECLOSER | 2748 | 20191113 | 126 | 705675 | 1045 | Distribution Circuit | 3rd Party | Vehicle | 890 | 87668 | 39.2081 | -121.2033 | FUCO 8391 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0124136 | OH | Sus | 0 | No | 2019 | NOV | Yes | Line to Ground | 1490838 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | OTHER | BROKEN SPLICE | 20191119 | 1405 | 710357 | 22 | Distribution Circuit | Equipment Failure/Involved | Overhead | 76 | 1672 | 38.7147 | -120.6082 | 4800 SIERRA SPRINGS DR | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on object | 19-0126412 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Open Circuit | 1492584 | CSO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | OTHER | 13512 | 20191128 | 1422 | 723089 | 154 | Distribution Circuit | Equipment Failure/Involved | Overhead | 894 | 32890 | 38.7602 | -120.6125 | N/OF 22109 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0130909 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Force Out | 1495597 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | SHADY GLEN-1102 | 152431102 | FUSE | 6361 | 20191128 | 748 | 722657 | 631 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3786 | 39.157 | -120.8886 | 3 SPANS LD SIDE OF 6361 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0130807 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Line | 1495491 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE | 36689 | 20191130 | 2350 | 725392 | 1133 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4481 | 39.2022 | -121.0878 | CROOKS- MICHAEL: 10976 BONNIEVIEW WY | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0131866 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Three Phase Fault | 1496566 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21121 | 20191202 | 505 | 726994 | 350 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2100 | 38.6788 | -120.7208 | 3 SPANS LOAD SIDE OF 21121 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0132165 | OH | Sus | 0 | No | 2019 | DEC | Yes | Line to Ground | 1496849 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | OTHER | WIRE DOWN @ MTR#101021730 | 20191202 | 1540 | 727839 | 180 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 180 | 38.7812 | -120.62 | 3 SPAN SOURCE SIDE OF MTR 1010217130 | Overcast-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on object | 19-0132585 | OH | Sus | 0 | No | 2019 | DEC | Yes | Force Out | 1497001 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6617 | 20191208 | 859 | 733743 | 525 | Distribution Circuit | Equipment Failure/Involved | Overhead | 55 | 19179 | 39.3202 | -120.4334 | 5 SPANS LD SIDE OF FU 6653 SAP ID# 100002185 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0135036 | OH | Sus | 0 | No | 2019 | DEC | Yes | Line to Ground | 1498828 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 8253 | 20200102 | 1233 | 753797 | 214 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 464 | 57925 | 39.2867 | -121.0268 | 16623 LAKE VERA PURDON RD. NEVADA CITY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0004496 | OH | Sus | 44143162 | No | 2020 | JAN | Yes | Line to Ground | 1503817 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE | 79313 | 20200110 | 1739 | 759108 | 1161 | Distribution Circuit | 3rd Party | Vehicle | 1 | 1161 | 38.7463 | -120.7584 | 1 SP LD SIDE OF C/OUT 79313 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 20-0007597 | OH | Sus | 0 | No | 2020 | JAN | Yes | Line to Line | 1505600 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 8372 | 20200113 | 1023 | 760123 | 354 | Distribution Circuit | Equipment Failure/Involved | Overhead | 716 | 73094 | 38.6092 | -120.7025 | AT ON MAINLINE BET 54789 & 21151 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0007928 | OH | Sus | 44155022 | No | 2020 | JAN | Yes | Line to Ground | 1505962 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 186912 | 20200120 | 18 | 766326 | 599 | Distribution Circuit | Equipment Failure/Involved | Overhead | 687 | 110933 | 38.641 | -120.7043 | MELLO- ADAM 530-401-5814: MAINLINE at 21443 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0011298 | OH | Sus | 31486987 | No | 2020 | JAN | Yes | Line to Ground | 1507826 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1107 | 152691107 | FUSE | 5727 | 20200122 | 32 | 767638 | 829 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 33160 | 39.019 | -121.0518 | 13535 LAKEVIEW PLACE | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0012075 | OH | Sus | 31487068 | No | 2020 | JAN | Yes | Line to Ground | 1508235 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 1333 | 20200124 | 1057 | 769339 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 14625 | 38.6747 | -120.7232 | MTR#1008944286 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0013283 | OH | Sus | 44163956 | No | 2020 | JAN | Yes | Line to Ground | 1508983 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 9372 | 20200129 | 1235 | 772704 | 591 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2096 | 238266 | 38.714 | -120.9394 | POLE DOWN 1 SPAN WEST OF CGC 223030840239 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 20-0015049 | OH | Sus | 31488025 | No | 2020 | JAN | Yes | Line to Ground | 1510157 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | RECLOSER | 50072 | 20200206 | 1335 | 779482 | 228 | Distribution Circuit | Equipment Failure/Involved | Overhead | 638 | 32604 | 39.0757 | -121.1143 | 19327 MCCOURTNEY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0018200 | OH | Sus | 31489523 | No | 2020 | FEB | Yes | Line to Ground | 1512436 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1103 | 152481103 | FUSE | 8253 | 20200214 | 1007 | 791072 | 359 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 216 | 77544 | 39.2867 | -121.0268 | 16661 LAKE VERA PURDON RD | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0022276 | OH | Sus | 31490950 | No | 2020 | FEB | Yes | Line to Ground | 1515404 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE | 9027 | 20200301 | 1711 | 820962 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 12880 | 39.1707 | -121.0507 | 13431 HWY 49 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0027550 | OH | Sus | 44226122 | No | 2020 | MAR | Yes | Line to Ground | 1518746 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 30711 | 20200302 | 156 | 821137 | 590 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 14408 | 39.2145 | -120.8088 | 2 SP W/O 4181 ON HARD TAP TO NORTH | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0027613 | OH | Sus | 31493733 | yes | 2020 | MAR | Yes | Line to Ground | 1518808 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | LINCOLN-1104 | 153701104 | FUSE | 5393 | 20200313 | 657 | 848415 | 231 | Distribution Circuit | Animal | Bird found | 53 | 12243 | 38.9463 | -121.2467 | 1 SPAN LD SIDE OF FU 5393 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0031644 | OH | Sus | 31495677 | No | 2020 | MAR | Yes | Line to Line | 1521128 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | FUSE | 7919 | 20200314 | 2210 | 851541 | 1212 | Distribution Circuit | Vegetation | Tree - fell into line | 67 | 81204 | 38.7504 | -120.6322 | CORNER OF DOUGLAS FIR CT & DOUGLAS FIR DR | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0032160 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Line | 1521493 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 2459 | 20200317 | 1500 | 856962 | 267 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 18423 | 38.7721 | -120.5815 | MULTIPLE LOCATIONS | Partly Cloudy-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0033490 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Line | 1522476 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 18345 | 20200321 | 1304 | 860599 | 192 | Distribution Circuit | Vegetation | Tree - branch fell on line | 88 | 16896 | 38.6645 | -120.8541 | MTR 1010348190 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0034944 | OH | Sus | 0 | No | 2020 | MAR | Yes | Line to Ground | 1523430 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE | 1313 | 20200329 | 640 | 869241 | 446 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 9435 | 38.7588 | -120.7204 | 3430 N CANYON RD | Overcast-Fog-Drizzle-32-90 F | Transformer (OH) | Broken, wire on ground | 20-0036995 | OH | Sus | 0 | No | 2020 | MAR | Yes | Line to Ground | 1524401 | TXO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1102 | 152491102 | FUSE | 6103 | 20200329 | 827 | 869257 | 438 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 13578 | 39.0468 | -120.9969 | 1309 SAGE RD | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 20-0036994 | OH | Sus | 0 | No | 2020 | MAR | Yes | Line to Line | 1524400 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE | 1463 | 20200405 | 2242 | 883478 | 971 | Distribution Circuit | Vegetation | Tree - fell into line | 253 | 216913 | 38.7471 | -120.6443 | COR OF CEDAR DR & FERN AVE | Partly Cloudy-Fog-Snow-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0038736 | OH | Sus | 0 | yes | 2020 | APR | Yes | Line to Line | 1525543 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | FUSE | 7079 | 20200405 | 2330 | 883498 | 670 | Distribution Circuit | Vegetation | Tree - branch fell on line | 309 | 196725 | 38.7533 | -120.5967 | FULTON- ERIC: 5828 Ritz Rd.- Pollock Pines | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0038696 | OH | Sus | 0 | yes | 2020 | APR | Yes | Line to Ground | 1525509 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 12685 | 20200406 | 853 | 884713 | 103 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 2987 | 38.6463 | -120.5639 | at CGC# 224108536137 | Overcast-Fog-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0038823 | OH | Sus | 0 | yes | 2020 | APR | Yes | Line to Ground | 1525622 | CSO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1102 | 152491102 | FUSE | 6241 | 20200407 | 18 | 886612 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 9572 | 39.0289 | -121.0037 | MTR#1004893446 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0039155 | OH | Sus | 0 | No | 2020 | APR | Yes | Line to Ground | 1525807 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | TRIP-SAVER | 5731 | 20200408 | 1836 | 892626 | 503 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 47282 | 38.9857 | -121.0221 | MTR# 1008890721 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0039902 | OH | Sus | 0 | No | 2020 | APR | Yes | Three Phase Fault | 1526233 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1101 | 152101101 | JUMPER | WIRE DOWN 5 SPANS LOAD SIDE OF FUCO 7901 | 20200411 | 1418 | 893851 | 304 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 608 | 39.4877 | -120.8541 | 5 SPANS LOAD SIDE OF FUCO 7901 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0040593 | OH | Sus | 44292033 | No | 2020 | APR | Yes | Open Circuit | 1526683 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 1555 | 20200414 | 251 | 894890 | 390 | Distribution Circuit | Vegetation | Tree - fell into line | 265 | 80733 | 38.6476 | -120.9178 | 4301 STEEP LANE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0041086 | OH | Sus | 44293809 | No | 2020 | APR | Yes | Line to Ground | 1526997 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 22355 | 20200425 | 1946 | 901558 | 249 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 10458 | 38.6321 | -120.9242 | 5619 CONIE LN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0044594 | OH | Sus | 44303780 | No | 2020 | APR | Yes | Line to Ground | 1529070 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE | 36033 | 20200428 | 426 | 902635 | 303 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 3636 | 38.9931 | -120.8963 | 2 SPANS LD SIDE OF 360303 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0045031 | OH | Sus | 31501485 | No | 2020 | APR | Yes | Line to Ground | 1529426 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 1975 | 20200505 | 1408 | 907569 | 152 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 2584 | 38.6669 | -120.9135 | SECOND PHASE GOING SOUTH ON CHILDHOOD LN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0047563 | OH | Sus | 44311348 | No | 2020 | MAY | Yes | Line to Line | 1530892 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE | 4637 | 20200516 | 102 | 914601 | 928 | Distribution Circuit | 3rd Party | Vehicle | 44 | 40832 | 39.1678 | -121.0464 | BROKEN POLE at CGC 222706054673- 1 PHASE OF WIRE DOWN S/O BROKEN POLE | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 20-0050827 | OH | Sus | 0 | No | 2020 | MAY | Yes | Line to Line | 1532799 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | FUSE | 43995 | 20200518 | 646 | 915678 | 297 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1188 | 39.0682 | -121.1397 | 21030 WILLS WAY | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0051173 | OH | Sus | 44326106 | yes | 2020 | MAY | Yes | Line to Ground | 1533077 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 5569 | 20200521 | 1427 | 919174 | 337 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 4044 | 39.2441 | -120.9624 | 14017 BANNER MT LOOK-OUT | Clear-32-90 F | Insulator | Broken, wire on object | 20-0053110 | OH | Sus | 44329185 | No | 2020 | MAY | Yes | Line to Ground | 1533948 | INS | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2108 | 153652108 | RECLOSER | 19622 | 20200526 | 1626 | 922039 | 221 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2502 | 206228 | 38.6569 | -120.9928 | MELLO- ADAM 530-401-5814: 3828 fairway | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 20-0054301 | OH | Sus | 44332121 | yes | 2020 | MAY | Yes | Line to Ground | 1534716 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1102 | 152201102 | FUSE | 8315 | 20200529 | 948 | 925044 | 85 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 255 | 39.5264 | -121.0159 | LD SIDE OF 8315 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 20-0055529 | OH | Sus | 0 | yes | 2020 | MAY | Yes | Force Out | 1535491 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 1104 | 20200529 | 932 | 925104 | 326 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 658 | 93311 | 38.9124 | -120.8201 | PASQUA-MARK 559 567-1146: wentworth springs rd.3 spans source of SSD 35987 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0055552 | OH | Sus | 44336256 | yes | 2020 | MAY | Yes | Line to Ground | 1535528 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1180 | 20200531 | 640 | 926729 | 357 | Distribution Circuit | Vegetation | Tree - branch fell on line | 137 | 18659 | 38.8952 | -120.9116 | 2 SPANS LD SIDE OF 4955 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0056027 | OH | Sus | 0 | No | 2020 | MAY | Yes | Line to Ground | 1535894 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1103 | 153661103 | JUMPER | WIRE DOWN SS OF MTR#1005286243 | 20200611 | 1604 | 937221 | 326 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 652 | 38.7159 | -120.7073 | MYERS- STEVEN 707 438-5171: 3033 Pioneer hill | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0060394 | OH | Sus | 0 | No | 2020 | JUN | Yes | Open Circuit | 1539109 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1110 | 152691110 | FUSE | 9159 | 20200623 | 1950 | 945681 | 636 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 636 | 39.051 | -121.0374 | 13350 magnolia rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0064169 | OH | Sus | 31506758 | yes | 2020 | JUN | Yes | Force Out | 1541904 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1102 | 152101102 | FUSE | 3209 | 20200702 | 423 | 956425 | 729 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 6561 | 39.3612 | -120.7975 | CGC 223405861885 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0067506 | OH | Sus | 31507536 | No | 2020 | JUL | Yes | Line to Line | 1543979 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | CLARKSVILLE-2103 | 153612103 | FUSE | 11049 | 20200716 | 848 | 965818 | 320 | Distribution Circuit | 3rd Party | Vehicle | 358 | 40848 | 38.6063 | -121.0218 | 5 SPANS LD SIDE OF 11049 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0072551 | OH | Sus | 0 | No | 2020 | JUL | Yes | Line to Line | 1547081 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 22337 | 20200805 | 2325 | 979809 | 509 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3054 | 38.6466 | -120.9224 | 1/2 SPAN LD SIDE OF 22337 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0080235 | OH | Sus | 31510726 | yes | 2020 | AUG | Yes | Line to Ground | 1552065 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 36327 | 20200809 | 1235 | 987254 | 480 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3030 | 39.155 | -121.1882 | CROOKS- MICHAEL: 14040 PARSONS | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 20-0081390 | OH | Sus | 31510946 | No | 2020 | AUG | Yes | Line to Ground | 1552765 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 8485 | 20200818 | 649 | 1018153 | 382 | Distribution Circuit | Vegetation | Tree - branch fell on line | 49 | 12796 | 39.0185 | -121.0183 | 2 SPANS W/OF CGC 222807549332 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0086555 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Line | 1556603 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | FUSE | 4109 | 20200819 | 401 | 1021345 | 539 | Distribution Circuit | Vegetation | Tree - branch fell on line | 30 | 15631 | 39.0838 | -121.1142 | COR OF LIME KILN RD & DUGGANS RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0087193 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Line | 1557017 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 20865 | 20200819 | 622 | 1021381 | 230 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1150 | 38.8279 | -120.9415 | SS SPAN TO CGC 222990042735 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0087255 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Line | 1557036 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE | 36033 | 20200820 | 1000 | 1025160 | 153 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 1836 | 38.9931 | -120.8963 | 2 SPANS LD SIDE OF 36033 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0087943 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Open Circuit | 1557502 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | BELL-1108 | 152701108 | FUSE | 5773 | 20200821 | 524 | 1026066 | 558 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 21762 | 39.011 | -121.1043 | 2 SPANS EAST OF 5773 RIGHT BEFORE THE LINE BUCKS- 12285 RIO OSO. | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0088373 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Ground | 1557723 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 20619 | 20200901 | 1245 | 1046535 | 389 | Distribution Circuit | 3rd Party | Vehicle | 18 | 7002 | 38.7219 | -120.6607 | IFO 4551 PUERTA DEL SOL RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0092272 | OH | Sus | 0 | No | 2020 | SEP | Yes | Line to Line | 1560320 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE | 6353 | 20200910 | 35 | 1062548 | 707 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 33229 | 39.1448 | -120.9074 | 2 AND 3 SP LD SIDE OF 6353 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0095848 | OH | Sus | 0 | No | 2020 | SEP | Yes | Line to Line | 1562705 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 18279 | 20200914 | 1317 | 1070489 | 362 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 3041 | 38.6349 | -120.6072 | 2 SPANS LOAD SIDE OF 18279 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0097413 | OH | Sus | 0 | No | 2020 | SEP | Yes | Line to Line | 1563622 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | FUSE | 40277 | 20201001 | 1440 | 1105236 | 134 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 268 | 38.7382 | -120.8571 | 1 SPAN LOAD SIDE OF 40277 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 20-0104084 | OH | Sus | 44484938 | yes | 2020 | OCT | Yes | Line to Line | 1567765 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 6852 | 20201002 | 110 | 1106034 | 272 | Distribution Circuit | 3rd Party | Vehicle | 2746 | 457483 | 38.7612 | -120.5582 | at 669489 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 20-0104264 | OH | Sus | 0 | No | 2020 | OCT | Yes | Line to Ground | 1567853 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 3307 | 20201010 | 1140 | 1114862 | 522 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 9918 | 39.2112 | -121.1665 | CGC 222372056465 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0107251 | OH | Sus | 0 | No | 2020 | OCT | Yes | Line to Ground | 1569846 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 18319 | 20201017 | 2241 | 1120111 | 982 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 42226 | 38.8081 | -120.9446 | at MTR#1007389121 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0110056 | OH | Sus | 31516131 | No | 2020 | OCT | Yes | Line to Ground | 1571576 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1110 | 153081110 | OCB | 1110/2 | 20201102 | 2053 | 1134833 | 495 | Distribution Circuit | Vegetation | Tree - fell into line | 1592 | 244781 | 38.7313 | -120.784 | BET 21695 & 21693 ON MAINLINE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0116308 | OH | Sus | 31517592 | No | 2020 | NOV | Yes | Line to Line | 1576498 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 9977 | 20201118 | 1200 | 1148619 | 243 | Distribution Circuit | Equipment Failure/Involved | Overhead | 60 | 14580 | 39.0001 | -121.0646 | WIRE DOWN 1 WEST OF 3071 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0122498 | OH | Sus | 44552504 | No | 2020 | NOV | Yes | Line to Ground | 1581034 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | RECLOSER | 2228 | 20201123 | 634 | 1152973 | 271 | Distribution Circuit | Animal | Bird found | 259 | 70189 | 39.2009 | -121.2091 | CROOKS- MICHAEL: 17836 INDIAN SPRINGS RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0124027 | OH | Sus | 31519300 | No | 2020 | NOV | Yes | Line to Line | 1582026 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 21407 | 20201207 | 647 | 1167368 | 404 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4848 | 38.7116 | -120.6263 | MTR# 1007386554 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0128390 | OH | Sus | 44578717 | No | 2020 | DEC | Yes | Line to Ground | 1584952 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 20535 | 20201207 | 541 | 1167296 | 480 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 17639 | 38.7338 | -120.6035 | 5800 LINX TRAIL | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0128430 | OH | Sus | 31519984 | No | 2020 | DEC | Yes | Line to Ground | 1585003 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 628635 | 20201207 | 608 | 1167665 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2195 | 38.7146 | -120.6094 | at D-E POLE LD SIDE OF FU 628635 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 20-0128379 | OH | Sus | 44578819 | No | 2020 | DEC | Yes | Line to Ground | 1584988 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 8855 | 20201207 | 1119 | 1168609 | 583 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2915 | 39.4675 | -121.0782 | 3 SPANS LD SIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0128609 | OH | Sus | 31519926 | No | 2020 | DEC | Yes | Line to Ground | 1585167 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | OTHER | WIRE DOWN @ 8400 CHARDONNAY | 20201211 | 713 | 1178588 | 370 | Distribution Circuit | Equipment Failure/Involved | Overhead | 718 | 63981 | 38.5762 | -120.6686 | 8400 CHARDONNAY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0129652 | OH | Sus | 0 | No | 2020 | DEC | Yes | Line to Ground | 1586322 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 5793 | 20201227 | 1441 | 1199540 | 254 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 80 | 19734 | 39.0048 | -121.0351 | MTR 1004686729 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0131961 | OH | Sus | 31522588 | No | 2020 | DEC | Yes | Line to Ground | 1589683 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1103 | 152561103 | FUSE | 39317 | 20201229 | 1153 | 1200776 | 215 | Distribution Circuit | 3rd Party | Vehicle | 5 | 1075 | 38.8629 | -121.1346 | LOAD SIDE OF CGC 222466743777 | Clear-32-90F | Crossarm, Wood | Broken, wire on object | 20-0132170 | OH | Sus | 31522768 | No | 2020 | DEC | Yes | Force Out | 1590003 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 34485 | 20210104 | 1804 | 1204168 | 370 | Distribution Circuit | Vegetation | Tree - branch fell on line | 75 | 22521 | 39.1233 | -121.0615 | 10541 LITTLE HOLLOW LN | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0004926 | OH | Sus | 31526896 | No | 2021 | JAN | Yes | Line to Ground | 1590821 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 5963 | 20210129 | 523 | 1240963 | 497 | Distribution Circuit | Vegetation | Tree - branch fell on line | 26 | 12922 | 38.6331 | -120.5421 | 7039 SUGAR PINE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0018204 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1600206 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 2487 | 20210129 | 842 | 1241234 | 416 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 416 | 38.6563 | -120.5262 | 2 SPANS | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0018474 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1600394 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1102 | 152301102 | JUMPER | WIRE DOWN @ 990 ALTA RES RD | 20210129 | 1739 | 1242988 | 1401 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 36870 | 39.2193 | -120.7861 | 990 ALTA RES RD. | Snow-Strong Winds-Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0019266 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1601124 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | EL DORADO PH-2101 | 152762101 | OTHER | 2493 | 20210129 | 952 | 1241421 | 237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 898 | 52552 | 38.773 | -120.2937 | MELLO- ADAM 530-401-5814: at LR 13532 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0017959 | OH | Sus | 0 | No | 2021 | JAN | Yes | Open Circuit | 1600240 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | JUMPER | OJS @ CGC#224215335930 | 20210129 | 920 | 1241321 | 255 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 765 | 38.6444 | -120.5248 | 7107 PINE HAVEN | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0018254 | OH | Sus | 0 | No | 2021 | JAN | Yes | Open Circuit | 1600248 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1102 | 152201102 | FUSE | 30593 | 20210201 | 1220 | 1245317 | 322 | Distribution Circuit | Environmental/External | Ice or snow | 8 | 2576 | 39.5206 | -120.9976 | SAP ID 100093353 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0020552 | OH | Sus | 0 | No | 2021 | FEB | Yes | Line to Line | 1602217 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHADY GLEN-1102 | 152431102 | FUSE | 6349 | 20210227 | 1139 | 1263586 | 364 | Distribution Circuit | Animal | Squirrel | 128 | 46592 | 39.1348 | -120.9227 | MTR: 1004079433 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0030279 | OH | Sus | 44666095 | No | 2021 | FEB | Yes | Line to Line | 1608341 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 4807 | 20210310 | 2111 | 1278189 | 840 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 12600 | 39.2181 | -120.7858 | ALTA RESEROIR RD & S/OF SUGAR PINE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0035085 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1611243 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 8189 | 20210310 | 803 | 1276943 | 176 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 5632 | 39.2062 | -121.0397 | LD SIDE OF 8189 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0034499 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Line | 1610960 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7039 | 20210310 | 922 | 1277139 | 468 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 23868 | 39.1992 | -121.0201 | RAGGIO- JAMES: 11327 cedar ridge dr | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0034560 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1610992 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | JUMPER | WIRE DOWN CORNER EASTVIEW PL N MEADOW VIEW DR | 20210310 | 806 | 1276962 | 443 | Distribution Circuit | Equipment Failure/Involved | Overhead | 80 | 26209 | 39.197 | -120.9933 | INTERSECTION OF N.MEADOW VIEW DR & EASTVIEW PLACE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0034619 | OH | Sus | 0 | No | 2021 | MAR | Yes | Open Circuit | 1611012 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1102 | 152301102 | RECLOSER | 1102/2 | 20210311 | 638 | 1278358 | 53 | Distribution Circuit | Vegetation | Tree - fell into line | 518 | 27454 | 39.214 | -120.8098 | ALTA RESEROIR RD & SUGAR PINE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0035085 | OH | Sus | 0 | No | 2021 | MAR | Yes | Force Out | 1611228 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | OTHER | WIRE DOWN 1 LD SIDE OF FUSE 5259 | 20210320 | 1510 | 1290428 | 517 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1551 | 39.2079 | -121.2401 | 1 LD SIDE OF 5259 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0039035 | OH | Sus | 0 | No | 2021 | MAR | Yes | Open Circuit | 1613644 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | FUSE | 4503 | 20210323 | 1332 | 1294228 | 378 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 22592 | 38.8778 | -120.9979 | 2281 INDIAN ROCK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0040039 | OH | Sus | 31534218 | No | 2021 | MAR | Yes | Line to Line | 1614386 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1102 | 152481102 | JUMPER | OJ'S/1/SPAN/SS/TO 3629 TO EOL | 20210401 | 821 | 1304826 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 405 | 39.2129 | -121.0062 | BY TRANSF at EOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0043556 | OH | Sus | 0 | No | 2021 | APR | Yes | Force Out | 1616769 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 97829 | 20210401 | 753 | 1304801 | 771 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 6939 | 38.9719 | -121.059 | 6 SPAN LD SIDE OF FU97829 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0043786 | OH | Sus | 31535068 | No | 2021 | APR | Yes | Line to Ground | 1616975 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | RECLOSER | 995672 | 20210420 | 45 | 1324267 | 595 | Distribution Circuit | Equipment Failure/Involved | Overhead | 217 | 37795 | 39.1336 | -121.0717 | CGC 222651253503 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0050642 | OH | Sus | 44754761 | No | 2021 | APR | Yes | Line to Ground | 1621464 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 81390 | 20210426 | 744 | 1333917 | 512 | Distribution Circuit | 3rd Party | Vehicle | 342 | 42570 | 38.8008 | -120.9078 | CORNER OF LAKOTAH AND COLD SPRIS | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0053019 | OH | Sus | 0 | No | 2021 | APR | Yes | Line to Line | 1623071 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 2015 | 20210427 | 1906 | 1335774 | 542 | Distribution Circuit | 3rd Party | Vehicle | 14 | 3544 | 38.5958 | -120.619 | 3/P/W OF CGC 223963533565 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0054049 | OH | Sus | 0 | No | 2021 | APR | Yes | Line to Line | 1623735 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1102 | 152241102 | FUSE | 31517 | 20210510 | 1210 | 1345112 | 322 | Distribution Circuit | Vegetation | Tree - fell into line | 974 | 51984 | 38.947 | -121.0455 | 1 SPAN SS OF 9909 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0059273 | OH | Sus | 0 | No | 2021 | MAY | Yes | Line to Line | 1627298 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 9519 | 20210617 | 634 | 1375892 | 365 | Distribution Circuit | 3rd Party | Vehicle | 146 | 48713 | 38.7148 | -120.6676 | 1 SPAN LD SIDE OF 9519 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0075378 | OH | Sus | 0 | No | 2021 | JUN | Yes | Line to Ground | 1637996 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | TRIP-SAVER | 7863 | 20210622 | 359 | 1381716 | 555 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 9858 | 39.0917 | -121.1772 | 15525 METCALF RD. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0077283 | OH | Sus | 31544225 | No | 2021 | JUN | Yes | Line to Line | 1639522 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | FUSE | 21315 | 20210628 | 1145 | 1387074 | 633 | Distribution Circuit | 3rd Party | Vehicle | 37 | 18894 | 38.6196 | -120.7647 | CAR POLE ACCIDENT at 2201 SANDRIDGE RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0080951 | OH | Sus | 0 | No | 2021 | JUN | Yes | Line to Line | 1642589 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 7671 | 20210629 | 1024 | 1387981 | 381 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 3508 | 39.148 | -121.0328 | 15274 CARRIE DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0081493 | OH | Sus | 31545041 | No | 2021 | JUN | Yes | Line to Line | 1642977 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1110 | 153081110 | OTHER | 13795 | 20210704 | 341 | 1391531 | 519 | Distribution Circuit | Equipment Failure/Involved | Overhead | 100 | 51900 | 38.7622 | -120.8606 | 1 SPAN S/OF 21725 ON MAINLINE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0084757 | OH | Sus | 44891740 | No | 2021 | JUL | Yes | Open Circuit | 1645292 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 9731 | 20210706 | 1406 | 1393012 | 315 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 7245 | 39.1533 | -121.0665 | 14638 FLICKER DR. | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0085422 | OH | Sus | 31545538 | No | 2021 | JUL | Yes | Line to Ground | 1645716 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE | 9123 | 20210711 | 1607 | 1399530 | 284 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 38056 | 38.7569 | -120.693 | 3971 AUDUBON DR | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0087738 | OH | Sus | 0 | No | 2021 | JUL | Yes | Line to Line | 1647189 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1110 | 152691110 | FUSE | 4871 | 20210711 | 1426 | 1399467 | 304 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 8816 | 39.0614 | -121.0192 | 1474 MAG | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0087722 | OH | Sus | 0 | No | 2021 | JUL | Yes | Force Out | 1647177 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11569 | 20210711 | 859 | 1399190 | 242 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 2904 | 38.6953 | -120.9397 | 2861 PONDEROSA RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0087689 | OH | Sus | 0 | No | 2021 | JUL | Yes | Line to Ground | 1647152 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1102 | 152241102 | FUSE | 6147 | 20210712 | 831 | 1400545 | 341 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 11444 | 38.9973 | -120.9795 | 2 SPANS LD SIDE OF CGC 222907748426 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0087978 | OH | Sus | 0 | No | 2021 | JUL | Yes | Line to Line | 1647492 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1105 | 152261105 | FUSE | 21977 | 20210715 | 1703 | 1405630 | 407 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2442 | 38.7146 | -120.8798 | 3/S/O 21977 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0090454 | OH | Sus | 31546489 | No | 2021 | JUL | Yes | Line to Line | 1648698 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1105 | 152561105 | FUSE | 65129 | 20210717 | 2320 | 1407230 | 990 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5940 | 38.8708 | -121.1444 | CGC 222435244031 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0091367 | OH | Sus | 31546644 | No | 2021 | JUL | Yes | Line to Ground | 1649293 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 1261 | 20210721 | 1655 | 1410502 | 613 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 11212 | 38.8011 | -120.8913 | 1 POLE E/O CGC 223163041678 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0093163 | OH | Sus | 0 | No | 2021 | JUL | Yes | Line to Line | 1650427 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 2197 | 20210727 | 749 | 1415623 | 430 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 7310 | 38.8265 | -120.812 | 5802 TRAVERSE CREEK RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0095423 | OH | Sus | 31548147 | No | 2021 | JUL | Yes | Line to Ground | 1652152 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1101 | 152271101 | RECLOSER | 1404 | 20210729 | 739 | 1418125 | 515 | Distribution Circuit | 3rd Party | Vehicle | 2216 | 318316 | 38.8748 | -121.1172 | HART-EMMETT/1506/530-906-2031: 2105 Andregg Rd ( at c/o pole 5549) | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0096574 | OH | Sus | 35277619 | No | 2021 | JUL | Yes | Three Phase Fault | 1652729 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | OCB | 1104/2 | 20210806 | 1203 | 1435839 | 347 | Distribution Circuit | Vegetation | Tree - fell into line | 2485 | 219922 | 38.7393 | -120.6773 | 2 SPANS N/OF 20847 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0101044 | OH | Sus | 0 | No | 2021 | AUG | Yes | Line to Ground | 1655229 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | RECLOSER | 2054 | 20210807 | 1648 | 1436822 | 181 | Distribution Circuit | Vegetation | Tree - branch fell on line | 218 | 30344 | 38.8964 | -121.1202 | 1.5 SPANS SS/OF CGC 222418545636 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0101577 | OH | Sus | 0 | No | 2021 | AUG | Yes | Line to Ground | 1655496 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 12392 | 20210810 | 736 | 1438725 | 291 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1421 | 156786 | 38.711 | -120.9433 | 1 W/OF 11613 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0102294 | OH | Sus | 0 | No | 2021 | AUG | Yes | Line to Ground | 1656043 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1102 | 152031102 | OCB | 1102/2 | 20210825 | 955 | 1452843 | 294 | Distribution Circuit | Animal | Squirrel | 1468 | 154952 | 39.2093 | -121.0615 | 1009806360 | Clear-32-90 F | Transformer (OH) | Broken, wire on ground | 21-0109075 | OH | Sus | 0 | No | 2021 | AUG | Yes | Multi-Fault | 1660791 | TXO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2108 | 153652108 | FUSE | 2659 | 20210826 | 2049 | 1455012 | 741 | Distribution Circuit | Vegetation | Tree - branch fell on line | 152 | 106752 | 38.661 | -120.9906 | 1 SPAN LD SIDE OF 2659 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0109917 | OH | Sus | 0 | No | 2021 | AUG | Yes | Line to Ground | 1661308 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11703 | 20210830 | 1425 | 1458376 | 468 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 7956 | 38.6903 | -120.9293 | 4109 BLACK OAK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0111349 | OH | Sus | 0 | No | 2021 | AUG | Yes | Line to Ground | 1662266 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1102 | 152491102 | OCB | 1102/2 | 20210905 | 2030 | 1462688 | 655 | Distribution Circuit | 3rd Party | Vehicle | 640 | 238111 | 39.0363 | -120.9882 | ORCUTT- JEFF/530-320-8405: placer hills rd at whispering pines LR2038 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0113800 | OH | Sus | 0 | No | 2021 | SEP | Yes | Line to Ground | 1663606 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE | 8971 | 20210908 | 1305 | 1464600 | 374 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2992 | 39.1726 | -121.0834 | 4 SPANS LD SIDE OF 8971 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0114811 | OH | Sus | 0 | No | 2021 | SEP | Yes | Line to Ground | 1664185 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | OTHER | WIRE DOWN 3 POLES LD SIDE OF 7047 | 20210916 | 418 | 1472841 | 368 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 3920 | 39.1922 | -121.0033 | 3 POLES LD SIDE OF 7047 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0118176 | OH | Sus | 0 | No | 2021 | SEP | Yes | Line to Ground | 1666137 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1103 | 152561103 | RECLOSER | 604 | 20210917 | 2059 | 1474194 | 550 | Distribution Circuit | 3rd Party | Vehicle | 326 | 101353 | 38.8544 | -121.1507 | 2770 NEWCASTLE RD/1 POLE NORTH OF CGC 22534542873 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0119199 | OH | Sus | 0 | No | 2021 | SEP | Yes | Multi-Fault | 1666675 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 9903 | 20211001 | 1251 | 1484934 | 269 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 3228 | 39.0019 | -121.0504 | TX AT EOL. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0124898 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Line | 1670308 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | FUSE | 8167 | 20211007 | 2016 | 1489827 | 524 | Distribution Circuit | 3rd Party | Vehicle | 4 | 2096 | 39.098 | -121.1506 | CARPOLE 1P LD SIDE OF 8167 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0127450 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1671808 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE | 53269 | 20211022 | 851 | 1505703 | 381 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 381 | 39.1488 | -121.0791 | 53269 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0135035 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Line | 1676723 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 3813 | 20211026 | 950 | 1521326 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1800 | 39.3452 | -121.0783 | 5 LD SIDE OF 3813 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0138075 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1679251 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 1445 | 20211102 | 1753 | 1532598 | 532 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 7588 | 38.8109 | -120.8052 | R/O 6150 PYRAMID VIEW LN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0141416 | OH | Sus | 45038761 | No | 2021 | NOV | Yes | Line to Ground | 1681279 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1101 | 152201101 | FUSE | 4413 | 20211107 | 2224 | 1536983 | 509 | Distribution Circuit | 3rd Party | Vehicle | 46 | 18539 | 39.4399 | -121.0776 | 1/S/O CGC 222583564515 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0143195 | OH | Sus | 0 | No | 2021 | NOV | Yes | Line to Line | 1682478 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 94195 | 20211120 | 2233 | 1552255 | 1040 | Distribution Circuit | Vegetation | Tree - fell into line | 1534 | 119067 | 38.7607 | -120.505 | 14 POLES E/OF 63464 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0149133 | OH | Sus | 0 | No | 2021 | NOV | Yes | Line to Ground | 1687072 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | TRANSFORMER | 222809852969 | 20211207 | 2207 | 1561601 | 827 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 827 | 39.1171 | -121.0109 | FEDERMEYER- ROBERT 916 642-326: 20406 tiger tail rd. | Clear-32-90F | Transformer (OH) | Broken, wire on ground | 21-0155871 | OH | Sus | 35310639 | No | 2021 | DEC | Yes | Line to Ground | 1692401 | TXO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1102 | 152301102 | FUSE | 6407 | 20211216 | 244 | 1574089 | 614 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 66218 | 39.2088 | -120.8165 | 4 SPANS SS OF CGC 223340056180 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 21-0158847 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1695864 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 9021 | 20211220 | 1215 | 1578054 | 117 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 234 | 38.7779 | -120.4741 | 3 SPANS LD SIDE OF 9021 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0159855 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1697148 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | CLARKSVILLE-2105 | 153612105 | FUSE | 20041 | 20211221 | 955 | 1578559 | 305 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 11624 | 38.6542 | -121.0356 | MTR# 1009955701 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0159974 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1697363 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 8145 | 20211223 | 647 | 1579609 | 390 | Distribution Circuit | Vegetation | Tree - fell into line | 189 | 73710 | 38.6977 | -120.9365 | 2900 N SHINGLE RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160254 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1697690 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | FUSE | 41479 | 20211223 | 634 | 1579617 | 550 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 550 | 38.6755 | -120.9287 | 1 POLE E/OF 41479 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160287 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Line | 1697727 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SUMMIT-1101 | 152591101 | OTHER | 6627 | 20211224 | 306 | 1580405 | 466 | Distribution Circuit | Equipment Failure/Involved | Overhead | 44 | 20504 | 39.3247 | -120.3841 | WIRE DOWN 1 SPAN LD SIDE OF 6627- C/O LOLA MONTEZ&T-BAR CRT | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160416 | OH | Sus | 0 | No | 2021 | DEC | Yes | Open Circuit | 1697872 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6617 | 20211224 | 1622 | 1580890 | 126 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 7056 | 39.3203 | -120.4331 | 7 SPAN LD SIDE OF 6617 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0160471 | OH | Sus | 0 | No | 2021 | DEC | Yes | Line to Ground | 1697937 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | FUSE | 1469 | 20211231 | 244 | 1590450 | 894 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 30396 | 38.7409 | -120.6631 | 4400 PONDEROSA WAY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0161021 | OH | Sus | 0 | No | 2021 | DEC | Yes | Force Out | 1699904 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE | 18461 | 20220102 | 102 | 1592084 | 1122 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4488 | 38.726 | -120.7371 | CGC 223615638886 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0005204 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Ground | 1700400 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2102 | 152762102 | JUMPER | OJ'S 3FT SITTING @ DEAD END | 20220104 | 945 | 1594746 | 656 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1968 | 38.7605 | -120.5804 | POLE at CGC 224052640158 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0005939 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Ground | 1700901 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 7522 | 20220104 | 2059 | 1595289 | 51 | Distribution Circuit | Vegetation | Tree - fell into line | 416 | 21216 | 38.8154 | -120.8221 | MTR 1004521156 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 22-0006240 | OH | Sus | 0 | No | 2022 | JAN | Yes | Force Out | 1701066 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | JUMPER | OJ 1 SPAN S/OF CGC#222781252548 | 20220108 | 1259 | 1598179 | 179 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 358 | 39.1054 | -121.0212 | at CGC#222783252481 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0007600 | OH | Sus | 0 | No | 2022 | JAN | Yes | Force Out | 1701596 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BELL-1109 | 152701109 | SWITCH | P795 | 20220109 | 1309 | 1598769 | 291 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 15423 | 38.9524 | -121.0571 | BROKEN POLE- WIRE DOWN 2 WEST OF 537 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0007699 | OH | Sus | 0 | No | 2022 | JAN | Yes | Force Out | 1701724 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | DRUM-1101 | 152321101 | FUSE | 77663 | 20220109 | 1000 | 1598673 | 186 | Distribution Circuit | Environmental/External | Ice or snow | 3 | 558 | 39.2574 | -120.7664 | LD SIDE OF 77663 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0007752 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Ground | 1701706 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 9349 | 20220109 | 1727 | 1598907 | 1386 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 63756 | 38.9354 | -120.7471 | LD SIDE OF 9349 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0007811 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Ground | 1701757 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 31095 | 20220109 | 1727 | 1599101 | 1120 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 6720 | 38.9261 | -120.7781 | LD SIDE OF FUSES | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0007878 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Ground | 1701810 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | EL DORADO PH-2101 | 152762101 | FUSE | 1571 | 20220121 | 1144 | 1607313 | 653 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 44404 | 38.7745 | -120.2979 | 11640 KYBURZ DR | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0012547 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Line | 1704004 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1101 | 152101101 | RECLOSER | 804 | 20220125 | 1718 | 1612190 | 1310 | Distribution Circuit | Vegetation | Tree - fell into line | 604 | 777946 | 39.5596 | -120.8241 | 1 SPAN SS OF 2730 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0014306 | OH | Sus | 45148551 | No | 2022 | JAN | Yes | Line to Line | 1705091 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1107 | 152481107 | FUSE | 3999 | 20220130 | 2050 | 1616854 | 1048 | Distribution Circuit | 3rd Party | Vehicle | 7 | 3648 | 39.2091 | -121.0559 | 2 SPANS LD SIDE OF CGC 222692356304 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0016182 | OH | Sus | 0 | No | 2022 | JAN | Yes | Three Phase Fault | 1706144 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | OTHER | WIRE DOWN 1 SPAN LD SIDE 20745 | 20220202 | 1206 | 1619362 | 631 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1262 | 38.8219 | -120.8086 | WIRE DOWN 1 SPAN LD SIDE 20745 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0017782 | OH | Sus | 0 | No | 2022 | FEB | Yes | Line to Ground | 1707104 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | RECLOSER | 50486 | 20220204 | 1812 | 1621519 | 27 | Distribution Circuit | Environmental/External | Ice or snow | 915 | 24705 | 38.9928 | -120.8828 | AT C225 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0018928 | OH | Sus | 0 | No | 2022 | FEB | Yes | Line to Ground | 1707702 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1102 | 152181102 | OTHER | HOT WIRE DOWN @ 223223249503 | 20220204 | 1859 | 1621565 | 1019 | Distribution Circuit | Equipment Failure/Involved | Overhead | 423 | 132285 | 39.02 | -120.8693 | CGC 223223249503 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0018939 | OH | Sus | 45165751 | No | 2022 | FEB | Yes | Line to Ground | 1707712 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | BELL-1107 | 152701107 | FUSE | 30617 | 20220208 | 1003 | 1623332 | 394 | Distribution Circuit | 3rd Party | Vehicle | 15 | 5910 | 38.9632 | -121.1496 | 1/SPAN/SS TO CGC#222397047310 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0019810 | OH | Sus | 0 | No | 2022 | FEB | Yes | Line to Ground | 1708466 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | TRIP-SAVER | 7203 | 20220209 | 1803 | 1624365 | 465 | Distribution Circuit | Equipment Failure/Involved | Overhead | 237 | 49763 | 39.1806 | -121.1896 | LD SIDE OF 7883 & LD SIDE OF CGC 222382554710 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0020556 | OH | Sus | 45168901 | No | 2022 | FEB | Yes | Line to Ground | 1708834 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2108 | 153652108 | OTHER | WIRE DOWN S/OF CGC 222887035632 | 20220209 | 935 | 1623915 | 319 | Distribution Circuit | Equipment Failure/Involved | Overhead | 97 | 14293 | 38.6397 | -120.9893 | S/OF CGC 222887035632 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0020325 | OH | Sus | 45168626 | No | 2022 | FEB | Yes | Open Circuit | 1708772 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 33749 | 20220220 | 939 | 1632767 | 396 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 4 | 1584 | 39.1657 | -121.0391 | CGC#222722054667 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0024555 | OH | Sus | 0 | No | 2022 | FEB | Yes | Line to Line | 1711455 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | OTHER | WIRE DOWN @ 2893 JASPER RD | 20220314 | 1940 | 1648573 | 470 | Distribution Circuit | Equipment Failure/Involved | Overhead | 404 | 56931 | 38.7621 | -120.9887 | 2893 JASPER RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0033794 | OH | Sus | 45211271 | No | 2022 | MAR | Yes | Open Circuit | 1717068 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 6515 | 20220320 | 1430 | 1652075 | 334 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2004 | 39.0044 | -121.0165 | CGC#222801448795 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0036142 | OH | Sus | 31597888 | No | 2022 | MAR | Yes | Line to Line | 1718483 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | OTHER | WIRE DOWN @ SW 84477 | 20220321 | 1325 | 1652905 | 289 | Distribution Circuit | Equipment Failure/Involved | Overhead | 455 | 111192 | 38.7653 | -120.7044 | 84477 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 22-0036542 | OH | Sus | 0 | No | 2022 | MAR | Yes | Line to Ground | 1718781 | CSO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 21403 | 20220408 | 1926 | 1666268 | 246 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 738 | 38.7072 | -120.627 | 4 SPANS LD SIDE OF 21403 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0044777 | OH | Sus | 45247083 | No | 2022 | APR | Yes | Line to Line | 1723953 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1102 | 152481102 | FUSE | 9257 | 20220411 | 1346 | 1668914 | 344 | Distribution Circuit | Vegetation | Tree - fell into line | 46 | 5848 | 39.2008 | -120.932 | CGC 223061055995 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0045684 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Line | 1724707 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1107 | 152261107 | RECLOSER | 1402 | 20220411 | 1514 | 1669345 | 664 | Distribution Circuit | Equipment Failure/Involved | Overhead | 941 | 310904 | 38.7201 | -120.861 | 2900 STAGECOACH RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0045648 | OH | Sus | 0 | No | 2022 | APR | Yes | Three Phase Fault | 1724682 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 77546 | 20220417 | 1146 | 1675142 | 508 | Distribution Circuit | Equipment Failure/Involved | Overhead | 434 | 68597 | 38.5709 | -120.7329 | 2 POLES S/E/OF 21351 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0050700 | OH | Sus | 0 | No | 2022 | APR | Yes | Three Phase Fault | 1728776 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 9205 | 20220421 | 436 | 1677910 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 14637 | 39.2457 | -120.9581 | 3 SPANS S/OF CGC 222969057585 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0052310 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Line | 1729798 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1102 | 152241102 | FUSE | 8487 | 20220421 | 409 | 1677905 | 775 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 5251 | 38.9855 | -121.0061 | 100 FT SS/OF CGC 222816048126 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0052348 | OH | Sus | 45262411 | No | 2022 | APR | Yes | Line to Line | 1729812 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-1104 | 153651104 | FUSE | 22303 | 20220421 | 716 | 1678047 | 197 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 394 | 38.6136 | -120.9538 | 2 SPANS LD SIDE OF FUCO 2303 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0052386 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Ground | 1729832 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | TAMARACK-1101 | 152291101 | FUSE | 6615 | 20220422 | 31 | 1678843 | 907 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 96194 | 39.3223 | -120.4359 | 1 P N/O 6611 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0053185 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Line | 1730267 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 20721 | 20220425 | 1446 | 1681140 | 169 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 1014 | 38.79 | -120.817 | FIRST HARDTAP LD SIDE OF 20721- FIRST POLE TO THE SOUTH 1 SPAN OF WIRE DOWN | Clear-32-90 F | Insulator | Broken, wire on ground | 22-0054208 | OH | Sus | 45267126 | No | 2022 | APR | Yes | Line to Ground | 1730966 | INS | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | RECLOSER | 50072 | 20220430 | 1108 | 1685223 | 499 | Distribution Circuit | 3rd Party | Vehicle | 643 | 73654 | 39.0757 | -121.1143 | FEDERMEYER- ROBERT 916 642-326: 16102 Duggans Rd. | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 22-0056431 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Ground | 1732483 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE | 2663 | 20220517 | 1202 | 1698870 | 629 | Distribution Circuit | 3rd Party | Vehicle | 12 | 7548 | 38.7252 | -120.7351 | MTR# 1005286951 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0062962 | OH | Sus | 0 | No | 2022 | MAY | Yes | Line to Line | 1737065 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 9783 | 20220531 | 1945 | 1715129 | 340 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 6120 | 39.1546 | -121.0651 | 4 SPANS LD SIDE OF 9783 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0068547 | OH | Sus | 0 | No | 2022 | MAY | Yes | Line to Line | 1740664 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 6837 | 20220601 | 1357 | 1715779 | 248 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 52 | 12896 | 38.9977 | -121.0232 | METER # 1004698601 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0068939 | OH | Sus | 31605060 | No | 2022 | JUN | Yes | Line to Line | 1740948 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-2102 | 153662102 | FUSE | 18279 | 20220606 | 1413 | 1720645 | 596 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 4768 | 38.6349 | -120.6072 | 2 SPANS LD SIDE OF 18279 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0070711 | OH | Sus | 0 | No | 2022 | JUN | Yes | Line to Line | 1742213 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1104 | 152691104 | FUSE | 4173 | 20220606 | 1047 | 1720395 | 759 | Distribution Circuit | Vegetation | Tree - fell into line | 98 | 74382 | 39.109 | -121.0302 | 3 SPANS LD SIDE OF 4173 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0070607 | OH | Sus | 0 | No | 2022 | JUN | Yes | Line to Ground | 1742160 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | OTHER | WIRER DOWN @ CGC 223145248523 | 20220621 | 1911 | 1737379 | 316 | Distribution Circuit | Vegetation | Tree - fell into line | 138 | 43023 | 38.9936 | -120.8944 | CGC 223145248523 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0076705 | OH | Sus | 31606815 | No | 2022 | JUN | Yes | Open Circuit | 1746465 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | CLARKSVILLE-2103 | 153612103 | RECLOSER | 593454 | 20220623 | 503 | 1739562 | 447 | Distribution Circuit | 3rd Party | Vehicle | 375 | 42969 | 38.6057 | -121.0236 | CGC 222913032606 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 22-0077523 | OH | Sus | 0 | No | 2022 | JUN | Yes | Line to Ground | 1747056 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | RECLOSER | 1802 | 20220720 | 1530 | 1761523 | 618 | Distribution Circuit | 3rd Party | Vehicle | 1658 | 220720 | 39.0162 | -120.8351 | MROFKA- MATT 530-537-4552: 5100 Cold Springs Dr | Clear-32-90F | Conductor, Overhead | Broken, wire on object | 22-0087812 | OH | Sus | 0 | No | 2022 | JUL | Yes | Line to Ground | 1753826 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | RECLOSER | 76178 | 20220720 | 1717 | 1761592 | 234 | Distribution Circuit | Vegetation | Tree - fell into line | 628 | 40027 | 39.0014 | -121.0224 | 6 SP LD SD OF FUCO 35743 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0087867 | OH | Sus | 31609098 | No | 2022 | JUL | Yes | Line to Line | 1753837 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | RECLOSER | 995672 | 20220722 | 56 | 1762777 | 976 | Distribution Circuit | Vegetation | Tree - fell into line | 217 | 36772 | 39.1336 | -121.0717 | 11218 AGNES | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0088472 | OH | Sus | 35372265 | No | 2022 | JUL | Yes | Line to Ground | 1754154 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1104 | 152481104 | TRIP-SAVER | 7181 | 20220806 | 1000 | 1774787 | 354 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 15576 | 39.2455 | -121.0444 | 4 SPANS LD SIDE 7181 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0094556 | OH | Sus | 31612146 | No | 2022 | AUG | Yes | Line to Ground | 1758138 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER | 51486 | 20220806 | 1617 | 1774973 | 308 | Distribution Circuit | Vegetation | Tree - fell into line | 1066 | 115381 | 39.1911 | -120.9965 | 4 SPAN LD SIDE OF 6757 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0094609 | OH | Sus | 0 | No | 2022 | AUG | Yes | Line to Line | 1758172 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 6852 | 20220904 | 1443 | 1798836 | 178 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2083 | 255379 | 38.7606 | -120.5589 | T4NAPHA: Sly park rd cross of Mormon Emigrant trail | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0105669 | OH | Sus | 45439005 | No | 2022 | SEP | Yes | Line to Ground | 1765591 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | RECLOSER | 6852 | 20220910 | 944 | 1807782 | 285 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 2078 | 251510 | 38.7148 | -120.5815 | 4579 ELDERWOOD LANE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0108793 | OH | Sus | 0 | No | 2022 | SEP | Yes | Line to Ground | 1767626 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1103 | 152561103 | RECLOSER | 604 | 20220910 | 119 | 1807510 | 598 | Distribution Circuit | Equipment Failure/Involved | Overhead | 329 | 54408 | 38.8544 | -121.1507 | RICHARDS- ADAM: SAP ID 100060419 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 22-0108748 | OH | Sus | 0 | No | 2022 | SEP | Yes | Line to Line | 1767550 | CSO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | MOUNTAIN QUARRIES-2101 | 152282101 | RECLOSER | 1346 | 20221004 | 2153 | 1828802 | 420 | Distribution Circuit | Vegetation | Tree - fell into line | 1598 | 164478 | 38.8931 | -120.9977 | MROFKA- MATT 530-537-4552: 1 span North and one span South of Cutouts 30985 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0117928 | OH | Sus | 31617768 | No | 2022 | OCT | Yes | Line to Ground | 1774102 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER | 51486 | 20221024 | 1412 | 1844467 | 345 | Distribution Circuit | Vegetation | Tree - fell into line | 1045 | 51658 | 39.1911 | -120.9965 | S/O CGC222847755716 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0124351 | OH | Sus | 0 | No | 2022 | OCT | Yes | Line to Ground | 1778728 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2110 | 153652110 | RECLOSER | 51800 | 20221103 | 1212 | 1852639 | 716 | Distribution Circuit | 3rd Party | Vehicle | 1009 | 200681 | 38.6635 | -120.9306 | DEVLIN- MICHAEL/50-919-0454: One span s of 1285 c/o | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0127467 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Line | 1781193 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1106 | 152481106 | FUSE | 7073 | 20221108 | 1000 | 1857173 | 547 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 7145 | 39.1639 | -120.9687 | LARGE TREE LIMB INTO CONDUCTOR at 17722 COLFAX HYWY 174 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0128987 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Line | 1782150 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | FORESTHILL-1101 | 152181101 | FUSE | 4241 | 20221109 | 403 | 1858631 | 722 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 12274 | 39.0532 | -120.7557 | 6/N/O 4241 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0129448 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Line | 1782479 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | TRANSFORMER | 222861757326 | 20221111 | 659 | 1860494 | 498 | Distribution Circuit | Vegetation | Tree - fell into line | 309 | 22366 | 39.2362 | -120.9906 | RAGGIO- JAMES: 12478 hillcrest dr | Clear-32-90 F | Transformer (OH) | Broken, wire on ground | 22-0130300 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Ground | 1783037 | TXO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1102 | 152201102 | FUSE | 30593 | 20221112 | 1413 | 1861302 | 240 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 1680 | 39.5206 | -120.9976 | 29 POLES LD SIDE OF 30593 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0130587 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Ground | 1783317 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 20221115 | 2243 | 1863597 | 894 | Distribution Circuit | Vegetation | Tree - fell into line | 936 | 66344 | 38.7391 | -120.6681 | 1/N/O 22083 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0131438 | OH | Sus | 35403893 | No | 2022 | NOV | Yes | Line to Ground | 1783971 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 1577 | 20221122 | 1712 | 1868032 | 490 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1960 | 38.819 | -120.8072 | 3 SPANS LD SIDE OF 1577 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0133649 | OH | Sus | 45569055 | No | 2022 | NOV | Yes | Force Out | 1785224 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | RECLOSER | 2234 | 20221130 | 702 | 1871739 | 329 | Distribution Circuit | Equipment Failure/Involved | Overhead | 270 | 59282 | 38.8956 | -121.1358 | JUST N/OF 9423 ON THE MAINLINE | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 22-0135031 | OH | Sus | 45577100 | No | 2022 | NOV | Yes | Line to Ground | 1786263 | CSO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | RECLOSER | 2204 | 20221201 | 838 | 1872871 | 276 | Distribution Circuit | Vegetation | Tree - fell into line | 948 | 37866 | 39.2643 | -120.9855 | 1/E/O 969 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0135460 | OH | Sus | 0 | No | 2022 | DEC | Yes | Multi-Fault | 1786650 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1103 | 152561103 | RECLOSER | 2198 | 20221204 | 519 | 1875616 | 518 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 452 | 82216 | 38.8637 | -121.1283 | VILLAGOMEZ-LUCAS 408-489-2019: R141 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0136403 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1787351 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | JUMPER | WIRE DOWN @ 7220 PINE CONE DR. | 20221211 | 700 | 1885447 | 294 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2082 | 169992 | 38.7383 | -120.5685 | DEQUINE- WES: Wire down at 7220 pine cone | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0138848 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1789675 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | EL DORADO PH-2101 | 152762101 | FUSE | 3349 | 20221211 | 324 | 1885627 | 898 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5705 | 38.7751 | -120.4256 | BOULET- JON 209-986-9746: 7575 ice house road | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0138754 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1789716 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 22771 | 20221211 | 1208 | 1885797 | 467 | Distribution Circuit | Vegetation | Tree - fell into line | 453 | 101511 | 38.7166 | -120.5803 | DEQUINE- WES: Tree fell at 6092 Speckled Rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0138946 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1789778 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 3377 | 20221211 | 949 | 1885587 | 462 | Distribution Circuit | Vegetation | Tree - fell into line | 173 | 79926 | 38.9439 | -120.7215 | 5341 VOLCANOVILLE RD | Clear-32-90 F | Conductor, Overhead | On Ground | 22-0138961 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1789787 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE | 7147 | 20221227 | 225 | 1898037 | 893 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 52687 | 39.2454 | -121.0566 | 1 SPAN LD SIDE at 15461 SHANNON WAY | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0141500 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1793177 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 4383 | 20221227 | 135 | 1898099 | 782 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 60728 | 39.234 | -120.9851 | Y SS OF 7323 & 2 & 3RD SPAN E/O 31753 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0141446 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793122 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | LINCOLN-1101 | 153701101 | FUSE | 30599 | 20221227 | 718 | 1898589 | 227 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1135 | 38.8876 | -121.2058 | GCG 222265044650 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0141581 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793260 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | JUMPER | OPEN JUMPERS 21355 BURKE RD | 20221227 | 826 | 1898685 | 632 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2528 | 39.1922 | -121.2357 | RAGGIO- JAMES: 21355 Burke rd | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0141592 | OH | Sus | 0 | No | 2022 | DEC | Yes | Open Circuit | 1793273 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1106 | 152261106 | FUSE | 11321 | 20221230 | 1418 | 1902327 | 224 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 2464 | 38.7054 | -120.7628 | 4 SPANS LD SIDE OF CGC# 223553438364 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0142265 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1794054 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | JUMPER | OJS 3 SPANS E/OF CGC#222600051287 | 20230101 | 735 | 1908859 | 610 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1220 | 39.0712 | -121.0837 | 1 P E/OF CGC#222600051287 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0004486 | OH | Sus | 0 | No | 2023 | JAN | Yes | Force Out | 1795086 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | FUSE | 328161 | 20230101 | 519 | 1907816 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 102 | 22162 | 39.0344 | -121.096 | 1 SPAN LD SIDE OF CGC 222516249937 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0004329 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1794925 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | FUSE | 5365 | 20230113 | 2132 | 1952604 | 1029 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 44910 | 38.8911 | -121.1255 | 1 SS OF FUCO 30453 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0015955 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Ground | 1804785 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | APPLE HILL-1104 | 153661104 | JUMPER | WIRE DOWN | 20230117 | 1324 | 1959691 | 349 | Distribution Circuit | Vegetation | Tree - fell into line | 65 | 22619 | 38.7406 | -120.6558 | 3 SPANS SS OF 22085 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0017726 | OH | Sus | 0 | No | 2023 | JAN | Yes | Open Circuit | 1806230 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | JUMPER | OJS 2 SPANS SS OF CGC 223425541680 | 20230119 | 2250 | 1962868 | 913 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 2006 | 38.8055 | -120.7997 | 1 SPAN SS OF CGC 223425541680 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0019190 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1806962 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 11439 | 20230122 | 2002 | 1965028 | 811 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 49471 | 38.7331 | -120.789 | 2972 ANDERSON WAY | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0019969 | OH | Sus | 31634964 | No | 2023 | JAN | Yes | Line to Line | 1807402 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 11469 | 20230122 | 2346 | 1965281 | 866 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 19052 | 38.7956 | -120.8033 | CGC 223440840716 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0020003 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1807434 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 374539 | 20230125 | 1522 | 1968229 | 628 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 628 | 38.8159 | -120.9163 | WIRE DOWN 2 SP LD SD OF FUCO 374539 DO TO TREE LIMB TAGGED MOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0021442 | OH | Sus | 31635644 | No | 2023 | JAN | Yes | Line to Line | 1808192 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | DRUM-1101 | 152321101 | RECLOSER | 1101/2 | 20230126 | 127 | 1968437 | 864 | Distribution Circuit | Environmental/External | Ice or snow | 202 | 137094 | 39.2562 | -120.7669 | WIRE DOWN 5 SP SS OF FUCO 9215 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0021521 | OH | Sus | 31635651 | No | 2023 | JAN | Yes | Line to Line | 1808259 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | JUMPER | OJS 4 POLES N/OF CGC 222798748141 | 20230127 | 1229 | 1969888 | 251 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 2 | 502 | 38.9854 | -121.0169 | 3 POLES N/OF CGC 222798748141 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0022385 | OH | Sus | 0 | No | 2023 | JAN | Yes | Force Out | 1808688 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | ALLEGHANY-1102 | 152101102 | FUSE | 57465 | 20230205 | 330 | 1977145 | 499 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 10978 | 39.3625 | -120.7904 | CGC 223481561971 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0025335 | OH | Sus | 35424879 | No | 2023 | FEB | Yes | Line to Ground | 1810640 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | CLARKSVILLE-2104 | 153612104 | RECLOSER | 13352 | 20230209 | 1609 | 1981204 | 561 | Distribution Circuit | Animal | Bird found | 1008 | 143528 | 38.6858 | -121.0119 | SOUTH WEST OF FUSE 20465 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0027268 | OH | Sus | 31636526 | No | 2023 | FEB | Yes | Line to Ground | 1811972 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | FUSE | 2669 | 20230215 | 1120 | 1986083 | 153 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 2295 | 38.7475 | -120.7978 | 3 SPANS N/OF CGC 223436439398 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0029197 | OH | Sus | 31636910 | No | 2023 | FEB | Yes | Line to Ground | 1813507 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | EL DORADO PH-2101 | 152762101 | FUSE | 13100 | 20230302 | 823 | 2019450 | 460 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 9200 | 38.7853 | -120.6077 | 5-7 SPANS LD SIDE OF 13100 | Clear-32-90F | Conductor, Overhead | On Ground | 23-0038879 | OH | Sus | 0 | No | 2023 | MAR | Yes | Force Out | 1820910 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | JUMPER | 465074 | 20230304 | 1339 | 2022501 | 372 | Distribution Circuit | Vegetation | Tree - fell into line | 104 | 13943 | 38.8999 | -121.1023 | WIRE DOWN at CGC#222557745041 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0040000 | OH | Sus | 0 | No | 2023 | MAR | Yes | Open Circuit | 1821756 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1110 | 152691110 | FUSE | 30745 | 20230308 | 918 | 2026434 | 330 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 18480 | 39.0433 | -120.9863 | 2 SPANS LD SIDE OF 30745 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0041607 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1822878 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PIKE CITY-1102 | 152201102 | OCB | 1102/2 | 20230308 | 721 | 2026284 | 4439 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 35504 | 39.4382 | -120.9965 | 4 S/OF 8803 | Overcast-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0041494 | OH | Sus | 0 | No | 2023 | MAR | Yes | None | 1822812 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1104 | 152481104 | FUSE | 7147 | 20230310 | 316 | 2029996 | 649 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 31867 | 39.2454 | -121.0566 | 2 SPANS LD SIDE OF CGC 222686057677 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0042870 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1823631 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | EL DORADO PH-2101 | 152762101 | RECLOSER | 13532 | 20230310 | 435 | 2030074 | 727 | Distribution Circuit | Equipment Failure/Involved | Overhead | 705 | 64371 | 38.773 | -120.2933 | 3 E/OF 6161 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 23-0042740 | OH | Sus | 0 | No | 2023 | MAR | Yes | Three Phase Fault | 1823554 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | RECLOSER | 76178 | 20230311 | 1639 | 2032692 | 228 | Distribution Circuit | Vegetation | Tree - fell into line | 628 | 89364 | 39.0014 | -121.0224 | 2 SP SS OF FUCO 34707 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0043522 | OH | Sus | 0 | No | 2023 | MAR | Yes | Three Phase Fault | 1824064 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | TRANSFORMER | 222597051445 | 20230311 | 2318 | 2032960 | 1165 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1165 | 39.0753 | -121.0866 | BRICKEY-ALEX 530-565-6311: 20647 hwy 49 | Overcast-Fog-32-90 F | Transformer (OH) | Broken, wire on ground | 23-0043680 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1824211 | TXO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 22943 | 20230312 | 1250 | 2033298 | 408 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4080 | 38.8061 | -120.9079 | SAP ID# 101381763 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 23-0043741 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1824258 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | FUSE | 30657 | 20230312 | 855 | 2033129 | 366 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 6222 | 38.8993 | -121.0951 | CGC 222571445075 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0043672 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1824205 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 34911 | 20230313 | 612 | 2033961 | 531 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 5310 | 39.0043 | -121.0306 | CGC#222756248755 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0043986 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1824467 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1109 | 152691109 | FUSE | 5707 | 20230313 | 1109 | 2034347 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 640 | 39.0256 | -121.0995 | 1 LD SIDE OF 5707 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0044157 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1824543 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 11705 | 20230313 | 42 | 2033863 | 739 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 30299 | 38.6888 | -120.9245 | 4500 TENNENNEE DR | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0043932 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1824447 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1112 | 153081112 | FUSE | 21923 | 20230315 | 807 | 2045502 | 363 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1076 | 38.7178 | -120.7964 | 2 SPANS LD SIDE OF 21923 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0046115 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1826015 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | ECHO SUMMIT-1101 | 158031101 | FUSE | 22793 | 20230318 | 1130 | 2051147 | 305 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 305 | 38.8248 | -120.0414 | LD SIDE OF C/OUTS 22793 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0048301 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1827519 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1110 | 152691110 | FUSE | 7487 | 20230320 | 21 | 2052514 | 806 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 17732 | 39.0798 | -121.0131 | 1 LD SIDE OF CGC 222770051540 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0048706 | OH | Sus | 31640092 | No | 2023 | MAR | Yes | Line to Ground | 1827871 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 3957 | 20230322 | 1410 | 2062915 | 215 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 18 | 3870 | 39.1854 | -121.0277 | 100' LD SIDE OF 3957 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0050739 | OH | Sus | 0 | No | 2023 | MAR | Yes | Force Out | 1829212 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | BRUNSWICK-1102 | 152481102 | FUSE | 7005 | 20230328 | 644 | 2069525 | 393 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 18399 | 39.2132 | -121.0136 | FEDERMEYER- ROBERT 916 642-326: 13135 greenhorn rd. | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 23-0053280 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1831003 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1110 | 152691110 | FUSE | 34935 | 20230328 | 1429 | 2070823 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 746 | 39.0519 | -121.0712 | TURNES-JOE 707-321-9880: 22525 Kingston ln | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0053749 | OH | Sus | 0 | No | 2023 | MAR | Yes | Three Phase Fault | 1831283 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | FUSE | 4529 | 20230328 | 853 | 2069821 | 499 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 10978 | 39.2269 | -121.1413 | 14643 COCHRAN RD | Overcast-32-90 F | Conductor, Overhead | On Ground | 23-0053383 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1831080 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 4163 | 20230328 | 937 | 2069981 | 162 | Distribution Circuit | Company Initiated | Coordination failure | 21 | 3402 | 38.8381 | -120.851 | 5048 SAILER CREEK RD | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0053562 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1831186 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-2106 | 153082106 | FUSE | 32349 | 20230328 | 937 | 2070556 | 525 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1575 | 38.8398 | -120.8531 | 5048 SAILER CREEK RD | Partly Cloudy-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0053565 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1831187 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | PLACERVILLE-2106 | 153082106 | RECLOSER | 19732 | 20230328 | 1725 | 2071233 | 337 | Distribution Circuit | Vegetation | Tree - fell into line | 1205 | 156401 | 38.7367 | -120.784 | S/OF 63099 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0053836 | OH | Sus | 0 | No | 2023 | MAR | Yes | Three Phase Fault | 1831340 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | SHINGLE SPRINGS-2105 | 153652105 | FUSE | 11859 | 20230328 | 1009 | 2070106 | 462 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 37266 | 38.6748 | -120.9573 | 1 LD SIDE OF 11859 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0053474 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1831129 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BONNIE NOOK-1102 | 152301102 | RECLOSER | 542186 | 20230329 | 915 | 2072600 | 599 | Distribution Circuit | Equipment Failure/Involved | Overhead | 92 | 55108 | 39.2144 | -120.8088 | MAINLINE AT 9593 | Partly Cloudy-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0054144 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1831541 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HIGGINS-1103 | 152691103 | FUSE | 9931 | 20230412 | 156 | 2086102 | 466 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 6524 | 39.1035 | -121.1093 | 3 LD SIDE OF 9931 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0059852 | OH | Sus | 45726955 | No | 2023 | APR | Yes | Line to Line | 1835014 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | EL DORADO PH-2101 | 152762101 | RECLOSER | 13532 | 20230418 | 247 | 2090983 | 618 | Distribution Circuit | Vegetation | Tree - fell into line | 705 | 175848 | 38.773 | -120.2933 | CGC# 225235841367 | Overcast-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0061861 | OH | Sus | 35438503 | No | 2023 | APR | Yes | Multi-Fault | 1836539 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | JUMPER | OJ 2 E/OF CGC 222676148908 | 20230418 | 1124 | 2091484 | 235 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 470 | 39.0052 | -121.058 | CGC 222676148908 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0062034 | OH | Sus | 31642572 | No | 2023 | APR | Yes | Force Out | 1836730 | CAW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | DIAMOND SPRINGS-1105 | 152261105 | RECLOSER | 19910 | 20230426 | 1616 | 2097752 | 114 | Distribution Circuit | Equipment Failure/Involved | Overhead | 610 | 38588 | 38.6313 | -120.8542 | FLYING BELLS at CGC 223295633853 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0065155 | OH | Sus | 0 | No | 2023 | APR | Yes | Line to Ground | 1838793 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2102 | 153132102 | FUSE | 3685 | 20230506 | 1109 | 2106148 | 611 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1833 | 39.2767 | -121.1943 | LINE & BUCK TWDS CGC 222294058645 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 23-0069162 | OH | Sus | 0 | No | 2023 | MAY | Yes | Line to Line | 1841361 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1103 | 153661103 | RECLOSER | 8412 | 20230511 | 1614 | 2110548 | 247 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 260 | 20136 | 38.7272 | -120.7379 | BOULET- JON 209-986-9746: At sap ID 101401691 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0071086 | OH | Sus | 45760047 | No | 2023 | MAY | Yes | Force Out | 1842630 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1103 | 153661103 | FUSE | 1431 | 20230517 | 1117 | 2114991 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 8192 | 38.7464 | -120.7505 | MTR# 1007480833 | Clear-32-90 F | Conductor, Overhead | On Ground | 23-0072804 | OH | Sus | 45766248 | No | 2023 | MAY | Yes | Line to Line | 1843989 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | RECLOSER | 2230 | 20230525 | 915 | 2121134 | 729 | Distribution Circuit | 3rd Party | Vehicle | 869 | 114758 | 38.8963 | -121.1379 | 307494 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0075448 | OH | Sus | 0 | No | 2023 | MAY | Yes | Three Phase Fault | 1845868 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PLACERVILLE-1110 | 153081110 | FUSE | 21671 | 20230605 | 1626 | 2129472 | 428 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 2568 | 38.7371 | -120.8099 | BET CGC 223399739220 & CGC 223401539205 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0079088 | OH | Sus | 31651318 | No | 2023 | JUN | Yes | Force Out | 1848108 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | WEIMAR-1102 | 152491102 | RECLOSER | 2038 | 20230617 | 1042 | 2139273 | 798 | Distribution Circuit | Vegetation | Tree - fell into line | 2846 | 282872 | 39.0317 | -121.0046 | 150 FEET SS OF CGC#222739549200 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0083365 | OH | Sus | 0 | No | 2023 | JUN | Yes | Line to Ground | 1851319 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | ALLEGHANY-1101 | 152101101 | FUSE | 7679 | 20230713 | 1558 | 2161872 | 478 | Distribution Circuit | Equipment Failure/Involved | Overhead | 168 | 80304 | 39.611 | -120.6049 | 1 SS OF FUSE 5469 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 23-0091999 | OH | Sus | 0 | No | 2023 | JUL | Yes | Open Circuit | 1857229 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1103 | 152031103 | RECLOSER | 2180 | 20230720 | 1257 | 2168966 | 531 | Distribution Circuit | 3rd Party | Vehicle | 518 | 39306 | 39.153 | -121.0774 | GCG 222622353715 | Clear-Above 90 | Pole-Wood | Broken, wire on ground | 23-0094720 | OH | Sus | 0 | No | 2023 | JUL | Yes | Line to Line | 1859110 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | RECLOSER | 11092 | 20230722 | 250 | 2170526 | 663 | Distribution Circuit | Vegetation | Tree - fell into line | 915 | 277214 | 38.7741 | -120.9204 | cgc 223089041380 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0095491 | OH | Sus | 0 | No | 2023 | JUL | Yes | Line to Ground | 1859550 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | GRASS VALLEY-1103 | 152031103 | FUSE | 83079 | 20230727 | 1002 | 2175463 | 419 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3771 | 39.1326 | -121.144 | 18487 MCOURTNEY RD- GRASS VALLEY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0097622 | OH | Sus | 0 | No | 2023 | JUL | Yes | Line to Ground | 1861007 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | COLUMBIA HILL-1101 | 152471101 | FUSE | 8035 | 20230804 | 1736 | 2182697 | 586 | Distribution Circuit | 3rd Party | Vehicle | 41 | 15122 | 39.3451 | -121.0765 | 11625 TYLER FOOTE RD- NEVADA CITY | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0100800 | OH | Sus | 0 | No | 2023 | AUG | Yes | Line to Ground | 1863179 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | DIAMOND SPRINGS-1103 | 152261103 | RECLOSER | 9432 | 20230812 | 1837 | 2189365 | 1189 | Distribution Circuit | Equipment Failure/Involved | Overhead | 555 | 622051 | 38.7312 | -120.8428 | 3 SPANS LD SIDE OF 8949 ON MAIN LINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0103667 | OH | Sus | 0 | No | 2023 | AUG | Yes | Line to Ground | 1865254 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 774652 | 20230819 | 1112 | 2195624 | 264 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 13 | 3432 | 38.693 | -120.7152 | BOULET- JON 209-986-9746: Approx 3813 Kincade dr- placerville | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0106350 | OH | Sus | 31663978 | No | 2023 | AUG | Yes | Line to Ground | 1867048 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHINGLE SPRINGS-2109 | 153652109 | FUSE | 20865 | 20230819 | 2110 | 2196476 | 974 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 4870 | 38.8277 | -120.9417 | CGC# 222990042735 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0106527 | OH | Sus | 31664104 | No | 2023 | AUG | Yes | Line to Line | 1867197 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER | 51486 | 20230820 | 210 | 2196683 | 613 | Distribution Circuit | Vegetation | Tree - fell into line | 867 | 121926 | 39.1911 | -120.9965 | LARGE TREE 4 SP LD SD OF FUCO 9481 WIRE DOWN | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0106556 | OH | Sus | 31664015 | No | 2023 | AUG | Yes | Line to Ground | 1867228 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | PENRYN-1107 | 152561107 | FUSE | 59597 | 20230820 | 46 | 2196650 | 779 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 3116 | 38.789 | -121.1642 | WIRE DOWN 1 SP LD SD OF FUCO 59597 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0106550 | OH | Sus | 31664025 | No | 2023 | AUG | Yes | Force Out | 1867221 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | OCB | 1101/2 | 20230822 | 2043 | 2199647 | 509 | Distribution Circuit | 3rd Party | Vehicle | 2430 | 221888 | 38.9566 | -121.0427 | CGC 222706047474 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0107784 | OH | Sus | 0 | No | 2023 | AUG | Yes | Line to Ground | 1868099 | PW | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | FUSE | 33703 | 20230828 | 2204 | 2204504 | 411 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 822 | 39.2057 | -121.0203 | 1ST SPAN LD SIDE OF 33703 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0109981 | OH | Sus | 0 | No | 2023 | AUG | Yes | Line to Line | 1869685 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1101 | 152271101 | JUMPER | 5245 | 20230828 | 909 | 2203834 | 370 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1110 | 38.8826 | -121.0968 | 5245 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0109753 | OH | Sus | 31665571 | No | 2023 | AUG | Yes | Open Circuit | 1869577 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-1104 | 153661104 | RECLOSER | 13512 | 20230902 | 1629 | 2208817 | 438 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 936 | 136254 | 38.7391 | -120.6681 | DEVLIN- MICHAEL/50-919-0454: 3201 Spencer?s rd camino | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0112157 | OH | Sus | 0 | No | 2023 | SEP | Yes | Line to Line | 1870971 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1106 | 152481106 | RECLOSER | 51484 | 20230912 | 2234 | 2217161 | 334 | Distribution Circuit | Vegetation | Tree - fell into line | 987 | 57218 | 39.1909 | -120.9998 | MICHALAK- NICK 530-255-0589: 12505 oak cir | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0115800 | OH | Sus | 45977566 | No | 2023 | SEP | Yes | Line to Line | 1873498 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | HALSEY-1101 | 152241101 | FUSE | 9937 | 20230918 | 1054 | 2221553 | 428 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 2430 | 172248 | 38.9566 | -121.0427 | 5 SPANS LD SIDE OF 9937 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0117755 | OH | Sus | 0 | No | 2023 | SEP | Yes | Line to Ground | 1874884 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | NARROWS-2105 | 153132105 | JUMPER | OPEN JUMPERS @ CGC 222464057255 | 20230922 | 1414 | 2225004 | 446 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2230 | 39.2359 | -121.1307 | CGC 222463657288 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0119929 | OH | Sus | 31669872 | No | 2023 | SEP | Yes | Force Out | 1876115 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | COLUMBIA HILL-1101 | 152471101 | RECLOSER | 583518 | 20231005 | 1033 | 2235608 | 537 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 37 | 7584 | 39.3256 | -121.1123 | 4 SP LD SD OF FUCO 4203 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0124903 | OH | Sus | 0 | No | 2023 | OCT | Yes | Line to Line | 1879651 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | APPLE HILL-2102 | 153662102 | RECLOSER | 9722 | 20231106 | 1 | 2260832 | 582 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3557 | 669009 | 38.6943 | -120.6784 | 1 SPAN LD SIDE OF 10753 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0136081 | OH | Sus | 31675406 | No | 2023 | NOV | Yes | Line to Ground | 1887962 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | SHADY GLEN-1102 | 152431102 | OTHER | WIRE DOWN AT 33251 ON MAIN LINE | 20231109 | 744 | 2264802 | 479 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1250 | 749160 | 39.1498 | -120.9028 | WIRE DOWN ON MAIN LINE BY FUCO 33251 1? - C? 1/0 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0137367 | OH | Sus | 46053749 | No | 2023 | NOV | Yes | Open Circuit | 1889087 | CO | OH | No | Yes
SIERRA | FIELD OPS NORTH | Tier 3 | BRUNSWICK-1105 | 152481105 | FUSE | 7371 | 20231129 | 1945 | 2280262 | 431 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 32 | 13792 | 39.2791 | -120.9786 | 2 SPANS SS OF CGC 222858758852 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0144031 | OH | Sus | 46073898 | No | 2023 | NOV | Yes | Line to Line | 1893772 | CO | OH | No | No
SIERRA | FIELD OPS NORTH | Tier 2 | WISE-1102 | 152271102 | FUSE | 44565 | 20231230 | 129 | 2302372 | 471 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 942 | 38.9338 | -121.1818 | 1 S/OF 44565 | Overcast-Fog-Rain-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 23-0149303 | OH | Sus | 46104730 | No | 2023 | DEC | Yes | Line to Ground | 1900601 | CSO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 15383 | 20130109 | 1602 | 727664 | 560 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 12320 | 38.4483 | -123.0005 | 8231 TYRONE RD | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0003198 | OH | Sus | 41836375 | yes | 2013 | JAN | Yes |  | 99305194 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 5024 | 20130127 | 1531 | 735254 | 256 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 396 | 101376 | 38.4956 | -123.0074 | Nott/3569: 4 SPANS LOADSIDE OF LR 5024(SUSPECT LIMB CAUSED ) | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0006414 | OH | Sus | 41846059 | No | 2013 | JAN | Yes | Line to Line | 99303115 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 2719 | 20130201 | 553 | 737204 | 244 | Distribution Circuit | Equipment Failure/Involved | Other | 16 | 3904 | 38.2184 | -122.7934 | Kikuchi/3581: 4669 Chileno Valley Rd- Petaluma | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0007410 | OH | Sus | 41848060 | No | 2013 | FEB | Yes |  | 99302521 | CSO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 7123 | 20130207 | 1407 | 3500491 | 220 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1100 | 38.6272 | -123.3199 | 3 SPANS LD SIDE OF 7123 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0008740 | OH | Sus | 30976018 | No | 2013 | FEB | Yes | Line to Line | 99301745 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 12383 | 20130219 | 1722 | 744243 | 564 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 7896 | 38.3394 | -122.5282 | 5 SPANS LOAD SIDE | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0011025 | OH | Sus | 41856429 | yes | 2013 | FEB | Yes | Multi-Fault | 99300285 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 2021 | 20130305 | 2355 | 752119 | 336 | Distribution Circuit | Vegetation | Tree - branch fell on line | 183 | 38498 | 38.5031 | -122.9364 | 11864 REDWOOD RD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0014405 | OH | Sus | 30981204 | yes | 2013 | MAR | Yes | Line to Line | 99297942 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 13597 | 20130305 | 2354 | 752115 | 540 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 18360 | 38.5052 | -122.9243 | 11191 TERRACE DRIVE | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0014436 | OH | Sus | 41862183 | yes | 2013 | MAR | Yes |  | 99297876 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 240 | 20130305 | 2142 | 751979 | 268 | Distribution Circuit | Vegetation | Tree - branch fell on line | 803 | 144959 | 38.4715 | -123.0469 | AUSTIN CREEK RD N/OF SYLVIA LANE | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0014369 | OH | Sus | 30981201 | yes | 2013 | MAR | Yes |  | 99297967 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1407 | 20130306 | 3 | 752127 | 844 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 15192 | 38.4978 | -122.9027 | 9215 RIO DELL COURT | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0014435 | OH | Sus | 30981206 | yes | 2013 | MAR | Yes | Line to Line | 99297877 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 9797 | 20130306 | 707 | 752462 | 328 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 7000 | 38.4156 | -122.9003 | 2156 GREEN HILL RD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0014527 | OH | Sus | 41862265 | yes | 2013 | MAR | Yes |  | 99297802 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 3891 | 20130306 | 527 | 752506 | 833 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 25823 | 38.5159 | -123.0644 | 2 LD SIDE OF 2891 AND WIRE DOWN AT MTR # 1006465884 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0014518 | OH | Sus | 0 | yes | 2013 | MAR | Yes | Line to Ground | 99297813 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | OTHER |  | 20130404 | 1806 | 766712 | 490 | Distribution Circuit | Equipment Failure/Involved | Other | 686 | 121588 | 38.5307 | -123.0881 | 7 SPANS FROM SW 4195 AT MTR#1008134582 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0021595 | OH | Sus | 30987512 | No | 2013 | APR | Yes | None | 99292848 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | SWITCH | 7621 | 20130404 | 1048 | 766512 | 153 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 19118 | 38.4777 | -122.9422 | Smith/4343: FALLEN TREE ON HIGHWAY 116- EAST OF GREEN VALLEY ROAD IN FORESTVILLE | Rain-32 - 90 F | Conductor, Overhead | On Ground | 13-0021436 | OH | Sus | 41876952 | No | 2013 | APR | Yes | None | 99292890 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 18253 | 20130404 | 1940 | 766735 | 642 | Distribution Circuit | Vegetation | Tree - branch fell on line | 39 | 20801 | 38.473 | -123.0241 | 21895 MESA GRANDE TERRACE- MONTE RIO (CORNER OF RIVER WAY/MESA GRANDE TERRACE) | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0021622 | OH | Sus | 41877136 | No | 2013 | APR | Yes | Line to Ground | 99292780 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 8699 | 20130407 | 2259 | 767978 | 483 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2415 | 38.3897 | -122.9206 | 1P BEYOND FUCO'S 8699 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0022127 | OH | Sus | 41877795 | yes | 2013 | APR | Yes | Line to Line | 99292355 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 2101 | 20130410 | 1510 | 772500 | 639 | Distribution Circuit | Vegetation | Tree - fell into line | 224 | 123711 | 38.5194 | -122.9796 | LARGE REDWOOD AT 14910 RIO NIDO RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0023470 | OH | Sus | 30988728 | No | 2013 | APR | Yes | Line to Ground | 99291265 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1139 | 20130413 | 1540 | 774224 | 343 | Distribution Circuit | Equipment Failure/Involved | Other | 143 | 49049 | 38.5091 | -122.9196 | OLD RIVER RD AND WOODSIDE DR | Partly cloudy-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 13-0024217 | OH | Sus | 30989279 | No | 2013 | APR | Yes | None | 99290787 | CAW | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 12037 | 20130413 | 1017 | 774150 | 328 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 7216 | 38.3983 | -122.9736 | 3885 DEER MEADOW | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0024188 | OH | Sus | 0 | No | 2013 | APR | Yes | Line to Ground | 99290801 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 779 | 20130414 | 1448 | 774634 | 652 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 28688 | 38.5969 | -122.9891 | 8796 MILL CREEK RD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0024303 | OH | Sus | 0 | No | 2013 | APR | Yes | Line to Line | 99290685 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 781 | 20130414 | 1416 | 774648 | 799 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 11985 | 38.6024 | -123.0036 | 10 SPANS BEYOND 781 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0024333 | OH | Sus | 0 | No | 2013 | APR | Yes | Line to Line | 99290657 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 13983 | 20130414 | 1556 | 774593 | 239 | Distribution Circuit | Equipment Failure/Involved | Other | 103 | 7963 | 38.5336 | -123.1304 | 19230 FT ROSS RD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0024297 | OH | Sus | 0 | No | 2013 | APR | Yes | Line to Ground | 99290693 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 3891 | 20130415 | 1119 | 775094 | 351 | Distribution Circuit | Vegetation | Tree - bark fell into line | 31 | 10881 | 38.5159 | -123.0644 | 2 SPANS LD SIDE OF FUCO 3891 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0024541 | OH | Sus | 41883792 | yes | 2013 | APR | Yes |  | 99290497 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | MONTE RIO-1111 | 42811111 | OTHER |  | 20130416 | 1233 | 776434 | 400 | Distribution Circuit | Animal | Bird found | 389 | 82572 | 38.45 | -123.0592 | Arvig/3970: E/O # 26051 Hwy 116- Duncan Mills | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0024938 | OH | Sus | 41884713 | yes | 2013 | APR | Yes | Line to Ground | 99290198 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 36536 | 20130423 | 858 | 780086 | 475 | Distribution Circuit | 3rd Party | Vehicle | 790 | 77636 | 38.3143 | -122.7368 | 4 POLES FROM 79249 TWD 710255 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0026529 | OH | Sus | 0 | yes | 2013 | APR | Yes | Three Phase Fault | 99289006 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2225 | 20130423 | 510 | 779930 | 382 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 34380 | 38.524 | -122.6538 | 3180 CALISTOGA RD. | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0026478 | OH | Sus | 41887364 | yes | 2013 | APR | Yes | Line to Line | 99289058 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 15417 | 20130424 | 2132 | 781304 | 358 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 5728 | 38.4215 | -122.9569 | 3 SPANS LD SIDE OF FUCO 15417 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0027083 | OH | Sus | 41888577 | No | 2013 | APR | Yes | Line to Ground | 99288681 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 15707 | 20130429 | 1417 | 783480 | 319 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 8613 | 38.5448 | -122.6487 | Horner/3888: 3430 CHALFANT. APPROX 7 SPANS LD SIDE OF FUCO 15707 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0028054 | OH | Sus | 30993171 | No | 2013 | APR | Yes | Line to Line | 99287906 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 3069 | 20130501 | 947 | 785004 | 493 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2465 | 38.6052 | -122.9827 | 8152 MILL CREEK RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0028627 | OH | Sus | 41891460 | yes | 2013 | MAY | Yes |  | 99287443 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 12997 | 20130501 | 2151 | 785514 | 954 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 3602 | 38.503 | -122.9538 | LD SIDE OF SBCO'S 12995 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0028773 | OH | Sus | 41891650 | yes | 2013 | MAY | Yes | Line to Line | 99287293 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 42419 | 20130505 | 712 | 787419 | 463 | Distribution Circuit | Vegetation | Tree - bark fell into line | 2 | 926 | 38.5218 | -123.0615 | 3600 EAST AUSTIN CREEK RD IN CAZADERO- at 4 SPANS BEYOND LCO 42419 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0029578 | OH | Sus | 41892955 | yes | 2013 | MAY | Yes |  | 99286724 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 2659 | 20130508 | 124 | 789657 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 15022 | 38.5068 | -123.0702 | COR OF CAZ HWY AND SUNRISE MTN RD. | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0030354 | OH | Sus | 41894084 | No | 2013 | MAY | Yes |  | 99286057 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 134 | 20130515 | 120 | 793055 | 732 | Distribution Circuit | Vegetation | Tree - fell into line | 230 | 66074 | 38.5589 | -123.2702 | NEAR MTR # 1009170955 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0031981 | OH | Sus | 41897874 | No | 2013 | MAY | Yes |  | 99284996 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | MONTE RIO-1111 | 42811111 | FUSE | 1157 | 20130515 | 1830 | 793454 | 453 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2265 | 38.4369 | -123.0973 | 9 SPANS SOURCE SIDE OF RISER C/OUT 41294 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0032182 | OH | Sus | 41899619 | No | 2013 | MAY | Yes |  | 99284868 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 15035 | 20130518 | 1428 | 794644 | 332 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 3652 | 38.5458 | -122.6448 | 3402 KINGVILLE RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0032784 | OH | Sus | 41900807 | No | 2013 | MAY | Yes | Line to Ground | 99284469 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 12997 | 20130528 | 1137 | 799769 | 303 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 3939 | 38.503 | -122.9538 | 1 SPAN LD SIDE OF C/O 12997 | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 13-0034829 | OH | Sus | 30999097 | No | 2013 | MAY | Yes | Line to Line | 99282967 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | SWITCH | RSB5 | 20130528 | 1517 | 799894 | 283 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1582 | 38.5378 | -123.0901 | 18595 KING RIDGE RD- CAZADERO | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 13-0034951 | OH | Sus | 41904460 | No | 2013 | MAY | Yes |  | 99282941 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE | 2331 | 20130528 | 102 | 799410 | 188 | Distribution Circuit | Equipment Failure/Involved | Other | 13 | 2444 | 38.3652 | -123.0707 | ON THE UNFUSED TAP LINE LOCATED 1 SPAN E/OF FUCO 2331 (TWD THE TRANSFORMER at COORDINATES 2169390 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0034633 | OH | Sus | 0 | No | 2013 | MAY | Yes | Line to Line | 99283062 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 659 | 20130601 | 1726 | 802028 | 244 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 4392 | 38.2342 | -122.6902 | 218018520708 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0035870 | OH | Sus | 41906273 | No | 2013 | JUN | Yes | Line to Line | 99282335 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 2987 | 20130612 | 413 | 809141 | 662 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 43178 | 38.5419 | -123.0902 | 19779 KING RIDGE RD X-St.: 2MI AWAY FRM CAZADERO HWY | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0038913 | OH | Sus | 31002312 | No | 2013 | JUN | Yes | Line to Ground | 99280252 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4537 | 20130613 | 1833 | 810096 | 682 | Distribution Circuit | 3rd Party | Vehicle | 11 | 7502 | 38.5246 | -123.2647 | 6P LD SIDE OF FUCO'S 4537 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0039545 | OH | Sus | 31002736 | No | 2013 | JUN | Yes | Three Phase Fault | 99279925 | PW | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 3327 | 20130618 | 912 | 812420 | 1035 | Distribution Circuit | 3rd Party | Vehicle | 5 | 5175 | 38.2003 | -122.7162 | 2600 CHILENO VALLEY RD | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0040528 | OH | Sus | 31003599 | No | 2013 | JUN | Yes | Line to Line | 99279244 | PW | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 781 | 20130625 | 1440 | 817196 | 170 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 2550 | 38.6024 | -123.0036 | 10250 MILL CREEK RD | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0042599 | OH | Sus | 0 | yes | 2013 | JUN | Yes | Line to Ground | 99277951 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 6121 | 20130625 | 820 | 816701 | 460 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 3884 | 38.5402 | -122.6376 | 5828 GATES RD | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0042500 | OH | Sus | 41918420 | yes | 2013 | JUN | Yes |  | 99277992 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | FULTON-1102 | 42561102 | FUSE | 909 | 20130629 | 1711 | 820707 | 499 | Distribution Circuit | 3rd Party | Aircraft | 28 | 11337 | 38.6094 | -122.7756 | INGRAM- JEFF/4: 6225 W SODA ROCK LN | Clear-Above 90 F | Conductor, Overhead | Broken, wire on ground | 13-0043817 | OH | Sus | 0 | yes | 2013 | JUN | Yes | Line to Ground | 99277041 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24918 | 20130704 | 1442 | 825530 | 330 | Distribution Circuit | Vegetation | Tree - fell into line | 182 | 60060 | 38.5912 | -122.92 | 4885 MILL CREEK RD | Clear-Above 90 F | Conductor, Overhead | Broken, wire on ground | 13-0045220 | OH | Sus | 41921920 | yes | 2013 | JUL | Yes | Line to Line | 99275858 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | OTHER |  | 20130705 | 237 | 826115 | 453 | Distribution Circuit | Vegetation | Tree - branch fell on line | 241 | 55698 | 38.4133 | -122.9728 | AT MTR # 1007687082 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0045319 | OH | Sus | 31006935 | yes | 2013 | JUL | Yes | None | 99275743 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | FUSE | 14593 | 20130713 | 2139 | 831026 | 561 | Distribution Circuit | 3rd Party | Vehicle | 15 | 8415 | 38.5183 | -122.7204 | 1ST POLE S/OF LCO 14593 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0047233 | OH | Sus | 0 | No | 2013 | JUL | Yes | Line to Line | 99274391 | PW | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 2359 | 20130817 | 2032 | 850327 | 478 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 26427 | 38.3579 | -122.5258 | 1140 HILL RD- GLEN ELLEN | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0055412 | OH | Sus | 31015524 | No | 2013 | AUG | Yes | Line to Line | 99268807 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 4133 | 20130818 | 814 | 850453 | 506 | Distribution Circuit | Equipment Failure/Involved | Other | 10 | 3557 | 38.1492 | -122.823 | 5600 MARSHALL PETALUMA RD | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0055447 | OH | Sus | 41944863 | No | 2013 | AUG | Yes | None | 99268730 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | OCB | OCB | 20130826 | 233 | 855613 | 1340 | Distribution Circuit | Vegetation | Tree - fell into line | 3884 | 2163188 | 38.4715 | -123.012 | 17350 GUERNEWOOD LN | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0057374 | OH | Sus | 31017148 | No | 2013 | AUG | Yes | Line to Line | 99267169 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1313 | 20130902 | 1940 | 859697 | 452 | Distribution Circuit | Vegetation | Tree - fell into line | 108 | 48816 | 38.5041 | -122.9883 | 15140 DRAKE RD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0059193 | OH | Sus | 41949758 | yes | 2013 | SEP | Yes | Line to Line | 99266021 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1109 | 42631109 | SWITCH | 6159 | 20130907 | 1052 | 862231 | 776 | Distribution Circuit | 3rd Party | Vehicle | 61 | 11762 | 38.1622 | -122.6845 | AT FUCO 2623 (POINT REYES-PETALUMA RD at 8 POLES S/ SAN ANTONIO RD.) | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0060418 | OH | Sus | 31019785 | No | 2013 | SEP | Yes | None | 99265168 | PW | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | OTHER |  | 20130913 | 440 | 865461 | 293 | Distribution Circuit | Equipment Failure/Involved | Other | 791 | 56050 | 38.2997 | -122.8269 | 9999 VALLEY FORD RD | Fog-32 - 90 F | Conductor, Overhead | On Ground | 13-0061717 | OH | Sus | 41956700 | No | 2013 | SEP | Yes |  | 99264216 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1102 | 42821102 | FUSE | 593 | 20130917 | 1124 | 867394 | 307 | Distribution Circuit | Vegetation | Tree - branch fell on line | 72 | 25826 | 38.833 | -123.0109 | GEYSERS RD at 4 SPANS ON THE SOURCE-SIDE OF LCO 595 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0062530 | OH | Sus | 41960680 | No | 2013 | SEP | Yes | Line to Ground | 99263564 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1989 | 20130917 | 1451 | 867550 | 186 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 7998 | 38.522 | -122.9972 | 16270 RIO NIDO RD. GUERNVILLE | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0062618 | OH | Sus | 41960883 | No | 2013 | SEP | Yes |  | 99263530 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 891 | 20130921 | 716 | 869850 | 375 | Distribution Circuit | Vegetation | Tree - branch fell on line | 94 | 20625 | 38.39 | -122.8848 | 1 POLE SOUTH OF 930 FURLONG RD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0063601 | OH | Sus | 41962646 | yes | 2013 | SEP | Yes |  | 99262890 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 77153 | 20130921 | 528 | 869780 | 632 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5688 | 38.534 | -123.0864 | 18170 MARY ST | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0063617 | OH | Sus | 31023138 | yes | 2013 | SEP | Yes | Line to Line | 99262880 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1101 | 42091101 | TRANSFORMER |  | 20131001 | 708 | 875825 | 592 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1776 | 38.4325 | -122.9049 | 3550 BONES RD | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0066041 | OH | Sus | 31025269 | No | 2013 | OCT | Yes | Line to Ground | 99260983 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 3107 | 20131003 | 2223 | 877778 | 477 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 1431 | 38.3372 | -122.512 | 1/8 MILE S/OF ARNOLD DR | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0067097 | OH | Sus | 31025997 | yes | 2013 | OCT | Yes | Line to Ground | 99260315 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 429 | 20131003 | 1659 | 877543 | 446 | Distribution Circuit | Vegetation | Tree - branch fell on line | 64 | 17879 | 38.4735 | -123.0227 | Galea/3472: MOSCOW RD AND CENTER | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0067028 | OH | Sus | 41967580 | yes | 2013 | OCT | Yes |  | 99260445 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 474 | 20131003 | 1347 | 877378 | 1499 | Distribution Circuit | Vegetation | Tree - fell into line | 182 | 202194 | 38.5056 | -122.6458 | Fechter/3471: MAIN LINE NEAR 6550 MAYACAMAS RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0066942 | OH | Sus | 31025932 | yes | 2013 | OCT | Yes |  | 99260326 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | SONOMA-1104 | 42721104 | FUSE | 6533 | 20131003 | 2315 | 877862 | 1029 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 17493 | 38.3022 | -122.5531 | 4700 GROVE ST | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0067130 | OH | Sus | 31026030 | yes | 2013 | OCT | Yes |  | 99260299 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6899 | 20131005 | 237 | 879081 | 330 | Distribution Circuit | Equipment Failure/Involved | Other | 81 | 21162 | 38.3925 | -122.9733 | 3970 JOY RD | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0067497 | OH | Sus | 41967995 | No | 2013 | OCT | Yes | Line to Ground | 99260009 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | RINCON-1104 | 43321104 | OCB | OCB | 20131005 | 609 | 879091 | 691 | Distribution Circuit | 3rd Party | Vehicle | 3986 | 356853 | 38.4897 | -122.6663 | RISER FUCO 7093 at HWY 12- 250' W/OF BRUSH CREEK RD | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0067499 | OH | Sus | 0 | No | 2013 | OCT | Yes |  | 99260007 | PW | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 8227 | 20131022 | 1113 | 888545 | 297 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 5049 | 38.5037 | -123.0301 | 15550 CAMINO DEL ROYO | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0071285 | OH | Sus | 41975937 | No | 2013 | OCT | Yes |  | 99257139 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4543 | 20131104 | 1320 | 896190 | 565 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 10 | 5650 | 38.5894 | -123.3032 | 3 SPANS FROM EOL ON 4543 TAP LINE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0074293 | OH | Sus | 41983310 | No | 2013 | NOV | Yes | Line to Line | 99254930 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1102 | 42821102 | FUSE | 2815 | 20131119 | 610 | 904307 | 515 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6180 | 38.8467 | -123.0189 | 3P BEYOND FUCO'S 2815 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0076905 | OH | Sus | 0 | yes | 2013 | NOV | Yes |  | 99252644 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1102 | 42821102 | OTHER |  | 20131123 | 204 | 913375 | 231 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 693 | 38.7649 | -123.0159 | 1325 HIATT RD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078872 | OH | Sus | 0 | yes | 2013 | NOV | Yes |  | 99251164 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1102 | 42821102 | RECLOSER | 674 | 20131123 | 516 | 913427 | 664 | Distribution Circuit | Vegetation | Tree - branch fell on line | 221 | 58089 | 38.8295 | -123.0065 | Nott/3569: 226 PRESTON DR 3 SPANS SOURCE OF 17355 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078901 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Multi-Fault | 99251151 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1103 | 43071103 | FUSE | 13333 | 20131123 | 3 | 911056 | 1038 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 12456 | 38.3737 | -122.5175 | 2-3 SPANS WEST OF FUCO 13333 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0078851 | OH | Sus | 0 | yes | 2013 | NOV | Yes | Line to Ground | 99251173 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | OTHER |  | 20131205 | 403 | 919698 | 482 | Distribution Circuit | Equipment Failure/Involved | Other | 465 | 24325 | 38.614 | -122.8295 | BAILACHE AVE at TOYON DR | Clear-Below 32 F | Connector or Splice (OH) | Broken, wire on object | 13-0080620 | OH | Sus | 42039626 | No | 2013 | DEC | Yes | Line to Ground | 99249535 | CSO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1067 | 20131214 | 1429 | 927700 | 195 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 110 | 26313 | 38.4934 | -123.0062 | 16689 NEELEY RD. GUERNVILLE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0082366 | OH | Sus | 42046275 | No | 2013 | DEC | Yes |  | 99247771 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1102 | 42821102 | FUSE | 595 | 20131227 | 1235 | 934491 | 535 | Distribution Circuit | Equipment Failure/Involved | Other | 48 | 10380 | 38.8471 | -123.0204 | 4 SPANS LD SIDE OF FUCO 15747 | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 13-0083513 | OH | Sus | 31045317 | No | 2013 | DEC | Yes | Three Phase Fault | 99246082 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 7271 | 20131228 | 1507 | 934870 | 141 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 53 | 6548 | 38.486 | -122.9629 | AT SBCO 15353 TWD LD SIDE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0083575 | OH | Sus | 42051341 | No | 2013 | DEC | Yes |  | 99245981 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | OCB | OCB | 20140103 | 1736 | 937097 | 927 | Distribution Circuit | 3rd Party | Vehicle | 1345 | 238865 | 38.3096 | -122.732 | POLE WITH SW 1653 ( E/VALLEY FORD RD & FALLON TWO ROCK ) | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0002158 | OH | Sus | 31046700 | No | 2014 | JAN | Yes | Multi-Fault | 99245373 | PW | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 140 | 20140123 | 1742 | 946388 | 608 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 141 | 43968 | 38.4671 | -123.0158 | MONTE VISTA TERRACE at FUCO'S 7535 ON MAIN LINE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0006030 | OH | Sus | 31051783 | yes | 2014 | JAN | Yes |  | 99243068 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1067 | 20140202 | 635 | 958047 | 390 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 42900 | 38.4934 | -123.0062 | 16745 NEELEY | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0008115 | OH | Sus | 31053922 | yes | 2014 | FEB | Yes | Line to Line | 99241777 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 1059 | 20140207 | 1611 | 961724 | 369 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 16236 | 38.527 | -123.0877 | 5590 CAZADERO HWY | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0009698 | OH | Sus | 42073079 | yes | 2014 | FEB | Yes |  | 99240948 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | FUSE | 3287 | 20140208 | 1317 | 963070 | 583 | Distribution Circuit | Vegetation | Tree - branch fell on line | 165 | 49005 | 38.3383 | -122.7856 | at 5 SPANS FROM RISER CUTOUTS 12609 TWD LCO 8459 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0009992 | OH | Sus | 0 | yes | 2014 | FEB | Yes |  | 99240670 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1101 | 42091101 | OTHER |  | 20140208 | 745 | 962789 | 741 | Distribution Circuit | 3rd Party | Vehicle | 377 | 105011 | 38.4735 | -122.9023 | Horner/3888: at # 7170 HWY 116 | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0009876 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Open Circuit | 99240751 | PW | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 250 | 20140208 | 2119 | 963573 | 408 | Distribution Circuit | Vegetation | Tree - fell into line | 278 | 48930 | 38.4817 | -123.0114 | 12800 MAYS CANYON ROAD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0010046 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Three Phase Fault | 99240558 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 11929 | 20140209 | 518 | 963860 | 352 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 9834 | 38.4179 | -122.8862 | 2020 COFFEE LN IN SEBASTOPOL | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0010092 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Three Phase Fault | 99240541 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1067 | 20140209 | 1225 | 964239 | 297 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 32670 | 38.4934 | -123.0062 | 16860 NEELEY RD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0010150 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Three Phase Fault | 99240475 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 3447 | 20140210 | 1627 | 965352 | 708 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 12036 | 38.5148 | -122.6289 | AT METER #1007510193 | Partly cloudy-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0010529 | OH | Sus | 31055963 | yes | 2014 | FEB | Yes | Line to Line | 99240172 | CAW | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | SWITCH | J2N2 | 20140211 | 1016 | 965751 | 443 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 22751 | 38.356 | -122.5393 | ON THE SINGLE-PHASE TAP FEEDING THE TRANSFORMER at COORDINATES 2184560 25190 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0010615 | OH | Sus | 42075839 | No | 2014 | FEB | Yes | None | 99240087 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | SECTIONALIZER | 106 | 20140215 | 2036 | 968088 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 29313 | 38.3713 | -122.9111 | 1100 VALLEY FORD-FREESTONE RD- VALLEY FORD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0011540 | OH | Sus | 42079304 | No | 2014 | FEB | Yes | Line to Line | 99239458 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 5691 | 20140220 | 906 | 969810 | 589 | Distribution Circuit | 3rd Party | Vehicle | 10 | 5890 | 38.4124 | -122.8914 | 10750 OCCIDENTAL RD. at GREEN HILL RD (1P LD SIDE) | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on object | 14-0012299 | OH | Sus | 31057717 | No | 2014 | FEB | Yes | Line to Line | 99238915 | PW | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | OTHER |  | 20140226 | 2010 | 973079 | 950 | Distribution Circuit | Vegetation | Tree - branch fell on line | 3 | 2850 | 38.231 | -122.9141 | 3 POLES ON THE LOAD-SIDE OF LCO 4219 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0013745 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Open Circuit | 99237979 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 3809 | 20140227 | 550 | 973466 | 1229 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 27708 | 38.5491 | -123.2124 | Arvig/3970: 28503 Bohan Dillon rd- Cazadero | Fog-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0013853 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Ground | 99237910 | PW | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 2305 | 20140227 | 559 | 973471 | 751 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2253 | 38.5094 | -123.097 | 5 SPANS PAST FUCO 2305 | Fog-32 - 90 F | Conductor, Overhead | On Ground | 14-0014007 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Ground | 99237856 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 96029 | 20140227 | 1351 | 973883 | 408 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1632 | 38.4823 | -123.0142 | COR OF OLD MONTE RIO RD AND CNOPIUS RD- MONTE RIO | Overcast-32 - 90 F | Conductor, Overhead | On Ground | 14-0014020 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Line | 99237855 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 8405 | 20140228 | 515 | 974360 | 584 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2920 | 38.5007 | -122.9214 | 2 SPAN LD SIDE OF FUCO 8405 | Drizzle-32 - 90 F | Conductor, Overhead | On Ground | 14-0014241 | OH | Sus | 0 | yes | 2014 | FEB | Yes | Line to Line | 99237658 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1139 | 20140312 | 854 | 983269 | 745 | Distribution Circuit | Vegetation | Tree - fell into line | 144 | 107280 | 38.5091 | -122.9196 | 10473 COZY CT | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0017554 | OH | Sus | 0 | yes | 2014 | MAR | Yes | Line to Line | 99235245 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 429 | 20140312 | 1045 | 983448 | 375 | Distribution Circuit | Vegetation | Tree - branch fell on line | 116 | 40224 | 38.4735 | -123.0227 | WS/ EAST ST 100' S/ 2ND ST | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0017541 | OH | Sus | 0 | yes | 2014 | MAR | Yes | Line to Ground | 99235252 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | OCB | OCB | 20140312 | 702 | 982968 | 674 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4990 | 1336613 | 38.4715 | -123.012 | 217126530529 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0017439 | OH | Sus | 0 | yes | 2014 | MAR | Yes | Multi-Fault | 99235334 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1053 | 20140312 | 836 | 983192 | 320 | Distribution Circuit | Vegetation | Tree - branch fell on line | 112 | 35840 | 38.4952 | -123.0101 | Arvig/3970: 17515 Summit ave- Guerneville | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0017503 | OH | Sus | 0 | yes | 2014 | MAR | Yes | Line to Ground | 99235273 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | RINCON-1103 | 43321103 | OCB | OCB | 20140329 | 1753 | 991553 | 574 | Distribution Circuit | Equipment Failure/Involved | Other | 1032 | 156242 | 38.4898 | -122.6661 | LD SIDE OF FUCO/SBCO 15133 & NG T361 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0021433 | OH | Sus | 42099623 | yes | 2014 | MAR | Yes |  | 99232559 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 7271 | 20140331 | 1126 | 992401 | 274 | Distribution Circuit | Vegetation | Tree - branch fell on line | 53 | 10622 | 38.486 | -122.9629 | AT FUCO 8885 | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0021829 | OH | Sus | 42100198 | yes | 2014 | MAR | Yes | Line to Line | 99232303 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1499 | 20140331 | 1125 | 992400 | 228 | Distribution Circuit | Environmental/External | Lightning | 132 | 30096 | 38.5088 | -122.9292 | AT FUCO 1499 - 2 LOCATIONS | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0021764 | OH | Sus | 42100181 | yes | 2014 | MAR | Yes | Line to Line | 99232322 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 36536 | 20140401 | 2332 | 993834 | 712 | Distribution Circuit | 3rd Party | Vehicle | 791 | 143396 | 38.3143 | -122.7368 | 4000 ROBLAR RD- COTATI | Fog-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0022318 | OH | Sus | 0 | yes | 2014 | APR | Yes | Line to Ground | 99231730 | PW | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 525 | 20140401 | 1505 | 993554 | 230 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 8510 | 38.4048 | -122.8963 | 1355 FURLONG RD | Drizzle-32 - 90 F | Conductor, Overhead | On Ground | 14-0022256 | OH | Sus | 42100844 | yes | 2014 | APR | Yes | Line to Line | 99232036 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 3891 | 20140404 | 1441 | 995314 | 889 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 10279 | 38.5159 | -123.0644 | 17825 OLD CAZADERO RD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0023150 | OH | Sus | 42102556 | No | 2014 | APR | Yes | Line to Ground | 99231473 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | SWITCH | J2N2 | 20140419 | 50 | 1001458 | 315 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 8185 | 38.5116 | -122.9224 | WESTSIDE RD IN FORESTVILLE- at 3 SPANS W/ THE TRANSFORMER at COORDINATES 2173660 30912 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0025981 | OH | Sus | 42110638 | No | 2014 | APR | Yes | Open Circuit | 99229619 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 2379 | 20140429 | 1518 | 1007630 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 8157 | 38.5016 | -122.9308 | 11494 TERRACE DR. FORESTVILLE | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0028184 | OH | Sus | 31072562 | yes | 2014 | APR | Yes |  | 99228034 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 36536 | 20140513 | 1623 | 1014680 | 309 | Distribution Circuit | Vegetation | Tree - fell into line | 781 | 88489 | 38.3143 | -122.7368 | 1 SPAN S/OF 7705 TWD 10165 MAINLINE. | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0031522 | OH | Sus | 42122933 | yes | 2014 | MAY | Yes | Line to Ground | 99225907 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 2885 | 20140514 | 1844 | 1015743 | 766 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4596 | 38.2713 | -122.7157 | END OF TAP | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0031904 | OH | Sus | 31076325 | yes | 2014 | MAY | Yes | Line to Line | 99225609 | PW | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 12013 | 20140526 | 633 | 1024069 | 405 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 3645 | 38.3694 | -122.9105 | 12983 BODEGA HWY- SEBASTOPOL | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0034257 | OH | Sus | 31078385 | No | 2014 | MAY | Yes | Line to Line | 99223969 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1101 | 43071101 | FUSE | 4817 | 20140604 | 1120 | 1028444 | 836 | Distribution Circuit | Equipment Failure/Involved | Other | 75 | 47202 | 38.3999 | -122.5697 | 2837 BRISTOL RD- KENWOOD | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0036229 | OH | Sus | 42134052 | No | 2014 | JUN | Yes | None | 99222610 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 296 | 20140606 | 758 | 1029398 | 389 | Distribution Circuit | 3rd Party | Vehicle | 119 | 23035 | 38.2073 | -122.6761 | 3053 CHILENO VALLEY RD | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0036571 | OH | Sus | 31081022 | No | 2014 | JUN | Yes | Line to Ground | 99222376 | PW | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1101 | 42821101 | FUSE | 7295 | 20140610 | 111 | 1032074 | 829 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 28186 | 38.8637 | -123.0878 | 33710 HWY 128 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0037397 | OH | Sus | 0 | yes | 2014 | JUN | Yes | Line to Ground | 99221784 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 3447 | 20140614 | 1536 | 1034706 | 733 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 16 | 11728 | 38.5148 | -122.6289 | 6585 ERLAND ROAD- SANTA ROSA | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0038420 | OH | Sus | 42138878 | No | 2014 | JUN | Yes | Line to Line | 99221017 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 246 | 20140621 | 649 | 1037560 | 476 | Distribution Circuit | Vegetation | Tree - fell into line | 544 | 46724 | 38.3659 | -122.5276 | 3111 WARM SPRINGS RD- GLEN ELLEN | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0039721 | OH | Sus | 42142704 | No | 2014 | JUN | Yes | Line to Line | 99220117 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 7697 | 20140629 | 1953 | 1041705 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4616 | 38.5158 | -123.0649 | 3600 E. AUTSTIN CREEK RD | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0041318 | OH | Sus | 42146832 | No | 2014 | JUN | Yes | Three Phase Fault | 99218874 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | SONOMA-1105 | 42721105 | FUSE | 6781 | 20140702 | 1128 | 1043460 | 328 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 5904 | 38.291 | -122.4125 | 2 SPANS LOAD SIDE OF 6781 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0042068 | OH | Sus | 42148371 | No | 2014 | JUL | Yes | Line to Line | 99218351 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 208 | 20140707 | 1751 | 1045786 | 282 | Distribution Circuit | Vegetation | Tree - branch fell on line | 184 | 23648 | 38.2262 | -122.7215 | 4803 SPRING HILL RD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0043023 | OH | Sus | 42149985 | No | 2014 | JUL | Yes | Line to Ground | 99217719 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 18253 | 20140710 | 1347 | 1047435 | 384 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 39 | 14976 | 38.473 | -123.0241 | MESA GRANDE TERRACE | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0043748 | OH | Sus | 31088096 | yes | 2014 | JUL | Yes | Line to Line | 99217229 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 13723 | 20140715 | 1557 | 1049923 | 78 | Distribution Circuit | Equipment Failure/Involved | Other | 6 | 468 | 38.5049 | -123.1372 | 4545 MUNIZ RANCH RD- JENNER | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0044692 | OH | Sus | 0 | No | 2014 | JUL | Yes | Line to Ground | 99216578 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 74315 | 20140717 | 1706 | 1051258 | 370 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 7030 | 38.4909 | -123.0602 | 2105 CAZADERO HWY | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0045270 | OH | Sus | 42156384 | No | 2014 | JUL | Yes | Line to Line | 99216206 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1102 | 43071102 | FUSE | 7125 | 20140724 | 204 | 1054295 | 686 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5488 | 38.3658 | -122.5743 | 6564 SONOMA MTN RD- GLEN ELLEN | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0046539 | OH | Sus | 31090808 | yes | 2014 | JUL | Yes |  | 99215289 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 1691 | 20140724 | 1156 | 1054532 | 354 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 708 | 38.3918 | -122.9323 | 2 SPANS LOAD SIDE OF 1691 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0046692 | OH | Sus | 42159042 | yes | 2014 | JUL | Yes | Line to Line | 99215194 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 659 | 20140724 | 1311 | 1054569 | 204 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 3468 | 38.2342 | -122.6902 | 380 STADLER | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0046739 | OH | Sus | 42159163 | yes | 2014 | JUL | Yes | None | 99215181 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | RECLOSER | 132 | 20140809 | 253 | 1063430 | 464 | Distribution Circuit | Vegetation | Tree - branch fell on line | 929 | 75790 | 38.2648 | -122.8054 | 2 SPANS SOURCE SIDE OF 30501 SHORLINE HWY- FALLON | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0050054 | OH | Sus | 0 | No | 2014 | AUG | Yes |  | 99212809 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1101 | 43071101 | FUSE | 3749 | 20140811 | 2324 | 1065145 | 346 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 4252 | 38.4004 | -122.5681 | 1 SPAN LD SIDE OF 17631 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0050439 | OH | Sus | 42168805 | yes | 2014 | AUG | Yes |  | 99212490 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | SWITCH | J2N2 | 20140815 | 1400 | 1066962 | 702 | Distribution Circuit | Vegetation | Tree - fell into line | 790 | 176221 | 38.4819 | -123.0529 | 1205 AUSTIN CRK RD. | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0051261 | OH | Sus | 31095281 | No | 2014 | AUG | Yes | Line to Ground | 99211885 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | SECTIONALIZER | 244 | 20140821 | 630 | 1069615 | 281 | Distribution Circuit | Equipment Failure/Involved | Other | 359 | 71865 | 38.3456 | -122.7783 | 5217 BLANK RD | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0052158 | OH | Sus | 42174857 | No | 2014 | AUG | Yes | Line to Ground | 99211247 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 1797 | 20140831 | 212 | 1075279 | 413 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 7021 | 38.4202 | -122.9523 | Kikuchi/1512: 2520 SteppsRd- Sebastopol | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0054293 | OH | Sus | 42179140 | No | 2014 | AUG | Yes | None | 99209765 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 1787 | 20140913 | 718 | 1080690 | 482 | Distribution Circuit | 3rd Party | Vehicle | 332 | 82662 | 38.4199 | -122.9308 | 1787 | Overcast-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0056726 | OH | Sus | 31100895 | No | 2014 | SEP | Yes | Three Phase Fault | 99208152 | PW | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 3259 | 20140924 | 1337 | 1086813 | 864 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 8256 | 38.4002 | -122.9541 | 2193 MARRA RD | Overcast-32 - 90 F | Pole-Wood | Broken, wire on object | 14-0059003 | OH | Sus | 31103197 | No | 2014 | SEP | Yes | Line to Line | 99206573 | PW | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1313 | 20140929 | 1034 | 1090013 | 274 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 109 | 29866 | 38.5041 | -122.9884 | 14902 MELODY | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0060211 | OH | Sus | 0 | No | 2014 | SEP | Yes | Line to Line | 99205671 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 2373 | 20141001 | 1635 | 1091443 | 701 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 6 | 4206 | 38.5096 | -122.9607 | 10 SPANS LD SIDE OF FUCO 2373 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0060796 | OH | Sus | 42200291 | No | 2014 | OCT | Yes | Line to Ground | 99205327 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 256 | 20141009 | 1910 | 1095294 | 563 | Distribution Circuit | Equipment Failure/Involved | Other | 1487 | 236850 | 38.4698 | -123.0146 | 5 SPANS PAST LR 292 AT FUCO 17195 & 4 SPANS LINE SIDE 28000 HWY 116 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0062700 | OH | Sus | 42204289 | No | 2014 | OCT | Yes | Three Phase Fault | 99204189 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 292 | 20141010 | 513 | 1095383 | 436 | Distribution Circuit | Equipment Failure/Involved | Other | 154 | 25496 | 38.4619 | -123.0418 | MAINLINE/3 SPANS LD SIDE OF FUCO 98731 | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 14-0062723 | OH | Sus | 42204297 | No | 2014 | OCT | Yes | Line to Line | 99204151 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1109 | 42631109 | OTHER |  | 20141010 | 1441 | 1095811 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1056 | 38.1742 | -122.6256 | 969 SAN ANTONIO RD. | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0062898 | OH | Sus | 31106795 | No | 2014 | OCT | Yes | Line to Ground | 99204057 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | OTHER |  | 20141012 | 1434 | 1096354 | 601 | Distribution Circuit | Equipment Failure/Involved | Other | 230 | 114101 | 38.5573 | -123.2721 | 2 SPANS LD SIDE OF LR 134 ( 31090 TIMBER COVE RD. ) | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0063056 | OH | Sus | 42207176 | No | 2014 | OCT | Yes | Line to Ground | 99203524 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 1249 | 20141019 | 1457 | 1099400 | 245 | Distribution Circuit | Vegetation | Tree - fell into line | 185 | 62810 | 38.3784 | -122.5531 | 2781 WARM SPRINGS RD- GLENN ELLEN | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0064560 | OH | Sus | 31108702 | No | 2014 | OCT | Yes | Line to Ground | 99202989 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | OTHER |  | 20141026 | 1626 | 1103226 | 518 | Distribution Circuit | Equipment Failure/Involved | Other | 103 | 33911 | 38.3937 | -123.0887 | 6707 HWY 1- BODEGA BAY | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0066224 | OH | Sus | 42216062 | No | 2014 | OCT | Yes | Line to Ground | 99201825 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 433 | 20141122 | 803 | 1116537 | 296 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 9768 | 38.5091 | -122.9284 | 4 SPANS LD SIDE OF FUCO 433 - 12300 WESTSIDE RD - | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0071572 | OH | Sus | 42280137 | No | 2014 | NOV | Yes | Line to Ground | 99198250 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1101 | 43071101 | FUSE | 15877 | 20141126 | 1231 | 1118478 | 535 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2140 | 38.3996 | -122.5128 | 2 SPANS LD SIDE OF 15877 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0072227 | OH | Sus | 42281513 | No | 2014 | NOV | Yes | Line to Line | 99197737 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 3055 | 20141129 | 511 | 1119190 | 672 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 8169 | 38.4073 | -122.9273 | 13400 FRATI LN | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0072402 | OH | Sus | 31118049 | No | 2014 | NOV | Yes | Line to Ground | 99197582 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 134 | 20141202 | 748 | 1120544 | 376 | Distribution Circuit | Vegetation | Tree - fell into line | 230 | 53525 | 38.5589 | -123.2702 | SS OF 88323 SBCO at 22105 TIMBER COVE RD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0072849 | OH | Sus | 31118617 | yes | 2014 | DEC | Yes |  | 99197209 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 8493 | 20141202 | 1202 | 1120909 | 318 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 13674 | 38.5327 | -123.2713 | 21002 HWY 1- JENNER | Heavy rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0072952 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99197157 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1031 | 20141204 | 1613 | 1124769 | 279 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 6696 | 38.4926 | -122.9614 | 11726 CANYON RD. | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0073877 | OH | Sus | 31119446 | yes | 2014 | DEC | Yes |  | 99196421 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | RECLOSER | 658 | 20141205 | 1333 | 1125296 | 390 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 40896 | 38.4451 | -122.9103 | 3 SPANS W/OF 12072 GREEN VALLEY RD. | Drizzle-32 - 90 F | Conductor, Overhead | On Ground | 14-0074038 | OH | Sus | 42291560 | No | 2014 | DEC | Yes | Multi-Fault | 99196219 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 8139 | 20141205 | 1655 | 1125428 | 472 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 16992 | 38.4981 | -123.0729 | 66 SUNRISE MTN RD | Rain-32 - 90 F | Conductor, Overhead | On Ground | 14-0074083 | OH | Sus | 42291576 | No | 2014 | DEC | Yes | Line to Line | 99196195 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 2021 | 20141209 | 831 | 1127445 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 183 | 56421 | 38.5031 | -122.9364 | MTR#1007761814- # 11815 ORCHARD RD. FORESTVILLE | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0074504 | OH | Sus | 31120332 | No | 2014 | DEC | Yes |  | 99195656 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 7123 | 20141213 | 1420 | ODB-9919 | 200 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 1000 | 38.6272 | -123.3199 | 2P BEYOND FUCO'S 7123 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076783 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99193312 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | OTHER |  | 20141213 | 1550 | 1140024 | 62 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 62 | 38.3845 | -122.9827 | 17411 TAYLOR | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076788 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193309 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 2301 | 20141213 | 852 | 1139565 | 477 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 8586 | 38.5285 | -123.0954 | 500 KRAMER | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076733 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193354 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | SONOMA-1104 | 42721104 | FUSE | 6533 | 20141213 | 920 | 1139594 | 420 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 1622 | 38.3022 | -122.5531 | 1SP SS OF FUCO 12475 HARD TAP | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076709 | OH | Sus | 0 | yes | 2014 | DEC | Yes |  | 99193379 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | RECLOSER | 132 | 20141215 | 313 | 1140747 | 688 | Distribution Circuit | Vegetation | Tree - fell into line | 929 | 208517 | 38.2648 | -122.8054 | WEST SIDE OF FUCO 2555 ( BET CERINI AND FAIRBANKS RD ) | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 14-0076929 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Multi-Fault | 99193055 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 12211 | 20141215 | 350 | 1140760 | 587 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1761 | 38.2057 | -122.6822 | 1 SPAN LD SIDE OF 12211 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0076945 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99193041 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 12383 | 20141219 | 715 | 1144157 | 928 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 12992 | 38.3394 | -122.5282 | 3 SPANS LD SIDE OF FUCO 12383 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077686 | OH | Sus | 31122278 | No | 2014 | DEC | Yes | Line to Ground | 99192225 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 56225 | 20141219 | 1450 | 1144546 | 250 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 8178 | 38.4846 | -123.0587 | Arvig/3970: 1440 cazadero hwy- cazadero | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077738 | OH | Sus | 42301427 | No | 2014 | DEC | Yes | Line to Ground | 99192183 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 79306 | 20141221 | 402 | 1145336 | 749 | Distribution Circuit | 3rd Party | Vehicle | 403 | 88288 | 38.3719 | -122.9112 | 13279 BODEGA HWY NEAR RASBERRY LANE | Rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0077857 | OH | Sus | 0 | No | 2014 | DEC | Yes | Line to Ground | 99192028 | PW | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 8303 | 20141221 | 853 | 1145420 | 627 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3135 | 38.3887 | -122.9246 | Deignan/3571: R/O 13229 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0077885 | OH | Sus | 42301654 | No | 2014 | DEC | Yes | Line to Line | 99191998 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 769 | 20141223 | 2214 | 1146894 | 536 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 8000 | 38.5963 | -122.9143 | 3131 WALLACE CREEK RD | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078174 | OH | Sus | 31123162 | No | 2014 | DEC | Yes | Line to Ground | 99191618 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 7183 | 20141224 | 1509 | 1147615 | 292 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 11680 | 38.3774 | -122.9677 | MTR#1009711166 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078288 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99191517 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1989 | 20141224 | 1315 | 1147434 | 165 | Distribution Circuit | Vegetation | Tree - branch fell on line | 43 | 7095 | 38.522 | -122.9972 | MTR#1008910831 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078245 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Ground | 99191556 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 2027 | 20141224 | 2041 | 1147994 | 274 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 7398 | 38.5189 | -122.9801 | 8 SPANS LD SIDE OF 2027 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078376 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99191445 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 3899 | 20141226 | 1750 | 1148930 | 940 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 4700 | 38.5317 | -123.0874 | MTR #1007897524 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078597 | OH | Sus | 31123497 | No | 2014 | DEC | Yes | Line to Line | 99191140 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | RECLOSER | 87402 | 20141226 | 1819 | 1148941 | 1375 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 49500 | 38.1635 | -122.8912 | 9400 MARSHALL PETALUMA RD- APPROX 25 SPANS LD SIDE OF LR87402 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0078600 | OH | Sus | 42303585 | No | 2014 | DEC | Yes | Line to Line | 99191138 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1109 | 42631109 | RECLOSER | 296 | 20141228 | 1537 | 1149569 | 817 | Distribution Circuit | Equipment Failure/Involved | Other | 343 | 103296 | 38.2203 | -122.6439 | HIGH SIDE OF FUCO 2603 ON MAIN LINE | Partly cloudy-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0078736 | OH | Sus | 31123590 | No | 2014 | DEC | Yes | Multi-Fault | 99190991 | CSO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 8227 | 20150116 | 1048 | 1164755 | 207 | Distribution Circuit | Vegetation | Tree - branch fell on line | 17 | 3519 | 38.5037 | -123.0301 | 14415 CAMINO DEL ARROYO | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0005139 | OH | Sus | 0 | No | 2015 | JAN | Yes | Line to Ground | 99187791 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1101 | 43071101 | FUSE | 4817 | 20150120 | 1333 | 1166179 | 268 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 73 | 19564 | 38.3999 | -122.5697 | 2800 BLK OF BRISTOL | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0005749 | OH | Sus | 42318905 | No | 2015 | JAN | Yes | Line to Line | 99187433 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 5152 | 20150128 | 625 | 1169228 | 607 | Distribution Circuit | 3rd Party | Vehicle | 16 | 9712 | 38.55 | -122.6677 | 6 POLES LOAD SIDE OF LR 5152 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0007589 | OH | Sus | 31131026 | No | 2015 | JAN | Yes | Multi-Fault | 99186569 | PW | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE | 2331 | 20150205 | 2234 | 1172998 | 451 | Distribution Circuit | Vegetation | Tree - branch fell on line | 13 | 5863 | 38.3652 | -123.0707 | 6 SPANS N/OF FUCO 16935 | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 15-0009765 | OH | Sus | 42328901 | yes | 2015 | FEB | Yes | Line to Line | 99185349 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1102 | 42821102 | FUSE | 17797 | 20150209 | 1615 | 1186942 | 1032 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1032 | 38.7925 | -123.1631 | 216682642100 | Strong winds-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 15-0012279 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Line | 99182756 | CAW | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 2305 | 20150209 | 1621 | 1186945 | 149 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 447 | 38.5094 | -123.097 | 216895230822 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0012287 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99183069 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | OTHER |  | 20150217 | 1436 | 1191705 | 576 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 111 | 42229 | 38.5439 | -123.2914 | 22193 HWY 1 | Fog-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0013809 | OH | Sus | 42334907 | No | 2015 | FEB | Yes | Line to Ground | 99181655 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | RECLOSER | 77670 | 20150223 | 1325 | 1194781 | 554 | Distribution Circuit | Vegetation | Tree - branch fell on line | 513 | 85762 | 38.5025 | -122.7368 | CARRIAGE LANE E/OF CARRIAGE COURT | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0015168 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99180778 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 6121 | 20150223 | 730 | 1194391 | 845 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11830 | 38.5402 | -122.6376 | 1/P/LOADSIDE OF 6121 | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0015025 | OH | Sus | 31136404 | yes | 2015 | FEB | Yes | Line to Line | 99180836 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 94261 | 20150223 | 802 | 1194429 | 384 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 8832 | 38.4716 | -122.6843 | 1885 LOS OLIVOS | Strong winds-32 - 90 F | Conductor, Overhead | On Ground | 15-0014979 | OH | Sus | 31136325 | yes | 2015 | FEB | Yes | Line to Line | 99180867 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 296 | 20150301 | 648 | 1197687 | 400 | Distribution Circuit | Equipment Failure/Involved | Other | 119 | 20536 | 38.2073 | -122.6761 | MAINLINE BET 12211 & 12213 956 CHILENO VALLEY RD | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0016458 | OH | Sus | 42340406 | No | 2015 | MAR | Yes | Line to Ground | 99179944 | CSO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 250 | 20150331 | 1624 | 1210848 | 566 | Distribution Circuit | Vegetation | Tree - fell into line | 61 | 34526 | 38.4817 | -123.0114 | AT SW 419 ( OLD MONTE RIO RD W/OF MAY ) | Clear-32 - 90 F | Switch | Broken, wire on ground | 15-0023373 | OH | Sus | 31145000 | No | 2015 | MAR | Yes | Multi-Fault | 99176028 | SW | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | SONOMA-1104 | 42721104 | OTHER |  | 20150403 | 1049 | 1212170 | 361 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 1444 | 38.313 | -122.548 | 5251 GROVE ST | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0024096 | OH | Sus | 31145642 | No | 2015 | APR | Yes | Line to Ground | 99175514 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 2473 | 20150412 | 2214 | 1218282 | 479 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 20597 | 38.7103 | -122.9249 | 1 SPAN SS OF FUCO 2913 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0026120 | OH | Sus | 31147704 | No | 2015 | APR | Yes | Line to Ground | 99173927 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | RINCON-1103 | 43321103 | OCB | OCB | 20150418 | 704 | 1221215 | 234 | Distribution Circuit | Animal | Bird found | 1460 | 109235 | 38.4898 | -122.6661 | ON MAIN LINE at TAP 13417 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0027563 | OH | Sus | 42371070 | No | 2015 | APR | Yes |  | 99173027 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2225 | 20150425 | 2040 | 1225104 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 34152 | 38.524 | -122.6538 | 3133 CALISTOGA RD/TREE DOWN. 5444 GATES RD/WIRE DOWN | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0029600 | OH | Sus | 42373980 | yes | 2015 | APR | Yes | None | 99171760 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 37326 | 20150426 | 1555 | 1225332 | 1140 | Distribution Circuit | Equipment Failure/Involved | Other | 51 | 36474 | 38.5345 | -123.2752 | RISER FUCO 4427 at HWY 1- TIMBER COVE INN | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0029659 | OH | Sus | 31150967 | No | 2015 | APR | Yes | Line to Line | 99171599 | PW | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1102 | 42821102 | FUSE | 809 | 20150501 | 1021 | 1227910 | 384 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 6912 | 38.883 | -123.0464 | 2 SPANS SS OF FUCO 943 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0031116 | OH | Sus | 0 | No | 2015 | MAY | Yes | Line to Line | 99170802 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 208 | 20150518 | 1424 | 1236445 | 812 | Distribution Circuit | 3rd Party | Vehicle | 181 | 26401 | 38.2262 | -122.7215 | 217759521622 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0035007 | OH | Sus | 31155724 | No | 2015 | MAY | Yes | Multi-Fault | 99167997 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 2993 | 20150521 | 923 | 1237891 | 377 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 2850 | 38.5974 | -122.9924 | 4 SPANS LD SIDE OF FUCO 2993 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0035686 | OH | Sus | 42392978 | No | 2015 | MAY | Yes | Three Phase Fault | 99167511 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 636 | 20150528 | 2035 | 1240813 | 483 | Distribution Circuit | Animal | Bird found | 138 | 21067 | 38.2617 | -122.7158 | 217871421872 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0037114 | OH | Sus | 42397041 | No | 2015 | MAY | Yes | Line to Ground | 99166597 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 769 | 20150530 | 1401 | 1241409 | 637 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 21126 | 38.5963 | -122.9143 | 4100 WALLACE CREEK | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0037418 | OH | Sus | 31158191 | No | 2015 | MAY | Yes | Line to Line | 99166389 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24918 | 20150609 | 2324 | 1248093 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 183 | 58560 | 38.5912 | -122.92 | 3721 MILL CREEK RD | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0039901 | OH | Sus | 42402702 | yes | 2015 | JUN | Yes | Line to Ground | 99164537 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 1027 | 20150611 | 1239 | 1249301 | 261 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 3132 | 38.4853 | -122.9766 | 12022 MAYS CANYON RD- GUERNEVILLE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0040452 | OH | Sus | 0 | No | 2015 | JUN | Yes | Line to Line | 99164110 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 7347 | 20150611 | 2031 | 1249521 | 861 | Distribution Circuit | Vegetation | Tree - fell into line | 68 | 11029 | 38.5034 | -122.9483 | 9048 GILROY AVE- GUERNEVILLE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0040526 | OH | Sus | 31160881 | No | 2015 | JUN | Yes | Line to Ground | 99164032 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 1071 | 20150618 | 2111 | 1253084 | 530 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3710 | 38.474 | -122.9173 | GUERNEVILLE HWY. W/O MARTINELLI | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0042011 | OH | Sus | 0 | No | 2015 | JUN | Yes | None | 99162964 | CO | OH | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 883 | 20150701 | 314 | 1260032 | 417 | Distribution Circuit | Vegetation | Tree - branch fell on line | 242 | 43197 | 38.4075 | -122.9482 | 16353 COLEMAN VALLEY RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0044459 | OH | Sus | 42417951 | yes | 2015 | JUL | Yes | Line to Ground | 1143121 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | OTHER | 104 | 20150707 | 1138 | 1264287 | 465 | Distribution Circuit | Vegetation | Tree - fell into line | 1483 | 118832 | 38.403 | -122.9202 | Mainline at FUCO 547669 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0046003 | OH | Sus | 0 | yes | 2015 | JUL | Yes | Line to Ground | 1144201 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | RECLOSER | 132 | 20150709 | 1410 | 1265752 | 88 | Distribution Circuit | Company Initiated | Improper Construction | 1087 | 47330 | 38.2648 | -122.8054 | MAINLINE at CORNER OF HWY 1 AND DILLION BEARCH RD- TOMALES | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0046629 | OH | Sus | 0 | yes | 2015 | JUL | Yes | Line to Ground | 1144632 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 891 | 20150810 | 1054 | 1285897 | 280 | Distribution Circuit | Vegetation | Tree - branch fell on line | 94 | 12735 | 38.39 | -122.8849 | 1095 FURLONG | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0054064 | OH | Sus | 42448434 | No | 2015 | AUG | Yes | Line to Line | 1150037 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 15413 | 20150810 | 1531 | 1286096 | 325 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 7800 | 38.422 | -122.9546 | 2 SPANS LD SIDE OF FUCO 15413 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0054166 | OH | Sus | 31175090 | No | 2015 | AUG | Yes | Line to Line | 1150077 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | RINCON-1104 | 43321104 | OCB | OCB | 20150811 | 1806 | 1286842 | 465 | Distribution Circuit | 3rd Party | Metallic Balloon | 5025 | 237242 | 38.4897 | -122.6663 | ACROSS FROM 775 BENICIA DR- SANTA ROSA | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0054408 | OH | Sus | 42449408 | No | 2015 | AUG | Yes | Line to Line | 1150276 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | FUSE | 3287 | 20150822 | 1453 | 1293015 | 342 | Distribution Circuit | Vegetation | Tree - fell into line | 144 | 34819 | 38.3383 | -122.7857 | BLANK at CANFIELD SOURCE SIDE OF 8459 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0056747 | OH | Sus | 42455991 | No | 2015 | AUG | Yes | Line to Ground | 1151898 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 3539 | 20150829 | 330 | 1296568 | 628 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 4780 | 38.6225 | -122.8281 | Kikuchi/1512: Dirt road across from 3204 Rio Lindo Ave- Healdsburg | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0058127 | OH | Sus | 0 | yes | 2015 | AUG | Yes | Line to Line | 1152830 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 5152 | 20150829 | 1001 | 1296714 | 628 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 10048 | 38.5501 | -122.6677 | Galea/3472: 4300 PORTER CREEK RD | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0058169 | OH | Sus | 42460215 | yes | 2015 | AUG | Yes | Line to Ground | 1152875 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | OCB | OCB | 20150830 | 1204 | 1297212 | 821 | Distribution Circuit | Vegetation | Tree - fell into line | 3894 | 697525 | 38.4715 | -123.012 | at IFO MTR # 1007660861 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0058256 | OH | Sus | 31180476 | No | 2015 | AUG | Yes | Line to Line | 1152967 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 13539 | 20150903 | 927 | 1299525 | 527 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1 | 527 | 38.5544 | -123.2565 | LD SIDE 13539 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0059084 | OH | Sus | 42464338 | No | 2015 | SEP | Yes | Line to Ground | 1153630 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4367 | 20150916 | 2333 | 1307291 | 768 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 14592 | 38.5488 | -123.2445 | 2SP LD SIDE OF FUCO 4367 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0061833 | OH | Sus | 42476029 | No | 2015 | SEP | Yes | Line to Ground | 1155548 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1101 | 42091101 | SWITCH | 83201 | 20150919 | 951 | 1308511 | 244 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 488 | 38.4755 | -122.9069 | W/SI MARTINELLI RD- 575' N/OF HWY 116- FORESTVILLE | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0062267 | OH | Sus | 31185691 | No | 2015 | SEP | Yes | Line to Ground | 1155888 | CSO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 18699 | 20150923 | 312 | 1310592 | 408 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 8160 | 38.3772 | -122.8783 | 1580 W. SEXTON RD. | Clear-32-90 F | Conductor, Overhead | On Ground | 15-0062822 | OH | Sus | 42481758 | No | 2015 | SEP | Yes | Line to Line | 1156340 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 636 | 20150929 | 1000 | 1313655 | 432 | Distribution Circuit | Equipment Failure/Involved | Overhead | 140 | 24995 | 38.2618 | -122.7159 | Moore/3612: 1 SPAN SOURCE SIDE 12227 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0066317 | OH | Sus | 42485682 | No | 2015 | SEP | Yes | Line to Ground | 1159441 | CSO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 1249 | 20151010 | 1028 | 1319876 | 412 | Distribution Circuit | Equipment Failure/Involved | Overhead | 185 | 33716 | 38.3784 | -122.5531 | 5597 ENTERPRISE RD. GLENN ELLEN | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0069404 | OH | Sus | 42496112 | No | 2015 | OCT | Yes | Line to Ground | 1161650 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1101 | 42091101 | FUSE | 6499 | 20151124 | 1343 | 1348015 | 427 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 4456 | 38.468 | -122.9085 | SS OF METER 1007221596 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0080625 | OH | Sus | 0 | yes | 2015 | NOV | Yes | Line to Ground | 1170573 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MONTE RIO-1111 | 42811111 | FUSE | 90489 | 20151203 | 921 | 1352514 | 369 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1107 | 38.4174 | -123.0986 | 6 & 7 SPANS LINE SIDE OF 4147 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | On Ground | 15-0082437 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1172142 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 797 | 20151205 | 1841 | 1354448 | 477 | Distribution Circuit | 3rd Party | Vehicle | 12 | 5724 | 38.5035 | -122.9002 | MT. JACKSON AND WESTSIDE | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 15-0082966 | OH | Sus | 0 | No | 2015 | DEC | Yes | Three Phase Fault | 1172565 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 9797 | 20151206 | 249 | 1354552 | 600 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 12600 | 38.4152 | -122.9003 | INGRAM- JEFF/4: 2172 GREEN HILL RD | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083010 | OH | Sus | 42583658 | No | 2015 | DEC | Yes | Three Phase Fault | 1172611 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 11987 | 20151206 | 850 | 1354623 | 435 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 2433 | 38.4295 | -122.9384 | 4083 HEATHER LANE | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083029 | OH | Sus | 42583741 | No | 2015 | DEC | Yes | Force Out | 1172641 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4947 | 20151207 | 1742 | 1355339 | 576 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 31680 | 38.5577 | -123.0969 | 21855 KING RIDGE RD- 1.8 MILES LD SIDE OF FUCO 4947 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083289 | OH | Sus | 42584980 | No | 2015 | DEC | Yes | Line to Ground | 1172893 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 4619 | 20151209 | 1117 | 1356236 | 324 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2268 | 38.4867 | -123.015 | KOTULA- JOHN: 18198 Hwy 116 in front of georges hideaway traveling west bound. SSD 4619 open | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 15-0083580 | OH | Sus | 31205160 | yes | 2015 | DEC | Yes | Line to Line | 1173241 | CAW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1101 | 43071101 | FUSE | 4817 | 20151210 | 1952 | 1358235 | 691 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 13523 | 38.4 | -122.5697 | SS OF 2577 KEISER RD- KENWOOD/METER #1009577321 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0084100 | OH | Sus | 31205457 | yes | 2015 | DEC | Yes | Line to Ground | 1173713 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 15463 | 20151210 | 750 | 1357328 | 330 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3300 | 38.4707 | -122.95 | 14200 GREEN VALLEY RD | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083865 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1173502 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1101 | 42091101 | SWITCH | 83201 | 20151210 | 1245 | 1357716 | 210 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 420 | 38.4756 | -122.9069 | Moore/3612: 7525 HWY 116 CANYON ROCK CO. | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083987 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1173620 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 11973 | 20151210 | 444 | 1357033 | 511 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 3066 | 38.3921 | -122.922 | 3 SPANS LOAD SIDE OF 11973 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083885 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1173528 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 547669 | 20151210 | 502 | 1357055 | 786 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4716 | 38.411 | -122.9442 | 3 SPAND LD SIDE OF 547669 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083957 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1173598 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 15401 | 20151210 | 347 | 1356994 | 543 | Distribution Circuit | Vegetation | Tree - branch fell on line | 103 | 55929 | 38.4246 | -122.9613 | 121 RAILROAD AVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083792 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1173432 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 3970 | 20151210 | 353 | 1356967 | 422 | Distribution Circuit | Vegetation | Tree - fell into line | 2570 | 205045 | 38.4997 | -123.0054 | Nott/3569: RIVER RD AT ARMSTRONGS WOOD RD | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083763 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1173403 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1101 | 42091101 | FUSE | 6485 | 20151220 | 1810 | 1367215 | 855 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 6840 | 38.4668 | -122.9087 | 15 SPANS LD SIDE 6485 | Overcast-Rain-32-90 F | Conductor, Overhead | On Ground | 15-0086329 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Line | 1176292 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | RECLOSER | 120 | 20151221 | 1353 | 1367940 | 858 | Distribution Circuit | Vegetation | Tree - fell into line | 495 | 135232 | 38.4637 | -123.0083 | MTR# 1007253332 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 15-0086461 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1176455 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1102 | 42271102 | FUSE | 681 | 20151222 | 727 | 1368853 | 919 | Distribution Circuit | Vegetation | Tree - branch fell on line | 129 | 12283 | 38.2838 | -122.7101 | 120 JEWETT RD | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086677 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1176674 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 1795 | 20151222 | 436 | 1368717 | 1034 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 11266 | 38.3845 | -122.8737 | 1039 SEXTON RD- SEBASTOPOL | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 15-0086756 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1176774 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 547669 | 20151222 | 106 | 1368392 | 584 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3504 | 38.411 | -122.9442 | 1 SPAN LD SIDE OF FUCO 547669 | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | On Ground | 15-0086578 | OH | Sus | 42595890 | yes | 2015 | DEC | Yes | Three Phase Fault | 1176571 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 240 | 20151222 | 828 | 1369108 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 806 | 287456 | 38.4715 | -123.0471 | 1305 AUSTIN CREEK ROAD- CAZADERO | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086737 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Ground | 1176753 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 12221 | 20151222 | 526 | 1368797 | 1012 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 10120 | 38.2197 | -122.6836 | ACROSS FROM 1412 SPRING HILL RD- PETALUMA | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086725 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1176739 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | PENNGROVE-1101 | 43471101 | SWITCH | 7227 | 20151223 | 951 | 1370123 | 253 | Distribution Circuit | Equipment Failure/Involved | Overhead | 38 | 9614 | 38.3477 | -122.6091 | 5125 LICHAU RD IN PENNGROVE | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0086939 | OH | Sus | 42596848 | No | 2015 | DEC | Yes | None | 1176997 | CSO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 240 | 20160105 | 2009 | 1377842 | 415 | Distribution Circuit | Vegetation | Tree - fell into line | 806 | 220911 | 38.4715 | -123.0471 | Moore/3612: 1 SPAN LOAD SIDE LR23916/ WIRE AQLSO WRAPPED AT 1305 AUSTIN CREEK | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003212 | OH | Sus | 42601530 | yes | 2016 | JAN | Yes | Three Phase Fault | 1178827 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | FUSE | 2931 | 20160106 | 1522 | 1378772 | 402 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 6366 | 38.5087 | -122.7511 | Rendon/4754: 5083 KNOLLWOOD CT | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003562 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1179073 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | OTHER | WIRE DOWN 2 SPANS SOURCE SIDE OF 6493 | 20160106 | 1649 | 1378962 | 206 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1134 | 38.5172 | -122.9579 | 2 SPANS SOURCE SIDE OF 6493 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003606 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Force Out | 1179098 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 2379 | 20160114 | 1606 | 1383923 | 910 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 11368 | 38.5019 | -122.9306 | 11184 TAERRACE DR | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0005452 | OH | Sus | 0 | No | 2016 | JAN | Yes | Line to Ground | 1180538 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 2443 | 20160117 | 2200 | 1385789 | 828 | Distribution Circuit | Vegetation | Tree - branch fell on line | 10 | 8280 | 38.1938 | -122.911 | 2 SPANS LOAD SIDE OF 2443 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0005980 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1180946 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 6751 | 20160117 | 1428 | 1385553 | 488 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 63928 | 38.592 | -122.9622 | 7188 & 7230 MILL CREEK RD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0005913 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1180885 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FULTON-1102 | 42561102 | FUSE | 751 | 20160117 | 951 | 1385401 | 789 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 33 | 6135 | 38.6311 | -122.77 | 905 MAACAME LANE- HEALDSBURG | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on object | 16-0005878 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1180850 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 15379 | 20160118 | 322 | 1385873 | 666 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3330 | 38.4487 | -123.0017 | 3 SPANS LOAD SIDE OF 15379 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006001 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1180969 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 15399 | 20160118 | 1901 | 1386567 | 819 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 43407 | 38.4247 | -122.9608 | 66 RAILROAD | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006136 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1181093 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | SONOMA-1105 | 42721105 | FUSE | 6547 | 20160118 | 709 | 1385952 | 637 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 12103 | 38.3068 | -122.4103 | 3200 CASTLE RD | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006034 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1181003 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 4895 | 20160119 | 1338 | 1387710 | 256 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 38912 | 38.4116 | -122.9752 | COLEMAN VLY W/JOY RD TWD FUCO 1525 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006516 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1181357 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 3891 | 20160123 | 629 | 1390584 | 331 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 10261 | 38.5162 | -123.0644 | 16020 E AUSTIN CREEK RD/APPROX 3 SPANS LD SIDE OF FUCO 3891 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007713 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1182207 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 6113 | 20160123 | 104 | 1390492 | 506 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 43277 | 38.5381 | -122.6468 | 3133 CALISTOGA RD- SANTA ROSA | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007675 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1182164 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 14983 | 20160123 | 841 | 1390617 | 431 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 862 | 38.5553 | -122.6649 | 2 SPANS LD SIDE OF FUCO 14983 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007725 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1182223 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4553 | 20160124 | 1114 | 1391200 | 466 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 466 | 38.5528 | -123.2733 | LAST SPAN PAST FUCO 4553 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007860 | OH | Sus | 0 | No | 2016 | JAN | Yes | Line to Ground | 1182369 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | OTHER | WIRE DOWN 1P/N/OF FUCO 6927 | 20160125 | 118 | 1391435 | 385 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 11038 | 38.5977 | -122.9984 | 1P/N/OF FUCO 6927 ON MAINLINE | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0007917 | OH | Sus | 42616571 | No | 2016 | JAN | Yes | Line to Ground | 1182425 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 7951 | 20160129 | 1207 | 1394069 | 263 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 4471 | 38.4566 | -122.9364 | 13431 GREEN VLY RD. SEBASTOPOL | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | On Ground | 16-0009153 | OH | Sus | 0 | No | 2016 | JAN | Yes | Three Phase Fault | 1183270 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 3447 | 20160129 | 1235 | 1394058 | 332 | Distribution Circuit | Vegetation | Tree - branch fell on line | 16 | 5312 | 38.5157 | -122.6297 | 6501 ERLAND RD- ST HELENA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009180 | OH | Sus | 42620120 | No | 2016 | JAN | Yes | Line to Line | 1183279 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 296 | 20160201 | 2303 | 1396777 | 442 | Distribution Circuit | 3rd Party | Vehicle | 120 | 28631 | 38.2075 | -122.6755 | 2710 CHILENO VALLEY | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0009953 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1183940 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1101 | 43071101 | FUSE | 180929 | 20160208 | 1714 | 1400475 | 265 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 1146 | 38.4185 | -122.5745 | 1187 LAWNDALE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0011433 | OH | Sus | 0 | No | 2016 | FEB | Yes | Line to Ground | 1184990 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | RECLOSER | 568 | 20160306 | 1157 | 1422024 | 476 | Distribution Circuit | Vegetation | Tree - branch fell on line | 733 | 76299 | 38.5031 | -122.7355 | S/OF SW 3557 TWD FUCO 1199 & LR 5152 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018436 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190273 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 12417 | 20160306 | 655 | 1421259 | 414 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 5382 | 38.4222 | -122.919 | 12754 DUPONT RD | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018311 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190169 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1137 | 20160306 | 2314 | 1422900 | 706 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 59304 | 38.5271 | -123.0006 | 17200 SWEETWATER SPRINGS RD | Overcast-Fog-Heavy Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018615 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Three Phase Fault | 1190459 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | OLEMA-1101 | 42291101 | FUSE | 15735 | 20160306 | 211 | 1420704 | 961 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 6727 | 38.1609 | -122.8931 | Deignan/3571: 15735 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018153 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190024 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 5659 | 20160309 | 1219 | 1425863 | 825 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 11550 | 38.3834 | -122.8918 | SILALA LN X-St.: BODEGA WY- LD SIDE C/OUTS 5659 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0019652 | OH | Sus | 0 | No | 2016 | MAR | Yes | Line to Line | 1191315 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 4125 | 20160310 | 1345 | 1426579 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3032 | 38.1881 | -122.9128 | #22555 HWY #1 1750' N/CLARK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020033 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1191568 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | RECLOSER | 79140 | 20160310 | 2157 | 1426938 | 275 | Distribution Circuit | Vegetation | Tree - branch fell on line | 344 | 49626 | 38.2826 | -122.7557 | HESSONG- Ryan: PEPPER RD AT C/O18477 TWD 18431 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020172 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1191687 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | JUMPER | WIRE DOWN 11366 SUMMER HOME PARK RD | 20160310 | 943 | 1426392 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 182 | 4556 | 38.4999 | -122.9349 | 11366 SUMMER HOME PARK RD | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0019955 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1191539 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 3053 | 20160310 | 1042 | 1426456 | 783 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 82998 | 38.4189 | -122.9304 | 13383 DUPONT RD. | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0019915 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1191524 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 7237 | 20160311 | 1413 | 1428018 | 520 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3640 | 38.5615 | -123.2694 | Arvig/3970: near 31397 Sea View rd (Browns Mill) cazadero | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020554 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1191933 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | JUMPER | OJ PAST MTR 1007800536 | 20160311 | 100 | 1427025 | 385 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 385 | 38.5117 | -122.9172 | SAME | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020188 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Open Circuit | 1191711 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 2021 | 20160311 | 524 | 1427074 | 714 | Distribution Circuit | Vegetation | Tree - fell into line | 182 | 129948 | 38.5031 | -122.9366 | 11800 SUMMERHOME PARK RD IN FORESTVILLE | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0020193 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1191717 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 79306 | 20160311 | 1045 | 1427976 | 891 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 48726 | 38.3722 | -122.9117 | 1100 VALLEY FORD FREESTONE RD- VALLEY FORD | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020455 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1191862 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4537 | 20160313 | 1003 | 1430058 | 630 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6300 | 38.5247 | -123.2648 | INGRAM- JEFF/4: 5 SPANS S/O C/O'S 4537 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020937 | OH | Sus | 42655921 | yes | 2016 | MAR | Yes | Line to Line | 1192315 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1039 | 20160313 | 1343 | 1430249 | 409 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 42934 | 38.5035 | -122.9973 | 14180 WOODLAND DRIVE- GUERNEVILLE | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020962 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1192339 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 15599 | 20160313 | 2122 | 1430654 | 494 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 12350 | 38.5123 | -122.9847 | 15525 ORCHARD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0021102 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1192468 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 6435 | 20160313 | 928 | 1430003 | 668 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 16700 | 38.4968 | -122.644 | 6105 CLELAND RANCH RD | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0020914 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1192296 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 15399 | 20160328 | 1656 | 1440292 | 234 | Distribution Circuit | Vegetation | Tree - branch fell on line | 53 | 12402 | 38.4247 | -122.9608 | 5/S/LD/SIDE OF 15399 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0024574 | OH | Sus | 42664323 | yes | 2016 | MAR | Yes | None | 1195036 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | SWITCH | 12427 | 20160403 | 1201 | 1443616 | 441 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 3528 | 38.671 | -123.1947 | 22303 SKAGGS SPRINGS RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0025794 | OH | Sus | 31228811 | No | 2016 | APR | Yes | Line to Ground | 1195948 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | RINCON-1103 | 43321103 | OCB | 1103/2 | 20160418 | 717 | 1452707 | 562 | Distribution Circuit | 3rd Party | Vehicle | 1462 | 173257 | 38.4901 | -122.6661 | 1 SPAN LD SIDE OF SW 9579 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0029277 | OH | Sus | 31232106 | No | 2016 | APR | Yes | Line to Ground | 1198457 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 6435 | 20160422 | 1558 | 1456062 | 1150 | Distribution Circuit | Vegetation | Tree - branch fell on line | 25 | 28750 | 38.4968 | -122.644 | NOONAN- TODD: 6923 PLUM RANCH RD & 2 SPANS E/OF 10635 | Overcast-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0030788 | OH | Sus | 42684361 | yes | 2016 | APR | Yes | Line to Line | 1199439 | CSO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | RECLOSER | 132 | 20160423 | 817 | 1456576 | 397 | Distribution Circuit | Animal | Bird found | 1014 | 170386 | 38.2647 | -122.8057 | 1 SPAN SS OF 3415 TAP | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0030911 | OH | Sus | 42684529 | No | 2016 | APR | Yes | Line to Ground | 1199570 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 296 | 20160424 | 1710 | 1457268 | 958 | Distribution Circuit | Vegetation | Tree - fell into line | 120 | 23494 | 38.2075 | -122.6755 | 2 SPANS WIRE DOWN 3/S/LOADSIDE OF 86027 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0031057 | OH | Sus | 0 | yes | 2016 | APR | Yes | Line to Ground | 1199735 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 5152 | 20160426 | 415 | 1459092 | 535 | Distribution Circuit | 3rd Party | Vehicle | 16 | 8560 | 38.5499 | -122.6678 | 14983 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0031524 | OH | Sus | 0 | No | 2016 | APR | Yes | Multi-Fault | 1200132 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 2579 | 20160508 | 1318 | 1466690 | 285 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 3135 | 38.4982 | -123.0732 | 1/S/LS OF 2579 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0034717 | OH | Sus | 31237250 | No | 2016 | MAY | Yes | Line to Ground | 1202571 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 568 | 20160517 | 551 | 1470929 | 363 | Distribution Circuit | Equipment Failure/Involved | Overhead | 173 | 38112 | 38.5173 | -122.655 | 1 SPAN SOURCE SIDE OF CAP 476 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0036406 | OH | Sus | 42702653 | No | 2016 | MAY | Yes | Line to Line | 1203750 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1111 | 42751111 | FUSE | 14897 | 20160518 | 1906 | 1472332 | 464 | Distribution Circuit | 3rd Party | Vehicle | 81 | 37584 | 38.5628 | -122.8039 | 2 SS/OF C/OUT 2369 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0036898 | OH | Sus | 0 | yes | 2016 | MAY | Yes | Line to Line | 1204111 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 634 | 20160521 | 351 | 1474144 | 504 | Distribution Circuit | Animal | Bird found | 48 | 14367 | 38.2982 | -122.8208 | ON MAINLINE 1ST SPAN LD SIDE OF 4021 TWD 3443 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0037553 | OH | Sus | 42705139 | No | 2016 | MAY | Yes | Line to Ground | 1204591 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 779 | 20160526 | 1627 | 1477734 | 547 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 24615 | 38.5971 | -122.9894 | MTR 1009801204 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0038825 | OH | Sus | 42707773 | No | 2016 | MAY | Yes | Line to Ground | 1205542 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | SONOMA-1103 | 42721103 | FUSE | 99309 | 20160527 | 934 | 1478008 | 292 | Distribution Circuit | Vegetation | Tree - branch fell on line | 18 | 5256 | 38.3269 | -122.4321 | 16250 NORRBOM RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0038926 | OH | Sus | 31242578 | No | 2016 | MAY | Yes | Line to Ground | 1205637 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 10183 | 20160601 | 1055 | 1480679 | 309 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 5187 | 38.5162 | -123.0644 | 17200 OLD CAZADERO RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0040206 | OH | Sus | 31243315 | yes | 2016 | JUN | Yes | Line to Ground | 1206726 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 7389 | 20160604 | 2255 | 1483125 | 788 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 7220 | 38.5126 | -122.9338 | MTR# 5000013614 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0041119 | OH | Sus | 42712443 | No | 2016 | JUN | Yes | Line to Ground | 1207383 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 17907 | 20160606 | 1840 | 1484222 | 504 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 18144 | 38.5033 | -123.029 | at MTR#1007381472 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0041490 | OH | Sus | 42713338 | No | 2016 | JUN | Yes | Line to Line | 1207668 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 4661 | 20160620 | 1738 | 1492891 | 390 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 17160 | 38.5078 | -122.9895 | 1 SPAN LD SIDE FU 4661 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0044585 | OH | Sus | 42728520 | No | 2016 | JUN | Yes | Line to Ground | 1210012 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 678 | 20160622 | 1357 | 1494104 | 854 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 20405 | 38.4949 | -123.0109 | 17665 OLD MONTE RIO RD- MONTE RIO | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0045109 | OH | Sus | 0 | No | 2016 | JUN | Yes | Three Phase Fault | 1210404 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 6049 | 20160701 | 2206 | 1499856 | 1143 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5563 | 38.5986 | -122.912 | 2737 WALLACE CREEK RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0047531 | OH | Sus | 0 | yes | 2016 | JUL | Yes | Line to Ground | 1212079 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6233 | 20160705 | 1431 | 1501329 | 230 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 2990 | 38.4471 | -122.9241 | 5700 HARRISON GRADE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0047930 | OH | Sus | 42736035 | No | 2016 | JUL | Yes | Line to Ground | 1212448 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | SONOMA-1104 | 42721104 | FUSE | 14345 | 20160708 | 1858 | 1503063 | 237 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 8295 | 38.3096 | -122.5507 | 7199 GROVE ST | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0048730 | OH | Sus | 42737857 | No | 2016 | JUL | Yes | Line to Line | 1212960 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 5152 | 20160710 | 301 | 1507675 | 624 | Distribution Circuit | 3rd Party | Vehicle | 16 | 9984 | 38.5499 | -122.6678 | 1/P/E/OF 15033 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0048852 | OH | Sus | 0 | No | 2016 | JUL | Yes | Line to Ground | 1213086 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 4661 | 20160712 | 1829 | 1509095 | 239 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 10516 | 38.5078 | -122.9895 | 15462 OLD RIVER RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0049450 | OH | Sus | 42740427 | No | 2016 | JUL | Yes | Line to Ground | 1213531 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 1701 | 20160714 | 200 | 1509723 | 681 | Distribution Circuit | 3rd Party | Vehicle | 64 | 43584 | 38.4728 | -123.0474 | OPPOSITE 485 CAZADERO HWY 510' N/ OLD DUNCANS RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0049715 | OH | Sus | 0 | yes | 2016 | JUL | Yes | Line to Ground | 1213755 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1109 | 42631109 | FUSE | 2637 | 20160715 | 1426 | 1510786 | 379 | Distribution Circuit | 3rd Party | Vehicle | 2 | 758 | 38.1366 | -122.7092 | 2ND POLE FROM EOL | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0050269 | OH | Sus | 0 | No | 2016 | JUL | Yes | Line to Line | 1214098 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 346 | 20160729 | 1754 | 1518682 | 604 | Distribution Circuit | 3rd Party | Vehicle | 516 | 311664 | 38.5044 | -122.9975 | 6 SPANS LOAD SIDE OF 346 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0053719 | OH | Sus | 0 | No | 2016 | JUL | Yes | Line to Line | 1216451 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 53477 | 20160815 | 1059 | 1526643 | 253 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 57 | 14421 | 38.4961 | -123.0693 | 1/s/ls/of 53477 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0057361 | OH | Sus | 42769536 | No | 2016 | AUG | Yes | Line to Ground | 1218957 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 448 | 20160829 | 1515 | 1533933 | 398 | Distribution Circuit | 3rd Party | Vehicle | 1304 | 209922 | 38.3443 | -122.5145 | ARNOLD DR & MADRONE | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 16-0060832 | OH | Sus | 42778024 | No | 2016 | AUG | Yes | Line to Ground | 1221285 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1137 | 20160903 | 1427 | 1536369 | 298 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 25330 | 38.5271 | -123.0006 | 1 SPAN LD SIDE OF 8629 ON MAINLINE- 17990 SWEETWATER SPRINGS RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0062256 | OH | Sus | 31269039 | No | 2016 | SEP | Yes | Three Phase Fault | 1222192 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 2957 | 20160907 | 1938 | 1538072 | 1323 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 12246 | 38.5857 | -123.1193 | MTR 1009322806 | Clear-32-90 F | Conductor, Overhead | On Ground | 16-0063040 | OH | Sus | 0 | No | 2016 | SEP | Yes | Line to Line | 1222713 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 429 | 20160908 | 1545 | 1538573 | 260 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 65 | 9110 | 38.4734 | -123.0226 | 21760 MOSCOW RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0063305 | OH | Sus | 42783228 | No | 2016 | SEP | Yes | Line to Ground | 1222879 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 12055 | 20160921 | 1504 | 1545540 | 623 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 6 | 3738 | 38.4814 | -123.0073 | 1 SPAN LD SIDE OF 12055 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0066352 | OH | Sus | 42795809 | No | 2016 | SEP | Yes | Line to Line | 1225002 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 1795 | 20160927 | 2118 | 1548978 | 567 | Distribution Circuit | 3rd Party | Vehicle | 20 | 3914 | 38.3845 | -122.8737 | 1000 SEXTON RD & 2 POLES N/OF 1000 SEXTON RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0067997 | OH | Sus | 0 | yes | 2016 | SEP | Yes | Line to Line | 1226161 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | OTHER | WIRE DOWN | 20161001 | 2016 | 1551103 | 615 | Distribution Circuit | Equipment Failure/Involved | Overhead | 387 | 67753 | 38.3653 | -123.0707 | 2 SPANS FROM 2331 TWD 3209 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0068958 | OH | Sus | 31274580 | No | 2016 | OCT | Yes | Line to Ground | 1226865 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1997 | 20161003 | 1607 | 1552281 | 287 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 31570 | 38.502 | -123.0239 | 1ST SPAN LD SIDE OF 17907 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0069403 | OH | Sus | 42804083 | No | 2016 | OCT | Yes | Line to Ground | 1227196 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1101 | 42091101 | JUMPER | 83201 | 20161010 | 1006 | 1555749 | 336 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 672 | 38.4756 | -122.9069 | 2/S/LS/OF 83201 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0070811 | OH | Sus | 42810893 | No | 2016 | OCT | Yes | Line to Ground | 1228322 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | JUMPER | WIRE DOWN N/O OF 14699 | 20161013 | 814 | 1557414 | 359 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 17345 | 38.7253 | -122.9788 | N/O 14699 R C/O | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0071588 | OH | Sus | 42813657 | yes | 2016 | OCT | Yes | Line to Ground | 1228848 | CSO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | JUMPER | WIRE DOWN | 20161024 | 1533 | 1569068 | 712 | Distribution Circuit | Equipment Failure/Involved | Overhead | 178 | 17821 | 38.4096 | -123.0952 | 3 SPANS LD SIDE OF 4483 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0075184 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1231753 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1103 | 43071103 | FUSE | 13333 | 20161026 | 1549 | 1570398 | 396 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4752 | 38.3738 | -122.5176 | REAR OF 12850 DUNBAR RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0075743 | OH | Sus | 31280701 | No | 2016 | OCT | Yes | Line to Ground | 1232157 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 1593 | 20161027 | 2252 | 1571263 | 523 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2052 | 38.4742 | -122.9221 | 8651 HWY 116 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076173 | OH | Sus | 42868812 | yes | 2016 | OCT | Yes | Line to Ground | 1232444 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4613 | 20161029 | 913 | 1572501 | 807 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 807 | 38.5617 | -123.3113 | 23500 HWY 1 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076651 | OH | Sus | 42869439 | No | 2016 | OCT | Yes | Force Out | 1232755 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | OTHER | WIRE DOWN | 20161029 | 1048 | 1572622 | 450 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1494 | 61918 | 38.4112 | -122.9556 | 15301/15290 COLEMAN VALLEY RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0076655 | OH | Sus | 0 | No | 2016 | OCT | Yes | Line to Ground | 1232759 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1102 | 42891102 | FUSE | 8049 | 20161031 | 1952 | 1574691 | 248 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 4960 | 38.6945 | -122.8913 | 20261 GEYSERVILLE AVE | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0077275 | OH | Sus | 0 | No | 2016 | OCT | Yes | Line to Ground | 1233327 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 134 | 20161101 | 1247 | 1574727 | 780 | Distribution Circuit | Vegetation | Tree - fell into line | 232 | 73827 | 38.5588 | -123.2702 | 14/S/LS OF N/O SW 4535 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0077348 | OH | Sus | 31281760 | No | 2016 | NOV | Yes | Line to Line | 1233361 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 64758 | 20161102 | 1530 | 1575463 | 845 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 140586 | 38.5089 | -123.0696 | at FUCO 44785 ON THE MAINLINE- 6125 CAZADERO HWY | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0077631 | OH | Sus | 0 | No | 2016 | NOV | Yes | Line to Ground | 1233567 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | FUSE | 2295 | 20161112 | 431 | 1579950 | 559 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 21801 | 38.5501 | -122.7188 | 2639 LESLIE RD | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0079424 | OH | Sus | 42879108 | No | 2016 | NOV | Yes | Line to Line | 1234887 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | RECLOSER | 37368 | 20161116 | 2231 | 1582585 | 499 | Distribution Circuit | Vegetation | Tree - fell into line | 177 | 15523 | 38.3809 | -123.079 | Noonan- Todd/3469: 6700 HWY 1 BODEGA BAY | Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0080377 | OH | Sus | 42881642 | No | 2016 | NOV | Yes | Line to Ground | 1235648 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | RECLOSER | 322 | 20161119 | 1852 | 1585328 | 565 | Distribution Circuit | 3rd Party | Vehicle | 377 | 88784 | 38.3868 | -122.8901 | C/OUT POLE 5659 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0081167 | OH | Sus | 0 | yes | 2016 | NOV | Yes | Multi-Fault | 1236183 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | JUMPER | 1 OF 3 HOT WIRES DOWN | 20161119 | 935 | 1584933 | 301 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2741 | 66989 | 38.4988 | -122.972 | 4 SPANS FROM 12683 TWD 1073 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0081076 | OH | Sus | 0 | yes | 2016 | NOV | Yes | Line to Ground | 1236113 | CSO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6229 | 20161120 | 148 | 1585467 | 932 | Distribution Circuit | Equipment Failure/Involved | Overhead | 35 | 23950 | 38.4585 | -122.9351 | Kikuchi/1512: c/o 15477 - Green Valley Rd- Sebastopol | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081204 | OH | Sus | 0 | yes | 2016 | NOV | Yes | Line to Line | 1236227 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | JUMPER | WIRE DOWN 2 SPANS LD SIDE OF 13823 | 20161121 | 1348 | 1586648 | 307 | Distribution Circuit | Vegetation | Tree - branch fell on line | 38 | 11410 | 38.4736 | -123.0241 | ALVAREZ- RAFAEL: 21892 MOSCOW RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081495 | OH | Sus | 42883298 | No | 2016 | NOV | Yes | Line to Ground | 1236482 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | GUALALA-1111 | 42841111 | FUSE | 8493 | 20161122 | 859 | 1587029 | 361 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 2623 | 38.5329 | -123.2714 | 20801 HWY 1 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081633 | OH | Sus | 0 | No | 2016 | NOV | Yes | Line to Ground | 1236596 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 5152 | 20161202 | 156 | 1593130 | 455 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 7280 | 38.5499 | -122.6678 | Kikuchi/1512: 4300 Porter Creek Rd- Santa Rosa | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0083522 | OH | Sus | 42887893 | No | 2016 | DEC | Yes | Line to Ground | 1238092 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | JUMPER | WIRE DOWN 3 P/LD SIDE OF 6121 | 20161202 | 1044 | 1593509 | 396 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 5544 | 38.5401 | -122.6374 | 3 P/LD SIDE OF 6121 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0083625 | OH | Sus | 42888586 | No | 2016 | DEC | Yes | Line to Ground | 1238195 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 6399 | 20161207 | 1352 | 1596214 | 868 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 26040 | 38.5038 | -122.9115 | 10385 SCENIC DRIVE- FORESTVILLE | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0084377 | OH | Sus | 42892644 | No | 2016 | DEC | Yes | Line to Line | 1238958 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 781 | 20161214 | 1508 | 1602050 | 612 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 9180 | 38.6024 | -123.0033 | 4 SPANS LD SIDE OF FUCO 781 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085594 | OH | Sus | 42899872 | No | 2016 | DEC | Yes | Line to Line | 1240245 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1101 | 43071101 | FUSE | 15877 | 20161215 | 951 | 1602551 | 514 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2056 | 38.4006 | -122.5129 | 1 SS RCO 17849 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085702 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1240374 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 881 | 20161215 | 451 | 1602263 | 452 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4068 | 38.4062 | -122.9468 | Galea/3472: 1300 - 3 SPANS LD SIDE OF 881 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085641 | OH | Sus | 42900166 | yes | 2016 | DEC | Yes | Line to Line | 1240298 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 64758 | 20161215 | 1421 | 1602882 | 999 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 95526 | 38.5089 | -123.0696 | MTR#1009321064 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0085761 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Line | 1240430 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 4837 | 20161215 | 553 | 1602283 | 497 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 25844 | 38.4804 | -122.9967 | 19526 REDWOOD DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0085652 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Ground | 1240314 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | SONOMA-1104 | 42721104 | OTHER | WIRE DOWN 8 SPANS SS OF 9369 | 20161221 | 1810 | 1608745 | 478 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 14499 | 38.3177 | -122.546 | 8 SPANS SS OF 9369 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0086656 | OH | Sus | 31291155 | No | 2016 | DEC | Yes | Line to Ground | 1241732 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 525 | 20170104 | 134 | 1617530 | 926 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 14361 | 38.4049 | -122.8963 | Galea/3472: 1488 FURLONG | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003462 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1243639 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | JUMPER | OJ TWD MTR 1005531088 | 20170104 | 1406 | 1618517 | 55 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 55 | 38.4329 | -122.9091 | TWD MTR 1005531088 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0003679 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1243764 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MONTE RIO-1111 | 42811111 | FUSE | 93113 | 20170106 | 1529 | 1620527 | 116 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 580 | 38.4526 | -123.0574 | 2/s/LD/SIDE OF 93113 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004352 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Ground | 1244184 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 134 | 20170107 | 2352 | 1622368 | 5262 | Distribution Circuit | Vegetation | Tree - fell into line | 232 | 215685 | 38.5588 | -123.2702 | MTR #1008863028 & 2 SP S/O 4535 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004888 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1244687 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 2021 | 20170107 | 112 | 1620767 | 644 | Distribution Circuit | Vegetation | Tree - fell into line | 183 | 71652 | 38.5031 | -122.9366 | 11385 SUMMER HOME PARK RD | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004515 | OH | Sus | 42913894 | yes | 2017 | JAN | Yes | Line to Line | 1244341 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1102 | 42271102 | JUMPER | OJ'S @ MTR# 1007383379 | 20170112 | 817 | 1641107 | 203 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 406 | 38.2996 | -122.6945 | SOUTH OF MTR# 1007383379 | Overcast-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 17-0008311 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Three Phase Fault | 1247740 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 5156 | 20170112 | 1837 | 1641975 | 534 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3305 | 483226 | 38.3157 | -122.7354 | 1 SPAN N/OF 10475 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0008530 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247890 | CSO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 3031 | 20170112 | 425 | 1640945 | 953 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 16201 | 38.6045 | -122.9774 | SS OF 2629 | Partly Cloudy-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008279 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247719 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 2579 | 20170112 | 851 | 1641152 | 1706 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 17060 | 38.4982 | -123.0732 | 2 SPANS SS EOL | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008389 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1247788 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 8657 | 20170112 | 1850 | 1641991 | 1443 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 7215 | 38.5197 | -123.0846 | Noonan- Todd/3469: E.O.L. BEYOND C/OS. TOP OF HILL 4800 CAZ HWY | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0008629 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1247987 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 10905 | 20170115 | 301 | 1643905 | 569 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1138 | 38.6044 | -123.0059 | MILL CREEK ROAD 5 MILES W/WEST SIDE ROAD | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0009247 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Ground | 1248518 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 5152 | 20170125 | 907 | 1666720 | 298 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 4768 | 38.5499 | -122.6678 | 3 SPANS SS OF 9707 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0014711 | OH | Sus | 42932605 | yes | 2017 | JAN | Yes | Line to Ground | 1253359 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 2241 | 20170126 | 1054 | 1667682 | 297 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 1485 | 38.2702 | -122.8563 | SS OF MTR 1009169378 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0015320 | OH | Sus | 42933147 | No | 2017 | JAN | Yes | Line to Ground | 1253879 | CSO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | OTHER | 1 OF 3 HOT WIRES DOWN AT 91611 | 20170129 | 616 | 1669776 | 346 | Distribution Circuit | Equipment Failure/Involved | Overhead | 370 | 55400 | 38.3408 | -122.7781 | MAIN LINE AT FUCO 91611 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0015882 | OH | Sus | 42934554 | No | 2017 | JAN | Yes | Line to Ground | 1254308 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 2439 | 20170202 | 827 | 1672696 | 363 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 726 | 38.2165 | -122.9231 | 3/S/LD/OF 2439 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0016849 | OH | Sus | 31303321 | No | 2017 | FEB | Yes | Line to Line | 1255054 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24550 | 20170202 | 1133 | 1672930 | 255 | Distribution Circuit | Vegetation | Tree - fell into line | 223 | 27947 | 38.5793 | -122.878 | 6 SPANS SS OF FUCO 38536 ON MAINLINE | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0016911 | OH | Sus | 42937221 | No | 2017 | FEB | Yes | Line to Ground | 1255082 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24918 | 20170203 | 437 | 1673492 | 480 | Distribution Circuit | Vegetation | Tree - fell into line | 187 | 78372 | 38.5914 | -122.92 | 1 SPAN SOURCE SIDE OF FUCO 7649 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017082 | OH | Sus | 31303546 | yes | 2017 | FEB | Yes | Line to Line | 1255178 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 4663 | 20170204 | 1001 | 1674685 | 321 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2568 | 38.4983 | -122.9937 | MTR# 1009124077 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017448 | OH | Sus | 42939006 | No | 2017 | FEB | Yes | Line to Ground | 1255406 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 134 | 20170205 | 1700 | 1675491 | 705 | Distribution Circuit | Vegetation | Tree - fell into line | 232 | 129072 | 38.5588 | -123.2702 | PHIPPS MILL CAMPGROUND/ AT FUCO 10781 ON MAINLINE | Strong Winds-Rain-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017575 | OH | Sus | 0 | No | 2017 | FEB | Yes | Three Phase Fault | 1255541 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 8003 | 20170205 | 1906 | 1675555 | 723 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 13737 | 38.4777 | -123.0237 | 2 SPANS PAST FUCO 13489 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0017589 | OH | Sus | 0 | No | 2017 | FEB | Yes | Line to Ground | 1255553 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 6063 | 20170206 | 1618 | 1676901 | 829 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 7461 | 38.5947 | -122.9154 | 1 SS OF 3907 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017987 | OH | Sus | 42939820 | yes | 2017 | FEB | Yes | Line to Ground | 1255839 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 2021 | 20170206 | 1910 | 1677043 | 68 | Distribution Circuit | Equipment Failure/Involved | Overhead | 183 | 12444 | 38.5031 | -122.9366 | 5 SPANS LD SIDE OF 2021 | Overcast-Fog-Drizzle-32-90 F | Woodpin | Broken, wire on object | 17-0017924 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Force Out | 1255776 | WP | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1101 | 42091101 | JUMPER | WIRE DOWN 11 LD SD OF FUSE 6485 | 20170208 | 611 | 1681464 | 556 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4205 | 38.4664 | -122.9124 | 11 LD SIDE OF 6485 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0018869 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256608 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 15461 | 20170208 | 854 | 1681594 | 506 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2530 | 38.4626 | -122.9383 | 2 LD SIDE OF 15461 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019014 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256676 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | SANTA ROSA A-1111 | 42151111 | FUSE | 55443 | 20170208 | 2315 | 1682640 | 793 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 23790 | 38.4202 | -122.6749 | 4493 BENNETT VIEW DR | Overcast-Fog-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0019198 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256811 | CSO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 6927 | 20170216 | 1524 | 1690608 | 515 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 515 | 38.5975 | -122.9982 | 8810 MILL CREEK RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0021743 | OH | Sus | 42950216 | yes | 2017 | FEB | Yes | Line to Ground | 1258860 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 59153 | 20170219 | 1619 | 1701859 | 1161 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 5805 | 38.5424 | -123.2899 | 1/P/LD SIDE OF 59153 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0023494 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1260480 | CSO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 560 | 20170219 | 1927 | 1702027 | 1268 | Distribution Circuit | Vegetation | Tree - branch fell on line | 31 | 39308 | 38.5562 | -123.3034 | MM 42.86 HWY 1- FISK MILL COVE- XST-KRUSE RANCH RD AND 9 SPANS S/OF MM 42.86 | Strong Winds-Rain-Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0023569 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Multi-Fault | 1260560 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | SWITCH | 1007 | 20170227 | 2036 | 1715610 | 310 | Distribution Circuit | Equipment Failure/Involved | Overhead | 114 | 33180 | 38.4859 | -122.9621 | 5/SPANS FROM 12683 TWD 202 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0027175 | OH | Sus | 0 | No | 2017 | FEB | Yes | Line to Ground | 1263799 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 3970 | 20170227 | 1719 | 1715476 | 279 | Distribution Circuit | Vegetation | Tree - fell into line | 2573 | 251745 | 38.4997 | -123.0054 | 15999 RIVER RD GURNEVILLE/ 1/SPAN LD OF 524 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0027156 | OH | Sus | 42954995 | No | 2017 | FEB | Yes | Three Phase Fault | 1263785 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1043 | 20170228 | 807 | 1715857 | 366 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 732 | 38.5068 | -122.915 | 1 SPAN LOAD SIDE OF 1043 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0027279 | OH | Sus | 31308166 | No | 2017 | FEB | Yes | Line to Ground | 1263905 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1102 | 42821102 | FUSE | 17149 | 20170306 | 1058 | 1720987 | 315 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 9135 | 38.7853 | -123.0227 | 1 POLE LD SIDE OF FUCO 17149 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0028788 | OH | Sus | 42959645 | yes | 2017 | MAR | Yes | Line to Ground | 1265083 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 17225 | 20170309 | 211 | 1722972 | 685 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 24660 | 38.5094 | -122.9225 | 10661 RIVER DR | Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0029563 | OH | Sus | 0 | No | 2017 | MAR | Yes | Line to Line | 1265657 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 1761 | 20170324 | 712 | 1734352 | 507 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 16525 | 38.3789 | -122.8977 | MTR#1004759381 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0033347 | OH | Sus | 42976279 | yes | 2017 | MAR | Yes | Line to Ground | 1268421 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 5799 | 20170328 | 1339 | 1737644 | 386 | Distribution Circuit | Vegetation | Tree - branch fell on line | 41 | 15826 | 38.519 | -122.601 | MTR# 128545 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0034498 | OH | Sus | 42978867 | yes | 2017 | MAR | Yes | Line to Ground | 1269301 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 4673 | 20170330 | 1239 | 1739267 | 123 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 2706 | 38.284 | -122.7332 | 1 SPAN LD SIDE OF 4673 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0035085 | OH | Sus | 42980372 | yes | 2017 | MAR | Yes | Line to Ground | 1269782 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 6751 | 20170330 | 1157 | 1739360 | 868 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 111461 | 38.592 | -122.9622 | 7505 MILL CREEK | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0035109 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Ground | 1269800 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 6591 | 20170330 | 1254 | 1739454 | 308 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 24332 | 38.5235 | -122.9786 | 17137 MT JACKSON TRAIL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0035122 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Ground | 1269803 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | RINCON-1104 | 43321104 | OCB | 1104/2 | 20170330 | 1514 | 1739694 | 606 | Distribution Circuit | Vegetation | Tree - fell into line | 4004 | 245566 | 38.4901 | -122.6661 | Moore- Dave /3612: 1755 BRUSH CREEK RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0035171 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Ground | 1269822 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 6113 | 20170331 | 1422 | 1741480 | 602 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 17978 | 38.5381 | -122.6468 | 1 SPAN LD SIDE OF 6121 TAP | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0035647 | OH | Sus | 0 | yes | 2017 | MAR | Yes | Line to Line | 1270198 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | OTHER | WIRE DOWN 1 SPAN SOURCE SIDE OF 14555 | 20170403 | 1815 | 1743304 | 557 | Distribution Circuit | Vegetation | Tree - fell into line | 298 | 73252 | 38.5438 | -122.7205 | MAIN LINE AT FUCO 14555 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0036218 | OH | Sus | 42983131 | No | 2017 | APR | Yes | Line to Ground | 1270706 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 3183 | 20170408 | 1853 | 1753122 | 1107 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 3321 | 38.2422 | -122.8992 | 8 SPANS LD SIDE OF FUCO 3183 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038349 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1272401 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1101 | 42091101 | FUSE | 6485 | 20170408 | 1709 | 1753022 | 1091 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 8728 | 38.4668 | -122.9087 | MTR 1009076873 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0038351 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Line | 1272403 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6233 | 20170412 | 133 | 1755775 | 512 | Distribution Circuit | Environmental/External | Flood/Erosion | 13 | 6656 | 38.4471 | -122.9241 | 2/S/LD/S OF 6233 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0039381 | OH | Sus | 31318985 | No | 2017 | APR | Yes | Line to Ground | 1273272 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 560 | 20170414 | 1323 | 1757999 | 832 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 25792 | 38.5562 | -123.3034 | 3 SPANS LOAD SIDE OF 560 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0040393 | OH | Sus | 42995143 | No | 2017 | APR | Yes | Multi-Fault | 1273905 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 2373 | 20170418 | 650 | 1759946 | 820 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4920 | 38.5096 | -122.9609 | KOTULA- JON / 4343: UP MCPEAK. BEHIND KORBEL. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0041059 | OH | Sus | 31320218 | yes | 2017 | APR | Yes | Force Out | 1274469 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 6685 | 20170420 | 811 | 1761570 | 647 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 44141 | 38.5237 | -122.9788 | 15372 WILLOW RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0041600 | OH | Sus | 0 | No | 2017 | APR | Yes | Line to Ground | 1274854 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | JUMPER | WIRE DOWN HOT | 20170424 | 607 | 1765729 | 659 | Distribution Circuit | Vegetation | Tree - fell into line | 454 | 59061 | 38.5381 | -123.1197 | 1 SS OF MTR 1007687696 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0042300 | OH | Sus | 31321154 | No | 2017 | APR | Yes | Line to Line | 1275447 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 8057 | 20170429 | 1504 | 1770500 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 406 | 38.496 | -122.9377 | ALVAREZ- R /3885: 8720 MARTINELLI RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0043912 | OH | Sus | 43003699 | No | 2017 | APR | Yes | Line to Line | 1276533 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 246 | 20170502 | 1715 | 1772714 | 253 | Distribution Circuit | Vegetation | Tree - fell into line | 549 | 92609 | 38.3657 | -122.5275 | ON MAINLINE FEEDING TRIP SAVER 1249 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0044665 | OH | Sus | 43005967 | yes | 2017 | MAY | Yes | Three Phase Fault | 1277072 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1102 | 42821102 | RECLOSER | 262 | 20170506 | 527 | 1775994 | 655 | Distribution Circuit | Vegetation | Tree - branch fell on line | 363 | 61793 | 38.7977 | -122.991 | ON MAINLINE at 76875 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0045743 | OH | Sus | 31324252 | yes | 2017 | MAY | Yes | Line to Ground | 1277857 | CAW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 15383 | 20170512 | 735 | 1780538 | 335 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 7370 | 38.4483 | -123.0005 | 1 SPAN LD SIDE OF 15383- 8231 TYRONE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0047463 | OH | Sus | 31325426 | No | 2017 | MAY | Yes | Line to Line | 1279196 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1109 | 42631109 | RECLOSER | 128 | 20170517 | 1710 | 1784315 | 381 | Distribution Circuit | Vegetation | Tree - fell into line | 229 | 28077 | 38.2201 | -122.6439 | 2/S/LOADSIDE OF 2623 ON MAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0048665 | OH | Sus | 43018994 | No | 2017 | MAY | Yes | Line to Ground | 1280150 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | JUMPER | OJ'S @ MTR # 1009997686 | 20170524 | 1430 | 1789737 | 470 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 470 | 38.1963 | -122.8855 | METER # 1009997686 END OF CLARK RD | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on object | 17-0050433 | OH | Sus | 43022604 | No | 2017 | MAY | Yes | None | 1281379 | CSO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 10537 | 20170525 | 1655 | 1790693 | 661 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 2644 | 38.3985 | -122.9872 | 1 SPAN LD SIDE OF FUCO 10537 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0050815 | OH | Sus | 43023435 | No | 2017 | MAY | Yes | Line to Ground | 1281629 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | FUSE | 6581 | 20170606 | 1335 | 1798194 | 281 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 1405 | 38.3405 | -122.7526 | 1 LD SIDE OF FUCO 6581 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0053115 | OH | Sus | 43029377 | No | 2017 | JUN | Yes | Three Phase Fault | 1283395 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | SANTA ROSA A-1104 | 42151104 | FUSE | 3647 | 20170617 | 1953 | 1807221 | 341 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 12198 | 38.4675 | -122.689 | BRANCH FELL AT 4070 ALTA VISTA AVE. | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0055995 | OH | Sus | 0 | yes | 2017 | JUN | Yes | Line to Ground | 1285474 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | JUMPER | WIRE DOWN 9850 BARNETT VALLEY RD | 20170620 | 906 | 1812274 | 344 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 4872 | 38.3668 | -122.8684 | 9850 BARNETT VALLEY RD | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0056943 | OH | Sus | 0 | yes | 2017 | JUN | Yes | Line to Ground | 1286377 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 3355 | 20170622 | 1656 | 1815252 | 601 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5409 | 38.4761 | -122.9304 | 9000 HWY 116 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0057838 | OH | Sus | 0 | yes | 2017 | JUN | Yes | Line to Line | 1287040 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1103 | 43071103 | FUSE | 13333 | 20170625 | 1155 | 1817620 | 414 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 4968 | 38.3738 | -122.5176 | Deignan/3571: 12850 DUNBAR RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0058441 | OH | Sus | 43044668 | No | 2017 | JUN | Yes | Line to Line | 1287541 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 429 | 20170629 | 1812 | 1820958 | 477 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 20601 | 38.4734 | -123.0226 | 21229 VILLA GRANDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0059600 | OH | Sus | 43047266 | No | 2017 | JUN | Yes | Line to Line | 1288410 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 10343 | 20170705 | 1841 | 1824172 | 274 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 274 | 38.2853 | -122.7464 | 2 SPANS LD SIDE OF 10343 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0060713 | OH | Sus | 43049439 | No | 2017 | JUL | Yes | Line to Line | 1289159 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | OTHER | 3 OF 3 HOT WIRES DOWN | 20170717 | 121 | 1833181 | 563 | Distribution Circuit | Vegetation | Tree - fell into line | 1153 | 126343 | 38.4429 | -122.9914 | 7001 BOHEMIAN HWY | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0063304 | OH | Sus | 0 | No | 2017 | JUL | Yes | Line to Ground | 1291102 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 5549 | 20170725 | 1547 | 1839696 | 808 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 18584 | 38.3726 | -122.5385 | 4399 WARM SPRINGS RD- GLEN ELLEN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0065437 | OH | Sus | 43067423 | No | 2017 | JUL | Yes | Line to Ground | 1292616 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 12637 | 20170725 | 1358 | 1839626 | 276 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 36 | 9936 | 38.5017 | -123.0046 | 13972 FERN RD- GUERNEVILLE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0065385 | OH | Sus | 43067348 | No | 2017 | JUL | Yes | Line to Line | 1292598 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 6751 | 20170731 | 1310 | 1843215 | 885 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 118590 | 38.592 | -122.9622 | 8/P/PAST 6751 ON MAIN LINE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0066767 | OH | Sus | 0 | No | 2017 | JUL | Yes | Line to Ground | 1293511 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 2561 | 20170802 | 2155 | 1845097 | 955 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 20055 | 38.4113 | -122.965 | Moore- Shon/4250: 1 SPAN FROM METER# 1007526315 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0067550 | OH | Sus | 31340526 | yes | 2017 | AUG | Yes | Line to Ground | 1294033 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24918 | 20170805 | 1625 | 1847035 | 751 | Distribution Circuit | Vegetation | Tree - fell into line | 187 | 140437 | 38.5914 | -122.92 | 2 SPANS LD SIDE OF MTR 1007786111 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0068193 | OH | Sus | 31341080 | No | 2017 | AUG | Yes | Line to Ground | 1294501 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | PENNGROVE-1101 | 43471101 | OTHER | WIRE DOWN 1 PH @ SNGL PH JUST BEFORE 3793 | 20170815 | 2118 | 1853405 | 517 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 15209 | 38.3357 | -122.5918 | CONTRERAS- T /3463: 2955 SONOMA MOUNTAIN RD OR C/O 3793 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0070629 | OH | Sus | 43085627 | No | 2017 | AUG | Yes | Line to Ground | 1296215 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 448 | 20170820 | 1646 | 1855771 | 565 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1305 | 204241 | 38.3443 | -122.5145 | 15 DON TIMETEO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0071584 | OH | Sus | 31343744 | No | 2017 | AUG | Yes | Line to Line | 1296912 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | RINCON-1103 | 43321103 | RECLOSER | 7433 | 20170826 | 2029 | 1860173 | 382 | Distribution Circuit | Equipment Failure/Involved | Electrical Overload | 1383 | 361520 | 38.4722 | -122.653 | ON MAINLINE at 13059- 5701 DUPONT DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0073092 | OH | Sus | 43094540 | No | 2017 | AUG | Yes | Line to Ground | 1297973 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | RECLOSER | 77670 | 20170827 | 1509 | 1860504 | 788 | Distribution Circuit | Vegetation | Tree - fell into line | 400 | 214780 | 38.5022 | -122.737 | 5232 CARRIAGE LN | Clear-Above 90 | Pole-Wood | Broken, wire on ground | 17-0073179 | OH | Sus | 0 | yes | 2017 | AUG | Yes | Line to Ground | 1298051 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | TRIP-SAVER | 2359 | 20170830 | 157 | 1862960 | 639 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 55715 | 38.358 | -122.5256 | Noonan- Todd/3469: 1457 HILL RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0073984 | OH | Sus | 43095838 | No | 2017 | AUG | Yes | Line to Ground | 1298606 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | SANTA ROSA A-1107 | 42151107 | JUMPER | WIRE DOWN | 20170902 | 724 | 1866035 | 458 | Distribution Circuit | Equipment Failure/Involved | Overhead | 330 | 64356 | 38.4505 | -122.6872 | FUCO 9001 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0075088 | OH | Sus | 0 | yes | 2017 | SEP | Yes | Line to Ground | 1299385 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | SONOMA-1103 | 42721103 | FUSE | 5543 | 20170902 | 2125 | 1867532 | 972 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 71928 | 38.303 | -122.4409 | 2 SPANS LD SIDE OF 5543 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0075429 | OH | Sus | 0 | yes | 2017 | SEP | Yes | Line to Ground | 1299717 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | JUMPER | WIRE DOWN HOT @ 3170 WESTWOOD LN | 20170904 | 948 | 1869647 | 440 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 880 | 38.4052 | -122.9705 | 3170 WESTWOOD LN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0075808 | OH | Sus | 0 | yes | 2017 | SEP | Yes | Line to Ground | 1300067 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 61169 | 20170905 | 1243 | 1870663 | 777 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 20 | 15540 | 38.4921 | -123.0664 | 2325 CAZADERO HWY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0076120 | OH | Sus | 0 | No | 2017 | SEP | Yes | Line to Ground | 1300308 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24918 | 20170918 | 1441 | 1881109 | 448 | Distribution Circuit | Vegetation | Tree - branch fell on line | 187 | 83776 | 38.5914 | -122.92 | Nott/3569: 3721 MILL CREEK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0079789 | OH | Sus | 43113382 | No | 2017 | SEP | Yes | Line to Line | 1303050 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 2473 | 20170919 | 438 | 1881482 | 772 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 21895 | 38.7106 | -122.925 | Noonan- Todd/3469: 585 ROSSI RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0079875 | OH | Sus | 0 | No | 2017 | SEP | Yes | Line to Ground | 1303119 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 1955 | 20170924 | 1642 | 1885026 | 296 | Distribution Circuit | Vegetation | Tree - branch fell on line | 160 | 22574 | 38.3879 | -122.9715 | MTR#1007570521 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0081329 | OH | Sus | 43116676 | No | 2017 | SEP | Yes | Line to Ground | 1304105 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | CLOVERDALE-1102 | 42821102 | FUSE | 1387 | 20171010 | 1129 | 1897527 | 2996 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 37248 | 38.8409 | -122.9529 | 1009647650 & 100825255 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0085994 | OH | Sus | 0 | No | 2017 | OCT | Yes | Force Out | 1307237 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | RINCON-1102 | 43321102 | FUSE | 15249 | 20171010 | 1418 | 1897684 | 10242 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 9 | 92178 | 38.4854 | -122.6679 | MTR#1007528748 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0087223 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1308212 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | SONOMA-1103 | 42721103 | FUSE | 99309 | 20171010 | 700 | 1897119 | 16076 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 353672 | 38.3269 | -122.4321 | 6 POLES LD SIDE OF 99309 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086005 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1307247 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 320 | 20171011 | 1245 | 1898451 | 1565 | Distribution Circuit | Vegetation | Tree - branch fell on line | 145 | 226925 | 38.4989 | -123.0211 | 15180 CAZADERA RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0086350 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Line | 1307494 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1102 | 42891102 | FUSE | 188527 | 20171013 | 753 | 1899808 | 2211 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 11055 | 38.7317 | -122.8989 | 3 SP TWD C/OUT FROM METER#1009959849 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0087081 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Ground | 1308100 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | TRIP-SAVER | 999 | 20171019 | 2335 | 1904753 | 649 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 51271 | 38.422 | -122.954 | 21 HAMPTON RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0088846 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1309422 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | SONOMA-1103 | 42721103 | OTHER | WIRE DOWN NORRBOM RD MTR#1008107017 | 20171021 | 1814 | 1907292 | 1609 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 22 | 24938 | 38.3285 | -122.4393 | MTR#1008107017 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0089503 | OH | Sus | 0 | No | 2017 | OCT | Yes | Force Out | 1309967 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | JUMPER | OJ'S @ 1217 WIKIUP DR | 20171025 | 1011 | 1909252 | 184 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2 | 368 | 38.5098 | -122.7435 | W/O 1217 WIKIUP | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0090251 | OH | Sus | 0 | No | 2017 | OCT | Yes | Force Out | 1310510 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | RINCON-1102 | 43321102 | FUSE | 15265 | 20171026 | 1442 | 1910271 | 1477 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5124 | 38.4896 | -122.6673 | 1645 Baird Rd (MTR#1008903615) | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0090635 | OH | Sus | 0 | No | 2017 | OCT | Yes | Line to Line | 1310717 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1101 | 42091101 | FUSE | 1003 | 20171103 | 1204 | 1915139 | 146 | Distribution Circuit | Equipment Failure/Involved | Overhead | 69 | 10074 | 38.4763 | -122.9069 | 2 SPANS LD SIDE OF 1003 | Overcast-Fog-Rain-32-90 F | Insulator | Broken, wire on ground | 17-0092446 | OH | Sus | 0 | yes | 2017 | NOV | Yes | Line to Ground | 1312011 | INS | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 779 | 20171113 | 1857 | 1921777 | 1341 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 50440 | 38.5971 | -122.9894 | WIRE DOWN 1 SPAN SS OF 3033 | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0094794 | OH | Sus | 0 | No | 2017 | NOV | Yes | Line to Line | 1313785 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | RECLOSER | 120 | 20171115 | 2020 | 1923319 | 604 | Distribution Circuit | Vegetation | Tree - fell into line | 494 | 90969 | 38.4637 | -123.0083 | MTR# 1007253355 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0095377 | OH | Sus | 43215957 | yes | 2017 | NOV | Yes | Line to Line | 1314269 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 2027 | 20171115 | 732 | 1922646 | 255 | Distribution Circuit | Vegetation | Tree - branch fell on line | 28 | 7140 | 38.5191 | -122.98 | 14724 EAGLE NEST LN | Clear-32-90 F | Conductor, Overhead | On Ground | 17-0095069 | OH | Sus | 43214472 | yes | 2017 | NOV | Yes | Line to Ground | 1314067 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 568 | 20171120 | 1433 | 1926769 | 680 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 167 | 62410 | 38.5173 | -122.655 | 7/S/LS OF 929 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0096607 | OH | Sus | 31366547 | No | 2017 | NOV | Yes | Line to Ground | 1315174 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONROE-2103 | 43302103 | FUSE | 14615 | 20171124 | 913 | 1928588 | 275 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 62 | 17050 | 38.5175 | -122.7222 | 2 SPANS LD SIDE OF FUCO 14615- 1488 MICHELE WAY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0097377 | OH | Sus | 43221245 | No | 2017 | NOV | Yes | Line to Line | 1315634 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 2149 | 20171127 | 541 | 1929846 | 524 | Distribution Circuit | Vegetation | Tree - fell into line | 82 | 42968 | 38.3777 | -122.8781 | SS OF FUCO 18123 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0097707 | OH | Sus | 43222352 | yes | 2017 | NOV | Yes | Line to Ground | 1315927 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 15383 | 20171128 | 1001 | 1930950 | 318 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 6996 | 38.4483 | -123.0005 | 8231 TYRONE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0098083 | OH | Sus | 43223484 | No | 2017 | NOV | Yes | Line to Ground | 1316292 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | OTHER | WIRE DOWN MTR#1007662094 | 20171130 | 654 | 1932318 | 584 | Distribution Circuit | Vegetation | Tree - fell into line | 532 | 111884 | 38.3686 | -122.535 | MTR 1007662094- 4463 LAKESIDE DR- GLENN ELLEN | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0098537 | OH | Sus | 31367702 | No | 2017 | NOV | Yes | Line to Ground | 1316669 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 636 | 20171205 | 1704 | 1936881 | 522 | Distribution Circuit | Equipment Failure/Involved | Overhead | 142 | 23869 | 38.2618 | -122.7158 | CONTRERAS- T /3463: 5730 BODEGA AVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0100137 | OH | Sus | 43227597 | yes | 2017 | DEC | Yes | Line to Ground | 1317806 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | JUMPER | WIRE DOWN | 20171208 | 1719 | 1939265 | 4139 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 9779 | 38.6629 | -123.2356 | 4609 C/OUT POLE | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0100881 | OH | Sus | 43229525 | No | 2017 | DEC | Yes | Line to Ground | 1318524 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 568 | 20171209 | 658 | 1939399 | 441 | Distribution Circuit | Animal | Bird found | 167 | 24035 | 38.5173 | -122.655 | 10 SPANS LD SIDE OF 929 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0100915 | OH | Sus | 43229436 | No | 2017 | DEC | Yes | Line to Ground | 1318558 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1101 | 43321101 | JUMPER | 1251 | 20171214 | 1129 | 1942977 | 186 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 17 | 3156 | 38.4517 | -122.5744 | AT MTR 1007221702 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0101649 | OH | Sus | 43235201 | No | 2017 | DEC | Yes | Line to Ground | 1319537 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | OCB | 1121/2 | 20171215 | 1907 | 1943877 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 638 | 99293 | 38.5408 | -123.2237 | S/S TO 9425 BEN WAY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0101861 | OH | Sus | 43236420 | No | 2017 | DEC | Yes | Line to Line | 1319753 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER | 1067 | 20180104 | 1749 | 2210 | 530 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 57770 | 38.4934 | -123.0059 | 2 SPANS LD SIDE OF 1067 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0003716 | OH | Sus | 31372271 | yes | 2018 | JAN | Yes | Line to Line | 1323221 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 12153 | 20180108 | 1557 | 4127 | 248 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 744 | 38.4446 | -122.9204 | FUCO 12153 | Clear-32-90 F | Insulator | Broken, wire on object | 18-0004427 | OH | Sus | 43246416 | yes | 2018 | JAN | Yes | Force Out | 1323669 | INS | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 1047 | 20180108 | 1255 | 3968 | 915 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 44835 | 38.5319 | -123.0876 | 2 BROKEN POLES AT MTR# 5000012222- WIRE DOWN AT MTR # 1009769849 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0004361 | OH | Sus | 43246404 | yes | 2018 | JAN | Yes | Line to Line | 1323646 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | OTHER | 15383 | 20180108 | 2034 | 4327 | 889 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 18277 | 38.4483 | -123.0005 | 9 SPANS LD SIDE OF FUCO 15383 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0004489 | OH | Sus | 43246523 | yes | 2018 | JAN | Yes | Line to Ground | 1323722 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1101 | 43071101 | FUSE | 3749 | 20180109 | 1349 | 5208 | 180 | Distribution Circuit | Vegetation | Tree - branch fell on line | 21 | 3780 | 38.4006 | -122.5682 | 633 VIA FERRARI | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0004797 | OH | Sus | 0 | yes | 2018 | JAN | Yes | Line to Ground | 1323913 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE | 2239 | 20180211 | 1302 | 22733 | 776 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 3880 | 38.3448 | -123.0243 | 2 SPANS LD SIDE OF 2239 | Partly Cloudy-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 18-0013241 | OH | Sus | 0 | No | 2018 | FEB | Yes | Three Phase Fault | 1329413 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | FUSE | 2375 | 20180213 | 1214 | 24022 | 511 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 21 | 10731 | 38.5423 | -122.7203 | LD SIDE OF FUCO 2375 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0013860 | OH | Sus | 43278014 | No | 2018 | FEB | Yes | Line to Ground | 1329858 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 4837 | 20180218 | 1640 | 26786 | 399 | Distribution Circuit | Vegetation | Tree - branch fell on line | 52 | 20748 | 38.4804 | -122.9967 | 2 SPANS LD SIDE OF 4837 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0015259 | OH | Sus | 43280611 | yes | 2018 | FEB | Yes | Force Out | 1330696 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 634 | 20180226 | 401 | 31369 | 380 | Distribution Circuit | Equipment Failure/Involved | Overhead | 48 | 11865 | 38.2982 | -122.8208 | 15 SPANS LD SIDE OF 79249 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0017109 | OH | Sus | 43284506 | yes | 2018 | FEB | Yes | Line to Ground | 1332055 | CSO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | JUMPER | WIRE DOWN 1/S/OF 3409 | 20180301 | 643 | 34217 | 395 | Distribution Circuit | Vegetation | Tree - bark fell into line | 149 | 35562 | 38.2063 | -122.9202 | 1 SPAN SOUTH OF 3409 ON MAINLINE | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0018367 | OH | Sus | 43287212 | yes | 2018 | MAR | Yes | Line to Ground | 1332898 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 2373 | 20180301 | 2148 | 35800 | 942 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5652 | 38.5096 | -122.9609 | 12550 MCPEAK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0018930 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333284 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 104 | 20180301 | 1857 | 35614 | 913 | Distribution Circuit | Vegetation | Tree - fell into line | 1499 | 647323 | 38.403 | -122.9214 | 13330 OCCIDENTAL RD | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0018816 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333182 | CAW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 3421 | 20180314 | 1055 | 44111 | 900 | Distribution Circuit | Environmental/External | Lightning | 7 | 6300 | 38.2866 | -122.8527 | MTR# 1010196749 & 4 SPANS LD SIDE OF 3421 | Partly Cloudy-Drizzle-Lightning-32-90 F | Transformer (OH) | Broken, wire on ground | 18-0022724 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1335861 | TXO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 568 | 20180315 | 2209 | 45137 | 566 | Distribution Circuit | 3rd Party | Vehicle | 167 | 49045 | 38.5173 | -122.655 | 1 SPAN S/OF 1199 ON MAINLINE- CAMP NEWMAN - PORTER CREEK RD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023217 | OH | Sus | 43301931 | No | 2018 | MAR | Yes | Multi-Fault | 1336119 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1102 | 42271102 | TRIP-SAVER | 681 | 20180318 | 1025 | 47308 | 463 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 40260 | 38.2838 | -122.7101 | MTR# 1009647754 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0023887 | OH | Sus | 43303123 | No | 2018 | MAR | Yes | Line to Ground | 1336691 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1101 | 42091101 | FUSE | 6485 | 20180321 | 427 | 49112 | 758 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 6064 | 38.4668 | -122.9087 | 7 SPANS LD SIDE OF FUSES | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0024677 | OH | Sus | 43304152 | yes | 2018 | MAR | Yes | Multi-Fault | 1337228 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | FUSE | 3287 | 20180322 | 527 | 50171 | 422 | Distribution Circuit | Vegetation | Tree - fell into line | 175 | 73850 | 38.3381 | -122.7858 | 6000 BLANK RD | Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025276 | OH | Sus | 43305958 | yes | 2018 | MAR | Yes | Line to Ground | 1337490 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 2353 | 20180322 | 512 | 50225 | 453 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1812 | 38.6326 | -122.8307 | 2 SPANS SOURCE SIDE OF EOL | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025337 | OH | Sus | 43306110 | yes | 2018 | MAR | Yes | Line to Ground | 1337521 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 433 | 20180322 | 724 | 50280 | 509 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 16797 | 38.5091 | -122.9283 | 11955 WESTSIDE RD | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025324 | OH | Sus | 43306112 | yes | 2018 | MAR | Yes | Line to Ground | 1337510 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2223 | 20180322 | 740 | 50309 | 378 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 15680 | 38.5471 | -122.6692 | 3480 CALISTOGA | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025348 | OH | Sus | 43306118 | yes | 2018 | MAR | Yes | Line to Line | 1337528 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | FUSE | 6563 | 20180324 | 1540 | 52762 | 485 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5820 | 38.3217 | -122.7872 | 4 SPANS LOADSIDE OF 6563 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0026329 | OH | Sus | 0 | No | 2018 | MAR | Yes | Line to Ground | 1338166 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | TRIP-SAVER | 4859 | 20180325 | 720 | 52972 | 559 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 26832 | 38.4755 | -122.9527 | 14025 GREEN VALLEY RD | Clear-32-90 F | Conductor, Overhead | On Ground | 18-0026404 | OH | Sus | 43308453 | No | 2018 | MAR | Yes | Multi-Fault | 1338260 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1101 | 42571101 | OTHER | WIRE DOWN | 20180406 | 901 | 60702 | 423 | Distribution Circuit | Vegetation | Tree - fell into line | 1049 | 42343 | 38.3938 | -122.8951 | 920 FURLONG RD- SEBASTOPOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0029825 | OH | Sus | 43316563 | yes | 2018 | APR | Yes | Line to Ground | 1340878 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1102 | 42091102 | FUSE | 13669 | 20180407 | 614 | 61640 | 533 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 4797 | 38.509 | -122.8869 | 6 POLES LD SIDE OF 13669 | Overcast-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 18-0030201 | OH | Sus | 0 | yes | 2018 | APR | Yes | Three Phase Fault | 1341075 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 12383 | 20180411 | 1933 | 65049 | 617 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 8638 | 38.3393 | -122.5289 | 1 SPAN LOADSIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0031475 | OH | Sus | 0 | yes | 2018 | APR | Yes | Line to Line | 1342113 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1499 | 20180411 | 1906 | 64948 | 315 | Distribution Circuit | Vegetation | Tree - branch fell on line | 129 | 28135 | 38.5089 | -122.9291 | 11091 SEQUOIA RD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0031446 | OH | Sus | 0 | yes | 2018 | APR | Yes | Line to Line | 1342076 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1045 | 20180411 | 1759 | 64934 | 606 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 40602 | 38.5008 | -122.9054 | 1 SPAN LOADSIDE | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0031458 | OH | Sus | 0 | yes | 2018 | APR | Yes | Line to Ground | 1342091 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 8057 | 20180412 | 833 | 65349 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 325 | 38.496 | -122.9377 | 1 LD SIDE OF 8057 | Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0031670 | OH | Sus | 43323320 | yes | 2018 | APR | Yes | Line to Line | 1342289 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 8493 | 20180417 | 2308 | 69184 | 1226 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 47695 | 38.5329 | -123.2714 | 1 SPAN N/OF MTR#1007899182- 20885 HWY 1 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0033253 | OH | Sus | 43326942 | No | 2018 | APR | Yes | Line to Ground | 1343431 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1102 | 43071102 | OTHER | 7051 | 20180423 | 818 | 71891 | 418 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4598 | 38.3666 | -122.5653 | 4 SPANS LD SIDE OF 7051 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0034556 | OH | Sus | 31389606 | No | 2018 | APR | Yes | Force Out | 1344370 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2269 | 20180425 | 1349 | 73832 | 812 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 19488 | 38.5183 | -122.6032 | MTR # 1003850696 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0035535 | OH | Sus | 0 | No | 2018 | APR | Yes | Multi-Fault | 1344997 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 636 | 20180427 | 2206 | 75705 | 1005 | Distribution Circuit | Equipment Failure/Involved | Overhead | 141 | 36141 | 38.2618 | -122.7158 | MTR# 5000011262 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0036416 | OH | Sus | 43333110 | No | 2018 | APR | Yes | Line to Ground | 1345487 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24918 | 20180428 | 2036 | 76057 | 1069 | Distribution Circuit | Vegetation | Tree - fell into line | 187 | 199903 | 38.5914 | -122.92 | 4535 MILL CREEK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0036544 | OH | Sus | 43333221 | No | 2018 | APR | Yes | Line to Ground | 1345619 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1499 | 20180508 | 1923 | 81953 | 365 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 47723 | 38.5089 | -122.9291 | 11055 DELL AVE & 11091 DELL AVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0039404 | OH | Sus | 43339372 | No | 2018 | MAY | Yes | Line to Line | 1347607 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 560 | 20180509 | 1400 | 82502 | 1018 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 29522 | 38.5562 | -123.3034 | FISK MILL COVE MILE KARKER 42 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0039683 | OH | Sus | 43339946 | No | 2018 | MAY | Yes | Line to Ground | 1347853 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | TRIP-SAVER | 841 | 20180510 | 1647 | 83337 | 577 | Distribution Circuit | Vegetation | Tree - branch fell on line | 133 | 31753 | 38.5087 | -122.9261 | Moore- S/4308: BETWEEN C O 13597 AND METER# 1008019873 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0039981 | OH | Sus | 43344425 | No | 2018 | MAY | Yes | Line to Ground | 1348131 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | TRIP-SAVER | 6917 | 20180511 | 1013 | 83837 | 242 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 5959 | 38.3873 | -122.9728 | 17450 TAYLOR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0040240 | OH | Sus | 43345988 | yes | 2018 | MAY | Yes | Line to Ground | 1348335 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2225 | 20180511 | 1803 | 84346 | 311 | Distribution Circuit | Vegetation | Tree - fell into line | 90 | 27990 | 38.5242 | -122.6544 | 3166 CALISTOGA RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0040429 | OH | Sus | 43346461 | yes | 2018 | MAY | Yes | Line to Line | 1348435 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 636 | 20180519 | 1624 | 89814 | 236 | Distribution Circuit | Equipment Failure/Involved | Overhead | 141 | 15606 | 38.2618 | -122.7158 | 1 P/N/OF 4259 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0042546 | OH | Sus | 43351611 | No | 2018 | MAY | Yes | Line to Line | 1350129 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 4133 | 20180522 | 1325 | 91919 | 1042 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 31253 | 38.1494 | -122.8233 | 5600 PETALUMA MARSHALL RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0043287 | OH | Sus | 43353725 | No | 2018 | MAY | Yes | Three Phase Fault | 1350879 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | OTHER | HOT WIRE DOWN @ 2375 | 20180605 | 1345 | 102064 | 819 | Distribution Circuit | Vegetation | Tree - fell into line | 212 | 38493 | 38.5396 | -122.7208 | 2390 MARK WEST SPRINGS RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0047625 | OH | Sus | 0 | No | 2018 | JUN | Yes | Open Circuit | 1354100 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 737 | 20180610 | 1719 | 105889 | 411 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 2386 | 38.4084 | -122.9079 | MTR# 1010299830 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0049445 | OH | Sus | 43369565 | No | 2018 | JUN | Yes | Line to Ground | 1355506 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | RECLOSER | 322 | 20180618 | 1509 | 112225 | 724 | Distribution Circuit | 3rd Party | Vehicle | 375 | 94110 | 38.3868 | -122.8901 | 18689 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0052032 | OH | Sus | 0 | No | 2018 | JUN | Yes | Line to Line | 1357484 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1043 | 20180702 | 1710 | 123301 | 630 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1260 | 38.5068 | -122.915 | 1 LD SIDE OF 1043- 10140 CANYON RD | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0056492 | OH | Sus | 0 | No | 2018 | JUL | Yes | Multi-Fault | 1361163 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24550 | 20180714 | 1240 | 131638 | 552 | Distribution Circuit | 3rd Party | Vehicle | 225 | 20804 | 38.5793 | -122.878 | 2 SPANS SS OF 38536 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0059799 | OH | Sus | 0 | No | 2018 | JUL | Yes | Line to Ground | 1363775 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6877 | 20180717 | 1653 | 134079 | 555 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 12038 | 38.3942 | -122.9138 | 1 SS FU 7317 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0060829 | OH | Sus | 31400289 | yes | 2018 | JUL | Yes | Line to Line | 1364537 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6877 | 20180718 | 246 | 134376 | 524 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 6868 | 38.3942 | -122.9138 | at 12430 FIORI LN- SEBASTOPOL | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0060883 | OH | Sus | 0 | yes | 2018 | JUL | Yes | Line to Ground | 1364593 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 36536 | 20180731 | 634 | 145643 | 1183 | Distribution Circuit | 3rd Party | Vehicle | 792 | 162993 | 38.3142 | -122.7365 | CANFIELD & ROBLAR | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0065221 | OH | Sus | 0 | No | 2018 | JUL | Yes | Three Phase Fault | 1367911 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6543 | 20180731 | 1545 | 146119 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 8323 | 38.3683 | -122.9641 | 16721 BURL LN | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0065479 | OH | Sus | 43426906 | No | 2018 | JUL | Yes | Line to Ground | 1368112 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1109 | 42631109 | FUSE | 2621 | 20180802 | 2127 | 147932 | 377 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 5655 | 38.1683 | -122.6739 | 1 SPAN SS OF MTR #1007932553 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0066335 | OH | Sus | 43428965 | No | 2018 | AUG | Yes | Line to Line | 1368730 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1407 | 20180809 | 1621 | 152381 | 559 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 10062 | 38.4977 | -122.9026 | at FUCO 13491 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0068470 | OH | Sus | 31402437 | No | 2018 | AUG | Yes | Line to Line | 1370091 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | RINCON-1103 | 43321103 | OCB | 1103/2 | 20180822 | 1653 | 160482 | 487 | Distribution Circuit | Vegetation | Tree - branch fell on line | 700 | 129734 | 38.4901 | -122.6661 | 509 GARFEILD PARK AVE- at 15133 TWD 5197 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0072613 | OH | Sus | 31403994 | No | 2018 | AUG | Yes | Line to Line | 1372765 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | OTHER | 6399 | 20180826 | 1337 | 162668 | 358 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 11098 | 38.5038 | -122.9115 | 10385 SCENIC DR | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 18-0073589 | OH | Sus | 43448406 | No | 2018 | AUG | Yes | Line to Ground | 1373558 | CSO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1102 | 42091102 | FUSE | 13669 | 20180903 | 704 | 167343 | 302 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 2718 | 38.509 | -122.8869 | 7 SPANS LD SIDE OF 13669 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0075948 | OH | Sus | 43452904 | No | 2018 | SEP | Yes | Line to Ground | 1375322 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 3897 | 20180928 | 556 | 183114 | 620 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3100 | 38.5263 | -123.0906 | 2 POLES LD SIDE OF 3897- 5701 KRAMER RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0084428 | OH | Sus | 31410169 | No | 2018 | SEP | Yes | Line to Line | 1381334 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 7123 | 20181004 | 913 | 188135 | 487 | Distribution Circuit | Vegetation | Tree - branch fell on line | 5 | 2362 | 38.6276 | -123.319 | 4/S/LD SIDE OF 7123 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0086729 | OH | Sus | 43496927 | yes | 2018 | OCT | Yes | Line to Line | 1383078 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 79306 | 20181005 | 1608 | 189301 | 644 | Distribution Circuit | 3rd Party | Vehicle | 76 | 30009 | 38.3722 | -122.9117 | FUCO 10135 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0087497 | OH | Sus | 0 | No | 2018 | OCT | Yes | Three Phase Fault | 1383450 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 4895 | 20181015 | 814 | 195273 | 391 | Distribution Circuit | Vegetation | Tree - fell into line | 151 | 10201 | 38.4116 | -122.9752 | 17200 FITZPATRICK | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0090384 | OH | Sus | 0 | No | 2018 | OCT | Yes | Line to Ground | 1385619 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 12035 | 20181015 | 941 | 195402 | 84 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 3948 | 38.4041 | -123.0038 | 17200 FITZPATRICK | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0090444 | OH | Sus | 0 | No | 2018 | OCT | Yes | Line to Ground | 1385711 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | CLOVERDALE-1102 | 42821102 | FUSE | 12907 | 20181016 | 1630 | 196726 | 186 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 744 | 38.7756 | -122.8984 | 1 SPAN LD SIDE FU 12907 | Clear-32-90 F | Conductor, Overhead | On Ground | 18-0091127 | OH | Sus | 0 | No | 2018 | OCT | Yes | Line to Line | 1386174 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE | 2331 | 20181101 | 2045 | 207229 | 475 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 6650 | 38.3653 | -123.0706 | MTR # 1010375927 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0096498 | OH | Sus | 31414807 | No | 2018 | NOV | Yes | Line to Ground | 1389921 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4367 | 20181115 | 934 | 215810 | 641 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 19 | 12179 | 38.5489 | -123.2445 | Arvig/3471: corner of Seaview rd and Ben Wy- Cazadero | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0099985 | OH | Sus | 43540504 | No | 2018 | NOV | Yes | Line to Ground | 1392785 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | OTHER | WIRE-DOWN | 20181123 | 1430 | 223002 | 245 | Distribution Circuit | Vegetation | Tree - branch fell on line | 133 | 15033 | 38.5055 | -122.9245 | Nott/3569: 11025 TERRACE DR | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102605 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1394718 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | OTHER | 13817 | 20181123 | 1212 | 222893 | 243 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 9720 | 38.4641 | -123.013 | MTR#1007360020 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102580 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1394705 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 10179 | 20181124 | 829 | 223504 | 546 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1092 | 38.5405 | -123.1103 | 2 SPANS LD SIDE OF FUCO 10179 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102773 | OH | Sus | 0 | No | 2018 | NOV | Yes | Line to Line | 1394856 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 2989 | 20181124 | 1230 | 223686 | 495 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 1980 | 38.5324 | -123.1351 | INGRAM- JOHN: 6 SPANS L/S C/O 2989 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102798 | OH | Sus | 0 | No | 2018 | NOV | Yes | Line to Ground | 1394876 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | OTHER | 179993 | 20181127 | 1845 | 226105 | 1186 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 32544 | 38.539 | -123.118 | 1 SPAN W/OF 14363 FUSES (NO CUST AFFECTED FROM WIRE DOWN) | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104118 | OH | Sus | 43587192 | yes | 2018 | NOV | Yes | Force Out | 1395680 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1101 | 42091101 | FUSE | 6485 | 20181127 | 1504 | 225875 | 646 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 5168 | 38.4668 | -122.9087 | 7040 GIOVANETTI RD | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104002 | OH | Sus | 31416939 | yes | 2018 | NOV | Yes | Line to Ground | 1395616 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 74315 | 20181128 | 2142 | 226993 | 746 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 14076 | 38.491 | -123.063 | MTR 1007661080 | Clear-32-90 F | Conductor, Overhead | On Ground | 18-0104624 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1395939 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | OTHER | WIRE DOWN 2 SS CGC 217683022935 TWD 634 | 20181201 | 954 | s1397795 | 206 | Distribution Circuit | Equipment Failure/Involved | Overhead | 775 | 22166 | 38.295 | -122.8098 | 2 SS OF CGC 217683022935 TWD 634 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0099363 | OH | Sus | 35027438 | yes | 2018 | DEC | Yes | Open Circuit | 1397795 | CSO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | SONOMA-1104 | 42721104 | OTHER | WIRE DOWN 3 SPANS LD SIDE OF 16123 | 20181203 | 656 | 232256 | 351 | Distribution Circuit | Equipment Failure/Involved | Overhead | 358 | 89562 | 38.2976 | -122.5365 | 3 SPANS LD SIDE OF 16123 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0106340 | OH | Sus | 43605110 | No | 2018 | DEC | Yes | Line to Ground | 1397239 | CSO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | JUMPER | 1 OF 3 HOT WIRES DOWN | 20181205 | 551 | 234007 | 708 | Distribution Circuit | Vegetation | Tree - fell into line | 281 | 72284 | 38.4763 | -122.9537 | 10135 HWY 116 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0107166 | OH | Sus | 43606293 | yes | 2018 | DEC | Yes | Line to Ground | 1397672 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 5152 | 20181207 | 1435 | 235860 | 854 | Distribution Circuit | 3rd Party | Vehicle | 12 | 10248 | 38.5499 | -122.6678 | 4411 PORTER CREEK RD- 6 SPANS SS OF 15033 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0107951 | OH | Sus | 0 | No | 2018 | DEC | Yes | Line to Line | 1398296 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 18253 | 20181216 | 2258 | 241875 | 1086 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 29887 | 38.4731 | -123.0241 | MTR# 1007247410 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0109576 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Three Phase Fault | 1400207 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | JUMPER | WIRE DOWN 1 SPAN LD SIDE OF 7881 | 20181218 | 1320 | 243082 | 312 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 624 | 38.2759 | -122.8784 | INGRAM- JOHN: 2400 FALLON RD | Overcast-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0109883 | OH | Sus | 43617664 | No | 2018 | DEC | Yes | Line to Ground | 1400636 | CSO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE | 2331 | 20181219 | 1626 | 244112 | 239 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 3346 | 38.3653 | -123.0706 | 10 SPANS LD SIDE OF FUCO 2331 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | On Ground | 18-0110031 | OH | Sus | 43619367 | No | 2018 | DEC | Yes | Line to Ground | 1400882 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 5152 | 20181221 | 929 | 245012 | 690 | Distribution Circuit | 3rd Party | Vehicle | 12 | 8280 | 38.5499 | -122.6678 | 2 LD SIDE OF 14389 | Partly Cloudy-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 18-0110229 | OH | Sus | 0 | No | 2018 | DEC | Yes | Three Phase Fault | 1401217 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MONTE RIO-1111 | 42811111 | FUSE | 13717 | 20181222 | 1242 | 245672 | 476 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 476 | 38.4868 | -123.1389 | 2 SPANS LD SIDE OF 13717 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110338 | OH | Sus | 43621075 | No | 2018 | DEC | Yes | Line to Ground | 1401406 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 8493 | 20181224 | 1401 | 246289 | 850 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 33150 | 38.5329 | -123.2714 | MTR#5000024682- MTR#1005387127 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110510 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Three Phase Fault | 1401589 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 64917 | 20181224 | 1747 | 246431 | 210 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 840 | 38.4682 | -123.0049 | 20791 KINGSTON AVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110540 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Ground | 1401619 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | OCB | 1113/2 | 20181224 | 1419 | 246354 | 748 | Distribution Circuit | Vegetation | Tree - fell into line | 4075 | 616898 | 38.4714 | -123.0117 | 16225 DRAKES EXT (2 SPANS L/S/O SW1015 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110474 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Line | 1401552 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | ANNAPOLIS-1101 | 42861101 | FUSE | 7123 | 20181225 | 1017 | 247092 | 1828 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 9140 | 38.6276 | -123.319 | 2 SPANS LD SIDE OF 7123 ON THE SINGLE PHASE OH | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110654 | OH | Sus | 43621732 | No | 2018 | DEC | Yes | Line to Line | 1401736 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 12035 | 20181229 | 2145 | 249537 | 937 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 46850 | 38.4041 | -123.0038 | 12035 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0111090 | OH | Sus | 43623421 | No | 2018 | DEC | Yes | Line to Ground | 1402309 | CSO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 4523 | 20190105 | 1205 | 253950 | 1695 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 27120 | 38.536 | -123.1405 | 10 SP/N/OF FUCO 8971 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0004800 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1403347 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 74315 | 20190105 | 1148 | 253898 | 317 | Distribution Circuit | Vegetation | Tree - branch fell on line | 20 | 6340 | 38.491 | -123.0602 | 2105 CAZADERO HWY | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0004717 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1403271 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | JUMPER | WIRE DOWN | 20190105 | 1700 | 254726 | 304 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 6277 | 38.4877 | -123.0241 | 1 LD OF MTR# 1010344781 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0004905 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Open Circuit | 1403436 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 779 | 20190107 | 553 | 258568 | 427 | Distribution Circuit | Vegetation | Tree - branch fell on line | 45 | 19215 | 38.5971 | -122.9894 | 5356 PALMER CREEK | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005630 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1404080 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 3539 | 20190107 | 817 | 258598 | 358 | Distribution Circuit | Equipment Failure/Involved | Overhead | 13 | 4654 | 38.6225 | -122.8282 | Nott/3569: 3215 RIO LINDO AVE | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on object | 19-0005658 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Force Out | 1404097 | CSO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 4877 | 20190109 | 2022 | 262074 | 360 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 7920 | 38.3821 | -122.555 | 9100 BENNETT VALLEY RD | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0007176 | OH | Sus | 43628608 | yes | 2019 | JAN | Yes | Line to Ground | 1405010 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 1939 | 20190109 | 815 | 261351 | 1965 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 14945 | 38.4782 | -122.9384 | 7/S/LD/SIDE OF 1939 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0006750 | OH | Sus | 43628212 | yes | 2019 | JAN | Yes | Line to Ground | 1404806 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1101 | 43071101 | FUSE | 15877 | 20190115 | 810 | 265392 | 417 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1668 | 38.4006 | -122.5129 | 1 SPAN SS OF 17849 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0008952 | OH | Sus | 31421981 | yes | 2019 | JAN | Yes | Line to Line | 1406295 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | TRIP-SAVER | 891 | 20190118 | 1924 | 276277 | 1156 | Distribution Circuit | Vegetation | Tree - branch fell on line | 94 | 16009 | 38.3901 | -122.8854 | Moore- S/4308: 1175 FURLONG RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011979 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408315 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 7697 | 20190118 | 819 | 275325 | 1762 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 14096 | 38.5161 | -123.0648 | 2 SPANS SS OF MTR#1010252611 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011745 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Three Phase Fault | 1408189 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 487 | 20190118 | 816 | 275313 | 675 | Distribution Circuit | Vegetation | Tree - branch fell on line | 91 | 61425 | 38.4641 | -123.0115 | 3 WAY CORNER FEEDING 13839 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011674 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408157 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 6121 | 20190118 | 613 | 275193 | 2122 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 29708 | 38.5399 | -122.6386 | 6200 GATES RD | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0011761 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408201 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 4661 | 20190119 | 1937 | 276976 | 1478 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 65032 | 38.5078 | -122.9895 | 15480 OLD RIVER RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012175 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Ground | 1408527 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | TRIP-SAVER | 999 | 20190120 | 658 | 277101 | 307 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 24253 | 38.422 | -122.954 | 1 SPAN LOADSIDE TO EAST | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012514 | OH | Sus | 31422641 | yes | 2019 | JAN | Yes | Line to Ground | 1408863 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 66006 | 20190131 | 1533 | 284936 | 802 | Distribution Circuit | 3rd Party | Vehicle | 2077 | 489947 | 38.4055 | -122.9478 | 1 SPAN FROM 16575 TWDS 1617 ON MAINLINE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0016368 | OH | Sus | 0 | No | 2019 | JAN | Yes | Multi-Fault | 1411026 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 560 | 20190201 | 1830 | 285643 | 1273 | Distribution Circuit | Vegetation | Tree - branch fell on line | 229 | 42451 | 38.5562 | -123.3034 | 3 SPANS LD SIDE OF 560- 5 SPANS SOURCE SIDE OF MTR#1008863028- 25050 HWY 1 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0016752 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411213 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 5531 | 20190203 | 1318 | 289087 | 1523 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 25 | 8875 | 38.6773 | -123.0625 | 1 N/OF CGC 216848037078 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0017591 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1412003 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MONTE RIO-1111 | 42811111 | FUSE | 7385 | 20190219 | 1444 | 318985 | 521 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 39 | 20319 | 38.4831 | -123.1475 | 1 SS OF 13717 | Clear-32-90 F | Conductor, Overhead | On Ground | 19-0026195 | OH | Sus | 43682176 | yes | 2019 | FEB | Yes | Line to Ground | 1419042 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | JUMPER | 2 SPANS S/S MTR 1009647577 | 20190221 | 1339 | 320691 | 511 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 1022 | 38.4044 | -122.9491 | MTR 1009647577 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026982 | OH | Sus | 43683462 | yes | 2019 | FEB | Yes | Force Out | 1419474 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | TRIP-SAVER | 891 | 20190225 | 1712 | 323376 | 322 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 19320 | 38.3901 | -122.8854 | 300 RYAN RANCH RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0027973 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1420084 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 12717 | 20190225 | 1422 | 323197 | 499 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3992 | 38.4689 | -123.0521 | LD SIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0027941 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Multi-Fault | 1420066 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 6759 | 20190225 | 2204 | 323590 | 1100 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 25300 | 38.4634 | -123.0122 | 4 SPANS LD SIDE OF 6759 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0028045 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1420155 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 12061 | 20190301 | 938 | 328752 | 1667 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1667 | 38.484 | -122.9147 | 2 LD SIDE OF FUCO 12061- 8075 MARTINELLI RD | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0029698 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Line | 1421270 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 3041 | 20190302 | 943 | 329520 | 391 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 5083 | 38.3811 | -122.9885 | MTR#1009712084 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0030047 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Line | 1421533 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | JUMPER | WIRE DOWN | 20190303 | 808 | 330095 | 532 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2422 | 38.4654 | -122.9213 | Nott/3569: 7220 GIOVANETTI RD | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0030256 | OH | Sus | 0 | No | 2019 | MAR | Yes | Line to Ground | 1421713 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | RECLOSER | 132 | 20190304 | 1836 | 331076 | 416 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1019 | 88845 | 38.2647 | -122.8057 | KOTULA- JON/4343: #2 W of 2322 Fallon Two Rock RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0030607 | OH | Sus | 43690161 | No | 2019 | MAR | Yes | Multi-Fault | 1421920 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 6693 | 20190305 | 2205 | 331991 | 1224 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 34008 | 38.5562 | -123.3034 | AT SW 4535 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031021 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Multi-Fault | 1422228 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | JUMPER | OJ'S AT 14520 SOLARIDGE RD | 20190305 | 1702 | 331716 | 1290 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2956 | 38.5012 | -123.0093 | 14520 SOLARIDGE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0030957 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1422083 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 634 | 20190306 | 1523 | 333052 | 298 | Distribution Circuit | Equipment Failure/Involved | Overhead | 50 | 9175 | 38.2982 | -122.8208 | INGRAM- 4253: 3 SPANS L/S C/O 4021 ON MAIN LINE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031418 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1422369 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 4523 | 20190306 | 238 | 332320 | 873 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 13968 | 38.536 | -123.1405 | 4 LD SIDE OF FUSES | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031178 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Multi-Fault | 1422239 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | TRIP-SAVER | 7401 | 20190306 | 10 | 332044 | 655 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 43230 | 38.5037 | -122.9487 | 16115 TWD 12997 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031066 | OH | Sus | 43690689 | yes | 2019 | MAR | Yes | Line to Line | 1422176 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 320 | 20190306 | 12 | 332049 | 803 | Distribution Circuit | Vegetation | Tree - fell into line | 147 | 118041 | 38.4989 | -123.0211 | 15105 OLD CAZADERO HWY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031043 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1422154 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | OTHER | WIRE DOWN BET 14079 & REG 11047 | 20190306 | 17 | 332067 | 828 | Distribution Circuit | Equipment Failure/Involved | Overhead | 193 | 86639 | 38.3448 | -123.0184 | BETWEEN FUCO 14079 & REGS 11047 | Overcast-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031046 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Force Out | 1422157 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | RECLOSER | 132 | 20190308 | 615 | 334071 | 339 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1019 | 213505 | 38.2647 | -122.8057 | Kikuchi/2272: 5488 Middle Rd- Fallon | Partly Cloudy-Fog-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0031891 | OH | Sus | 43692407 | No | 2019 | MAR | Yes | Line to Ground | 1422702 | CSO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 616 | 20190312 | 1740 | 337800 | 1268 | Distribution Circuit | Vegetation | Tree - branch fell on line | 224 | 59142 | 38.3102 | -122.8518 | Deignan- Pat/3571: 17400 VALLEY FORD RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033176 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1423638 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 861496 | 20190312 | 729 | 336788 | 666 | Distribution Circuit | Vegetation | Tree - branch fell on line | 90 | 29751 | 38.358 | -122.5256 | 2600 LONDON RANCH RD: JACK LONDON STATE PARK | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0032881 | OH | Sus | 31428568 | yes | 2019 | MAR | Yes | Line to Ground | 1423455 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1102 | 42091102 | FUSE | 13669 | 20190312 | 1414 | 337355 | 395 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3555 | 38.509 | -122.8869 | Rendon/4754: 7 SPANS LOAD SIDE C/O 13669 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033120 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Three Phase Fault | 1423602 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | TRIP-SAVER | 841 | 20190312 | 1858 | 337929 | 1092 | Distribution Circuit | Vegetation | Tree - fell into line | 133 | 18871 | 38.5087 | -122.9261 | MTR# 1007934935 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033221 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Line | 1423680 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | JUMPER | WIRE DOWN | 20190312 | 1823 | 337676 | 1185 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 13035 | 38.5423 | -123.0016 | 2 SS OF MTR 1009125135 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0033188 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Open Circuit | 1423650 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4543 | 20190320 | 620 | 343433 | 474 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 4740 | 38.5893 | -123.3034 | 34285 KRUSE RANCH RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0035334 | OH | Sus | 43712011 | yes | 2019 | MAR | Yes | Line to Line | 1425288 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 134 | 20190322 | 1720 | 345501 | 1269 | Distribution Circuit | Vegetation | Tree - fell into line | 229 | 290601 | 38.5588 | -123.2702 | 22400 TIMBER COVE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0036204 | OH | Sus | 43714490 | No | 2019 | MAR | Yes | Line to Ground | 1425755 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | RECLOSER | 322 | 20190322 | 2323 | 345622 | 982 | Distribution Circuit | Vegetation | Tree - fell into line | 375 | 27672 | 38.3868 | -122.8901 | DOEDING- D 2411: 11266 BODEGA HWY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0036248 | OH | Sus | 31430272 | No | 2019 | MAR | Yes | Line to Ground | 1425800 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 17803 | 20190402 | 617 | 352120 | 943 | Distribution Circuit | Vegetation | Tree - branch fell on line | 8 | 7544 | 38.5216 | -123.0968 | MTR# 1009059338 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0039053 | OH | Sus | 43726355 | yes | 2019 | APR | Yes | Line to Line | 1427812 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1102 | 42821102 | RECLOSER | 156 | 20190405 | 1834 | 354626 | 843 | Distribution Circuit | 3rd Party | Vehicle | 590 | 204502 | 38.7991 | -122.9913 | MTR#1009945504 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0040219 | OH | Sus | 0 | No | 2019 | APR | Yes | Line to Ground | 1428509 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1043 | 20190410 | 2034 | 358486 | 348 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 696 | 38.5068 | -122.915 | LAST SPAN ON TAP | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0041464 | OH | Sus | 43736603 | yes | 2019 | APR | Yes | Line to Line | 1429522 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 4619 | 20190414 | 1058 | 360508 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2758 | 38.4867 | -123.015 | 1 SPAN LD SIDE OF 4619 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0042307 | OH | Sus | 43738669 | No | 2019 | APR | Yes | Line to Ground | 1430151 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | OTHER | WIRE DOWN SS 3891 | 20190417 | 626 | 362260 | 602 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 43786 | 38.5158 | -123.065 | SS OF 3891 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0043092 | OH | Sus | 43742413 | No | 2019 | APR | Yes | Line to Ground | 1430638 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1102 | 42891102 | FUSE | 2273 | 20190419 | 1138 | 363815 | 1434 | Distribution Circuit | Vegetation | Tree - branch fell on line | 22 | 31548 | 38.736 | -122.8364 | 13 SPANS LD SIDE OF FUSES | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0044402 | OH | Sus | 31434962 | No | 2019 | APR | Yes | Multi-Fault | 1431587 | CAW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 261774 | 20190425 | 1325 | 368152 | 1133 | Distribution Circuit | Vegetation | Tree - fell into line | 185 | 47067 | 38.3787 | -122.5531 | DOEDING- D 2411: 5761 SONOMA MTN RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0046198 | OH | Sus | 0 | No | 2019 | APR | Yes | Line to Ground | 1432849 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | OTHER | WIRE DOWN 1 N/OF TSV 999 | 20190502 | 2349 | 372747 | 1080 | Distribution Circuit | Vegetation | Tree - fell into line | 386 | 398448 | 38.4225 | -122.9543 | 1 POLE N/OF TRIPSAVER 999 ON THE MAINLINE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0048491 | OH | Sus | 0 | No | 2019 | MAY | Yes | Line to Ground | 1434256 | PW | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1101 | 42571101 | FUSE | 13545 | 20190503 | 1242 | 373271 | 361 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 361 | 38.3856 | -122.9033 | LD SIDE OF 13545 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0048689 | OH | Sus | 0 | No | 2019 | MAY | Yes | Line to Ground | 1434421 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 4571 | 20190515 | 2136 | 381338 | 1134 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 2268 | 38.1681 | -122.8937 | MOORE DAVE / 3612: 7 SPAN LOAD SIDE 4571 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052336 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1436978 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1102 | 43071102 | FUSE | 13499 | 20190515 | 1731 | 381292 | 1199 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 8393 | 38.3959 | -122.472 | 2 LD SIDE OF 13499 | Partly Cloudy-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052294 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Multi-Fault | 1436935 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 769 | 20190515 | 902 | 380638 | 353 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 10590 | 38.5963 | -122.9146 | 3000 WALLACE CREEK RD | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052045 | OH | Sus | 31440370 | yes | 2019 | MAY | Yes | Line to Line | 1436809 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | OTHER | WIRE DOWN 5 P/SS OF CGC# 217282033175 | 20190515 | 2131 | 381716 | 741 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 27780 | 38.5731 | -122.9595 | 5 P/SS/OF CGC# 217272033175 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052480 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1437125 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 560 | 20190515 | 2022 | 381450 | 985 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 26595 | 38.5562 | -123.3034 | 23350 HWY 1- 2 SPANS LD SIDE OF LR 560 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052320 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1436963 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 12997 | 20190515 | 1217 | 380874 | 358 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 1618 | 38.5031 | -122.9544 | 1ST & 3RD SPAN LD SIDE OF 12995 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052153 | OH | Sus | 43781826 | yes | 2019 | MAY | Yes | Line to Line | 1436873 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 12997 | 20190515 | 2041 | 381400 | 935 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 12155 | 38.5031 | -122.9544 | EOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052350 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Multi-Fault | 1436992 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 18581 | 20190515 | 1716 | 381156 | 235 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 1410 | 38.3843 | -122.8765 | 1715 W. SEXTON RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052286 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1436930 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 5831 | 20190515 | 2117 | 381504 | 1248 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 8736 | 38.3724 | -122.8716 | 4 SPANS LD SIDE OF FUCO 5831- 1815 SEXTON RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052456 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Line | 1437101 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 6217 | 20190516 | 1451 | 382658 | 1411 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 6378 | 38.5868 | -122.9279 | 1ST POLE OFF TAP FEEDING 17003 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052984 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Line | 1437383 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | FUSE | 649 | 20190516 | 2050 | 383027 | 1063 | Distribution Circuit | Vegetation | Tree - branch fell on line | 4 | 4252 | 38.5498 | -122.7115 | 2/S/LD SIDE OF 649 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053028 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1437419 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 5531 | 20190516 | 1430 | 382616 | 357 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 7157 | 38.6773 | -123.0625 | Nott/3569: 9 SPANS LOADSIDE 12501 SKAGGS SPRINGS RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052879 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1437334 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1101 | 42091101 | FUSE | 1003 | 20190518 | 1508 | 384343 | 742 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 46272 | 38.4763 | -122.9069 | 8350 MARTINELLI RD | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053682 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1437906 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 256 | 20190518 | 1119 | 384193 | 566 | Distribution Circuit | Vegetation | Tree - fell into line | 1592 | 143726 | 38.4698 | -123.0145 | 3 SPANS E/OF SW 7521 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053638 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Three Phase Fault | 1437882 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 669275 | 20190519 | 833 | 384977 | 615 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5535 | 38.4105 | -122.9493 | 14500 GRATON RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0053896 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1438107 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1102 | 42821102 | RECLOSER | 262 | 20190520 | 110 | 385716 | 866 | Distribution Circuit | Equipment Failure/Involved | Overhead | 359 | 99419 | 38.7977 | -122.991 | MAIN LINE 1 SPAN N/OF FUCO 15675 | Clear-32-90 F | Pole-Wood | Broken, wire on object | 19-0054150 | OH | Sus | 0 | No | 2019 | MAY | Yes | Multi-Fault | 1438348 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | TRIP-SAVER | 6751 | 20190521 | 6 | 386610 | 794 | Distribution Circuit | Vegetation | Tree - fell into line | 134 | 26473 | 38.592 | -122.9622 | FUCO 10905 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0054664 | OH | Sus | 31443410 | yes | 2019 | MAY | Yes | Line to Ground | 1438695 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | RECLOSER | 38514 | 20190521 | 600 | 386640 | 580 | Distribution Circuit | Vegetation | Tree - fell into line | 547 | 181630 | 38.5056 | -122.9307 | AT FUCO 2103 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0054678 | OH | Sus | 43790709 | yes | 2019 | MAY | Yes | Multi-Fault | 1438704 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | RECLOSER | 214 | 20190604 | 531 | 397039 | 322 | Distribution Circuit | Equipment Failure/Involved | Overhead | 397 | 67215 | 38.5031 | -122.7355 | DOEDING- D 2411: 1990 mark west spring rd | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0062328 | OH | Sus | 31450708 | yes | 2019 | JUN | Yes | Line to Line | 1445053 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1102 | 42891102 | OTHER | 732035 | 20190607 | 1310 | 400775 | 721 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4326 | 38.693 | -122.8855 | 13 SPANS LD SIDE OF 732035 | Clear-32-90 F | Conductor, Overhead | On Ground | 19-0064293 | OH | Sus | 0 | yes | 2019 | JUN | Yes | Line to Ground | 1446494 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | OTHER | WIRE DOWN MAINLINE @ 26150 HWY 1 | 20190611 | 606 | 405019 | 306 | Distribution Circuit | Vegetation | Tree - branch fell on line | 149 | 45571 | 38.237 | -122.9056 | MAINLINE PAST FIRST HARD TAP LD SIDE OF LR 148 | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 19-0065733 | OH | Sus | 0 | yes | 2019 | JUN | Yes | Open Circuit | 1447875 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | OCB | 1121/2 | 20190626 | 1301 | 429784 | 423 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 639 | 111069 | 38.5408 | -123.2237 | 2559 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0072290 | OH | Sus | 31455526 | No | 2019 | JUN | Yes | Line to Ground | 1452889 | CAW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | RECLOSER | 658 | 20190704 | 2000 | 441126 | 481 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 63011 | 38.4451 | -122.9104 | AT FUCO 12153 ON MAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0074656 | OH | Sus | 43867987 | No | 2019 | JUL | Yes | Line to Ground | 1454364 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 64758 | 20190705 | 352 | 441198 | 622 | Distribution Circuit | Vegetation | Tree - fell into line | 282 | 72328 | 38.5089 | -123.0696 | Arvig/3471: 18595 King Ridge rd- Cazadero | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0074675 | OH | Sus | 43867994 | No | 2019 | JUL | Yes | Multi-Fault | 1454386 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | SONOMA-1104 | 42721104 | JUMPER | WIRE DOWN 1 SPAN SS OF 950789 TWD EAST | 20190715 | 749 | 450516 | 427 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2348 | 38.3266 | -122.568 | 1 SPAN SOURCE SIDE S/B 950789 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0077351 | OH | Sus | 43879274 | No | 2019 | JUL | Yes | Line to Ground | 1456283 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 13193 | 20190720 | 928 | 462890 | 283 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1698 | 38.538 | -122.6472 | 325 BODMER LN | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0079444 | OH | Sus | 43890719 | No | 2019 | JUL | Yes | Line to Line | 1457563 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2269 | 20190728 | 49 | 473714 | 1106 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 26544 | 38.5183 | -122.6032 | KIKUCHI/2272: 8100 Tarwater Rd (Neal Creek Rd) | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0081895 | OH | Sus | 43899665 | No | 2019 | JUL | Yes | Line to Line | 1459187 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 6759 | 20190812 | 1210 | 503677 | 296 | Distribution Circuit | Vegetation | Tree - fell into line | 150 | 8205 | 38.4634 | -123.0122 | 9725 MAIN ST | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0086913 | OH | Sus | 43919153 | No | 2019 | AUG | Yes | Line to Line | 1462464 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | RINCON-1103 | 43321103 | OCB | 1103/2 | 20190812 | 2112 | 504768 | 411 | Distribution Circuit | 3rd Party | Vehicle | 2302 | 165663 | 38.4901 | -122.6661 | FUCO 14017 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0087094 | OH | Sus | 0 | No | 2019 | AUG | Yes | Three Phase Fault | 1462529 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 433 | 20190822 | 928 | 530707 | 938 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 30954 | 38.5091 | -122.9283 | 12300 WESTSIDE RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0090865 | OH | Sus | 43933640 | No | 2019 | AUG | Yes | Line to Line | 1465065 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER | 1991 | 20190823 | 1511 | 534716 | 603 | Distribution Circuit | Vegetation | Tree - fell into line | 51 | 30753 | 38.5445 | -122.9849 | 19000 SWEET WATER- MTR 1009796848 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0091633 | OH | Sus | 43937498 | No | 2019 | AUG | Yes | Multi-Fault | 1465414 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 801 | 20190830 | 1751 | 549224 | 328 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 36408 | 38.5165 | -122.9962 | 17300 WATSON RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0094251 | OH | Sus | 43942854 | No | 2019 | AUG | Yes | Line to Line | 1466920 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 1593 | 20190905 | 1900 | 556913 | 804 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 3216 | 38.4742 | -122.9221 | MTR# 1009127372 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0095841 | OH | Sus | 0 | No | 2019 | SEP | Yes | None | 1467982 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 903030 | 20190907 | 1736 | 562175 | 468 | Distribution Circuit | 3rd Party | Vehicle | 22 | 10296 | 38.382 | -122.5549 | 9050 BENNETT VALLEY RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0096476 | OH | Sus | 0 | yes | 2019 | SEP | Yes | Line to Ground | 1468388 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 12997 | 20190907 | 1700 | 562147 | 825 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7667 | 38.5031 | -122.9544 | 2 SPANS LOADSIDE 12997 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0096473 | OH | Sus | 0 | yes | 2019 | SEP | Yes | Line to Line | 1468384 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 12029 | 20190909 | 1253 | 564574 | 457 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 5484 | 38.3943 | -122.9647 | 1009911436 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0096900 | OH | Sus | 31471181 | No | 2019 | SEP | Yes | Line to Line | 1468760 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 1595 | 20190912 | 1846 | 576529 | 469 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2345 | 38.477 | -122.9333 | 1ST POLE LD SIDE OF 1595 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0098493 | OH | Sus | 0 | No | 2019 | SEP | Yes | Line to Line | 1469626 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 6175 | 20190915 | 1744 | 583416 | 1561 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 3122 | 38.5093 | -122.9878 | 3 SPANS LOADSIDE OF 6175 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0099273 | OH | Sus | 31471783 | No | 2019 | SEP | Yes | Line to Ground | 1470159 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | SANTA ROSA A-1111 | 42151111 | OTHER | WIRE DOWN 4324 MT TAYLOR RD | 20190916 | 719 | 583937 | 807 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 59231 | 38.4207 | -122.6759 | AT CUTOUTS 58425- WIRE DOWN 4324 MT TAYLOR RD | Partly Cloudy-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0099397 | OH | Sus | 0 | yes | 2019 | SEP | Yes | Open Circuit | 1470270 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 5531 | 20190924 | 627 | 608093 | 711 | Distribution Circuit | 3rd Party | Vehicle | 25 | 9853 | 38.6773 | -123.0625 | 2 E/OF 9485 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0102853 | OH | Sus | 0 | No | 2019 | SEP | Yes | Three Phase Fault | 1472351 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FULTON-1102 | 42561102 | FUSE | 751 | 20190928 | 1517 | 627800 | 333 | Distribution Circuit | Vegetation | Tree - branch fell on line | 35 | 11655 | 38.6311 | -122.77 | 2 LD SIDE OF CGC217831935454 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0105006 | OH | Sus | 0 | yes | 2019 | SEP | Yes | Line to Ground | 1473781 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MIRABEL-1101 | 42091101 | FUSE | 15423 | 20190928 | 1047 | 626035 | 581 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 581 | 38.4734 | -122.9015 | 1 SPAN LD SIDE OF FUCO 15423 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0104964 | OH | Sus | 0 | yes | 2019 | SEP | Yes | Line to Ground | 1473748 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 4537 | 20190929 | 2056 | 629460 | 1058 | Distribution Circuit | Equipment Failure/Involved | Overhead | 39 | 11856 | 38.5247 | -123.2648 | 1 SP LD SIDE OF C/OUT 4537 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0105272 | OH | Sus | 43973890 | No | 2019 | SEP | Yes | Line to Line | 1474004 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 14413 | 20191015 | 2152 | 659986 | 457 | Distribution Circuit | Animal | Bird found | 5 | 2285 | 38.2702 | -122.7834 | 3 SPANS SOUTH FO FUCO 14413 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0112113 | OH | Sus | 0 | No | 2019 | OCT | Yes | Line to Ground | 1480298 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | SONOMA-1104 | 42721104 | FUSE | 9667 | 20191028 | 2055 | 692622 | 1360 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 5440 | 38.2862 | -122.5456 | 7 SPANS LD SIDE OF 9667 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0118244 | OH | Sus | 0 | yes | 2019 | OCT | Yes | Line to Ground | 1487251 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1101 | 43071101 | OTHER | WIRE DOWN @ 10453 SLATTERY RD | 20191101 | 844 | 697294 | 734 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 18208 | 38.3957 | -122.5442 | 10453 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0119903 | OH | Sus | 0 | No | 2019 | NOV | Yes | Force Out | 1488674 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1109 | 42631109 | FUSE | 2607 | 20191117 | 2334 | 708862 | 460 | Distribution Circuit | 3rd Party | Vehicle | 56 | 25760 | 38.1901 | -122.6621 | 4665 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0125541 | OH | Sus | 0 | No | 2019 | NOV | Yes | Line to Line | 1491988 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 134 | 20191130 | 1338 | 724304 | 443 | Distribution Circuit | Vegetation | Tree - fell into line | 232 | 48508 | 38.5588 | -123.2702 | BETWEEN 9503 & 69993 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0131419 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Force Out | 1496120 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 4663 | 20191204 | 2223 | 730171 | 893 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 7144 | 38.4983 | -122.9937 | 16455 NEELY RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0133684 | OH | Sus | 44112689 | yes | 2019 | DEC | Yes | Line to Ground | 1497754 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | TRIP-SAVER | 4859 | 20191207 | 1320 | 732850 | 275 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 13200 | 38.4755 | -122.9527 | LD SIDE OF 4859 | Rain | Conductor, Overhead | Broken, wire on ground | 19-0134854 | OH | Sus | 0 | yes | 2019 | DEC | Yes | Multi-Fault | 1498654 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 1955 | 20191207 | 105 | 732105 | 801 | Distribution Circuit | Vegetation | Tree - fell into line | 161 | 128961 | 38.3879 | -122.9715 | R/O 2807 JOY RD | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0134662 | OH | Sus | 0 | yes | 2019 | DEC | Yes | Line to Ground | 1498414 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1997 | 20191208 | 1607 | 733944 | 424 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 47488 | 38.502 | -123.0239 | Nott/3569: 15607 OLD CAZADERO RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0135069 | OH | Sus | 44115438 | No | 2019 | DEC | Yes | Line to Line | 1498874 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 2027 | 20191214 | 36 | 738854 | 549 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 14823 | 38.5191 | -122.98 | 14734 EAGLESNEST LANE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0136527 | OH | Sus | 44122670 | No | 2019 | DEC | Yes | Line to Ground | 1500529 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | OTHER | WIRE DOWN SS MTR 1005515502 | 20200102 | 1314 | 753833 | 247 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 757 | 38.2666 | -122.7246 | SS OF MTR# 1005515502 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0004544 | OH | Sus | 44143173 | No | 2020 | JAN | Yes | Open Circuit | 1503829 | CSO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | OTHER | WIRE DOWN @ LR 213984 | 20200114 | 615 | 760582 | 700 | Distribution Circuit | 3rd Party | Vehicle | 799 | 219087 | 38.2986 | -122.8223 | SW POLE 1605/ IMMEDIATELY W/OF LR 213894 | Partly Cloudy-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 20-0008362 | OH | Sus | 44155347 | No | 2020 | JAN | Yes | Line to Ground | 1506094 | PW | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | OCB | 1113/2 | 20200129 | 641 | 772282 | 573 | Distribution Circuit | Vegetation | Tree - fell into line | 3919 | 925170 | 38.4714 | -123.0117 | DOEDING- D 2411: 17620 hwy 116 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0014789 | OH | Sus | 0 | No | 2020 | JAN | Yes | Line to Ground | 1509946 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 3903 | 20200131 | 1830 | 774693 | 585 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1170 | 38.6019 | -123.0033 | 3RD AND 5TH POLE LD SIDE OF FUCO 3903 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0016080 | OH | Sus | 31488336 | No | 2020 | JAN | Yes | Line to Ground | 1510856 | CAW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | JUMPER | WIRE DOWN 1 SPAN SS OF 6493 | 20200202 | 1602 | 775992 | 352 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2022 | 38.5194 | -122.958 | 1 SPAN SS OF 6493 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0016366 | OH | Sus | 44175142 | yes | 2020 | FEB | Yes | Line to Ground | 1511130 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 616 | 20200203 | 608 | 776169 | 495 | Distribution Circuit | 3rd Party | Vehicle | 225 | 69571 | 38.3102 | -122.8518 | NOONAN 3469: 13800 HWY 1 VALLEY FORD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0016440 | OH | Sus | 0 | No | 2020 | FEB | Yes | Line to Ground | 1511196 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | FUSE | 14593 | 20200206 | 433 | 778902 | 462 | Distribution Circuit | 3rd Party | Vehicle | 9 | 4158 | 38.5183 | -122.7205 | 1/P/S OF 14593 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0017902 | OH | Sus | 0 | No | 2020 | FEB | Yes | Line to Line | 1512222 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1102 | 42891102 | FUSE | 523 | 20200222 | 2112 | 800864 | 302 | Distribution Circuit | Equipment Failure/Involved | Overhead | 29 | 8555 | 38.6573 | -122.8317 | FIRST SPAN LOADSIDE FUCO 523 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0024981 | OH | Sus | 44208080 | No | 2020 | FEB | Yes | Line to Ground | 1517113 | CSO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | OTHER | WIRE DOWN ON GUY WIRE | 20200224 | 936 | 802457 | 306 | Distribution Circuit | Vegetation | Tree - branch fell on line | 107 | 31962 | 38.4771 | -122.9557 | 1 W/OF 8591 | Clear-32-90 F | Other | Broken, wire on object | 20-0025171 | OH | Sus | 0 | No | 2020 | FEB | Yes | Open Circuit | 1517314 | NON | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24550 | 20200327 | 949 | 868253 | 419 | Distribution Circuit | 3rd Party | Vehicle | 220 | 49449 | 38.5793 | -122.878 | CGC 217513332799 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on object | 20-0036610 | OH | Sus | 0 | No | 2020 | MAR | Yes | Line to Line | 1524206 | PW | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | CLOVERDALE-1102 | 42821102 | FUSE | 6953 | 20200404 | 1123 | 882264 | 374 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5236 | 38.772 | -122.9619 | MTR# 1009074665 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0038407 | OH | Sus | 44281564 | No | 2020 | APR | Yes | Line to Ground | 1525243 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | OCB | 1103/2 | 20200501 | 2042 | 905621 | 802 | Distribution Circuit | Animal | Bird found | 1460 | 233968 | 38.3098 | -122.7316 | SS SPAN TO SW 6589 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0046525 | OH | Sus | 44308068 | No | 2020 | MAY | Yes | Line to Line | 1530297 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 2439 | 20200502 | 1517 | 905875 | 400 | Distribution Circuit | Vegetation | Tree - branch fell on line | 2 | 800 | 38.2165 | -122.9231 | BET DILLON BEACH RD & HWY 1 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0046620 | OH | Sus | 31501777 | No | 2020 | MAY | Yes | Line to Ground | 1530383 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | OTHER | WIRE DOWN FT ROSS RD E/O NEISTRATH | 20200503 | 2356 | 906441 | 598 | Distribution Circuit | Equipment Failure/Involved | Overhead | 189 | 96796 | 38.5294 | -123.1809 | FT ROSS RD E/O NEISTRATH | Clear-32-90 F | Insulator | Broken, wire on ground | 20-0046772 | OH | Sus | 31501929 | No | 2020 | MAY | Yes | Open Circuit | 1530504 | INS | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 6217 | 20200505 | 1537 | 907643 | 473 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 16 | 7568 | 38.5868 | -122.9279 | 17003 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0047617 | OH | Sus | 44311357 | No | 2020 | MAY | Yes | Line to Ground | 1530908 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | RECLOSER | 322 | 20200506 | 527 | 907845 | 739 | Distribution Circuit | 3rd Party | Vehicle | 725 | 116519 | 38.3868 | -122.8901 | 11371 BODEGA HWY | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0047688 | OH | Sus | 0 | No | 2020 | MAY | Yes | Line to Ground | 1530955 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 240 | 20200511 | 1350 | 911388 | 224 | Distribution Circuit | Vegetation | Tree - branch fell on line | 811 | 91045 | 38.4715 | -123.0471 | 2 SPANS SS OF 969182 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0049155 | OH | Sus | 44320983 | yes | 2020 | MAY | Yes | Line to Ground | 1531958 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | TRIP-SAVER | 891 | 20200605 | 1818 | 932236 | 587 | Distribution Circuit | Vegetation | Tree - branch fell on line | 95 | 8081 | 38.3901 | -122.8854 | AT FUCO 13903 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0058317 | OH | Sus | 44344353 | yes | 2020 | JUN | Yes | Line to Line | 1537559 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24918 | 20200606 | 1440 | 932841 | 260 | Distribution Circuit | Vegetation | Tree - branch fell on line | 187 | 48620 | 38.5914 | -122.92 | 5/S/LS OF LR 24918 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0058447 | OH | Sus | 44344548 | yes | 2020 | JUN | Yes | Line to Ground | 1537679 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 429 | 20200606 | 1411 | 932799 | 564 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 12933 | 38.4734 | -123.0226 | INGRAM- 4253: 21940 RUSSIAN RIVER AVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0058466 | OH | Sus | 44344546 | yes | 2020 | JUN | Yes | Line to Ground | 1537696 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | RECLOSER | 70288 | 20200608 | 523 | 933832 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 156 | 64601 | 38.5287 | -123.1574 | 4 SPANS WEST OF 4167 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0058722 | OH | Sus | 31505342 | yes | 2020 | JUN | Yes | Line to Ground | 1537937 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | OTHER | WIRE DOWN | 20200612 | 1603 | 938024 | 221 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 187 | 40460 | 38.5909 | -122.9588 | 10/SP/SS/OF 6751 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0060729 | OH | Sus | 0 | yes | 2020 | JUN | Yes | Open Circuit | 1539345 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | OTHER | WIRE DOWN 6 SPANS SS OF 16347 | 20200619 | 20 | 942318 | 547 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 7868 | 38.6413 | -122.92 | 6 SPANS SS OF 16347 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0062919 | OH | Sus | 44360218 | No | 2020 | JUN | Yes | Line to Ground | 1540854 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 467555 | 20200625 | 1922 | 947557 | 568 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 3408 | 38.3966 | -122.9397 | 2/P/LD SIDE OF 467555 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0065110 | OH | Sus | 0 | No | 2020 | JUN | Yes | Line to Line | 1542547 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | OTHER | WIRE DOWN 1/SPAN SS OF 17045 | 20200627 | 334 | 948545 | 545 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1463 | 147943 | 38.3007 | -122.7451 | GRACIE- RICHARD: EP 1 Span SS of 17045 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0065628 | OH | Sus | 0 | No | 2020 | JUN | Yes | Open Circuit | 1542852 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | FUSE | 2375 | 20200628 | 145 | 949173 | 689 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 11713 | 38.5423 | -122.7203 | 1 SPAN LOAD SIDE | Clear | Conductor, Overhead | Broken, wire on ground | 20-0065770 | OH | Sus | 44368200 | No | 2020 | JUN | Yes | Line to Ground | 1542990 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24918 | 20200629 | 510 | 949651 | 643 | Distribution Circuit | 3rd Party | Vehicle | 171 | 109953 | 38.5914 | -122.92 | NOONAN 3469: 2 POLES SOURCE SIDE OF C/O POLE 6217 MILL CREEK RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0065990 | OH | Sus | 0 | No | 2020 | JUN | Yes | Line to Line | 1543136 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24918 | 20200705 | 117 | 957989 | 561 | Distribution Circuit | Vegetation | Tree - fell into line | 187 | 104907 | 38.5914 | -122.92 | 9/LD SIDE OF 6217 ON MAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0068422 | OH | Sus | 44377964 | No | 2020 | JUL | Yes | Line to Ground | 1544442 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 861496 | 20200710 | 359 | 961366 | 549 | Distribution Circuit | Vegetation | Tree - fell into line | 89 | 28253 | 38.358 | -122.5256 | 5 SPANS SS OF 6215 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0070341 | OH | Sus | 31508158 | No | 2020 | JUL | Yes | Line to Ground | 1545573 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 636 | 20200805 | 719 | 978986 | 775 | Distribution Circuit | 3rd Party | Vehicle | 141 | 31185 | 38.2618 | -122.7158 | at FUCO 12207 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0079813 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Ground | 1551763 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | SALMON CREEK-1101 | 43161101 | FUSE | 6059 | 20200805 | 142 | 978939 | 565 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 5554 | 38.3558 | -122.9804 | 1665 TANNERY CREEK RD | Overcast-Fog-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0079795 | OH | Sus | 44409889 | yes | 2020 | AUG | Yes | Line to Ground | 1551752 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | RECLOSER | 36536 | 20200806 | 357 | 979836 | 784 | Distribution Circuit | 3rd Party | Vehicle | 802 | 135640 | 38.3142 | -122.7365 | 1 W/OF 2137 | Overcast-Fog-32-90 F | Pole-Wood | Broken, wire on ground | 20-0080240 | OH | Sus | 0 | No | 2020 | AUG | Yes | Line to Ground | 1552072 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1101 | 43071101 | FUSE | 9719 | 20200813 | 915 | 995018 | 317 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 6974 | 38.4156 | -122.563 | 7 SPANS LD SIDE OF FUSES 9719 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0083024 | OH | Sus | 44434934 | yes | 2020 | AUG | Yes | Multi-Fault | 1553903 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 903030 | 20200814 | 2126 | 1003269 | 406 | Distribution Circuit | 3rd Party | Vehicle | 21 | 8526 | 38.382 | -122.5549 | 9 SPANS LD SIDE OF 903030 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0084014 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Ground | 1554547 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | TRIP-SAVER | 999 | 20200820 | 2044 | 1025942 | 321 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 25359 | 38.422 | -122.954 | 1 SPAN SOURCE SIDE OF MTR# 1009708972 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0088250 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Line | 1557606 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | OTHER | WIRE DOWN 4 SPANS N/OF 999 | 20200824 | 45 | 1028023 | 1063 | Distribution Circuit | Vegetation | Tree - fell into line | 388 | 408384 | 38.4234 | -122.9552 | 4 SPANS N/OF 999 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0089140 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Open Circuit | 1558276 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | JUMPER | 539938 | 20200829 | 1734 | 1040774 | 90 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 2970 | 38.5404 | -122.9849 | 13 SPANS SS OF 1991 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0091325 | OH | Sus | 0 | No | 2020 | AUG | Yes | Line to Ground | 1559767 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1101 | 42821101 | FUSE | 7295 | 20200904 | 2142 | 1055463 | 766 | Distribution Circuit | Vegetation | Tree - branch fell on line | 34 | 26044 | 38.863 | -123.0863 | 6 SPANS LD SIDE OF 7295 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0093640 | OH | Sus | 44458915 | No | 2020 | SEP | Yes | Line to Line | 1560977 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | OTHER | WIRE DOWN 2 SPANS W/OF 12683 | 20200909 | 821 | 1061841 | 369 | Distribution Circuit | Vegetation | Tree - branch fell on line | 115 | 38696 | 38.499 | -122.978 | 2 SPANS W/OF 12683 & 4 SPANS LD SIDE OF 1031 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0095395 | OH | Sus | 31513306 | yes | 2020 | SEP | Yes | Open Circuit | 1562524 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | OTHER | WIRE DOWN @ 7800 BOHEMIAN HWY | 20200921 | 2348 | 1086259 | 549 | Distribution Circuit | Vegetation | Tree - fell into line | 494 | 78609 | 38.4439 | -122.9942 | 7800 BOHEMIAN HWY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0099892 | OH | Sus | 44476575 | No | 2020 | SEP | Yes | Open Circuit | 1565171 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | RECLOSER | 24918 | 20200925 | 950 | 1092320 | 421 | Distribution Circuit | Vegetation | Tree - fell into line | 171 | 61247 | 38.5911 | -122.9201 | 1 SPAN SOURCE SIDE OF 818325 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0101509 | OH | Sus | 31514646 | No | 2020 | SEP | Yes | Line to Line | 1566094 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2223 | 20201006 | 1256 | 1112205 | 550 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 25300 | 38.5467 | -122.6697 | at 3615 CALISTOGA RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0105814 | OH | Sus | 44488801 | No | 2020 | OCT | Yes | Line to Ground | 1568921 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 4895 | 20201016 | 413 | 1119052 | 628 | Distribution Circuit | Vegetation | Tree - fell into line | 152 | 95456 | 38.4118 | -122.9751 | SPAN BETWEEN 12023 AND 6431 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0109467 | OH | Sus | 44499205 | No | 2020 | OCT | Yes | Line to Line | 1571249 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | RECLOSER | 322 | 20201026 | 442 | 1128407 | 804 | Distribution Circuit | Vegetation | Tree - fell into line | 1021 | 385695 | 38.3868 | -122.8901 | MTR# 1009723336 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0113280 | OH | Sus | 0 | yes | 2020 | OCT | Yes | Line to Ground | 1574638 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | OTHER | WIRE DOWN @ 6759 | 20201102 | 1718 | 1134808 | 387 | Distribution Circuit | Vegetation | Tree - fell into line | 106 | 38627 | 38.4634 | -123.0122 | at 6759 ON MAIN LINE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0116297 | OH | Sus | 0 | No | 2020 | NOV | Yes | Line to Ground | 1576489 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1035 | 20201106 | 255 | 1137044 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7891 | 38.4989 | -122.9929 | CONTRERAS- T /4463: 13752 GUERNE HILL RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0117609 | OH | Sus | 0 | No | 2020 | NOV | Yes | Line to Line | 1577379 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 568 | 20201108 | 1232 | 1139473 | 411 | Distribution Circuit | Equipment Failure/Involved | Overhead | 161 | 22582 | 38.5166 | -122.6547 | Nott/3569: 5000 ALPINE RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 20-0118481 | OH | Sus | 0 | No | 2020 | NOV | Yes | Line to Line | 1578115 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | OTHER | WIRE DOWN 1 LD SIDE OF MTR 1008107675 | 20201117 | 1149 | 1147284 | 413 | Distribution Circuit | Vegetation | Tree - fell into line | 234 | 49792 | 38.5469 | -123.2949 | 1 LD SIDE OF MTR 1008107675 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0121894 | OH | Sus | 44543693 | No | 2020 | NOV | Yes | Open Circuit | 1580626 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1101 | 43071101 | OTHER | 4817 | 20201120 | 1223 | 1150260 | 332 | Distribution Circuit | Vegetation | Tree - branch fell on line | 62 | 8312 | 38.3984 | -122.5802 | 2865 BRISTOL RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0123398 | OH | Sus | 44564057 | No | 2020 | NOV | Yes | Open Circuit | 1581627 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 15707 | 20201207 | 254 | 1167366 | 667 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 18009 | 38.5447 | -122.6483 | 3430 CHALFAMT RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0128415 | OH | Sus | 44578801 | No | 2020 | DEC | Yes | Line to Ground | 1584977 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1109 | 42631109 | OTHER | WIRE DOWN | 20201213 | 2220 | 1182892 | 876 | Distribution Circuit | 3rd Party | Vehicle | 230 | 25002 | 38.1563 | -122.6956 | 1 SPAN LD SIDE OF FUCO 893363 ON MAINLINE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0130218 | OH | Sus | 0 | No | 2020 | DEC | Yes | Open Circuit | 1586960 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | TRIP-SAVER | 15401 | 20201214 | 1211 | 1184755 | 430 | Distribution Circuit | Vegetation | Tree - fell into line | 104 | 44720 | 38.4246 | -122.9613 | 125 RAILROAD AVE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0130385 | OH | Sus | 31521768 | No | 2020 | DEC | Yes | Line to Line | 1587277 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 969182 | 20210104 | 759 | 1203009 | 461 | Distribution Circuit | Vegetation | Tree - fell into line | 561 | 147152 | 38.4901 | -123.0598 | Arvig/3471: 3415 Austin Creek rd- Cazadero | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0004543 | OH | Sus | 0 | No | 2021 | JAN | Yes | Three Phase Fault | 1590601 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1993 | 20210110 | 157 | 1207454 | 858 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 21450 | 38.5274 | -123.0007 | 6/SPANS LD SIDE OF 1993 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0006963 | OH | Sus | 44620200 | No | 2021 | JAN | Yes | Three Phase Fault | 1592062 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 2913 | 20210112 | 822 | 1208712 | 454 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 1436 | 38.7033 | -122.9205 | MTR 1010390519 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0007658 | OH | Sus | 0 | No | 2021 | JAN | Yes | Multi-Fault | 1592522 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1109 | 42631109 | RECLOSER | 128 | 20210122 | 841 | 1220542 | 409 | Distribution Circuit | 3rd Party | Vehicle | 230 | 44553 | 38.2203 | -122.6437 | 1/P/N/OF 6671 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0012453 | OH | Sus | 0 | No | 2021 | JAN | Yes | Multi-Fault | 1595681 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | RECLOSER | 334 | 20210209 | 419 | 1251164 | 505 | Distribution Circuit | 3rd Party | Vehicle | 91 | 34205 | 38.5009 | -122.9053 | 2 SPANS SS SIDE OF CAP 700 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0023338 | OH | Sus | 44645102 | No | 2021 | FEB | Yes | Line to Line | 1603891 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 8227 | 20210218 | 1607 | 1257493 | 305 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 5490 | 38.5037 | -123.0299 | 14455 CAMINO DEL ARROYO | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0027102 | OH | Sus | 44656080 | No | 2021 | FEB | Yes | Line to Ground | 1606128 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1102 | 43071102 | FUSE | 7125 | 20210220 | 104 | 1258272 | 846 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 6768 | 38.3658 | -122.5744 | 1 SPAN LD SIDE OF FUCO 7125 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0027599 | OH | Sus | 31530579 | No | 2021 | FEB | Yes | Line to Ground | 1606437 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1109 | 42631109 | RECLOSER | 128 | 20210220 | 101 | 1258271 | 743 | Distribution Circuit | Vegetation | Tree - fell into line | 230 | 64764 | 38.2203 | -122.6437 | 3 SPANS SS OF FUCO 567455 ON MAIN LINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0027595 | OH | Sus | 44657622 | No | 2021 | FEB | Yes | Line to Ground | 1606433 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1103 | 43071103 | JUMPER | WIRE DOWN AT MTR 1010493817 | 20210225 | 1205 | 1262439 | 643 | Distribution Circuit | Vegetation | Tree - branch fell on line | 99 | 26631 | 38.384 | -122.4818 | 1 SPAN LD SIDE OF MTR 1010493817 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0029630 | OH | Sus | 44664056 | No | 2021 | FEB | Yes | Open Circuit | 1607928 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | FUSE | 485 | 20210306 | 1253 | 1272028 | 280 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 280 | 38.4829 | -123.0002 | WIRE DOWN 1 SPAN LD SIDE OF 485 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0033080 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1610141 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 15453 | 20210306 | 955 | 1271309 | 441 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 882 | 38.462 | -122.9373 | 2/SP/LD SIDE OF 15453 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0033049 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1610129 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | OTHER | 3069 | 20210311 | 1310 | 1278956 | 455 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3185 | 38.6051 | -122.9833 | 1ST SPAN TO NW LD SIDE 3069 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0035394 | OH | Sus | 44680387 | No | 2021 | MAR | Yes | Open Circuit | 1611429 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | JUMPER | WIRE DOWN 20 SPANS LD SIDE OF 6217 FUCO | 20210316 | 1429 | 1285388 | 150 | Distribution Circuit | Equipment Failure/Involved | Overhead | 172 | 25060 | 38.5854 | -122.9439 | WIRE DOWN 20 SPANS SW OF 6217 FUCO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0037259 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1612670 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 2439 | 20210318 | 1123 | 1287632 | 262 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 524 | 38.2162 | -122.9225 | 3 SPANS LD SIDE OF 2439 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0038040 | OH | Sus | 31533641 | No | 2021 | MAR | Yes | Line to Ground | 1613135 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | OTHER | WIRE DOWN 2 SPANS N/OF 3443 | 20210323 | 418 | 1292762 | 370 | Distribution Circuit | Vegetation | Tree - bark fell into line | 868 | 166648 | 38.278 | -122.8 | 2 SPANS N/OF 3443 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0039623 | OH | Sus | 31534112 | No | 2021 | MAR | Yes | Open Circuit | 1614067 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 67329 | 20210323 | 1221 | 1293997 | 182 | Distribution Circuit | Animal | Bird found | 1 | 182 | 38.2067 | -122.7644 | LD SIDE OF FUCO 67329 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0039880 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1614309 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 6215 | 20210324 | 2233 | 1296600 | 1231 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 14772 | 38.3555 | -122.545 | 2211 LONDON RANCH RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0040707 | OH | Sus | 31534154 | No | 2021 | MAR | Yes | Three Phase Fault | 1614812 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 5687 | 20210402 | 1033 | 1305763 | 251 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 1506 | 38.4072 | -122.932 | 13799 OCCIDENTAL RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0044144 | OH | Sus | 44720129 | No | 2021 | APR | Yes | Multi-Fault | 1617205 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 560 | 20210506 | 1059 | 1342454 | 469 | Distribution Circuit | Equipment Failure/Involved | Overhead | 30 | 14070 | 38.5561 | -123.3034 | 7 SPANS LOAD SIDE OF 6745 | Clear-32-90 F | Crossarm, Wood | Broken, wire on object | 21-0057852 | OH | Sus | 31539628 | No | 2021 | MAY | Yes | Force Out | 1626211 | CAW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 208 | 20210509 | 2051 | 1344565 | 378 | Distribution Circuit | Equipment Failure/Involved | Overhead | 181 | 19359 | 38.2261 | -122.7211 | 7 SPANS LD IDE OF 4383 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0059031 | OH | Sus | 44779340 | No | 2021 | MAY | Yes | Multi-Fault | 1627022 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | OTHER | BROKEN CONDUCTOR @ 11000 VELLUTINI RD | 20210606 | 2221 | 1367135 | 730 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 19038 | 38.4887 | -122.9273 | 11000 VELLUTINI RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0070672 | OH | Sus | 31542268 | No | 2021 | JUN | Yes | Open Circuit | 1634970 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 429 | 20210608 | 723 | 1368172 | 670 | Distribution Circuit | 3rd Party | Vehicle | 66 | 44220 | 38.4735 | -123.023 | SBCO 13835 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0071336 | OH | Sus | 0 | No | 2021 | JUN | Yes | Line to Ground | 1635512 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | FUSE | 2881 | 20210609 | 1517 | 1369559 | 433 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 10798 | 38.3435 | -122.7573 | WIRE DOWN at 5050 GILCHRIST RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0072293 | OH | Sus | 44845421 | No | 2021 | JUN | Yes | Line to Line | 1635996 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | OTHER | 5773 | 20210611 | 1432 | 1371077 | 503 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 6036 | 38.3731 | -122.8672 | SS/OF 6705 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0073332 | OH | Sus | 44853338 | No | 2021 | JUN | Yes | Line to Ground | 1636566 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 5152 | 20210616 | 1115 | 1375273 | 278 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 3336 | 38.5498 | -122.6679 | 4300 PORTER CREEK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0075009 | OH | Sus | 31543750 | No | 2021 | JUN | Yes | Line to Ground | 1637829 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 6759 | 20210623 | 1437 | 1383148 | 344 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 7912 | 38.4634 | -123.0122 | Arvig/3471: 350' W/OF 9870 main st- monte rio | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0078266 | OH | Sus | 44875490 | No | 2021 | JUN | Yes | Line to Line | 1640282 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 883 | 20210629 | 1047 | 1387967 | 291 | Distribution Circuit | Vegetation | Tree - fell into line | 250 | 12510 | 38.4074 | -122.9484 | WILLOW CREEK RD AND COLEMAN VALLEY RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0081469 | OH | Sus | 31545039 | No | 2021 | JUN | Yes | Line to Ground | 1642965 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 13839 | 20210706 | 1653 | 1393129 | 401 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 7619 | 38.4637 | -123.013 | 21462 BONITA TERRACE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0085615 | OH | Sus | 31545824 | No | 2021 | JUL | Yes | Line to Line | 1645758 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 3895 | 20210707 | 2145 | 1394143 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 5984 | 38.5158 | -123.0795 | SECOND AND THIRD SPAN LD SIDE OF 3895 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0086227 | OH | Sus | 31545835 | No | 2021 | JUL | Yes | Line to Ground | 1646095 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | RECLOSER | 705777 | 20210715 | 942 | 1405269 | 371 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 45 | 16695 | 38.7102 | -122.9248 | 4 SPANS LD SIDE 705777 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0090081 | OH | Sus | 44908378 | No | 2021 | JUL | Yes | Line to Ground | 1648577 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 64758 | 20210721 | 2138 | 1410653 | 359 | Distribution Circuit | 3rd Party | Vehicle | 282 | 67014 | 38.5087 | -123.0696 | 3 SPAN S/OF 4167 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0093183 | OH | Sus | 44916460 | No | 2021 | JUL | Yes | Line to Line | 1650436 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | OCB | 1103/2 | 20210730 | 253 | 1420620 | 601 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1459 | 470318 | 38.3098 | -122.7316 | SCHILLING JASON / 2778: 388 MECHAM ROAD | Clear-32-90 F | Insulator | Broken, wire on ground | 21-0097183 | OH | Sus | 31548313 | No | 2021 | JUL | Yes | Multi-Fault | 1653073 | INS | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 2001 | 20210811 | 2010 | 1440544 | 554 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 9122 | 38.5028 | -122.9888 | TREE IN LINE 3 SPANS LD SIDE OF FUCO 15601 - 15865 EDGE HILL | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 21-0103361 | OH | Sus | 31549386 | No | 2021 | AUG | Yes | Line to Ground | 1656734 | CAW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 1205 | 20210813 | 1204 | 1441972 | 376 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1504 | 38.2496 | -122.7265 | WATTS- CHAD: 6 spans load side between SAP ID's 103143256 & 103143257 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0104236 | OH | Sus | 44947169 | No | 2021 | AUG | Yes | Line to Ground | 1657369 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 256 | 20210814 | 156 | 1442399 | 695 | Distribution Circuit | Vegetation | Tree - fell into line | 1259 | 436815 | 38.4901 | -123.0598 | 4/SPANS LD SIDE OF 4001 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0104483 | OH | Sus | 0 | No | 2021 | AUG | Yes | Line to Ground | 1657439 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 797 | 20210815 | 55 | 1443069 | 671 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 2572 | 38.5039 | -122.9005 | 2/SPANS LD SIDE OF 468859 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0104731 | OH | Sus | 31549622 | No | 2021 | AUG | Yes | Line to Ground | 1657672 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1101 | 42571101 | FUSE | 18707 | 20210901 | 2205 | 1460456 | 477 | Distribution Circuit | 3rd Party | Vehicle | 3 | 1431 | 38.3747 | -122.9078 | 1 POLE LD SIDE OF FUSES | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0112438 | OH | Sus | 31551032 | No | 2021 | SEP | Yes | Multi-Fault | 1662916 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 15707 | 20210908 | 1500 | 1464763 | 493 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 13311 | 38.5447 | -122.6483 | 3430 CHALFANT | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0114908 | OH | Sus | 44972802 | No | 2021 | SEP | Yes | Line to Line | 1664214 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FULTON-1107 | 42561107 | RECLOSER | 214 | 20210913 | 1317 | 1470785 | 336 | Distribution Circuit | Vegetation | Tree - fell into line | 452 | 59332 | 38.5031 | -122.7355 | 2 SPANS LD SIDE OF CGC 218025032582 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0116901 | OH | Sus | 31552031 | No | 2021 | SEP | Yes | Multi-Fault | 1665412 | CAW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | OTHER | WIRE DOWN 1 SPAN LD SIDE 15601 | 20210919 | 1340 | 1475653 | 503 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 3904 | 38.5027 | -122.9872 | 1 SPAN LD SIDE OF 15601 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0119589 | OH | Sus | 0 | No | 2021 | SEP | Yes | Line to Ground | 1667070 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | OTHER | WIRE DOWN AT 1310 LONDON RANCH RD | 20210922 | 603 | 1477688 | 518 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6216 | 38.3625 | -122.5288 | 1310 LONDON RANCH RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0120752 | OH | Sus | 31552475 | No | 2021 | SEP | Yes | Line to Ground | 1667785 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 448 | 20210929 | 817 | 1483145 | 349 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1304 | 79685 | 38.3443 | -122.5144 | 15655 Arnold Dr- Sonoma | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0123670 | OH | Sus | 44993894 | No | 2021 | SEP | Yes | Line to Line | 1669557 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 134 | 20211019 | 1929 | 1502381 | 818 | Distribution Circuit | Vegetation | Tree - fell into line | 233 | 189564 | 38.5592 | -123.2701 | 2 SPANS LD SIDE OF FUCO 59153 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0133354 | OH | Sus | 45016653 | No | 2021 | OCT | Yes | Line to Ground | 1675789 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 2371 | 20211021 | 1015 | 1504439 | 703 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 4218 | 38.5423 | -122.8717 | CGC # 217507932000 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0134436 | OH | Sus | 0 | No | 2021 | OCT | Yes | Three Phase Fault | 1676407 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER | 1313 | 20211021 | 9 | 1503892 | 357 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 39270 | 38.504 | -122.9884 | MELODY AVE AND DRAKE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0134157 | OH | Sus | 31555270 | No | 2021 | OCT | Yes | Line to Ground | 1676245 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 506 | 20211022 | 353 | 1505271 | 686 | Distribution Circuit | Vegetation | Tree - fell into line | 143 | 59675 | 38.4693 | -123.0137 | CORNER OF RIVER & MOSCOW RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0134819 | OH | Sus | 45019144 | No | 2021 | OCT | Yes | Line to Ground | 1676561 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 6759 | 20211022 | 12 | 1505175 | 397 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 9131 | 38.4634 | -123.0122 | 9815 MAIN ST | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0134813 | OH | Sus | 31555594 | No | 2021 | OCT | Yes | Line to Ground | 1676553 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 318 | 20211026 | 2310 | 1522494 | 692 | Distribution Circuit | Vegetation | Tree - fell into line | 437 | 138298 | 38.4046 | -122.9485 | 2 LD SIDE OF 318 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0138513 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1679464 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 246 | 20211029 | 835 | 1525013 | 526 | Distribution Circuit | Vegetation | Tree - fell into line | 528 | 57764 | 38.3657 | -122.5275 | 3 SPANS E/OF 11121 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0139670 | OH | Sus | 45024490 | No | 2021 | OCT | Yes | Line to Ground | 1680107 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1101 | 42821101 | JUMPER | DOWN WIRE 4 SPANS SS OF 6085 | 20211101 | 1322 | 1527376 | 266 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 23526 | 38.8339 | -123.0513 | 4 SPANS SS OF 6085 at 32725 HWY 128 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0140732 | OH | Sus | 45031462 | No | 2021 | NOV | Yes | None | 1680864 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1499 | 20211101 | 1431 | 1527384 | 536 | Distribution Circuit | Vegetation | Tree - fell into line | 131 | 70216 | 38.5089 | -122.9291 | 2 SS 7363 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0140805 | OH | Sus | 31573861 | No | 2021 | NOV | Yes | Line to Ground | 1680882 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 539938 | 20211101 | 1130 | 1527204 | 529 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 44436 | 38.5277 | -123 | INGRAM- 3888: 17200 SWEETWATER SPRINGS RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0140582 | OH | Sus | 31573313 | No | 2021 | NOV | Yes | Multi-Fault | 1680808 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | TRIP-SAVER | 1701 | 20211104 | 1614 | 1535109 | 675 | Distribution Circuit | Vegetation | Tree - branch fell on line | 66 | 44550 | 38.4728 | -123.0474 | 64 MAGIC MTN RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0142544 | OH | Sus | 31577708 | No | 2021 | NOV | Yes | Line to Ground | 1681867 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 6049 | 20211105 | 1322 | 1535838 | 213 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 852 | 38.5986 | -122.9118 | 6 SPANS LD SIDE OF 6049 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0142871 | OH | Sus | 0 | No | 2021 | NOV | Yes | Force Out | 1682121 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1105 | 42271105 | FUSE | 3315 | 20211113 | 443 | 1542168 | 404 | Distribution Circuit | Vegetation | Tree - fell into line | 33 | 4528 | 38.3217 | -122.7592 | SCHILLING JASON / 2778: 6400 PETERSON ROAD | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 21-0145198 | OH | Sus | 31578330 | No | 2021 | NOV | Yes | Line to Line | 1683943 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 12153 | 20211114 | 1613 | 1543994 | 557 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1114 | 38.4444 | -122.9202 | 2 SPANS LD SIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0145461 | OH | Sus | 45066176 | No | 2021 | NOV | Yes | Line to Ground | 1684240 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1109 | 42631109 | FUSE | 2613 | 20211118 | 902 | 1548755 | 227 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 1816 | 38.1849 | -122.6646 | 9 SPANS LD SIDE OF 2613 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0147716 | OH | Sus | 45070473 | No | 2021 | NOV | Yes | Line to Ground | 1686079 | CSO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1103 | 43071103 | FUSE | 15877 | 20211205 | 810 | 1559541 | 441 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1764 | 38.3982 | -122.5127 | 1 LD SIDE OF FUSES | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0155024 | OH | Sus | 45081863 | No | 2021 | DEC | Yes | Multi-Fault | 1691529 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | JUMPER | 1 OF 3 WIRES DOWN 2 SPAN LD SIDE OF FUCO 2443 | 20211208 | 1205 | 1562098 | 322 | Distribution Circuit | Equipment Failure/Involved | Overhead | 9 | 2898 | 38.1939 | -122.9104 | 2 SPANS LD SIDE OF 2443 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0156049 | OH | Sus | 45084752 | No | 2021 | DEC | Yes | Line to Ground | 1692654 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | RECLOSER | 208 | 20211220 | 753 | 1577776 | 457 | Distribution Circuit | Equipment Failure/Involved | Overhead | 179 | 23154 | 38.2261 | -122.7211 | HLEBAKOS- FRANK/1277: Tomales Rd at Arizona Ave | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0159823 | OH | Sus | 31588021 | No | 2021 | DEC | Yes | Line to Ground | 1697054 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | FUSE | 17881 | 20220103 | 2144 | 1594346 | 1236 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 9888 | 38.3646 | -122.5447 | 7920 EMERY | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0005783 | OH | Sus | 45106902 | No | 2022 | JAN | Yes | Line to Ground | 1700830 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | GEYSERVILLE-1101 | 42891101 | FUSE | 5531 | 20220104 | 606 | 1594571 | 723 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 8025 | 38.6773 | -123.0625 | 12000 SKAGGS SPRINGS RD | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0005812 | OH | Sus | 0 | No | 2022 | JAN | Yes | Three Phase Fault | 1700850 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | SANTA ROSA A-1104 | 42151104 | RECLOSER | 32180 | 20220119 | 1240 | 1605245 | 401 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 759 | 98914 | 38.4782 | -122.679 | HESSONG- 3884: LD SD 716 2 SPANS FROM EOL. WALLACE RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0011312 | OH | Sus | 45128169 | No | 2022 | JAN | Yes | Line to Ground | 1703495 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 1181 | 20220121 | 2308 | 1608054 | 805 | Distribution Circuit | Vegetation | Tree - fell into line | 111 | 89355 | 38.4027 | -122.9163 | 3 SPANS LD SIDE OF 1181 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0012806 | OH | Sus | 0 | No | 2022 | JAN | Yes | Force Out | 1704129 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | GEYSERVILLE-1102 | 42891102 | JUMPER | SBCO 1 SP SOURCE SIDE CGC 217578640034 | 20220122 | 16 | 1609381 | 770 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 770 | 38.765 | -122.8444 | CGC 217578640034 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0013040 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Ground | 1704379 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 3447 | 20220122 | 10 | 1608070 | 1010 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 17170 | 38.5152 | -122.6288 | 2 SPANS LD SIDE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0013001 | OH | Sus | 0 | No | 2022 | JAN | Yes | Multi-Fault | 1704343 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 655192 | 20220201 | 945 | 1617856 | 398 | Distribution Circuit | Vegetation | Tree - branch fell on line | 44 | 17512 | 38.5467 | -122.6696 | 3609 CALISTOGA RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0016818 | OH | Sus | 31591620 | No | 2022 | FEB | Yes | Line to Line | 1706605 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | CLOVERDALE-1102 | 42821102 | JUMPER | WIRE DOWN 1 SPAN FROM EOL | 20220206 | 422 | 1622114 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 934 | 38.7674 | -123.0521 | 1 SPAN FROM EOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0019061 | OH | Sus | 45166041 | No | 2022 | FEB | Yes | Line to Ground | 1707906 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 1709 | 20220214 | 937 | 1626911 | 237 | Distribution Circuit | Vegetation | Tree - branch fell on line | 171 | 24819 | 38.3737 | -122.8687 | 3696 BURNSIDE RD- SANTA ROSA | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0022015 | OH | Sus | 45177208 | No | 2022 | FEB | Yes | Line to Ground | 1709892 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 1525 | 20220304 | 1245 | 1642229 | 278 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 15290 | 38.4106 | -122.9828 | Galea/3472: AT RISER POLE 86115 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0029957 | OH | Sus | 45198399 | No | 2022 | MAR | Yes | Line to Ground | 1714627 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | FUSE | 1709 | 20220322 | 1003 | 1653412 | 503 | Distribution Circuit | Vegetation | Tree - fell into line | 171 | 44193 | 38.3737 | -122.8687 | 4185 BURNSIDE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0036776 | OH | Sus | 31597987 | No | 2022 | MAR | Yes | Line to Ground | 1719045 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | JUMPER | TREE IN LINES | 20220326 | 1059 | 1656334 | 425 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 888 | 38.6033 | -122.9162 | 10 SPANS LD SIDE OF 6049 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 22-0038883 | OH | Sus | 31599357 | No | 2022 | MAR | Yes | Line to Ground | 1720236 | CAW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 17907 | 20220327 | 356 | 1656572 | 473 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 17974 | 38.5034 | -123.0289 | 1 SPAN SS OF 7709 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0038965 | OH | Sus | 31599660 | No | 2022 | MAR | Yes | Line to Line | 1720301 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | RECLOSER | 70288 | 20220329 | 1039 | 1658845 | 469 | Distribution Circuit | Equipment Failure/Involved | Overhead | 845 | 240098 | 38.5286 | -123.1572 | 2 LD SIDE OF 4195 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 22-0039974 | OH | Sus | 45234284 | No | 2022 | MAR | Yes | Line to Ground | 1721034 | CSO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | CLOVERDALE-1102 | 42821102 | OTHER | WIRE DOWN @1381 | 20220404 | 1620 | 1662818 | 372 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 12270 | 38.7728 | -122.9075 | AT 1381 LD SIDE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0042594 | OH | Sus | 45239659 | No | 2022 | APR | Yes | Line to Ground | 1722613 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 2 | SONOMA-1105 | 42721105 | RECLOSER | 229588 | 20220410 | 243 | 1667201 | 797 | Distribution Circuit | Vegetation | Tree - fell into line | 184 | 99704 | 38.2871 | -122.4188 | 2 SPANS LD SIDE SAP#104008045 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0045060 | OH | Sus | 0 | No | 2022 | APR | Yes | Three Phase Fault | 1724216 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 2943 | 20220411 | 1235 | 1668675 | 691 | Distribution Circuit | Vegetation | Tree - fell into line | 136 | 65456 | 38.499 | -122.9038 | INGRAM- 3888: 9365 CHAMPS DE ELYSSES | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0045542 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Ground | 1724620 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 37520 | 20220411 | 1223 | 1668650 | 606 | Distribution Circuit | Vegetation | Tree - branch fell on line | 76 | 46056 | 38.5086 | -123.0693 | Arvig/3471: 15960 E Austin Creek Rd- Cazadero | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0045480 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Line | 1724573 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | TRIP-SAVER | 53477 | 20220414 | 927 | 1672383 | 297 | Distribution Circuit | Vegetation | Tree - branch fell on line | 57 | 16929 | 38.4962 | -123.0694 | 1 SS OF 8139 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0048130 | OH | Sus | 45255922 | No | 2022 | APR | Yes | Multi-Fault | 1726654 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | RECLOSER | 87402 | 20220416 | 321 | 1674075 | 497 | Distribution Circuit | Equipment Failure/Involved | Overhead | 31 | 15407 | 38.1632 | -122.8903 | 8000 marshall petaluma rd | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0050371 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Ground | 1728466 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 487 | 20220417 | 1514 | 1675216 | 603 | Distribution Circuit | Vegetation | Tree - fell into line | 148 | 64390 | 38.4646 | -123.0101 | AT FUCO 6759 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0050714 | OH | Sus | 31601202 | No | 2022 | APR | Yes | Line to Ground | 1728790 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 779 | 20220419 | 433 | 1676170 | 907 | Distribution Circuit | Vegetation | Tree - bark fell into line | 43 | 39001 | 38.5969 | -122.9892 | 2 SPANS SS/OF CGC# 217168532845 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0051365 | OH | Sus | 45260912 | No | 2022 | APR | Yes | Line to Ground | 1729293 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 969182 | 20220429 | 2056 | 1684910 | 688 | Distribution Circuit | Vegetation | Tree - branch fell on line | 564 | 141956 | 38.4901 | -123.0598 | 1 SPAN LD SIDE OF METER# 1007661081 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0056301 | OH | Sus | 31602139 | No | 2022 | APR | Yes | Line to Ground | 1732347 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 1623 | 20220503 | 1819 | 1687643 | 442 | Distribution Circuit | Equipment Failure/Involved | Overhead | 85 | 20383 | 38.2421 | -122.7086 | 1 SPAN W/OF 1131 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 22-0057487 | OH | Sus | 45277718 | No | 2022 | MAY | Yes | Line to Ground | 1733311 | CSO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 2435 | 20220507 | 1545 | 1690803 | 369 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 19926 | 38.2418 | -122.9052 | 1 SPAN S/S OF 7841 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0059343 | OH | Sus | 45285269 | No | 2022 | MAY | Yes | Line to Line | 1734466 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 66006 | 20220509 | 1230 | 1692187 | 804 | Distribution Circuit | Vegetation | Tree - fell into line | 255 | 74533 | 38.4053 | -122.9477 | 3 SPANS LD SIDE OF LR 66006 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 22-0059774 | OH | Sus | 31603055 | No | 2022 | MAY | Yes | Multi-Fault | 1734864 | CAW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | RECLOSER | 568 | 20220509 | 532 | 1691664 | 616 | Distribution Circuit | Equipment Failure/Involved | Overhead | 162 | 99980 | 38.5166 | -122.6547 | 6 SPANS LD SIDE OF REGS 69228 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0059553 | OH | Sus | 45285896 | No | 2022 | MAY | Yes | Line to Ground | 1734652 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | OTHER | WIRE DOWN N/OF 1667 | 20220510 | 1617 | 1693275 | 526 | Distribution Circuit | Equipment Failure/Involved | Overhead | 857 | 431930 | 38.2761 | -122.9 | WIRE DOWN N/OF 1667 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0060396 | OH | Sus | 45291413 | No | 2022 | MAY | Yes | Open Circuit | 1735219 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 937000 | 20220526 | 2248 | 1712145 | 1006 | Distribution Circuit | Vegetation | Tree - branch fell on line | 24 | 20153 | 38.4887 | -123.017 | JUMPERS at FUSESAVER 937000 & 1/SS OF CGC 217055730092 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0067275 | OH | Sus | 45319554 | No | 2022 | MAY | Yes | Line to Ground | 1739803 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 969182 | 20220610 | 411 | 1726907 | 561 | Distribution Circuit | Vegetation | Tree - fell into line | 564 | 175142 | 38.5087 | -123.0696 | SCHILLING JASON / 2778: 1 SP S/S C/O 3901 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0072518 | OH | Sus | 45333774 | No | 2022 | JUN | Yes | Line to Line | 1743329 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 8003 | 20220918 | 334 | 1813679 | 441 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 8379 | 38.4777 | -123.0236 | 1/SPAN PAST 21955 DUNCAN RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0111541 | OH | Sus | 31616241 | No | 2022 | SEP | Yes | Line to Ground | 1769569 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | RECLOSER | 64682 | 20220924 | 1426 | 1820871 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 148 | 21133 | 38.4646 | -123.0101 | PEDERSON- RYLEY/3473: 21452 Bonita Terrace- Monte Rio | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0114528 | OH | Sus | 31616916 | No | 2022 | SEP | Yes | Line to Line | 1771654 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | RECLOSER | 132 | 20221011 | 708 | 1834602 | 485 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1019 | 111011 | 38.2648 | -122.8056 | HLEBAKOS- FRANK/1277: 2 spans source side of fuses 4221 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0119954 | OH | Sus | 31618136 | No | 2022 | OCT | Yes | Line to Ground | 1775476 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 104 | 20221101 | 235 | 1849540 | 424 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1524 | 253551 | 38.4031 | -122.9214 | 5/P/LD SIDE OF 1689 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0126297 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Ground | 1780356 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 17803 | 20221107 | 905 | 1855764 | 310 | Distribution Circuit | Vegetation | Tree - branch fell on line | 9 | 2790 | 38.5216 | -123.0962 | 2 SPANS LD SIDE OF FUSES 17803 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0128461 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Ground | 1781880 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | PETALUMA C-1108 | 42631108 | FUSE | 3171 | 20221113 | 805 | 1861522 | 318 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3498 | 38.2437 | -122.8114 | 1315 TOMALES PETALUMA RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0130652 | OH | Sus | 45526121 | No | 2022 | NOV | Yes | Line to Ground | 1783380 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1112 | 42751112 | FUSE | 150571 | 20221123 | 1947 | 1868638 | 828 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 5238 | 38.6225 | -122.8282 | 2 SPANS LD SIDE OF 2353 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0133983 | OH | Sus | 45571532 | No | 2022 | NOV | Yes | Line to Line | 1785361 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | RECLOSER | 495692 | 20221206 | 954 | 1877209 | 419 | Distribution Circuit | Vegetation | Tree - fell into line | 347 | 145393 | 38.4098 | -122.9354 | METER 1009704269 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0136972 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1787888 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1112 | 42751112 | OTHER | WIRE DOWN 3 LD SIDE OF 3031 | 20221227 | 900 | 1898840 | 710 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 8460 | 38.606 | -122.9771 | 3 LD SIDE OF 3031 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0141645 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793329 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6561 | 20221227 | 839 | 1898794 | 515 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 23175 | 38.4296 | -122.9335 | 82620 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0141748 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1793436 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 8139 | 20221227 | 747 | 1898657 | 529 | Distribution Circuit | Vegetation | Tree - fell into line | 36 | 19044 | 38.4982 | -123.0729 | 66 SUNRISE MOUNTAIN RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0141580 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1793259 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | FUSE | 4523 | 20221230 | 1355 | 1902054 | 192 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 3072 | 38.536 | -123.1403 | 3 SPANS SS OF 8971 TWD 4523 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142248 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1794037 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER | 1989 | 20221230 | 928 | 1901926 | 269 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 11567 | 38.5219 | -122.9971 | 16201 RIO NIDO RD- GUERNEVILLE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142188 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1793968 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | CLOVERDALE-1102 | 42821102 | FUSE | 12905 | 20230103 | 1242 | 1911519 | 304 | Distribution Circuit | Equipment Failure/Involved | Overhead | 40 | 11241 | 38.7762 | -122.9308 | 1 SPAN SS 76875 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0005190 | OH | Sus | 45615957 | No | 2023 | JAN | Yes | Line to Ground | 1795708 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1112 | 42751112 | FUSE | 769 | 20230111 | 1134 | 1947762 | 576 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 16128 | 38.5962 | -122.9148 | 2 SPAN LD SIDE 769 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0013708 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1803119 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | FUSE | 13075 | 20230112 | 1205 | 1950055 | 135 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 135 | 38.549 | -123.2446 | UNKONW HARMON ON SITE AND FUCO WERE OPEN ALREADY | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0014485 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1803757 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | JUMPER | OJ'S LINE & BUS 1 POLSE S/OF FUCO 18673 | 20230113 | 952 | 1951610 | 164 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 164 | 38.5968 | -123.3025 | N/A | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015168 | OH | Sus | 0 | No | 2023 | JAN | Yes | None | 1804210 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 429 | 20230115 | 342 | 1955455 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 66 | 22110 | 38.4735 | -123.023 | CGC#217070829564 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016519 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1805277 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | OTHER | 933786 | 20230119 | 327 | 1961765 | 623 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 17965 | 38.4881 | -122.9208 | VELLUTINI RD AND YELLOWBRICK RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0018655 | OH | Sus | 45644913 | No | 2023 | JAN | Yes | Force Out | 1806720 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 6113 | 20230123 | 336 | 1965271 | 575 | Distribution Circuit | Vegetation | Tree - branch fell on line | 52 | 29900 | 38.5382 | -122.6465 | 1 SS/OF 6119 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0020034 | OH | Sus | 45647247 | No | 2023 | JAN | Yes | Line to Ground | 1807447 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | FUSE | 14095 | 20230127 | 1414 | 1970006 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 812 | 38.3449 | -123.0029 | 1SP LD SIDE OF 14095 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0022536 | OH | Sus | 45653110 | No | 2023 | JAN | Yes | Line to Ground | 1808720 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 2305 | 20230130 | 414 | 1971885 | 827 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2876 | 38.5104 | -123.0963 | FIRST POLE THAT BUCKES N/E LOAD SIDE OF 2325 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0022968 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1809188 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | FUSE | 1343 | 20230205 | 704 | 1977264 | 575 | Distribution Circuit | Equipment Failure/Involved | Overhead | 25 | 10440 | 38.2758 | -122.7662 | 4 LD SIDE OF 1343 | Clear-32-90 F | Other | Broken, wire on ground | 23-0025387 | OH | Sus | 45658909 | No | 2023 | FEB | Yes | Line to Ground | 1810681 | NON | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | FUSE | 551 | 20230206 | 532 | 1977827 | 437 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3933 | 38.4246 | -122.9568 | 2 SPANS S/S OF CGC# 217268327843 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0025542 | OH | Sus | 31636316 | No | 2023 | FEB | Yes | Line to Line | 1810818 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | COTATI-1103 | 42271103 | JUMPER | HOT WIRE DOWN 1 SPAN SS SIDE CGC 313088563110 | 20230214 | 305 | 1984287 | 538 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2360 | 38.2079 | -122.9073 | 1 SPAN SS SIDE CGC 313088563110 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0028419 | OH | Sus | 45671479 | No | 2023 | FEB | Yes | Open Circuit | 1812961 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1997 | 20230214 | 1457 | 1985172 | 393 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 44016 | 38.5018 | -123.0238 | 15607 OLD CAZADERO RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0028888 | OH | Sus | 31636881 | No | 2023 | FEB | Yes | Line to Ground | 1813248 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | RECLOSER | 322 | 20230306 | 448 | 2024220 | 610 | Distribution Circuit | Vegetation | Tree - fell into line | 376 | 66267 | 38.3871 | -122.89 | CGC 217430925728 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 23-0040543 | OH | Sus | 45688981 | No | 2023 | MAR | Yes | Line to Ground | 1822279 | CSO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | RECLOSER | 64758 | 20230308 | 706 | 2026266 | 662 | Distribution Circuit | Vegetation | Tree - fell into line | 284 | 45592 | 38.5087 | -123.0696 | 18595 KING RIDGE ROAD | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0041489 | OH | Sus | 45690155 | No | 2023 | MAR | Yes | Line to Ground | 1822811 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | DUNBAR-1103 | 43071103 | JUMPER | OJ'S S/S OF CGC# 218359528520 | 20230310 | 246 | 2030063 | 793 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 7214 | 38.4477 | -122.5738 | 7 SPANS LOAD SIDE OF 107941 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0042735 | OH | Sus | 0 | No | 2023 | MAR | Yes | None | 1823549 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FORT ROSS-1121 | 42851121 | TRIP-SAVER | 2987 | 20230310 | 237 | 2029958 | 283 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 7075 | 38.5423 | -123.0896 | 4 SPANS LD SIDE OF 4947 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0042772 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1823575 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | TRIP-SAVER | 4947 | 20230310 | 241 | 2030288 | 732 | Distribution Circuit | Vegetation | Tree - fell into line | 54 | 39528 | 38.5579 | -123.0951 | 4 SPANS LD SIDE OF 4947 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0042772 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1823576 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1101 | 42571101 | JUMPER | WIRE DOWN @ CGC 217489025790 | 20230312 | 1100 | 2033267 | 546 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 3474 | 38.3721 | -122.876 | CGC 217489025790 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0043723 | OH | Sus | 45698202 | No | 2023 | MAR | Yes | Force Out | 1824239 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | RECLOSER | 658 | 20230313 | 722 | 2034041 | 688 | Distribution Circuit | Vegetation | Tree - fell into line | 132 | 70584 | 38.4451 | -122.9104 | 2 SPANS LD SIDE CGC 217362028517 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0043956 | OH | Sus | 31639884 | No | 2023 | MAR | Yes | Multi-Fault | 1824457 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1111 | 42811111 | FUSE | 42419 | 20230315 | 910 | 2045634 | 511 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1022 | 38.5214 | -123.0614 | 3600 E AUSTIN CREEK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0046349 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1826165 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 2561 | 20230320 | 320 | 2052548 | 563 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 11823 | 38.4113 | -122.9652 | 4618 TIMBER LN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0048603 | OH | Sus | 31640126 | No | 2023 | MAR | Yes | Line to Line | 1827811 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | SALMON CREEK-1101 | 43161101 | RECLOSER | 37368 | 20230324 | 647 | 2065569 | 458 | Distribution Circuit | Equipment Failure/Involved | Overhead | 187 | 41889 | 38.3809 | -123.079 | 3 SPANS LD SIDE OF 87781- JUST LD SIDE OF R4071 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0051682 | OH | Sus | 45708581 | No | 2023 | MAR | Yes | Line to Line | 1829827 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | TRIP-SAVER | 1989 | 20230325 | 1341 | 2067060 | 300 | Distribution Circuit | Vegetation | Tree - branch fell on line | 43 | 12900 | 38.5219 | -122.9971 | 16270 RIO NIDO RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0052509 | OH | Sus | 31640450 | No | 2023 | MAR | Yes | Line to Ground | 1830463 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 560 | 20230328 | 514 | 2069508 | 587 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 6452 | 38.5561 | -123.3034 | 6 NORTH OF 6745 ON MAINLINE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0053220 | OH | Sus | 45709597 | No | 2023 | MAR | Yes | Line to Line | 1830975 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 6543 | 20230328 | 745 | 2069584 | 815 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 19560 | 38.3681 | -122.9641 | 1658 BURL LN | Overcast-Fog-Heavy Rain-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0053369 | OH | Sus | 0 | No | 2023 | MAR | Yes | Force Out | 1831072 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MOLINO-1102 | 42571102 | FUSE | 11455 | 20230328 | 853 | 2070167 | 367 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 367 | 38.3997 | -122.9585 | LD SIDE OF 11455 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0053413 | OH | Sus | 0 | No | 2023 | MAR | Yes | Force Out | 1831093 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | RINCON-1103 | 43321103 | FUSE | 2225 | 20230406 | 932 | 2081629 | 486 | Distribution Circuit | 3rd Party | Vehicle | 92 | 44712 | 38.5247 | -122.6543 | 5 SPANS LD SIDE OF 2225 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 23-0057887 | OH | Sus | 0 | No | 2023 | APR | Yes | Line to Ground | 1833790 | PW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FORT ROSS-1121 | 42851121 | RECLOSER | 612266 | 20230412 | 1411 | 2086786 | 679 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 26481 | 38.5329 | -123.2715 | 5 SPANS LD SIDE OF 612266 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0060242 | OH | Sus | 31642129 | No | 2023 | APR | Yes | Three Phase Fault | 1835254 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | RECLOSER | 120 | 20230607 | 1119 | 2131913 | 574 | Distribution Circuit | Vegetation | Tree - fell into line | 492 | 89723 | 38.4637 | -123.0083 | 3 SPANS LD SIDE 164359 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0079839 | OH | Sus | 31651531 | No | 2023 | JUN | Yes | Multi-Fault | 1848761 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 769 | 20230627 | 438 | 2146585 | 683 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 18499 | 38.5962 | -122.9148 | 3485 WALLACE CREEK RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0085899 | OH | Sus | 31653687 | No | 2023 | JUN | Yes | Line to Ground | 1853344 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | FUSE | 671411 | 20230627 | 1546 | 2147176 | 237 | Distribution Circuit | Vegetation | Tree - branch fell on line | 19 | 4503 | 38.4149 | -122.8997 | 2 SPANS LD SIDE OF FUCO 671411 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0086263 | OH | Sus | 45862191 | No | 2023 | JUN | Yes | Line to Ground | 1853527 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 448 | 20230629 | 2143 | 2149402 | 825 | Distribution Circuit | Vegetation | Tree - fell into line | 611 | 164059 | 38.3443 | -122.5144 | PEPPER- NICK / 2096: 2207 moringside mountain dr | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0087372 | OH | Sus | 45865302 | No | 2023 | JUN | Yes | Line to Ground | 1854186 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | DUNBAR-1102 | 43071102 | RECLOSER | 448 | 20230719 | 2358 | 2168536 | 776 | Distribution Circuit | Vegetation | Tree - fell into line | 610 | 246110 | 38.3443 | -122.5144 | 3 LD SIDE OF 98281 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0094462 | OH | Sus | 0 | No | 2023 | JUL | Yes | Line to Ground | 1858968 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | MOLINO-1102 | 42571102 | RECLOSER | 658 | 20230724 | 1513 | 2172734 | 462 | Distribution Circuit | Vegetation | Tree - branch fell on line | 132 | 24900 | 38.4451 | -122.9104 | GREEN VALLEY & GREEN VALLEY RD 2 SPANS OF WIRE DOWN at FUCO 15445 EACH DIRECTION | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0096150 | OH | Sus | 31656766 | No | 2023 | JUL | Yes | Line to Line | 1860107 | CAW | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | OTHER | WIRE DOWN 2 LD SIDE 1073 | 20230731 | 611 | 2178121 | 474 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 50431 | 38.4999 | -122.9822 | INGRAM- JOHN 3612: 2 SP L/S SW 1073 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0098544 | OH | Sus | 45906548 | No | 2023 | JUL | Yes | Open Circuit | 1861678 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 524 | 20230831 | 2017 | 2207409 | 318 | Distribution Circuit | Vegetation | Tree - fell into line | 1015 | 92566 | 38.5037 | -122.9936 | 1/S/SS CGC 217194131220 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0111535 | OH | Sus | 45947873 | No | 2023 | AUG | Yes | Line to Ground | 1870633 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1112 | 42811112 | RECLOSER | 212 | 20230929 | 2302 | 2231084 | 424 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 71232 | 38.4752 | -123.0022 | 1 LD SIDE OF 212 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0122798 | OH | Sus | 45994733 | No | 2023 | SEP | Yes | Line to Line | 1878028 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | RECLOSER | 202 | 20231012 | 1202 | 2241841 | 283 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 11251 | 38.4984 | -122.9914 | 11708 CANYON DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0127521 | OH | Sus | 46011941 | No | 2023 | OCT | Yes | Line to Ground | 1881652 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1101 | 42091101 | OTHER | WIRE DOWN 2/S/LD SIDE 15463 | 20231118 | 854 | 2272306 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3772 | 38.4705 | -122.9497 | 2/S/LD SIDE 15463 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0140825 | OH | Sus | 46061096 | No | 2023 | NOV | Yes | Open Circuit | 1891536 | CO | OH | No | Yes
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 1031 | 20231118 | 1304 | 2272653 | 329 | Distribution Circuit | Vegetation | Tree - fell into line | 115 | 11889 | 38.4926 | -122.9614 | 2/S/ LD SIDE 1031- 11726 CANYON DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0140907 | OH | Sus | 31676687 | No | 2023 | NOV | Yes | Line to Line | 1891595 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MIRABEL-1102 | 42091102 | FUSE | 1439 | 20231219 | 624 | 2295315 | 533 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 10648 | 38.4985 | -122.9412 | 12121 SUMNMERHOME PARK | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0148049 | OH | Sus | 46095496 | No | 2023 | DEC | Yes | Line to Ground | 1898863 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 2 | FITCH MOUNTAIN-1113 | 42751113 | FUSE | 1297 | 20231228 | 640 | 2301042 | 391 | Distribution Circuit | Vegetation | Tree - fell into line | 181 | 20400 | 38.6212 | -122.8301 | at SAP ID 103608540 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0149088 | OH | Sus | 46102427 | No | 2023 | DEC | Yes | Line to Ground | 1900269 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | CLOVERDALE-1102 | 42821102 | RECLOSER | 262 | 20231229 | 1229 | 2301944 | 394 | Distribution Circuit | Vegetation | Tree - fell into line | 363 | 143022 | 38.7987 | -122.9911 | BET 15703 TWD 15731 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0149216 | OH | Sus | 31680503 | No | 2023 | DEC | Yes | Multi-Fault | 1900510 | CO | OH | No | No
SONOMA | FIELD OPS NORTH | Tier 3 | MONTE RIO-1113 | 42811113 | FUSE | 7927 | 20231230 | 456 | 2302419 | 406 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 6090 | 38.5047 | -123.0052 | 3 SPANS LOAD SIDE OF 7927 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0149316 | OH | Sus | 31680507 | No | 2023 | DEC | Yes | Line to Line | 1900614 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | OTHER |  | 20130102 | 47 | 724284 | 684 | Distribution Circuit | Equipment Failure/Involved | Other | 38 | 25540 | 38.4034 | -120.6493 | 1 SPAN N/OF B527 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0001587 | OH | Sus | 41832834 | No | 2013 | JAN | Yes | Line to Ground | 99306156 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1701 | 163451701 | FUSE | L2659 | 20130219 | 1653 | 744211 | 472 | Distribution Circuit | Vegetation | Tree - bark fell into line | 345 | 155267 | 38.1373 | -120.4595 | Berry / 1853 / 840-7095: 798 Algiers st | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0011031 | OH | Sus | 41856435 | yes | 2013 | FEB | Yes | Line to Line | 99300281 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1102 | 162161102 | RECLOSER | 2646 | 20130220 | 1003 | 745076 | 510 | Distribution Circuit | Equipment Failure/Involved | Other | 417 | 103071 | 38.2993 | -120.6981 | MAINLINE AT FUCO 1299 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0011242 | OH | Sus | 41856821 | yes | 2013 | FEB | Yes | Line to Line | 99300067 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER | 3168 | 20130220 | 146 | 744751 | 794 | Distribution Circuit | Vegetation | Tree - fell into line | 877 | 31224 | 38.4143 | -120.6543 | 15815 PINE GROVE-VOLCANO RD- VOLCANO | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0011104 | OH | Sus | 30978350 | yes | 2013 | FEB | Yes | Line to Ground | 99300195 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L3713 | 20130315 | 652 | 757119 | 558 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 50 | 27900 | 38.4197 | -120.4887 | 16 POLES LD SIDE OF FUSES L3713 | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 13-0016794 | OH | Sus | 0 | No | 2013 | MAR | Yes | Line to Ground | 99296306 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | FUSE | 1519 | 20130424 | 1122 | 781045 | 965 | Distribution Circuit | 3rd Party | Vehicle | 84 | 79468 | 38.4353 | -120.7496 | L3161 | Clear-32 - 90 F | Pole-Wood | Broken, wire on object | 13-0026940 | OH | Sus | 30992203 | No | 2013 | APR | Yes | Line to Ground | 99288652 | PW | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | ELECTRA-1102 | 162161102 | OTHER |  | 20130626 | 1810 | 818017 | 509 | Distribution Circuit | Equipment Failure/Involved | Other | 1169 | 141469 | 38.3608 | -120.5661 | MBL HME REAR ENCO GAS STA ACR FRM CAL P BAR | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0042961 | OH | Sus | 0 | No | 2013 | JUN | Yes | Line to Ground | 99277465 | CSO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1704 | 163781704 | FUSE | L7523 | 20130710 | 2315 | 829516 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 162 | 25626 | 37.9364 | -120.62 | 1/P/N/OF L3583 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0046552 | OH | Sus | 31007860 | No | 2013 | JUL | Yes | Three Phase Fault | 99274800 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | OTHER |  | 20130923 | 1448 | 871860 | 199 | Distribution Circuit | Vegetation | Tree - fell into line | 223 | 38118 | 38.361 | -120.7524 | E/OF L6575 2 locations of troublle | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0064236 | OH | Sus | 0 | No | 2013 | SEP | Yes | Line to Ground | 99262289 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | L3803 | 20131001 | 1016 | 875960 | 599 | Distribution Circuit | 3rd Party | Vehicle | 233 | 29449 | 38.1116 | -120.5082 | N/OF METER#1009846495 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0066136 | OH | Sus | 31025379 | No | 2013 | OCT | Yes | Line to Line | 99260927 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | 1711 | 20131004 | 149 | 878035 | 379 | Distribution Circuit | Vegetation | Tree - fell into line | 145 | 27922 | 38.4982 | -120.5042 | SILVA- TONY: 21256 sierra circle-pioneer | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0067151 | OH | Sus | 0 | yes | 2013 | OCT | Yes | Line to Ground | 99260289 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L5681 | 20131015 | 1023 | 885041 | 547 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 12 | 6564 | 38.3876 | -120.447 | Machi- Andrew: 7980 SCHAAD RD- WILSEYVILE | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0069685 | OH | Sus | 31028552 | No | 2013 | OCT | Yes |  | 99258276 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 1277 | 20131207 | 120 | 921641 | 563 | Distribution Circuit | Equipment Failure/Involved | Other | 38 | 11824 | 38.2355 | -120.4994 | C/OF OF MCKINNEY DIGGINS RD & MCKINNEY DIGGINS PL | Snow-Below 32 F | Connector or Splice (OH) | Broken, wire on ground | 13-0081173 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Line | 99249032 | CSO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1701 | 163451701 | FUSE | 1623 | 20131207 | 1024 | 922662 | 364 | Distribution Circuit | Equipment Failure/Involved | Other | 264 | 96096 | 38.1245 | -120.4497 | L3347 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081336 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99248887 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1701 | 163451701 | FUSE | 1969 | 20131207 | 1708 | 923040 | 1319 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 3957 | 38.1075 | -120.4951 | 1ST SPAN LOAD SIDE 1969 | Partly cloudy-32 - 90 F | Cutout, fuse holder | Broken, wire on ground | 13-0081374 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99248801 | CFH | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | L3803 | 20131207 | 224 | 921783 | 168 | Distribution Circuit | Equipment Failure/Involved | Other | 233 | 39144 | 38.1116 | -120.5082 | Berry / 1853 / 840-7095: 2947 murphys grade rd | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081170 | OH | Sus | 0 | yes | 2013 | DEC | Yes |  | 99249035 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | 1639 | 20131207 | 446 | 921908 | 479 | Distribution Circuit | Environmental/External | Ice or snow | 50 | 23950 | 38.0925 | -120.4782 | METER 1004720871 | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081213 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99248997 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | L3319 | 20131207 | 333 | 921870 | 602 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 14432 | 38.0983 | -120.53 | Snowden / 1883 / 471-0057: 4418 ranch road | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081225 | OH | Sus | 0 | yes | 2013 | DEC | Yes |  | 99248983 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | OTHER |  | 20131207 | 927 | 922765 | 487 | Distribution Circuit | Equipment Failure/Involved | Other | 163 | 59361 | 38.2833 | -120.5572 | JESUS MARIA RD at FUSES 1289 | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0081303 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99248914 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 1051 | 20140121 | 835 | 944674 | 813 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 34 | 27642 | 38.4185 | -120.6471 | 2/P/N/OF MTR # 1004741030 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0005303 | OH | Sus | 31050832 | No | 2014 | JAN | Yes |  | 99243512 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 1391 | 20140125 | 1425 | 947652 | 790 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 41 | 32390 | 38.3305 | -120.5353 | METER #1004734377 - 1588 SIMPSON RD END OF THE ROAD- RAILROAD FLAT | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0006407 | OH | Sus | 31052233 | No | 2014 | JAN | Yes | Three Phase Fault | 99242795 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 4786 | 20140312 | 53 | 982849 | 868 | Distribution Circuit | Vegetation | Tree - fell into line | 180 | 46968 | 38.2321 | -120.5341 | Bennett Tom: 7043 TROUT LN | Heavy rain-32 - 90 F | Pole-Wood | Broken, wire on object | 14-0017406 | OH | Sus | 31062478 | yes | 2014 | MAR | Yes | Line to Line | 99235359 | PW | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L2303 | 20140312 | 219 | 982867 | 851 | Distribution Circuit | Vegetation | Tree - branch fell on line | 46 | 9820 | 38.4175 | -120.5975 | MTR #1005560465 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0017417 | OH | Sus | 31062473 | yes | 2014 | MAR | Yes | Line to Line | 99235353 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | OTHER |  | 20140312 | 234 | 982877 | 401 | Distribution Circuit | Vegetation | Tree - branch fell on line | 304 | 145622 | 38.4928 | -120.5131 | MTR #1004861686 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0017413 | OH | Sus | 42091067 | yes | 2014 | MAR | Yes | Line to Ground | 99235355 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER | 12256 | 20140312 | 623 | 982998 | 965 | Distribution Circuit | Vegetation | Tree - fell into line | 2084 | 604367 | 38.4439 | -120.509 | Borgen / 3080 / 602-6786: REAR 16470 MCKENZIE | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0017437 | OH | Sus | 0 | yes | 2014 | MAR | Yes | Multi-Fault | 99235336 | PW | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | RECLOSER | 4788 | 20140312 | 751 | 983119 | 739 | Distribution Circuit | Vegetation | Tree - fell into line | 781 | 374884 | 38.3316 | -120.5186 | De Valle / 1704 / 768-4600: 6821 RR FLAT RD/ | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0017470 | OH | Sus | 0 | yes | 2014 | MAR | Yes |  | 99235131 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 1341 | 20140315 | 1213 | 985063 | 307 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 89 | 27323 | 38.3173 | -120.5211 | 1159 TONETRAIL MTR#1004933640 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0018328 | OH | Sus | 42093855 | No | 2014 | MAR | Yes |  | 99234724 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | NORTH BRANCH-1101 | 163231101 | FUSE | 1115 | 20140316 | 652 | 985250 | 379 | Distribution Circuit | Equipment Failure/Involved | Other | 157 | 58105 | 38.2442 | -120.845 | Borgen / 3080 / 602-6786: 14337 HUNTER DR | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0018390 | OH | Sus | 42093926 | No | 2014 | MAR | Yes | Line to Line | 99234657 | CSO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 4786 | 20140415 | 1010 | 999750 | 812 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 735 | 104509 | 38.2321 | -120.5341 | Berry / 1853 / 840-7095: 17255 Jesus Maria Rd | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0025154 | OH | Sus | 31069548 | No | 2014 | APR | Yes | Line to Line | 99230101 | PW | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | OTHER |  | 20140430 | 1908 | 1008340 | 1002 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1002 | 38.3826 | -120.7433 | SILVA- TONY: 11970 new york ranch rd | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0028449 | OH | Sus | 42115463 | yes | 2014 | APR | Yes | Open Circuit | 99227818 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | FUSE | L1485 | 20140527 | 511 | 1024357 | 499 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 6302 | 38.3839 | -120.5611 | METER #1004807098 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0034334 | OH | Sus | 31078507 | No | 2014 | MAY | Yes | Line to Ground | 99223879 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1101 | 163541101 | RECLOSER | 1208 | 20140528 | 705 | 1025021 | 350 | Distribution Circuit | Animal | Squirrel | 478 | 60045 | 38.4373 | -120.8358 | MTR #1004974181 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 14-0034596 | OH | Sus | 31078774 | No | 2014 | MAY | Yes | Line to Ground | 99223721 | CSO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE | 1491 | 20140601 | 1227 | 1027061 | 704 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 156 | 28370 | 38.3987 | -120.6771 | BRASWELL- DAVID: 18121 bourbon st | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0035427 | OH | Sus | 31079751 | No | 2014 | JUN | Yes | Line to Line | 99223091 | PW | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | FUSE | L3801 | 20140606 | 1948 | 1029772 | 958 | Distribution Circuit | Vegetation | Tree - fell into line | 84 | 37557 | 38.4355 | -120.7474 | LINE & BUCK POLE SOURCE SIDE OF FCO L5671 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0036758 | OH | Sus | 31081234 | No | 2014 | JUN | Yes | Line to Ground | 99222290 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | OTHER |  | 20140715 | 900 | 1049638 | 567 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 30485 | 38.4205 | -120.5175 | Bell / 1914 / 770-3677: 914 Skull flat rd | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0044571 | OH | Sus | 42154654 | No | 2014 | JUL | Yes | Open Circuit | 99216326 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | IONE-1101 | 163881101 | FUSE | 305417 | 20140729 | 828 | ODB-9921 | 354 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 1 | 354 | 38.3742 | -120.9337 | 3/W/OF FUSES 305417 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0047686 | OH | Sus | 0 | No | 2014 | JUL | Yes |  | 99214432 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1102 | 163541102 | RECLOSER | 2642 | 20140731 | 1815 | 1059064 | 343 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 6174 | 38.5013 | -120.8481 | MTR #1004736134 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0048447 | OH | Sus | 42161937 | yes | 2014 | JUL | Yes | Line to Ground | 99213997 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | RECLOSER | 11212 | 20140803 | 1851 | 1060442 | 553 | Distribution Circuit | 3rd Party | Vehicle | 119 | 10085 | 38.0864 | -120.572 | CAROL KENNEDY AND HWY 49 | Overcast-32 - 90 F | Conductor, Overhead | On Ground | 14-0048840 | OH | Sus | 31092736 | No | 2014 | AUG | Yes | Three Phase Fault | 99213608 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1701 | 163451701 | FUSE | 8865 | 20140806 | 1435 | 1062237 | 305 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 915 | 38.1604 | -120.477 | C/OF SAN DOMINGO & SHEEP RANCH RD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0049534 | OH | Sus | 31093560 | No | 2014 | AUG | Yes | Line to Ground | 99213167 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 9149 | 20140810 | 1014 | 1063884 | 253 | Distribution Circuit | Equipment Failure/Involved | Other | 43 | 10879 | 38.2111 | -120.6848 | Bennett Tom: 5SPANS E/O GOLD STRIKE ON LEONARD RD | Clear-32 - 90 F | Insulator | Broken, wire on object | 14-0050134 | OH | Sus | 31094086 | No | 2014 | AUG | Yes |  | 99212723 | INS | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | 1573 | 20140814 | 1046 | 1066350 | 863 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 123 | 22433 | 38.0467 | -120.63 | BRASWELL- DAVID: 1281 Appaloosa Wy | Clear-32 - 90 F | Conductor, Overhead | On Ground | 14-0050974 | OH | Sus | 31095029 | No | 2014 | AUG | Yes | Line to Ground | 99212012 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 1535 | 20140914 | 2050 | 1081289 | 985 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 11035 | 38.3845 | -120.513 | MTR #1004935532 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0056893 | OH | Sus | 31101088 | No | 2014 | SEP | Yes | Line to Ground | 99207978 | PW | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | L1147 | 20140920 | 2005 | 1085021 | 893 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 5358 | 38.1049 | -120.4657 | MTR#1004821671 | Lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0058183 | OH | Sus | 0 | No | 2014 | SEP | Yes | Line to Line | 99207118 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | STANISLAUS-1702 | 162821702 | OCB | OCB | 20140920 | 1944 | 1085015 | 1338 | Distribution Circuit | Vegetation | Tree - fell into line | 11494 | 4724375 | 38.1401 | -120.37 | 6 SPANS SOUTH OF MTR #1004820426 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0058177 | OH | Sus | 0 | No | 2014 | SEP | Yes | Three Phase Fault | 99207041 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | RECLOSER | 12606 | 20140925 | 1005 | 1087775 | 356 | Distribution Circuit | Equipment Failure/Involved | Other | 319 | 67537 | 38.1805 | -120.9261 | S/S OF MTR 878R09 | Drizzle-32 - 90 F | Conductor, Overhead | On Ground | 14-0059349 | OH | Sus | 0 | yes | 2014 | SEP | Yes | None | 99206316 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | OCB | OCB | 20141011 | 1019 | 1096002 | 392 | Distribution Circuit | Animal | Bird found | 2882 | 388696 | 38.1702 | -120.6684 | DEVALLE- CLAY: L-13424 | Clear-32 - 90 F | Recloser | Broken, wire on ground | 14-0062956 | OH | Sus | 31106807 | No | 2014 | OCT | Yes | Line to Line | 99203984 | RCA | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1101 | 163541101 | RECLOSER | 4768 | 20141117 | 641 | 1113819 | 369 | Distribution Circuit | Animal | Bird found | 192 | 37523 | 38.4804 | -120.8598 | MTR# 1006423995 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0070350 | OH | Sus | 42275168 | No | 2014 | NOV | Yes | Line to Ground | 99199026 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1101 | 163541101 | FUSE | L3481 | 20141214 | 452 | 1140256 | 343 | Distribution Circuit | Equipment Failure/Involved | Other | 66 | 22638 | 38.42 | -120.8237 | LOC 14581 CHURCH ST. AMADOR CITY- MTR # 1005017167 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on object | 14-0076838 | OH | Sus | 0 | No | 2014 | DEC | Yes | Line to Ground | 99193185 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | OTHER |  | 20141231 | 1030 | 1157159 | 474 | Distribution Circuit | Equipment Failure/Involved | Other | 1486 | 504423 | 38.4778 | -120.521 | Crane / 2234 / 817-5392: 18505 TIMBERLIN RD | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0079722 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Open Circuit | 99189992 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L3851 | 20150211 | 225 | 1188265 | 527 | Distribution Circuit | 3rd Party | Vehicle | 52 | 18044 | 38.2632 | -120.4876 | 6829 SWISS RANCH ROAD- MOUNTAIN RANCH- CA- AMADOR COUNTY- ANGELS CAMP DISTRICT | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0012625 | OH | Sus | 0 | No | 2015 | FEB | Yes | Line to Line | 99182486 | PW | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L2013 | 20150315 | 2247 | 1203958 | 343 | Distribution Circuit | 3rd Party | Vehicle | 57 | 14520 | 38.3347 | -120.5327 | Bell D. / 1914 / 770-3677: 364 RIDGE RD RAILROAD FLAT RD | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0019709 | OH | Sus | 0 | No | 2015 | MAR | Yes | Line to Ground | 99178032 | PW | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 1257 | 20150330 | 624 | 1209603 | 587 | Distribution Circuit | 3rd Party | Vehicle | 241 | 21815 | 38.4415 | -120.5418 | MTR # 1009642348 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0022835 | OH | Sus | 31144444 | No | 2015 | MAR | Yes | Line to Ground | 99176311 | PW | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | OTHER |  | 20150425 | 1728 | 1225060 | 797 | Distribution Circuit | 3rd Party | Vehicle | 2 | 1594 | 38.3846 | -120.7864 | 12900 RIDGE RD at 7TH DAY CURCH | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0029586 | OH | Sus | 31150881 | yes | 2015 | APR | Yes | Line to Ground | 99171763 | PW | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L1701 | 20150601 | 1601 | 1242306 | 681 | Distribution Circuit | 3rd Party | Vehicle | 17 | 5541 | 38.1632 | -120.6483 | UNION MINE RD & HWY 49 | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0037733 | OH | Sus | 31158463 | No | 2015 | JUN | Yes | Line to Line | 99166126 | PW | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1103 | 163011103 | RECLOSER | 3152 | 20150616 | 207 | 1251448 | 878 | Distribution Circuit | 3rd Party | Vehicle | 140 | 13731 | 38.3597 | -120.8198 | MTR#1009322364 POLE WITH TRANSFORMER ON IT WAS HIT | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0041211 | OH | Sus | 31161547 | No | 2015 | JUN | Yes | Line to Ground | 99163487 | PW | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | L5423 | 20150627 | 2228 | 1257975 | 517 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 517 | 38.1206 | -120.6253 | 1 SPAN N/W OF MTR #5000016211 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0043798 | OH | Sus | 31164725 | No | 2015 | JUN | Yes | Line to Line | 99161554 | CO | OH | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | L7283 | 20150702 | 1726 | 1262081 | 696 | Distribution Circuit | Environmental/External | Lightning | 47 | 19192 | 38.314 | -120.2558 | Berry / 1853 / 840-7095: 4599 Bigfoot Cir | Partly Cloudy-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0045207 | OH | Sus | 31165781 | yes | 2015 | JUL | Yes | Line to Line | 1143624 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L3679 | 20150715 | 827 | 1268384 | 949 | Distribution Circuit | Vegetation | Tree - fell into line | 153 | 58620 | 38.4444 | -120.5319 | L3539 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0047581 | OH | Sus | 0 | No | 2015 | JUL | Yes | Line to Line | 1145381 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | OTHER | WIRE DOWN @ MTR 1004974732 | 20150731 | 2113 | 1281058 | 1384 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 337 | 33559 | 38.3817 | -120.5615 | MTR #1004974732 | Clear-32-90 F | Conductor, Overhead | On Ground | 15-0052033 | OH | Sus | 31173255 | No | 2015 | JUL | Yes | Line to Ground | 1148537 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | FUSE | 1369 | 20150830 | 1705 | 1297344 | 738 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 40298 | 38.4058 | -120.5359 | TAP 1 SPAN E/OF 1487 & JUST EAST OF HARD TAP at MTR 1004807425 TWD 1369 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0058273 | OH | Sus | 42460498 | No | 2015 | AUG | Yes | Line to Ground | 1152983 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 80930 | 20150910 | 2219 | 1303762 | 17249 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 351 | 744282 | 38.1945 | -120.5851 | FIELD | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 15-0060626 | OH | Sus | 0 | yes | 2015 | SEP | Yes | Line to Line | 1154676 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1102 | 163011102 | RECLOSER | 99214 | 20150925 | 1546 | 1312067 | 434 | Distribution Circuit | Vegetation | Tree - branch fell on line | 449 | 49114 | 38.3629 | -120.7749 | 1P/S/OF 517665 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0063655 | OH | Sus | 0 | No | 2015 | SEP | Yes | Line to Line | 1156938 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L1733 | 20150925 | 1231 | 1311974 | 997 | Distribution Circuit | Equipment Failure/Involved | Overhead | 16 | 8680 | 38.3147 | -120.5269 | 2P S/OF MTR 1004858779 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0063635 | OH | Sus | 0 | No | 2015 | SEP | Yes | Line to Line | 1156928 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L2685 | 20151006 | 2113 | 1318006 | 648 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 27216 | 38.2356 | -120.374 | STAGG DR AND LAKEMONT DR EAST INTERSECTION | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 15-0068520 | OH | Sus | 31189166 | No | 2015 | OCT | Yes | Line to Line | 1161061 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 1825 | 20151017 | 823 | 1323987 | 608 | Distribution Circuit | Environmental/External | Lightning | 32 | 19456 | 38.4138 | -120.6545 | MACHI- ANDREW: multi damages on crestview | Partly Cloudy-Lightning-32-90 F | Transformer (OH) | Broken, wire on ground | 15-0071215 | OH | Sus | 0 | yes | 2015 | OCT | Yes | Line to Line | 1162938 | TXO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1102 | 162161102 | FUSE | 2135 | 20151103 | 1504 | 1334793 | 574 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 19 | 5146 | 38.2997 | -120.6874 | MTR# 1008760777 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0075359 | OH | Sus | 31197345 | yes | 2015 | NOV | Yes | Line to Ground | 1166250 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 93116 | 20151119 | 2036 | 1345622 | 474 | Distribution Circuit | Equipment Failure/Involved | Overhead | 605 | 97926 | 38.3838 | -120.527 | MTR #1004805594 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0079403 | OH | Sus | 42573669 | No | 2015 | NOV | Yes | Line to Ground | 1169570 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CLAY-1101 | 163341101 | OCB | 1101/2 | 20151126 | 635 | 1348962 | 440 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1694 | 210766 | 38.3422 | -120.9349 | IONE 60KV TAP- POLE 0/12 GUY ACROSS PRI AND WIRE DOWN BET POLES 1/3 AND 1/2 ON MAIN LINE | Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 15-0081245 | OH | Sus | 42577479 | No | 2015 | NOV | Yes | Line to Line | 1171057 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L1749 | 20151203 | 1319 | 1352930 | 353 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 3177 | 38.3564 | -120.6496 | at MTR # 1004741366 | Overcast-Rain-32-90 F | Crossarm, Wood | Broken, wire on ground | 15-0082530 | OH | Sus | 31204115 | yes | 2015 | DEC | Yes | Line to Line | 1172215 | CAW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L2643 | 20151208 | 1241 | 1355825 | 224 | Distribution Circuit | 3rd Party | Other | 5 | 1120 | 38.2154 | -120.6748 | DEVALLE- CLAY: LOAD SIDE FUSES L-2643 7026 RAILROAD FLAT RD | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083435 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Ground | 1173059 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | FUSE | 11809 | 20151210 | 747 | 1357315 | 507 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 10647 | 38.1836 | -120.8903 | 7 P NW/OF 11809 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0083882 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1173524 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | OCB | 4786 | 20151222 | 59 | 1368388 | 660 | Distribution Circuit | Vegetation | Tree - fell into line | 2941 | 915497 | 38.4208 | -120.549 | MAIN LINE S/OF L1613 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086564 | OH | Sus | 0 | yes | 2015 | DEC | Yes | Line to Line | 1176558 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | 6851 | 20151223 | 1405 | 1370440 | 1549 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 18100 | 38.0944 | -120.5858 | 3P/S/OF MTR 1004240428 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 15-0086994 | OH | Sus | 0 | No | 2015 | DEC | Yes | Three Phase Fault | 1177059 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L3851 | 20160103 | 1802 | 1376245 | 20 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 1060 | 38.2633 | -120.4871 | 2 POLES N/E OF MTR #1004720562 | Overcast-32-90 F | Insulator | Broken, wire on object | 16-0002583 | OH | Sus | 0 | No | 2016 | JAN | Yes | Force Out | 1178509 | INS | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5379 | 20160106 | 2049 | 1379123 | 769 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 5953 | 38.2519 | -120.3527 | SILVA- TONY / 1705: 1455 lilac drive arnold | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003656 | OH | Sus | 31210820 | yes | 2016 | JAN | Yes | Line to Ground | 1179150 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 1311 | 20160112 | 1530 | 1382301 | 536 | Distribution Circuit | 3rd Party | Vehicle | 81 | 43416 | 38.3832 | -120.5328 | MTR# 1004974677 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0004864 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1180143 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CLAY-1103 | 163341103 | FUSE | 721 | 20160119 | 811 | 1386837 | 255 | Distribution Circuit | Vegetation | Tree - branch fell on line | 42 | 8224 | 38.308 | -120.974 | MTR# 1009848417 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006261 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1181188 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | OTHER | WIRE DOWN SS MTR #1004733972 | 20160119 | 2133 | 1388193 | 342 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 6624 | 38.4009 | -120.4973 | 2 SPANS SS MTR #1004733972 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0006691 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Open Circuit | 1181499 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L1149 | 20160206 | 1457 | 1399528 | 468 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 27 | 12636 | 38.4772 | -120.6269 | 18621 PONDEROSA WAY | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0011082 | OH | Sus | 31217942 | No | 2016 | FEB | Yes | Line to Line | 1184753 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1102 | 162991102 | FUSE | D3227 | 20160207 | 1851 | 1399867 | 655 | Distribution Circuit | 3rd Party | Vehicle | 41 | 26855 | 38.1397 | -120.8926 | 1P/N/OF 12397 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0011182 | OH | Sus | 31217991 | No | 2016 | FEB | Yes | Line to Ground | 1184845 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | FUSE | 1341 | 20160209 | 955 | 1400699 | 906 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 91 | 82446 | 38.3173 | -120.5209 | MTR #1004933642 & 1 P/W/OF MTR# 1004933.642 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0011552 | OH | Sus | 0 | No | 2016 | FEB | Yes | Line to Line | 1185108 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | ELECTRA-1102 | 162161102 | FUSE | 1299 | 20160218 | 701 | 1407903 | 512 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 8192 | 38.34 | -120.5899 | MTR# 1004840443 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013747 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186792 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | FUSE | L1639 | 20160306 | 446 | 1421089 | 590 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 5170 | 38.2673 | -120.5033 | Bennett Tom: 6085 CALAVERAS CIRCLE | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018291 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190155 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | ELECTRA-1102 | 162161102 | FUSE | 1299 | 20160311 | 1825 | 1428633 | 399 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 6384 | 38.34 | -120.5899 | 5 LD SIDE OF 1299 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020641 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1192013 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | RECLOSER | 3142 | 20160312 | 24 | 1428993 | 680 | Distribution Circuit | Environmental/External | Ice or snow | 1538 | 297003 | 38.3018 | -120.277 | WIRE DOWN POLE LD SIDE MID SPAN OF MTR# 1004652960 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020710 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1192083 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | 1485 | 20160313 | 1010 | 1430105 | 418 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 6270 | 38.4866 | -120.6121 | MTR #1004863193 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0020943 | OH | Sus | 42655924 | yes | 2016 | MAR | Yes | Open Circuit | 1192320 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | FUSE | L2363 | 20160415 | 1642 | 1451621 | 736 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4472 | 38.4567 | -120.7864 | REANO- ANTHONY: QUARTZ MNT | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0029045 | OH | Sus | 42680311 | yes | 2016 | APR | Yes | Line to Line | 1198202 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1102 | 163541102 | OTHER | WIRE DOWN SS OF MTR# 1004837569 | 20160415 | 1828 | 1451686 | 497 | Distribution Circuit | Vegetation | Tree - branch fell on line | 79 | 13823 | 38.5476 | -120.7431 | REANO- ANTHONY: at MTR # 1004837569 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0029047 | OH | Sus | 42680307 | yes | 2016 | APR | Yes | Line to Ground | 1198204 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | OTHER | WIRE DOWN 1 P/E/OF 2227 | 20160422 | 1411 | 1455963 | 349 | Distribution Circuit | Equipment Failure/Involved | Overhead | 433 | 110405 | 38.0915 | -120.4822 | 1 P/E/OF 2227 | Overcast-Rain-32-90 F | Transformer (OH) | Broken, wire on ground | 16-0030729 | OH | Sus | 0 | yes | 2016 | APR | Yes | Open Circuit | 1199401 | TXO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | FUSE | 1417 | 20160423 | 1025 | 1456639 | 775 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2118 | 38.3245 | -120.507 | MTR# 1008760565 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0030926 | OH | Sus | 0 | No | 2016 | APR | Yes | Line to Line | 1199590 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | OTHER | WIRE DOWN HOT @ MTR#100499747 | 20160424 | 2035 | 1457509 | 847 | Distribution Circuit | Environmental/External | Lightning | 27 | 5625 | 38.4451 | -120.7083 | MTR #1004979747 | Overcast-Drizzle-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0031146 | OH | Sus | 0 | yes | 2016 | APR | Yes | Open Circuit | 1199824 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | FUSE | L3887 | 20160424 | 2026 | 1457497 | 299 | Distribution Circuit | Environmental/External | Lightning | 6 | 1794 | 38.4417 | -120.7024 | L3887 | Overcast-Drizzle-Lightning-32-90 F | Transformer (OH) | Broken, wire on ground | 16-0031156 | OH | Sus | 0 | yes | 2016 | APR | Yes | Line to Line | 1199835 | TXO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 1601 | 20160425 | 1129 | 1458393 | 480 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 3 | 1440 | 38.2662 | -120.5857 | 8 SPANS LD SIDE OF MTR# 1009024466 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0031342 | OH | Sus | 0 | yes | 2016 | APR | Yes | Line to Ground | 1199993 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | OCB | 1102/2 | 20160425 | 1331 | 1458561 | 338 | Distribution Circuit | Environmental/External | Lightning | 4589 | 208981 | 38.4128 | -120.6607 | R283 | Partly Cloudy-32-90 F | Regulator | Broken, wire on ground | 16-0031326 | OH | Sus | 0 | yes | 2016 | APR | Yes | Force Out | 1199984 | REG | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 83331 | 20160430 | 630 | 1461941 | 446 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 2230 | 38.3503 | -120.5124 | MTR 1008715744 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0032820 | OH | Sus | 31235538 | yes | 2016 | APR | Yes | Line to Line | 1201087 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | 9825 | 20160524 | 1236 | 1475918 | 234 | Distribution Circuit | 3rd Party | Vehicle | 87 | 10678 | 38.0811 | -120.668 | 5P SS MTR #1008707903 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0038096 | OH | Sus | 0 | No | 2016 | MAY | Yes | Line to Ground | 1205070 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L1971 | 20160529 | 1318 | 1478884 | 399 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 17 | 5019 | 38.4607 | -120.5192 | 1008924127 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0039612 | OH | Sus | 31242865 | No | 2016 | MAY | Yes | Three Phase Fault | 1206238 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | FUSE | L3161 | 20160615 | 1309 | 1489479 | 409 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 23963 | 38.4433 | -120.7568 | MTR# 1008907771 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0043476 | OH | Sus | 0 | No | 2016 | JUN | Yes | Line to Ground | 1209214 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5111 | 20160618 | 2153 | 1492015 | 554 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4432 | 38.2328 | -120.349 | 1 SPAN WEST OF MTR # 1004163032 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0044284 | OH | Sus | 0 | No | 2016 | JUN | Yes | Line to Line | 1209749 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | OTHER | WIRE DOWN 3 SE/OF L6633 | 20160622 | 2346 | 1494395 | 482 | Distribution Circuit | Equipment Failure/Involved | Overhead | 115 | 33595 | 38.0426 | -120.5157 | 3 SE/OF L6633 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0045212 | OH | Sus | 42729949 | No | 2016 | JUN | Yes | Line to Ground | 1210482 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L1641 | 20160629 | 2144 | 1498659 | 871 | Distribution Circuit | Vegetation | Tree - fell into line | 121 | 32325 | 38.2679 | -120.5027 | MTR#5000058458 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0046761 | OH | Sus | 0 | No | 2016 | JUN | Yes | Line to Line | 1211569 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L3849 | 20160725 | 1532 | 1515845 | 705 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 19951 | 38.3426 | -120.6963 | 3 N/OF MTR#1004804388 | Clear-Above 90 | Conductor, Overhead | On Ground | 16-0052398 | OH | Sus | 31259507 | yes | 2016 | JUL | Yes | Line to Ground | 1215580 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1102 | 162991102 | FUSE | 93139 | 20160729 | 1529 | 1518569 | 594 | Distribution Circuit | 3rd Party | Vehicle | 11 | 6534 | 38.1604 | -120.8539 | 2 S/OF 93139 | Clear-Above 90 | Pole-Wood | Broken, wire on ground | 16-0053688 | OH | Sus | 0 | No | 2016 | JUL | Yes | Line to Ground | 1216438 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | FUSE | 11653 | 20160916 | 744 | 1542606 | 391 | Distribution Circuit | 3rd Party | Vehicle | 51 | 7566 | 38.1496 | -120.945 | MTR#1004160881 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0065085 | OH | Sus | 0 | No | 2016 | SEP | Yes | Line to Line | 1224063 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L2875 | 20160922 | 1058 | 1546224 | 247 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 10 | 2470 | 38.2414 | -120.5816 | 10351 STOREY RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0066724 | OH | Sus | 0 | No | 2016 | SEP | Yes | Line to Ground | 1225269 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE | L699 | 20161016 | 1358 | 1562979 | 390 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 5878 | 38.3951 | -120.6789 | MTR 1004977967 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0072896 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1229930 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2101 | 163692101 | FUSE | 4913 | 20161016 | 2120 | 1563737 | 438 | Distribution Circuit | Vegetation | Tree - fell into line | 136 | 59568 | 38.4203 | -120.0971 | MTR 1004655410 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0073060 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Line | 1230087 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L1725 | 20161016 | 2231 | 1563804 | 1007 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 31217 | 38.4831 | -120.5485 | 1 S/OF L3291 | Overcast-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0073085 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Line | 1230109 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1102 | 163541102 | OTHER | WIRE DOWN @ 16600 TYLER RD | 20161118 | 17 | 1583771 | 409 | Distribution Circuit | Equipment Failure/Involved | Overhead | 53 | 21677 | 38.5231 | -120.7194 | 16600 TYLER RD FIDDLETON CA | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0080737 | OH | Sus | 42882054 | yes | 2016 | NOV | Yes | Line to Ground | 1235856 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | OTHER | WIRE DOWN HOT AT MTR #1006417107 | 20161119 | 1950 | 1585409 | 563 | Distribution Circuit | Vegetation | Tree - fell into line | 682 | 139923 | 38.2948 | -120.5023 | MTR #1006417107 (4354 ROLLING OAK DR) | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081190 | OH | Sus | 42882762 | yes | 2016 | NOV | Yes | Line to Ground | 1236210 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | FUSE | L2775 | 20161123 | 511 | 1587628 | 309 | Distribution Circuit | Vegetation | Tree - branch fell on line | 23 | 4020 | 38.4267 | -120.7159 | 3 SS/OF TRASNF MTR# 1004804486 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0081866 | OH | Sus | 42884040 | No | 2016 | NOV | Yes | Line to Ground | 1236716 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | OTHER | L2229 | 20161127 | 702 | 1589715 | 292 | Distribution Circuit | Animal | Bird found | 6 | 1752 | 38.3523 | -120.7468 | 1 N/OF FUCO L2229 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0082411 | OH | Sus | 42884853 | yes | 2016 | NOV | Yes | Open Circuit | 1237166 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5009 | 20161127 | 535 | 1589679 | 378 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 7938 | 38.2641 | -120.3217 | 1654 PEBBLE BEACH WAY | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0082416 | OH | Sus | 31285764 | yes | 2016 | NOV | Yes | Line to Line | 1237168 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L1613 | 20161129 | 1256 | 1591392 | 446 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 3 | 1338 | 38.3922 | -120.5236 | MCCARTNEY MARK 2024: LOAD SIDE OF L1613 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0082957 | OH | Sus | 42885891 | No | 2016 | NOV | Yes | Three Phase Fault | 1237584 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L3849 | 20161223 | 1401 | 1609833 | 674 | Distribution Circuit | Vegetation | Tree - fell into line | 55 | 21194 | 38.3426 | -120.6963 | 5 SPANS EAST OF TX MTR #1004937836 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0086819 | OH | Sus | 0 | No | 2016 | DEC | Yes | Line to Line | 1242002 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L2049 | 20170124 | 714 | 1665577 | 2076 | Distribution Circuit | Vegetation | Tree - fell into line | 118 | 244968 | 38.2997 | -120.2717 | LD SIDE L2049 | Partly Cloudy-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0014374 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1253095 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 1391 | 20170206 | 1308 | 1676727 | 397 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 16674 | 38.3307 | -120.5351 | JUST LD SIDE 1391 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017847 | OH | Sus | 31304205 | yes | 2017 | FEB | Yes | Three Phase Fault | 1255730 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER | 3172 | 20170208 | 623 | 1681394 | 608 | Distribution Circuit | Vegetation | Tree - fell into line | 2926 | 420168 | 38.4101 | -120.6517 | L2149 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0018858 | OH | Sus | 31304629 | yes | 2017 | FEB | Yes | Three Phase Fault | 1256602 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | RECLOSER | 12606 | 20170210 | 922 | 1684797 | 387 | Distribution Circuit | Equipment Failure/Involved | Overhead | 321 | 71727 | 38.1805 | -120.9262 | 3 TO 4 SPANS WEST OF C3440 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019838 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1257280 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 1419 | 20170213 | 645 | 1687085 | 370 | Distribution Circuit | Equipment Failure/Involved | Overhead | 133 | 49210 | 38.2128 | -120.5592 | MTR 1006983823 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0020638 | OH | Sus | 31305376 | No | 2017 | FEB | Yes | Line to Line | 1257987 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | STANISLAUS-1701 | 162821701 | FUSE | 2697 | 20170226 | 625 | 1714246 | 1026 | Distribution Circuit | Equipment Failure/Involved | Overhead | 7 | 7182 | 38.1508 | -120.4404 | 1N OF 2697 | Clear-Below 32 F | Pole-Wood | Broken, wire on ground | 17-0026851 | OH | Sus | 0 | No | 2017 | FEB | Yes | Line to Line | 1263551 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 11236 | 20170227 | 801 | 1714824 | 734 | Distribution Circuit | 3rd Party | Vehicle | 181 | 17834 | 38.1697 | -120.6677 | 4 P/SE/OF L4131 | Partly Cloudy-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0026980 | OH | Sus | 0 | No | 2017 | FEB | Yes | Line to Line | 1263658 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2102 | 163692102 | FUSE | L1695 | 20170228 | 808 | 1715732 | 1815 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 3630 | 38.3556 | -120.2074 | 1 LD SIDE OF L1695 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0027326 | OH | Sus | 31308301 | No | 2017 | FEB | Yes | Line to Line | 1263941 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | 91563 | 20170308 | 927 | 1722369 | 430 | Distribution Circuit | Vegetation | Tree - fell into line | 50 | 17279 | 38.3186 | -120.2549 | LD SIDE OF MTR 1004242168 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0029389 | OH | Sus | 31311290 | No | 2017 | MAR | Yes | Line to Line | 1265529 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | OTHER | WIRE DOWN 3 SPANS SW OF MTR# 1004974986 | 20170317 | 710 | 1728905 | 349 | Distribution Circuit | Animal | Bird found | 1970 | 89126 | 38.3603 | -120.7527 | 3 SPANS SW OF MTR# 1004974986 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0031432 | OH | Sus | 42972728 | No | 2017 | MAR | Yes | Open Circuit | 1267045 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER | OJ @ 15585 HINTON RD | 20170325 | 1111 | 1735314 | 463 | Distribution Circuit | Vegetation | Tree - fell into line | 69 | 6679 | 38.4345 | -120.568 | at 15585 HINTON RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0033710 | OH | Sus | 31314730 | yes | 2017 | MAR | Yes | Open Circuit | 1268660 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L3335 | 20170409 | 740 | 1753424 | 159 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 159 | 38.236 | -120.5825 | 2 POLES LOAD SIDE OF TRANSFORMER MTR #1010146917 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0038429 | OH | Sus | 0 | No | 2017 | APR | Yes | Line to Line | 1272484 | CSO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | RECLOSER | 91216 | 20170424 | 1151 | 1765994 | 932 | Distribution Circuit | Equipment Failure/Involved | Overhead | 427 | 63099 | 38.4349 | -120.7501 | at FUCO 70951 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0042499 | OH | Sus | 0 | No | 2017 | APR | Yes | Three Phase Fault | 1275546 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | ELECTRA-1102 | 162161102 | FUSE | 92251 | 20170511 | 1515 | 1780195 | 715 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 715 | 38.3436 | -120.5834 | JUST E/OF 92251 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0047377 | OH | Sus | 31325324 | No | 2017 | MAY | Yes | Line to Line | 1279125 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L6515 | 20170609 | 2150 | 1800879 | 671 | Distribution Circuit | 3rd Party | Vehicle | 3 | 2013 | 38.461 | -120.5263 | 1 W/OF FUCO L6515 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0054145 | OH | Sus | 0 | No | 2017 | JUN | Yes | Line to Line | 1284037 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | OTHER | WIRE DOWN 1/P/NOF & 1/P/E/OF MTR # 1004935044 | 20170622 | 936 | 1814850 | 428 | Distribution Circuit | Equipment Failure/Involved | Overhead | 59 | 22732 | 38.3975 | -120.4724 | 1/P/N/OF & 1/P/E/OF MTR # 1004935044 | Clear-Heat Wave-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0057686 | OH | Sus | 0 | yes | 2017 | JUN | Yes | Line to Ground | 1286967 | CAW | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 3 | ELECTRA-1102 | 162161102 | FUSE | L5783 | 20170702 | 1151 | 1822355 | 448 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 20 | 7740 | 38.3459 | -120.5659 | DORRIS RYAN 1914: 4556 INDEPENDENCE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0060070 | OH | Sus | 43048182 | No | 2017 | JUL | Yes | Line to Line | 1288750 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1102 | 162991102 | FUSE | L3665 | 20170707 | 1812 | 1825836 | 423 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 1593 | 38.1365 | -120.8679 | ON 1 PHASE TAP 2 E/OF L3665 | Clear-Drizzle-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0061333 | OH | Sus | 43052361 | yes | 2017 | JUL | Yes | Line to Ground | 1289539 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | 1557 | 20170710 | 1850 | 1828569 | 550 | Distribution Circuit | Equipment Failure/Involved | Other | 11 | 6050 | 38.354 | -120.7422 | REANO- ANTHONY // 2009: 1 S/E OF MTR# 1009024412 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0061874 | OH | Sus | 31336353 | No | 2017 | JUL | Yes | Line to Ground | 1289987 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | OTHER | WIRE DWN 4 NW/OF MTR 1004804388 | 20170724 | 1952 | 1839110 | 530 | Distribution Circuit | Vegetation | Tree - bark fell into line | 55 | 14281 | 38.3528 | -120.7112 | 4 NW/OF MTR 1004804388 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0065145 | OH | Sus | 31338986 | No | 2017 | JUL | Yes | Open Circuit | 1292432 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L3233 | 20170726 | 955 | 1840145 | 453 | Distribution Circuit | Vegetation | Tree - fell into line | 6 | 2718 | 38.382 | -120.5086 | 2 POLES LD SIDE L3233 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0065604 | OH | Sus | 0 | No | 2017 | JUL | Yes | Line to Line | 1292751 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | NORTH BRANCH-1101 | 163231101 | OTHER | WIRE DOWN S/S OF MTR#1005574893 | 20170804 | 1009 | 1846312 | 326 | Distribution Circuit | Environmental/External | Lightning | 398 | 4134 | 38.2171 | -120.8411 | SS OF MTR 1005574893 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0068000 | OH | Sus | 0 | No | 2017 | AUG | Yes | Open Circuit | 1294353 | CSO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5369 | 20170806 | 1856 | 1847455 | 616 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 10472 | 38.2558 | -120.3537 | 3 S/OF FUCO L5369 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0068306 | OH | Sus | 31341116 | No | 2017 | AUG | Yes | Multi-Fault | 1294587 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 93116 | 20170812 | 336 | 1850967 | 682 | Distribution Circuit | Vegetation | Tree - fell into line | 341 | 41834 | 38.3838 | -120.527 | 2PE/OF R281 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0069789 | OH | Sus | 0 | No | 2017 | AUG | Yes | Three Phase Fault | 1295624 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L2313 | 20170828 | 458 | 1861006 | 450 | Distribution Circuit | Vegetation | Tree - fell into line | 112 | 37600 | 38.4171 | -120.5863 | MTR #1004932770 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0073275 | OH | Sus | 0 | yes | 2017 | AUG | Yes | Line to Ground | 1298152 | CAW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1701 | 162821701 | FUSE | 1113 | 20170828 | 948 | 1861247 | 196 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 4116 | 38.2084 | -120.3676 | Bennett Tom / 1851: 1 POLE S/E OF C/O 1113 | Clear-Heat Wave-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0073393 | OH | Sus | 0 | yes | 2017 | AUG | Yes | Line to Line | 1298233 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE | L4043 | 20171103 | 1549 | 1915405 | 1451 | Distribution Circuit | Equipment Failure/Involved | Overhead | 12 | 5652 | 38.4265 | -120.6929 | MTR 5000059906 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0092535 | OH | Sus | 0 | yes | 2017 | NOV | Yes | Line to Line | 1312048 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER | 1305 | 20171117 | 518 | 1924527 | 478 | Distribution Circuit | Vegetation | Tree - fell into line | 94 | 44932 | 38.4009 | -120.5045 | REANO- ANTHONY // 2009: 6 LD SIDE 1305 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0095804 | OH | Sus | 0 | yes | 2017 | NOV | Yes | Line to Ground | 1314572 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | 2681 | 20171206 | 823 | 1937158 | 364 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 364 | 38.3199 | -120.2635 | SILVA- TONY / 1705: c/o 2681 across from USFS fire station DORRINGTON | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0100245 | OH | Sus | 31368584 | No | 2017 | DEC | Yes | Line to Ground | 1317949 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1102 | 162161102 | RECLOSER | 4756 | 20180106 | 432 | 3051 | 796 | Distribution Circuit | Vegetation | Tree - fell into line | 524 | 41613 | 38.3164 | -120.713 | 3 SPANS NORTH WEST OF 4756 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on object | 18-0003970 | OH | Sus | 43245624 | No | 2018 | JAN | Yes | Three Phase Fault | 1323411 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | ELECTRA-1102 | 162161102 | FUSE | L5783 | 20180123 | 610 | 12282 | 437 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 4007 | 38.3456 | -120.5659 | MTR 1004933343 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0008066 | OH | Sus | 0 | No | 2018 | JAN | Yes | Line to Ground | 1326008 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | OTHER | 67293 | 20180205 | 1751 | 19826 | 453 | Distribution Circuit | Equipment Failure/Involved | Overhead | 223 | 33935 | 38.3628 | -120.7315 | 1 SPAN E/OF L6575 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0011684 | OH | Sus | 43267571 | No | 2018 | FEB | Yes | Line to Ground | 1328354 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | RECLOSER | 97924 | 20180227 | 700 | 32522 | 75 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 1500 | 38.3232 | -120.2538 | 7 E/OF 4691 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0017600 | OH | Sus | 0 | yes | 2018 | FEB | Yes | Line to Line | 1332333 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 3168 | 20180302 | 507 | 35947 | 191 | Distribution Circuit | 3rd Party | Vehicle | 1064 | 119266 | 38.4142 | -120.6538 | 1 E/OF L2471 | Overcast-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 18-0018972 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333324 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | OTHER | WIRE DOWN 1 N/O 35576 | 20180303 | 1023 | 37379 | 299 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 11986 | 38.418 | -120.6133 | MTR #1004737494- 1 N/O 35576 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019392 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Open Circuit | 1333597 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | 1711 | 20180303 | 831 | 37253 | 564 | Distribution Circuit | Vegetation | Tree - fell into line | 147 | 77288 | 38.4983 | -120.5045 | at MTR#1004856510 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019409 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333611 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L685 | 20180304 | 607 | 37893 | 437 | Distribution Circuit | Vegetation | Tree - branch fell on line | 47 | 8821 | 38.4011 | -120.6359 | 2 SPANS E OF at MTR#1004840824 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0019550 | OH | Sus | 0 | No | 2018 | MAR | Yes | Line to Ground | 1333745 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CLAY-1103 | 163341103 | OCB | 1103/2 | 20180306 | 1757 | 39447 | 400 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1435 | 142000 | 38.3422 | -120.935 | REANO- ANTHONY // 2009: 3 ld side 1495 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0020396 | OH | Sus | 43290263 | No | 2018 | MAR | Yes | Multi-Fault | 1334390 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2101 | 163692101 | RECLOSER | 10416 | 20180317 | 125 | 48277 | 5125 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 292125 | 38.4983 | -120.2183 | S/OF MTR 1006494939 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0024229 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1336934 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L3843 | 20180321 | 1553 | 49639 | 777 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2856 | 38.2313 | -120.7083 | at MTR#1005428037 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 18-0025152 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1337366 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | OTHER | WIRE DOWN LD SIDE L1137 | 20180418 | 1152 | 69502 | 335 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 2010 | 38.4024 | -120.4877 | BETWEEN 3RD & 4TH POLE LD SIDE OF L1137 | Overcast-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0033415 | OH | Sus | 31389222 | No | 2018 | APR | Yes | Open Circuit | 1343537 | CAW | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 93116 | 20180526 | 1323 | 94502 | 555 | Distribution Circuit | Vegetation | Tree - fell into line | 611 | 77540 | 38.3838 | -120.527 | 77204 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0044636 | OH | Sus | 31393676 | No | 2018 | MAY | Yes | Line to Line | 1351727 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER | 3172 | 20180611 | 1948 | 106752 | 633 | Distribution Circuit | 3rd Party | Vehicle | 2928 | 364608 | 38.4101 | -120.6517 | MTR #1004804494 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0049807 | OH | Sus | 31395449 | No | 2018 | JUN | Yes | Line to Ground | 1355812 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | TRIP-SAVER | 1391 | 20180716 | 1031 | 132762 | 683 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 42 | 28686 | 38.3306 | -120.5352 | MTR #1004734375 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0060187 | OH | Sus | 0 | No | 2018 | JUL | Yes | Three Phase Fault | 1364140 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L5681 | 20180717 | 944 | 133661 | 378 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 5292 | 38.3878 | -120.4469 | MTR #1008768437 | Clear-32-90F | Conductor, Overhead | On Ground | 18-0060592 | OH | Sus | 31400217 | yes | 2018 | JUL | Yes | Line to Line | 1364442 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | OTHER | WIRE DOWN S/OF 1167 | 20180718 | 2043 | 135145 | 511 | Distribution Circuit | Vegetation | Tree - fell into line | 607 | 75822 | 38.2291 | -120.5411 | S/OF 1167 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 18-0061254 | OH | Sus | 31400334 | yes | 2018 | JUL | Yes | Line to Ground | 1364864 | CAW | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 2111 | 20180718 | 114 | 134352 | 642 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 6420 | 38.3631 | -120.5613 | REANO- ANTHONY // 2009: 2 SPANS N E OF LINE & BUCK at MTR# 1004978425 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 18-0060882 | OH | Sus | 31400322 | yes | 2018 | JUL | Yes | Line to Ground | 1364592 | CAW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1102 | 163541102 | FUSE | L3821 | 20180719 | 402 | 135246 | 683 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 3590 | 38.4976 | -120.7714 | MACHI- ANDREW // 1852: near 20050 quartz mnt rd | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0061291 | OH | Sus | 0 | yes | 2018 | JUL | Yes | Line to Line | 1364899 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1701 | 162821701 | FUSE | 1681 | 20180730 | 1436 | 145323 | 745 | Distribution Circuit | Vegetation | Tree - fell into line | 24 | 17880 | 38.1987 | -120.3647 | DEVALLE- CLAY 1704: FUSES 1681 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 18-0065131 | OH | Sus | 31401706 | No | 2018 | JUL | Yes | Multi-Fault | 1367828 | CAW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1701 | 162821701 | JUMPER | DDE 1SP S/OF 1681 | 20180730 | 2130 | 145552 | 325 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 650 | 38.198 | -120.3648 | 1681 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0065131 | OH | Sus | 31401706 | No | 2018 | JUL | Yes | Force Out | 1367869 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1701 | 163451701 | TRIP-SAVER | 1623 | 20180903 | 1334 | 167457 | 540 | Distribution Circuit | Vegetation | Tree - branch fell on line | 276 | 149040 | 38.1247 | -120.45 | 1203 GREEN MEADOW CT | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0075993 | OH | Sus | 43453134 | No | 2018 | SEP | Yes | Line to Line | 1375348 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L1631 | 20181007 | 843 | 190049 | 943 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 53751 | 38.2641 | -120.5842 | DORRIS RYAN 1914: 2 POLES N/O C/O's L5253 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0087904 | OH | Sus | 31411666 | yes | 2018 | OCT | Yes | Line to Line | 1383832 | PW | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L3851 | 20181017 | 1414 | 197492 | 726 | Distribution Circuit | 3rd Party | Vehicle | 53 | 13192 | 38.2633 | -120.4871 | 6323 SWISS RANCH | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0091459 | OH | Sus | 0 | No | 2018 | OCT | Yes | Line to Ground | 1386450 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | FUSE | 11783 | 20181019 | 906 | 198424 | 224 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 672 | 38.1813 | -120.9632 | BEYOND 11783 BET WHERE LINE BUCKS TO THE WEST AND EOL | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0092066 | OH | Sus | 43511611 | No | 2018 | OCT | Yes | Line to Ground | 1386827 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | FUSE | 65557 | 20181022 | 1948 | 200452 | 571 | Distribution Circuit | 3rd Party | Vehicle | 3 | 1713 | 38.4246 | -120.756 | 2 POLE N/OF MTR 1004732928 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0093086 | OH | Sus | 0 | No | 2018 | OCT | Yes | Line to Line | 1387465 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | RECLOSER | 3166 | 20181123 | 1214 | 222905 | 266 | Distribution Circuit | Vegetation | Tree - fell into line | 330 | 39424 | 38.4065 | -120.6704 | 3 E/OF MTR# 1004933366 ON MANZANITA WAY | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0102567 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Line | 1394698 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1701 | 163451701 | TRIP-SAVER | 6807 | 20181128 | 2324 | 227115 | 139 | Distribution Circuit | Vegetation | Tree - fell into line | 186 | 25854 | 38.1241 | -120.4507 | AT MTR #1005419154 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0104666 | OH | Sus | 43587893 | yes | 2018 | NOV | Yes | Line to Ground | 1395980 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | 9825 | 20181221 | 2018 | 245366 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 91 | 12040 | 38.081 | -120.668 | 7240 TAPADERO ST | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110299 | OH | Sus | 43621105 | No | 2018 | DEC | Yes | Line to Ground | 1401320 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | TRIP-SAVER | 1341 | 20181231 | 1606 | 250846 | 2691 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 16801 | 38.3173 | -120.5209 | MTR# 1008760756 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0111275 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Ground | 1402530 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1102 | 163011102 | OTHER | WIRE DOWN | 20190103 | 654 | 252303 | 350 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1254 | 100562 | 38.3709 | -120.7863 | S/E OF L7467 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0003906 | OH | Sus | 43625061 | No | 2019 | JAN | Yes | Line to Ground | 1402836 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | RECLOSER | 4788 | 20190103 | 1340 | 252606 | 979 | Distribution Circuit | 3rd Party | Vehicle | 710 | 207088 | 38.3314 | -120.5187 | 1 N/OF MTR# 1004818961 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0004169 | OH | Sus | 31420230 | No | 2019 | JAN | Yes | Line to Ground | 1402924 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | 1151 | 20190107 | 807 | 259085 | 581 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 1922 | 38.2774 | -120.3184 | LINE & BUCK LD SIDE OF 1151 GOING SOUTH | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0005736 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Three Phase Fault | 1404145 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | JUMPER | WIRE DOWN 2P/W/OF LB FEEDING MTR 1008714431 | 20190115 | 1631 | 266167 | 613 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1839 | 38.2743 | -120.5266 | 2P/W/OF LB FEEDING MTR 1008714431 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0009271 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Open Circuit | 1406408 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1701 | 163451701 | FUSE | L2969 | 20190120 | 2211 | 277814 | 1089 | Distribution Circuit | Equipment Failure/Involved | Overhead | 5 | 5445 | 38.1385 | -120.4131 | 3 N/OF L2969 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012775 | OH | Sus | 0 | yes | 2019 | JAN | Yes | Line to Line | 1409107 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | RECLOSER | 6074 | 20190127 | 1709 | 282207 | 237 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1419 | 113230 | 38.3928 | -120.7927 | SHAKE RIDGE & STONE JUGG | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0014840 | OH | Sus | 43659377 | No | 2019 | JAN | Yes | Line to Ground | 1410250 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | OTHER | WIRE DOWN @ MTR# 1004979750 | 20190128 | 1859 | 282898 | 397 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1844 | 92290 | 38.4417 | -120.709 | MTR# 1004979750 - 17125 SHAKE RIDGE RD | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0015289 | OH | Sus | 0 | No | 2019 | JAN | Yes | Force Out | 1410431 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L2065 | 20190203 | 455 | 288435 | 717 | Distribution Circuit | Vegetation | Tree - fell into line | 333 | 238761 | 38.3008 | -120.2732 | LD SIDE OF L2065 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0017438 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1411854 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L3851 | 20190206 | 1948 | 295181 | 2528 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 96064 | 38.2633 | -120.4871 | LD SIDE OF L3851 | Partly Cloudy-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019539 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413439 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 1425 | 20190206 | 1948 | 295191 | 1339 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 64272 | 38.2709 | -120.4948 | LD SIDE | Partly Cloudy-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019543 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413442 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 35576 | 20190206 | 118 | 293818 | 1203 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 67368 | 38.4176 | -120.6137 | MACHI- ANDREW // 1852: 14500 pioneer volcano rd | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0018803 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1412869 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1101 | 163201101 | FUSE | 1315 | 20190206 | 2216 | 294936 | 3654 | Distribution Circuit | Vegetation | Tree - branch fell on line | 53 | 187097 | 38.3776 | -120.554 | MTR 1004980757 | Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019445 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413379 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | 1391 | 20190206 | 2040 | 295088 | 2275 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 91000 | 38.3306 | -120.5352 | AT MTR #1010390315 | Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019509 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413407 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | JUMPER | OJ 1 E/OF MTR# 1004732874 | 20190206 | 2040 | 295420 | 2924 | Distribution Circuit | Equipment Failure/Involved | Overhead | 10 | 29240 | 38.336 | -120.5283 | MTR# 1004732874 | Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0019656 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1413506 | PW | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L2013 | 20190206 | 2040 | 295094 | 1025 | Distribution Circuit | Equipment Failure/Involved | Overhead | 51 | 52275 | 38.3346 | -120.5325 | MTR# 1004732874 | Fog-Below 32 F | Pole-Wood | Broken, wire on ground | 19-0019673 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413510 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1101 | 163201101 | TRIP-SAVER | 1369 | 20190206 | 1509 | 294489 | 2936 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 217264 | 38.4058 | -120.5359 | 3/P/NE/1487- 2/P/NE 1487- AT C/OUT POLE 1487 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0019787 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413574 | CAW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L5217 | 20190207 | 1024 | 295217 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1088 | 38.2786 | -120.5069 | 2SP LOAD SIDE OF L5217 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0019551 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413449 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L5701 | 20190207 | 1825 | 295676 | 1195 | Distribution Circuit | 3rd Party | Vehicle | 34 | 8762 | 38.4046 | -120.6618 | 2 SE/OF MTR 1005450797 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0019796 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413581 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | 6829 | 20190207 | 1207 | 295356 | 7368 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 36840 | 38.3422 | -120.4522 | 6829 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0019696 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413520 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L3231 | 20190207 | 1105 | 295282 | 3205 | Distribution Circuit | Vegetation | Tree - fell into line | 9 | 27937 | 38.3802 | -120.5157 | MTR 1004980198 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0020286 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1413991 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | FUSE | L5725 | 20190208 | 758 | 295953 | 472 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 7552 | 38.3744 | -120.4772 | MTR #1004934423- MTR #1004934433 & JUST W/OF THAT TRANSF BEFORE THE 4-WAY | Partly Cloudy-Below 32 F | Conductor, Overhead | On Ground | 19-0019972 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1413739 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | TRANSFORMER | 320041568630 | 20190208 | 1452 | 296390 | 2776 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 2776 | 38.3849 | -120.4866 | HOLLAND- DONAVON: 3030 JURS RD | Overcast-32-90 F | Transformer | Broken, wire on ground | 19-0020368 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414043 | TX | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | TRIP-SAVER | L3355 | 20190211 | 1823 | 300242 | 1277 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 61296 | 38.5061 | -120.4938 | GRANILLO- D // 1990: 24 P/W/O L3355 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0021240 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1414833 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 37276 | 20190211 | 1144 | 299632 | 237 | Distribution Circuit | Vegetation | Tree - fell into line | 794 | 84848 | 38.2391 | -120.3364 | MTR #1004162048 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0021035 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414707 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2101 | 163692101 | FUSE | 5885 | 20190218 | 1148 | 317552 | 219 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 3066 | 38.416 | -120.1334 | S/OF CGC 321061870005 | Clear-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0025609 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1418656 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L7247 | 20190219 | 1258 | 318834 | 1380 | Distribution Circuit | Vegetation | Tree - fell into line | 73 | 3541 | 38.4316 | -120.6246 | LOADSIDE OF L7247 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026181 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1419035 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | JUMPER | JPRS 1 N/OF L7253 | 20190219 | 1749 | 319170 | 1089 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1089 | 38.4324 | -120.6245 | L7247 LOADSIDE | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026181 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1419054 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | TRIP-SAVER | L3355 | 20190221 | 1140 | 320571 | 560 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 26880 | 38.5061 | -120.4938 | 6 S/OF WANDERING HILLS RD AND SHAKE RIDGE RD | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0026963 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1419468 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | FUSE | L1141 | 20190327 | 1533 | 348730 | 673 | Distribution Circuit | Vegetation | Tree - fell into line | 64 | 43072 | 38.4083 | -120.7513 | MCCARTNEY- MARK // 2024: at SAP# 101263171 | Overcast-Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0037584 | OH | Sus | 31431366 | yes | 2019 | MAR | Yes | Line to Line | 1426726 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1102 | 162991102 | OTHER | WIRE DOWN | 20190408 | 1701 | 356063 | 294 | Distribution Circuit | Equipment Failure/Involved | Overhead | 123 | 36001 | 38.1384 | -120.8902 | COLLINS- EAN // 2028: iro 5479 PLEASANT OAKS RD | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0040663 | OH | Sus | 43730362 | No | 2019 | APR | Yes | Open Circuit | 1428893 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 2 | STANISLAUS-1701 | 162821701 | FUSE | L3165 | 20190409 | 1609 | 356929 | 278 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 4448 | 38.158 | -120.3859 | 3 P/SS OF MTR #1008776717 | Overcast-Drizzle-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0041071 | OH | Sus | 43731286 | yes | 2019 | APR | Yes | Line to Ground | 1429165 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER | 45292 | 20190420 | 1347 | 364491 | 1021 | Distribution Circuit | Vegetation | Tree - fell into line | 1355 | 314836 | 38.4536 | -120.53 | DORRIS- RYAN // 1914: 17480 BARTON DR- PIONEER | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0044584 | OH | Sus | 31434346 | yes | 2019 | APR | Yes | Line to Ground | 1431749 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | OTHER | WIRE DOWN 1 SPAN SOURCE SIDE OF 12282 OPEN | 20190429 | 559 | 369820 | 208 | Distribution Circuit | Animal | Bird found | 1031 | 166155 | 38.088 | -120.5377 | WIRE DOWN 1 SPAN SOURCE SIDE OF 12282 ¦ 15 POLES LOADSIDE OF 12282 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0046919 | OH | Sus | 43754618 | yes | 2019 | APR | Yes | Line to Ground | 1433312 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 93116 | 20190507 | 924 | 375424 | 581 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 609 | 95077 | 38.3838 | -120.527 | 2754 INDEPENDENCE RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0049573 | OH | Sus | 0 | No | 2019 | MAY | Yes | Line to Line | 1435055 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | JUMPER | WIRE DOWN 1 SOURCE MTR# 1005018683 | 20190525 | 2013 | 390290 | 48 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 48 | 38.4189 | -120.4893 | 1 SOURCE SIDE OF MTR# 1005018683 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0057644 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Open Circuit | 1441146 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | JUMPER | L9755 FUSES | 20190527 | 106 | 391053 | 603 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 6633 | 38.4538 | -120.7931 | MTR# 1004807122 | Overcast-Fog-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0057919 | OH | Sus | 0 | No | 2019 | MAY | Yes | Line to Line | 1441436 | CAW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | FUSE | 1315 | 20190529 | 2026 | 393040 | 1115 | Distribution Circuit | Vegetation | Tree - fell into line | 53 | 41235 | 38.3776 | -120.554 | MCCARTNEY- MARK // 2024: 1958 QUAIL LN. WEST POINT | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0059265 | OH | Sus | 31449052 | yes | 2019 | MAY | Yes | Line to Line | 1442510 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 1037 | 20190613 | 2013 | 409536 | 446 | Distribution Circuit | Vegetation | Tree - fell into line | 43 | 19178 | 38.4171 | -120.646 | AQUEDUCT S/OF MTR# 1004857915 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0067460 | OH | Sus | 31453653 | No | 2019 | JUN | Yes | Line to Line | 1448964 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | OTHER | L2079 | 20190715 | 2112 | 453176 | 870 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2199 | 38.3883 | -120.4955 | SOURCE SIDE OF MTR# 1009606599 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0077733 | OH | Sus | 31457526 | No | 2019 | JUL | Yes | Line to Ground | 1456418 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE | L1499 | 20190719 | 1655 | 462353 | 449 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 8229 | 38.405 | -120.6925 | MTR 1004803981 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0079343 | OH | Sus | 31458835 | No | 2019 | JUL | Yes | Line to Line | 1457437 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | FUSE | L3723 | 20190809 | 2233 | 498264 | 1289 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 28687 | 38.0653 | -120.6563 | MTR 1010518203 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0086467 | OH | Sus | 0 | No | 2019 | AUG | Yes | Line to Line | 1462016 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | OCB | 1702/2 | 20190816 | 1056 | 517156 | 1010 | Distribution Circuit | 3rd Party | Vehicle | 4171 | 1026547 | 38.0572 | -120.5343 | SILVA- TONY // 1705: 536 hwy 49 | Clear-Above 90 | Pole-Wood | Broken, wire on ground | 19-0088785 | OH | Sus | 0 | yes | 2019 | AUG | Yes | Line to Ground | 1463649 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | RECLOSER | 6074 | 20190821 | 926 | 527279 | 274 | Distribution Circuit | 3rd Party | Vehicle | 2307 | 155934 | 38.3928 | -120.7927 | MCDANIEL- TONY // 1704: 1 ne of L6021 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0090318 | OH | Sus | 0 | No | 2019 | AUG | Yes | Line to Line | 1464798 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 2 | NORTH BRANCH-1101 | 163231101 | OTHER | WIRE DOWN 3 SE/OF MTR# 1004657060 | 20190915 | 936 | 583270 | 574 | Distribution Circuit | 3rd Party | Vehicle | 32 | 5378 | 38.1203 | -120.8036 | WIRE DOWN 4 SE/OF MTR# 1004657060 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0099234 | OH | Sus | 0 | No | 2019 | SEP | Yes | Open Circuit | 1470127 | PW | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 34416 | 20191003 | 1936 | 642177 | 504 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 451 | 39585 | 38.3988 | -120.5256 | MTR #1004736704 | Clear-32-90 F | Conductor, Overhead | On Ground | 19-0107224 | OH | Sus | 31474097 | No | 2019 | OCT | Yes | Line to Ground | 1475191 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 93116 | 20191018 | 1640 | 670813 | 571 | Distribution Circuit | 3rd Party | Vehicle | 610 | 91899 | 38.3838 | -120.527 | REANO- TONY // 2009: CURT OUT POLE 2111 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0113616 | OH | Sus | 44010843 | No | 2019 | OCT | Yes | Line to Line | 1481081 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | OCB | 1102/2 | 20191128 | 525 | 722583 | 494 | Distribution Circuit | Vegetation | Tree - fell into line | 1476 | 555862 | 38.4208 | -120.549 | 8 S/OF L1503 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0130759 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Multi-Fault | 1495444 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE | L3725 | 20191206 | 114 | 731012 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 44 | 13128 | 38.4029 | -120.7073 | 17401 KIT LN | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0134178 | OH | Sus | 0 | yes | 2019 | DEC | Yes | Line to Line | 1498098 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | FUSE | 4587 | 20200110 | 1250 | 758799 | 704 | Distribution Circuit | 3rd Party | Vehicle | 115 | 80960 | 38.16 | -120.8954 | 1 POLE E/O 16057 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 20-0007379 | OH | Sus | 0 | No | 2020 | JAN | Yes | Three Phase Fault | 1505548 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | FUSE | L7437 | 20200126 | 729 | 770280 | 774 | Distribution Circuit | Vegetation | Tree - fell into line | 10 | 7740 | 38.4155 | -120.6897 | 1 N/OF L7437 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 20-0013746 | OH | Sus | 0 | No | 2020 | JAN | Yes | Line to Line | 1509282 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 1888 | 20200128 | 846 | 771490 | 412 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 1469 | 89467 | 38.2367 | -120.3628 | 5 SPANS S/S OF L2041 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0014330 | OH | Sus | 0 | No | 2020 | JAN | Yes | Line to Ground | 1509707 | CAW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | TRIP-SAVER | L1697 | 20200201 | 751 | 774884 | 449 | Distribution Circuit | 3rd Party | Vehicle | 247 | 24557 | 38.3794 | -120.6379 | Roberts- Ron 209-986-6628: 11875 tabeau rd pine grove | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0016192 | OH | Sus | 0 | No | 2020 | FEB | Yes | Line to Line | 1510938 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | NORTH BRANCH-1101 | 163231101 | TRIP-SAVER | TS1115 | 20200206 | 1801 | 779682 | 452 | Distribution Circuit | Equipment Failure/Involved | Overhead | 160 | 27840 | 38.2444 | -120.8446 | 2 NE/OF 1287 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0018323 | OH | Sus | 44180491 | No | 2020 | FEB | Yes | Line to Ground | 1512479 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 4790 | 20200213 | 842 | 790173 | 800 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1961 | 303344 | 38.3868 | -120.5244 | MTR#1004934080 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0021734 | OH | Sus | 31490856 | No | 2020 | FEB | Yes | Multi-Fault | 1515063 | CAW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2101 | 163692101 | FUSE | 1591 | 20200219 | 818 | 795357 | 470 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1410 | 38.529 | -120.2331 | 5 LD SIDE OF 1591 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0023357 | OH | Sus | 0 | No | 2020 | FEB | Yes | Three Phase Fault | 1516167 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | L2065 | 20200302 | 38 | 821111 | 683 | Distribution Circuit | Vegetation | Tree - fell into line | 334 | 59492 | 38.3008 | -120.2732 | 1N/OF MTR # 1004652233 | Clear-Strong Winds-Below 32 F | Crossarm, Wood | Broken, wire on ground | 20-0027609 | OH | Sus | 31493732 | yes | 2020 | MAR | Yes | Line to Ground | 1518804 | CAW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | JUMPER | L3431 | 20200319 | 1400 | 859044 | 275 | Distribution Circuit | Equipment Failure/Involved | Overhead | 8 | 2200 | 38.3748 | -120.4573 | SS OF 6691 6135 BLUE MOUNTAIN RD | Overcast-Drizzle-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0034294 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Ground | 1523032 | CSO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | OTHER | 13438 | 20200320 | 1419 | 859761 | 283 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1489 | 136103 | 38.4738 | -120.6265 | BET L2133 AND MTR #1004938591 | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 20-0034738 | OH | Sus | 0 | No | 2020 | MAR | Yes | Open Circuit | 1523286 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER | 6080 | 20200325 | 1014 | 864714 | 258 | Distribution Circuit | Equipment Failure/Involved | Overhead | 938 | 121015 | 38.4612 | -120.6579 | CGC # 223701528497 ON SHAKERIDGE E/O L581 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0035978 | OH | Sus | 44273623 | No | 2020 | MAR | Yes | Line to Ground | 1523917 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | RECLOSER | 72036 | 20200405 | 834 | 882744 | 471 | Distribution Circuit | Vegetation | Tree - fell into line | 614 | 76694 | 38.4129 | -120.5501 | 1 W/OF 679 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0038511 | OH | Sus | 31498948 | yes | 2020 | APR | Yes | Line to Ground | 1525345 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | OTHER | 5343 | 20200406 | 936 | 884761 | 504 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1088 | 38.2741 | -120.3308 | 8 LD SIDE OF 5343 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0038929 | OH | Sus | 0 | yes | 2020 | APR | Yes | Line to Ground | 1525700 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 1597 | 20200502 | 1301 | 905923 | 375 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 22500 | 38.3023 | -120.708 | Roberts- Ron 209-986-6628: 8900 cener st. | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 20-0046596 | OH | Sus | 0 | No | 2020 | MAY | Yes | Force Out | 1530370 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1102 | 163541102 | RECLOSER | 2642 | 20200506 | 2224 | 908540 | 381 | Distribution Circuit | Equipment Failure/Involved | Overhead | 24 | 7332 | 38.5013 | -120.8481 | SOUTH ON MAINLINE JUST WEST OF CGC #223299131604 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0047960 | OH | Sus | 44312283 | No | 2020 | MAY | Yes | Line to Ground | 1531181 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1103 | 163011103 | FUSE | L1247 | 20200517 | 1208 | 915203 | 248 | Distribution Circuit | Vegetation | Tree - branch fell on line | 27 | 6696 | 38.3448 | -120.867 | L3863 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0050999 | OH | Sus | 44325937 | yes | 2020 | MAY | Yes | Line to Ground | 1532936 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | JUMPER | 43019 | 20200529 | 901 | 925055 | 488 | Distribution Circuit | 3rd Party | Vehicle | 5 | 2440 | 38.4183 | -120.5983 | 43019 TO EOL | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 20-0055553 | OH | Sus | 0 | yes | 2020 | MAY | Yes | Open Circuit | 1535529 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L3377 | 20200602 | 1725 | 928804 | 1212 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 23028 | 38.3522 | -120.5093 | 1 N/OF 1779 & 5 SPANS E/OF 1779 ON EOL 3 SPAN TAP GOING TWD EAST | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0056751 | OH | Sus | 31504818 | No | 2020 | JUN | Yes | Line to Line | 1536514 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | 9775 | 20200618 | 543 | 941648 | 304 | Distribution Circuit | Vegetation | Tree - branch fell on line | 40 | 11454 | 38.3435 | -120.7179 | 4 POLES S/E/OF 9775 ON SINGLE PHASE TAP 4 S/OF | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0062494 | OH | Sus | 31506312 | No | 2020 | JUN | Yes | Line to Ground | 1540610 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1101 | 163541101 | OTHER | WIRE DOWN 3/S/N/OF 1563 | 20200619 | 430 | 942335 | 398 | Distribution Circuit | Vegetation | Tree - fell into line | 563 | 90879 | 38.4186 | -120.822 | 3SP N/OF 1563 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0062922 | OH | Sus | 44360219 | No | 2020 | JUN | Yes | Line to Ground | 1540858 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L3679 | 20200708 | 1051 | 960063 | 355 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 155 | 16523 | 38.4444 | -120.5319 | CGC #224250028465 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0069539 | OH | Sus | 35185532 | No | 2020 | JUL | Yes | Line to Line | 1545157 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | RECLOSER | 3170 | 20200917 | 2312 | 1079641 | 572 | Distribution Circuit | Vegetation | Tree - fell into line | 691 | 163626 | 38.4151 | -120.6853 | BETWEEN SBCO 92011 FUCO 515715 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0098791 | OH | Sus | 31514032 | No | 2020 | SEP | Yes | Three Phase Fault | 1564419 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | FUSE | 6681 | 20201007 | 1142 | 1112858 | 241 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1068 | 28005 | 38.3079 | -120.2673 | SILVA- TONY // 1705: 3737 shoshonev dr | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0106078 | OH | Sus | 0 | No | 2020 | OCT | Yes | Line to Ground | 1569158 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1103 | 163011103 | FUSE | L9743 | 20201114 | 310 | 1144676 | 598 | Distribution Circuit | Equipment Failure/Involved | Overhead | 11 | 3678 | 38.349 | -120.8505 | CGC# 223283625255 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 20-0120920 | OH | Sus | 0 | No | 2020 | NOV | Yes | Line to Line | 1579740 | CAW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | L5791 | 20201115 | 936 | 1145483 | 554 | Distribution Circuit | 3rd Party | Vandalism | 13 | 7202 | 38.4102 | -120.5557 | 1 LD SIDE OF L5791 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0121066 | OH | Sus | 0 | No | 2020 | NOV | Yes | Line to Line | 1579984 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | FUSE | 16059 | 20201118 | 115 | 1148100 | 747 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 27 | 10105 | 38.1634 | -120.9181 | 1 POLE E/OF MTR #1004597795 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 20-0122213 | OH | Sus | 0 | No | 2020 | NOV | Yes | Line to Line | 1580836 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | OTHER | WIRE DOWN S/OF MTR 1005790897 | 20201207 | 1013 | 1168428 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 489 | 38.4864 | -120.5352 | S/OF MTR 1005790897 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0128489 | OH | Sus | 0 | No | 2020 | DEC | Yes | Line to Ground | 1585093 | CAW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | RECLOSER | 11212 | 20201217 | 2023 | 1193112 | 178 | Distribution Circuit | Equipment Failure/Involved | Overhead | 126 | 10962 | 38.0863 | -120.5718 | 15 S/S/OF L1085 | Clear-32-90 F | Woodpin | Broken, wire on ground | 20-0130994 | OH | Sus | 0 | No | 2020 | DEC | Yes | Line to Ground | 1588245 | WP | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | OTHER | 4786 | 20210106 | 849 | 1205163 | 264 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 840 | 82440 | 38.2321 | -120.5349 | EAST PHASE SOUTH /OF L5209 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0001110 | OH | Sus | 35124428 | No | 2021 | JAN | Yes | Open Circuit | 1591254 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | RECLOSER | 12612 | 20210129 | 330 | 1240917 | 641 | Distribution Circuit | 3rd Party | Vehicle | 323 | 119678 | 38.1783 | -120.927 | 2 POLES E/OF D7987l1 SPAN S/E OF D4719 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0018118 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1600142 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L1117 | 20210403 | 2157 | 1306557 | 1134 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 13972 | 38.4914 | -120.7132 | 1 SPAN W/OF & 1 SPAN SW/OF L1117 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0044502 | OH | Sus | 31535240 | No | 2021 | APR | Yes | Line to Line | 1617431 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CLAY-1103 | 163341103 | OTHER | WIRE DOWN HOT BET POLES 7/2A & 0/1 | 20210410 | 1244 | 1312804 | 485 | Distribution Circuit | Equipment Failure/Involved | Overhead | 22 | 2560 | 38.3413 | -120.9179 | BET POLES 7/2A & 0/1 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0047191 | OH | Sus | 44734994 | No | 2021 | APR | Yes | Open Circuit | 1619164 | CSO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | RECLOSER | 3168 | 20210510 | 541 | 1344619 | 257 | Distribution Circuit | Animal | Bird found | 1072 | 247380 | 38.4143 | -120.6541 | MAINLINE JUST SS/OF 43777 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0059047 | OH | Sus | 31540124 | No | 2021 | MAY | Yes | Line to Line | 1627035 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | OTHER | WIRE DOWN 14055 QUARTZ MTN RD | 20210620 | 619 | 1380092 | 323 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 15045 | 38.455 | -120.7668 | TAKE OFF POLE TO CGC# 223533028910 14055 QUARTZ MTN RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0076748 | OH | Sus | 31544220 | No | 2021 | JUN | Yes | Line to Ground | 1639015 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1101 | 163751101 | RECLOSER | 3166 | 20210702 | 826 | 1390474 | 320 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 8000 | 38.4069 | -120.6707 | FIRST SPAN LD SIDE OF L699 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0084076 | OH | Sus | 31545297 | No | 2021 | JUL | Yes | Line to Line | 1644874 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | RECLOSER | 47968 | 20210712 | 836 | 1400622 | 549 | Distribution Circuit | 3rd Party | Vehicle | 211 | 97511 | 38.2321 | -120.5505 | Whiskey slid rd at CGC 319795563520 | Clear-32-90F | Pole-Wood | Broken, wire on object | 21-0087916 | OH | Sus | 35270908 | No | 2021 | JUL | Yes | Line to Line | 1647401 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | JUMPER | WIRE DOWN HOT 2SP SW/OF 90421 | 20210712 | 1558 | 1402206 | 191 | Distribution Circuit | 3rd Party | Vehicle | 1779 | 317357 | 38.4601 | -120.5194 | 2 SP SW/OF 90421/27258 COLUMBIA DR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0088390 | OH | Sus | 44905839 | No | 2021 | JUL | Yes | Line to Ground | 1647603 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | OTHER | 6080 | 20210816 | 827 | 1443717 | 301 | Distribution Circuit | Vegetation | Tree - branch fell on line | 316 | 5764 | 38.4854 | -120.7005 | 1 SPAN SOURCE SIDE OF 846131 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0104892 | OH | Sus | 31549627 | No | 2021 | AUG | Yes | Line to Ground | 1657852 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | OTHER | D9321 | 20210902 | 521 | 1460560 | 416 | Distribution Circuit | Equipment Failure/Involved | Overhead | 148 | 43539 | 38.1447 | -120.9447 | 3 P/S/OF CGC# CGC# 318723360051 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0112466 | OH | Sus | 44962460 | No | 2021 | SEP | Yes | Open Circuit | 1662939 | CSO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | RECLOSER | 8482 | 20210913 | 315 | 1470330 | 628 | Distribution Circuit | 3rd Party | Vehicle | 876 | 399562 | 38.0748 | -120.5688 | CGC 319540458038 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0116590 | OH | Sus | 0 | No | 2021 | SEP | Yes | Line to Ground | 1665219 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | WEST POINT-1102 | 163201102 | FUSE | L1481 | 20211028 | 1312 | 1524311 | 446 | Distribution Circuit | Vegetation | Tree - fell into line | 16 | 4026 | 38.388 | -120.5428 | 1 W/OF CGC# 319851368620 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0139435 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Line | 1679974 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | 2143 | 20220102 | 1056 | 1592399 | 435 | Distribution Circuit | Equipment Failure/Involved | Overhead | 67 | 29145 | 38.2303 | -120.6003 | CGC 319710663215 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 22-0005179 | OH | Sus | 0 | No | 2022 | JAN | Yes | Force Out | 1700365 | CAW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L5111 | 20220102 | 828 | 1592624 | 1778 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 21336 | 38.2329 | -120.3486 | MULTIPLE LOCATIONS | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 22-0005310 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Ground | 1700555 | CAW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 685 | 20220108 | 1044 | 1598184 | 381 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 381 | 38.4551 | -120.5307 | CGC# 224214029047 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0007601 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Ground | 1701597 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | OTHER | WIRE DOWN HOT CGC# 223717525700 | 20220423 | 2012 | 1680111 | 481 | Distribution Circuit | Equipment Failure/Involved | Overhead | 374 | 39757 | 38.3651 | -120.7047 | CGC# 223717525700 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 22-0053709 | OH | Sus | 0 | No | 2022 | APR | Yes | Line to Ground | 1730551 | CAW | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2101 | 163692101 | FUSE | 1769 | 20220518 | 1614 | 1702310 | 202 | Distribution Circuit | Environmental/External | Ice or snow | 1 | 202 | 38.5365 | -120.2383 | 6 POLES S/W OF CGC# 225071832440 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0063647 | OH | Sus | 0 | No | 2022 | MAY | Yes | Line to Line | 1737412 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | STANISLAUS-1701 | 162821701 | RECLOSER | 1812 | 20220612 | 931 | 1729337 | 669 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 913 | 219673 | 38.1832 | -120.3754 | 3034 FOREST LN | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0073392 | OH | Sus | 0 | No | 2022 | JUN | Yes | Line to Line | 1743964 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CORRAL-1101 | 162991101 | RECLOSER | 12612 | 20220807 | 555 | 1775173 | 692 | Distribution Circuit | 3rd Party | Vehicle | 322 | 58394 | 38.1783 | -120.927 | 3 N/OF D4719 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 22-0094664 | OH | Sus | 35375981 | No | 2022 | AUG | Yes | Line to Line | 1758220 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | MARTELL-1101 | 163011101 | RECLOSER | 91216 | 20220918 | 1319 | 1814511 | 443 | Distribution Circuit | Vegetation | Tree - fell into line | 427 | 113921 | 38.4351 | -120.7495 | GIANGREGORIO- SEAN: 16520 Lake canyon rd- sutter creek | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 22-0111655 | OH | Sus | 0 | No | 2022 | SEP | Yes | Line to Line | 1769687 | CAW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L359 | 20221026 | 957 | 1845856 | 304 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 49 | 8368 | 38.3968 | -120.6591 | DORRIS- RYAN // 1914: Sap. 101255184 (4 SPANS S/OF MTR#1004804127 ) | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0124982 | OH | Sus | 31619503 | No | 2022 | OCT | Yes | Line to Line | 1779272 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | RECLOSER | 1850 | 20221103 | 116 | 1852099 | 813 | Distribution Circuit | Vegetation | Tree - fell into line | 4398 | 922647 | 38.2413 | -120.3611 | WALSH- PETE: 1850 Choctaw Rd | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0127266 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Ground | 1781018 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 1439 | 20221211 | 345 | 1884921 | 680 | Distribution Circuit | Vegetation | Tree - fell into line | 244 | 52336 | 38.4905 | -120.7137 | 16130 MT WHITNEY- FIDDLETOWN | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0138815 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1789643 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2101 | 163692101 | FUSE | 5149 | 20221212 | 1547 | 1887956 | 754 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 10556 | 38.4477 | -120.0711 | 5SP LD SIDE | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0139418 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1790243 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | CLAY-1103 | 163341103 | OCB | 1103/2 | 20221213 | 32 | 1887885 | 879 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1655 | 423897 | 38.3422 | -120.935 | 1102 CIR AT 95933 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 22-0139410 | OH | Sus | 31631451 | No | 2022 | DEC | Yes | Line to Ground | 1790229 | CSO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | 5163 | 20221227 | 536 | 1898463 | 382 | Distribution Circuit | Vegetation | Tree - fell into line | 59 | 22538 | 38.4381 | -120.5702 | 2 POLES S/W OF CGC #224116328672- 3 POLES S/W OF CGC #224116328672- 4 POLES S/W OF CGC #224116328672 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 22-0141529 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Line | 1793205 | CAW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2101 | 163692101 | JUMPER | WIRE DOWN 1 P S/OF CGC #321061870005 | 20221228 | 1139 | 1900654 | 751 | Distribution Circuit | Equipment Failure/Involved | Overhead | 14 | 8102 | 38.4218 | -120.1306 | 1 POLE S/OF CGC #321061870005 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0141959 | OH | Sus | 45606422 | No | 2022 | DEC | Yes | Line to Ground | 1793691 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2101 | 163692101 | FUSE | 1232 | 20221230 | 315 | 1901763 | 682 | Distribution Circuit | Equipment Failure/Involved | Overhead | 920 | 221369 | 38.4163 | -120.1332 | CGC #321216470585 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0142150 | OH | Sus | 45611062 | No | 2022 | DEC | Yes | Line to Ground | 1793923 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 1541 | 20230113 | 1216 | 1951898 | 524 | Distribution Circuit | Vegetation | Tree - fell into line | 34 | 17816 | 38.4504 | -120.644 | CGC 223833228338 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0015389 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1804297 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | RECLOSER | 3142 | 20230115 | 605 | 1955514 | 356 | Distribution Circuit | Vegetation | Tree - fell into line | 911 | 249076 | 38.3016 | -120.277 | S/OF CGC#320651965215 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0016528 | OH | Sus | 0 | No | 2023 | JAN | Yes | Multi-Fault | 1805285 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | STANISLAUS-1702 | 162821702 | FUSE | L2679 | 20230117 | 224 | 1959040 | 709 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 49630 | 38.2417 | -120.3725 | LD SIDE OF CGC 320372063492 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0017527 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1806161 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | L359 | 20230205 | 611 | 1977225 | 465 | Distribution Circuit | Vegetation | Tree - fell into line | 49 | 22785 | 38.3968 | -120.6591 | 1 S/OF CGC 223808026695 & 4 S/OF CGC 223808026695 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0025357 | OH | Sus | 31636190 | No | 2023 | FEB | Yes | Line to Ground | 1810655 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | SALT SPRINGS-2102 | 163692102 | OTHER | WIRE DOWN 10 POLES SW OF R203 | 20230217 | 705 | 1987311 | 544 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3546 | 1697082 | 38.3231 | -120.2534 | 10 POLES SW OF R203 | Overcast-Below 32 F | Conductor, Overhead | Broken, wire on ground | 23-0029985 | OH | Sus | 45677824 | No | 2023 | FEB | Yes | Line to Ground | 1813843 | CO | OH | No | Yes
STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | L1629 | 20230305 | 606 | 2023271 | 743 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2972 | 38.4327 | -120.5956 | CGC# 224023528229 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0040306 | OH | Sus | 0 | No | 2023 | MAR | Yes | Force Out | 1822043 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | RECLOSER | 4790 | 20230311 | 556 | 2031960 | 746 | Distribution Circuit | Vegetation | Tree - fell into line | 1978 | 189178 | 38.3869 | -120.5242 | 5 N/OF L3231 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0043335 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1823932 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | CALAVERAS CEMENT-1101 | 162211101 | FUSE | L1637 | 20230328 | 1039 | 2070348 | 503 | Distribution Circuit | Vegetation | Tree - fell into line | 35 | 17605 | 38.2444 | -120.512 | 3 & 4 POLE LD SIDE OF CGC 319977363606 | Overcast-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 23-0053500 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1831148 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1102 | 163541102 | FUSE | 1241 | 20230328 | 1134 | 2070383 | 343 | Distribution Circuit | Vegetation | Tree - fell into line | 80 | 27440 | 38.5461 | -120.744 | 2 LD SIDE OF 1241 | Overcast-Drizzle-Strong Winds-32-90 F | Crossarm, Wood | Broken, wire on ground | 23-0053588 | OH | Sus | 0 | No | 2023 | MAR | Yes | Three Phase Fault | 1831198 | CAW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 1439 | 20230328 | 938 | 2070003 | 471 | Distribution Circuit | Vegetation | Tree - fell into line | 245 | 55374 | 38.4905 | -120.7137 | 3 SRD SIDE OF L2997 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0053435 | OH | Sus | 31640556 | No | 2023 | MAR | Yes | Three Phase Fault | 1831101 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | PINE GROVE-1102 | 163751102 | FUSE | 67999 | 20230328 | 1006 | 2070159 | 412 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 1648 | 38.4043 | -120.6516 | 2 POLES LD SIDE FOUND OF 67999 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0053483 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Line | 1831135 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | FUSE | 352707 | 20230328 | 1021 | 2070153 | 165 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1320 | 38.4377 | -120.5666 | 1 LD SIDE OF 352707 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0053485 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1831137 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | OLETA-1102 | 163541102 | FUSE | L1185 | 20230330 | 37 | 2073816 | 643 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 4501 | 38.5054 | -120.7667 | 5 SPANS W/O L1185 & WEST at BUCK | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0054727 | OH | Sus | 31640714 | No | 2023 | MAR | Yes | Line to Ground | 1831815 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1102 | 163201102 | FUSE | 2121 | 20230410 | 857 | 2084210 | 379 | Distribution Circuit | 3rd Party | Vehicle | 91 | 13396 | 38.4725 | -120.5271 | 1 POLE S/OF CGC# 224202729842 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0059069 | OH | Sus | 0 | No | 2023 | APR | Yes | Line to Line | 1834530 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | SALT SPRINGS-2101 | 163692101 | JUMPER | WIREDOWN @ CGC 321158870104 | 20230426 | 719 | 2097470 | 294 | Distribution Circuit | Equipment Failure/Involved | Overhead | 46 | 3935 | 38.4248 | -120.0965 | CGC 321158870104 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0064908 | OH | Sus | 0 | No | 2023 | APR | Yes | Line to Ground | 1838724 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | PINE GROVE-1102 | 163751102 | RECLOSER | 35576 | 20230715 | 2249 | 2163935 | 861 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 50423 | 38.4173 | -120.6138 | LOAD SIDE OF FUCO L891 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0092746 | OH | Sus | 45888783 | No | 2023 | JUL | Yes | Line to Line | 1857764 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | ELECTRA-1101 | 162161101 | FUSE | L5187 | 20230822 | 2312 | 2199728 | 414 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1912 | 33798 | 38.3463 | -120.7015 | 2 SPANS S/OF CGC #223703525170 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0107836 | OH | Sus | 45937447 | No | 2023 | AUG | Yes | Line to Line | 1868148 | CO | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 2 | FROGTOWN-1702 | 163451702 | RECLOSER | 75252 | 20231004 | 1310 | 2234721 | 631 | Distribution Circuit | 3rd Party | Vehicle | 825 | 153945 | 38.0509 | -120.6244 | 4 POLES LD SIDE OF CGC 319698155433 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0124421 | OH | Sus | 0 | No | 2023 | OCT | Yes | Line to Line | 1879341 | PW | OH | No | No
STOCKTON | FIELD OPS CENTRAL | Tier 3 | WEST POINT-1101 | 163201101 | RECLOSER | 12256 | 20231101 | 2307 | 2257888 | 254 | Distribution Circuit | 3rd Party | Vehicle | 1782 | 370846 | 38.4437 | -120.5088 | SS 695825 FUCO | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0134951 | OH | Sus | 0 | No | 2023 | NOV | Yes | Line to Line | 1886999 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER | 9250 | 20130113 | 1254 | 729361 | 896 | Distribution Circuit | 3rd Party | Vehicle | 1495 | 194905 | 37.8368 | -120.2611 | 20580 FERRETTI RD- GROVELAND | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on object | 13-0003895 | OH | Sus | 30970915 | No | 2013 | JAN | Yes |  | 99304744 | PW | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2102 | 254432102 | OCB | OCB | 20130219 | 1931 | 744442 | 503 | Distribution Circuit | Equipment Failure/Involved | Other | 1332 | 595572 | 37.2272 | -119.6902 | 2/P/W/OF 69105 | Clear-32 - 90 F | Conductor, Overhead | On Ground | 13-0011038 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Line to Ground | 99300185 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 19625 | 20130219 | 1955 | 744504 | 1141 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 32123 | 37.2667 | -119.6968 | LOADSIDE OF MTR 1005877687 | Rain-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0011129 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Line to Line | 99300181 | PW | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 6288 | 20130219 | 2045 | 744569 | 1410 | Distribution Circuit | Environmental/External | Ice or snow | 174 | 170760 | 37.264 | -119.7336 | Dahlem / 1847 / 559-493-8472: WELLS RD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0011179 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Line to Ground | 99300138 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 9197 | 20130219 | 1817 | 744667 | 461 | Distribution Circuit | Equipment Failure/Involved | Other | 137 | 67361 | 37.9493 | -120.364 | 2/SPANS/LD SIDE 19598 | Snow-Below 32 F | Conductor, Overhead | On Ground | 13-0011090 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Line to Ground | 99300240 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | L1209 | 20130219 | 1625 | 744141 | 456 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 74 | 59136 | 37.9627 | -120.2913 | Trujillo / 1708 / 768-3532: 16106 TUOLUMNE RD | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0011079 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Line to Ground | 99300201 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE | 10309 | 20130219 | 2117 | 744636 | 1331 | Distribution Circuit | Vegetation | Tree - fell into line | 31 | 41261 | 37.5642 | -119.94 | Cederlof / 2076 / 559-760-7819: 5008 colorado rd | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0011081 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Line to Ground | 99300200 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | OAKHURST-1101 | 254421101 | RECLOSER | 6220 | 20130219 | 1936 | 744467 | 2652 | Distribution Circuit | Equipment Failure/Involved | Other | 141 | 346388 | 37.3598 | -119.7398 | CANYON CROSSING 2 SPANS N/O FUCO 10665 at 41125 ROAD 600- AHWAHNEE | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0011070 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Line to Line | 99299964 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 21894 | 20130219 | 1813 | 744385 | 542 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 7046 | 37.9834 | -120.3927 | McKinnon / 2074 / 573-0394: SOURCE SPAN METER# 1009435712 | Snow-32 - 90 F | Conductor, Overhead | On Ground | 13-0011092 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Multi-Fault | 99300238 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 5596 | 20130219 | 1904 | 744398 | 888 | Distribution Circuit | Equipment Failure/Involved | Other | 270 | 134560 | 37.2121 | -119.5536 | 53611 ROAD 200 NORTH FORK TOWARDS METER #34H486 | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on object | 13-0011113 | OH | Sus | 0 | yes | 2013 | FEB | Yes | None | 99300191 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 12193 | 20130220 | 212 | 744763 | 681 | Distribution Circuit | Equipment Failure/Involved | Other | 84 | 57204 | 37.2524 | -119.7038 | Dahlem / 1847 / 559-493-8472: VEATER RANCH RD | Snow-Below 32 F | Connector or Splice (OH) | Broken, wire on ground | 13-0011111 | OH | Sus | 0 | yes | 2013 | FEB | Yes |  | 99300193 | CSO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 5514 | 20130220 | 201 | 744766 | 859 | Distribution Circuit | Equipment Failure/Involved | Other | 268 | 230212 | 37.2281 | -119.7628 | METER #1006637546 | Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 13-0011125 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Multi-Fault | 99300184 | PW | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 5676 | 20130220 | 710 | 744819 | 875 | Distribution Circuit | Environmental/External | Ice or snow | 48 | 42000 | 37.2413 | -119.7369 | UNKNOWN | Snow-Below 32 F | Conductor, Overhead | On Ground | 13-0011234 | OH | Sus | 0 | yes | 2013 | FEB | Yes |  | 99300071 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 5683 | 20130220 | 1333 | 745346 | 1272 | Distribution Circuit | Equipment Failure/Involved | Other | 33 | 21015 | 37.254 | -119.7116 | METER #1009133633 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0011346 | OH | Sus | 0 | yes | 2013 | FEB | Yes | None | 99299958 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | OTHER |  | 20130220 | 1237 | 745269 | 368 | Distribution Circuit | Equipment Failure/Involved | Other | 2 | 736 | 37.3967 | -119.8398 | Wheeler / 5686 / 559-333-2360: 3711 INDIAN PEAK ROAD | Partly cloudy-32 - 90 F | Conductor, Overhead | On Ground | 13-0011317 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Line to Ground | 99300032 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1103 | 252531103 | OTHER |  | 20130220 | 1208 | 745242 | 337 | Distribution Circuit | Equipment Failure/Involved | Other | 9 | 2301 | 37.1881 | -119.4662 | Stewart / 2037 / 675-0335: 59412 rd 225 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0011349 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Line to Ground | 99300021 | CSO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 6345 | 20130220 | 1232 | 745263 | 392 | Distribution Circuit | Equipment Failure/Involved | Other | 12 | 3824 | 37.1873 | -119.5494 | W/OF MTR 1005671114 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0011447 | OH | Sus | 0 | yes | 2013 | FEB | Yes | Line to Ground | 99299993 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | RECLOSER | 5100 | 20130409 | 601 | 771299 | 529 | Distribution Circuit | Vegetation | Tree - fell into line | 454 | 47526 | 37.2315 | -119.4946 | HARD TAP W/OF METER #1006020128 BLACK OAK TREE | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0022850 | OH | Sus | 30988320 | yes | 2013 | APR | Yes | Multi-Fault | 99291752 | PW | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 63269 | 20130511 | 1848 | 791479 | 507 | Distribution Circuit | 3rd Party | Vehicle | 1 | 507 | 38.0019 | -120.4097 | McKinnon / 2074 / 573-0394: TX POLE TO 20920 JAMESTOWN RD | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0031293 | OH | Sus | 0 | No | 2013 | MAY | Yes | Line to Line | 99285479 | PW | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 4575 | 20130616 | 1805 | 811455 | 383 | Distribution Circuit | 3rd Party | Vehicle | 14 | 2901 | 37.5436 | -119.9147 | 2/P/S/OF MTR# 1009698943 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0040053 | OH | Sus | 31003225 | No | 2013 | JUN | Yes | Line to Ground | 99279573 | PW | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 5596 | 20130628 | 1139 | 819340 | 357 | Distribution Circuit | Vegetation | Tree - grew into line | 270 | 46790 | 37.2121 | -119.5536 | MULTIPLE LOCATIONS HOT POLE AT MTR 1006023239 | Clear-Above 90 F | Conductor, Overhead | Broken, wire on object | 13-0043441 | OH | Sus | 31005986 | yes | 2013 | JUN | Yes | None | 99277339 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20130703 | 838 | 824645 | 761 | Distribution Circuit | Vegetation | Tree - fell into line | 169 | 42749 | 37.8185 | -120.0962 | Murch / 1851 / 770-3673: LR9210 LOCKED OUT-TREE FELL IN CAMP TAWONGA | Partly cloudy-Above 90 F | Conductor, Overhead | On Ground | 13-0044893 | OH | Sus | 0 | yes | 2013 | JUL | Yes | Line to Ground | 99276092 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1701 | 163351701 | FUSE | S1625 | 20130707 | 1227 | 827169 | 543 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 2741 | 37.9819 | -120.3828 | 240 WEST CHURCH LANE- SONORA at METER 1004901167 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0045616 | OH | Sus | 41922324 | No | 2013 | JUL | Yes | Line to Ground | 99275474 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 6165 | 20130718 | 1452 | 833751 | 422 | Distribution Circuit | 3rd Party | Vehicle | 203 | 84691 | 37.2004 | -119.7556 | Dahlem / 1847 / 559-493-8472: 31444 NORTH DOME | Clear-Above 90 F | Pole-Wood | Broken, wire on ground | 13-0048472 | OH | Sus | 31009571 | No | 2013 | JUL | Yes | Multi-Fault | 99273551 | PW | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1703 | 163351703 | RECLOSER | 9330 | 20130727 | 1738 | 839542 | 818 | Distribution Circuit | Vegetation | Tree - fell into line | 599 | 316014 | 37.8309 | -120.237 | MAINLINE at 22037 & 21665 | Clear-Above 90 F | Pole-Wood | Broken, wire on ground | 13-0050622 | OH | Sus | 31011381 | No | 2013 | JUL | Yes | Line to Line | 99271981 | PW | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 21461 | 20130808 | 1518 | 845194 | 747 | Distribution Circuit | 3rd Party | Vehicle | 129 | 96363 | 37.9572 | -120.3101 | METER #1004902511 | Clear-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0053389 | OH | Sus | 31013734 | No | 2013 | AUG | Yes | Three Phase Fault | 99270287 | PW | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 10375 | 20130906 | 2350 | 862093 | 494 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 19760 | 37.457 | -119.9454 | 1/P/E/OF 10375 | Lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0060371 | OH | Sus | 41952123 | No | 2013 | SEP | Yes | Line to Ground | 99265210 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20130909 | 847 | 863087 | 425 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 169 | 45380 | 37.8185 | -120.0962 | McKinnon / 2074 / 573-0394: 12 SPANS LOAD SIDE L429 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0060687 | OH | Sus | 41952803 | No | 2013 | SEP | Yes | Line to Ground | 99264805 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 6285 | 20130918 | 2234 | 868318 | 848 | Distribution Circuit | 3rd Party | Vehicle | 217 | 114648 | 37.191 | -119.7891 | Dahlem / 1847 / 559-493-8472: 41252 LILLY MT DRIVE | Clear-32 - 90 F | Pole-Wood | Broken, wire on object | 13-0062991 | OH | Sus | 31022502 | No | 2013 | SEP | Yes | Multi-Fault | 99263268 | PW | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2103 | 254432103 | FUSE | 5868 | 20130921 | 1646 | 870577 | 855 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 10222 | 37.2051 | -119.7163 | Dahlem / 1847 / 559-493-8472: 30666 HOGANS MT RD | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0063833 | OH | Sus | 0 | yes | 2013 | SEP | Yes | Line to Line | 99262631 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1704 | 163781704 | OTHER |  | 20131115 | 830 | 902810 | 324 | Distribution Circuit | Equipment Failure/Involved | Other | 130 | 12858 | 37.8885 | -120.5175 | 6060 OBYRNES FERRY RD | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 13-0076317 | OH | Sus | 41987733 | No | 2013 | NOV | Yes |  | 99253292 | CSO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | OTHER |  | 20131120 | 353 | 905649 | 417 | Distribution Circuit | Equipment Failure/Involved | Fire- pole | 194 | 70708 | 37.733 | -120.2139 | 1 SPAN N/O BOOSTER 8237 at 10678 HWY 49 S/E OF PENON BLANCO ROAD | Drizzle-32 - 90 F | Jumper | Broken, wire on ground | 13-0077206 | OH | Sus | 41990268 | yes | 2013 | NOV | Yes |  | 99252612 | JMP | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 19692 | 20131207 | 615 | 921971 | 332 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 12284 | 37.9537 | -120.3893 | WIRE DOWN at METER #1004239993 | Snow-Below 32 F | Conductor, Overhead | On Ground | 13-0081305 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Line | 99248912 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 19692 | 20131207 | 1259 | 922840 | 251 | Distribution Circuit | Vegetation | Tree - branch fell on line | 37 | 9287 | 37.9537 | -120.3893 | AT MTR #100423993 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081305 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Line | 99248888 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | FUSE | 1257 | 20131207 | 1321 | 922865 | 193 | Distribution Circuit | Equipment Failure/Involved | Other | 86 | 16598 | 38.0388 | -120.3834 | 11920 YANKEE HILL ROAD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081335 | OH | Sus | 0 | yes | 2013 | DEC | Yes |  | 99248889 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1704 | 163351704 | FUSE | 20809 | 20131207 | 1416 | 922926 | 345 | Distribution Circuit | Equipment Failure/Involved | Other | 49 | 14025 | 38.0332 | -120.3676 | WIRE DOWN 1/P/E/OF 20809 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081359 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99248869 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2102 | 254452102 | RECLOSER | 10880 | 20131207 | 403 | 921903 | 522 | Distribution Circuit | Equipment Failure/Involved | Other | 467 | 222853 | 37.462 | -119.9505 | MTR 1005642481 | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0081178 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99249029 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 7429 | 20131207 | 510 | 921924 | 464 | Distribution Circuit | Equipment Failure/Involved | Other | 18 | 8352 | 37.3738 | -119.8728 | METER # 1006382130 | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0081295 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99248919 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 4555 | 20131207 | 1619 | 923096 | 1211 | Distribution Circuit | Equipment Failure/Involved | Other | 56 | 67816 | 37.3532 | -119.9576 | LD SIDE OF 4555 | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081372 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99248802 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2102 | 254452102 | OTHER |  | 20131207 | 1604 | 923131 | 1381 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 4423 | 37.4347 | -119.9804 | Lafata / 1848 / 470-3284: 4168 BURL DR. MARIPOSA | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 13-0081378 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99248800 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER | 84318 | 20131207 | 322 | 921845 | 954 | Distribution Circuit | Vegetation | Tree - fell into line | 584 | 324597 | 37.8547 | -120.2039 | Breaux / 1806 / 768-3522: 20461 Pine Mountain Dr Groveland | Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 13-0081180 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Line | 99249027 | PW | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1705 | 163781705 | FUSE | L349 | 20131207 | 147 | 921682 | 848 | Distribution Circuit | Equipment Failure/Involved | Other | 988 | 18417 | 37.96 | -120.4251 | Trujillo- M / 1708 / 768-3532: 18468 DALY CT | Snow-32 - 90 F | Pole-Wood | Broken, wire on ground | 13-0081147 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99249047 | PW | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 1637 | 20131207 | 256 | 921959 | 370 | Distribution Circuit | Equipment Failure/Involved | Other | 226 | 106978 | 37.999 | -120.392 | 1167 SHAW FLAT ROAD | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0081184 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99249023 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 26345 | 20131207 | 1128 | 922820 | 451 | Distribution Circuit | Vegetation | Tree - fell into line | 17 | 7667 | 38.0174 | -120.3958 | 2/P/S/OF 26345 | Overcast-32 - 90 F | Conductor, Overhead | On Ground | 13-0081361 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Three Phase Fault | 99248868 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1704 | 163761704 | RECLOSER | 8070 | 20131207 | 305 | 921939 | 691 | Distribution Circuit | Environmental/External | Ice or snow | 295 | 160699 | 37.9758 | -120.4466 | Haygood- K / 2011 / 564-1084: RAWHIDE | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0081176 | OH | Sus | 31040995 | yes | 2013 | DEC | Yes | Line to Ground | 99249030 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | TAR FLAT-0401 | 163240401 | FUSE | 1875 | 20131207 | 810 | 922117 | 253 | Distribution Circuit | Vegetation | Tree - branch fell on line | 143 | 36179 | 37.9872 | -120.3797 | MTR # 1004902713 WIRE DOWN ON BACK FEED FUSES STILL CLOSED | Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 13-0081222 | OH | Sus | 0 | yes | 2013 | DEC | Yes | Line to Ground | 99248986 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | RECLOSER | 9190 | 20140202 | 1341 | 958562 | 408 | Distribution Circuit | Vegetation | Tree - fell into line | 797 | 105286 | 38.0054 | -120.4054 | 21875 SHAWS FLAT | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0008172 | OH | Sus | 42069010 | yes | 2014 | FEB | Yes | Line to Ground | 99241676 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1705 | 163781705 | RECLOSER | 10580 | 20140209 | 1437 | 964368 | 722 | Distribution Circuit | Vegetation | Tree - grew into line | 357 | 184218 | 37.9489 | -120.4258 | MTR 1009244698 | Overcast-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0010162 | OH | Sus | 31055666 | yes | 2014 | FEB | Yes | Line to Line | 99240376 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE | 13446 | 20140227 | 408 | 973448 | 412 | Distribution Circuit | Vegetation | Tree - fell into line | 110 | 45320 | 37.5349 | -119.9826 | 1 SPAN E/O FUSE 13446 ON THE LOAD SIDE | Rain-32 - 90 F | Crossarm, Wood | Broken, wire on ground | 14-0013744 | OH | Sus | 31059422 | yes | 2014 | FEB | Yes | Line to Ground | 99237981 | CAW | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | OTHER |  | 20140311 | 2309 | 982845 | 499 | Distribution Circuit | Vegetation | Tree - fell into line | 139 | 26740 | 37.3223 | -119.5647 | BETWEEN METER #1006579700 AND METER #1006636418 | Strong winds-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0017396 | OH | Sus | 31062491 | yes | 2014 | MAR | Yes | Line to Ground | 99234592 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 10592 | 20140312 | 610 | 982980 | 433 | Distribution Circuit | Vegetation | Tree - fell into line | 128 | 47438 | 37.3224 | -119.6338 | WIRE DOWN AT FUSE 2946 | Strong winds-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0017428 | OH | Sus | 0 | yes | 2014 | MAR | Yes | Multi-Fault | 99235345 | PW | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 20084 | 20140402 | 140 | 993880 | 379 | Distribution Circuit | Equipment Failure/Involved | Other | 55 | 20845 | 37.9499 | -120.2813 | 16580 VERGUS ROAD at METER #1005716287 | Snow-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0022328 | OH | Sus | 42100970 | yes | 2014 | APR | Yes | Multi-Fault | 99231942 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1704 | 163761704 | FUSE | 1001 | 20140421 | 509 | 1002049 | 718 | Distribution Circuit | 3rd Party | Vehicle | 66 | 29686 | 37.9977 | -120.44 | Trujillo- M / 1708 / 768-3532: HWY 49 & FRAGUERO | Partly cloudy-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0026114 | OH | Sus | 31070494 | No | 2014 | APR | Yes | Line to Ground | 99229470 | PW | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | OTHER |  | 20140425 | 643 | 1004277 | 458 | Distribution Circuit | Animal | Other | 1891 | 259264 | 37.8514 | -120.3611 | Trujillo- M / 1708 / 768-3532: 1/N/O/40265 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0027140 | OH | Sus | 31071604 | yes | 2014 | APR | Yes | Three Phase Fault | 99228806 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 2443 | 20140426 | 247 | 1004938 | 590 | Distribution Circuit | Vegetation | Tree - fell into line | 119 | 70210 | 38.0312 | -120.4259 | BREAUX- PARIS: 22466 S Airport Rd in field across from spc 46 | Drizzle-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0027473 | OH | Sus | 0 | yes | 2014 | APR | Yes | Line to Line | 99228585 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | RECLOSER | 4500 | 20140506 | 1718 | 1011222 | 491 | Distribution Circuit | Equipment Failure/Involved | Other | 518 | 74331 | 37.4301 | -120.0996 | MTR# 1006161463 | Lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0029794 | OH | Sus | 0 | yes | 2014 | MAY | Yes | Line to Ground | 99227007 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1704 | 163781704 | OCB | OCB | 20140602 | 835 | 1027300 | 514 | Distribution Circuit | 3rd Party | Vehicle | 2965 | 555049 | 37.9042 | -120.4979 | METER #1004457585 1/S N/W OF CAP | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0035481 | OH | Sus | 31080048 | No | 2014 | JUN | Yes | Three Phase Fault | 99223035 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | OAKHURST-1102 | 254421102 | OTHER |  | 20140725 | 1357 | 1055335 | 127 | Distribution Circuit | 3rd Party | Vehicle | 928 | 10324 | 37.3124 | -119.648 | WIRE DOWN HOT 1/P/N/OF 5830 | Clear-Above 90 F | Conductor, Overhead | Broken, wire on ground | 14-0047004 | OH | Sus | 0 | yes | 2014 | JUL | Yes | None | 99215010 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 21665 | 20140819 | 2105 | 1069073 | 690 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 29846 | 37.8179 | -120.1278 | 23111 ELMORE RD- GROVELAND | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0051918 | OH | Sus | 31095961 | No | 2014 | AUG | Yes | Line to Line | 99211398 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MERCED FALLS-1102 | 252811102 | RECLOSER | 9480 | 20140914 | 1447 | 1081192 | 658 | Distribution Circuit | Equipment Failure/Involved | Other | 1561 | 101377 | 37.646 | -120.3112 |  | Partly cloudy-Above 90 F | Crossarm, Wood | Broken, wire on ground | 14-0056874 | OH | Sus | 0 | No | 2014 | SEP | Yes |  | 99208019 | CAW | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2101 | 254452101 | OCB | OCB | 20141030 | 812 | 1106111 | 706 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 3741 | 330890 | 37.5045 | -120.0082 | 4836 TRAINGLE RD | Partly cloudy-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0067019 | OH | Sus | 31111654 | No | 2014 | OCT | Yes | Line to Line | 99201365 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 10060 | 20141116 | 656 | 1113516 | 512 | Distribution Circuit | Equipment Failure/Involved | Other | 2701 | 402672 | 37.2925 | -119.5318 | 322673030153 | Rain-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0070276 | OH | Sus | 42274323 | No | 2014 | NOV | Yes | Three Phase Fault | 99199090 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MIWUK-1702 | 163661702 | RECLOSER | 47143 | 20141129 | 1032 | 1119284 | 442 | Distribution Circuit | Vegetation | Tree - fell into line | 339 | 48950 | 38.0046 | -120.2627 | MCGETTIGAN- MATTHEW: C/O AMERICAN RIVER AND CRYSTAL FALLS | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 14-0072412 | OH | Sus | 31118086 | No | 2014 | NOV | Yes | Line to Ground | 99197573 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 24876 | 20141231 | 303 | 1156075 | 807 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 3228 | 37.3528 | -119.6035 | 1P N/OF MTR #1006017845 | Combination wind/rain/lightning-32 - 90 F | Pole-Wood | Broken, wire on ground | 14-0079606 | OH | Sus | 0 | yes | 2014 | DEC | Yes | Line to Line | 99189553 | PW | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | FUSE | 1335 | 20150205 | 912 | 1172571 | 307 | Distribution Circuit | Equipment Failure/Involved | Other | 1 | 307 | 37.8035 | -120.2944 | 5/S/S/OF 1335 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0009479 | OH | Sus | 0 | yes | 2015 | FEB | Yes | Line to Ground | 99185514 | CSO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 5732 | 20150214 | 1422 | 1190152 | 608 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 45 | 6462 | 37.399 | -119.7004 | Cederlof / 2076 / 559-760-7819: 46617 rd 620 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0013366 | OH | Sus | 31134717 | No | 2015 | FEB | Yes | Line to Line | 99182001 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 48691 | 20150220 | 213 | 1192885 | 427 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 22905 | 37.9909 | -120.2789 | MTR 1004862569 | Clear-32 - 90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0014469 | OH | Sus | 42336014 | No | 2015 | FEB | Yes | Line to Line | 99181274 | CSO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1704 | 163351704 | FUSE | 20809 | 20150407 | 1515 | 1215267 | 297 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 13959 | 38.0332 | -120.3676 | MCGETTIGAN- MATTHEW: C/O GUNSIGHT AND QUAIL MINE | Combination wind/rain/lightning-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0025059 | OH | Sus | 0 | yes | 2015 | APR | Yes | Line to Ground | 99174885 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | RECLOSER | 47488 | 20150606 | 1635 | 1244902 | 620 | Distribution Circuit | 3rd Party | Vehicle | 575 | 100729 | 37.9652 | -120.2511 | 1P N/OF L1655 (WILLOW & OAK) | Lightning-32 - 90 F | Pole-Wood | Broken, wire on ground | 15-0039059 | OH | Sus | 31159521 | No | 2015 | JUN | Yes | Line to Ground | 99165221 | PW | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 12236 | 20150627 | 2344 | 1257983 | 675 | Distribution Circuit | Vegetation | Tree - fell into line | 217 | 126790 | 37.5328 | -119.835 | DANIELI- PRESTON: 2/P/N/OF MTR 1009072170 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0043803 | OH | Sus | 31164730 | No | 2015 | JUN | Yes | Line to Ground | 99161552 | CSO | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1704 | 163761704 | FUSE | 20361 | 20150627 | 1851 | 1257894 | 181 | Distribution Circuit | Vegetation | Tree - branch fell on line | 29 | 5249 | 37.992 | -120.4398 | TX FEEDING MTR #1004862914 | Clear-32 - 90 F | Conductor, Overhead | Broken, wire on ground | 15-0043784 | OH | Sus | 42416769 | No | 2015 | JUN | Yes | Line to Line | 99161600 | CO | OH | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 64615 | 20150715 | 1901 | 1268745 | 264 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 6 | 1584 | 38.0125 | -120.2842 | LINE AND BUCK TAP TO WEST NORTH OF 64615 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0047765 | OH | Sus | 42427185 | No | 2015 | JUL | Yes | Line to Ground | 1145448 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | 2363 | 20150727 | 1711 | 1278241 | 1078 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 12649 | 38.0408 | -120.2291 | LD SIDE OF at MTR # 1005428415 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0050806 | OH | Sus | 0 | No | 2015 | JUL | Yes | Line to Line | 1147780 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 2181 | 20150730 | 1911 | 1280503 | 565 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 26776 | 37.8103 | -120.133 | BREAUX- PARIS: 23057 Hells Hollow Rd 2/spns/S/W/COs 2181 | Partly Cloudy-Above 90 | Conductor, Overhead | Broken, wire on ground | 15-0051772 | OH | Sus | 31173089 | No | 2015 | JUL | Yes | Line to Ground | 1148362 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1704 | 163781704 | FUSE | 21433 | 20150814 | 1744 | 1288636 | 863 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1726 | 37.8872 | -120.4978 | McKinnon / 2074 / 573-0394: TX POLE TO CAL TRAN METER # 1005427921 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0055160 | OH | Sus | 0 | No | 2015 | AUG | Yes | Three Phase Fault | 1150780 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1701 | 162831701 | FUSE | L1123 | 20150904 | 1431 | 1300264 | 519 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 155 | 44725 | 38.1976 | -120.0125 | MTR #1004717958 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0059433 | OH | Sus | 31181717 | No | 2015 | SEP | Yes | Line to Line | 1153811 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER | 76030 | 20150918 | 1705 | 1308318 | 638 | Distribution Circuit | 3rd Party | Vehicle | 181 | 35222 | 37.8992 | -120.4551 | 1 SP S/OF MTR # 1006424138 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0062207 | OH | Sus | 0 | No | 2015 | SEP | Yes | Three Phase Fault | 1155832 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | 1887 | 20151004 | 1648 | 1316851 | 632 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 331 | 142141 | 38.0605 | -120.2692 | 16800 ESTRALITA DR | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 15-0067853 | OH | Sus | 31188456 | yes | 2015 | OCT | Yes | Line to Ground | 1160622 | CAW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 12236 | 20151105 | 816 | 1336024 | 493 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 217 | 27676 | 37.5328 | -119.835 | MTR# 1006384892 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0075831 | OH | Sus | 31197887 | No | 2015 | NOV | Yes | Line to Line | 1166664 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | FUSE | 10522 | 20151116 | 1035 | 1343133 | 396 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 6182 | 37.6192 | -120.212 | MTR# 1006145230 | Clear-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0078375 | OH | Sus | 0 | yes | 2015 | NOV | Yes | Line to Line | 1168839 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 1871 | 20151121 | 1036 | 1346464 | 367 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 50 | 18350 | 38.0679 | -120.1872 | 5 POLES LD SIDE OF 1871 | Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0079868 | OH | Sus | 42575176 | No | 2015 | NOV | Yes | Line to Ground | 1169988 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1702 | 163351702 | JUMPER | WIRE DOWN @ MTR # 1004821585 | 20151124 | 1327 | 1348068 | 325 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1102 | 252460 | 38.0162 | -120.2723 | WIRE DOWN at MTR # 1004821585 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on object | 15-0080616 | OH | Sus | 42576397 | yes | 2015 | NOV | Yes | Line to Ground | 1170570 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | JUMPER | 21549 | 20151223 | 2328 | 1370621 | 519 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 19827 | 37.3738 | -119.6115 | S/OF MTR #1006021770 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | On Ground | 15-0087043 | OH | Sus | 42597065 | No | 2015 | DEC | Yes | Line to Ground | 1177110 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1705 | 163781705 | FUSE | 6697 | 20151223 | 604 | 1370108 | 414 | Distribution Circuit | Vegetation | Tree - fell into line | 178 | 73692 | 37.9607 | -120.426 | 4 SPANS LOAD SIDE 6697 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 15-0086925 | OH | Sus | 31208459 | No | 2015 | DEC | Yes | Three Phase Fault | 1176956 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | OAKHURST-1103 | 254421103 | FUSE | 5727 | 20151225 | 44 | 1371535 | 874 | Distribution Circuit | Environmental/External | Ice or snow | 259 | 87847 | 37.5461 | -119.647 | at MTR# 1005536996 | Partly Cloudy-Fog-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 15-0087260 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Ground | 1177341 | CSO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2103 | 254432103 | RECLOSER | 10820 | 20151231 | 1327 | 1375337 | 177 | Distribution Circuit | 3rd Party | Vehicle | 764 | 73036 | 37.1549 | -119.7343 | 1 SS OF 8191 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 15-0087944 | OH | Sus | 0 | No | 2015 | DEC | Yes | Line to Ground | 1178278 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1705 | 163351705 | FUSE | 20315 | 20160106 | 2159 | 1379171 | 841 | Distribution Circuit | Vegetation | Tree - fell into line | 87 | 73167 | 37.9905 | -120.2264 | MTR 1004860965 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0003663 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Line | 1179157 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 5120 | 20160106 | 2125 | 1379151 | 2632 | Distribution Circuit | Environmental/External | Ice or snow | 519 | 1024009 | 37.4809 | -119.6372 | 6SP N/N/E/OF MTR #1005515876- SS 5120 | Overcast-Fog-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0003668 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Three Phase Fault | 1179162 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 19484 | 20160107 | 109 | 1379247 | 357 | Distribution Circuit | Environmental/External | Ice or snow | 48 | 17136 | 37.9961 | -120.2528 | BREAUX- PARIS: 20538 Charlotte Ct | Overcast-Fog-Drizzle-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0003679 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1179175 | CSO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | OCB | 1103/2 | 20160110 | 2214 | 1381282 | 550 | Distribution Circuit | Animal | Other | 3525 | 253505 | 37.3218 | -119.6342 | 1 P E/OF 6302 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0004409 | OH | Sus | 0 | No | 2016 | JAN | Yes | Three Phase Fault | 1179848 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MIWUK-1702 | 163661702 | FUSE | S2125 | 20160111 | 944 | 1381464 | 636 | Distribution Circuit | 3rd Party | Vehicle | 11 | 1586 | 38.0059 | -120.2667 | EOL at MTR# 1004856563 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0004505 | OH | Sus | 0 | No | 2016 | JAN | Yes | Line to Line | 1179933 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 6285 | 20160116 | 609 | 1384836 | 622 | Distribution Circuit | Animal | Other | 367 | 120150 | 37.191 | -119.789 | at 6285 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0005757 | OH | Sus | 0 | No | 2016 | JAN | Yes | Line to Line | 1180727 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MERCED FALLS-1102 | 252811102 | RECLOSER | 9470 | 20160119 | 1828 | 1388089 | 680 | Distribution Circuit | 3rd Party | Vehicle | 978 | 94490 | 37.646 | -120.3111 | 1 E/OF 25108 IN BET 25108 & C807 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0006622 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Multi-Fault | 1181431 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 57503 | 20160120 | 906 | 1388415 | 420 | Distribution Circuit | 3rd Party | Vehicle | 6 | 2520 | 37.2212 | -119.5117 | 56646 WILD PLUM | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0006847 | OH | Sus | 0 | No | 2016 | JAN | Yes | Line to Line | 1181619 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | WOODWARD-2108 | 255292108 | OTHER | WIRE DOWN FEEDING TWD 22865 RD 211 | 20160127 | 1136 | 1393077 | 404 | Distribution Circuit | Equipment Failure/Involved | Overhead | 57 | 8194 | 37.081 | -119.6926 | 22865 RD 211 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0008703 | OH | Sus | 31215430 | No | 2016 | JAN | Yes | Line to Ground | 1182952 | CSO | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | INDIAN FLAT-1104 | 252691104 | JUMPER | WIRE DOWN BETWEEN 10344 | 20160131 | 938 | 1394754 | 554 | Distribution Circuit | Equipment Failure/Involved | Overhead | 60 | 17622 | 37.6986 | -119.7605 | Bebout/ /559-676-1325: C/O 10344 | Overcast-Snow-Below 32 F | Connector or Splice (OH) | Broken, wire on ground | 16-0009416 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1183492 | CSO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | RECLOSER | 10240 | 20160131 | 1637 | 1395231 | 733 | Distribution Circuit | Vegetation | Tree - fell into line | 464 | 115224 | 37.5245 | -119.9173 | BETWEEN C509 & 10002 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009474 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Line to Ground | 1183551 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 5120 | 20160131 | 507 | 1394729 | 2098 | Distribution Circuit | Vegetation | Tree - fell into line | 420 | 698189 | 37.4809 | -119.6372 | 11 POLES LD SIDE OF 5589 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0009358 | OH | Sus | 0 | yes | 2016 | JAN | Yes | Three Phase Fault | 1183448 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 23239 | 20160206 | 259 | 1399304 | 885 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 13581 | 37.9858 | -120.2825 | BREAUX- PARIS: 20140 Chipmunk Rd | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0011042 | OH | Sus | 0 | No | 2016 | FEB | Yes | Line to Line | 1184711 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | 23489 | 20160209 | 1041 | 1400784 | 219 | Distribution Circuit | Vegetation | Tree - branch fell on line | 6 | 1314 | 38.0309 | -120.2404 | MTR #1004814981 | Clear-32-90 F | Conductor, Overhead | On Ground | 16-0011565 | OH | Sus | 42626799 | No | 2016 | FEB | Yes | Line to Line | 1185112 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1704 | 163761704 | FUSE | S1341 | 20160218 | 1049 | 1408303 | 176 | Distribution Circuit | Vegetation | Tree - branch fell on line | 113 | 10966 | 37.9601 | -120.4519 | MTR# 1004734206 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0013806 | OH | Sus | 0 | yes | 2016 | FEB | Yes | Line to Ground | 1186828 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 1993 | 20160303 | 1557 | 1415341 | 754 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 20 | 15080 | 37.8233 | -120.1928 | MTR 1004732804- 1P S/OF MTR #1004732804 | Overcast-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0017076 | OH | Sus | 31222952 | No | 2016 | MAR | Yes | Line to Line | 1189088 | CAW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | COARSEGOLD-2102 | 254432102 | JUMPER | WIRE DOWN 38045 | 20160306 | 736 | 1421365 | 274 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 716 | 37.3062 | -119.6091 | 38045 CEADER CREEK | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018355 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Open Circuit | 1190207 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9180 | 20160306 | 107 | 1420859 | 362 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3016 | 480667 | 37.9527 | -120.3681 | BET S115 & L1207 (W/OF L1207 at TAKE OFF POLE) | Strong Winds-Heavy Rain-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018111 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1189981 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 48853 | 20160306 | 623 | 1421203 | 221 | Distribution Circuit | Vegetation | Tree - fell into line | 70 | 11608 | 37.3294 | -119.6363 | MTR# 1006380894 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018287 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190151 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 26356 | 20160306 | 1158 | 1422022 | 494 | Distribution Circuit | Vegetation | Tree - bark fell into line | 4 | 1976 | 38.034 | -120.3803 | MTR# 1005418968 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018479 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1190317 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1102 | 252531102 | JUMPER | WIRE DOWN ON TREE 2 N/OF MTR# 1006639337 | 20160306 | 1254 | 1422248 | 236 | Distribution Circuit | Equipment Failure/Involved | Overhead | 168 | 6164 | 37.2603 | -119.54 | 2 N/OF MTR# 1006639337 | Partly Cloudy-32-90 F | Insulator | Broken, wire on object | 16-0018471 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Ground | 1190309 | INS | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 19717 | 20160307 | 1221 | 1424020 | 184 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 3162 | 37.9238 | -120.3513 | 16880 LIME KILN RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0018897 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Three Phase Fault | 1190690 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | RECLOSER | 65908 | 20160314 | 1759 | 1431500 | 478 | Distribution Circuit | Vegetation | Tree - fell into line | 660 | 60845 | 37.9575 | -120.3133 | 14044 & 13978 TUOLUMNE RD | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0021356 | OH | Sus | 31225116 | yes | 2016 | MAR | Yes | Line to Line | 1192644 | CAW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | S1933 | 20160314 | 511 | 1430821 | 577 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6924 | 38.0109 | -120.4198 | BREAUX- PARIS: 10231 Von Kleiben | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 16-0021136 | OH | Sus | 0 | yes | 2016 | MAR | Yes | Line to Line | 1192505 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE | 4579 | 20160330 | 951 | 1441569 | 474 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 33 | 8762 | 37.5502 | -119.9259 | MTR # 1007098643 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 16-0024994 | OH | Sus | 31228132 | No | 2016 | MAR | Yes | Line to Ground | 1195383 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MERCED FALLS-1102 | 252811102 | FUSE | 22768 | 20160409 | 603 | 1447405 | 633 | Distribution Circuit | Equipment Failure/Involved | Overhead | 75 | 47475 | 37.6532 | -120.3201 | Mayo / 2078 / 631-1388: 14377 Avenida Central | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0027399 | OH | Sus | 0 | yes | 2016 | APR | Yes | Line to Line | 1196988 | PW | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20160411 | 1453 | 1448988 | 474 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 157 | 38354 | 37.8183 | -120.0961 | SIUDZINSKI- MARK: 3 spans loadside of L429 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0027865 | OH | Sus | 31230611 | No | 2016 | APR | Yes | Line to Ground | 1197401 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1704 | 163781704 | RECLOSER | 88630 | 20160419 | 1032 | 1453641 | 296 | Distribution Circuit | 3rd Party | Contact with High Voltage- 3rd party | 4 | 1184 | 37.9006 | -120.5169 | 4SP/LOAD SIDE OF 88630 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0029685 | OH | Sus | 42682191 | No | 2016 | APR | Yes | Line to Ground | 1198767 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 10788 | 20160422 | 1438 | 1455954 | 439 | Distribution Circuit | Vegetation | Tree - fell into line | 76 | 16776 | 37.2869 | -119.6558 | 3 S/OF 10426 | Overcast-Rain-Lightning-32-90 F | Pole-Wood | Broken, wire on ground | 16-0030736 | OH | Sus | 0 | yes | 2016 | APR | Yes | Line to Line | 1199403 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1704 | 163761704 | FUSE | S1341 | 20160427 | 2012 | 1460508 | 176 | Distribution Circuit | Equipment Failure/Involved | Overhead | 114 | 7084 | 37.9601 | -120.4519 | MTR #1004902373 | Overcast-Rain-Lightning-32-90 F | Crossarm, Wood | Broken, wire on object | 16-0032119 | OH | Sus | 0 | yes | 2016 | APR | Yes | Force Out | 1200554 | CAW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | FUSE | L1473 | 20160502 | 2338 | 1463600 | 370 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4070 | 38.0425 | -120.3774 | MTR# 1004861032 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0033372 | OH | Sus | 42689117 | No | 2016 | MAY | Yes | Line to Line | 1201580 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER | 9480 | 20160505 | 834 | 1464885 | 394 | Distribution Circuit | Vegetation | Tree - branch fell on line | 595 | 63870 | 37.6317 | -120.1547 | 1 S/OF 4543 | Overcast-32-90 F | Conductor, Overhead | On Ground | 16-0033937 | OH | Sus | 31236727 | yes | 2016 | MAY | Yes | Line to Ground | 1202029 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | OCB | 2101/2 | 20160516 | 239 | 1470120 | 569 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1248 | 252330 | 37.5858 | -120.1258 | WIRE DOWN 1 P/N/OF FUCO 24029 | Clear-32-90 F | Insulator | Broken, wire on ground | 16-0036163 | OH | Sus | 31238692 | No | 2016 | MAY | Yes | Line to Ground | 1203574 | INS | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE | 10022 | 20160615 | 1431 | 1489544 | 371 | Distribution Circuit | Vegetation | Tree - branch fell on line | 74 | 15253 | 37.3042 | -119.6009 | TX MTR #1005673188 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0043496 | OH | Sus | 31247634 | No | 2016 | JUN | Yes | Line to Line | 1209222 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | TAR FLAT-0402 | 163240402 | OTHER | WIRE DOWN DEAD END POLE AT 11928 CA-49 | 20160616 | 1952 | 1491046 | 688 | Distribution Circuit | 3rd Party | Vehicle | 2 | 1376 | 38.0034 | -120.3829 | DEAD END POLE AT 11928 CA-49 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on object | 16-0043854 | OH | Sus | 0 | No | 2016 | JUN | Yes | Open Circuit | 1209460 | PW | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | RECLOSER | 8120 | 20160703 | 1500 | 1500598 | 480 | Distribution Circuit | Vegetation | Tree - fell into line | 418 | 38812 | 38.0254 | -120.405 | 49507 FUCO | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 16-0047689 | OH | Sus | 31250855 | No | 2016 | JUL | Yes | Line to Line | 1212234 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | TAR FLAT-0401 | 163240401 | FUSE | 1875 | 20160714 | 1343 | 1510054 | 383 | Distribution Circuit | Vegetation | Tree - fell into line | 144 | 23094 | 37.9871 | -120.3797 | MTR # 1004902703 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 16-0049939 | OH | Sus | 31257404 | yes | 2016 | JUL | Yes | Line to Line | 1213886 | CO | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2487 | 20160721 | 1051 | 1513601 | 332 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 244 | 30527 | 38.0618 | -120.1974 | MCGETTIGAN- MATTHEW: C/O RED CEDAR & WHITE FIR | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0051534 | OH | Sus | 31258517 | No | 2016 | JUL | Yes | Line to Line | 1214972 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | COARSEGOLD-2102 | 254432102 | RECLOSER | 5380 | 20160722 | 847 | 1514091 | 353 | Distribution Circuit | 3rd Party | Vehicle | 354 | 27810 | 37.3089 | -119.5849 | at MTR# 1005616117 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0051771 | OH | Sus | 0 | No | 2016 | JUL | Yes | Line to Line | 1215113 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1704 | 163781704 | RECLOSER | 8040 | 20160727 | 1153 | 1517098 | 385 | Distribution Circuit | Vegetation | Tree - fell into line | 139 | 14734 | 37.8996 | -120.5039 | E/ OF AND N/OF MTR# 1007303471 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 16-0052942 | OH | Sus | 42754212 | yes | 2016 | JUL | Yes | Line to Ground | 1215995 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 90320 | 20160811 | 2351 | 1525164 | 702 | Distribution Circuit | 3rd Party | Vehicle | 996 | 217504 | 37.8474 | -120.2022 | 1 POLE SOUTH OF LR90320 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0056786 | OH | Sus | 0 | No | 2016 | AUG | Yes | Three Phase Fault | 1218499 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 90589 | 20160814 | 105 | 1526058 | 389 | Distribution Circuit | 3rd Party | Vehicle | 2 | 778 | 37.2244 | -119.769 | 1P/N/OF 90859 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0057170 | OH | Sus | 0 | No | 2016 | AUG | Yes | Line to Line | 1218777 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER | 76030 | 20160815 | 1543 | 1526880 | 727 | Distribution Circuit | 3rd Party | Vehicle | 184 | 122905 | 37.8992 | -120.4551 | 1 N/OF 4907 | Clear-Above 90 | Pole-Wood | Broken, wire on ground | 16-0057465 | OH | Sus | 31263432 | No | 2016 | AUG | Yes | Three Phase Fault | 1219008 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE | 21164 | 20160902 | 1300 | 1535955 | 147 | Distribution Circuit | Vegetation | Tree - fell into line | 37 | 2855 | 37.498 | -119.9094 | 1 3/4 SPAN N/OF MTR# 1005640251 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0062082 | OH | Sus | 42780812 | No | 2016 | SEP | Yes | Line to Ground | 1222055 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 10788 | 20160908 | 1313 | 1538472 | 519 | Distribution Circuit | 3rd Party | Vehicle | 76 | 6900 | 37.2869 | -119.6558 | MTR 1006641890 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 16-0063252 | OH | Sus | 0 | No | 2016 | SEP | Yes | Line to Ground | 1222855 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | S1933 | 20160920 | 314 | 1544496 | 421 | Distribution Circuit | Vegetation | Tree - fell into line | 11 | 4631 | 38.0109 | -120.4198 | CGC 320225554900 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0065861 | OH | Sus | 31272195 | No | 2016 | SEP | Yes | Line to Ground | 1224612 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 10496 | 20160929 | 1043 | 1549976 | 907 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 4834 | 37.4753 | -119.7295 | Lafata / 1848 / 470-3284: 6140 CHOWCHILLA MTN RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0068471 | OH | Sus | 0 | No | 2016 | SEP | Yes | Line to Line | 1226542 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 10493 | 20161015 | 2102 | 1561981 | 438 | Distribution Circuit | Vegetation | Tree - fell into line | 168 | 73584 | 37.5639 | -119.8548 | 3 SPANS N/OF 10493 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072700 | OH | Sus | 31277975 | yes | 2016 | OCT | Yes | Line to Line | 1229739 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 23544 | 20161015 | 1812 | 1561731 | 487 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 487 | 38.0887 | -120.1437 | MCGETTIGAN- MATTHEW: 2 spans load side of 23544 | Overcast-Drizzle-32-90 F | Insulator | Broken, wire on object | 16-0072639 | OH | Sus | 42815641 | yes | 2016 | OCT | Yes | Line to Ground | 1229680 | INS | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20161016 | 1751 | 1563532 | 840 | Distribution Circuit | Vegetation | Tree - fell into line | 158 | 79992 | 37.8183 | -120.0961 | 2 SPANS LD SIDE S1215 AND S1999 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0072999 | OH | Sus | 0 | yes | 2016 | OCT | Yes | Line to Ground | 1230029 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | RECLOSER | 10940 | 20161104 | 1056 | 1576553 | 283 | Distribution Circuit | 3rd Party | Vehicle | 7925 | 624024 | 37.9883 | -120.2832 | 2 SS OF 23515 | Clear-32-90 F | Pole-Wood | Broken, wire on object | 16-0078045 | OH | Sus | 0 | No | 2016 | NOV | Yes | Line to Line | 1233888 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 5571 | 20161109 | 906 | 1578699 | 218 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 9 | 1586 | 37.4532 | -119.6413 | Lafata / 1848 / 470-3284: HWY 41 .1 MI S OF SUGAR PINE RAILROAD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0078863 | OH | Sus | 31283226 | No | 2016 | NOV | Yes | Line to Ground | 1234512 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | FUSE | 5558 | 20161109 | 912 | 1578689 | 242 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 2 | 484 | 37.2948 | -119.5347 | BEYOND 5558 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0078927 | OH | Sus | 31283231 | No | 2016 | NOV | Yes | Line to Ground | 1234560 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2102 | 254432102 | OTHER | WIRE DOWN S/O MTR 1005674918 | 20161116 | 2008 | 1582514 | 497 | Distribution Circuit | Equipment Failure/Involved | Overhead | 17 | 5712 | 37.1688 | -119.6683 | 1 P SE/OF & 2 P SW/OF MTR # 1005674918 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0080372 | OH | Sus | 42881640 | No | 2016 | NOV | Yes | Line to Ground | 1235642 | CSO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2103 | 254432103 | RECLOSER | 5020 | 20161117 | 931 | 1583123 | 339 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1149 | 157409 | 37.2065 | -119.7141 | MTR 1006018897 & 1 S/OF 10300 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0080459 | OH | Sus | 42881870 | No | 2016 | NOV | Yes | Line to Ground | 1235749 | CSO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 10496 | 20161127 | 1848 | 1590136 | 396 | Distribution Circuit | Equipment Failure/Involved | Overhead | 18 | 7128 | 37.4753 | -119.7295 | 3 P W/OF MTR # 1008951638 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0082504 | OH | Sus | 0 | yes | 2016 | NOV | Yes | Force Out | 1237241 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S1217 | 20161127 | 242 | 1589606 | 599 | Distribution Circuit | Environmental/External | Ice or snow | 43 | 16523 | 38.047 | -120.2018 | BREAUX- PARIS 4062: 22812 Coffill Rd | Overcast-Fog-Snow-Below 32 F | Insulator | Broken, wire on ground | 16-0082424 | OH | Sus | 0 | yes | 2016 | NOV | Yes | Line to Ground | 1237174 | INS | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | JUMPER | WIRE DOWN 2 E/O MTR1004211382 | 20161127 | 840 | 1589843 | 341 | Distribution Circuit | Vegetation | Tree - branch fell on line | 1 | 341 | 38.0563 | -120.2184 | 2 E/OF MTR # 1004211382 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0082435 | OH | Sus | 0 | yes | 2016 | NOV | Yes | Open Circuit | 1237182 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1101 | 254421101 | FUSE | 5533 | 20161127 | 1642 | 1590066 | 604 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 1208 | 37.4213 | -119.7113 | 1 S/OF MTR 1006375881 | Partly Cloudy-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on ground | 16-0082482 | OH | Sus | 31285779 | yes | 2016 | NOV | Yes | Line to Ground | 1237223 | CAW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 5120 | 20161127 | 53 | 1589614 | 977 | Distribution Circuit | Equipment Failure/Involved | Overhead | 421 | 390149 | 37.4809 | -119.6372 | 5 N/OF 5581 LD SIDE OF MTR 1005670817 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0082390 | OH | Sus | 0 | yes | 2016 | NOV | Yes | Line to Line | 1237146 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1101 | 254421101 | FUSE | 5533 | 20161128 | 859 | 1590335 | 513 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2 | 1026 | 37.4213 | -119.7113 | 2 SPANS SS OF MTR 1006375880 | Overcast-Fog-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 16-0082669 | OH | Sus | 42885254 | No | 2016 | NOV | Yes | Line to Ground | 1237378 | CSO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1103 | 252531103 | FUSE | 10279 | 20161202 | 653 | 1593180 | 127 | Distribution Circuit | Vegetation | Tree - fell into line | 180 | 22860 | 37.2326 | -119.4712 | MULTIPLE LOCATIONS BEYOND FUCO 10279 | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 16-0083541 | OH | Sus | 0 | No | 2016 | DEC | Yes | Line to Ground | 1238110 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | 147619 | 20161210 | 2131 | 1599495 | 947 | Distribution Circuit | Vegetation | Tree - fell into line | 62 | 24536 | 38.0177 | -120.2686 | TX METER #1004816686 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 16-0085046 | OH | Sus | 0 | yes | 2016 | DEC | Yes | Line to Line | 1239600 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 1637 | 20170107 | 2259 | 1622433 | 283 | Distribution Circuit | Vegetation | Tree - fell into line | 230 | 58733 | 37.999 | -120.3919 | BET 1637 AND MTR# 1004901902 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0004880 | OH | Sus | 42914802 | yes | 2017 | JAN | Yes | Line to Ground | 1244678 | CO | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | JUMPER | WIRE DOWN E/OF MTR 1005713488 | 20170112 | 719 | 1641289 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 2176 | 38.0347 | -120.258 | E/OF MTR 1005713488 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 17-0008375 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Line | 1247778 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MIWUK-1702 | 163661702 | RECLOSER | 68380 | 20170113 | 1236 | 1642591 | 480 | Distribution Circuit | Vegetation | Tree - fell into line | 448 | 80801 | 38.0151 | -120.2744 | 19283 | Clear-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0008796 | OH | Sus | 31296346 | yes | 2017 | JAN | Yes | Line to Ground | 1248081 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 23547 | 20170124 | 48 | 1666049 | 2292 | Distribution Circuit | Equipment Failure/Involved | Overhead | 34 | 77928 | 38.0922 | -120.1355 | 25929 MONO DR | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0014466 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Multi-Fault | 1253159 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | FUSE | 5502 | 20170124 | 942 | 1665483 | 3182 | Distribution Circuit | Vegetation | Tree - fell into line | 81 | 184269 | 37.2959 | -119.5214 | LD SIDE 5502 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0014294 | OH | Sus | 0 | yes | 2017 | JAN | Yes | Line to Ground | 1253038 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | L527 | 20170127 | 1356 | 1668850 | 209 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 150 | 31350 | 38.0498 | -120.2242 | L527 | Clear-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0015706 | OH | Sus | 42934234 | No | 2017 | JAN | Yes | Line to Ground | 1254159 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 23939 | 20170131 | 1510 | 1671515 | 996 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 140 | 21346 | 37.7126 | -120.1088 | MTR # 1007101157 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0016457 | OH | Sus | 0 | No | 2017 | JAN | Yes | Line to Line | 1254739 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | FUSE | 6095 | 20170206 | 541 | 1675873 | 574 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 16344 | 37.2381 | -119.519 | MTR 1007053189 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0017698 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Three Phase Fault | 1255650 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE | 12238 | 20170208 | 1923 | 1682463 | 632 | Distribution Circuit | Vegetation | Tree - branch fell on line | 11 | 2227 | 37.4871 | -119.8032 | ON TAP SOUTH WEST OF MTR # 1006384409 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0019153 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256765 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | RECLOSER | 37282 | 20170208 | 1544 | 1682239 | 722 | Distribution Circuit | Animal | Other | 2066 | 127270 | 37.4622 | -119.9482 | CGC# 321611734129 | Overcast-Fog-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0019112 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Ground | 1256726 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | OAKHURST-1101 | 254421101 | FUSE | 5672 | 20170208 | 1359 | 1682033 | 219 | Distribution Circuit | Equipment Failure/Involved | Overhead | 76 | 15369 | 37.3237 | -119.778 | MTR # 1006379018 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0019082 | OH | Sus | 0 | yes | 2017 | FEB | Yes | Line to Line | 1256703 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 79097 | 20170211 | 1029 | 1685985 | 337 | Distribution Circuit | Vegetation | Tree - branch fell on line | 12 | 4044 | 37.5864 | -119.8512 | 3 SPANS N/E OF 79097 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0020321 | OH | Sus | 31305295 | No | 2017 | FEB | Yes | Line to Ground | 1257702 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | OAKHURST-1103 | 254421103 | FUSE | 10662 | 20170214 | 1323 | 1688485 | 767 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 6642 | 37.3652 | -119.712 | TX MTR #1005283103 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0021076 | OH | Sus | 0 | No | 2017 | FEB | Yes | Line to Line | 1258343 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | 92593 | 20170303 | 1215 | 1718680 | 395 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 290 | 114550 | 38.0594 | -120.268 | MTR #1004559074 & 1004240462 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 17-0028175 | OH | Sus | 31309081 | No | 2017 | MAR | Yes | Line to Line | 1264564 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1704 | 163761704 | RECLOSER | 8070 | 20170303 | 1011 | 1718531 | 341 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 363 | 39867 | 37.9758 | -120.4466 | MTR #1004938867 | Partly Cloudy-32-90 F | Conductor, Overhead | On Ground | 17-0028133 | OH | Sus | 31308965 | No | 2017 | MAR | Yes | Line to Ground | 1264541 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | OAKHURST-1103 | 254421103 | FUSE | 5727 | 20170305 | 839 | 1719815 | 864 | Distribution Circuit | Vegetation | Tree - fell into line | 259 | 110631 | 37.5461 | -119.647 | MTR 1010194946 & 1ST TX POLE NORTH OF 5728 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0028471 | OH | Sus | 42958963 | yes | 2017 | MAR | Yes | Three Phase Fault | 1264832 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MERCED FALLS-1102 | 252811102 | RECLOSER | 38748 | 20170312 | 2035 | 1725652 | 494 | Distribution Circuit | Equipment Failure/Involved | Overhead | 293 | 70260 | 37.7017 | -120.3395 | 1P/S/OF 55527 | Clear-32-90 F | Insulator | Broken, wire on object | 17-0030274 | OH | Sus | 31311908 | No | 2017 | MAR | Yes | Line to Ground | 1266210 | INS | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | S1577 | 20170321 | 1439 | 1732167 | 930 | Distribution Circuit | Vegetation | Tree - fell into line | 92 | 85405 | 38.0263 | -120.2459 | L855 | Overcast-Fog-Heavy Rain-Lightning-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0032466 | OH | Sus | 31313851 | yes | 2017 | MAR | Yes | Multi-Fault | 1267816 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2485 | 20170405 | 1344 | 1744773 | 717 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 92 | 22970 | 38.0518 | -120.2027 | MTR # 1004737621 23495 KREITZER WAY | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0036805 | OH | Sus | 0 | No | 2017 | APR | Yes | Line to Ground | 1271170 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2102 | 254452102 | FUSE | 7247 | 20170413 | 1653 | 1757351 | 752 | Distribution Circuit | Vegetation | Tree - fell into line | 42 | 21794 | 37.4466 | -119.898 | 1 E/OF 4 WAY THAT IS W/OF MTR# 1005154786 | Partly Cloudy-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 17-0040109 | OH | Sus | 0 | yes | 2017 | APR | Yes | Line to Ground | 1273722 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 2657 | 20170413 | 911 | 1756844 | 322 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 4762 | 37.991 | -120.4135 | 1P/SS/OF MTR 1004240574 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0039888 | OH | Sus | 42993699 | yes | 2017 | APR | Yes | Line to Ground | 1273596 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2477 | 20170415 | 1710 | 1758619 | 631 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 22 | 13882 | 38.02 | -120.2224 | MTR 1004861524 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0040527 | OH | Sus | 0 | No | 2017 | APR | Yes | Line to Line | 1274031 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | RECLOSER | 6210 | 20170420 | 1625 | 1762108 | 1005 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 32160 | 37.269 | -119.7137 | SOURCE SIDE OF 10322 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0041781 | OH | Sus | 31320810 | No | 2017 | APR | Yes | Line to Ground | 1274967 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | RECLOSER | 37288 | 20170420 | 1617 | 1762165 | 544 | Distribution Circuit | Vegetation | Tree - fell into line | 691 | 159420 | 37.4205 | -119.8772 | Elam /1916 / 559-760-1774: 3908 INDIAN PEAK | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0041788 | OH | Sus | 31320807 | No | 2017 | APR | Yes | Line to Ground | 1274974 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 1715 | 20170423 | 1136 | 1765235 | 414 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 6888 | 37.9194 | -120.3504 | 15900 LINE KILN RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0042215 | OH | Sus | 31321143 | No | 2017 | APR | Yes | Line to Ground | 1275380 | CO | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | OTHER | WIRE DOWN @ MTR 1009437218 | 20170428 | 1639 | 1769842 | 411 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 1029 | 37.9122 | -120.258 | MTR 1009437218 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0043794 | OH | Sus | 43003546 | yes | 2017 | APR | Yes | Open Circuit | 1276393 | CSO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | OTHER | WIRE DOWN AT MTR #1004898140 | 20170429 | 1210 | 1770449 | 527 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 805 | 115347 | 38.0194 | -120.4093 | MTR #1004898140 & NORTH IN MAINLINE | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 17-0043886 | OH | Sus | 31322660 | No | 2017 | APR | Yes | Open Circuit | 1276508 | CAW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 5596 | 20170506 | 1106 | 1776149 | 466 | Distribution Circuit | Equipment Failure/Involved | Overhead | 263 | 59313 | 37.212 | -119.5539 | NEAR MTR #1006376365 | Overcast-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0045793 | OH | Sus | 43008063 | yes | 2017 | MAY | Yes | Line to Ground | 1277920 | CSO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 6285 | 20170515 | 1600 | 1782596 | 606 | Distribution Circuit | Vegetation | Tree - fell into line | 224 | 20007 | 37.191 | -119.7891 | MTR 1008855210 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0048096 | OH | Sus | 31325928 | No | 2017 | MAY | Yes | Line to Line | 1279709 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | COARSEGOLD-2102 | 254432102 | TRIP-SAVER | 10207 | 20170610 | 624 | 1800952 | 656 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 11166 | 37.2983 | -119.6165 | MTR #1010203429 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 17-0054164 | OH | Sus | 0 | No | 2017 | JUN | Yes | Line to Line | 1284059 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 20587 | 20170621 | 1356 | 1813936 | 464 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 11 | 5104 | 38.1013 | -120.125 | BREAUX- PARIS 4062: 26494 Crystal Rd Long Barn | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0057405 | OH | Sus | 0 | yes | 2017 | JUN | Yes | Line to Ground | 1286691 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | RECLOSER | 4410 | 20170707 | 1431 | 1825609 | 896 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 658 | 554306 | 37.5011 | -119.809 | Lafata / 1848 / 470-3284: WESTFALL RD 3 S/O 87467 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0061288 | OH | Sus | 43052231 | yes | 2017 | JUL | Yes | Line to Ground | 1289510 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1704 | 163761704 | RECLOSER | 55798 | 20170712 | 20 | 1829522 | 378 | Distribution Circuit | Equipment Failure/Involved | Overhead | 364 | 56929 | 37.9759 | -120.4466 | 1 POLE N/OF 95951 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0062203 | OH | Sus | 43058076 | No | 2017 | JUL | Yes | Line to Ground | 1290249 | CSO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1704 | 163761704 | FUSE | 20361 | 20170717 | 1905 | 1834185 | 290 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 2950 | 37.992 | -120.4398 | S/OF MTR # 1004858721 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0063524 | OH | Sus | 0 | No | 2017 | JUL | Yes | Line to Ground | 1291298 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | OCB | 9470 | 20170718 | 123 | 1834361 | 11132 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 2284 | 14358 | 37.5858 | -120.1258 | Lafata / 1848 / 470-3284: detwiler fire - MAINLINE N/O BV SUB GONE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 17-0063494 | OH | Sus | 0 | No | 2017 | JUL | Yes | Force Out | 1291312 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | JUMPER | WIRE DOWN HOT @ MTR# 1005642690 | 20170801 | 1745 | 1844119 | 565 | Distribution Circuit | Vegetation | Tree - fell into line | 396 | 15180 | 37.4636 | -119.7386 | at MTR# 1005642690 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0067149 | OH | Sus | 0 | No | 2017 | AUG | Yes | Line to Ground | 1293744 | CO | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 5571 | 20170829 | 1247 | 1862552 | 15986 | Distribution Circuit | Vegetation | Tree - cutting- PG&E contractor | 946 | 5894785 | 37.4532 | -119.6413 | SINGLE PHASE TAP GOING WEST OF 5571 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 17-0073823 | OH | Sus | 0 | No | 2017 | AUG | Yes | Line to Ground | 1298507 | CO | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MERCED FALLS-1102 | 252811102 | FUSE | 8522 | 20170904 | 1756 | 1870000 | 608 | Distribution Circuit | 3rd Party | Vehicle | 50 | 30400 | 37.6559 | -120.3488 | 1 N/OF VILLARREAL ON ALAMO | Clear-Heat Wave-Above 90 | Pole-Wood | Broken, wire on ground | 17-0075888 | OH | Sus | 31348994 | yes | 2017 | SEP | Yes | Line to Line | 1300130 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 6064 | 20170908 | 2114 | 1873727 | 395 | Distribution Circuit | Vegetation | Tree - fell into line | 377 | 49858 | 37.9604 | -120.3764 | 1/S/E/OF 21067 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0077137 | OH | Sus | 43102388 | No | 2017 | SEP | Yes | Line to Ground | 1301030 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1705 | 163781705 | OCB | 1705/2 | 20170918 | 2350 | 1881407 | 905 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2523 | 382303 | 37.9035 | -120.4971 | POLES 7- 8 & 9 LOAD SIDE OF SWITCH 9059 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0079858 | OH | Sus | 31351880 | No | 2017 | SEP | Yes | Line to Ground | 1303099 | CSO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | S1557 | 20170929 | 1445 | 1888267 | 574 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 135 | 36746 | 38.0657 | -120.2752 | 16630 HILLSIDE DR | Clear-32-90 F | Crossarm, Wood | Broken, wire on object | 17-0082961 | OH | Sus | 0 | No | 2017 | SEP | Yes | Line to Line | 1305048 | CAW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | TRIP-SAVER | 803 | 20171003 | 1715 | 1890287 | 274 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 29866 | 38.0417 | -120.3867 | 2P/W/OF MTR 1004899087 | Clear-Strong Winds-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0083893 | OH | Sus | 43123846 | yes | 2017 | OCT | Yes | Line to Line | 1305689 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1704 | 163761704 | FUSE | 20361 | 20171003 | 1523 | 1890256 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 6728 | 37.992 | -120.4398 | 9624 MORMAN CREEK | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 17-0083873 | OH | Sus | 0 | yes | 2017 | OCT | Yes | Line to Ground | 1305678 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | OTHER | WIRE DOWN 2/P/S & 1/P/W/OF 961393 | 20171107 | 1133 | 1917580 | 201 | Distribution Circuit | Equipment Failure/Involved | Overhead | 23 | 4576 | 37.9435 | -120.2439 | 17555 APPLE COLONY RD- TUOLUMNE | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 17-0093234 | OH | Sus | 43208252 | No | 2017 | NOV | Yes | Open Circuit | 1312681 | CSO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | S1793 | 20180109 | 856 | 4801 | 234 | Distribution Circuit | Vegetation | Tree - fell into line | 27 | 2470 | 37.9719 | -120.2605 | MTR #1004858271 | Overcast-Drizzle-32-90 F | Conductor, Overhead | On Ground | 18-0004669 | OH | Sus | 31372953 | yes | 2018 | JAN | Yes | Line to Ground | 1323856 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | RECLOSER | 2101/2 | 20180116 | 2055 | 9406 | 553 | Distribution Circuit | Animal | Bird found | 1254 | 300920 | 37.4958 | -120.0437 | AT METER 1007101268 & WIRE DOWN S/OF 24006 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0006595 | OH | Sus | 43254875 | No | 2018 | JAN | Yes | Line to Line | 1325108 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | OTHER | WIRE DOWN | 20180120 | 654 | 11195 | 496 | Distribution Circuit | Animal | Bird found | 2813 | 214833 | 37.963 | -120.3137 | ON TUOLUMNE RD at FUCO 27308 | Clear-Below 32 F | Connector or Splice (OH) | Broken, wire on ground | 18-0007573 | OH | Sus | 43258181 | No | 2018 | JAN | Yes | Open Circuit | 1325672 | CSO | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | INDIAN FLAT-1104 | 252691104 | OTHER | WIRE DOWN W/OF 13434 | 20180122 | 1406 | 12095 | 222 | Distribution Circuit | Equipment Failure/Involved | Overhead | 605 | 131122 | 37.6742 | -119.7856 | W/OF 13434 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0007922 | OH | Sus | 0 | No | 2018 | JAN | Yes | Line to Ground | 1325927 | CSO | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1101 | 254421101 | FUSE | 5533 | 20180125 | 834 | 13664 | 498 | Distribution Circuit | Environmental/External | Ice or snow | 2 | 996 | 37.4213 | -119.7113 | 7 POLES LD SIDE OF 5533 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 18-0008877 | OH | Sus | 43261223 | No | 2018 | JAN | Yes | Line to Ground | 1326479 | CSO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 4681 | 20180222 | 2205 | 29736 | 597 | Distribution Circuit | Vegetation | Tree - fell into line | 97 | 57909 | 37.4515 | -119.8508 | 2 S/OF MTR#1006382204 | Partly Cloudy-Fog-Below 32 F | Crossarm, Wood | Broken, wire on ground | 18-0016579 | OH | Sus | 31380339 | yes | 2018 | FEB | Yes | Line to Ground | 1331601 | CAW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | RECLOSER | 10320 | 20180227 | 228 | 32463 | 552 | Distribution Circuit | Equipment Failure/Involved | Overhead | 244 | 92134 | 37.2141 | -119.5525 | 7 N/OF 10320 | Overcast-Snow-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0017587 | OH | Sus | 31381332 | yes | 2018 | FEB | Yes | Line to Ground | 1332322 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | OAKHURST-1101 | 254421101 | FUSE | 5532 | 20180301 | 1557 | 35253 | 1411 | Distribution Circuit | Vegetation | Tree - fell into line | 262 | 156058 | 37.4022 | -119.7329 | 2 SPANS S/OF 22743 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0018775 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333149 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE | L1123 | 20180301 | 1740 | 35459 | 1065 | Distribution Circuit | Vegetation | Tree - fell into line | 155 | 165075 | 38.1976 | -120.0125 | McKinnon / 2074 / 573-0394: wtr # 1004759552 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0018841 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333199 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE | 26305 | 20180301 | 2253 | 35850 | 835 | Distribution Circuit | Vegetation | Tree - fell into line | 100 | 46424 | 38.1956 | -120.0115 | MTR# 1004717551 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0018960 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333316 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE | 26312 | 20180301 | 2218 | 35816 | 2544 | Distribution Circuit | Vegetation | Tree - fell into line | 21 | 53424 | 38.1963 | -120.0118 | 1 E/OF 26312 | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0019226 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333425 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 76863 | 20180302 | 716 | 36009 | 716 | Distribution Circuit | Vegetation | Tree - fell into line | 127 | 90932 | 37.8492 | -120.2097 | MTR # 1004815059 | Overcast-Fog-Snow-Below 32 F | Pole-Wood | Broken, wire on ground | 18-0019030 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Three Phase Fault | 1333350 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 27335 | 20180302 | 959 | 35957 | 405 | Distribution Circuit | Vegetation | Tree - fell into line | 63 | 25410 | 37.8134 | -120.1192 | MTR #1004902081 & 2 N/O 2029 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019065 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333363 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | TRIP-SAVER | 803 | 20180302 | 532 | 35953 | 879 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 49059 | 38.0417 | -120.3867 | SIUDZINSKI- MARK: 12543 remington mine | Overcast-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0019033 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333352 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | RECLOSER | 37282 | 20180302 | 1943 | 36795 | 1103 | Distribution Circuit | Vegetation | Tree - fell into line | 2078 | 146446 | 37.4622 | -119.9482 | at MTR#1005154020 | Overcast-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019246 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333452 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1702 | 163351702 | FUSE | 1289 | 20180303 | 1616 | 37674 | 1134 | Distribution Circuit | Vegetation | Tree - fell into line | 29 | 32886 | 38.0394 | -120.2346 | MTR 1008707943 LD SIDE OF 1289 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019485 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333674 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 9210 | 20180303 | 120 | 36997 | 2288 | Distribution Circuit | Equipment Failure/Involved | Overhead | 157 | 312642 | 37.8183 | -120.0961 | SOURCE SIDE OF FUCO 27342 & at S1999 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019342 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333545 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | INDIAN FLAT-1104 | 252691104 | FUSE | 10213 | 20180303 | 713 | 37139 | 33 | Distribution Circuit | 3rd Party | Customer Equipment | 1 | 33 | 37.6731 | -119.7998 | 2 S/OF 10213 | Overcast-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0019325 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Force Out | 1333530 | CO | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 21548 | 20180303 | 333 | 37088 | 685 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 2055 | 38.0454 | -120.2079 | 23310 HWY 108 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0019314 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333517 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 8667 | 20180303 | 302 | 37256 | 828 | Distribution Circuit | Vegetation | Tree - fell into line | 354 | 240996 | 38.0355 | -120.2262 | at MTR# 1004856780 | Overcast-Fog-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0019356 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333561 | CO | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2525 | 20180303 | 640 | 37123 | 670 | Distribution Circuit | Vegetation | Tree - fell into line | 13 | 8710 | 38.0594 | -120.2154 | MTR# 101037655 & 1004213122 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0019376 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333585 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S1219 | 20180303 | 1033 | 37377 | 305 | Distribution Circuit | Vegetation | Tree - branch fell on line | 403 | 34563 | 38.0581 | -120.1864 | 20792 TELELE TRL | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0019411 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1333613 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | L2213 | 20180303 | 218 | 37117 | 2117 | Distribution Circuit | Vegetation | Tree - fell into line | 41 | 27712 | 38.0199 | -120.2222 | at MTR#1004861472 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on object | 18-0019433 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333628 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | RECLOSER | 38218 | 20180303 | 158 | 37026 | 790 | Distribution Circuit | Vegetation | Tree - fell into line | 2969 | 1218636 | 38.0486 | -120.2438 | at 23502 (MAIN LINE)- 8-12 SP S/OF L1005- 1P S/OF 1771- 3 W/OF L1615 | Overcast-Fog-Snow-Below 32 F | Crossarm, Wood | Broken, wire on ground | 18-0019299 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Three Phase Fault | 1333502 | CAW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | S2243 | 20180303 | 202 | 37095 | 754 | Distribution Circuit | Vegetation | Tree - fell into line | 232 | 174928 | 38.0384 | -120.2478 | 1P E/OF MTR #1004720593 | Overcast-Fog-Below 32 F | Crossarm, Wood | Broken, wire on ground | 18-0019317 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1333523 | CAW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE | 2387 | 20180304 | 1037 | 38013 | 1871 | Distribution Circuit | Equipment Failure/Involved | Overhead | 6 | 11226 | 38.1518 | -120.0539 | 1 P W OF MTR#500140599 | Partly Cloudy-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 18-0019585 | OH | Sus | 31382524 | No | 2018 | MAR | Yes | Three Phase Fault | 1333780 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 19767 | 20180322 | 1127 | 50676 | 396 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2772 | 38.0108 | -120.2918 | 3 POLES N/W AND 2 POLES S/W OF 19767 | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025504 | OH | Sus | 31385498 | yes | 2018 | MAR | Yes | Line to Line | 1337600 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE | 22075 | 20180322 | 1236 | 50725 | 489 | Distribution Circuit | Vegetation | Tree - fell into line | 86 | 20519 | 37.4974 | -119.8338 | MTR# 1005638184 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025621 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1337636 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | L1167 | 20180322 | 1110 | 50625 | 800 | Distribution Circuit | Vegetation | Tree - fell into line | 32 | 19781 | 38.0091 | -120.2316 | 21656 SOUTH KNOX/2SP S/OF MTR #1004938505 | Overcast-Fog-Heavy Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0025539 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1337609 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | TRANSFORMER | 66945 | 20180322 | 1723 | 51161 | 1362 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 1362 | 37.3319 | -119.5727 | TRANSFORMER MTR#1010246089 | Overcast-Fog-Rain-32-90 F | Pole-Wood | Broken, wire on ground | 18-0025973 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Ground | 1337898 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1704 | 163761704 | FUSE | S1341 | 20180322 | 17 | 49953 | 708 | Distribution Circuit | Equipment Failure/Involved | Overhead | 114 | 55841 | 37.9601 | -120.4519 | 31 POLES N/OF S1341 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0025256 | OH | Sus | 43305954 | yes | 2018 | MAR | Yes | Line to Line | 1337472 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 6819 | 20180323 | 1535 | 52091 | 232 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 232 | 38.0361 | -120.2101 | SIUDZINSKI- MARK: at 6819 FUSES | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0026113 | OH | Sus | 0 | yes | 2018 | MAR | Yes | Line to Line | 1337977 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 5596 | 20180419 | 1150 | 70113 | 560 | Distribution Circuit | Equipment Failure/Involved | Overhead | 266 | 61190 | 37.212 | -119.5539 | MTR# 1006579664 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 18-0033741 | OH | Sus | 0 | No | 2018 | APR | Yes | Line to Line | 1343760 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | RECLOSER | 4500 | 20180430 | 2200 | 77063 | 545 | Distribution Circuit | 3rd Party | Vehicle | 531 | 104914 | 37.4304 | -120.0991 | REGS 8216 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 18-0037068 | OH | Sus | 0 | No | 2018 | APR | Yes | Three Phase Fault | 1345979 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | L2107 | 20180529 | 4 | 95457 | 672 | Distribution Circuit | 3rd Party | Vehicle | 1861 | 110640 | 37.844 | -120.2114 | MTR 1004736862 | Clear-32-90F | Pole-Wood | Broken, wire on object | 18-0044945 | OH | Sus | 0 | yes | 2018 | MAY | Yes | Line to Ground | 1351973 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | JUMPER | OJS @ MTR# 1004719395 | 20180618 | 252 | 111673 | 774 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 23220 | 37.8642 | -120.2177 | MTR# 1004241275 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0051812 | OH | Sus | 0 | No | 2018 | JUN | Yes | Line to Line | 1357276 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2103 | 254432103 | OCB | 2103/2 | 20180619 | 1441 | 113097 | 186 | Distribution Circuit | Animal | Bird found | 2015 | 123838 | 37.2274 | -119.6906 | 2 S/OF 10783 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0052327 | OH | Sus | 43376901 | No | 2018 | JUN | Yes | Three Phase Fault | 1357784 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1103 | 252531103 | SWITCH | 5443 | 20180710 | 1908 | 128495 | 362 | Distribution Circuit | Environmental/External | Fire- Forest/Grass | 576 | 7488 | 37.2338 | -119.5041 | TRANS POLE 0/2 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on object | 18-0058587 | OH | Sus | 0 | yes | 2018 | JUL | Yes | Force Out | 1362677 | CSO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | RECLOSER | 4160 | 20180713 | 2234 | 131276 | 386 | Distribution Circuit | Animal | Bird found | 794 | 103372 | 37.4958 | -120.0437 | 1 N/OF MTR# 1006535500 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 18-0059705 | OH | Sus | 43401025 | No | 2018 | JUL | Yes | Line to Ground | 1363668 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1705 | 163781705 | FUSE | 53401 | 20180714 | 1522 | 131763 | 908 | Distribution Circuit | Vegetation | Tree - fell into line | 22 | 19976 | 37.9655 | -120.402 | BREAUX- PARIS 4062: 11292 McKibbon Dr Jamestown | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0059858 | OH | Sus | 31399946 | No | 2018 | JUL | Yes | Multi-Fault | 1363797 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | INDIAN FLAT-1104 | 252691104 | OTHER | WIRE DOWN NEAR 308805 | 20180716 | 811 | 132517 | 654 | Distribution Circuit | Equipment Failure/Involved | Overhead | 282 | 147760 | 37.6759 | -119.778 | JUST LD SIDE OF 308805 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on object | 18-0060177 | OH | Sus | 0 | No | 2018 | JUL | Yes | Open Circuit | 1364138 | CSO | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | OTHER | WIRE DOWN @ 19510 PORTO FINO | 20180731 | 1157 | 145990 | 207 | Distribution Circuit | 3rd Party | Other | 13 | 2438 | 37.974 | -120.2465 | 19510 PORTO FINO | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0065388 | OH | Sus | 43426691 | No | 2018 | JUL | Yes | Line to Ground | 1368051 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | OAKHURST-1101 | 254421101 | FUSE | 27200 | 20180805 | 1356 | 149354 | 293 | Distribution Circuit | Vegetation | Tree - fell into line | 25 | 7325 | 37.393 | -119.7516 | 1 P/E & 1 P/S OF MTR #1005022933 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 18-0066905 | OH | Sus | 0 | No | 2018 | AUG | Yes | Force Out | 1369204 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | RECLOSER | 8120 | 20180918 | 1151 | 176594 | 771 | Distribution Circuit | 3rd Party | Vehicle | 430 | 79100 | 38.0254 | -120.405 | at L2073 WITH 3 SPANS GOING BACK TO SOURCE | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0080882 | OH | Sus | 31406728 | No | 2018 | SEP | Yes | Line to Ground | 1378917 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | RECLOSER | 8120 | 20180927 | 1447 | 182845 | 517 | Distribution Circuit | Vegetation | Tree - fell into line | 430 | 51706 | 38.0254 | -120.405 | 1 W/OF 26354 | Clear-Above 90 | Conductor, Overhead | Broken, wire on ground | 18-0084242 | OH | Sus | 31409835 | No | 2018 | SEP | Yes | Line to Line | 1381230 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | L2155 | 20181002 | 1037 | 185849 | 636 | Distribution Circuit | Vegetation | Tree - branch fell on line | 15 | 9540 | 37.9491 | -120.2563 | DEAD END POLE at MTR 5T3502 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 18-0085648 | OH | Sus | 0 | yes | 2018 | OCT | Yes | Line to Line | 1382358 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1704 | 163351704 | FUSE | 20775 | 20181004 | 1835 | 188647 | 490 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 980 | 38.0172 | -120.3564 | BREAUX- PARIS 4062: 2/P/NE/FUCO 20775 behind 21156 Lyons Bald Mountain | Overcast-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0087112 | OH | Sus | 31411068 | yes | 2018 | OCT | Yes | Line to Ground | 1383195 | CAW | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | RECLOSER | 5310 | 20181012 | 1532 | 194032 | 472 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 1123 | 51894 | 37.2286 | -119.7102 | DAHLEM / 1847 / 559-493-8472: 36902 CEDAR MOUNTAIN LN | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 18-0089960 | OH | Sus | 31412549 | No | 2018 | OCT | Yes | Line to Ground | 1385212 | CAW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2103 | 254432103 | FUSE | 87159 | 20181020 | 1727 | 199424 | 573 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 2292 | 37.2053 | -119.6845 | AT MTR #1010207042 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0092506 | OH | Sus | 0 | No | 2018 | OCT | Yes | Line to Ground | 1387116 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | JUMPER | UN-NUMBERED FUCO | 20181103 | 1156 | 208092 | 613 | Distribution Circuit | 3rd Party | Vehicle | 19 | 7891 | 38.0646 | -120.2707 | MTR 1004240193 | Clear-32-90 F | Pole-Wood | Broken, wire on object | 18-0096783 | OH | Sus | 0 | No | 2018 | NOV | Yes | Line to Line | 1390272 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 26389 | 20181106 | 1128 | 209829 | 379 | Distribution Circuit | Vegetation | Tree - branch fell on line | 472 | 39666 | 37.9882 | -120.3881 | MTR# 1010471275 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0097463 | OH | Sus | 0 | No | 2018 | NOV | Yes | Line to Ground | 1390947 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 20181110 | 2337 | 213194 | 633 | Distribution Circuit | 3rd Party | Vehicle | 824 | 58920 | 38.0069 | -120.3478 | FUCO 91773 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0098890 | OH | Sus | 0 | No | 2018 | NOV | Yes | Line to Line | 1391968 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 10373 | 20181111 | 1409 | 213501 | 761 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 19 | 1769 | 37.4787 | -119.8686 | MTR 1005639143 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0099049 | OH | Sus | 0 | No | 2018 | NOV | Yes | Line to Ground | 1392031 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S2253 | 20181122 | 300 | 221664 | 902 | Distribution Circuit | Vegetation | Tree - fell into line | 96 | 31687 | 38.0331 | -120.233 | 1SP S/OF MTR #1004861015 | Overcast-Fog-Drizzle-32-90 F | Conductor, Overhead | On Ground | 18-0102252 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Ground | 1394394 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1705 | 163781705 | FUSE | 24314 | 20181124 | 2042 | 223941 | 528 | Distribution Circuit | Vegetation | Tree - fell into line | 56 | 29568 | 37.9619 | -120.4178 | 2 E/OF 24314 | Partly Cloudy-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0103021 | OH | Sus | 31416760 | No | 2018 | NOV | Yes | Line to Line | 1394992 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER | 76030 | 20181128 | 1106 | 226483 | 590 | Distribution Circuit | 3rd Party | Vehicle | 189 | 31404 | 37.8992 | -120.4551 | 1 N/W OF MTR# 1005427965 | Overcast-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 18-0104308 | OH | Sus | 0 | yes | 2018 | NOV | Yes | Line to Line | 1395801 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 1673 | 20181202 | 305 | 231433 | 360 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 2880 | 38.0112 | -120.4188 | MTR # 1004736683 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0106023 | OH | Sus | 31417481 | No | 2018 | DEC | Yes | Line to Line | 1396940 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1702 | 163351702 | FUSE | 22618 | 20181203 | 1319 | 232741 | 684 | Distribution Circuit | 3rd Party | Vehicle | 30 | 5720 | 38.0513 | -120.2135 | MTR 100473340 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 18-0106528 | OH | Sus | 0 | No | 2018 | DEC | Yes | Line to Line | 1397364 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | RECLOSER | 65908 | 20181206 | 641 | 234728 | 126 | Distribution Circuit | Animal | Bird found | 666 | 55227 | 37.9575 | -120.3133 | BET 21459 & SW 96519 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0107501 | OH | Sus | 0 | No | 2018 | DEC | Yes | Line to Ground | 1397902 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 46623 | 20181212 | 1035 | 238654 | 264 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 14 | 3696 | 37.5072 | -119.8434 | 1 W/OF 46623 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0108787 | OH | Sus | 43614020 | No | 2018 | DEC | Yes | Line to Ground | 1399200 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | L1209 | 20181217 | 502 | 242036 | 373 | Distribution Circuit | Vegetation | Tree - fell into line | 75 | 8463 | 37.9627 | -120.2916 | 3P/E/OF MTR 1004899449 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0109600 | OH | Sus | 31418781 | yes | 2018 | DEC | Yes | Line to Line | 1400239 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 23223 | 20181218 | 1011 | 242960 | 566 | Distribution Circuit | Equipment Failure/Involved | Overhead | 80 | 10112 | 37.9786 | -120.3151 | 1 SS/OF MTR#1008772966 | Clear-32-90 F | Woodpin | Broken, wire on ground | 18-0109845 | OH | Sus | 0 | No | 2018 | DEC | Yes | Line to Ground | 1400590 | WP | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | FUSE | 10353 | 20181220 | 1025 | 244675 | 904 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 19 | 17176 | 37.5762 | -119.8532 | 1.5SP S/OF MTR #1007100759 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 18-0110140 | OH | Sus | 31419421 | No | 2018 | DEC | Yes | Line to Line | 1401100 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1704 | 163351704 | TRIP-SAVER | 803 | 20181224 | 1809 | 246730 | 221 | Distribution Circuit | Vegetation | Tree - fell into line | 109 | 9704 | 38.0461 | -120.3654 | 23255 WOODS CREEK WAY | Overcast-Fog-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0110545 | OH | Sus | 43621705 | yes | 2018 | DEC | Yes | Line to Ground | 1401624 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2102 | 254432102 | JUMPER | 43403 FUSES & OH TAP DOWN | 20181228 | 711 | 248583 | 355 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 355 | 37.2561 | -119.5653 | 34969 RD 223 | Clear-Below 32 F | Conductor, Overhead | Broken, wire on ground | 18-0110948 | OH | Sus | 31419920 | No | 2018 | DEC | Yes | Line to Ground | 1402130 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 96353 | 20181231 | 957 | 250142 | 563 | Distribution Circuit | Vegetation | Tree - fell into line | 12 | 6756 | 37.3231 | -119.5648 | DAHLEM / 1847 / 559-493-8472: 39500 BRIER PLACE | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 18-0111258 | OH | Sus | 0 | yes | 2018 | DEC | Yes | Line to Line | 1402513 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 10060 | 20181231 | 911 | 250074 | 1940 | Distribution Circuit | Vegetation | Tree - fell into line | 104 | 85232 | 37.2927 | -119.5325 | PORTER JR.- JOHN: 37907 EMORY LN | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 18-0111180 | OH | Sus | 31420266 | yes | 2018 | DEC | Yes | Line to Line | 1402415 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | L1773 | 20190105 | 1547 | 254496 | 243 | Distribution Circuit | Vegetation | Tree - branch fell on line | 252 | 39971 | 37.9584 | -120.3215 | JEO 460215 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0004870 | OH | Sus | 43626634 | yes | 2019 | JAN | Yes | Line to Ground | 1403406 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | RECLOSER | 10400 | 20190110 | 251 | 262158 | 788 | Distribution Circuit | 3rd Party | Vehicle | 1458 | 136681 | 37.2216 | -119.7687 | JNO 10573 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0007321 | OH | Sus | 31421646 | No | 2019 | JAN | Yes | Line to Line | 1405162 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 46623 | 20190120 | 2137 | 277757 | 348 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 4872 | 37.5072 | -119.8434 | 1 W/OF 46623 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0012778 | OH | Sus | 43641240 | yes | 2019 | JAN | Yes | Line to Ground | 1409110 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | S1359 | 20190121 | 1523 | 278453 | 707 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 2121 | 38.0211 | -120.4329 | SIUDZINSKI- MARK: 1 POLE AND 3 POLE LOAD SIDE OF S1359 | Partly Cloudy-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0012889 | OH | Sus | 0 | No | 2019 | JAN | Yes | Line to Line | 1409230 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | JUMPER | A & B PHASES BROKEN @ CGC# 322360028030 | 20190203 | 826 | 288734 | 334 | Distribution Circuit | Vegetation | Tree - fell into line | 47 | 13706 | 37.2679 | -119.69 | CGC# 322360028030 | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0017501 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1411916 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | OTHER | WIRE DOWN 1 SP LD SIDE OF L465 | 20190206 | 1517 | 294500 | 2793 | Distribution Circuit | Vegetation | Tree - fell into line | 1 | 2793 | 37.8504 | -120.1685 | 1SP LD OF L465 | Partly Cloudy-Drizzle-32-90 F | Pole-Wood | Broken, wire on ground | 19-0020041 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1413776 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 9817 | 20190206 | 1001 | 294123 | 3134 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 27360 | 37.9659 | -120.3132 | 3SP SS OF CGC 320570053500 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0019685 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Line | 1413515 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1702 | 163351702 | JUMPER | WIRE DOWN N/OF MTR# 1004902033 | 20190208 | 830 | 295973 | 1563 | Distribution Circuit | Vegetation | Tree - fell into line | 30 | 43785 | 38.0265 | -120.2865 | MTR# 1004902033 | Partly Cloudy-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0019986 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Open Circuit | 1413749 | CO | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | BEAR VALLEY-2105 | 252192105 | JUMPER | WIRE DOWN @ MTR# 1007092937 | 20190211 | 1503 | 300038 | 182 | Distribution Circuit | Vegetation | Tree - fell into line | 129 | 1846 | 37.7563 | -120.1393 | MTR# 1007092937 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 19-0021176 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Force Out | 1414774 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 5544 | 20190211 | 1335 | 299929 | 146 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1168 | 37.4554 | -119.6411 | LD SIDE OF 5544 | Clear-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0021061 | OH | Sus | 0 | yes | 2019 | FEB | Yes | Line to Ground | 1414721 | CO | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | OTHER | WIRE DOWN 1 E/OF MTR# 1007063322 | 20190304 | 919 | 330713 | 296 | Distribution Circuit | Equipment Failure/Involved | Overhead | 81 | 23692 | 37.5965 | -120.1861 | 1 E/OF MTR# 1007063322 | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0030438 | OH | Sus | 43689822 | No | 2019 | MAR | Yes | Line to Ground | 1421861 | CSO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 7427 | 20190306 | 1656 | 333179 | 290 | Distribution Circuit | Vegetation | Tree - fell into line | 14 | 4060 | 37.4002 | -119.8783 | .5 SPAN E OF MTR #1005643945 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0031485 | OH | Sus | 0 | yes | 2019 | MAR | Yes | Line to Ground | 1422421 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 10516 | 20190311 | 1245 | 336301 | 615 | Distribution Circuit | Animal | Other | 36 | 5446 | 37.4723 | -119.8758 | MTR# 1005637063 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0032670 | OH | Sus | 0 | No | 2019 | MAR | Yes | Line to Ground | 1423308 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | FUSE | 23334 | 20190319 | 1252 | 342984 | 244 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 313 | 70602 | 37.9892 | -120.3328 | 2 SE/OF MTR# 1004241751 - 20502 PHOENIX LAKE RD | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0035101 | OH | Sus | 43711436 | No | 2019 | MAR | Yes | Line to Line | 1425124 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1704 | 163781704 | RECLOSER | 8040 | 20190329 | 938 | 350118 | 535 | Distribution Circuit | Equipment Failure/Involved | Overhead | 135 | 25839 | 37.8996 | -120.5039 | 5 P LD SIDE OF MTR #1005775132 OPEN | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0038234 | OH | Sus | 43722795 | No | 2019 | MAR | Yes | Line to Ground | 1427185 | CSO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | RECLOSER | 4170 | 20190409 | 1521 | 356875 | 885 | Distribution Circuit | Vegetation | Tree - fell into line | 662 | 162762 | 37.6103 | -120.1339 | S/OF 77095 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0041008 | OH | Sus | 0 | yes | 2019 | APR | Yes | Line to Ground | 1429121 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 4597 | 20190409 | 1527 | 357224 | 950 | Distribution Circuit | Vegetation | Tree - fell into line | 18 | 17100 | 37.733 | -120.0818 | MTR 1006385569 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0041008 | OH | Sus | 0 | yes | 2019 | APR | Yes | Line to Ground | 1429180 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 1949 | 20190409 | 1510 | 356846 | 914 | Distribution Circuit | Vegetation | Tree - bark fell into line | 155 | 28200 | 37.853 | -120.1659 | MTR 1008889962 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0041056 | OH | Sus | 31433234 | yes | 2019 | APR | Yes | Line to Ground | 1429152 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | FUSE | 22357 | 20190409 | 1454 | 356832 | 174 | Distribution Circuit | Vegetation | Tree - fell into line | 4 | 696 | 37.9799 | -120.3298 | SIUDZINSKI- MARK: 14381 edgemont acres | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0041006 | OH | Sus | 43731033 | yes | 2019 | APR | Yes | Line to Line | 1429120 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 2262 | 20190420 | 1106 | 364366 | 749 | Distribution Circuit | Vegetation | Tree - bark fell into line | 84 | 16586 | 37.2859 | -119.6311 | MTR # 1005022497 | Overcast-32-90 F | Pole-Wood | Broken, wire on ground | 19-0044583 | OH | Sus | 0 | yes | 2019 | APR | Yes | Line to Ground | 1431748 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | WOODWARD-2108 | 255292108 | FUSE | 13044 | 20190510 | 42 | 377434 | 328 | Distribution Circuit | Vegetation | Tree - fell into line | 48 | 15744 | 37.0505 | -119.6495 | MTR# 1005773068 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0050592 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Line to Ground | 1435739 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | RECLOSER | 8120 | 20190515 | 2326 | 381650 | 546 | Distribution Circuit | Vegetation | Tree - branch fell on line | 431 | 193382 | 38.0254 | -120.405 | MTR# 1005519957 | Overcast-Heavy Rain-32-90 F | Jumper | Broken, wire on ground | 19-0052471 | OH | Sus | 43783264 | yes | 2019 | MAY | Yes | Line to Line | 1437119 | JMP | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1704 | 163351704 | RECLOSER | 8140 | 20190516 | 155 | 381827 | 468 | Distribution Circuit | Vegetation | Tree - fell into line | 921 | 70461 | 38.0069 | -120.3478 | 2 POLES LD SIDE OF 22953 | Overcast-Heavy Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0052499 | OH | Sus | 0 | yes | 2019 | MAY | Yes | Multi-Fault | 1437145 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 48691 | 20190519 | 1218 | 385202 | 503 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 8794 | 37.9911 | -120.2788 | MTR# 1008770243 | Overcast-32-90 F | Crossarm, Wood | Broken, wire on ground | 19-0053957 | OH | Sus | 31442854 | yes | 2019 | MAY | Yes | Line to Line | 1438171 | CAW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | L2153 | 20190718 | 1758 | 459745 | 737 | Distribution Circuit | Vegetation | Tree - fell into line | 39 | 5955 | 37.9496 | -120.2648 | 1 N/OF & 2 N/OF MTR# 1004934029 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0078981 | OH | Sus | 31458821 | No | 2019 | JUL | Yes | Line to Line | 1457198 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 1715 | 20190719 | 638 | 459930 | 507 | Distribution Circuit | Vegetation | Tree - fell into line | 78 | 24042 | 37.9194 | -120.3504 | SIUDZINSKI- MARK: at mtr 1004862052 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0079030 | OH | Sus | 0 | No | 2019 | JUL | Yes | Line to Line | 1457250 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | OTHER | WIRE DOWN 1 E/OF 4 S/OF 89943 | 20190723 | 1652 | 469660 | 427 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1206 | 513358 | 37.2143 | -119.5059 | 1 E/OF 4 S/OF 89943 | Partly Cloudy-Above 90 | Conductor, Overhead | Broken, wire on ground | 19-0080383 | OH | Sus | 43897222 | yes | 2019 | JUL | Yes | Open Circuit | 1458207 | CO | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | TAR FLAT-0402 | 163240402 | JUMPER | 1W OF CGC 320343554108 | 20190725 | 954 | 471056 | 481 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 481 | 37.9859 | -120.382 | CGC 320343554108 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0081040 | OH | Sus | 0 | No | 2019 | JUL | Yes | Force Out | 1458643 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER | 3186 | 20190801 | 2302 | 477534 | 634 | Distribution Circuit | 3rd Party | Vehicle | 1257 | 316121 | 37.8621 | -120.2265 | MTR #1004239590 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0083631 | OH | Sus | 0 | No | 2019 | AUG | Yes | Line to Line | 1460260 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 5324 | 20190806 | 748 | 485513 | 413 | Distribution Circuit | 3rd Party | Vehicle | 1053 | 74454 | 37.1952 | -119.5872 | 51469 ROAD 200- NORTH FORK | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0084621 | OH | Sus | 0 | No | 2019 | AUG | Yes | Line to Ground | 1460992 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1704 | 163351704 | FUSE | 20809 | 20190807 | 43 | 487604 | 307 | Distribution Circuit | Vegetation | Tree - fell into line | 52 | 15964 | 38.0332 | -120.3676 | MTR# 1004899970 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0085048 | OH | Sus | 43910494 | No | 2019 | AUG | Yes | Line to Ground | 1461219 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | FUSE | 24006 | 20190829 | 1121 | 546808 | 498 | Distribution Circuit | 3rd Party | Vehicle | 5 | 2490 | 37.5032 | -120.0458 | EOL TX | Clear-32-90 F | Anchor or Guy | Broken, wire on ground | 19-0093607 | OH | Sus | 0 | No | 2019 | AUG | Yes | Line to Line | 1466659 | ANC | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | RECLOSER | 37288 | 20190916 | 1435 | 585340 | 359 | Distribution Circuit | Vegetation | Tree - fell into line | 698 | 121254 | 37.4205 | -119.8772 | 3RD SPAN NORTH OF FUCO 7429 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0099772 | OH | Sus | 31471919 | yes | 2019 | SEP | Yes | Line to Ground | 1470445 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2101 | 254452101 | OTHER | WIRE DOWN 1 W/OF MTR# 1007099599 | 20190922 | 1152 | 603613 | 644 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2287 | 133232 | 37.5168 | -119.9162 | 1 W/OF MTR# 1007099599 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0102232 | OH | Sus | 0 | No | 2019 | SEP | Yes | Line to Ground | 1471900 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1103 | 252531103 | FUSE | 10524 | 20190926 | 1227 | 618220 | 328 | Distribution Circuit | 3rd Party | Vehicle | 20 | 6560 | 37.2323 | -119.4693 | 2 S & 1 W/OF 105242 S & 1 W/OF 10524 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0104172 | OH | Sus | 0 | yes | 2019 | SEP | Yes | Line to Line | 1473259 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | S1767 | 20191001 | 934 | 633866 | 569 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 7 | 3983 | 38.016 | -120.225 | MTR# 1004733921 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0105922 | OH | Sus | 0 | No | 2019 | OCT | Yes | Line to Line | 1474419 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2269 | 20191014 | 1132 | 657193 | 648 | Distribution Circuit | 3rd Party | Vehicle | 85 | 10560 | 38.0392 | -120.2091 | 1 W/OF MTR# 1010108793 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0111263 | OH | Sus | 0 | No | 2019 | OCT | Yes | Line to Ground | 1479936 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE | 97905 | 20191015 | 35 | 658753 | 247 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3 | 741 | 37.3223 | -119.6173 | 2 N/OF 97905 | Clear-32-90 F | Insulator | Broken, wire on ground | 19-0111571 | OH | Sus | 43999647 | No | 2019 | OCT | Yes | Force Out | 1480022 | INS | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | OCB | 1703/2 | 20191104 | 109 | 698909 | 743 | Distribution Circuit | 3rd Party | Vehicle | 3603 | 465345 | 37.9799 | -120.4136 | L399 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 19-0120594 | OH | Sus | 0 | No | 2019 | NOV | Yes | Three Phase Fault | 1489010 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER | 76030 | 20191111 | 943 | 704321 | 823 | Distribution Circuit | 3rd Party | Vehicle | 191 | 38170 | 37.8992 | -120.4551 | 2 SPANS LD SIDE OF S1057 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 19-0123520 | OH | Sus | 0 | No | 2019 | NOV | Yes | Line to Line | 1490478 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2102 | 254432102 | RECLOSER | 10330 | 20191128 | 710 | 722633 | 478 | Distribution Circuit | Vegetation | Tree - fell into line | 1273 | 211524 | 37.2516 | -119.562 | 35972 TEAFORD POYAH | Overcast-Snow-32-90 F | Pole-Wood | Broken, wire on ground | 19-0130769 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Three Phase Fault | 1495452 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 601 | 20191129 | 748 | 723366 | 284 | Distribution Circuit | Equipment Failure/Involved | Overhead | 27 | 7668 | 37.9771 | -120.2718 | 19310 BLACK OAK | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 19-0131036 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Line | 1495737 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | JUMPER | OJ NW OF 321820030723 | 20191129 | 1140 | 723581 | 245 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 490 | 37.3483 | -119.8761 | 321820030723 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0131068 | OH | Sus | 0 | yes | 2019 | NOV | Yes | Line to Ground | 1495767 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | FUSE | 74256 | 20191205 | 1505 | 730810 | 102 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 102 | 37.2909 | -119.5303 | DAHLEM- JUSTIN // 1847: BASS LAKE | Partly Cloudy-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 19-0134001 | OH | Sus | 0 | No | 2019 | DEC | Yes | Line to Ground | 1498016 | CSO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | RECLOSER | 4160 | 20191207 | 2225 | 733463 | 703 | Distribution Circuit | Vegetation | Tree - branch fell on line | 794 | 113872 | 37.4958 | -120.0437 | Martin- Blair 559-474-5296: 3151 HIGHWAY 140 CATHYS VALLEY | Overcast-Fog-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 19-0134964 | OH | Sus | 44115323 | yes | 2019 | DEC | Yes | Multi-Fault | 1498753 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 673480 | 20200317 | 3 | 856091 | 1032 | Distribution Circuit | Environmental/External | Ice or snow | 499 | 178373 | 37.2881 | -119.5197 | BET 5TH & 6TH POLE LD SIDE OF 673480 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0033110 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Ground | 1522256 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | FUSE | 2267 | 20200319 | 1706 | 859170 | 170 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 1360 | 38.0857 | -120.1565 | 5 POLES LD SIDE 2267 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0034376 | OH | Sus | 0 | yes | 2020 | MAR | Yes | Line to Ground | 1523062 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER | 86032 | 20200406 | 247 | 885954 | 996 | Distribution Circuit | Vegetation | Tree - fell into line | 19 | 18888 | 38.1849 | -119.9915 | MTR# 1005419520 | Overcast-Fog-Snow-Below 32 F | Conductor, Overhead | Broken, wire on ground | 20-0039003 | OH | Sus | 0 | yes | 2020 | APR | Yes | Force Out | 1525727 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | OTHER | WIRE DOWN SOURCE SIDE 21017 | 20200407 | 2055 | 890343 | 1134 | Distribution Circuit | Vegetation | Tree - fell into line | 45 | 50795 | 37.8011 | -119.8806 | WIRE DOWN SOURCE SIDE 21017- WIRE ON CROSSARM 4 SPANS SOURCE SIDE OF 714303 | Partly Cloudy-Drizzle-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0039456 | OH | Sus | 0 | No | 2020 | APR | Yes | Line to Ground | 1525982 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | FUSE 10623 | 20200417 | 2128 | 897284 | 350 | Distribution Circuit | Environmental/External | Lightning | 72 | 18128 | 37.2251 | -119.716 | 2 POLES LD SIDE OF MTR # 1005670488 | Overcast-Drizzle-32-90 F | Insulator | Broken, wire on ground | 20-0042489 | OH | Sus | 0 | No | 2020 | APR | Yes | Line to Ground | 1527830 | INS | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 19515 | 20200421 | 1142 | 898787 | 433 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 43 | 7257 | 37.9969 | -120.2396 | MTR# 1010355192 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0043246 | OH | Sus | 31500881 | No | 2020 | APR | Yes | Line to Ground | 1528304 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 4562 | 20200421 | 915 | 898638 | 490 | Distribution Circuit | Animal | Other | 73 | 4450 | 37.4517 | -119.8524 | CGC #321846934885 (EOL SINGLE ?) | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0043178 | OH | Sus | 0 | No | 2020 | APR | Yes | Line to Line | 1528274 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | RECLOSER | 11270 | 20200517 | 1146 | 915182 | 351 | Distribution Circuit | Equipment Failure/Involved | Overhead | 369 | 90769 | 38.022 | -120.4318 | BREAUX- PARIS // 4062: 3 N/OF LR 11270 | Partly Cloudy-32-90 F | Crossarm, Wood | Broken, wire on ground | 20-0050990 | OH | Sus | 31503288 | yes | 2020 | MAY | Yes | Line to Ground | 1532928 | CAW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | RECLOSER | 4160 | 20200518 | 1544 | 917008 | 228 | Distribution Circuit | Equipment Failure/Involved | Overhead | 797 | 151997 | 37.4958 | -120.0437 | 2 SPANS W/OF CGC # 321301335635 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0051495 | OH | Sus | 44326528 | yes | 2020 | MAY | Yes | Line to Line | 1533192 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 23223 | 20200627 | 2338 | 949159 | 767 | Distribution Circuit | Vegetation | Tree - fell into line | 79 | 13899 | 37.9786 | -120.3151 | 20261 BARBARA RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0065766 | OH | Sus | 31507184 | No | 2020 | JUN | Yes | Line to Line | 1542986 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | FUSE | 63417 | 20200711 | 2003 | 962555 | 476 | Distribution Circuit | Vegetation | Tree - fell into line | 7 | 2024 | 37.1945 | -119.5016 | CGC #322930025358 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0070883 | OH | Sus | 31508460 | yes | 2020 | JUL | Yes | Force Out | 1545946 | CO | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1101 | 254421101 | OCB | 1101/2 | 20200729 | 847 | 974232 | 140 | Distribution Circuit | Company Initiated | Construction Activity/equip- company | 3025 | 329234 | 37.3218 | -119.6343 | FB at 10249 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0071879 | OH | Sus | 35117329 | No | 2020 | JUL | Yes | Line to Ground | 1550128 | CSO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | FUSE | 2421 | 20200818 | 748 | 1018339 | 627 | Distribution Circuit | Vegetation | Tree - fell into line | 28 | 6506 | 37.3642 | -119.6262 | 50600 ROAD 220 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 20-0086575 | OH | Sus | 0 | yes | 2020 | AUG | Yes | Line to Line | 1556617 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 10374 | 20201108 | 1327 | 1139518 | 430 | Distribution Circuit | Vegetation | Tree - fell into line | 40 | 6700 | 37.46 | -119.9017 | 3 P E/OF MTR # 1006908337 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 20-0118516 | OH | Sus | 0 | No | 2020 | NOV | Yes | Three Phase Fault | 1578139 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1705 | 163781705 | FUSE | 2677 | 20201117 | 1006 | 1147108 | 288 | Distribution Circuit | Equipment Failure/Involved | Overhead | 58 | 8876 | 37.9271 | -120.4202 | MTR# 1004904132 R/O 16827 DUTCH MINE RD | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 20-0121825 | OH | Sus | 44543276 | No | 2020 | NOV | Yes | Line to Line | 1580593 | CSO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 22189 | 20201208 | 1410 | 1172607 | 369 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 11 | 4059 | 37.981 | -120.3064 | MTR 1004858631 | Clear-32-90 F | Conductor, Overhead | Broken, wire on object | 20-0128990 | OH | Sus | 31520053 | No | 2020 | DEC | Yes | Line to Line | 1585514 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | OTHER | WIRE DOWN 1S/SS/1753 | 20201226 | 914 | 1199057 | 486 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1887 | 383213 | 38.0064 | -120.3015 | WIRE DOWN JUST SS OF 1753 SBCO | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 20-0131868 | OH | Sus | 0 | No | 2020 | DEC | Yes | Line to Ground | 1589584 | CSO | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | CURTIS-1705 | 163351705 | JUMPER | OJ 1 SS OF MTR# 1004737686 | 20210122 | 737 | 1220558 | 615 | Distribution Circuit | Vegetation | Tree - fell into line | 23 | 14145 | 38.0336 | -120.2287 | MTR# 1004737686 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0012463 | OH | Sus | 0 | No | 2021 | JAN | Yes | Force Out | 1595684 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 69311 | 20210123 | 1103 | 1221768 | 462 | Distribution Circuit | Vegetation | Tree - fell into line | 3 | 1386 | 37.4859 | -119.8612 | 5360 DORA RD | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0013255 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1596216 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | JUMPER | OJ 1 W/OF CGC# 322346032763 | 20210123 | 1346 | 1221887 | 141 | Distribution Circuit | Equipment Failure/Involved | Overhead | 1 | 141 | 37.3971 | -119.6951 | 3 SPANS SOURCE SIDE OF CGC #322340832682 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0013297 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1596247 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | BEAR VALLEY-2105 | 252192105 | SWITCH | 23336 | 20210129 | 636 | 1241594 | 446 | Distribution Circuit | Equipment Failure/Involved | Overhead | 71 | 29090 | 37.7504 | -120.1216 | CGC #321116845635 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0018158 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Ground | 1600272 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | FUSE | 22613 | 20210129 | 1450 | 1242130 | 334 | Distribution Circuit | Vegetation | Tree - fell into line | 60 | 20040 | 38.0463 | -120.2244 | 6 POLES LD SIDE 22613 & 8 LD SIDE OF 22613 | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0018521 | OH | Sus | 0 | No | 2021 | JAN | Yes | Force Out | 1600421 | PW | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | OTHER | 825573 | 20210129 | 837 | 1241219 | 641 | Distribution Circuit | Vegetation | Tree - fell into line | 5 | 3205 | 38.0466 | -120.2191 | at 825573 | Clear-32-90F | Conductor, Overhead | On Ground | 21-0018573 | OH | Sus | 0 | No | 2021 | JAN | Yes | Open Circuit | 1600459 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | OAKHURST-1103 | 254421103 | RECLOSER | 10190 | 20210129 | 756 | 1241138 | 570 | Distribution Circuit | Vegetation | Tree - fell into line | 8 | 4560 | 37.4145 | -119.6272 | 4 & 5 SPANS SS OF 5459 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 21-0018170 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1600178 | CAW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN #3 PH-1101 | 252531101 | RECLOSER | 673480 | 20210129 | 935 | 1241912 | 376 | Distribution Circuit | Vegetation | Tree - fell into line | 580 | 200302 | 37.3241 | -119.5481 | WIRE WRAPPED AT MTR# 1006375781- 1 SPAN OF WIRE DOWN 2 E/OF 5663 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0018228 | OH | Sus | 0 | No | 2021 | JAN | Yes | Line to Line | 1600357 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1702 | 163661702 | SWITCH | 531976 | 20210210 | 1907 | 1252660 | 111 | Distribution Circuit | Equipment Failure/Involved | Overhead | 45 | 4995 | 38.0524 | -120.2316 | TUCK- MATT // 2074: two poles load side of lr 531976 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0024261 | OH | Sus | 44650637 | No | 2021 | FEB | Yes | Force Out | 1604389 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MARIPOSA-2102 | 254452102 | FUSE | 4556 | 20210212 | 354 | 1253491 | 364 | Distribution Circuit | Vegetation | Tree - fell into line | 85 | 30940 | 37.4395 | -119.9413 | MARTIN- BLAIR // 559-474-5296: 4118 SULLIVAN RD | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 21-0024834 | OH | Sus | 44651290 | No | 2021 | FEB | Yes | Line to Ground | 1604707 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 22185 | 20210225 | 902 | 1262075 | 303 | Distribution Circuit | Equipment Failure/Involved | Overhead | 4 | 1212 | 37.9697 | -120.2544 | 1 POLE LD SIDE OF 2215 | Clear-32-90 F | Crossarm, Wood | Broken, wire on object | 21-0029436 | OH | Sus | 31531472 | No | 2021 | FEB | Yes | Force Out | 1607800 | CAW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | RECLOSER | 37288 | 20210310 | 419 | 1276711 | 496 | Distribution Circuit | Vegetation | Tree - branch fell on line | 705 | 253650 | 37.421 | -119.8768 | CGC #321883633178 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0034304 | OH | Sus | 0 | No | 2021 | MAR | Yes | Line to Ground | 1610839 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1705 | 163781705 | FUSE | 53159 | 20210328 | 514 | 1301829 | 349 | Distribution Circuit | 3rd Party | Fire- house or bldg. | 1 | 349 | 37.9643 | -120.4048 | 1 SPAN LOAD SIDE OF 53159 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0041874 | OH | Sus | 31534520 | No | 2021 | MAR | Yes | Line to Ground | 1615606 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 10588 | 20210424 | 2342 | 1333280 | 842 | Distribution Circuit | 3rd Party | Vehicle | 78 | 52465 | 37.2461 | -119.8825 | 2 POLES LD SIDE OF 10798 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0052831 | OH | Sus | 0 | No | 2021 | APR | Yes | Line to Ground | 1622888 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 2497 | 20210425 | 1143 | 1333513 | 607 | Distribution Circuit | Vegetation | Tree - fell into line | 20 | 2510 | 38.0111 | -120.291 | SIUDZINSKI- MARK // 1806: 16304 HIDDEN VALLEY RD | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0052884 | OH | Sus | 0 | No | 2021 | APR | Yes | Line to Line | 1622937 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1704 | 163781704 | RECLOSER | 88630 | 20210706 | 1300 | 1392965 | 582 | Distribution Circuit | 3rd Party | Vehicle | 5 | 2910 | 37.9012 | -120.5175 | CASTILLO- STEVE // 1974: 6000 OYBRENES FERRY RD | Clear-32-90F | Pole-Wood | Broken, wire on ground | 21-0085296 | OH | Sus | 0 | No | 2021 | JUL | Yes | Three Phase Fault | 1645695 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | S1617 | 20210731 | 1532 | 1427100 | 320 | Distribution Circuit | 3rd Party | Vehicle | 62 | 19840 | 37.9857 | -120.2645 | 1 LD SIDE OF S1617 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 21-0098088 | OH | Sus | 0 | No | 2021 | JUL | Yes | Line to Ground | 1653625 | PW | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | RECLOSER | 65908 | 20210916 | 907 | 1473025 | 192 | Distribution Circuit | 3rd Party | Tree - cutting- 3rd party | 682 | 77303 | 37.9574 | -120.3132 | 1 SP LD SIDE OF 27300 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 21-0118278 | OH | Sus | 31551906 | No | 2021 | SEP | Yes | Line to Line | 1666225 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | RECLOSER | 1103/2 | 20211008 | 626 | 1489916 | 386 | Distribution Circuit | Equipment Failure/Involved | Overhead | 899 | 347014 | 37.2537 | -119.5192 | ELAM- JON // 1916: SW 5443 | Clear-32-90 F | Connector or Splice (OH) | Broken, wire on ground | 21-0127479 | OH | Sus | 0 | No | 2021 | OCT | Yes | Line to Ground | 1671833 | CSO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER | 11800 | 20211107 | 513 | 1536661 | 521 | Distribution Circuit | Vegetation | Tree - fell into line | 684 | 143860 | 38.0243 | -120.2213 | TUCK- MATT // 2074: 22500 | Clear-32-90 F | Crossarm, Wood | Broken, wire on ground | 21-0143097 | OH | Sus | 35300216 | No | 2021 | NOV | Yes | Three Phase Fault | 1682363 | CAW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2101 | 252192101 | RECLOSER | 4160 | 20211216 | 1625 | 1575080 | 338 | Distribution Circuit | Equipment Failure/Involved | Overhead | 804 | 251497 | 37.4963 | -120.0432 | CGC #321273835729 | Clear-32-90F | Connector or Splice (OH) | Broken, wire on ground | 21-0158961 | OH | Sus | 45094600 | No | 2021 | DEC | Yes | Multi-Fault | 1696005 | CSO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN #3 PH-1102 | 252531102 | RECLOSER | 1102/2 | 20211223 | 1257 | 1579997 | 398 | Distribution Circuit | Vegetation | Tree - fell into line | 262 | 99056 | 37.2537 | -119.5192 | 2 SPANS WEST O 2212 | Clear-32-90F | Crossarm, Wood | Broken, wire on object | 21-0160296 | OH | Sus | 31588336 | No | 2021 | DEC | Yes | Line to Line | 1697736 | CAW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | RECLOSER | 10940 | 20220106 | 14 | 1596289 | 458 | Distribution Circuit | Vegetation | Tree - fell into line | 1155 | 57096 | 37.9883 | -120.2832 | 17180 ALDERMAN | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0006649 | OH | Sus | 31588904 | No | 2022 | JAN | Yes | Line to Ground | 1701240 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | FUSE | 4911 | 20220108 | 958 | 1598155 | 620 | Distribution Circuit | 3rd Party | Vehicle | 129 | 39466 | 37.9802 | -120.248 | S2041 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0007617 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Ground | 1701612 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | SAN JOAQUIN #3 PH-1103 | 252531103 | FUSE | 6094 | 20220121 | 1609 | 1607644 | 228 | Distribution Circuit | Vegetation | Tree - fell into line | 15 | 3420 | 37.2424 | -119.52 | CGC# 322866727162 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0012748 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Line | 1704073 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE | L1123 | 20220121 | 1125 | 1607291 | 518 | Distribution Circuit | Vegetation | Tree - fell into line | 154 | 62753 | 38.1975 | -120.0126 | 1 SPAN S/OF MTR #1004717959 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0012472 | OH | Sus | 0 | No | 2022 | JAN | Yes | Line to Line | 1703981 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | RACETRACK-1703 | 163761703 | FUSE | 5957 | 20220307 | 1752 | 1644317 | 545 | Distribution Circuit | Vegetation | Tree - branch fell on line | 14 | 7630 | 38.0329 | -120.4002 | 2P S/OF 5957 | Strong Winds-Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0030934 | OH | Sus | 45200355 | No | 2022 | MAR | Yes | Line to Line | 1715324 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | FUSE | 4629 | 20220506 | 1023 | 1690002 | 582 | Distribution Circuit | Vegetation | Tree - fell into line | 144 | 26179 | 37.7103 | -120.111 | CGC #321179944405 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0059025 | OH | Sus | 0 | No | 2022 | MAY | Yes | Line to Line | 1734238 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | OTHER | 37282 | 20220617 | 244 | 1733585 | 372 | Distribution Circuit | Equipment Failure/Involved | Overhead | 2122 | 396343 | 37.462 | -119.9483 | LD SIDE OF 8686 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0075391 | OH | Sus | 45345168 | No | 2022 | JUN | Yes | Open Circuit | 1745379 | CO | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | STANISLAUS-1701 | 162821701 | OCB | 1701/2 | 20220723 | 2147 | 1764226 | 1005 | Distribution Circuit | 3rd Party | Vehicle | 2188 | 1548232 | 38.1401 | -120.3697 | 1 P/W/OF AND 1 P/S/OF L431 - HWY 4 X- PARROTS FERRY | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 22-0089059 | OH | Sus | 0 | No | 2022 | JUL | Yes | Line to Line | 1754608 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER | 9690 | 20221107 | 1610 | 1856353 | 469 | Distribution Circuit | Equipment Failure/Involved | Overhead | 689 | 323141 | 38.1888 | -120.0082 | 31 SPANS S/OF 9690 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0128695 | OH | Sus | 45513981 | No | 2022 | NOV | Yes | Line to Ground | 1781971 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER | 9690 | 20221108 | 739 | 1856839 | 509 | Distribution Circuit | Vegetation | Tree - fell into line | 689 | 347794 | 38.1888 | -120.0082 | 1 SPAN LOAD SIDE OF 79597 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 22-0128833 | OH | Sus | 0 | No | 2022 | NOV | Yes | Line to Ground | 1782075 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | COARSEGOLD-2102 | 254432102 | FUSE | 10142 | 20221203 | 435 | 1874858 | 437 | Distribution Circuit | Vegetation | Tree - fell into line | 57 | 24909 | 37.2725 | -119.5761 | CGC#322679928348 | Clear-32-90F | Crossarm, Wood | Broken, wire on ground | 22-0136254 | OH | Sus | 31629359 | No | 2022 | DEC | Yes | Line to Ground | 1787189 | CAW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | RECLOSER | 9690 | 20221212 | 1748 | 1887518 | 482 | Distribution Circuit | Environmental/External | Ice or snow | 689 | 169154 | 38.1888 | -120.0082 | CGC #321282360288 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 22-0139354 | OH | Sus | 0 | No | 2022 | DEC | Yes | Line to Ground | 1790175 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 10788 | 20230115 | 2306 | 1956437 | 851 | Distribution Circuit | Vegetation | Tree - fell into line | 77 | 65527 | 37.2869 | -119.6558 | CGC 322477828555 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0016857 | OH | Sus | 0 | No | 2023 | JAN | Yes | Line to Line | 1805555 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | OTHER | 2 PH WIRE DOWN 1 SPAN SS 83402 | 20230115 | 533 | 1955556 | 502 | Distribution Circuit | Vegetation | Tree - fell into line | 38 | 15806 | 38.139 | -120.0621 | 1 SPAN SS 83402 | Clear-32-90F | Conductor, Overhead | Broken, wire on ground | 23-0016545 | OH | Sus | 0 | No | 2023 | JAN | Yes | Open Circuit | 1805297 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SPRING GAP-1702 | 162831702 | FUSE | L1707 | 20230117 | 851 | 1959847 | 798 | Distribution Circuit | Equipment Failure/Involved | Overhead | 28 | 22344 | 38.1872 | -120.0021 | CGC #321431461423 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0017791 | OH | Sus | 0 | No | 2023 | JAN | Yes | Three Phase Fault | 1806252 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 23243 | 20230301 | 653 | 2017666 | 3667 | Distribution Circuit | Equipment Failure/Involved | Overhead | 128 | 140606 | 37.9853 | -120.282 | L895 | Partly Cloudy-Below 32 F | Pole-Wood | Broken, wire on ground | 23-0038481 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1820670 | PW | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2101 | 254452101 | FUSE | 11906 | 20230305 | 106 | 2023087 | 676 | Distribution Circuit | Vegetation | Tree - fell into line | 26 | 4472 | 37.5114 | -119.9943 | WIRE DOWN N/OF CGC 321464837090 | Overcast-Fog-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0040181 | OH | Sus | 0 | No | 2023 | MAR | Yes | Force Out | 1821929 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | FUSE | 1949 | 20230311 | 1744 | 2032772 | 1470 | Distribution Circuit | Environmental/External | Lightning | 155 | 227746 | 37.8529 | -120.1659 | 320945849806-320945549839-320948049814-320951549839-320949549747-320947549781 1 SRC SIDE OF CGC 320 | Overcast-Rain-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0043624 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1824164 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1703 | 163351703 | RECLOSER | 90320 | 20230313 | 308 | 2033882 | 673 | Distribution Circuit | Equipment Failure/Involved | Overhead | 3074 | 237044 | 37.8473 | -120.2023 | 1 SS OF CGC# 321045049147 | Overcast-Fog-Drizzle-32-90 F | Crossarm, Wood | Broken, wire on object | 23-0043929 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1824443 | CAW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2103 | 254432103 | FUSE | 5519 | 20230326 | 839 | 2067531 | 18 | Distribution Circuit | Company Initiated | Return Circuit Normal | 120 | 2160 | 37.1415 | -119.6791 | 31511 RIDGEWOOD WAY- NORTH FORK | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0037696 | OH | Sus | 0 | No | 2023 | MAR | Yes | None | 1830580 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1702 | 163351702 | FUSE | 48691 | 20230328 | 1418 | 2070801 | 505 | Distribution Circuit | Vegetation | Tree - fell into line | 74 | 37370 | 37.991 | -120.2788 | 3 SP LOAD SIDE 48691 | Overcast-Rain-Strong Winds-32-90 F | Pole-Wood | Broken, wire on ground | 23-0053777 | OH | Sus | 0 | No | 2023 | MAR | Yes | Three Phase Fault | 1831298 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | BEAR VALLEY-2105 | 252192105 | JUMPER | WIRE DOWN 1 SPAN W/O MTR 1010269803 | 20230330 | 1601 | 2074649 | 209 | Distribution Circuit | Vegetation | Tree - fell into line | 2 | 418 | 37.7344 | -120.07 | 1 SPAN W/O MTR 1010269803 | Overcast-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0055219 | OH | Sus | 0 | No | 2023 | MAR | Yes | Open Circuit | 1832020 | CO | OH | No | Yes
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | MIWUK-1701 | 163661701 | RECLOSER | 953336 | 20230330 | 1029 | 2074257 | 517 | Distribution Circuit | Vegetation | Tree - fell into line | 922 | 190072 | 38.0678 | -120.1869 | 1 SPAN W/OF CGC#321007957419 | Partly Cloudy-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0054912 | OH | Sus | 0 | No | 2023 | MAR | Yes | Line to Ground | 1831930 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2102 | 254452102 | FUSE | 4969 | 20230404 | 1342 | 2080039 | 268 | Distribution Circuit | Vegetation | Tree - bark fell into line | 62 | 16616 | 37.4335 | -119.8958 | S/OF CGC# 321731033285 | Clear-32-90 F | Conductor, Overhead | Broken, wire on ground | 23-0057169 | OH | Sus | 45715581 | No | 2023 | APR | Yes | Line to Ground | 1833279 | CO | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | CURTIS-1705 | 163351705 | RECLOSER | 39256 | 20230630 | 1451 | 2150015 | 643 | Distribution Circuit | 3rd Party | Vehicle | 523 | 147451 | 37.9571 | -120.3087 | CGC# 320632653326 | Clear-Above 90 | Pole-Wood | Broken, wire on ground | 23-0087698 | OH | Sus | 31653955 | No | 2023 | JUN | Yes | Line to Ground | 1854412 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | PEORIA FLAT-1701 | 163781701 | RECLOSER | 90090 | 20230802 | 1302 | 2180708 | 464 | Distribution Circuit | 3rd Party | Vehicle | 2704 | 382862 | 37.9028 | -120.4538 | CGC# 100000038760 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0099632 | OH | Sus | 31658031 | No | 2023 | AUG | Yes | Line to Line | 1862502 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | COARSEGOLD-2104 | 254432104 | FUSE | 5679 | 20230914 | 2346 | 2219240 | 585 | Distribution Circuit | 3rd Party | Vehicle | 125 | 37635 | 37.2396 | -119.7772 | 1 POLE SOUTH EAST OF CGC 32253526918. | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0116930 | OH | Sus | 0 | No | 2023 | SEP | Yes | Line to Line | 1874154 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 3 | SAN JOAQUIN POWER HOUSE NO 2 | 252521103 | OCB | 1103/2 | 20231124 | 2126 | 2276747 | 801 | Distribution Circuit | 3rd Party | Vehicle | 871 | 208611 | 37.2036 | -119.4971 | CGC #322710725881 | Clear-32-90 F | Pole-Wood | Broken, wire on ground | 23-0142725 | OH | Sus | 0 | No | 2023 | NOV | Yes | Line to Line | 1892632 | PW | OH | No | No
YOSEMITE | FIELD OPS CENTRAL | Tier 2 | MARIPOSA-2101 | 254452101 | RECLOSER | 4190 | 20231215 | 1254 | 2292622 | 426 | Distribution Circuit | 3rd Party | Vehicle | 2832 | 347077 | 37.5051 | -120.038 | CGC# 321076633025 | Partly Cloudy-32-90 F | Pole-Wood | Broken, wire on ground | 23-0147584 | OH | Sus | 35517751 | No | 2023 | DEC | Yes | Line to Ground | 1898182 | PW | OH | No | No

## Metric 3.02
Metric 3.02: Wires Down non-MEDs (Distribution)
Definition | (# Events/HFTD Circuit Miles (D))*1000
2022 HFTD Circuit Miles (D) | 25270.5
2023 HFTD Circuit Miles (D) | 25059.94
2023 Target | 41.4025
Year | WD Events | WD Events/1,000 Miles
2013 | 651 | 25.7613
2014 | 869 | 34.3879
2015 | 794 | 31.42
2016 | 1211 | 47.9215
2017 | 1074 | 42.5001
2018 | 877 | 34.7045
2019 | 945 | 37.3954
2020 | 460 | 18.203
2021 | 475 | 18.7966
2022 | 466 | 18.4405
2023 | 478 | 19.0743
|  | 10.4494 | STD
|  | 30.9531 | Average
|  | 41.4025 | 1 STD

## HFTD WD non-MED Summary
HFTD WIRE-DOWN OUTAGE DETAILS (2013 - 2023)
DISTRIBUTION CIRCUIT & TRANSFORMER-ONLY OUTAGES
(Excluding 2.5b ME Days)
System | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
SYSTEM | 2013 | 39 | 57 | 54 | 72 | 59 | 67 | 45 | 40 | 57 | 53 | 28 | 80 | 651
SYSTEM | 2014 | 28 | 120 | 93 | 58 | 57 | 47 | 56 | 43 | 45 | 76 | 52 | 194 | 869
SYSTEM | 2015 | 38 | 112 | 48 | 50 | 33 | 65 | 47 | 56 | 55 | 41 | 57 | 192 | 794
SYSTEM | 2016 | 204 | 56 | 242 | 87 | 60 | 61 | 65 | 41 | 54 | 140 | 83 | 118 | 1211
SYSTEM | 2017 | 141 | 184 | 133 | 95 | 76 | 67 | 68 | 71 | 61 | 57 | 82 | 39 | 1074
SYSTEM | 2018 | 82 | 44 | 169 | 65 | 55 | 56 | 95 | 47 | 30 | 58 | 67 | 109 | 877
SYSTEM | 2019 | 138 | 129 | 141 | 65 | 115 | 63 | 59 | 52 | 67 | 25 | 42 | 49 | 945
SYSTEM | 2020 | 44 | 40 | 39 | 52 | 58 | 42 | 21 | 41 | 29 | 22 | 36 | 36 | 460
SYSTEM | 2021 | 53 | 33 | 59 | 31 | 24 | 38 | 36 | 25 | 31 | 41 | 45 | 59 | 475
SYSTEM | 2022 | 49 | 25 | 32 | 58 | 34 | 37 | 26 | 18 | 23 | 22 | 46 | 96 | 466
SYSTEM | 2023 | 81 | 33 | 138 | 32 | 24 | 21 | 27 | 32 | 19 | 14 | 18 | 39 | 478
System | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
10-Year Averages (2013-2022) | Count of Events | 81.6 | 80 | 101 | 63.3 | 57.1 | 54.3 | 51.8 | 43.4 | 45.2 | 53.5 | 53.8 | 97.2 | 782.2
| Monthly Percentage | 10.43% | 10.23% | 12.91% | 8.093% | 7.3% | 6.942% | 6.622% | 5.548% | 5.779% | 6.84% | 6.878% | 12.43% | 100%
System | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Targets | 2023 | 4.3192 | 4.2345 | 5.346 | 3.3505 | 3.0224 | 2.8741 | 2.7418 | 2.2972 | 2.3925 | 2.8318 | 2.8477 | 5.1449 | 41.4025
System | Year | Jan | Feb | Mar | Apr | May | Jun | Jul | Aug | Sep | Oct | Nov | Dec | Total
Events | 2023 | 81 | 33 | 138 | 32 | 24 | 21 | 27 | 32 | 19 | 14 | 18 | 39 | 478
Monthly Metric | 2023 | 3.2323 | 1.3168 | 5.5068 | 1.2769 | 0.9577 | 0.83799 | 1.0774 | 1.2769 | 0.75818 | 0.55866 | 0.71828 | 1.5563 | 19.0743
YTD Metric | 2023 | 3.2323 | 4.5491 | 10.0559 | 11.3328 | 12.2905 | 13.1285 | 14.2059 | 15.4829 | 16.2411 | 16.7997 | 17.518 | 19.0743

## OH Dlines in HFTD
Source: Extracted from EDGIS as of 1/1/2023.
CIRCUITNAME | CIRCUITID | TOTALMILES | T3MILES | T2MILES | Z1MILES | T1MILES
2101 | 259932101 | 12.23 |  | 3.79 | 0.49 | 7.95
18TH STREET 0401 | 22390401 | 1.27 |  |  |  | 1.27
18TH STREET 0402 | 22390402 | 1.82 |  |  |  | 1.82
21ST AVENUE 0401 | 22550401 | 1.89 |  |  |  | 1.89
21ST AVENUE 0402 | 22550402 | 3.27 |  |  |  | 3.27
21ST AVENUE 0403 | 22550403 | 1.84 |  |  |  | 1.84
6TH AVENUE 0401 | 22530401 | 1.27 |  |  |  | 1.27
6TH AVENUE 0402 | 22530402 | 1.22 |  |  |  | 1.22
6TH AVENUE 0403 | 22530403 | 1.78 |  |  |  | 1.78
7TH STANDARD 2101 | 254582101 | 2.56 |  |  |  | 2.56
7TH STANDARD 2102 | 254582102 | 13.3 |  |  |  | 13.3
7TH STANDARD 2103 | 254582103 | 22.46 |  |  |  | 22.46
7TH STANDARD 2104 | 254582104 | 0.04 |  |  |  | 0.04
8TH AVENUE 0401 | 12670401 | 4.89 |  |  |  | 4.89
ACTON 0401 | 22470401 | 3.87 |  |  |  | 3.87
ACTON 0402 | 22470402 | 4.44 |  |  |  | 4.44
AIRWAYS 1101 | 252041101 | 1.48 |  |  |  | 1.48
AIRWAYS 1102 | 252041102 | 7.65 |  |  |  | 7.65
AIRWAYS 1103 | 252041103 | 7.65 |  |  |  | 7.65
AIRWAYS 1104 | 252041104 | 2 |  |  |  | 2
AIRWAYS 1105 | 252041105 | 1.35 |  |  |  | 1.35
AIRWAYS 1106 | 252041106 | 8.18 |  |  |  | 8.18
AIRWAYS 1107 | 252041107 | 43.6 |  |  |  | 43.6
AIRWAYS 1108 | 252041108 | 11.64 |  |  |  | 11.64
ALHAMBRA 1101 | 14101101 | 8.4 |  |  |  | 8.4
ALHAMBRA 1102 | 14101102 | 14.11 |  | 0.13 |  | 13.98
ALHAMBRA 1105 | 14101105 | 45.1 | 0.85 | 36.9 |  | 7.35
ALLEGHANY 1101 | 152101101 | 77.01 | 32.35 | 27.11 | 7.07 | 10.48
ALLEGHANY 1102 | 152101102 | 17.69 | 17.69 |  |  | 0
ALMADEN 1101 | 82311101 | 18.33 |  |  |  | 18.33
ALMADEN 1102 | 82311102 | 21.83 |  |  |  | 21.83
ALMADEN 1110 | 82311110 | 8.45 |  |  |  | 8.45
ALMADEN 1111 | 82311111 | 9.78 |  |  |  | 9.78
ALPAUGH 1103 | 254001103 | 26.94 |  |  |  | 26.94
ALPAUGH 1104 | 254001104 | 55.72 |  |  |  | 55.72
ALPAUGH 1106 | 254001106 | 52.45 |  |  |  | 52.45
ALPINE 1101 | 163561101 | 0.87 |  |  |  | 0.87
ALTO 1120 | 42031120 | 20.38 |  | 3.9 |  | 16.48
ALTO 1121 | 42031121 | 16.46 |  |  | 0.34 | 16.12
ALTO 1122 | 42031122 | 22.26 | 9.14 | 3.65 | 0.18 | 9.29
ALTO 1123 | 42031123 | 10.32 |  | 0.47 |  | 9.85
ALTO 1124 | 42031124 | 35 | 27.96 |  |  | 7.04
ALTO 1125 | 42031125 | 44.79 | 26.36 | 10.96 |  | 7.47
AMES 1101 | 83901101 | 0.12 |  |  |  | 0.12
AMES 1102 | 83901102 | 3.29 |  |  |  | 3.29
ANDERSON 1101 | 103261101 | 19.91 |  | 11.03 |  | 8.88
ANDERSON 1102 | 103261102 | 3.75 |  |  |  | 3.75
ANDERSON 1103 | 103261103 | 31.66 |  | 7.13 |  | 24.53
ANGIOLA 1102 | 252151102 | 35.82 |  |  |  | 35.82
ANGIOLA 1103 | 252151103 | 46.05 |  |  |  | 46.05
ANGIOLA 1104 | 252151104 | 19.61 |  |  |  | 19.61
ANITA 1101 | 102841101 | 34.47 |  |  |  | 34.47
ANITA 1102 | 102841102 | 34.8 |  |  |  | 34.8
ANITA 1105 | 102841105 | 16.84 |  |  |  | 16.84
ANITA 1106 | 102841106 | 90.29 |  | 0.48 |  | 89.81
ANNAPOLIS 1101 | 42861101 | 51 |  | 51 |  | 0
ANTELOPE 1101 | 252021101 | 39.88 |  | 0.92 |  | 38.96
ANTELOPE 1102 | 252021102 | 25.34 |  |  |  | 25.34
ANTLER 1101 | 103271101 | 61.21 | 8.17 | 51.94 |  | 1.1
APPLE HILL 1103 | 153661103 | 59.82 | 14.77 | 35.12 |  | 9.93
APPLE HILL 1104 | 153661104 | 95.48 | 55.35 | 35.42 |  | 4.71
APPLE HILL 2102 | 153662102 | 364.72 | 123.52 | 228.47 |  | 12.73
ARANA 0401 | 83010401 | 3.49 |  |  |  | 3.49
ARANA 0402 | 83010402 | 2.98 |  |  |  | 2.98
ARBUCKLE 1101 | 62081101 | 42.78 |  |  |  | 42.78
ARBUCKLE 1102 | 62081102 | 62.84 |  |  |  | 62.84
ARBUCKLE 1103 | 62081103 | 0.04 |  |  |  | 0.04
ARBUCKLE 1104 | 62081104 | 94.76 |  | 1.92 |  | 92.84
ARCATA 1105 | 192021105 | 43.95 |  |  |  | 43.95
ARCATA 1106 | 192021106 | 10.16 |  |  |  | 10.16
ARCATA 1121 | 192021121 | 28.95 |  | 6.84 |  | 22.11
ARCATA 1122 | 192021122 | 68.05 |  | 20.44 |  | 47.61
ARCATA 1123 | 192021123 | 5.97 |  |  |  | 5.97
ARCATA 1124 | 192021124 | 0 |  |  |  | 0
ARLINGTON 0401 | 13700401 | 4.17 |  | 0.94 |  | 3.23
ARVIN 1101 | 253801101 | 30.09 |  | 0.1 |  | 29.99
ARVIN 1102 | 253801102 | 17.87 |  |  |  | 17.87
ARVIN 1103 | 253801103 | 20.6 |  |  |  | 20.6
ASHLAN AVE 1102 | 252051102 | 13.21 |  |  |  | 13.21
ASHLAN AVE 1103 | 252051103 | 9.29 |  |  |  | 9.29
ASHLAN AVE 1104 | 252051104 | 14.01 |  |  |  | 14.01
ASHLAN AVE 1106 | 252051106 | 16.98 |  |  |  | 16.98
ASHLAN AVE 1107 | 252051107 | 8.32 |  |  |  | 8.32
ASHLAN AVE 1108 | 252051108 | 11.18 |  |  |  | 11.18
ASHLAN AVE 1109 | 252051109 | 15.66 |  |  |  | 15.66
ASHLAN AVE 1111 | 252051111 | 6.76 |  |  |  | 6.76
ASHLAN AVE 1112 | 252051112 | 9.52 |  |  |  | 9.52
ASHLAN AVE 1113 | 252051113 | 9.82 |  |  |  | 9.82
ASHLAN AVE 1114 | 252051114 | 8.36 |  |  |  | 8.36
ASHLAN AVE 1116 | 252051116 | 19.06 |  |  |  | 19.06
ASHLAN AVE 2101 | 252052101 | 2.23 |  |  |  | 2.23
ASHLAN AVE 2105 | 252052105 | 16.39 |  |  |  | 16.39
ASHLAN AVE 2110 | 252052110 | 6.72 |  |  |  | 6.72
ASHLAN AVE 2115 | 252052115 | 5.51 |  |  |  | 5.51
ASHLAN AVE 2117 | 252052117 | 1.88 |  |  |  | 1.88
ASHLAN AVE 2118 | 252052118 | 9.56 |  |  |  | 9.56
ASHLAN AVE 2119 | 252052119 | 14.08 |  |  |  | 14.08
ATASCADERO 1101 | 182541101 | 62.26 | 13.74 | 32.02 |  | 16.5
ATASCADERO 1102 | 182541102 | 17.38 |  | 3.4 |  | 13.98
ATASCADERO 1103 | 182541103 | 127.77 | 37.11 | 55.99 |  | 34.67
ATWATER 1102 | 253611102 | 84.23 |  |  |  | 84.23
ATWATER 1103 | 253611103 | 23.19 |  |  |  | 23.19
ATWATER 1104 | 253611104 | 12.89 |  |  |  | 12.89
ATWATER 1105 | 253611105 | 6.8 |  |  |  | 6.8
ATWATER 1106 | 253611106 | 36.74 |  |  |  | 36.74
ATWATER 1107 | 253611107 | 30.58 |  |  |  | 30.58
ATWATER 1108 | 253611108 | 61.07 |  |  |  | 61.07
AUBERRY 1101 | 254151101 | 241.34 | 32.07 | 206.96 |  | 2.31
AUBERRY 1102 | 254151102 | 129.03 |  | 129.03 |  | 0
AUBURN 1101 | 152161101 | 4.92 |  | 3.14 |  | 1.78
AUBURN 1102 | 152161102 | 8.96 |  | 2.98 |  | 5.98
AVENA 1701 | 163571701 | 90.74 |  |  |  | 90.74
AVENA 1702 | 163571702 | 80.23 |  |  |  | 80.23
AVENAL 2101 | 255002101 | 63.31 |  |  |  | 63.31
AVENAL 2102 | 255002102 | 2.46 |  |  |  | 2.46
AVENAL 2103 | 255002103 | 2.45 |  |  |  | 2.45
BABEL 0401 | 13850401 | 3.08 |  |  |  | 3.08
BAHIA 1101 | 43251101 | 3.06 |  |  |  | 3.06
BAHIA 1102 | 43251102 | 14.2 |  |  |  | 14.2
BAHIA 1103 | 43251103 | 11.04 |  |  |  | 11.04
BAHIA 1104 | 43251104 | 18.33 |  |  |  | 18.33
BAHIA 1105 | 43251105 | 13.99 |  |  |  | 13.99
BAIR 1103 | 24261103 | 0.53 |  |  |  | 0.53
BAIR 1105 | 24261105 | 2.15 |  |  |  | 2.15
BAKERSFIELD 1101 | 253371101 | 7.45 |  |  |  | 7.45
BAKERSFIELD 1102 | 253371102 | 17.62 |  |  |  | 17.62
BAKERSFIELD 1105 | 253371105 | 6.46 |  |  |  | 6.46
BAKERSFIELD 1106 | 253371106 | 11.77 |  |  |  | 11.77
BAKERSFIELD 1107 | 253371107 | 3.68 |  |  |  | 3.68
BAKERSFIELD 1110 | 253371110 | 5.95 |  |  |  | 5.95
BAKERSFIELD 1114 | 253371114 | 15.73 |  |  |  | 15.73
BAKERSFIELD 1115 | 253371115 | 5.68 |  |  |  | 5.68
BAKERSFIELD 1116 | 253371116 | 16.76 |  |  |  | 16.76
BAKERSFIELD 1118 | 253371118 | 11.39 |  |  |  | 11.39
BAKERSFIELD 2104 | 253372104 | 34.92 |  |  |  | 34.92
BAKERSFIELD 2106 | 253372106 | 31.5 |  |  |  | 31.5
BAKERSFIELD 2107 | 253372107 | 0.01 |  |  |  | 0.01
BAKERSFIELD 2109 | 253372109 | 32.08 |  |  |  | 32.08
BALCH NO 1 1101 | 252501101 | 14.65 |  | 14.65 |  | 0
BALFOUR 1101 | 14321101 | 49.93 |  |  |  | 49.93
BANCROFT 0401 | 13030401 | 8.41 |  | 0 |  | 8.41
BANCROFT 0402 | 13030402 | 4.59 |  | 0.12 |  | 4.47
BANGOR 1101 | 103191101 | 198 | 1.73 | 188.06 |  | 8.21
BANTA 1101 | 162471101 | 32.94 |  |  |  | 32.94
BANTA 1102 | 162471102 | 15.2 |  |  |  | 15.2
BANTA 1103 | 162471103 | 60.59 |  |  |  | 60.59
BARRETT 0401 | 13020401 | 6.59 |  |  |  | 6.59
BARRETT 0402 | 13020402 | 5.89 |  |  |  | 5.89
BARRY 1101 | 152111101 | 32.02 |  |  |  | 32.02
BARRY 1102 | 152111102 | 17.71 |  |  |  | 17.71
BARRY 1103 | 152111103 | 33.06 |  |  |  | 33.06
BARTON 1101 | 253571101 | 5.98 |  |  |  | 5.98
BARTON 1102 | 253571102 | 4.5 |  |  |  | 4.5
BARTON 1104 | 253571104 | 11.68 |  |  |  | 11.68
BARTON 1105 | 253571105 | 4.79 |  |  |  | 4.79
BARTON 1106 | 253571106 | 5.96 |  |  |  | 5.96
BARTON 1108 | 253571108 | 18.95 |  |  |  | 18.95
BARTON 1109 | 253571109 | 7.17 |  |  |  | 7.17
BARTON 1110 | 253571110 | 16.36 |  |  |  | 16.36
BARTON 1111 | 253571111 | 15.57 |  |  |  | 15.57
BARTON 1112 | 253571112 | 3.34 |  |  |  | 3.34
BARTON 1114 | 253571114 | 12.8 |  |  |  | 12.8
BARTON 1115 | 253571115 | 15.3 |  |  |  | 15.3
BARTON 1116 | 253571116 | 9.32 |  |  |  | 9.32
BASALT 1101 | 42461101 | 10.84 |  |  |  | 10.84
BASALT 1104 | 42461104 | 0.67 |  |  |  | 0.67
BASALT 1105 | 42461105 | 1.65 |  |  |  | 1.65
BASALT 1106 | 42461106 | 68.66 |  | 1.67 |  | 66.99
BAY MEADOWS 1102 | 24011102 | 4.99 |  |  |  | 4.99
BAY MEADOWS 1103 | 24011103 | 6.84 |  |  |  | 6.84
BAY MEADOWS 1104 | 24011104 | 16.71 |  |  |  | 16.71
BAY MEADOWS 1105 | 24011105 | 6.64 |  |  |  | 6.64
BAY MEADOWS 1106 | 24011106 | 0.86 |  |  |  | 0.86
BAY MEADOWS 1107 | 24011107 | 3.17 |  |  |  | 3.17
BAY MEADOWS 1108 | 24011108 | 1.05 |  |  |  | 1.05
BAY MEADOWS 2101 | 24012101 | 17.87 |  |  |  | 17.87
BAY MEADOWS 2102 | 24012102 | 14.26 |  | 3.98 |  | 10.28
BAY MEADOWS 2103 | 24012103 | 0 |  |  |  | 0
BAYWOOD 1101 | 182801101 | 29.06 |  | 3.37 |  | 25.69
BEACH (Q) 0402 | 22340402 | 2.01 |  |  |  | 2.01
BEAR VALLEY 2101 | 252192101 | 166.69 |  | 100.85 |  | 65.84
BEAR VALLEY 2105 | 252192105 | 157.18 | 7.5 | 149.68 |  | 0
BECK STREET 0401 | 12640401 | 1.58 |  |  |  | 1.58
BELL 1107 | 152701107 | 50.39 |  | 42.56 |  | 7.83
BELL 1108 | 152701108 | 66.64 |  | 54.7 |  | 11.94
BELL 1109 | 152701109 | 18.2 |  | 14.03 |  | 4.17
BELL 1110 | 152701110 | 11.18 |  | 0.16 |  | 11.02
BELLE HAVEN 0401 | 24020401 | 9.43 |  |  |  | 9.43
BELLE HAVEN 0402 | 24020402 | 4.67 |  |  |  | 4.67
BELLE HAVEN 0403 | 24020403 | 5.51 |  |  |  | 5.51
BELLE HAVEN 0404 | 24020404 | 8.64 |  |  |  | 8.64
BELLE HAVEN 0405 | 24020405 | 7.39 |  |  |  | 7.39
BELLE HAVEN 0406 | 24020406 | 9.28 |  |  |  | 9.28
BELLE HAVEN 0407 | 24020407 | 6.35 |  |  |  | 6.35
BELLE HAVEN 0408 | 24020408 | 5.2 |  |  |  | 5.2
BELLE HAVEN 0409 | 24020409 | 3.86 |  |  |  | 3.86
BELLE HAVEN 1101 | 24021101 | 1.59 |  |  |  | 1.59
BELLE HAVEN 1102 | 24021102 | 1.68 |  |  |  | 1.68
BELLE HAVEN 1103 | 24021103 | 1.89 |  |  |  | 1.89
BELLE HAVEN 1104 | 24021104 | 5.68 |  |  |  | 5.68
BELLE HAVEN 1105 | 24021105 | 10.56 |  |  |  | 10.56
BELLE HAVEN 1106 | 24021106 | 15.57 |  |  |  | 15.57
BELLE HAVEN 1107 | 24021107 | 1.27 |  |  |  | 1.27
BELLEVUE 1102 | 43181102 | 43.24 |  | 0.16 |  | 43.08
BELLEVUE 1104 | 43181104 | 12.56 |  |  |  | 12.56
BELLEVUE 2101 | 43182101 | 66.04 | 7.02 | 19 |  | 40.02
BELLEVUE 2103 | 43182103 | 5.72 |  |  |  | 5.72
BELLEVUE 2105 | 43182105 | 4.02 |  |  |  | 4.02
BELLEVUE 2107 | 43182107 | 11.32 |  |  |  | 11.32
BELMONT 0401 | 24030401 | 5.89 |  |  |  | 5.89
BELMONT 0402 | 24030402 | 6.99 |  |  |  | 6.99
BELMONT 0403 | 24030403 | 4.65 |  |  |  | 4.65
BELMONT 0406 | 24030406 | 5.02 |  |  |  | 5.02
BELMONT 1102 | 24031102 | 15.15 |  |  |  | 15.15
BELMONT 1103 | 24031103 | 18.58 |  | 3.37 |  | 15.21
BELMONT 1104 | 24031104 | 7.05 |  |  |  | 7.05
BELMONT 1105 | 24031105 | 0.64 |  |  |  | 0.64
BELMONT 1106 | 24031106 | 1.65 |  |  |  | 1.65
BELMONT 1107 | 24031107 | 0.97 |  |  |  | 0.97
BELMONT 1109 | 24031109 | 0 |  |  |  | 0
BELMONT 1110 | 24031110 | 24.15 |  | 0.11 |  | 24.04
BELRIDGE 1A 1101 | 254371101 | 0.09 |  |  |  | 0.09
BELRIDGE 1B 1101 | 254381101 | 0.01 |  |  |  | 0.01
BEN LOMOND 0401 | 83040401 | 23.05 | 23.05 |  |  | 0
BEN LOMOND 1101 | 83041101 | 15.12 | 15.12 |  |  | 0
BERESFORD 0401 | 24040401 | 1.08 |  |  |  | 1.08
BERESFORD 0402 | 24040402 | 2.38 |  |  |  | 2.38
BERESFORD 0403 | 24040403 | 12.19 |  | 5.39 |  | 6.8
BERESFORD 0404 | 24040404 | 5.74 |  |  |  | 5.74
BERKELEY F 0401 | 12060401 | 0 |  |  |  | 0
BERKELEY F 0402 | 12060402 | 2.13 |  | 0.14 |  | 1.99
BERKELEY F 0403 | 12060403 | 2.19 |  |  |  | 2.19
BERKELEY F 0404 | 12060404 | 3.68 |  |  |  | 3.68
BERKELEY F 0405 | 12060405 | 0.97 |  |  |  | 0.97
BERKELEY F 0406 | 12060406 | 3.79 |  |  |  | 3.79
BERKELEY F 0407 | 12060407 | 0.01 |  |  |  | 0.01
BERKELEY F 0408 | 12060408 | 0.79 |  |  |  | 0.79
BERKELEY F 0409 | 12060409 | 3.58 |  |  |  | 3.58
BERKELEY F 0410 | 12060410 | 2.86 |  |  |  | 2.86
BERKELEY F 0411 | 12060411 | 4.42 |  |  |  | 4.42
BERKELEY F 1102 | 12061102 | 0.27 |  |  |  | 0.27
BERKELEY F 1103 | 12061103 | 6.52 | 1.96 |  |  | 4.56
BERKELEY F 1104 | 12061104 | 3.25 |  |  |  | 3.25
BERKELEY F 1105 | 12061105 | 11.37 |  | 1.78 |  | 9.59
BERKELEY T 0401 | 12660401 | 2.5 |  |  |  | 2.5
BERKELEY T 0402 | 12660402 | 1.35 |  |  |  | 1.35
BERKELEY T 0403 | 12660403 | 0.86 |  |  |  | 0.86
BERKELEY T 0404 | 12660404 | 1.08 |  |  |  | 1.08
BERRENDA A 1101 | 254261101 | 0.02 |  |  |  | 0.02
BERRENDA C 0401 | 254480401 | 0.02 |  |  |  | 0.02
BETHEL BANK 0401 | 18150401 | 0.78 |  |  |  | 0.78
BIG BASIN 1101 | 82841101 | 54.98 | 54.98 |  |  | 0
BIG BASIN 1102 | 82841102 | 66.99 | 63.85 | 3.14 |  | 0
BIG BEND 1101 | 103751101 | 56.91 | 42.41 | 14.49 |  | 0.01
BIG BEND 1102 | 103751102 | 18.14 | 18.04 |  |  | 0.1
BIG MEADOWS 2101 | 102812101 | 70.18 |  | 53.01 |  | 17.17
BIG RIVER 1101 | 43081101 | 86.02 |  | 69.95 |  | 16.07
BIOLA 1101 | 252211101 | 90.07 |  |  |  | 90.07
BIOLA 1102 | 252211102 | 32.39 |  |  |  | 32.39
BIOLA 1103 | 252211103 | 80.25 |  |  |  | 80.25
BIOLA 1104 | 252211104 | 50.08 |  |  |  | 50.08
BLACKWELL 1102 | 254681102 | 30.4 |  |  |  | 30.4
BLACKWELL 2101 | 254682101 | 22.89 |  |  |  | 22.89
BLUE LAKE 1101 | 192181101 | 7.32 |  |  | 0.31 | 7.01
BLUE LAKE 1102 | 192181102 | 68.77 |  |  | 0.02 | 68.75
BOGARD 1101 | 103301101 | 0.51 |  | 0.51 |  | 0
BOGUE 1102 | 153781102 | 17.69 |  |  |  | 17.69
BOGUE 1103 | 153781103 | 16.17 |  |  |  | 16.17
BOGUE 1104 | 153781104 | 9.44 |  |  |  | 9.44
BOGUE 1105 | 153781105 | 10.46 |  |  |  | 10.46
BOGUE 1106 | 153781106 | 59.4 |  |  |  | 59.4
BOGUE 1107 | 153781107 | 15.81 |  |  |  | 15.81
BOGUE 1108 | 63781108 | 0.54 |  |  |  | 0.54
BOLINAS 1101 | 42261101 | 51.63 | 27.17 | 7.48 |  | 16.98
BOLTHOUSE FARMS 1101 | 258181101 | 0.02 |  |  |  | 0.02
BONITA 1101 | 255391101 | 53.96 |  |  |  | 53.96
BONITA 1102 | 255391102 | 30.43 |  |  |  | 30.43
BONITA 1103 | 255391103 | 44.61 |  |  |  | 44.61
BONNIE NOOK 1101 | 152301101 | 14.44 | 14.44 |  |  | 0
BONNIE NOOK 1102 | 152301102 | 33.99 | 33.99 |  |  | 0
BONNIE NOOK 1103 | 152301103 | 0.33 | 0.33 |  |  | 0
BORDEN 1101 | 255121101 | 68.11 |  |  |  | 68.11
BORDEN 1102 | 255121102 | 25.89 |  |  |  | 25.89
BORDEN 1103 | 255121103 | 86.39 |  |  |  | 86.39
BORONDA 1101 | 182461101 | 7.92 |  |  |  | 7.92
BORONDA 1102 | 182461102 | 4.35 |  |  |  | 4.35
BOSWELL 1101 | 254941101 | 0.02 |  |  |  | 0.02
BOWLES 1101 | 253531101 | 69.15 |  |  |  | 69.15
BOWLES 1102 | 253531102 | 33.46 |  |  |  | 33.46
BOWLES 1103 | 253531103 | 26.61 |  |  |  | 26.61
BOWLES 1104 | 253531104 | 41.49 |  |  |  | 41.49
BRENTWOOD 2104 | 14592104 | 2.34 |  |  |  | 2.34
BRENTWOOD 2105 | 14592105 | 78.65 |  | 10.38 |  | 68.27
BRENTWOOD 2106 | 14592106 | 5.97 |  |  |  | 5.97
BRENTWOOD 2108 | 14592108 | 6.13 |  |  |  | 6.13
BRENTWOOD 2109 | 14592109 | 1.28 |  |  |  | 1.28
BRENTWOOD 2110 | 14592110 | 3.44 |  |  |  | 3.44
BRENTWOOD 2111 | 14592111 | 7.29 |  |  |  | 7.29
BRENTWOOD 2112 | 14592112 | 94.53 |  |  |  | 94.53
BRENTWOOD 2113 | 14592113 | 8.18 |  |  |  | 8.18
BRIDGEVILLE 1101 | 192461101 | 24.84 | 4.67 | 17.93 |  | 2.24
BRIDGEVILLE 1102 | 192461102 | 43.26 | 20.63 | 10.32 |  | 12.31
BRITTON 1104 | 83611104 | 1.18 |  |  |  | 1.18
BRITTON 1105 | 83611105 | 5.11 |  |  |  | 5.11
BRITTON 1106 | 83611106 | 3.72 |  |  |  | 3.72
BRITTON 1107 | 83611107 | 5.45 |  |  |  | 5.45
BRITTON 1108 | 83611108 | 1.73 |  |  |  | 1.73
BRITTON 1109 | 83611109 | 2.44 |  |  |  | 2.44
BRITTON 1110 | 83611110 | 11.66 |  |  |  | 11.66
BRITTON 1111 | 83611111 | 1.27 |  |  |  | 1.27
BRITTON 1112 | 83611112 | 1.84 |  |  |  | 1.84
BRITTON 1113 | 83611113 | 1.35 |  |  |  | 1.35
BRITTON 1114 | 83611114 | 4.99 |  |  |  | 4.99
BRITTON 1115 | 83611115 | 1.12 |  |  |  | 1.12
BROOKSIDE 0401 | 13210401 | 3.69 |  |  |  | 3.69
BROWNS VALLEY 1101 | 152921101 | 66.44 |  | 44.15 |  | 22.29
BRUNSWICK 1102 | 152481102 | 54.25 | 46.98 | 4.7 |  | 2.57
BRUNSWICK 1103 | 152481103 | 66.02 | 40.51 | 17.91 |  | 7.6
BRUNSWICK 1104 | 152481104 | 57.96 | 26.28 | 29.68 |  | 2
BRUNSWICK 1105 | 152481105 | 118.4 | 113.95 | 4.2 |  | 0.25
BRUNSWICK 1106 | 152481106 | 178.45 | 119.58 | 49.39 |  | 9.48
BRUNSWICK 1107 | 152481107 | 19.52 | 3.13 | 5.71 |  | 10.68
BRUNSWICK 1110 | 152481110 | 32.9 |  | 22.79 |  | 10.11
BUCKS CREEK 1102 | 102211102 | 0.03 | 0.03 |  |  | 0
BUCKS CREEK 1103 | 102211103 | 12.87 | 9.91 | 2.66 |  | 0.3
BUELLTON 1101 | 183041101 | 104.22 | 4.83 | 72.61 |  | 26.78
BUELLTON 1102 | 183041102 | 28.19 |  | 16.03 |  | 12.16
BUENA VISTA 1101 | 182261101 | 0.71 |  |  |  | 0.71
BUENA VISTA 1102 | 182261102 | 11.11 |  |  |  | 11.11
BUENA VISTA 1103 | 182261103 | 7.59 |  |  |  | 7.59
BUENA VISTA 1104 | 182261104 | 3.97 |  |  |  | 3.97
BUENA VISTA 1106 | 182261106 | 12.92 |  |  |  | 12.92
BULLARD 1101 | 253961101 | 14.34 |  |  |  | 14.34
BULLARD 1102 | 253961102 | 2.78 |  |  |  | 2.78
BULLARD 1103 | 253961103 | 8.11 |  |  |  | 8.11
BULLARD 1104 | 253961104 | 8.04 |  |  |  | 8.04
BULLARD 1105 | 253961105 | 3.46 |  |  |  | 3.46
BULLARD 1106 | 253961106 | 3.69 |  |  |  | 3.69
BULLARD 1107 | 253961107 | 2.4 |  |  |  | 2.4
BULLARD 1108 | 253961108 | 1.62 |  |  |  | 1.62
BULLARD 1109 | 253961109 | 5.4 |  |  |  | 5.4
BULLARD 1110 | 253961110 | 4.21 |  |  |  | 4.21
BULLARD 1113 | 253961113 | 5.22 |  |  |  | 5.22
BULLARD 2111 | 253962111 | 4.45 |  |  |  | 4.45
BULLARD 2112 | 253962112 | 11.11 |  |  |  | 11.11
BULLARD 2114 | 253962114 | 5.36 |  |  |  | 5.36
BURLINGAME 0401 | 24050401 | 3.14 |  |  |  | 3.14
BURLINGAME 0402 | 24050402 | 5.89 |  |  |  | 5.89
BURLINGAME 0403 | 24050403 | 3.86 |  |  |  | 3.86
BURLINGAME 0404 | 24050404 | 3.98 |  |  |  | 3.98
BURLINGAME 0405 | 24050405 | 3.25 |  |  |  | 3.25
BURLINGAME 2101 | 24052101 | 6.82 |  |  |  | 6.82
BURNEY 1101 | 103311101 | 59.78 |  | 50.93 |  | 8.85
BURNEY 1102 | 103311102 | 4.06 |  | 0.64 |  | 3.42
BURNS 2101 | 183582101 | 29.14 | 29.14 |  |  | 0
BUTTE 1103 | 103081103 | 60.18 |  |  |  | 60.18
BUTTE 1104 | 103081104 | 52.15 |  |  |  | 52.15
BUTTE 1105 | 103081105 | 37.8 | 26.62 | 3.43 |  | 7.75
BUTTE 1106 | 103081106 | 11.84 |  |  |  | 11.84
BUTTE 1107 | 103081107 | 109.39 |  |  |  | 109.39
CABRILLO 1103 | 183101103 | 102.06 |  | 57.4 |  | 44.66
CABRILLO 1104 | 183101104 | 76.03 |  | 30.33 |  | 45.7
CADET 1101 | 254821101 | 0.03 |  |  |  | 0.03
CAL WATER 1102 | 255451102 | 26.43 |  | 3.72 |  | 22.71
CAL WATER 1103 | 255451103 | 8.81 |  |  |  | 8.81
CALAVERAS CEMENT 1101 | 162211101 | 242.75 | 7.77 | 218.19 |  | 16.79
CALFLAX 1101 | 253441101 | 27.49 |  |  |  | 27.49
CALFLAX 1102 | 253441102 | 20.43 |  |  |  | 20.43
CALFLAX 1103 | 253441103 | 29.03 |  |  |  | 29.03
CALFLAX 1104 | 253441104 | 18.61 |  |  |  | 18.61
CALIFORNIA AVE 1102 | 252281102 | 11.42 |  |  |  | 11.42
CALIFORNIA AVE 1103 | 252281103 | 7.76 |  |  |  | 7.76
CALIFORNIA AVE 1104 | 252281104 | 3.58 |  |  |  | 3.58
CALIFORNIA AVE 1106 | 252281106 | 9.78 |  |  |  | 9.78
CALIFORNIA AVE 1108 | 252281108 | 9.61 |  |  |  | 9.61
CALIFORNIA AVE 1110 | 252281110 | 11.08 |  |  |  | 11.08
CALIFORNIA AVE 1111 | 252281111 | 6.73 |  |  |  | 6.73
CALIFORNIA AVE 1112 | 252281112 | 4.93 |  |  |  | 4.93
CALIFORNIA AVE 1113 | 252281113 | 6.5 |  |  |  | 6.5
CALIFORNIA AVE 1114 | 252281114 | 19.38 |  |  |  | 19.38
CALIFORNIA AVE 1116 | 252281116 | 9.35 |  |  |  | 9.35
CALIFORNIA AVE 1117 | 252281117 | 1.27 |  |  |  | 1.27
CALISTOGA 1101 | 42711101 | 115.63 | 83.32 | 15.49 |  | 16.82
CALISTOGA 1102 | 42711102 | 45.68 | 22.32 | 1.53 |  | 21.83
CALPELLA 1101 | 43411101 | 101.17 | 4.03 | 77.84 |  | 19.3
CALPELLA 1102 | 43411102 | 7.52 |  | 1.79 |  | 5.73
CALPINE 1144 | 48011144 | 30.59 | 28.37 | 2.22 |  | 0
CALPINE 1146 | 48011146 | 5.61 | 5.61 |  |  | 0
CAMBRIA 1101 | 182771101 | 31.04 |  | 24.35 |  | 6.69
CAMBRIA 1102 | 182771102 | 27.24 |  | 15.77 |  | 11.47
CAMDEN 1102 | 252301102 | 40.15 |  |  |  | 40.15
CAMDEN 1103 | 252301103 | 127.81 |  |  |  | 127.81
CAMDEN 1104 | 252301104 | 77.5 |  |  |  | 77.5
CAMDEN 1105 | 252301105 | 58.83 |  |  |  | 58.83
CAMP EVERS 2103 | 83622103 | 61.29 | 44.84 | 0.83 |  | 15.62
CAMP EVERS 2104 | 83622104 | 36.49 | 26.64 | 0.58 |  | 9.27
CAMP EVERS 2105 | 83622105 | 78.47 | 73.46 | 2.13 |  | 2.88
CAMP EVERS 2106 | 83622106 | 145.75 | 132.84 | 2.97 |  | 9.94
CAMPHORA 0401 | 182070401 | 0.43 |  |  |  | 0.43
CAMPHORA 1101 | 182071101 | 51.89 |  | 3.89 |  | 48
CANAL 1101 | 252091101 | 56.42 |  |  |  | 56.42
CANAL 1102 | 252091102 | 15.33 |  |  |  | 15.33
CANAL 1103 | 252091103 | 53.58 |  |  |  | 53.58
CANAL 1104 | 252091104 | 9.93 |  |  |  | 9.93
CANAL 1105 | 252091105 | 17.32 |  |  |  | 17.32
CANAL 1106 | 252091106 | 7.86 |  |  |  | 7.86
CANTUA 1101 | 253591101 | 24.04 |  |  |  | 24.04
CANTUA 1102 | 253591102 | 47.75 |  |  |  | 47.75
CANTUA 1103 | 253591103 | 35.78 |  |  |  | 35.78
CANTUA 1104 | 253591104 | 0.17 |  |  |  | 0.17
CANTUA 1105 | 253591105 | 15.12 |  |  |  | 15.12
CANTUA 1106 | 253591106 | 0.16 |  |  |  | 0.16
CAPAY 1101 | 102111101 | 48.81 |  |  |  | 48.81
CAPAY 1102 | 102111102 | 73.95 |  |  |  | 73.95
CARBONA 1101 | 163091101 | 39.11 |  |  |  | 39.11
CARBONA 1103 | 163091103 | 3.63 |  |  |  | 3.63
CARLOTTA 1121 | 192291121 | 51.97 |  | 21.08 |  | 30.89
CARNATION 2101 | 255282101 | 0.01 |  |  |  | 0.01
CARNERAS 1102 | 252321102 | 16.83 |  |  |  | 16.83
CARNERAS 1103 | 252321103 | 41.62 |  |  |  | 41.62
CAROLANDS 0401 | 24060401 | 4.52 |  |  |  | 4.52
CAROLANDS 0402 | 24060402 | 0.03 |  |  |  | 0.03
CAROLANDS 0403 | 24060403 | 13.35 |  |  |  | 13.35
CAROLANDS 0404 | 24060404 | 10.2 |  | 4.16 |  | 6.04
CARQUINEZ 1103 | 43281103 | 14.67 |  |  |  | 14.67
CARQUINEZ 1104 | 43281104 | 0.38 |  |  |  | 0.38
CARQUINEZ 1105 | 43281105 | 5.68 |  |  |  | 5.68
CARRIZO PLAINS 1101 | 253461101 | 105.92 |  |  |  | 105.92
CARUTHERS 1101 | 252371101 | 81.8 |  |  |  | 81.8
CARUTHERS 1102 | 252371102 | 69.76 |  |  |  | 69.76
CARUTHERS 1104 | 252371104 | 80.71 |  |  |  | 80.71
CARUTHERS 1105 | 252371105 | 56.41 |  |  |  | 56.41
CASSERLY 0401 | 83110401 | 3.07 |  |  |  | 3.07
CASSIDY 2107 | 254272107 | 59.41 |  |  |  | 59.41
CASSIDY 2108 | 254272108 | 34.09 |  |  |  | 34.09
CASTRO 0401 | 22480401 | 2.93 |  |  |  | 2.93
CASTRO 0402 | 22480402 | 2.62 |  |  |  | 2.62
CASTRO VALLEY 1102 | 14091102 | 22.74 | 0.35 | 1.15 |  | 21.24
CASTRO VALLEY 1103 | 14091103 | 15.67 |  |  |  | 15.67
CASTRO VALLEY 1104 | 14091104 | 7.33 |  |  |  | 7.33
CASTRO VALLEY 1105 | 14091105 | 30.22 |  | 2.18 |  | 28.04
CASTRO VALLEY 1107 | 14091107 | 16.06 |  |  |  | 16.06
CASTRO VALLEY 1108 | 14091108 | 38.75 | 12.59 | 4.16 |  | 22
CASTRO VALLEY 1109 | 14091109 | 8.02 |  |  |  | 8.02
CASTRO VALLEY 1110 | 14091110 | 24.81 | 15.57 | 6.7 |  | 2.54
CASTRO VALLEY 1111 | 14091111 | 7.89 | 1.54 | 3.92 |  | 2.43
CASTROVILLE 2103 | 182352103 | 81.37 |  |  |  | 81.37
CASTROVILLE 2104 | 182352104 | 50.51 |  |  |  | 50.51
CATLETT 1101 | 153761101 | 0.03 |  |  |  | 0.03
CATLETT 1102 | 153761102 | 106.14 |  |  |  | 106.14
CATLETT 1105 | 153761105 | 54.16 |  |  |  | 54.16
CAWELO B 1101 | 252621101 | 0.01 |  |  |  | 0.01
CAWELO C 1101 | 252631101 | 0.02 |  |  |  | 0.02
CAYETANO 2109 | 14422109 | 49.59 | 12.1 | 21.65 |  | 15.84
CAYETANO 2111 | 14422111 | 12.25 |  | 5.36 |  | 6.89
CAYUCOS 1101 | 182551101 | 46.25 |  | 0.46 |  | 45.79
CAYUCOS 1102 | 182551102 | 57.27 | 9.06 | 4.98 |  | 43.23
CEDAR CREEK 1101 | 103321101 | 109.66 | 20.98 | 88.68 |  | 0
CELERON 1101 | 255271101 | 0.15 |  |  |  | 0.15
CHALLENGE 1101 | 103201101 | 48.27 | 48.04 | 0.23 |  | 0
CHALLENGE 1102 | 103201102 | 62.85 | 60.21 | 2.64 |  | 0
CHANNEL 1101 | 163071101 | 9.93 |  |  |  | 9.93
CHANNEL 1102 | 163071102 | 8.38 |  |  |  | 8.38
CHARCA 1102 | 254501102 | 47.97 |  |  |  | 47.97
CHARCA 1103 | 254501103 | 41.41 |  |  |  | 41.41
CHARCA 1106 | 254501106 | 18.69 |  |  |  | 18.69
CHEROKEE 1101 | 163651101 | 19.87 |  |  |  | 19.87
CHEROKEE 1102 | 163651102 | 36.3 |  |  |  | 36.3
CHESTER 1101 | 103181101 | 8.16 |  | 2.12 |  | 6.04
CHESTER 1102 | 103181102 | 5.3 |  | 2.31 |  | 2.99
CHICO A 0401 | 102050401 | 2.2 |  |  |  | 2.2
CHICO A 0402 | 102050402 | 5.65 |  |  |  | 5.65
CHICO A 1101 | 102051101 | 8.09 |  |  |  | 8.09
CHICO A 1102 | 102051102 | 9.3 |  |  |  | 9.3
CHICO A 1103 | 102051103 | 4.86 |  |  |  | 4.86
CHICO B 1101 | 102491101 | 4.56 |  |  |  | 4.56
CHICO B 1103 | 102491103 | 8.02 |  |  |  | 8.02
CHICO B 1105 | 102491105 | 10.85 |  |  |  | 10.85
CHICO B 1106 | 102491106 | 2.01 |  |  |  | 2.01
CHICO C 0401 | 102650401 | 2.77 |  |  |  | 2.77
CHOLAME 1101 | 182561101 | 96.97 |  |  |  | 96.97
CHOLAME 2102 | 182562102 | 215.33 |  | 59 |  | 156.33
CHOWCHILLA 1101 | 254101101 | 63.03 |  |  |  | 63.03
CHOWCHILLA 1102 | 254101102 | 13.15 |  |  |  | 13.15
CHOWCHILLA 1103 | 254101103 | 46.85 |  |  |  | 46.85
CHOWCHILLA 1104 | 254101104 | 80.6 |  |  |  | 80.6
CHOWCHILLA 1105 | 254101105 | 11.89 |  |  |  | 11.89
CHOWCHILLA 1106 | 254101106 | 54.75 |  |  |  | 54.75
CLARK ROAD 1101 | 103091101 | 0.02 |  | 0.02 |  | 0
CLARK ROAD 1102 | 103091102 | 136.63 | 32.87 | 89.63 |  | 14.13
CLARKSVILLE 2103 | 153612103 | 50.41 | 19.61 | 10.52 |  | 20.28
CLARKSVILLE 2104 | 153612104 | 75.66 | 41.19 | 21.88 |  | 12.59
CLARKSVILLE 2105 | 153612105 | 13.34 | 5.79 | 4.75 |  | 2.8
CLARKSVILLE 2106 | 153612106 | 2.21 |  | 0.48 |  | 1.73
CLARKSVILLE 2109 | 153612109 | 12.26 | 1.98 | 1.96 |  | 8.32
CLARKSVILLE 2110 | 153612110 | 7.03 |  |  |  | 7.03
CLAY 1101 | 163341101 | 40.58 |  | 26.32 |  | 14.26
CLAY 1102 | 163341102 | 2.09 |  | 0.82 |  | 1.27
CLAY 1103 | 163341103 | 112.62 |  | 49.68 |  | 62.94
CLAYTON 1103 | 12021103 | 4.33 |  |  |  | 4.33
CLAYTON 1104 | 12021104 | 13.4 |  |  |  | 13.4
CLAYTON 2211 | 12022211 | 10.48 |  |  |  | 10.48
CLAYTON 2212 | 12022212 | 58.62 | 28.9 | 18.66 |  | 11.06
CLAYTON 2213 | 12022213 | 4.84 |  | 2.51 |  | 2.33
CLAYTON 2214 | 12022214 | 5.89 |  |  |  | 5.89
CLAYTON 2215 | 12022215 | 30.8 | 2.92 | 5.47 |  | 22.41
CLAYTON 2216 | 12022216 | 18.71 |  |  |  | 18.71
CLAYTON 2217 | 12022217 | 19.79 |  |  |  | 19.79
CLAYTON 2218 | 12022218 | 8.34 |  |  |  | 8.34
CLEAR LAKE 1101 | 42141101 | 112.61 | 6.05 | 12.29 |  | 94.27
CLEAR LAKE 1102 | 42141102 | 36.63 |  | 3.97 |  | 32.66
CLOVERDALE 1101 | 42821101 | 36.64 |  | 24.35 |  | 12.29
CLOVERDALE 1102 | 42821102 | 108.77 | 47.23 | 30.21 |  | 31.33
CLOVIS 1101 | 254081101 | 3.97 |  |  |  | 3.97
CLOVIS 1102 | 254081102 | 25.59 |  |  |  | 25.59
CLOVIS 1103 | 254081103 | 1.95 |  |  |  | 1.95
CLOVIS 1104 | 254081104 | 0.43 |  |  |  | 0.43
CLOVIS 1105 | 254081105 | 7.73 |  |  |  | 7.73
CLOVIS 1106 | 254081106 | 4.99 |  |  |  | 4.99
CLOVIS 1107 | 254081107 | 10.71 |  |  |  | 10.71
CLOVIS 1108 | 254081108 | 11.47 |  |  |  | 11.47
CLOVIS 2109 | 254082109 | 3.85 |  |  |  | 3.85
CLOVIS 2110 | 254082110 | 11.47 |  |  |  | 11.47
CLOVIS 2111 | 254082111 | 8.84 |  |  |  | 8.84
CMC 1101 | 183111101 | 2.01 |  | 2.01 |  | 0
CMC 1102 | 183111102 | 0.48 |  | 0.48 |  | 0
COALINGA NO 1 1106 | 252161106 | 8.96 |  |  |  | 8.96
COALINGA NO 1 1107 | 252161107 | 4.04 |  |  |  | 4.04
COALINGA NO 1 1108 | 252161108 | 60.22 |  |  |  | 60.22
COALINGA NO 1 1109 | 252161109 | 27.26 |  |  |  | 27.26
COALINGA NO 2 1104 | 252381104 | 0.16 |  |  |  | 0.16
COALINGA NO 2 1105 | 252381105 | 76.34 |  |  |  | 76.34
COALINGA NO 2 1106 | 252381106 | 42.94 |  |  |  | 42.94
COALINGA NO 2 1107 | 252381107 | 38.43 |  |  |  | 38.43
COARSEGOLD 2102 | 254432102 | 72.98 | 58.15 | 14.83 |  | 0
COARSEGOLD 2103 | 254432103 | 122.4 |  | 93.29 |  | 29.11
COARSEGOLD 2104 | 254432104 | 265.16 | 2.83 | 243.51 |  | 18.82
COLONY 1101 | 162231101 | 28.9 |  |  |  | 28.9
COLONY 1102 | 162231102 | 47.74 |  |  |  | 47.74
COLUMBIA HILL 1101 | 152471101 | 89.55 | 71.94 | 17.61 |  | 0
COLUMBUS 1103 | 253951103 | 7.87 |  |  |  | 7.87
COLUMBUS 1104 | 253951104 | 8.27 |  |  |  | 8.27
COLUMBUS 1105 | 253951105 | 16.06 |  |  |  | 16.06
COLUMBUS 1106 | 253951106 | 14.29 |  |  |  | 14.29
COLUMBUS 1109 | 253951109 | 5.58 |  |  |  | 5.58
COLUMBUS 1110 | 253951110 | 6.52 |  |  |  | 6.52
COLUSA 1100 | 62021100 | 0.02 |  |  |  | 0.02
COLUSA 1101 | 62021101 | 113.67 |  |  |  | 113.67
COLUSA JUNCTION 1101 | 62071101 | 29 |  |  |  | 29
CONCORD NO 1 0401 | 12960401 | 4.75 |  |  |  | 4.75
CONCORD NO 1 0402 | 12960402 | 3.77 |  |  |  | 3.77
CONTRA COSTA 2103 | 13652103 | 22.62 |  |  |  | 22.62
CONTRA COSTA 2104 | 13652104 | 10.89 |  |  |  | 10.89
CONTRA COSTA 2105 | 13652105 | 0.04 |  |  |  | 0.04
CONTRA COSTA 2106 | 13652106 | 0.02 |  |  |  | 0.02
CONTRA COSTA 2107 | 13652107 | 12.73 |  |  |  | 12.73
CONTRA COSTA 2108 | 13652108 | 0.88 |  |  |  | 0.88
CONTRA COSTA 2109 | 13652109 | 13.87 |  |  |  | 13.87
CONTRA COSTA 2110 | 13652110 | 0.55 |  |  |  | 0.55
CONTRA COSTA 2112 | 13652112 | 0.04 |  |  |  | 0.04
CONTRA COSTA 2113 | 13652113 | 15.09 |  |  |  | 15.09
CONTRA COSTA 2114 | 13652114 | 1.91 |  |  |  | 1.91
CONTRA COSTA 2115 | 13652115 | 6.76 |  |  |  | 6.76
CONTRA COSTA 2116 | 13652116 | 23.1 |  |  |  | 23.1
COPPERMINE 1104 | 252411104 | 102.71 |  | 9.04 |  | 93.67
COPPERMINE 1106 | 252411106 | 7.93 |  |  |  | 7.93
COPPERMINE 1112 | 252411112 | 15.85 |  |  |  | 15.85
COPPERMINE 2110 | 252412110 | 0 |  |  |  | 0
COPUS 1102 | 253871102 | 30.83 |  |  |  | 30.83
COPUS 1103 | 253871103 | 24.39 |  |  |  | 24.39
COPUS 1104 | 253871104 | 39.16 |  |  |  | 39.16
CORCORAN 1101 | 252171101 | 0.52 |  |  |  | 0.52
CORCORAN 1102 | 252171102 | 0.04 |  |  |  | 0.04
CORCORAN 1104 | 252171104 | 26.71 |  |  |  | 26.71
CORCORAN 1106 | 252171106 | 45.04 |  |  |  | 45.04
CORCORAN 1108 | 252171108 | 23.47 |  |  |  | 23.47
CORCORAN 1112 | 252171112 | 45.42 |  |  |  | 45.42
CORCORAN 1116 | 252171116 | 56.58 |  |  |  | 56.58
CORCORAN 1117 | 252171117 | 0.54 |  |  |  | 0.54
CORCORAN 1118 | 252171118 | 52.18 |  |  |  | 52.18
CORDELIA 1101 | 62701101 | 0.02 |  |  |  | 0.02
CORDELIA 1102 | 62701102 | 0.04 |  |  |  | 0.04
CORDELIA 1104 | 62701104 | 61.99 |  |  |  | 61.99
CORDELIA 1110 | 62701110 | 8.94 |  |  |  | 8.94
CORDELIA 1112 | 62701112 | 16.1 |  |  |  | 16.1
CORNING 1101 | 103331101 | 143.58 |  | 49.53 |  | 94.05
CORNING 1102 | 103331102 | 192.36 |  | 79.8 |  | 112.56
CORNING 1103 | 103331103 | 66.42 |  |  |  | 66.42
CORNING 1104 | 103331104 | 106.3 |  |  |  | 106.3
CORONA 1101 | 43491101 | 22.81 |  |  |  | 22.81
CORONA 1102 | 43491102 | 1.38 |  |  |  | 1.38
CORONA 1103 | 43491103 | 17.44 |  | 0.46 |  | 16.98
CORRAL 1101 | 162991101 | 170.22 |  | 119.68 |  | 50.54
CORRAL 1102 | 162991102 | 64.32 |  | 48.46 |  | 15.86
CORRAL 1103 | 162991103 | 80.53 |  | 17.68 |  | 62.85
CORTINA 1101 | 63121101 | 76.57 |  | 1.32 |  | 75.25
COTATI 1102 | 42271102 | 34.61 |  | 15.6 |  | 19.01
COTATI 1103 | 42271103 | 110.88 |  | 84.03 |  | 26.85
COTATI 1104 | 42271104 | 19.32 |  | 8.43 |  | 10.89
COTATI 1105 | 42271105 | 131.49 |  | 42.8 |  | 88.69
COTTLE 1701 | 163711701 | 89.87 |  |  |  | 89.87
COTTLE 1702 | 163711702 | 37 |  |  |  | 37
COTTLE 1703 | 163711703 | 26.78 |  |  |  | 26.78
COTTLE 1704 | 163711704 | 14.6 |  |  |  | 14.6
COTTLE 1707 | 163711707 | 47.15 |  |  |  | 47.15
COTTLE 1708 | 163711708 | 129.9 |  |  |  | 129.9
COTTONWOOD 1101 | 102931101 | 100.91 |  | 69.99 |  | 30.92
COTTONWOOD 1102 | 102931102 | 82.71 |  | 55.8 |  | 26.91
COTTONWOOD 1103 | 102931103 | 161.03 |  | 133.87 |  | 27.16
COUNTRY CLUB 0401 | 163120401 | 2.11 |  |  |  | 2.11
COUNTRY CLUB 0402 | 163120402 | 4.65 |  |  |  | 4.65
COUNTRY CLUB 0403 | 163120403 | 2.7 |  |  |  | 2.7
COUNTRY CLUB 1101 | 163121101 | 12 |  |  |  | 12
COUNTRY CLUB 1102 | 163121102 | 1.34 |  |  |  | 1.34
COUNTRY CLUB 1103 | 163121103 | 6.25 |  |  |  | 6.25
COUNTRY CLUB 1104 | 163121104 | 7.2 |  |  |  | 7.2
COUNTRY CLUB 1105 | 163121105 | 1.64 |  |  |  | 1.64
COUNTRY CLUB 1106 | 163121106 | 8.96 |  |  |  | 8.96
COVELO 1101 | 43061101 | 120.63 |  | 17.54 |  | 103.09
CRESCENT MILLS 2101 | 103132101 | 79.32 |  | 42.08 |  | 37.24
CRESSEY 2103 | 254702103 | 152.7 |  |  |  | 152.7
CRESSEY 2104 | 254702104 | 94.86 |  |  |  | 94.86
CRESTA 1101 | 102251101 | 1.7 | 0.41 | 1.3 |  | -0.01
CROWS LANDING 1101 | 163251101 | 44.59 |  |  |  | 44.59
CROWS LANDING 1102 | 163251102 | 7.56 |  |  |  | 7.56
CURTIS 1701 | 163351701 | 20.14 |  | 12.23 |  | 7.91
CURTIS 1702 | 163351702 | 117.69 | 22.46 | 87.13 |  | 8.1
CURTIS 1703 | 163351703 | 197.92 | 17.43 | 177.18 |  | 3.31
CURTIS 1704 | 163351704 | 75.97 | 24.28 | 51.12 |  | 0.57
CURTIS 1705 | 163351705 | 88.26 | 14.37 | 69.8 |  | 4.09
CUYAMA 1103 | 253141103 | 79.98 |  | 2.58 |  | 77.4
CUYAMA 1104 | 253141104 | 17.89 |  |  |  | 17.89
CUYAMA 2101 | 253142101 | 63.13 |  | 3.39 |  | 59.74
CUYAMA 2102 | 253142102 | 35.86 |  |  |  | 35.86
DAIRYLAND 1102 | 252421102 | 81.4 |  |  |  | 81.4
DAIRYLAND 1105 | 252421105 | 64.77 |  |  |  | 64.77
DAIRYLAND 1109 | 252421109 | 48.59 |  |  |  | 48.59
DAIRYLAND 1110 | 252421110 | 35 |  |  |  | 35
DAIRYLAND 1111 | 252421111 | 26.7 |  |  |  | 26.7
DAIRYLAND 1112 | 252421112 | 62.34 |  |  |  | 62.34
DAIRYLAND 1113 | 252421113 | 83.52 |  |  |  | 83.52
DAIRYVILLE 1101 | 103341101 | 43.01 |  |  |  | 43.01
DALY CITY 0401 | 22640401 | 5.65 |  |  |  | 5.65
DALY CITY 1101 | 22641101 | 3.43 |  |  |  | 3.43
DALY CITY 1102 | 22641102 | 7.54 |  |  |  | 7.54
DALY CITY 1103 | 22641103 | 4.73 |  |  |  | 4.73
DALY CITY 1104 | 22641104 | 10.98 |  |  |  | 10.98
DALY CITY 1105 | 22641105 | 10.65 |  |  |  | 10.65
DALY CITY 1106 | 22641106 | 9.94 |  |  |  | 9.94
DALY CITY 1107 | 22641107 | 5.3 |  |  |  | 5.3
DALY CITY 1108 | 22641108 | 2.92 |  |  |  | 2.92
DALY CITY 1109 | 22641109 | 6.23 |  |  |  | 6.23
DALY CITY 1110 | 22641110 | 1.78 |  |  |  | 1.78
DALY CITY 1111 | 22641111 | 6.94 |  |  |  | 6.94
DALY CITY 1112 | 22641112 | 14.04 |  |  |  | 14.04
DALY CITY 1115 | 22641115 | 0.03 |  |  |  | 0.03
DAVIS 1101 | 62041101 | 37.51 |  |  |  | 37.51
DAVIS 1102 | 62041102 | 6.46 |  |  |  | 6.46
DAVIS 1103 | 62041103 | 5.85 |  |  |  | 5.85
DAVIS 1104 | 62041104 | 5.72 |  |  |  | 5.72
DAVIS 1105 | 62041105 | 8.02 |  |  |  | 8.02
DAVIS 1106 | 62041106 | 42.71 |  |  |  | 42.71
DAVIS 1107 | 62041107 | 84.37 |  |  |  | 84.37
DAVIS 1108 | 62041108 | 3.34 |  |  |  | 3.34
DAVIS 1109 | 62041109 | 4.45 |  |  |  | 4.45
DAVIS 1110 | 62041110 | 1.83 |  |  |  | 1.83
DAVIS 1111 | 62041111 | 7.24 |  |  |  | 7.24
DAVIS 1112 | 62041112 | 46.6 |  |  |  | 46.6
DAYTON ROAD 0401 | 102940401 | 2.11 |  |  |  | 2.11
DEEPWATER 1105 | 63621105 | 4.12 |  |  |  | 4.12
DEEPWATER 1106 | 63621106 | 0.06 |  |  |  | 0.06
DEEPWATER 1107 | 63621107 | 28.7 |  |  |  | 28.7
DEEPWATER 1108 | 63621108 | 0.09 |  |  |  | 0.09
DEEPWATER 1109 | 63621109 | 4.17 |  |  |  | 4.17
DEER CREEK PH 0401 | 158450401 | 1.12 | 1.12 |  |  | 0
DEL MAR 1103 | 152581103 | 13.01 |  |  |  | 13.01
DEL MAR 1104 | 152581104 | 0 |  |  |  | 0
DEL MAR 2105 | 152582105 | 13.85 |  |  |  | 13.85
DEL MAR 2106 | 152582106 | 3.18 |  |  |  | 3.18
DEL MAR 2109 | 152582109 | 6.88 |  | 2.03 |  | 4.85
DEL MAR 2110 | 152582110 | 1.77 |  |  |  | 1.77
DEL MONTE 1101 | 182221101 | 14.88 |  | 0.49 |  | 14.39
DEL MONTE 2102 | 182222102 | 16.27 |  | 0.66 |  | 15.61
DEL MONTE 2103 | 182222103 | 36.72 |  | 12.3 |  | 24.42
DEL MONTE 2104 | 182222104 | 59.25 |  | 43.85 |  | 15.4
DEL MONTE 2105 | 182222105 | 20.14 |  | 1.04 |  | 19.1
DELEVAN 1101 | 69551101 | 0.6 |  |  |  | 0.6
DELEVAN 1102 | 69551102 | 0.61 |  |  |  | 0.61
DESCHUTES 1101 | 103351101 | 130.44 | 7.48 | 99.43 |  | 23.53
DESCHUTES 1104 | 103351104 | 112.8 |  | 60.22 |  | 52.58
DEVILS DEN 1101 | 253451101 | 44.8 |  |  |  | 44.8
DEVILS DEN 1102 | 253451102 | 33.33 |  |  |  | 33.33
DIAMOND SPRINGS 1103 | 152261103 | 53.26 | 10.2 | 22.95 |  | 20.11
DIAMOND SPRINGS 1104 | 152261104 | 18.15 | 7.56 | 4.89 |  | 5.7
DIAMOND SPRINGS 1105 | 152261105 | 131.88 | 75.04 | 48.36 |  | 8.48
DIAMOND SPRINGS 1106 | 152261106 | 120.12 |  | 109.72 |  | 10.4
DIAMOND SPRINGS 1107 | 152261107 | 57.33 | 34.14 | 17.88 |  | 5.31
DINUBA 1102 | 254091102 | 22.52 |  |  |  | 22.52
DINUBA 1104 | 254091104 | 85.42 |  |  |  | 85.42
DINUBA 1105 | 254091105 | 99.83 |  |  |  | 99.83
DINUBA 1106 | 254091106 | 10.29 |  |  |  | 10.29
DIVIDE 1101 | 182571101 | 15.49 |  |  |  | 15.49
DIVIDE 1102 | 182571102 | 47.79 |  |  |  | 47.79
DIVIDE 1103 | 182571103 | 21.03 |  | 2.38 |  | 18.65
DIXON 1102 | 62061102 | 10.84 |  |  |  | 10.84
DIXON 1103 | 62061103 | 126.63 |  |  |  | 126.63
DIXON 1104 | 62061104 | 11.67 |  |  |  | 11.67
DIXON 1105 | 62061105 | 23.75 |  |  |  | 23.75
DIXON 1106 | 62061106 | 10.06 |  |  |  | 10.06
DIXON LANDING 2101 | 14722101 | 10.74 |  |  |  | 10.74
DIXON LANDING 2102 | 14722102 | 10.86 |  |  |  | 10.86
DIXON LANDING 2103 | 14722103 | 2.81 |  |  |  | 2.81
DIXON LANDING 2105 | 14722105 | 1.68 |  |  |  | 1.68
DIXON LANDING 2109 | 14722109 | 10.59 |  |  |  | 10.59
DIXON LANDING 2111 | 14722111 | 0.13 |  |  |  | 0.13
DOBBINS 1101 | 153741101 | 81.65 | 26.57 | 54.01 |  | 1.07
DOLAN RD 1102 | 182381102 | 0.45 |  |  |  | 0.45
DOLAN ROAD 1101 | 182381101 | 69.09 |  | 2.77 |  | 66.32
DOLAN ROAD 1103 | 182381103 | 3 |  |  |  | 3
DOLAN ROAD 1104 | 182381104 | 5.06 |  |  |  | 5.06
DOS PALOS 1101 | 254041101 | 75.66 |  |  |  | 75.66
DOS PALOS 1102 | 254041102 | 0.21 |  |  |  | 0.21
DRUM 1101 | 152321101 | 18.36 | 18.32 | 0.04 |  | 0
DUMBARTON 1102 | 14471102 | 16.47 |  |  |  | 16.47
DUMBARTON 1103 | 14471103 | 1.48 |  |  |  | 1.48
DUMBARTON 1104 | 14471104 | 13.19 |  |  |  | 13.19
DUMBARTON 1106 | 14471106 | 7.25 |  |  |  | 7.25
DUMBARTON 1107 | 14471107 | 10.35 |  |  |  | 10.35
DUMBARTON 1108 | 14471108 | 3.94 |  |  |  | 3.94
DUMBARTON 1109 | 14471109 | 3.71 |  |  |  | 3.71
DUMBARTON 1110 | 14471110 | 6.95 |  |  |  | 6.95
DUMBARTON 2111 | 14472111 | 6.41 |  |  |  | 6.41
DUNBAR 1101 | 43071101 | 53.4 | 26.42 | 2.62 |  | 24.36
DUNBAR 1102 | 43071102 | 62.11 | 7.2 | 42.28 |  | 12.63
DUNBAR 1103 | 43071103 | 60.09 | 20.67 | 14.76 |  | 24.66
DUNLAP 1102 | 254061102 | 55.46 |  | 55.46 |  | 0
DUNLAP 1103 | 254061103 | 71.32 |  | 71.32 |  | 0
DUNNIGAN 1101 | 63811101 | 78.06 |  |  |  | 78.06
EAST GRAND 0401 | 22570401 | 4.71 |  |  |  | 4.71
EAST GRAND 0404 | 22570404 | 3.82 |  |  |  | 3.82
EAST GRAND 1101 | 22571101 | 7.95 |  |  |  | 7.95
EAST GRAND 1102 | 22571102 | 2.21 |  |  |  | 2.21
EAST GRAND 1103 | 22571103 | 1.51 |  |  |  | 1.51
EAST GRAND 1104 | 22571104 | 15.54 |  |  |  | 15.54
EAST GRAND 1105 | 22571105 | 5.55 |  |  |  | 5.55
EAST GRAND 1106 | 22571106 | 3.7 |  |  |  | 3.7
EAST GRAND 1107 | 22571107 | 13.53 |  |  |  | 13.53
EAST GRAND 1108 | 22571108 | 3.86 |  |  |  | 3.86
EAST GRAND 1109 | 22571109 | 2.08 |  |  |  | 2.08
EAST GRAND 1110 | 22571110 | 3.34 |  |  |  | 3.34
EAST GRAND 1111 | 22571111 | 0.88 |  |  |  | 0.88
EAST GRAND 1114 | 22571114 | 0 |  |  |  | 0
EAST GRAND 1115 | 22571115 | 0 |  |  |  | 0
EAST MARYSVILLE 1105 | 152331105 | 39.25 |  |  |  | 39.25
EAST MARYSVILLE 1107 | 152331107 | 8.01 |  |  |  | 8.01
EAST MARYSVILLE 1108 | 152331108 | 67.82 |  |  |  | 67.82
EAST NICOLAUS 1101 | 152151101 | 68.88 |  |  |  | 68.88
EAST NICOLAUS 1102 | 152151102 | 58.28 |  |  |  | 58.28
EAST NICOLAUS 1103 | 152151103 | 93.3 |  |  |  | 93.3
EAST QUINCY 1101 | 102551101 | 17.43 | 1.69 | 2.06 |  | 13.68
EAST STOCKTON 0401 | 163130401 | 8.35 |  |  |  | 8.35
EAST STOCKTON 0402 | 163130402 | 9.76 |  |  |  | 9.76
EAST STOCKTON 1101 | 163131101 | 14.59 |  |  |  | 14.59
EAST STOCKTON 1102 | 163131102 | 16.09 |  |  |  | 16.09
ECHO SUMMIT 1101 | 158031101 | 14.7 |  | 5.9 | 0.04 | 8.76
EDENVALE 1101 | 82951101 | 9.68 |  |  |  | 9.68
EDENVALE 1102 | 82951102 | 5.72 |  | 0.52 |  | 5.2
EDENVALE 1103 | 82951103 | 0.31 |  |  |  | 0.31
EDENVALE 2105 | 82952105 | 37.05 |  | 2.32 |  | 34.73
EDENVALE 2106 | 82952106 | 16.89 |  |  |  | 16.89
EDENVALE 2107 | 82952107 | 0.07 |  |  |  | 0.07
EDENVALE 2108 | 82952108 | 2.87 |  |  |  | 2.87
EDENVALE 2109 | 82952109 | 2.47 |  |  |  | 2.47
EDENVALE 2110 | 82952110 | 0 |  |  |  | 0
EDENVALE 2112 | 82952112 | 1.33 |  |  |  | 1.33
EDENVALE 2113 | 82952113 | 2.42 |  | 0.02 |  | 2.4
EDES 1101 | 13681101 | 8.54 |  |  |  | 8.54
EDES 1103 | 13681103 | 12.44 |  |  |  | 12.44
EDES 1105 | 13681105 | 3.78 |  |  |  | 3.78
EDES 1110 | 13681110 | 7.49 |  |  |  | 7.49
EDES 1111 | 13681111 | 4.22 |  |  |  | 4.22
EDES 1112 | 13681112 | 17.11 | 0.58 | 14.67 |  | 1.86
EDES 1113 | 13681113 | 4.47 |  |  |  | 4.47
EDES 1114 | 13681114 | 10.4 |  |  |  | 10.4
EEL RIVER 1102 | 192381102 | 144.59 |  | 40.02 |  | 104.57
EEL RIVER 1103 | 192381103 | 59.35 |  | 3.2 |  | 56.15
EIGHT MILE 2101 | 163912101 | 72.61 |  |  |  | 72.61
EIGHT MILE 2102 | 163912102 | 29.37 |  |  |  | 29.37
EIGHT MILE 2103 | 163912103 | 0 |  |  |  | 0
EIGHT MILE 2104 | 163912104 | 1.36 |  |  |  | 1.36
EIGHT MILE 2105 | 163912105 | 0.49 |  |  |  | 0.49
EIGHT MILE 2106 | 163912106 | 30.16 |  |  |  | 30.16
EL CAPITAN 0004 | 253880004 | 0.01 |  |  |  | 0.01
EL CAPITAN 1102 | 253881102 | 16.59 |  |  |  | 16.59
EL CAPITAN 1103 | 253881103 | 69.97 |  |  |  | 69.97
EL CAPITAN 1104 | 253881104 | 47.15 |  |  |  | 47.15
EL CAPITAN 1105 | 253881105 | 4.84 |  |  |  | 4.84
EL CAPITAN 1106 | 253881106 | 14.32 |  |  |  | 14.32
EL CAPITAN 2109 | 253882109 | 4.48 |  |  |  | 4.48
EL CAPITAN 2110 | 253882110 | 14.69 |  |  |  | 14.69
EL CERRITO G 1101 | 12501101 | 10.12 |  |  |  | 10.12
EL CERRITO G 1102 | 12501102 | 7.8 |  |  |  | 7.8
EL CERRITO G 1103 | 12501103 | 9.05 |  |  |  | 9.05
EL CERRITO G 1104 | 12501104 | 7.85 |  |  |  | 7.85
EL CERRITO G 1105 | 12501105 | 31.68 | 5.58 | 18.89 |  | 7.21
EL CERRITO G 1106 | 12501106 | 4.65 |  |  |  | 4.65
EL CERRITO G 1107 | 12501107 | 3.59 |  |  |  | 3.59
EL CERRITO G 1108 | 12501108 | 14.41 |  | 0 |  | 14.41
EL CERRITO G 1109 | 12501109 | 8 |  |  |  | 8
EL CERRITO G 1110 | 12501110 | 10.16 |  | 0.69 |  | 9.47
EL CERRITO G 1111 | 12501111 | 12.63 |  | 0.2 |  | 12.43
EL CERRITO G 1112 | 12501112 | 24.55 | 1.65 | 0.35 |  | 22.55
EL CERRITO G 1113 | 12501113 | 11.39 |  | 0.1 |  | 11.29
EL CERRITO G 1114 | 12501114 | 6.77 |  |  |  | 6.77
EL DORADO PH 2101 | 152762101 | 138.06 | 102.15 | 25.45 | 0.73 | 9.73
EL DORADO PH 2102 | 152762102 | 33.96 | 33.96 |  |  | 0
EL NIDO 1101 | 252451101 | 57.51 |  |  |  | 57.51
EL NIDO 1102 | 252451102 | 59.45 |  |  |  | 59.45
EL NIDO 1103 | 252451103 | 59.98 |  |  |  | 59.98
EL NIDO 1104 | 252451104 | 86.58 |  |  |  | 86.58
EL PATIO 1101 | 82921101 | 0 |  |  |  | 0
EL PATIO 1102 | 82921102 | 0.98 |  |  |  | 0.98
EL PATIO 1103 | 82921103 | 13.12 |  |  |  | 13.12
EL PATIO 1104 | 82921104 | 11.87 |  |  |  | 11.87
EL PATIO 1105 | 82921105 | 6.94 |  |  |  | 6.94
EL PATIO 1107 | 82921107 | 15.62 |  |  |  | 15.62
EL PATIO 1108 | 82921108 | 6.72 |  |  |  | 6.72
EL PATIO 1109 | 82921109 | 10.55 |  |  |  | 10.55
EL PATIO 1111 | 82921111 | 0.77 |  |  |  | 0.77
EL PATIO 1112 | 82921112 | 19.44 |  |  |  | 19.44
EL PATIO 1113 | 82921113 | 4.75 |  |  |  | 4.75
EL PATIO 1114 | 82921114 | 0.6 |  |  |  | 0.6
EL PATIO 1116 | 82921116 | 8.73 |  |  |  | 8.73
EL PATIO 1117 | 82921117 | 4.17 |  |  |  | 4.17
EL PATIO 1118 | 82921118 | 10.88 |  |  |  | 10.88
EL PATIO 1119 | 82921119 | 8.25 |  |  |  | 8.25
EL PECO 1102 | 253981102 | 52.17 |  |  |  | 52.17
EL PECO 1105 | 253981105 | 101.89 |  |  |  | 101.89
EL PECO 1106 | 253981106 | 38.58 |  |  |  | 38.58
ELECTRA 1101 | 162161101 | 85.08 |  | 81.56 |  | 3.52
ELECTRA 1102 | 162161102 | 19.54 |  | 16.97 |  | 2.57
ELK 1101 | 42981101 | 106.63 |  | 73.18 |  | 33.45
ELK CREEK 1101 | 102781101 | 172.65 |  | 79.1 |  | 93.55
ELK HILLS 1104 | 252441104 | 57.39 |  |  |  | 57.39
ELK HILLS 1106 | 252441106 | 21.37 |  |  |  | 21.37
EMBARCADERO (Z) 1112 | 22871112 | 0 |  |  |  | 0
EMBARCADERO (Z) 1113 | 22871113 | 0.32 |  |  |  | 0.32
EMBARCADERO (Z) 1114 | 22871114 | 0 |  |  |  | 0
EMBARCADERO (Z) 1115 | 22871115 | 0.24 |  |  |  | 0.24
EMBARCADERO (Z) 1116 | 22871116 | 1.05 |  |  |  | 1.05
EMBARCADERO (Z) 1118 | 22871118 | 0.08 |  |  |  | 0.08
EMBARCADERO (Z) 1120 | 22871120 | 0.32 |  |  |  | 0.32
EMBARCADERO (Z) 1122 | 22871122 | 0.01 |  |  |  | 0.01
EMBARCADERO (Z) 1123 | 22871123 | 0.36 |  |  |  | 0.36
EMERALD LAKE 0401 | 24080401 | 13.09 | 2.09 | 6.87 |  | 4.13
EMERALD LAKE 0402 | 24080402 | 6.56 |  | 6.56 |  | 0
ERTA 0403 | 83510403 | 2.98 |  |  |  | 2.98
ERTA 0404 | 83510404 | 6.52 |  |  |  | 6.52
ESQUON 1101 | 102171101 | 69.97 |  |  |  | 69.97
ESQUON 1102 | 102171102 | 50.49 |  |  |  | 50.49
ESQUON 1103 | 102171103 | 20.35 |  |  |  | 20.35
ESTUDILLO 0401 | 13480401 | 4.74 |  | 0.79 |  | 3.95
EUREKA A 1103 | 192121103 | 10.42 |  |  |  | 10.42
EUREKA A 1106 | 192121106 | 1.81 |  |  |  | 1.81
EUREKA A 1107 | 192121107 | 4.5 |  |  |  | 4.5
EUREKA E 1101 | 192331101 | 13.29 |  |  |  | 13.29
EUREKA E 1104 | 192331104 | 26.88 |  | 0.03 |  | 26.85
EUREKA E 1105 | 192331105 | 7.24 |  |  |  | 7.24
EVERGREEN 2101 | 82012101 | 2.53 |  |  |  | 2.53
EVERGREEN 2102 | 82012102 | 10.73 |  |  |  | 10.73
EVERGREEN 2103 | 82012103 | 19.17 |  |  |  | 19.17
EVERGREEN 2104 | 82012104 | 3.54 |  |  |  | 3.54
EVERGREEN 2105 | 82012105 | 4.63 |  |  |  | 4.63
FAIRHAVEN 1103 | 192451103 | 9.43 |  |  |  | 9.43
FAIRHAVEN 1104 | 192451104 | 3.32 |  |  |  | 3.32
FAIRMOUNT 0401 | 12650401 | 5.6 |  | 1.33 |  | 4.27
FAIRMOUNT 0402 | 12650402 | 5.07 |  |  |  | 5.07
FAIRVIEW 2206 | 13432206 | 14.25 |  |  |  | 14.25
FAIRVIEW 2207 | 13432207 | 50.47 |  | 20.92 |  | 29.55
FAIRVIEW 2208 | 13432208 | 10 |  |  |  | 10
FAIRWAY 1103 | 182061103 | 6.79 |  |  |  | 6.79
FAIRWAY 1104 | 182061104 | 22.91 |  |  |  | 22.91
FAIRWAY 1106 | 182061106 | 5.5 |  |  |  | 5.5
FAIRWAY 1107 | 182061107 | 19 |  |  |  | 19
FAIRWAY 1108 | 182061108 | 11.41 |  |  |  | 11.41
FAMOSO 1101 | 252461101 | 39.07 |  |  |  | 39.07
FAMOSO 1102 | 252461102 | 27.37 |  |  |  | 27.37
FAMOSO 1103 | 252461103 | 32.96 |  |  |  | 32.96
FAMOSO 1105 | 252461105 | 10.04 |  |  |  | 10.04
FAMOSO 1107 | 252461107 | 18.81 |  |  |  | 18.81
FELLOWS 2103 | 254242103 | 26.76 |  |  |  | 26.76
FELLOWS 2104 | 254242104 | 77.9 |  |  |  | 77.9
FIGARDEN 2102 | 254552102 | 23.69 |  |  |  | 23.69
FIGARDEN 2103 | 254552103 | 5.48 |  |  |  | 5.48
FIGARDEN 2104 | 254552104 | 1.81 |  |  |  | 1.81
FIGARDEN 2105 | 254552105 | 12.63 |  |  |  | 12.63
FIGARDEN 2107 | 254552107 | 5.43 |  |  |  | 5.43
FIGARDEN 2108 | 254552108 | 4.96 |  |  |  | 4.96
FIGARDEN 2109 | 254552109 | 3.9 |  |  |  | 3.9
FIGARDEN 2110 | 254552110 | 15.8 |  |  |  | 15.8
FIGARDEN 2111 | 254552111 | 4.81 |  |  |  | 4.81
FIGARDEN 2112 | 254552112 | 31.03 |  |  |  | 31.03
FIGARDEN 2113 | 254552113 | 11.42 |  |  |  | 11.42
FIREBAUGH 1101 | 253471101 | 92.25 |  |  |  | 92.25
FIREBAUGH 1102 | 253471102 | 52.69 |  |  |  | 52.69
FIREBAUGH 1103 | 253471103 | 75.36 |  |  |  | 75.36
FITCH MOUNTAIN 1111 | 42751111 | 30.49 |  | 0.29 |  | 30.2
FITCH MOUNTAIN 1112 | 42751112 | 0.01 |  |  |  | 0.01
FITCH MOUNTAIN 1113 | 42751113 | 145.6 | 30.76 | 46.39 |  | 68.45
FLINT 1101 | 152531101 | 18.33 |  | 6.33 |  | 12
FLINT 1102 | 152531102 | 0.12 |  | 0.12 |  | 0
FLORENCE 0401 | 12690401 | 4.28 |  | 0.82 |  | 3.46
FMC 1105 | 83871105 | 16.57 |  |  |  | 16.57
FMC 1108 | 83871108 | 1.35 |  |  |  | 1.35
FMC 1109 | 83871109 | 1.02 |  |  |  | 1.02
FMC 1111 | 83871111 | 1.56 |  |  |  | 1.56
FOOTHILL 1101 | 182951101 | 39.49 |  | 18.83 |  | 20.66
FOOTHILL 1102 | 182951102 | 18.11 |  | 8.48 |  | 9.63
FORESTHILL 1101 | 152181101 | 64.53 | 64.48 | 0.05 |  | 0
FORESTHILL 1102 | 152181102 | 29.48 | 21.71 | 7.77 |  | 0
FORT BRAGG A 1101 | 42761101 | 81.06 |  | 70.39 |  | 10.67
FORT BRAGG A 1102 | 42761102 | 81.62 |  | 66.03 |  | 15.59
FORT BRAGG A 1103 | 42761103 | 2.71 |  | 0.07 |  | 2.64
FORT BRAGG A 1104 | 42761104 | 38.88 |  | 24.89 |  | 13.99
FORT ORD 1101 | 182401101 | 16.86 |  |  |  | 16.86
FORT ORD 2105 | 182402105 | 7.39 |  |  |  | 7.39
FORT ORD 2106 | 182402106 | 24.22 |  | 2.2 |  | 22.02
FORT ORD 2107 | 182402107 | 19.41 |  | 3.78 |  | 15.63
FORT ORD 2108 | 182402108 | 0.9 |  |  |  | 0.9
FORT ROSS 1121 | 42851121 | 93.69 | 21.97 | 70.01 |  | 1.71
FORT SEWARD 1121 | 192321121 | 48.08 |  | 36.14 |  | 11.94
FORT SEWARD 1122 | 192321122 | 21.83 |  | 17.43 |  | 4.4
FRANKLIN 1101 | 13921101 | 9.2 |  | 1.27 |  | 7.93
FRANKLIN 1102 | 13921102 | 4.41 |  |  |  | 4.41
FRANKLIN 1103 | 13921103 | 12.4 |  |  |  | 12.4
FRANKLIN 1104 | 13921104 | 14.67 |  | 7.41 |  | 7.26
FREMONT 1103 | 14351103 | 4.37 |  |  |  | 4.37
FREMONT 1104 | 14351104 | 21.61 |  | 1.08 |  | 20.53
FREMONT 1107 | 14351107 | 15.13 |  |  |  | 15.13
FREMONT 1108 | 14351108 | 4.88 |  |  |  | 4.88
FREMONT 1109 | 14351109 | 13.63 |  |  |  | 13.63
FREMONT 1110 | 14351110 | 10.36 |  |  |  | 10.36
FREMONT 1112 | 14351112 | 0.18 |  |  |  | 0.18
FRENCH CAMP 1101 | 163291101 | 15.5 |  |  |  | 15.5
FRENCH CAMP 1102 | 163291102 | 87 |  |  |  | 87
FRENCH CAMP 1103 | 163291103 | 1.23 |  |  |  | 1.23
FRENCH CAMP 1104 | 163291104 | 5.61 |  |  |  | 5.61
FRENCH GULCH 1101 | 103381101 | 15.98 |  | 15.98 |  | 0
FRENCH GULCH 1102 | 103381102 | 18.73 |  | 18.63 |  | 0.1
FROGTOWN 1701 | 163451701 | 71.73 | 6.65 | 63.84 |  | 1.24
FROGTOWN 1702 | 163451702 | 230.42 |  | 205 |  | 25.42
FRUITLAND 1141 | 192311141 | 26.4 |  | 23.43 |  | 2.97
FRUITLAND 1142 | 192311142 | 67.15 |  | 57.05 | 0.03 | 10.07
FRUITVALE 1101 | 253391101 | 3.34 |  |  |  | 3.34
FRUITVALE 1103 | 253391103 | 12.63 |  |  |  | 12.63
FRUITVALE 1104 | 253391104 | 11.22 |  |  |  | 11.22
FRUITVALE 1105 | 253391105 | 3.41 |  |  |  | 3.41
FRUITVALE 1106 | 253391106 | 9.5 |  |  |  | 9.5
FRUITVALE 1108 | 253391108 | 9.13 |  |  |  | 9.13
FULTON 1101 | 42561101 | 6.7 |  |  |  | 6.7
FULTON 1102 | 42561102 | 61.63 | 1.64 | 26.31 |  | 33.68
FULTON 1103 | 42561103 | 0.01 |  |  |  | 0.01
FULTON 1104 | 42561104 | 8.47 |  | 0.41 |  | 8.06
FULTON 1105 | 42561105 | 41.6 |  |  |  | 41.6
FULTON 1106 | 42561106 | 4.89 |  |  |  | 4.89
FULTON 1107 | 42561107 | 48.31 | 35.17 | 0.01 |  | 13.13
GABILAN 1101 | 182331101 | 72.7 |  | 4.55 |  | 68.15
GABILAN 1102 | 182331102 | 9.77 |  |  |  | 9.77
GALLO 1101 | 254901101 | 0.72 |  |  |  | 0.72
GALLO 1102 | 254901102 | 0.08 |  |  |  | 0.08
GANSNER 1101 | 103021101 | 44.06 | 3 | 30.42 |  | 10.64
GANSO 1103 | 254541103 | 39.42 |  |  |  | 39.42
GANSO 1104 | 254541104 | 37.38 |  |  |  | 37.38
GARBERVILLE 1101 | 192221101 | 161.52 |  | 82.19 |  | 79.33
GARBERVILLE 1102 | 192221102 | 136.61 |  | 122.01 |  | 14.6
GARBERVILLE 1103 | 192221103 | 2.24 |  | 0.48 |  | 1.76
GARCIA 0401 | 43040401 | 2.46 |  | 2.46 |  | 0
GARDNER 0401 | 254930401 | 0.02 |  |  |  | 0.02
GATES 1101 | 253931101 | 15.24 |  |  |  | 15.24
GATES 1102 | 253931102 | 41.79 |  |  |  | 41.79
GATES 1104 | 253931104 | 25.54 |  |  |  | 25.54
GATES 1105 | 253931105 | 39.31 |  |  |  | 39.31
GATES 1106 | 253931106 | 44.6 |  |  |  | 44.6
GATES 1107 | 253931107 | 2.52 |  |  |  | 2.52
GATES 1108 | 253931108 | 2.57 |  |  |  | 2.57
GATES 1109 | 253931109 | 0.3 |  |  |  | 0.3
GATES 1110 | 253931110 | 43.24 |  |  |  | 43.24
GERBER 1101 | 103391101 | 40 |  |  |  | 40
GERBER 1102 | 103391102 | 85.04 |  |  |  | 85.04
GEYSERVILLE 1101 | 42891101 | 138.39 |  | 70.28 |  | 68.11
GEYSERVILLE 1102 | 42891102 | 118.66 | 20.31 | 33.86 |  | 64.49
GIFFEN 1102 | 253151102 | 41.33 |  |  |  | 41.33
GIFFEN 1103 | 253151103 | 50.44 |  |  |  | 50.44
GIFFEN 1106 | 253151106 | 2.17 |  |  |  | 2.17
GIFFEN 1107 | 253151107 | 2.65 |  |  |  | 2.65
GILL 0401 | 13550401 | 3.25 |  |  |  | 3.25
GILL 0402 | 13550402 | 3.92 |  |  |  | 3.92
GIRVAN 1101 | 103401101 | 106.5 | 42.25 | 58.87 |  | 5.38
GIRVAN 1102 | 103401102 | 76.13 | 33.58 | 10.82 |  | 31.73
GLENN 1101 | 102601101 | 137.02 |  | 0.26 |  | 136.76
GLENWOOD 0404 | 24090404 | 6.06 |  |  |  | 6.06
GLENWOOD 0405 | 24090405 | 5.74 |  |  |  | 5.74
GLENWOOD 0406 | 24090406 | 2.31 |  |  |  | 2.31
GLENWOOD 1101 | 24091101 | 5.42 |  |  |  | 5.42
GLENWOOD 1102 | 24091102 | 7.17 |  |  |  | 7.17
GOLDTREE 1105 | 182581105 | 14.64 |  | 6.84 |  | 7.8
GOLDTREE 1107 | 182581107 | 3.53 |  | 0.94 |  | 2.59
GOLDTREE 1108 | 182581108 | 21.57 |  | 3.45 |  | 18.12
GONZALES 1101 | 182131101 | 25.94 |  | 3.89 |  | 22.05
GONZALES 1102 | 182131102 | 0.72 |  |  |  | 0.72
GONZALES 1103 | 182131103 | 6.69 |  |  |  | 6.69
GONZALES 1104 | 182131104 | 54.29 |  | 0.74 |  | 53.55
GOOSE LAKE 1101 | 254201101 | 0.54 |  |  |  | 0.54
GOOSE LAKE 1103 | 254201103 | 74.16 |  |  |  | 74.16
GOOSE LAKE 1106 | 254201106 | 66.48 |  |  |  | 66.48
GOOSE LAKE 2104 | 254202104 | 47.72 |  |  |  | 47.72
GRAND ISLAND 2223 | 62462223 | 96.76 |  |  |  | 96.76
GRAND ISLAND 2224 | 62462224 | 63.62 |  |  |  | 63.62
GRAND ISLAND 2225 | 62462225 | 65.18 |  |  |  | 65.18
GRAND ISLAND 2226 | 62462226 | 20.89 |  |  |  | 20.89
GRAND ISLAND 2227 | 62462227 | 157.79 |  |  |  | 157.79
GRANT 1102 | 14381102 | 4.42 |  |  |  | 4.42
GRANT 1103 | 14381103 | 4.19 |  |  |  | 4.19
GRANT 1104 | 14381104 | 19.29 |  |  |  | 19.29
GRANT 1105 | 14381105 | 13.96 |  |  |  | 13.96
GRANT 1106 | 14381106 | 17.02 |  |  |  | 17.02
GRANT 1107 | 14381107 | 5.37 |  |  |  | 5.37
GRANT 1108 | 14381108 | 22.69 |  |  |  | 22.69
GRASS VALLEY 1101 | 152031101 | 18.82 | 2.31 | 13.78 |  | 2.73
GRASS VALLEY 1102 | 152031102 | 5.79 |  | 0.06 |  | 5.73
GRASS VALLEY 1103 | 152031103 | 87.67 |  | 86.04 |  | 1.63
GRAYS FLAT 0401 | 102530401 | 10.63 |  | 10.63 |  | 0
GREEN VALLEY 2101 | 83192101 | 155.9 | 32.68 | 7.64 |  | 115.58
GREEN VALLEY 2102 | 83192102 | 45.84 |  |  |  | 45.84
GREEN VALLEY 2103 | 83192103 | 68.74 |  |  |  | 68.74
GREEN VALLEY 2104 | 83192104 | 30.18 |  |  |  | 30.18
GREENBRAE 1101 | 43091101 | 1.82 |  |  |  | 1.82
GREENBRAE 1102 | 43091102 | 13.42 | 5.73 |  |  | 7.69
GREENBRAE 1103 | 43091103 | 7.41 |  | 0.75 |  | 6.66
GREENBRAE 1104 | 43091104 | 18.38 |  | 0.18 |  | 18.2
GUALALA 1111 | 42841111 | 37.83 |  | 33.18 |  | 4.65
GUALALA 1112 | 42841112 | 47.39 |  | 42.92 |  | 4.47
GUERNSEY 1101 | 252661101 | 43.38 |  |  |  | 43.38
GUERNSEY 1102 | 252661102 | 41.59 |  |  |  | 41.59
GUERNSEY 1103 | 252661103 | 31.65 |  |  |  | 31.65
GUERNSEY 1104 | 252661104 | 29.96 |  |  |  | 29.96
GUERNSEY 1105 | 252661105 | 2.17 |  |  |  | 2.17
GUERNSEY 1106 | 252661106 | 36.97 |  |  |  | 36.97
GUERNSEY 1108 | 252661108 | 2.17 |  |  |  | 2.17
GUSTINE 1101 | 163111101 | 79.66 |  |  |  | 79.66
GUSTINE 1102 | 163111102 | 137.4 |  |  |  | 137.4
HALF MOON BAY 1101 | 24101101 | 47.06 | 12.56 | 12.37 |  | 22.13
HALF MOON BAY 1102 | 24101102 | 48.04 | 5.57 | 2.86 |  | 39.61
HALF MOON BAY 1103 | 24101103 | 166.4 | 1.42 | 122.3 |  | 42.68
HALSEY 1101 | 152241101 | 68.69 |  | 68.69 |  | 0
HALSEY 1102 | 152241102 | 59.63 |  | 49.36 |  | 10.27
HAMILTON A 1101 | 102121101 | 37.39 |  |  |  | 37.39
HAMILTON A 1102 | 102121102 | 43.6 |  |  |  | 43.6
HAMILTON BRANCH 1101 | 102361101 | 34.47 |  | 24.32 |  | 10.15
HAMMER 1101 | 163301101 | 5.5 |  |  |  | 5.5
HAMMER 1102 | 163301102 | 2.76 |  |  |  | 2.76
HAMMER 1103 | 163301103 | 3.75 |  |  |  | 3.75
HAMMER 1104 | 163301104 | 10.64 |  |  |  | 10.64
HAMMER 1105 | 163301105 | 10.83 |  |  |  | 10.83
HAMMER 1106 | 163301106 | 7.23 |  |  |  | 7.23
HAMMER 1108 | 163301108 | 6.01 |  |  |  | 6.01
HAMMER 1109 | 163301109 | 3.85 |  |  |  | 3.85
HAMMONDS 1101 | 253401101 | 35.11 |  |  |  | 35.11
HAMMONDS 1102 | 253401102 | 44.27 |  |  |  | 44.27
HAMMONDS 1104 | 253401104 | 66.3 |  |  |  | 66.3
HARDING 0401 | 163310401 | 1.01 |  |  |  | 1.01
HARDING 0402 | 163310402 | 3.86 |  |  |  | 3.86
HARDING 0403 | 163310403 | 1.54 |  |  |  | 1.54
HARDING 0404 | 163310404 | 2.7 |  |  |  | 2.7
HARDING 0405 | 163310405 | 2.9 |  |  |  | 2.9
HARDING 0406 | 163310406 | 3.16 |  |  |  | 3.16
HARDWICK 1101 | 253711101 | 71.93 |  |  |  | 71.93
HARDWICK 1102 | 253711102 | 97.84 |  |  |  | 97.84
HARRIS 1108 | 192431108 | 32.62 |  | 1.71 |  | 30.91
HARRIS 1109 | 192431109 | 49.85 |  | 14.29 |  | 35.56
HARTER 1102 | 152851102 | 4.39 |  |  |  | 4.39
HARTER 1104 | 152851104 | 7.24 |  |  |  | 7.24
HARTER 1105 | 152851105 | 23.51 |  |  |  | 23.51
HARTER 1106 | 152851106 | 2.12 |  |  |  | 2.12
HARTER 1107 | 152851107 | 10.23 |  |  |  | 10.23
HARTLEY 1101 | 43211101 | 72.18 |  | 34.7 |  | 37.48
HARTLEY 1102 | 43211102 | 27.56 |  | 4.06 |  | 23.5
HATTON 1101 | 182291101 | 32.97 | 2.67 | 17.71 |  | 12.59
HATTON 1102 | 182291102 | 22.45 |  | 11.39 |  | 11.06
HAYWARD O 0401 | 12240401 | 3.3 |  |  |  | 3.3
HAYWARD O 0402 | 12240402 | 3.71 |  |  |  | 3.71
HENRIETTA 1104 | 252681104 | 36 |  |  |  | 36
HENRIETTA 1106 | 252681106 | 45.91 |  |  |  | 45.91
HENRIETTA 1108 | 252681108 | 22.66 |  |  |  | 22.66
HENRIETTA 1110 | 252681110 | 86.11 |  |  |  | 86.11
HERDLYN 1102 | 163741102 | 76.17 |  |  |  | 76.17
HERDLYN 1103 | 163741103 | 99.21 |  |  |  | 99.21
HICKS 1108 | 83431108 | 12.13 |  |  |  | 12.13
HICKS 1109 | 83431109 | 14.97 |  |  |  | 14.97
HICKS 1110 | 83431110 | 8 |  |  |  | 8
HICKS 1111 | 83431111 | 21.87 |  |  |  | 21.87
HICKS 1112 | 83431112 | 4.43 |  |  |  | 4.43
HICKS 1113 | 83431113 | 19.24 |  |  |  | 19.24
HICKS 1114 | 83431114 | 9.51 |  |  |  | 9.51
HICKS 1115 | 83431115 | 15.41 |  | 0.05 |  | 15.36
HICKS 1116 | 83431116 | 34.25 |  | 13.95 |  | 20.3
HICKS 2101 | 83432101 | 42.38 | 2.24 | 10.16 |  | 29.98
HICKS 2102 | 83432102 | 3.9 |  |  |  | 3.9
HICKS 2103 | 83432103 | 21.55 | 5.28 | 2.09 |  | 14.18
HICKS 2105 | 83432105 | 9.68 |  |  |  | 9.68
HICKS 2111 | 83432111 | 4.57 |  |  |  | 4.57
HIGGINS 1103 | 152691103 | 148.33 |  | 143.51 |  | 4.82
HIGGINS 1104 | 152691104 | 87.96 |  | 72.5 |  | 15.46
HIGGINS 1107 | 152691107 | 32.53 |  | 17.87 |  | 14.66
HIGGINS 1108 | 152691108 | 0.02 |  |  |  | 0.02
HIGGINS 1109 | 152691109 | 86.65 |  | 82.85 |  | 3.8
HIGGINS 1110 | 152691110 | 57.25 |  | 48.9 |  | 8.35
HIGHLANDS 1101 | 43361101 | 0.03 |  | 0.03 |  | 0
HIGHLANDS 1102 | 43361102 | 64.29 | 10.7 | 29.29 |  | 24.3
HIGHLANDS 1103 | 43361103 | 123.89 |  | 110.34 |  | 13.55
HIGHLANDS 1104 | 43361104 | 29.23 |  | 11.91 |  | 17.32
HIGHWAY 1101 | 42651101 | 11.19 |  |  |  | 11.19
HIGHWAY 1102 | 42651102 | 19.88 |  |  |  | 19.88
HIGHWAY 1103 | 42651103 | 6.3 |  |  |  | 6.3
HIGHWAY 1104 | 42651104 | 9.56 |  |  |  | 9.56
HIGHWAY 1105 | 42651105 | 1.04 |  |  |  | 1.04
HIGHWAY 1106 | 42651106 | 15.26 |  |  |  | 15.26
HILLSDALE 0401 | 24110401 | 7.46 |  |  |  | 7.46
HILLSDALE 0402 | 24110402 | 8.02 |  |  |  | 8.02
HILLSDALE 0403 | 24110403 | 3.27 |  |  |  | 3.27
HILLSDALE 0404 | 24110404 | 5.69 |  |  |  | 5.69
HILLSDALE 0405 | 24110405 | 5.9 |  |  |  | 5.9
HOLLISTER 2101 | 182492101 | 25.56 |  |  |  | 25.56
HOLLISTER 2102 | 182492102 | 108.31 |  | 27.73 |  | 80.58
HOLLISTER 2103 | 182492103 | 13.55 |  |  |  | 13.55
HOLLISTER 2104 | 182492104 | 122.85 |  | 6.34 |  | 116.51
HOLLISTER 2105 | 182492105 | 164.92 |  | 64.36 |  | 100.56
HOLLISTER 2106 | 182492106 | 39.29 |  | 8.09 |  | 31.2
HOLLYWOOD 0401 | 13170401 | 5.36 |  | 2.78 |  | 2.58
HONCUT 1101 | 103211101 | 115.13 |  |  |  | 115.13
HONCUT 1102 | 103211102 | 149.07 |  | 2.57 |  | 146.5
HOOPA 1101 | 192401101 | 136.98 | 4.88 | 99.7 |  | 32.4
HOPLAND 1101 | 42251101 | 130.72 |  | 81.59 |  | 49.13
HORSESHOE 1101 | 152571101 | 36.25 |  | 4.93 |  | 31.32
HORSESHOE 1102 | 152571102 | 14.83 |  |  |  | 14.83
HORSESHOE 1103 | 152571103 | 5.24 |  |  |  | 5.24
HORSESHOE 1104 | 152571104 | 11.65 |  | 1.97 |  | 9.68
HORSESHOE 1105 | 152571105 | 2.27 |  |  |  | 2.27
HORSESHOE 1106 | 152571106 | 15.3 |  |  |  | 15.3
HUMBOLDT BAY 1101 | 192341101 | 12.9 |  |  |  | 12.9
HUMBOLDT BAY 1102 | 192341102 | 41.57 |  | 6.33 |  | 35.24
HUNTERS POINT (P) 1101 | 22331101 | 3.73 |  |  |  | 3.73
HUNTERS POINT (P) 1102 | 22331102 | 8.28 |  |  |  | 8.28
HUNTERS POINT (P) 1103 | 22331103 | 5.78 |  |  |  | 5.78
HUNTERS POINT (P) 1104 | 22331104 | 3.62 |  |  |  | 3.62
HUNTERS POINT (P) 1105 | 22331105 | 10.4 |  |  |  | 10.4
HUNTERS POINT (P) 1106 | 22331106 | 1.53 |  |  |  | 1.53
HUNTERS POINT (P) 1107 | 22331107 | 5.26 |  |  |  | 5.26
HUNTERS POINT (P) 1108 | 22331108 | 5.72 |  |  |  | 5.72
HUNTERS POINT (P) 1109 | 22331109 | 1.61 |  |  |  | 1.61
HURON 1106 | 253161106 | 17.05 |  |  |  | 17.05
HURON 1107 | 253161107 | 0.34 |  |  |  | 0.34
HURON 1108 | 253161108 | 10.15 |  |  |  | 10.15
HURON 1109 | 253161109 | 0.34 |  |  |  | 0.34
HURON 1112 | 253161112 | 13.8 |  |  |  | 13.8
HURON 1116 | 253161116 | 19.73 |  |  |  | 19.73
IGNACIO 1101 | 42481101 | 11.63 | 0.5 | 5.72 |  | 5.41
IGNACIO 1102 | 42481102 | 8.52 |  |  |  | 8.52
IGNACIO 1103 | 42481103 | 2.77 |  | 0.62 |  | 2.15
IGNACIO 1104 | 42481104 | 57.17 |  | 6.33 |  | 50.84
IGNACIO 1105 | 42481105 | 20.2 |  | 4.75 |  | 15.45
INDIAN FLAT 1104 | 252691104 | 16.12 |  | 16.12 |  | 0
INDUSTRIAL ACRES 0411 | 182300411 | 2.02 |  |  |  | 2.02
INDUSTRIAL ACRES 0412 | 182300412 | 9.79 |  |  |  | 9.79
INDUSTRIAL ACRES 0413 | 182300413 | 3.71 |  |  |  | 3.71
INDUSTRIAL ACRES 0415 | 182300415 | 1.43 |  |  |  | 1.43
IONE 1101 | 163881101 | 28.99 |  | 14.89 |  | 14.1
JACINTO 1101 | 102851101 | 77.3 |  |  |  | 77.3
JACINTO 1102 | 102851102 | 80.77 |  |  |  | 80.77
JACOBS CORNER 1101 | 254771101 | 62.36 |  |  |  | 62.36
JACOBS CORNER 1102 | 254771102 | 51.45 |  |  |  | 51.45
JAMESON 1101 | 63801101 | 0.01 |  |  |  | 0.01
JAMESON 1102 | 63801102 | 20.16 |  | 8 |  | 12.16
JAMESON 1103 | 63801103 | 10.84 |  | 2.19 |  | 8.65
JAMESON 1104 | 63801104 | 0.08 |  |  |  | 0.08
JAMESON 1105 | 63801105 | 63.85 |  | 16.19 |  | 47.66
JANES CREEK 1101 | 192391101 | 29.32 |  |  |  | 29.32
JANES CREEK 1102 | 192391102 | 6.26 |  |  |  | 6.26
JANES CREEK 1103 | 192391103 | 42.51 |  |  |  | 42.51
JANES CREEK 1104 | 192391104 | 2.57 |  |  |  | 2.57
JARVIS 1101 | 13501101 | 13.72 |  | 0.58 |  | 13.14
JARVIS 1103 | 13501103 | 3.42 |  |  |  | 3.42
JARVIS 1104 | 13501104 | 4.42 |  |  |  | 4.42
JARVIS 1105 | 13501105 | 6.84 |  |  |  | 6.84
JARVIS 1106 | 13501106 | 4.78 |  |  |  | 4.78
JARVIS 1108 | 13501108 | 17.68 |  | 0.7 |  | 16.98
JARVIS 1109 | 13501109 | 4.15 |  |  |  | 4.15
JARVIS 1110 | 13501110 | 5.96 |  |  |  | 5.96
JARVIS 1111 | 13501111 | 18.99 | 0.91 | 0.03 |  | 18.05
JARVIS 1112 | 13501112 | 7.24 |  |  |  | 7.24
JERSEY ISLAND 0401 | 18320401 | 2.88 |  |  |  | 2.88
JESSUP 1101 | 103441101 | 79.63 | 0.2 | 63.69 |  | 15.74
JESSUP 1102 | 103441102 | 86.62 |  | 53.34 |  | 33.28
JESSUP 1103 | 103441103 | 38.12 |  | 3.92 |  | 34.2
JOLON 1102 | 182981102 | 105.89 |  | 65.47 |  | 40.42
JOLON 1103 | 182981103 | 18.57 |  | 12.51 |  | 6.06
JUDAH 0401 | 22400401 | 3.69 |  |  |  | 3.69
JUDAH 0402 | 22400402 | 2.14 |  |  |  | 2.14
KANAKA 1101 | 103221101 | 72.46 | 45.63 | 26.47 |  | 0.36
KEARNEY 1104 | 252701104 | 73.13 |  |  |  | 73.13
KEARNEY 1106 | 252701106 | 39.27 |  |  |  | 39.27
KEARNEY 1110 | 252701110 | 50.46 |  |  |  | 50.46
KEARNEY 1113 | 252701113 | 0.63 |  |  |  | 0.63
KEARNEY 1114 | 252701114 | 13.36 |  |  |  | 13.36
KERCKHOFF 1101 | 252561101 | 34.21 |  | 34.21 |  | 0
KERMAN 1101 | 252711101 | 145.36 |  |  |  | 145.36
KERMAN 1102 | 252711102 | 58.45 |  |  |  | 58.45
KERMAN 1103 | 252711103 | 56.38 |  |  |  | 56.38
KERMAN 1104 | 252711104 | 65.97 |  |  |  | 65.97
KERMAN 1106 | 252711106 | 75.66 |  |  |  | 75.66
KERMAN 1108 | 252711108 | 28.11 |  |  |  | 28.11
KERN OIL 1103 | 252721103 | 11.39 |  |  |  | 11.39
KERN OIL 1104 | 252721104 | 39.14 |  |  |  | 39.14
KERN OIL 1106 | 252721106 | 44.03 |  | 1.31 |  | 42.72
KERN OIL 1107 | 252721107 | 21.16 |  |  |  | 21.16
KERN OIL 1108 | 252721108 | 7.69 |  |  |  | 7.69
KERN OIL 1109 | 252721109 | 11.24 |  |  |  | 11.24
KERN OIL 1110 | 252721110 | 8.55 |  |  |  | 8.55
KERN OIL 1112 | 252721112 | 0.07 |  |  |  | 0.07
KERN OIL 1114 | 252721114 | 21.52 |  |  |  | 21.52
KERN OIL 1116 | 252721116 | 4.59 |  |  |  | 4.59
KERN POWER 2101 | 255262101 | 1.99 |  |  |  | 1.99
KERN POWER 2102 | 255262102 | 4.35 |  |  |  | 4.35
KERN POWER 2103 | 255262103 | 12.51 |  |  |  | 12.51
KERN POWER 2104 | 255262104 | 5.06 |  |  |  | 5.06
KERN POWER 2105 | 255262105 | 12.54 |  |  |  | 12.54
KESWICK 1101 | 103451101 | 51.27 | 47.91 | 3.31 |  | 0.05
KETTLEMAN HILLS 1101 | 252731101 | 38.7 |  |  |  | 38.7
KETTLEMAN HILLS 2104 | 252732104 | 34.6 |  |  |  | 34.6
KING CITY 1101 | 182031101 | 6.91 |  |  |  | 6.91
KING CITY 1102 | 182031102 | 21.54 |  |  |  | 21.54
KING CITY 1103 | 182031103 | 27.78 |  | 17.75 |  | 10.03
KING CITY 1104 | 182031104 | 14.02 |  |  |  | 14.02
KING CITY 1105 | 182031105 | 3.09 |  |  |  | 3.09
KING CITY 1106 | 182031106 | 71.72 |  |  |  | 71.72
KING CITY 1107 | 182031107 | 0.02 |  |  |  | 0.02
KING CITY 1108 | 182031108 | 0.02 |  |  |  | 0.02
KINGSBURG 1102 | 252241102 | 15.54 |  |  |  | 15.54
KINGSBURG 1108 | 252241108 | 41.31 |  |  |  | 41.31
KINGSBURG 1110 | 252241110 | 86.22 |  |  |  | 86.22
KINGSBURG 1111 | 252241111 | 81.82 |  |  |  | 81.82
KINGSBURG 1112 | 252241112 | 14.15 |  |  |  | 14.15
KINGSBURG 1113 | 252241113 | 51.34 |  |  |  | 51.34
KINGSBURG 1114 | 252241114 | 18.59 |  |  |  | 18.59
KINGSBURG 1116 | 252241116 | 113.79 |  |  |  | 113.79
KIRKER 2103 | 14452103 | 8.01 |  |  |  | 8.01
KIRKER 2104 | 14452104 | 17.21 |  | 4.01 |  | 13.2
KIRKER 2105 | 14452105 | 9.31 |  |  |  | 9.31
KIRKER 2106 | 14452106 | 16.23 |  |  |  | 16.23
KIRKER 2107 | 14452107 | 8.05 |  |  |  | 8.05
KIRKER 2108 | 14452108 | 9.57 |  |  |  | 9.57
KIRKER 2109 | 14452109 | 8.62 |  |  |  | 8.62
KNIGHTS LANDING 1101 | 62721101 | 45.1 |  |  |  | 45.1
KNIGHTS LANDING 1102 | 62721102 | 118.89 |  |  |  | 118.89
KONOCTI 1102 | 43311102 | 145.87 | 64.06 | 61.13 |  | 20.68
KONOCTI 1108 | 43311108 | 33.04 |  | 20.4 |  | 12.64
LAKEVIEW 1102 | 253411102 | 52.33 |  |  |  | 52.33
LAKEVIEW 1103 | 253411103 | 22.68 |  |  |  | 22.68
LAKEVIEW 1106 | 253411106 | 36.9 |  |  |  | 36.9
LAKEVIEW 1107 | 253411107 | 26.06 |  |  |  | 26.06
LAKEVILLE 1101 | 43371101 | 19.67 |  |  |  | 19.67
LAKEVILLE 1102 | 43371102 | 50.36 | 0.07 | 18.06 |  | 32.23
LAKEVILLE 1105 | 43371105 | 4.22 |  |  |  | 4.22
LAKEWOOD 1101 | 13531101 | 0.72 |  |  |  | 0.72
LAKEWOOD 1102 | 13531102 | 9.57 |  | 0.1 |  | 9.47
LAKEWOOD 1103 | 13531103 | 2.57 |  |  |  | 2.57
LAKEWOOD 1104 | 13531104 | 11.74 |  |  |  | 11.74
LAKEWOOD 2107 | 13532107 | 33.31 |  | 7.77 |  | 25.54
LAKEWOOD 2108 | 13532108 | 0.53 |  |  |  | 0.53
LAKEWOOD 2109 | 13532109 | 7.27 | 0.42 |  |  | 6.85
LAKEWOOD 2110 | 13532110 | 22.68 |  |  |  | 22.68
LAKEWOOD 2111 | 13532111 | 2.29 |  |  |  | 2.29
LAKEWOOD 2112 | 13532112 | 8.9 |  |  |  | 8.9
LAKEWOOD 2223 | 13532223 | 9.13 |  |  |  | 9.13
LAKEWOOD 2224 | 13532224 | 31.47 | 0.82 |  |  | 30.65
LAKEWOOD 2225 | 13532225 | 3.34 |  |  |  | 3.34
LAKEWOOD 2226 | 13532226 | 8 |  |  |  | 8
LAKEWOOD 2227 | 13532227 | 7.89 | 0.03 |  |  | 7.86
LAMMERS 1101 | 162771101 | 9.67 |  |  |  | 9.67
LAMMERS 1102 | 162771102 | 3.55 |  |  |  | 3.55
LAMMERS 1103 | 162771103 | 9.36 |  |  |  | 9.36
LAMMERS 1105 | 162771105 | 1.79 |  |  |  | 1.79
LAMMERS 1106 | 162771106 | 2.29 |  |  |  | 2.29
LAMMERS 1107 | 162771107 | 9.14 |  |  |  | 9.14
LAMMERS 1108 | 162771108 | 1.11 |  |  |  | 1.11
LAMONT 1102 | 253911102 | 69.13 |  | 3.49 |  | 65.64
LAMONT 1103 | 253911103 | 26.85 |  |  |  | 26.85
LAMONT 1104 | 253911104 | 53.32 |  | 1.43 |  | 51.89
LAMONT 1105 | 253911105 | 37.1 |  |  |  | 37.1
LAMONT 1106 | 253911106 | 22.49 |  |  |  | 22.49
LAMONT 1107 | 253911107 | 46.12 |  |  |  | 46.12
LARKIN (Y) 1107 | 22801107 | 2.36 |  |  |  | 2.36
LARKIN (Y) 1108 | 22801108 | 0.11 |  |  |  | 0.11
LARKIN (Y) 1109 | 22801109 | 0.3 |  |  |  | 0.3
LARKIN (Y) 1110 | 22801110 | 0.99 |  |  |  | 0.99
LARKIN (Y) 1111 | 22801111 | 0.12 |  |  |  | 0.12
LARKIN (Y) 1119 | 22801119 | 1.72 |  |  |  | 1.72
LARKIN (Y) 1120 | 22801120 | 2.1 |  |  |  | 2.1
LARKIN (Y) 1127 | 22801127 | 1.53 |  |  |  | 1.53
LARKIN (Y) 1128 | 22801128 | 0.11 |  |  |  | 0.11
LARKIN (Y) 1135 | 22801135 | 1.65 |  |  |  | 1.65
LARKIN (Y) 1136 | 22801136 | 1.29 |  |  |  | 1.29
LARKIN (Y) 1137 | 22801137 | 0.01 |  |  |  | 0.01
LARKIN (Y) 1138 | 22801138 | 1.48 |  |  |  | 1.48
LARKIN (Y) 1140 | 22801140 | 0.08 |  |  |  | 0.08
LARKIN (Y) 1141 | 22801141 | 0.03 |  |  |  | 0.03
LAS GALLINAS A 1103 | 42991103 | 5.28 |  |  |  | 5.28
LAS GALLINAS A 1104 | 42991104 | 12.95 |  | 0.28 |  | 12.67
LAS GALLINAS A 1105 | 42991105 | 21.48 | 8.41 | 2.85 |  | 10.22
LAS GALLINAS A 1106 | 42991106 | 15.83 | 0.02 | 1.16 |  | 14.65
LAS GALLINAS A 1107 | 42991107 | 8.05 |  | 0.02 |  | 8.03
LAS PALMAS 1101 | 254921101 | 0.27 |  |  |  | 0.27
LAS POSITAS 2103 | 14402103 | 2.99 |  |  |  | 2.99
LAS POSITAS 2104 | 14402104 | 11.37 |  |  |  | 11.37
LAS POSITAS 2105 | 14402105 | 3.76 |  |  |  | 3.76
LAS POSITAS 2106 | 14402106 | 16.19 |  |  |  | 16.19
LAS POSITAS 2107 | 14402107 | 11.24 |  |  |  | 11.24
LAS POSITAS 2108 | 14402108 | 19.96 |  | 6.85 |  | 13.11
LAS POSITAS 2109 | 14402109 | 13.26 |  |  |  | 13.26
LAS POSITAS 2110 | 14402110 | 19.65 |  |  |  | 19.65
LAS PULGAS 0401 | 24120401 | 8.88 |  | 1.97 |  | 6.91
LAS PULGAS 0402 | 24120402 | 2.57 |  |  |  | 2.57
LAS PULGAS 0403 | 24120403 | 7.84 |  |  |  | 7.84
LAS PULGAS 0404 | 24120404 | 4.05 |  |  |  | 4.05
LATHROP 0402 | 163030402 | 0.04 |  |  |  | 0.04
LAURELES 1111 | 182371111 | 106.2 | 5.72 | 99.39 |  | 1.09
LAURELES 1112 | 182371112 | 43.16 |  | 33.05 |  | 10.11
LAWNDALE 0401 | 22440401 | 4.73 |  |  |  | 4.73
LAWNDALE 0402 | 22440402 | 4.75 |  |  |  | 4.75
LAWRENCE 1102 | 83421102 | 0.08 |  |  |  | 0.08
LAWRENCE 1103 | 83421103 | 0.23 |  |  |  | 0.23
LAWRENCE 1104 | 83421104 | 9.34 |  |  |  | 9.34
LAWRENCE 1105 | 83421105 | 1.07 |  |  |  | 1.07
LAWRENCE 1106 | 83421106 | 2.77 |  |  |  | 2.77
LAWRENCE 1107 | 83421107 | 4.63 |  |  |  | 4.63
LAWRENCE 1108 | 83421108 | 0.86 |  |  |  | 0.86
LAWRENCE 1109 | 83421109 | 1.96 |  |  |  | 1.96
LAWRENCE 1110 | 83421110 | 4.92 |  |  |  | 4.92
LAWRENCE 1111 | 83421111 | 3.71 |  |  |  | 3.71
LAWRENCE 1112 | 83421112 | 11.06 |  |  |  | 11.06
LAWRENCE 1113 | 83421113 | 5.65 |  |  |  | 5.65
LAYTONVILLE 1101 | 42681101 | 79.53 |  | 51.72 |  | 27.81
LAYTONVILLE 1102 | 42681102 | 125.38 | 3.39 | 107.15 |  | 14.84
LE GRAND 1104 | 255361104 | 56.91 |  |  |  | 56.91
LE GRAND 1106 | 255361106 | 59.89 |  |  |  | 59.89
LE GRAND 1110 | 255361110 | 91.79 |  |  |  | 91.79
LE GRAND 1112 | 255361112 | 68.74 |  |  |  | 68.74
LEMOORE 1101 | 253601101 | 41.55 |  |  |  | 41.55
LEMOORE 1102 | 253601102 | 11.54 |  |  |  | 11.54
LEMOORE 1103 | 253601103 | 14.43 |  |  |  | 14.43
LEMOORE 1104 | 253601104 | 49.88 |  |  |  | 49.88
LEMOORE 1105 | 253601105 | 12.03 |  |  |  | 12.03
LERDO 1110 | 253491110 | 11.91 |  |  |  | 11.91
LERDO 1111 | 253491111 | 36.22 |  |  |  | 36.22
LERDO 1112 | 253491112 | 23.94 |  |  |  | 23.94
LERDO 1113 | 253491113 | 38.51 |  |  |  | 38.51
LERDO 1114 | 253491114 | 9.9 |  |  |  | 9.9
LERDO 1115 | 253491115 | 15.88 |  |  |  | 15.88
LERDO 1116 | 253491116 | 42.26 |  |  |  | 42.26
LINCOLN 1101 | 153701101 | 50.24 |  | 16.09 |  | 34.15
LINCOLN 1102 | 153701102 | 9.58 |  |  |  | 9.58
LINCOLN 1104 | 153701104 | 136.5 |  | 33.43 |  | 103.07
LINCOLN 1105 | 153701105 | 32.24 |  |  |  | 32.24
LINCOLN 2108 | 153702108 | 1.63 |  |  |  | 1.63
LINCOLN 2109 | 153702109 | 0.86 |  |  |  | 0.86
LINDEN 1101 | 162071101 | 34.75 |  |  |  | 34.75
LINDEN 1103 | 162071103 | 60.06 |  |  |  | 60.06
LINDEN 1104 | 162071104 | 56 |  |  |  | 56
LIVE OAK 1101 | 153771101 | 28.43 |  |  |  | 28.43
LIVE OAK 1102 | 153771102 | 25.68 |  |  |  | 25.68
LIVE OAK 1104 | 153771104 | 112.27 |  |  |  | 112.27
LIVERMORE 1101 | 12141101 | 6.04 |  |  |  | 6.04
LIVERMORE 1102 | 12141102 | 4.22 |  |  |  | 4.22
LIVERMORE 1103 | 12141103 | 4.61 |  |  |  | 4.61
LIVERMORE 1104 | 12141104 | 8.63 |  |  |  | 8.63
LIVINGSTON 1101 | 252261101 | 103.25 |  |  |  | 103.25
LIVINGSTON 1102 | 252261102 | 13.62 |  |  |  | 13.62
LIVINGSTON 1104 | 252261104 | 50.61 |  |  |  | 50.61
LIVINGSTON 1105 | 252261105 | 88.76 |  |  |  | 88.76
LIVINGSTON 1106 | 252261106 | 55.35 |  |  |  | 55.35
LLAGAS 2101 | 83182101 | 101.98 |  | 21.37 |  | 80.61
LLAGAS 2102 | 83182102 | 12.63 |  |  |  | 12.63
LLAGAS 2103 | 83182103 | 16.71 |  |  |  | 16.71
LLAGAS 2104 | 83182104 | 30.02 |  | 2.68 |  | 27.34
LLAGAS 2105 | 83182105 | 17.55 | 0.12 | 0.46 |  | 16.97
LLAGAS 2106 | 83182106 | 32.26 |  | 1.18 |  | 31.08
LLAGAS 2107 | 83182107 | 22.28 | 3.63 | 2.64 |  | 16.01
LOCKEFORD 2101 | 163682101 | 90.85 |  |  |  | 90.85
LOCKEFORD 2102 | 163682102 | 242.45 |  |  |  | 242.45
LOCKHEED NO 2 1103 | 83001103 | 0.52 |  |  |  | 0.52
LOCKHEED NO 2 1106 | 83001106 | 0.37 |  |  |  | 0.37
LOCKHEED NO 2 1107 | 83001107 | 0.77 |  |  |  | 0.77
LOCKHEED NO 2 1108 | 83001108 | 1.25 |  |  |  | 1.25
LODI 1101 | 162111101 | 44.39 |  |  |  | 44.39
LODI 1102 | 162111102 | 97.07 |  |  |  | 97.07
LOGAN CREEK 2101 | 103142101 | 163.28 |  |  |  | 163.28
LOGAN CREEK 2102 | 103142102 | 240.91 |  | 3.48 |  | 237.43
LOGAN CREEK 2103 | 103142103 | 3.17 |  |  |  | 3.17
LOGAN CREEK 2199 | 103142199 | 0.03 |  |  |  | 0.03
LONE TREE 2101 | 13232101 | 1.15 |  |  |  | 1.15
LONE TREE 2102 | 13232102 | 16.62 |  |  |  | 16.62
LONE TREE 2105 | 13232105 | 21.8 |  | 10.71 |  | 11.09
LOS ALTOS 1103 | 82241103 | 6.79 |  |  |  | 6.79
LOS ALTOS 1104 | 82241104 | 12.93 |  |  |  | 12.93
LOS ALTOS 1105 | 82241105 | 1.81 |  |  |  | 1.81
LOS ALTOS 1106 | 82241106 | 9.93 |  |  |  | 9.93
LOS ALTOS 1107 | 82241107 | 2.96 |  |  |  | 2.96
LOS COCHES 1101 | 182151101 | 24.47 |  | 2.29 |  | 22.18
LOS COCHES 1102 | 182151102 | 28.95 |  |  |  | 28.95
LOS GATOS 1101 | 82021101 | 20.95 |  | 11.8 |  | 9.15
LOS GATOS 1102 | 82021102 | 6.1 |  | 1.1 |  | 5
LOS GATOS 1106 | 82021106 | 70.61 | 67.35 | 2.43 |  | 0.83
LOS GATOS 1107 | 82021107 | 93.96 | 80.52 | 12.66 |  | 0.78
LOS GATOS 1108 | 82021108 | 6.17 | 1.13 | 3.28 |  | 1.76
LOS MOLINOS 1101 | 103481101 | 55.79 |  | 0.19 |  | 55.6
LOS MOLINOS 1102 | 103481102 | 49.36 |  |  |  | 49.36
LOS OSITOS 2101 | 182082101 | 33.71 |  |  |  | 33.71
LOS OSITOS 2102 | 182082102 | 51.57 |  | 2.48 |  | 49.09
LOS OSITOS 2103 | 182082103 | 177.64 |  | 44.31 |  | 133.33
LOST HILLS 1101 | 254281101 | 0.01 |  |  |  | 0.01
LOW GAP 1101 | 192411101 | 72.3 |  | 70.59 |  | 1.71
LOYOLA 0401 | 82160401 | 8.28 |  |  |  | 8.28
LOYOLA 0403 | 82160403 | 8.84 |  |  |  | 8.84
LOYOLA 1101 | 82161101 | 19.35 |  |  |  | 19.35
LOYOLA 1102 | 82161102 | 50.86 |  | 0.02 |  | 50.84
LUCERNE 1103 | 43351103 | 52.89 |  | 26.64 |  | 26.25
LUCERNE 1106 | 43351106 | 47.64 |  | 36.79 |  | 10.85
MABURY 1101 | 82191101 | 4.18 |  |  |  | 4.18
MABURY 1103 | 82191103 | 7.89 |  |  |  | 7.89
MABURY 1104 | 82191104 | 13.71 |  |  |  | 13.71
MABURY 1105 | 82191105 | 0.85 |  |  |  | 0.85
MABURY 1106 | 82191106 | 15.05 |  |  |  | 15.05
MADERA 1102 | 252761102 | 0.02 |  |  |  | 0.02
MADERA 1104 | 252761104 | 14.64 |  |  |  | 14.64
MADERA 1106 | 252761106 | 8.71 |  |  |  | 8.71
MADERA 1112 | 252761112 | 12.27 |  |  |  | 12.27
MADERA 1114 | 252761114 | 9.68 |  |  |  | 9.68
MADERA 1116 | 252761116 | 2.89 |  |  |  | 2.89
MADERA 1118 | 252761118 | 9.02 |  |  |  | 9.02
MADERA 1119 | 252761119 | 126.08 |  |  |  | 126.08
MADISON 1103 | 63171103 | 72.69 |  |  |  | 72.69
MADISON 1105 | 63171105 | 84.8 |  | 0.35 |  | 84.45
MADISON 2101 | 63172101 | 166.84 |  | 5.25 |  | 161.59
MAGUNDEN 1101 | 252771101 | 19.48 |  |  |  | 19.48
MAGUNDEN 1104 | 252771104 | 5.18 |  |  |  | 5.18
MAGUNDEN 1105 | 252771105 | 13.72 |  |  |  | 13.72
MAGUNDEN 1106 | 252771106 | 16.02 |  |  |  | 16.02
MAGUNDEN 1108 | 252771108 | 30.66 |  | 3.93 |  | 26.73
MAGUNDEN 2108 | 252772108 | 45.23 |  |  |  | 45.23
MAGUNDEN 2109 | 252772109 | 14.41 |  |  |  | 14.41
MAINE PRAIRIE 0401 | 68670401 | 0.06 |  |  |  | 0.06
MALAGA 1101 | 254251101 | 3.55 |  |  |  | 3.55
MALAGA 1102 | 254251102 | 55.39 |  |  |  | 55.39
MALAGA 1103 | 254251103 | 20.18 |  |  |  | 20.18
MALAGA 1104 | 254251104 | 15.37 |  |  |  | 15.37
MALAGA 1105 | 254251105 | 0.64 |  |  |  | 0.64
MALAGA 1106 | 254251106 | 9.25 |  |  |  | 9.25
MALAGA 1107 | 254251107 | 2.65 |  |  |  | 2.65
MALAGA 1108 | 254251108 | 20.04 |  |  |  | 20.04
MALAGA 1109 | 254251109 | 3.31 |  |  |  | 3.31
MALAGA 1110 | 254251110 | 15.38 |  |  |  | 15.38
MALAGA 1111 | 254251111 | 8.89 |  |  |  | 8.89
MANCHESTER 1101 | 253921101 | 11.83 |  |  |  | 11.83
MANCHESTER 1102 | 253921102 | 13.62 |  |  |  | 13.62
MANCHESTER 1103 | 253921103 | 7.17 |  |  |  | 7.17
MANCHESTER 1104 | 253921104 | 3.97 |  |  |  | 3.97
MANCHESTER 1105 | 253921105 | 9.04 |  |  |  | 9.04
MANCHESTER 1106 | 253921106 | 14.91 |  |  |  | 14.91
MANCHESTER 1107 | 253921107 | 8.68 |  |  |  | 8.68
MANCHESTER 1108 | 253921108 | 14.64 |  |  |  | 14.64
MANCHESTER 1109 | 253921109 | 15.79 |  |  |  | 15.79
MANCHESTER 1110 | 253921110 | 14.46 |  |  |  | 14.46
MANCHESTER 1111 | 253921111 | 14.44 |  |  |  | 14.44
MANCHESTER 1112 | 253921112 | 15.95 |  |  |  | 15.95
MANTECA 1701 | 162611701 | 6.15 |  |  |  | 6.15
MANTECA 1702 | 162611702 | 14.06 |  |  |  | 14.06
MANTECA 1703 | 162611703 | 15.7 |  |  |  | 15.7
MANTECA 1704 | 162611704 | 7.55 |  |  |  | 7.55
MANTECA 1705 | 162611705 | 34.85 |  |  |  | 34.85
MANTECA 1706 | 162611706 | 7.49 |  |  |  | 7.49
MANTECA 1707 | 162611707 | 7.94 |  |  |  | 7.94
MANTECA 1708 | 162611708 | 9.7 |  |  |  | 9.7
MAPLE 0401 | 13520401 | 3.66 |  |  |  | 3.66
MAPLE CREEK 1101 | 192101101 | 32.8 |  | 9.28 |  | 23.52
MARICOPA 1101 | 254211101 | 38.36 |  |  |  | 38.36
MARICOPA 1102 | 254211102 | 37.75 |  |  |  | 37.75
MARINA (F) 0401 | 22780401 | 0.53 |  |  |  | 0.53
MARINA (F) 0402 | 22780402 | 0.48 |  |  |  | 0.48
MARINA (F) 0403 | 22780403 | 0.04 |  |  |  | 0.04
MARINA (F) 0404 | 22780404 | 0.37 |  |  |  | 0.37
MARINA (F) 0405 | 22780405 | 0.14 |  |  |  | 0.14
MARINA (F) 0407 | 22780407 | 1.42 |  |  |  | 1.42
MARINA (F) 0408 | 22780408 | 0.52 |  |  |  | 0.52
MARINA (F) 1101 | 22781101 | 0 |  |  |  | 0
MARINA (F) 1102 | 22781102 | 0 |  |  |  | 0
MARINA (F) 1103 | 22781103 | 0.2 |  |  |  | 0.2
MARIPOSA 2101 | 254452101 | 257.85 | 75.47 | 177.45 |  | 4.93
MARIPOSA 2102 | 254452102 | 257.9 | 56.8 | 188.16 |  | 12.94
MARIPOSA REMOTE 0001 | 257010001 | 0.01 |  | 0.01 |  | 0
MARTELL 1101 | 163011101 | 82.53 |  | 70.23 |  | 12.3
MARTELL 1102 | 163011102 | 12.11 |  | 6.88 |  | 5.23
MARTELL 1103 | 163011103 | 29.39 |  | 20.31 |  | 9.08
MARYSVILLE 1102 | 152011102 | 7.44 |  |  |  | 7.44
MARYSVILLE 1103 | 152011103 | 12.03 |  |  |  | 12.03
MARYSVILLE 1104 | 152011104 | 5.54 |  |  |  | 5.54
MARYSVILLE 1105 | 152011105 | 8.6 |  |  |  | 8.6
MARYSVILLE 1106 | 152011106 | 3.53 |  |  |  | 3.53
MARYSVILLE 1107 | 152011107 | 8.52 |  |  |  | 8.52
MARYSVILLE 1108 | 152011108 | 51.56 |  |  |  | 51.56
MAXWELL 1102 | 62881102 | 60.09 |  |  |  | 60.09
MAXWELL 1105 | 62881105 | 88.64 |  | 3.9 |  | 84.74
MAXWELL 1106 | 62881106 | 29.6 |  |  |  | 29.6
MC ARTHUR 1101 | 103491101 | 178.95 |  | 64.9 |  | 114.05
MC ARTHUR 1102 | 103491102 | 30.19 |  | 1.08 |  | 29.11
MC CALL 1101 | 254121101 | 95.02 |  |  |  | 95.02
MC CALL 1102 | 254121102 | 25.11 |  |  |  | 25.11
MC CALL 1103 | 254121103 | 17.18 |  |  |  | 17.18
MC CALL 1104 | 254121104 | 16.64 |  |  |  | 16.64
MC CALL 1105 | 254121105 | 15.14 |  |  |  | 15.14
MC CALL 1106 | 254121106 | 76.93 |  |  |  | 76.93
MC CALL 1107 | 254121107 | 100.02 |  |  |  | 100.02
MC CALL 1108 | 254121108 | 56.04 |  |  |  | 56.04
MC FARLAND 1101 | 253181101 | 14.15 |  |  |  | 14.15
MC FARLAND 1102 | 253181102 | 42.12 |  |  |  | 42.12
MC FARLAND 1104 | 253181104 | 37.95 |  |  |  | 37.95
MC FARLAND 1105 | 253181105 | 19.83 |  |  |  | 19.83
MC KEE 1103 | 83531103 | 21.98 |  | 0.58 |  | 21.4
MC KEE 1104 | 83531104 | 15.57 |  |  |  | 15.57
MC KEE 1105 | 83531105 | 8.32 |  |  |  | 8.32
MC KEE 1106 | 83531106 | 15.19 |  |  |  | 15.19
MC KEE 1107 | 83531107 | 38.03 |  | 2.68 |  | 35.35
MC KEE 1108 | 83531108 | 10.44 |  | 0.66 |  | 9.78
MC KEE 1109 | 83531109 | 1.77 |  |  |  | 1.77
MC KEE 1110 | 83531110 | 1.67 |  |  |  | 1.67
MC KEE 1111 | 83531111 | 26.63 |  | 8.7 |  | 17.93
MC KEE 1112 | 83531112 | 16.68 |  |  |  | 16.68
MC MULLIN 1104 | 254411104 | 62.11 |  |  |  | 62.11
MC MULLIN 1105 | 254411105 | 57.86 |  |  |  | 57.86
MC MULLIN 1106 | 254411106 | 93.72 |  |  |  | 93.72
MCKITTRICK 1101 | 252781101 | 52.72 |  |  |  | 52.72
MEADOW LANE 2102 | 14302102 | 0.01 |  |  |  | 0.01
MEADOW LANE 2103 | 14302103 | 21.46 |  |  |  | 21.46
MEADOW LANE 2104 | 14302104 | 4.17 |  |  |  | 4.17
MEADOW LANE 2105 | 14302105 | 14.37 |  |  |  | 14.37
MEADOW LANE 2106 | 14302106 | 23.43 | 0.74 | 0.11 |  | 22.58
MEADOW LANE 2107 | 14302107 | 8.44 |  |  |  | 8.44
MEADOW LANE 2108 | 14302108 | 23.89 |  |  |  | 23.89
MEADOW LANE 2109 | 14302109 | 0.58 |  |  |  | 0.58
MEADOW LANE 2110 | 14302110 | 6.57 |  |  |  | 6.57
MENDOCINO 1101 | 42951101 | 74.59 | 13.37 | 18.76 |  | 42.46
MENDOCINO 1102 | 42951102 | 0.05 |  |  |  | 0.05
MENDOTA 1101 | 252311101 | 1.61 |  |  |  | 1.61
MENDOTA 1102 | 252311102 | 103.48 |  |  |  | 103.48
MENDOTA 1103 | 252311103 | 15.79 |  |  |  | 15.79
MENDOTA 1104 | 252311104 | 62.33 |  |  |  | 62.33
MENLO 0401 | 24130401 | 6.41 |  |  |  | 6.41
MENLO 0402 | 24130402 | 7.55 |  |  |  | 7.55
MENLO 0403 | 24130403 | 8.26 |  |  |  | 8.26
MENLO 0404 | 24130404 | 8.17 |  |  |  | 8.17
MENLO 1101 | 24131101 | 1.51 |  |  |  | 1.51
MENLO 1102 | 24131102 | 63.69 | 0.01 | 28.25 |  | 35.43
MENLO 1103 | 24131103 | 56.98 |  | 39.73 |  | 17.25
MENLO 1104 | 24131104 | 16.79 |  |  |  | 16.79
MERCED 1108 | 252801108 | 69.46 |  |  |  | 69.46
MERCED 1114 | 252801114 | 58.04 |  |  |  | 58.04
MERCED 1116 | 252801116 | 77.62 |  |  |  | 77.62
MERCED 2101 | 252802101 | 29.94 |  |  |  | 29.94
MERCED 2102 | 252802102 | 25.96 |  |  |  | 25.96
MERCED FALLS 1102 | 252811102 | 153.29 |  | 93.43 |  | 59.86
MERIDIAN 1101 | 62541101 | 57.74 |  |  |  | 57.74
MERIDIAN 1102 | 62541102 | 71.9 |  |  |  | 71.9
MESA 1101 | 182821101 | 81.81 | 11.14 | 37.25 |  | 33.42
MESA 1102 | 182821102 | 3.69 |  |  |  | 3.69
MESA 1103 | 182821103 | 75.79 |  | 9.98 |  | 65.81
MESA 1104 | 182821104 | 41.29 |  |  |  | 41.29
METTLER 1109 | 163701109 | 20.37 |  |  |  | 20.37
METTLER 1110 | 163701110 | 38.04 |  |  |  | 38.04
MIDDLE RIVER 1101 | 162091101 | 31.34 |  |  |  | 31.34
MIDDLE RIVER 1102 | 162091102 | 32.09 |  |  |  | 32.09
MIDDLE RIVER 1103 | 162091103 | 28.53 |  |  |  | 28.53
MIDDLETOWN 1101 | 43141101 | 105.9 | 80.67 | 9.22 |  | 16.01
MIDDLETOWN 1102 | 43141102 | 56.08 | 0.04 | 38.32 |  | 17.72
MIDDLETOWN 1103 | 43141103 | 35.5 | 6.14 | 13.98 |  | 15.38
MIDWAY 1101 | 252611101 | 60.33 |  |  |  | 60.33
MIDWAY 1102 | 252611102 | 52.66 |  |  |  | 52.66
MIDWAY 1103 | 252611103 | 30.61 |  |  |  | 30.61
MIDWAY 1104 | 252611104 | 36.82 |  |  |  | 36.82
MILLBRAE 0401 | 22690401 | 2.82 |  |  |  | 2.82
MILLBRAE 0403 | 22690403 | 4.9 |  |  |  | 4.9
MILLBRAE 0404 | 22690404 | 7.08 |  |  |  | 7.08
MILLBRAE 1101 | 22691101 | 3.98 |  |  |  | 3.98
MILLBRAE 1102 | 22691102 | 4.76 |  |  |  | 4.76
MILLBRAE 1103 | 22691103 | 0.18 |  |  |  | 0.18
MILLBRAE 1104 | 22691104 | 15.9 |  |  |  | 15.9
MILLBRAE 1105 | 22691105 | 0.26 |  |  |  | 0.26
MILLBRAE 1106 | 22691106 | 3.71 |  |  |  | 3.71
MILLBRAE 1107 | 22691107 | 4.77 |  |  |  | 4.77
MILLBRAE 1108 | 22691108 | 14.15 |  |  |  | 14.15
MILPITAS 1101 | 82831101 | 4.1 |  |  |  | 4.1
MILPITAS 1103 | 82831103 | 0.07 |  |  |  | 0.07
MILPITAS 1104 | 82831104 | 1.04 |  |  |  | 1.04
MILPITAS 1105 | 82831105 | 4.73 |  | 0.07 |  | 4.66
MILPITAS 1106 | 82831106 | 3.14 |  |  |  | 3.14
MILPITAS 1108 | 82831108 | 13.3 |  | 0.02 |  | 13.28
MILPITAS 1109 | 82831109 | 49.48 |  | 29.94 |  | 19.54
MILPITAS 2110 | 82832110 | 10.37 |  |  |  | 10.37
MILPITAS 2111 | 82832111 | 1.8 |  |  |  | 1.8
MILPITAS 2112 | 82832112 | 0.87 |  |  |  | 0.87
MILPITAS 2113 | 82832113 | 0.12 |  |  |  | 0.12
MILPITAS 2114 | 82832114 | 0.17 |  |  |  | 0.17
MIRA VISTA 0401 | 12330401 | 8.69 |  |  |  | 8.69
MIRA VISTA 0403 | 12330403 | 7.1 |  |  |  | 7.1
MIRABEL 1101 | 42091101 | 51.35 | 19.95 | 8.95 |  | 22.45
MIRABEL 1102 | 42091102 | 57.6 | 31.89 | 4.82 |  | 20.89
MISSION (X) 0401 | 22010401 | 1.63 |  |  |  | 1.63
MISSION (X) 1102 | 22011102 | 0.17 |  |  |  | 0.17
MISSION (X) 1108 | 22011108 | 5.24 |  |  |  | 5.24
MISSION (X) 1109 | 22011109 | 1.13 |  |  |  | 1.13
MISSION (X) 1110 | 22011110 | 5.72 |  |  |  | 5.72
MISSION (X) 1113 | 22011113 | 2.63 |  |  |  | 2.63
MISSION (X) 1116 | 22011116 | 3.02 |  |  |  | 3.02
MISSION (X) 1118 | 22011118 | 0.6 |  |  |  | 0.6
MISSION (X) 1124 | 22011124 | 0.71 |  |  |  | 0.71
MISSION (X) 1125 | 22011125 | 0.97 |  |  |  | 0.97
MISSION (X) 1127 | 22011127 | 0.47 |  |  |  | 0.47
MISSION (X) 1128 | 22011128 | 0.77 |  |  |  | 0.77
MIWUK 1701 | 163661701 | 76.12 | 74.58 | 1.54 |  | 0
MIWUK 1702 | 163661702 | 74.53 | 71.89 | 2.64 |  | 0
MOLINO 1101 | 42571101 | 90.26 | 7.16 | 26.47 |  | 56.63
MOLINO 1102 | 42571102 | 161.09 | 90.1 | 19.53 |  | 51.46
MOLINO 1103 | 42571103 | 77.75 |  |  |  | 77.75
MOLINO 1104 | 42571104 | 61.22 |  | 2.38 |  | 58.84
MONARCH 0401 | 162300401 | 3.2 |  |  |  | 3.2
MONARCH 0402 | 162300402 | 2.84 |  |  |  | 2.84
MONARCH 0403 | 162300403 | 4.61 |  |  |  | 4.61
MONROE 1104 | 43301104 | 5.21 |  |  |  | 5.21
MONROE 1105 | 43301105 | 10.67 |  |  |  | 10.67
MONROE 1106 | 43301106 | 13.49 |  |  |  | 13.49
MONROE 2102 | 43302102 | 4.86 |  |  |  | 4.86
MONROE 2103 | 43302103 | 11.52 | 0.45 |  |  | 11.07
MONROE 2107 | 43302107 | 10.36 | 0.61 |  |  | 9.75
MONTAGUE 2101 | 83892101 | 0.87 |  |  |  | 0.87
MONTAGUE 2102 | 83892102 | 0.81 |  |  |  | 0.81
MONTAGUE 2103 | 83892103 | 0.94 |  |  |  | 0.94
MONTAGUE 2104 | 83892104 | 0.84 |  |  |  | 0.84
MONTAGUE 2105 | 83892105 | 0.78 |  |  |  | 0.78
MONTAGUE 2106 | 83892106 | 0 |  |  |  | 0
MONTAGUE 2108 | 83892108 | 0.93 |  |  |  | 0.93
MONTAGUE 2109 | 83892109 | 0.81 |  |  |  | 0.81
MONTE RIO 1111 | 42811111 | 63.88 | 43.76 | 13.32 |  | 6.8
MONTE RIO 1112 | 42811112 | 19.68 | 19.68 |  |  | 0
MONTE RIO 1113 | 42811113 | 61.04 | 61.04 |  |  | 0
MONTICELLO 1101 | 43051101 | 123.11 |  | 107.78 |  | 15.33
MORAGA 1101 | 13801101 | 25.72 | 16.41 | 4.79 |  | 4.52
MORAGA 1102 | 13801102 | 13.3 | 2.91 | 2.1 |  | 8.29
MORAGA 1103 | 13801103 | 17.44 | 0.12 | 2 |  | 15.32
MORAGA 1104 | 13801104 | 21.15 | 0.01 | 13.63 |  | 7.51
MORAGA 1105 | 13801105 | 19.72 | 6.87 | 0.81 |  | 12.04
MORGAN HILL 2104 | 83242104 | 20.9 |  | 5.74 |  | 15.16
MORGAN HILL 2105 | 83242105 | 82.09 | 14.1 | 35.87 |  | 32.12
MORGAN HILL 2106 | 83242106 | 39.06 |  | 0.12 |  | 38.94
MORGAN HILL 2108 | 83242108 | 13.09 |  |  |  | 13.09
MORGAN HILL 2109 | 83242109 | 26.36 |  | 2.45 |  | 23.91
MORGAN HILL 2110 | 83242110 | 32.65 |  | 2.22 |  | 30.43
MORGAN HILL 2111 | 83242111 | 72.48 | 16.46 | 35 |  | 21.02
MORMON 1101 | 163211101 | 62.42 |  |  |  | 62.42
MORMON 1102 | 163211102 | 87.99 |  |  |  | 87.99
MORMON 1103 | 163211103 | 23.44 |  |  |  | 23.44
MORRO BAY 1101 | 183011101 | 46.06 | 0.49 | 4.88 |  | 40.69
MORRO BAY 1102 | 183011102 | 57.81 | 4.03 | 17.91 |  | 35.87
MOSHER 2104 | 163722104 | 0.01 |  |  |  | 0.01
MOSHER 2107 | 163722107 | 3.13 |  |  |  | 3.13
MOSHER 2108 | 163722108 | 1.88 |  |  |  | 1.88
MOSHER 2110 | 163722110 | 2.21 |  |  |  | 2.21
MOSHER 2111 | 163722111 | 17.44 |  |  |  | 17.44
MOUNTAIN QUARRIES 2101 | 152282101 | 223.64 | 22.68 | 200 |  | 0.96
MOUNTAIN VIEW 1102 | 82031102 | 14.28 |  |  |  | 14.28
MOUNTAIN VIEW 1103 | 82031103 | 2.86 |  |  |  | 2.86
MOUNTAIN VIEW 1104 | 82031104 | 7.76 |  |  |  | 7.76
MOUNTAIN VIEW 1105 | 82031105 | 9.51 |  |  |  | 9.51
MOUNTAIN VIEW 1106 | 82031106 | 7.34 |  |  |  | 7.34
MOUNTAIN VIEW 1107 | 82031107 | 19.28 |  |  |  | 19.28
MOUNTAIN VIEW 1108 | 82031108 | 14.67 |  |  |  | 14.67
MOUNTAIN VIEW 1109 | 82031109 | 9.97 |  |  |  | 9.97
MOUNTAIN VIEW 1110 | 82031110 | 9.36 |  |  |  | 9.36
MOUNTAIN VIEW 1111 | 82031111 | 1.74 |  |  |  | 1.74
MOUNTAIN VIEW 1112 | 82031112 | 0.97 |  |  |  | 0.97
MOUNTAIN VIEW 1113 | 82031113 | 3.99 |  |  |  | 3.99
MOUNTAIN VIEW 1114 | 82031114 | 6.63 |  |  |  | 6.63
MT EDEN 1101 | 13761101 | 6.7 |  |  |  | 6.7
MT EDEN 1102 | 13761102 | 6.58 |  |  |  | 6.58
MT EDEN 1103 | 13761103 | 13.07 |  |  |  | 13.07
MT EDEN 1104 | 13761104 | 14 |  |  |  | 14
MT EDEN 1105 | 13761105 | 7.04 |  |  |  | 7.04
MT EDEN 1106 | 13761106 | 6.73 |  |  |  | 6.73
MT EDEN 1107 | 13761107 | 6.07 |  |  |  | 6.07
MT EDEN 1108 | 13761108 | 23.46 |  |  |  | 23.46
MT EDEN 1109 | 13761109 | 16.98 |  |  |  | 16.98
MT EDEN 1110 | 13761110 | 3.22 |  |  |  | 3.22
MT EDEN 1111 | 13761111 | 3.24 |  |  |  | 3.24
MT EDEN 1112 | 13761112 | 16.45 |  |  |  | 16.45
MT EDEN 1113 | 13761113 | 2.64 |  |  |  | 2.64
MT EDEN 1114 | 13761114 | 3.58 |  |  |  | 3.58
NAPA 1102 | 42021102 | 32.45 |  | 0.27 |  | 32.18
NAPA 1103 | 42021103 | 14.85 |  |  |  | 14.85
NAPA 1105 | 42021105 | 15.53 |  |  |  | 15.53
NAPA 1106 | 42021106 | 1.24 |  |  |  | 1.24
NAPA 1109 | 42021109 | 11.66 |  |  |  | 11.66
NAPA 1110 | 42021110 | 13.28 |  |  |  | 13.28
NAPA 1112 | 42021112 | 51.86 |  | 19.24 |  | 32.62
NARROWS 2101 | 153132101 | 61.45 |  | 61.45 |  | 0
NARROWS 2102 | 153132102 | 117.57 |  | 93.54 |  | 24.03
NARROWS 2104 | 153132104 | 0 |  | 0 |  | 0
NARROWS 2105 | 153132105 | 196.33 |  | 176.75 |  | 19.58
NARROWS PH 1151 | 153131151 | 0.2 |  | 0.2 |  | 0
NEW HOPE 1101 | 162081101 | 38.35 |  |  |  | 38.35
NEW HOPE 1102 | 162081102 | 50.59 |  |  |  | 50.59
NEWARK 12KV 1101 | 12221101 | 1.44 |  |  |  | 1.44
NEWARK 12KV 1102 | 12221102 | 8.4 |  |  |  | 8.4
NEWARK 12KV 1103 | 12221103 | 18.1 |  |  |  | 18.1
NEWARK 12KV 1104 | 12221104 | 0.37 |  |  |  | 0.37
NEWARK 12KV 1105 | 12221105 | 1.54 |  |  |  | 1.54
NEWARK 12KV 1106 | 12221106 | 18.36 |  |  |  | 18.36
NEWARK 12KV 1107 | 12221107 | 21.46 |  |  |  | 21.46
NEWARK 12KV 1108 | 12221108 | 0.95 |  |  |  | 0.95
NEWARK 21KV 2102 | 12232102 | 2.68 |  |  |  | 2.68
NEWARK 21KV 2103 | 12232103 | 17.79 |  |  |  | 17.79
NEWARK 21KV 2104 | 12232104 | 4.99 |  |  |  | 4.99
NEWARK 21KV 2105 | 12232105 | 2.51 |  |  |  | 2.51
NEWARK 21KV 2107 | 12232107 | 7.02 |  |  |  | 7.02
NEWARK 21KV 2108 | 12232108 | 4.82 |  |  |  | 4.82
NEWARK 21KV 2109 | 12232109 | 0 |  |  |  | 0
NEWARK 21KV 2110 | 12232110 | 3.19 |  |  |  | 3.19
NEWARK 21KV 2111 | 12232111 | 0 |  |  |  | 0
NEWBURG 1131 | 192151131 | 39.09 |  | 5.67 |  | 33.42
NEWBURG 1132 | 192151132 | 22.27 |  | 1.29 |  | 20.98
NEWBURG 1133 | 192151133 | 16.92 |  | 2.38 |  | 14.54
NEWHALL 1109 | 254461109 | 66.55 |  |  |  | 66.55
NEWHALL 1111 | 254461111 | 53.93 |  |  |  | 53.93
NEWMAN 1101 | 162741101 | 36.53 |  |  |  | 36.53
NEWMAN 1102 | 162741102 | 9.51 |  |  |  | 9.51
NEWMAN 1105 | 162741105 | 42.69 |  |  |  | 42.69
NEWMAN 1106 | 162741106 | 32.51 |  |  |  | 32.51
NORCO 1101 | 254691101 | 39.26 |  |  |  | 39.26
NORCO 1102 | 254691102 | 7.67 |  |  |  | 7.67
NORD 1103 | 103071103 | 18.51 |  |  |  | 18.51
NORD 1104 | 103071104 | 50.35 |  |  |  | 50.35
NORD 1105 | 103071105 | 6.99 |  |  |  | 6.99
NORD 1106 | 103071106 | 10.83 |  |  |  | 10.83
NORIEGA 0401 | 22510401 | 1.55 |  |  |  | 1.55
NORIEGA 0402 | 22510402 | 1.76 |  |  |  | 1.76
NORTECH 2107 | 82462107 | 0.11 |  |  |  | 0.11
NORTECH 2109 | 82462109 | 3.15 |  |  |  | 3.15
NORTECH 2110 | 82462110 | 9.47 |  |  |  | 9.47
NORTECH 2111 | 82462111 | 0.71 |  |  |  | 0.71
NORTH BRANCH 1101 | 163231101 | 88.31 |  | 62.34 |  | 25.97
NORTH DUBLIN 2101 | 14052101 | 1.87 |  | 1.4 |  | 0.47
NORTH DUBLIN 2103 | 14052103 | 21.69 |  | 18.65 |  | 3.04
NORTH TOWER 1102 | 42041102 | 18.7 |  |  |  | 18.7
NORTH TOWER 1103 | 42041103 | 13.04 |  |  |  | 13.04
NORTH TOWER 1104 | 42041104 | 19.71 |  |  |  | 19.71
NORTH TOWER 1108 | 42041108 | 13.3 |  |  |  | 13.3
NORTH TOWER 2101 | 42042101 | 4.42 |  | 0.52 |  | 3.9
NORTH TOWER 2104 | 42042104 | 4.21 |  |  |  | 4.21
NOTRE DAME 1101 | 102041101 | 1.6 |  |  |  | 1.6
NOTRE DAME 1102 | 102041102 | 10.61 |  |  |  | 10.61
NOTRE DAME 1103 | 102041103 | 7.85 |  | 0.57 |  | 7.28
NOTRE DAME 1104 | 102041104 | 35.86 | 17.95 | 9.74 |  | 8.17
NOVATO 1101 | 42211101 | 7.33 |  | 1.2 |  | 6.13
NOVATO 1102 | 42211102 | 0.59 |  |  |  | 0.59
NOVATO 1103 | 42211103 | 2.95 |  |  |  | 2.95
NOVATO 1104 | 42211104 | 24.36 |  | 3.45 |  | 20.91
OAK 0401 | 12600401 | 5.41 |  | 3.45 |  | 1.96
OAK PARK 0401 | 163270401 | 2.48 |  |  |  | 2.48
OAK PARK 0402 | 163270402 | 0.5 |  |  |  | 0.5
OAKHURST 1101 | 254421101 | 91.78 | 2.56 | 88.37 |  | 0.85
OAKHURST 1102 | 254421102 | 16.32 | 1.17 | 11.32 |  | 3.83
OAKHURST 1103 | 254421103 | 125.45 | 80.93 | 41.88 |  | 2.64
OAKLAND C 1108 | 12011108 | 2.04 |  |  |  | 2.04
OAKLAND C 1109 | 12011109 | 3.28 |  |  |  | 3.28
OAKLAND C 1110 | 12011110 | 1.25 |  |  |  | 1.25
OAKLAND C 1112 | 12011112 | 1.16 |  |  |  | 1.16
OAKLAND C 1113 | 12011113 | 3.36 |  |  |  | 3.36
OAKLAND C 1114 | 12011114 | 3.27 |  |  |  | 3.27
OAKLAND C 1115 | 12011115 | 1.24 |  |  |  | 1.24
OAKLAND C 1116 | 12011116 | 2.47 |  |  |  | 2.47
OAKLAND C 1117 | 12011117 | 2.97 |  |  |  | 2.97
OAKLAND C 1118 | 12011118 | 3.32 |  |  |  | 3.32
OAKLAND C 1119 | 12011119 | 0.43 |  |  |  | 0.43
OAKLAND C 1120 | 12011120 | 2.96 |  |  |  | 2.96
OAKLAND C 1121 | 12011121 | 1.91 |  |  |  | 1.91
OAKLAND C 1132 | 12011132 | 1.22 |  |  |  | 1.22
OAKLAND C 1133 | 12011133 | 0.03 |  |  |  | 0.03
OAKLAND C 1134 | 12011134 | 1.4 |  |  |  | 1.4
OAKLAND D 0406 | 12040406 | 3.19 |  |  |  | 3.19
OAKLAND D 0407 | 12040407 | 0.33 |  |  |  | 0.33
OAKLAND D 0408 | 12040408 | 4.08 |  |  |  | 4.08
OAKLAND D 0410 | 12040410 | 2.75 |  |  |  | 2.75
OAKLAND D 1101 | 12041101 | 0.16 |  |  |  | 0.16
OAKLAND D 1102 | 12041102 | 2.85 |  |  |  | 2.85
OAKLAND D 1103 | 12041103 | 0.34 |  |  |  | 0.34
OAKLAND D 1104 | 12041104 | 5.93 |  |  |  | 5.93
OAKLAND D 1105 | 12041105 | 8.27 |  |  |  | 8.27
OAKLAND D 1106 | 12041106 | 8.78 |  |  |  | 8.78
OAKLAND D 1107 | 12041107 | 2.51 |  |  |  | 2.51
OAKLAND D 1110 | 12041110 | 5.47 |  |  |  | 5.47
OAKLAND D 1111 | 12041111 | 7.81 |  |  |  | 7.81
OAKLAND D 1112 | 12041112 | 10.64 | 1.95 | 0.41 |  | 8.28
OAKLAND D 1115 | 12041115 | 2.74 |  |  |  | 2.74
OAKLAND D 1116 | 12041116 | 2.81 |  |  |  | 2.81
OAKLAND D 1117 | 12041117 | 0.5 |  |  |  | 0.5
OAKLAND D 1130 | 12041130 | 6.44 |  |  |  | 6.44
OAKLAND D 1131 | 12041131 | 7.74 |  |  |  | 7.74
OAKLAND D 1132 | 12041132 | 2.79 |  |  |  | 2.79
OAKLAND D 1133 | 12041133 | 2.97 |  |  |  | 2.97
OAKLAND D 1134 | 12041134 | 5.07 |  |  |  | 5.07
OAKLAND D 1202 | 12041202 | 0.24 |  |  |  | 0.24
OAKLAND I 0401 | 12080401 | 3.23 |  |  |  | 3.23
OAKLAND I 0402 | 12080402 | 5.11 |  |  |  | 5.11
OAKLAND J 0401 | 12090401 | 4.63 |  |  |  | 4.63
OAKLAND J 0403 | 12090403 | 6.3 |  |  |  | 6.3
OAKLAND J 0408 | 12090408 | 4.57 |  |  |  | 4.57
OAKLAND J 0409 | 12090409 | 3 |  |  |  | 3
OAKLAND J 1101 | 12091101 | 10.41 |  |  |  | 10.41
OAKLAND J 1102 | 12091102 | 18.3 |  | 6.01 |  | 12.29
OAKLAND J 1103 | 12091103 | 2.78 |  |  |  | 2.78
OAKLAND J 1104 | 12091104 | 6.84 |  |  |  | 6.84
OAKLAND J 1105 | 12091105 | 20.26 |  | 1.52 |  | 18.74
OAKLAND J 1106 | 12091106 | 18.02 |  | 1.89 |  | 16.13
OAKLAND J 1108 | 12091108 | 9.25 |  |  |  | 9.25
OAKLAND J 1109 | 12091109 | 0.04 |  |  |  | 0.04
OAKLAND J 1110 | 12091110 | 2.08 |  |  |  | 2.08
OAKLAND J 1111 | 12091111 | 4.67 |  |  |  | 4.67
OAKLAND J 1112 | 12091112 | 5.51 |  |  |  | 5.51
OAKLAND J 1114 | 12091114 | 0 |  |  |  | 0
OAKLAND J 1115 | 12091115 | 3.9 |  |  |  | 3.9
OAKLAND J 1116 | 12091116 | 23.48 |  | 0.48 |  | 23
OAKLAND J 1117 | 12091117 | 13.12 |  |  |  | 13.12
OAKLAND J 1118 | 12091118 | 13.87 |  | 0.31 |  | 13.56
OAKLAND K 1101 | 12101101 | 7.27 | 1.09 | 1.47 |  | 4.71
OAKLAND K 1102 | 12101102 | 14.94 | 14.94 |  |  | 0
OAKLAND K 1103 | 12101103 | 10.68 | 1.13 | 4.84 |  | 4.71
OAKLAND K 1104 | 12101104 | 14.89 | 9.56 | 5.33 |  | 0
OAKLAND L 1101 | 12111101 | 5.82 |  |  |  | 5.82
OAKLAND L 1102 | 12111102 | 1.28 |  |  |  | 1.28
OAKLAND L 1103 | 12111103 | 4.69 |  |  |  | 4.69
OAKLAND L 1105 | 12111105 | 2.48 |  |  |  | 2.48
OAKLAND L 1106 | 12111106 | 0.35 |  |  |  | 0.35
OAKLAND L 1107 | 12111107 | 1.47 |  |  |  | 1.47
OAKLAND L 1108 | 12111108 | 0 |  |  |  | 0
OAKLAND X 0401 | 12540401 | 5.5 |  |  |  | 5.5
OAKLAND X 0402 | 12540402 | 1.77 |  |  |  | 1.77
OAKLAND X 1101 | 12541101 | 5.29 |  | 0.5 |  | 4.79
OAKLAND X 1102 | 12541102 | 6.37 |  |  |  | 6.37
OAKLAND X 1103 | 12541103 | 7.68 |  |  |  | 7.68
OAKLAND X 1104 | 12541104 | 13.22 | 10.71 | 1.35 |  | 1.16
OAKLAND X 1105 | 12541105 | 19.38 |  | 2.51 |  | 16.87
OAKLAND X 1106 | 12541106 | 22.88 | 4.14 | 10.81 |  | 7.93
OAKLAND X 1107 | 12541107 | 12.92 |  |  |  | 12.92
OAKLAND X 1109 | 12541109 | 7.1 |  |  |  | 7.1
OAKLAND X 1110 | 12541110 | 0.43 |  |  |  | 0.43
OAKLAND X 1111 | 12541111 | 1.03 |  |  |  | 1.03
OAKLAND X 1112 | 12541112 | 3.93 |  |  |  | 3.93
OAKLAND X 1114 | 12541114 | 5.08 |  |  |  | 5.08
OAKLAND X 1115 | 12541115 | 12.61 |  |  |  | 12.61
OCEAN 0401 | 22580401 | 3.7 |  |  |  | 3.7
OCEAN 0402 | 22580402 | 2.96 |  |  |  | 2.96
OCEANO 1102 | 182601102 | 54.18 |  | 37.12 |  | 17.06
OCEANO 1103 | 182601103 | 11.37 |  | 1.11 |  | 10.26
OCEANO 1104 | 182601104 | 112.15 | 6.75 | 78.81 |  | 26.59
OCEANO 1105 | 182601105 | 23.59 |  | 0.66 |  | 22.93
OCEANO 1106 | 182601106 | 29.36 |  | 1.96 |  | 27.4
OCEANO 1108 | 182601108 | 11.07 |  |  |  | 11.07
OILFIELDS 1102 | 182391102 | 39.1 |  |  |  | 39.1
OILFIELDS 1103 | 182391103 | 144.71 |  | 116.94 |  | 27.77
OLD RIVER 1101 | 252821101 | 41.99 |  |  |  | 41.99
OLD RIVER 1102 | 252821102 | 49.41 |  |  |  | 49.41
OLD RIVER 1103 | 252821103 | 35.34 |  |  |  | 35.34
OLD RIVER 1104 | 252821104 | 58.21 |  |  |  | 58.21
OLD RIVER 1105 | 252821105 | 15.44 |  |  |  | 15.44
OLEMA 1101 | 42291101 | 123.11 | 15.44 | 55.47 |  | 52.2
OLETA 1101 | 163541101 | 116.76 | 4.66 | 84.68 |  | 27.42
OLETA 1102 | 163541102 | 98.63 |  | 56.04 |  | 42.59
OLIVEHURST 1101 | 152901101 | 21.81 |  |  |  | 21.81
OLIVEHURST 1102 | 152901102 | 6.02 |  |  |  | 6.02
OLIVEHURST 1103 | 152901103 | 47.14 |  |  |  | 47.14
OLIVEHURST 1104 | 152901104 | 11.38 |  |  |  | 11.38
OLIVEHURST 1105 | 152901105 | 53.94 |  |  |  | 53.94
OREGON TRAIL 1102 | 103521102 | 49.03 |  | 44.69 |  | 4.34
OREGON TRAIL 1103 | 103521103 | 112.31 |  | 109.37 |  | 2.94
OREGON TRAIL 1104 | 103521104 | 73.39 |  | 60.53 |  | 12.86
ORICK 1101 | 192261101 | 7.98 |  |  |  | 7.98
ORICK 1102 | 192261102 | 23.29 |  |  |  | 23.29
ORINDA 0401 | 12350401 | 5.37 | 0.1 | 3.37 |  | 1.9
ORINDA 0402 | 12350402 | 6.61 | 3.19 | 3.16 |  | 0.26
ORLAND B 1101 | 102701101 | 29.28 |  |  |  | 29.28
ORLAND B 1102 | 102701102 | 20.04 |  |  |  | 20.04
ORLAND B 1103 | 102701103 | 94.38 |  |  |  | 94.38
ORO FINO 1101 | 103031101 | 31.74 | 31.74 |  |  | 0
ORO FINO 1102 | 103031102 | 109.38 | 83.12 | 26.26 |  | 0
ORO LOMA 1102 | 255371102 | 1.07 |  |  |  | 1.07
ORO LOMA 1103 | 255371103 | 1.1 |  |  |  | 1.1
ORO LOMA 1106 | 255371106 | 72.81 |  |  |  | 72.81
ORO LOMA 1108 | 255371108 | 55.53 |  |  |  | 55.53
ORO LOMA 1115 | 255371115 | 73.78 |  |  |  | 73.78
ORO LOMA 1116 | 255371116 | 24.7 |  |  |  | 24.7
ORO LOMA 1117 | 255371117 | 50.2 |  |  |  | 50.2
ORO LOMA 1118 | 255371118 | 42.74 |  |  |  | 42.74
OROSI 1101 | 252841101 | 50.36 |  |  |  | 50.36
OROSI 1102 | 252841102 | 34.84 |  | 0.8 |  | 34.04
OROSI 1103 | 252841103 | 37.72 |  |  |  | 37.72
OROSI 1104 | 252841104 | 55.84 |  |  |  | 55.84
OROVILLE 0402 | 102520402 | 1.58 |  |  |  | 1.58
OROVILLE 0403 | 102520403 | 2.03 |  |  |  | 2.03
OROVILLE 1101 | 102521101 | 23.53 |  |  |  | 23.53
OROVILLE 1102 | 102521102 | 6.28 |  |  |  | 6.28
OROVILLE 1103 | 102521103 | 10.36 |  |  |  | 10.36
OROVILLE 1104 | 102521104 | 9.87 |  |  |  | 9.87
ORTIGA 1105 | 254311105 | 42.41 |  |  |  | 42.41
ORTIGA 1106 | 254311106 | 53.7 |  |  |  | 53.7
OTTER 1101 | 182941101 | 26.95 | 14.55 | 7.09 |  | 5.31
OTTER 1102 | 182941102 | 53.79 | 4.38 | 48.32 |  | 1.09
PACIFIC GROVE 0421 | 182440421 | 3.34 |  |  |  | 3.34
PACIFIC GROVE 0422 | 182440422 | 6.89 |  | 0.13 |  | 6.76
PACIFIC GROVE 0423 | 182440423 | 1.68 |  |  |  | 1.68
PACIFIC GROVE 0424 | 182440424 | 8.97 |  |  |  | 8.97
PACIFIC PIPE GRAPEVI 1101 | 255441101 | 0.02 |  |  |  | 0.02
PACIFICA 1101 | 22811101 | 9.23 | 0.07 | 0.74 |  | 8.42
PACIFICA 1102 | 22811102 | 20.1 | 1.34 | 1.38 |  | 17.38
PACIFICA 1103 | 22811103 | 14.13 | 0.19 | 0.77 |  | 13.17
PACIFICA 1104 | 22811104 | 7.18 |  | 0.7 |  | 6.48
PALMER 1101 | 183031101 | 62.6 |  | 39.46 |  | 23.14
PALO SECO 0401 | 13180401 | 4.73 |  | 4.71 |  | 0.02
PANAMA 2101 | 253422101 | 38.65 |  |  |  | 38.65
PANAMA 2102 | 253422102 | 32.89 |  |  |  | 32.89
PANOCHE 1101 | 253671101 | 24.31 |  |  |  | 24.31
PANOCHE 1102 | 253671102 | 42.59 |  |  |  | 42.59
PANOCHE 1103 | 253671103 | 122.18 |  | 44.24 |  | 77.94
PANORAMA 1101 | 103461101 | 39.18 |  | 12.98 |  | 26.2
PANORAMA 1102 | 103461102 | 84.44 |  | 29.99 |  | 54.45
PARADISE 1103 | 102831103 | 36.04 | 18.47 | 14.79 |  | 2.78
PARADISE 1104 | 102831104 | 31 | 20.97 | 1.32 |  | 8.71
PARADISE 1105 | 102831105 | 48.1 | 45.54 |  |  | 2.56
PARADISE 1106 | 102831106 | 8.84 | 8.3 |  |  | 0.54
PARKWAY 1101 | 42051101 | 7.12 |  |  |  | 7.12
PARKWAY 1102 | 42051102 | 0 |  |  |  | 0
PARKWAY 1103 | 42051103 | 6.7 |  |  |  | 6.7
PARLIER 1102 | 252291102 | 10.97 |  |  |  | 10.97
PARLIER 1103 | 252291103 | 40.84 |  |  |  | 40.84
PARLIER 1104 | 252291104 | 49.86 |  |  |  | 49.86
PARLIER 1105 | 252291105 | 21.42 |  |  |  | 21.42
PARSONS 0401 | 13660401 | 1.32 |  |  |  | 1.32
PARSONS 0402 | 13660402 | 3.43 |  |  |  | 3.43
PASO ROBLES 1101 | 182611101 | 6.57 |  |  |  | 6.57
PASO ROBLES 1102 | 182611102 | 6.41 |  |  |  | 6.41
PASO ROBLES 1103 | 182611103 | 60.48 |  | 38.53 |  | 21.95
PASO ROBLES 1104 | 182611104 | 65.55 |  | 37.15 |  | 28.4
PASO ROBLES 1106 | 182611106 | 11.46 |  |  |  | 11.46
PASO ROBLES 1107 | 182611107 | 37.7 |  | 0.26 |  | 37.44
PASO ROBLES 1108 | 182611108 | 12.43 |  |  |  | 12.43
PAUL SWEET 2101 | 83252101 | 28.44 |  |  |  | 28.44
PAUL SWEET 2102 | 83252102 | 18 | 3.7 | 0.73 |  | 13.57
PAUL SWEET 2103 | 83252103 | 16.87 |  |  |  | 16.87
PAUL SWEET 2104 | 83252104 | 38.37 | 17.2 |  |  | 21.17
PAUL SWEET 2105 | 83252105 | 40.87 | 6.8 | 0.8 |  | 33.27
PAUL SWEET 2106 | 83252106 | 51.86 | 30.65 | 5.23 |  | 15.98
PAUL SWEET 2107 | 83252107 | 49.49 | 4.04 | 4.24 |  | 41.21
PAUL SWEET 2108 | 83252108 | 20.72 |  |  |  | 20.72
PAUL SWEET 2109 | 83252109 | 23.6 | 0.85 | 2.02 |  | 20.73
PEABODY 2102 | 63642102 | 7.01 |  |  |  | 7.01
PEABODY 2104 | 63642104 | 6.76 |  |  |  | 6.76
PEABODY 2105 | 63642105 | 61.12 |  |  |  | 61.12
PEABODY 2106 | 63642106 | 1.08 |  | 0.39 |  | 0.69
PEABODY 2107 | 63642107 | 194.05 |  |  |  | 194.05
PEABODY 2108 | 63642108 | 3.02 |  | 0.34 |  | 2.68
PEABODY 2109 | 63642109 | 3.63 |  |  |  | 3.63
PEABODY 2112 | 63642112 | 3.45 |  |  |  | 3.45
PEABODY 2113 | 63642113 | 9.73 |  | 1.02 |  | 8.71
PEACHTON 1101 | 103241101 | 68.89 |  |  |  | 68.89
PEACHTON 1102 | 103241102 | 67.67 |  |  |  | 67.67
PEACHTON 1103 | 103241103 | 60.88 |  |  |  | 60.88
PEASE 1101 | 153751101 | 6.84 |  |  |  | 6.84
PEASE 1102 | 153751102 | 3.98 |  |  |  | 3.98
PEASE 1103 | 153751103 | 97.44 |  |  |  | 97.44
PEASE 1104 | 153751104 | 62.57 |  |  |  | 62.57
PEASE 1105 | 153751105 | 8.24 |  |  |  | 8.24
PENNGROVE 1101 | 43471101 | 41.73 |  | 20.09 |  | 21.64
PENRYN 1103 | 152561103 | 80.22 |  | 67.15 |  | 13.07
PENRYN 1105 | 152561105 | 91.41 |  | 33.91 |  | 57.5
PENRYN 1106 | 152561106 | 25.83 |  | 0.81 |  | 25.02
PENRYN 1107 | 152561107 | 83.96 |  | 35.97 |  | 47.99
PENTLAND 1101 | 255311101 | 0.02 |  |  |  | 0.02
PEORIA 1701 | 163781701 | 84.58 |  | 77.43 |  | 7.15
PEORIA 1704 | 163781704 | 118.03 |  | 58.71 |  | 59.32
PEORIA 1705 | 163781705 | 70.02 |  | 57.46 |  | 12.56
PERRY 1101 | 183071101 | 83.71 | 7.18 | 58.34 |  | 18.19
PETALUMA A 0411 | 42120411 | 3.06 |  |  |  | 3.06
PETALUMA A 0413 | 42120413 | 2.37 |  |  |  | 2.37
PETALUMA C 1101 | 42631101 | 0.51 |  |  |  | 0.51
PETALUMA C 1102 | 42631102 | 4.21 |  |  |  | 4.21
PETALUMA C 1105 | 42631105 | 10.67 |  |  |  | 10.67
PETALUMA C 1106 | 42631106 | 9 |  |  |  | 9
PETALUMA C 1108 | 42631108 | 118.47 |  | 75.79 |  | 42.68
PETALUMA C 1109 | 42631109 | 66.6 |  | 48.74 |  | 17.86
PETALUMA C 1110 | 42631110 | 0.25 |  |  |  | 0.25
PETROL 1101 | 252541101 | 0.03 |  |  |  | 0.03
PHILO 1101 | 42601101 | 96.11 |  | 76.49 |  | 19.62
PHILO 1102 | 42601102 | 105.92 |  | 88.3 |  | 17.62
PIERCY 2109 | 83912109 | 19.9 |  |  |  | 19.9
PIERCY 2110 | 83912110 | 27.42 |  | 19.66 |  | 7.76
PIERCY 2111 | 83912111 | 0.91 |  |  |  | 0.91
PIKE CITY 1101 | 152201101 | 34.03 | 34.03 |  |  | 0
PIKE CITY 1102 | 152201102 | 9.52 | 9.52 |  |  | 0
PINE GROVE 1101 | 163751101 | 71.79 |  | 71.79 |  | 0
PINE GROVE 1102 | 163751102 | 176.13 | 85.35 | 90.78 |  | 0
PINECREST 0401 | 163160401 | 3.15 | 1.12 | 1.95 |  | 0.08
PINEDALE 2101 | 252852101 | 1.43 |  |  |  | 1.43
PINEDALE 2102 | 252852102 | 2.76 |  |  |  | 2.76
PINEDALE 2103 | 252852103 | 1.98 |  |  |  | 1.98
PINEDALE 2105 | 252852105 | 1.76 |  |  |  | 1.76
PINEDALE 2106 | 252852106 | 5.43 |  |  |  | 5.43
PINEDALE 2107 | 252852107 | 1.59 |  |  |  | 1.59
PINEDALE 2109 | 252852109 | 7.14 |  |  |  | 7.14
PINEDALE 2110 | 252852110 | 0.19 |  |  |  | 0.19
PINEDALE 2111 | 252852111 | 0.75 |  |  |  | 0.75
PIPER BANK 0401 | 18120401 | 1.56 |  |  |  | 1.56
PIT NO 1 1101 | 103721101 | 52.88 |  | 29.54 |  | 23.34
PIT NO 3 2101 | 103732101 | 48.49 |  | 47.46 |  | 1.03
PIT NO 5 1101 | 101321101 | 23.62 |  | 23.62 |  | 0
PIT NO 7 1101 | 103501101 | 2.84 |  | 2.84 |  | 0
PITTSBURG 0401 | 12160401 | 1.04 |  |  |  | 1.04
PITTSBURG 0402 | 12160402 | 1.87 |  |  |  | 1.87
PLACER 1101 | 152461101 | 7.71 |  | 1.26 |  | 6.45
PLACER 1102 | 152461102 | 2.12 |  | 1.86 |  | 0.26
PLACER 1103 | 152461103 | 29.53 |  | 12.08 |  | 17.45
PLACER 1104 | 152461104 | 13.39 |  | 0.52 |  | 12.87
PLACERVILLE 1109 | 153081109 | 11.05 |  | 10.76 |  | 0.29
PLACERVILLE 1110 | 153081110 | 34.41 | 0.73 | 32.66 |  | 1.02
PLACERVILLE 1111 | 153081111 | 16.69 |  | 14.73 |  | 1.96
PLACERVILLE 1112 | 153081112 | 29.78 |  | 27.54 |  | 2.24
PLACERVILLE 2106 | 153082106 | 273.51 | 179.49 | 93.76 |  | 0.26
PLAINFIELD 1101 | 63441101 | 33.73 |  |  |  | 33.73
PLAINFIELD 1105 | 63441105 | 51.66 |  |  |  | 51.66
PLAINFIELD 1106 | 63441106 | 32.79 |  |  |  | 32.79
PLEASANT GROVE 2103 | 152442103 | 1.88 |  |  |  | 1.88
PLEASANT GROVE 2104 | 152442104 | 2.42 |  |  |  | 2.42
PLEASANT GROVE 2107 | 152442107 | 0.02 |  |  |  | 0.02
PLEASANT GROVE 2108 | 152442108 | 2.1 |  |  |  | 2.1
PLEASANT GROVE 2110 | 152442110 | 34.64 |  |  |  | 34.64
PLUMAS 1101 | 153731101 | 32.33 |  |  |  | 32.33
PLUMAS 1102 | 153731102 | 5.63 |  |  |  | 5.63
PLUMAS 2106 | 153732106 | 31.95 |  |  |  | 31.95
PLUMAS 2107 | 153732107 | 39.77 |  |  |  | 39.77
PLYMOUTH 0401 | 22680401 | 4.7 |  |  |  | 4.7
POINT ARENA 1101 | 43381101 | 66.15 |  | 44.25 |  | 21.9
POINT MORETTI 1101 | 82931101 | 53.94 | 29.9 | 17.32 |  | 6.72
POINT PINOLE 1101 | 14261101 | 20.99 |  |  |  | 20.99
POINT PINOLE 1102 | 14261102 | 14.06 |  |  |  | 14.06
POINT PINOLE 1103 | 14261103 | 0.01 |  |  |  | 0.01
PORTOLA 0401 | 22610401 | 2.45 |  |  |  | 2.45
PORTOLA 0402 | 22610402 | 3.5 |  |  |  | 3.5
POSO MOUNTAIN 2101 | 253642101 | 59.33 |  | 48.76 |  | 10.57
POSO MOUNTAIN 2103 | 253642103 | 20.45 |  | 18.43 |  | 2.02
POSO MOUNTAIN 2104 | 253642104 | 12.55 |  | 8.03 |  | 4.52
POTRERO PP (A) 1101 | 22031101 | 7.2 |  |  |  | 7.2
POTRERO PP (A) 1102 | 22031102 | 0.48 |  |  |  | 0.48
POTRERO PP (A) 1103 | 22031103 | 1.8 |  |  |  | 1.8
POTRERO PP (A) 1104 | 22031104 | 0.3 |  |  |  | 0.3
POTRERO PP (A) 1105 | 22031105 | 1.52 |  |  |  | 1.52
POTRERO PP (A) 1107 | 22031107 | 0.9 |  |  |  | 0.9
POTRERO PP (A) 1108 | 22031108 | 3.5 |  |  |  | 3.5
POTRERO PP (A) 1109 | 22031109 | 5.2 |  |  |  | 5.2
POTRERO PP (A) 1110 | 22031110 | 6.49 |  |  |  | 6.49
POTRERO PP (A) 1112 | 22031112 | 0.93 |  |  |  | 0.93
POTRERO PP (A) 1113 | 22031113 | 1.74 |  |  |  | 1.74
POTRERO PP (A) 1114 | 22031114 | 0.07 |  |  |  | 0.07
POTRERO PP (A) 1115 | 22031115 | 0.84 |  |  |  | 0.84
POTRERO PP (A) 1116 | 22031116 | 2.21 |  |  |  | 2.21
POTRERO PP (A) 1117 | 22031117 | 4.93 |  |  |  | 4.93
POTRERO PP (A) 1118 | 22031118 | 4.29 |  |  |  | 4.29
POTRERO PP (A) 1119 | 22031119 | 2.51 |  |  |  | 2.51
POTRERO PP (A) 1121 | 22031121 | 0.17 |  |  |  | 0.17
POTTER VALLEY P H 1104 | 42281104 | 18.84 | 0.11 | 4.57 |  | 14.16
POTTER VALLEY P H 1105 | 42281105 | 73.4 | 4.64 | 43.35 |  | 25.41
PRUNEDALE 1107 | 182961107 | 46.88 |  |  |  | 46.88
PRUNEDALE 1110 | 182961110 | 79.81 |  | 0.24 |  | 79.57
PUEBLO 1102 | 43291102 | 8.99 |  |  | 0.09 | 8.9
PUEBLO 1103 | 43291103 | 8.1 |  |  |  | 8.1
PUEBLO 1104 | 43291104 | 50.91 |  | 28.41 | 0.05 | 22.45
PUEBLO 1105 | 43291105 | 70.1 |  | 20.73 | 0.05 | 49.32
PUEBLO 2101 | 43292101 | 11.6 |  |  |  | 11.6
PUEBLO 2102 | 43292102 | 98.08 | 21.14 | 0.74 |  | 76.2
PUEBLO 2103 | 43292103 | 77.46 | 37.61 | 8.1 |  | 31.75
PURISIMA 1101 | 182971101 | 58.3 |  | 17.62 |  | 40.68
PUTAH CREEK 1102 | 63681102 | 50.82 |  | 26.6 |  | 24.22
PUTAH CREEK 1103 | 63681103 | 36.51 |  | 3.76 |  | 32.75
PUTAH CREEK 1105 | 63681105 | 83.61 |  | 1.78 |  | 81.83
RACETRACK 1703 | 163761703 | 62.12 | 1.46 | 54.53 |  | 6.13
RACETRACK 1704 | 163761704 | 45.38 |  | 45.38 |  | 0
RADUM 1101 | 13151101 | 1.62 |  |  |  | 1.62
RADUM 1102 | 13151102 | 1.15 |  |  |  | 1.15
RADUM 1105 | 13151105 | 11.8 | 1.14 | 1.9 |  | 8.76
RAINBOW 1103 | 254441103 | 16.9 |  |  |  | 16.9
RAINBOW 1105 | 254441105 | 23.72 |  |  |  | 23.72
RAINBOW 1106 | 254441106 | 122.11 |  |  |  | 122.11
RALSTON 1101 | 24141101 | 14.47 | 0.41 | 8.52 |  | 5.54
RALSTON 1102 | 24141102 | 10.74 |  | 3.77 |  | 6.97
RANCHERS COTTON 1000 | 254801000 | 0.01 |  |  |  | 0.01
RANCHERS COTTON 1101 | 254801101 | 14.12 |  |  |  | 14.12
RANDOLPH 0401 | 22590401 | 0 |  |  |  | 0
RANDOLPH 0402 | 22590402 | 1.27 |  |  |  | 1.27
RANDOLPH 0403 | 22590403 | 3.12 |  |  |  | 3.12
RAWSON 1103 | 103531103 | 39.98 |  | 2.75 |  | 37.23
RED BLUFF 1101 | 103541101 | 74.44 |  | 47.63 |  | 26.81
RED BLUFF 1102 | 103541102 | 1.48 |  |  |  | 1.48
RED BLUFF 1103 | 103541103 | 37.99 |  | 16.8 |  | 21.19
RED BLUFF 1104 | 103541104 | 93.4 |  | 66.12 |  | 27.28
RED BLUFF 1105 | 103541105 | 37.7 |  | 13.6 |  | 24.1
REDBUD 1101 | 43191101 | 66.17 | 19.24 | 21.65 |  | 25.28
REDBUD 1102 | 43191102 | 58.39 | 0.65 | 27.84 |  | 29.9
REDWOOD CITY 0402 | 24160402 | 1.25 |  |  |  | 1.25
REDWOOD CITY 0403 | 24160403 | 2.15 |  |  |  | 2.15
REDWOOD CITY 0404 | 24160404 | 1.61 |  |  |  | 1.61
REDWOOD CITY 0405 | 24160405 | 3.35 |  |  |  | 3.35
REDWOOD CITY 0406 | 24160406 | 6.58 |  |  |  | 6.58
REDWOOD CITY 0408 | 24160408 | 5.6 |  |  |  | 5.6
REDWOOD CITY 0409 | 24160409 | 4.91 |  |  |  | 4.91
REDWOOD CITY 0410 | 24160410 | 5.42 |  |  |  | 5.42
REDWOOD CITY 1101 | 24161101 | 1.94 |  |  |  | 1.94
REDWOOD CITY 1102 | 24161102 | 1.63 |  |  |  | 1.63
REDWOOD CITY 1103 | 24161103 | 1.59 |  |  |  | 1.59
REDWOOD CITY 1104 | 24161104 | 0.98 |  |  |  | 0.98
REDWOOD CITY 1105 | 24161105 | 7.26 |  |  |  | 7.26
REEDLEY 1101 | 252341101 | 26.41 |  |  |  | 26.41
REEDLEY 1104 | 252341104 | 82.43 |  | 1.69 |  | 80.74
REEDLEY 1106 | 252341106 | 123.19 |  |  |  | 123.19
REEDLEY 1110 | 252341110 | 42.16 |  |  |  | 42.16
REEDLEY 1112 | 252341112 | 89.86 |  | 0.78 |  | 89.08
RENFRO 2101 | 254572101 | 31.34 |  |  |  | 31.34
RENFRO 2102 | 254572102 | 4.41 |  |  |  | 4.41
RENFRO 2103 | 254572103 | 25.47 |  |  |  | 25.47
RENFRO 2105 | 254572105 | 10.08 |  |  |  | 10.08
RENFRO 2107 | 254572107 | 6.74 |  |  |  | 6.74
RESEARCH 2101 | 14692101 | 7.79 |  |  |  | 7.79
RESEARCH 2102 | 14692102 | 20.7 | 2.17 |  |  | 18.53
RESERVATION ROAD 1101 | 182731101 | 36.95 |  | 29.08 |  | 7.87
RESERVATION ROAD 1102 | 182731102 | 58.33 |  | 19.69 |  | 38.64
RESERVE OIL 1101 | 254181101 | 2.19 |  |  |  | 2.19
RICE 1101 | 62831101 | 53.25 |  |  |  | 53.25
RICE 1102 | 62831102 | 62.18 |  |  |  | 62.18
RICE 1103 | 62831103 | 77.94 |  |  |  | 77.94
RICE 1104 | 62831104 | 32.94 |  |  |  | 32.94
RICHMOND Q 0401 | 12520401 | 5.95 |  |  |  | 5.95
RICHMOND Q 0402 | 12520402 | 3.61 |  |  |  | 3.61
RICHMOND R 1118 | 13471118 | 2.97 |  |  |  | 2.97
RICHMOND R 1119 | 13471119 | 3.58 |  |  |  | 3.58
RICHMOND R 1120 | 13471120 | 2.97 |  |  |  | 2.97
RICHMOND R 1121 | 13471121 | 4.47 |  |  |  | 4.47
RICHMOND R 1122 | 13471122 | 3.86 |  |  |  | 3.86
RICHMOND R 1123 | 13471123 | 1.33 |  |  |  | 1.33
RICHMOND R 1124 | 13471124 | 6.75 |  |  |  | 6.75
RICHMOND R 1125 | 13471125 | 4.61 |  |  |  | 4.61
RICHMOND R 1126 | 13471126 | 13.05 |  |  |  | 13.05
RICHMOND R 1127 | 13471127 | 20.27 |  |  |  | 20.27
RICHMOND R 1128 | 13471128 | 7.55 |  |  |  | 7.55
RICHMOND R 1129 | 13471129 | 13.87 |  |  |  | 13.87
RICHMOND R 1130 | 13471130 | 15.96 |  |  |  | 15.96
RIDGE 0401 | 12840401 | 2.66 |  | 2.66 |  | 0
RIDGE 0402 | 12840402 | 2.4 |  | 1.75 |  | 0.65
RINCON 1101 | 43321101 | 38.12 | 16.46 | 5.75 |  | 15.91
RINCON 1102 | 43321102 | 19.26 | 0.01 | 2.61 |  | 16.64
RINCON 1103 | 43321103 | 47.95 | 40.61 | 4.37 |  | 2.97
RINCON 1104 | 43321104 | 11.53 | 1.92 |  |  | 9.61
RIO BRAVO 1101 | 252861101 | 20.93 |  |  |  | 20.93
RIO BRAVO 1102 | 252861102 | 36.79 |  |  |  | 36.79
RIO BRAVO 1103 | 252861103 | 26.97 |  |  |  | 26.97
RIO BRAVO 1104 | 252861104 | 8.61 |  |  |  | 8.61
RIO BRAVO 1106 | 252861106 | 62.94 |  |  |  | 62.94
RIO DELL 1101 | 192251101 | 19.46 |  |  |  | 19.46
RIO DELL 1102 | 192251102 | 73.38 |  | 49.2 | 0.76 | 23.42
RIPON 1701 | 163801701 | 64.88 |  |  |  | 64.88
RIPON 1702 | 163801702 | 24.67 |  |  |  | 24.67
RIPON 1703 | 163801703 | 83.43 |  |  |  | 83.43
RIPON 1704 | 163801704 | 9.74 |  |  |  | 9.74
RISING RIVER 1101 | 103551101 | 58.65 |  | 43.52 |  | 15.13
RIVER ROCK 1101 | 255251101 | 0.02 |  |  |  | 0.02
RIVERBANK 1711 | 163191711 | 36.14 |  |  |  | 36.14
RIVERBANK 1712 | 163191712 | 54.39 |  |  |  | 54.39
RIVERBANK 1713 | 163191713 | 54.12 |  |  |  | 54.12
RIVERBANK 1714 | 163191714 | 33.84 |  |  |  | 33.84
RIVERBANK 1715 | 163191715 | 92.48 |  |  |  | 92.48
RIVERBANK 1716 | 163191716 | 26.89 |  |  |  | 26.89
ROB ROY 2104 | 83692104 | 159.83 | 39.36 | 62.04 |  | 58.43
ROB ROY 2105 | 83692105 | 66.26 | 26.89 | 11.33 |  | 28.04
ROCKLIN 1101 | 152061101 | 4.72 |  |  |  | 4.72
ROCKLIN 1102 | 152061102 | 18.66 |  |  |  | 18.66
ROCKLIN 1103 | 152061103 | 5.11 |  |  |  | 5.11
ROCKLIN 1104 | 152061104 | 3.3 |  |  |  | 3.3
ROSEDALE 1101 | 254761101 | 12.1 |  |  |  | 12.1
ROSEDALE 2102 | 254762102 | 3.72 |  |  |  | 3.72
ROSSMOOR 1101 | 14161101 | 30.55 | 2.13 | 10.74 |  | 17.68
ROSSMOOR 1102 | 14161102 | 1.45 | 0.45 |  |  | 1
ROSSMOOR 1103 | 14161103 | 2.58 |  |  |  | 2.58
ROSSMOOR 1104 | 14161104 | 19.43 |  | 0.3 |  | 19.13
ROSSMOOR 1105 | 14161105 | 4.27 |  |  |  | 4.27
ROSSMOOR 1106 | 14161106 | 16.09 | 0.58 | 2.84 |  | 12.67
ROSSMOOR 1107 | 14161107 | 10.51 | 0.03 |  |  | 10.48
ROSSMOOR 1108 | 14161108 | 13.12 | 1.97 | 3.14 |  | 8.01
ROSSMOOR 1109 | 14161109 | 13.98 | 6.35 | 1.14 |  | 6.49
ROUGH AND READY ISLA 1102 | 163081102 | 54.28 |  |  |  | 54.28
ROUND MOUNTAIN 1101 | 109001101 | 0.02 |  | 0.02 |  | 0
RUSS RANCH 1101 | 192471101 | 0.22 |  |  |  | 0.22
RUSSELL (SMUD) 2101 | 63142101 | 5.14 |  |  |  | 5.14
RUSSELL 0401 | 13310401 | 3.41 |  |  |  | 3.41
RUSSELL 0402 | 13310402 | 3.34 |  |  |  | 3.34
SALINAS 1101 | 182011101 | 8.27 |  |  |  | 8.27
SALINAS 1102 | 182011102 | 21.22 |  |  |  | 21.22
SALINAS 1103 | 182011103 | 10.8 |  |  |  | 10.8
SALINAS 1104 | 182011104 | 31.51 |  |  |  | 31.51
SALINAS 1105 | 182011105 | 10.9 |  |  |  | 10.9
SALINAS 1106 | 182011106 | 18.61 |  |  |  | 18.61
SALINAS 1107 | 182011107 | 7.19 |  |  |  | 7.19
SALINAS 1108 | 182011108 | 2.73 |  |  |  | 2.73
SALINAS 1109 | 182011109 | 20.41 |  |  |  | 20.41
SALMON CREEK 1101 | 43161101 | 47.28 | 7.21 | 14.96 |  | 25.11
SALT SPRINGS 2101 | 163692101 | 21.96 |  | 17.07 | 1.36 | 3.53
SALT SPRINGS 2102 | 163692102 | 51.97 | 42.09 | 9.81 |  | 0.07
SAN ARDO 1101 | 182191101 | 56.61 |  | 2.67 |  | 53.94
SAN ARDO 1102 | 182191102 | 124.26 |  |  |  | 124.26
SAN BENITO 2101 | 182742101 | 48.3 |  | 4.28 |  | 44.02
SAN BENITO 2102 | 182742102 | 12.95 |  |  |  | 12.95
SAN BENITO 2103 | 182742103 | 0.59 |  |  |  | 0.59
SAN BENITO 2104 | 182742104 | 51.43 |  | 26.66 |  | 24.77
SAN BERNARD 1101 | 253191101 | 41.93 |  | 1.17 |  | 40.76
SAN BERNARD 1102 | 253191102 | 11.98 |  |  |  | 11.98
SAN BERNARD 1104 | 253191104 | 9.26 |  |  |  | 9.26
SAN BRUNO 0401 | 22700401 | 3.61 |  |  |  | 3.61
SAN BRUNO 0402 | 22700402 | 3.11 |  |  |  | 3.11
SAN BRUNO 0403 | 22700403 | 5.03 |  |  |  | 5.03
SAN CARLOS 0401 | 24180401 | 1.65 |  |  |  | 1.65
SAN CARLOS 0402 | 24180402 | 4.29 |  |  |  | 4.29
SAN CARLOS 0403 | 24180403 | 6.92 |  |  |  | 6.92
SAN CARLOS 0404 | 24180404 | 8.75 |  |  |  | 8.75
SAN CARLOS 0405 | 24180405 | 8.18 |  |  |  | 8.18
SAN CARLOS 0406 | 24180406 | 6.54 |  |  |  | 6.54
SAN CARLOS 1101 | 24181101 | 1.46 |  |  |  | 1.46
SAN CARLOS 1102 | 24181102 | 0.46 |  |  |  | 0.46
SAN CARLOS 1103 | 24181103 | 16.49 |  | 3.82 |  | 12.67
SAN CARLOS 1104 | 24181104 | 22.03 |  | 10.61 |  | 11.42
SAN JOAQUIN #2 1103 | 252521103 | 79.88 | 10.31 | 69.57 |  | 0
SAN JOAQUIN #3 1101 | 252531101 | 24.33 | 22.76 | 1.57 |  | 0
SAN JOAQUIN #3 1102 | 252531102 | 11.39 | 5.46 | 5.94 |  | -0.01
SAN JOAQUIN #3 1103 | 252531103 | 56.28 | 30.39 | 25.89 |  | 0
SAN JOAQUIN 1106 | 252361106 | 52.04 |  |  |  | 52.04
SAN JOAQUIN 1108 | 252361108 | 41.1 |  |  |  | 41.1
SAN JOAQUIN 1112 | 252361112 | 42.24 |  |  |  | 42.24
SAN JOSE A 0403 | 82250403 | 3.98 |  |  |  | 3.98
SAN JOSE A 0404 | 82250404 | 1.66 |  |  |  | 1.66
SAN JOSE A 0405 | 82250405 | 1.83 |  |  |  | 1.83
SAN JOSE A 0407 | 82250407 | 1.83 |  |  |  | 1.83
SAN JOSE A 0408 | 82250408 | 2.39 |  |  |  | 2.39
SAN JOSE A 0410 | 82250410 | 4.56 |  |  |  | 4.56
SAN JOSE A 1109 | 82251109 | 0.62 |  |  |  | 0.62
SAN JOSE A 1110 | 82251110 | 9.02 |  |  |  | 9.02
SAN JOSE A 1111 | 82251111 | 0.12 |  |  |  | 0.12
SAN JOSE A 1112 | 82251112 | 10.55 |  |  |  | 10.55
SAN JOSE B 1101 | 82261101 | 0.16 |  |  |  | 0.16
SAN JOSE B 1102 | 82261102 | 0.26 |  |  |  | 0.26
SAN JOSE B 1104 | 82261104 | 0.48 |  |  |  | 0.48
SAN JOSE B 1105 | 82261105 | 8.63 |  |  |  | 8.63
SAN JOSE B 1106 | 82261106 | 0.7 |  |  |  | 0.7
SAN JOSE B 1107 | 82261107 | 9.06 |  |  |  | 9.06
SAN JOSE B 1108 | 82261108 | 8.07 |  |  |  | 8.07
SAN JOSE B 1109 | 82261109 | 0.38 |  |  |  | 0.38
SAN JOSE B 1110 | 82261110 | 13.27 |  |  |  | 13.27
SAN JOSE B 1111 | 82261111 | 0.08 |  |  |  | 0.08
SAN JOSE B 1112 | 82261112 | 12.52 |  |  |  | 12.52
SAN JOSE B 1113 | 82261113 | 0.1 |  |  |  | 0.1
SAN JOSE B 1114 | 82261114 | 0.68 |  |  |  | 0.68
SAN JOSE B 1115 | 82261115 | 0.78 |  |  |  | 0.78
SAN JOSE B 1116 | 82261116 | 5 |  |  |  | 5
SAN JOSE B 1117 | 82261117 | 3.63 |  |  |  | 3.63
SAN JUSTO 1101 | 183181101 | 55.93 |  | 37.23 |  | 18.7
SAN LEANDRO U 1101 | 13111101 | 3.89 |  |  |  | 3.89
SAN LEANDRO U 1102 | 13111102 | 12.39 |  |  |  | 12.39
SAN LEANDRO U 1103 | 13111103 | 1.93 |  |  |  | 1.93
SAN LEANDRO U 1104 | 13111104 | 6.25 |  |  |  | 6.25
SAN LEANDRO U 1105 | 13111105 | 7.75 |  |  |  | 7.75
SAN LEANDRO U 1106 | 13111106 | 12.37 |  |  |  | 12.37
SAN LEANDRO U 1107 | 13111107 | 15.01 |  |  |  | 15.01
SAN LEANDRO U 1108 | 13111108 | 8.49 |  |  |  | 8.49
SAN LEANDRO U 1109 | 13111109 | 19.8 | 0.86 | 11.57 |  | 7.37
SAN LEANDRO U 1110 | 13111110 | 18.9 |  |  |  | 18.9
SAN LEANDRO U 1111 | 13111111 | 2.29 |  |  |  | 2.29
SAN LEANDRO U 1112 | 13111112 | 3.96 |  |  |  | 3.96
SAN LEANDRO U 1113 | 13111113 | 7.11 |  |  |  | 7.11
SAN LEANDRO U 1114 | 13111114 | 29.07 |  | 9.53 |  | 19.54
SAN LEANDRO U 1115 | 13111115 | 1.47 |  |  |  | 1.47
SAN LEANDRO U 1116 | 13111116 | 3.8 |  |  |  | 3.8
SAN LEANDRO U 1151 | 13111151 | 5.95 |  |  |  | 5.95
SAN LORENZO 0401 | 13460401 | 4.37 |  |  |  | 4.37
SAN LUIS OBISPO 1101 | 182631101 | 36.78 | 10.18 | 15.4 |  | 11.2
SAN LUIS OBISPO 1102 | 182631102 | 13.44 |  | 0.58 |  | 12.86
SAN LUIS OBISPO 1103 | 182631103 | 38.96 |  | 20.21 |  | 18.75
SAN LUIS OBISPO 1104 | 182631104 | 82.39 | 21.32 | 36.56 |  | 24.51
SAN LUIS OBISPO 1105 | 182631105 | 11.79 |  | 1.43 |  | 10.36
SAN LUIS OBISPO 1107 | 182631107 | 50.34 | 24.62 | 21.75 |  | 3.97
SAN LUIS OBISPO 1108 | 182631108 | 10.03 |  | 1.61 |  | 8.42
SAN MATEO 0404 | 24190404 | 5.08 |  |  |  | 5.08
SAN MATEO 0407 | 24190407 | 3.59 |  |  |  | 3.59
SAN MATEO 0408 | 24190408 | 5.63 |  |  |  | 5.63
SAN MATEO 0409 | 24190409 | 3.13 |  |  |  | 3.13
SAN MATEO 0410 | 24190410 | 5.15 |  |  |  | 5.15
SAN MATEO 2101 | 24192101 | 7.25 |  |  |  | 7.25
SAN MATEO 2102 | 24192102 | 13.01 |  |  |  | 13.01
SAN MIGUEL 1104 | 182661104 | 144.71 |  | 23.74 |  | 120.97
SAN MIGUEL 1105 | 182661105 | 20.16 |  | 1.39 |  | 18.77
SAN MIGUEL 1106 | 182661106 | 74.23 |  | 37.82 |  | 36.41
SAN MIGUEL 1107 | 182661107 | 5.74 |  |  |  | 5.74
SAN PABLO 1105 | 14371105 | 19.47 |  |  |  | 19.47
SAN PABLO 1106 | 14371106 | 0.65 |  |  |  | 0.65
SAN RAFAEL 1101 | 42011101 | 27.43 | 12.24 | 1.2 |  | 13.99
SAN RAFAEL 1102 | 42011102 | 4.85 |  |  |  | 4.85
SAN RAFAEL 1103 | 42011103 | 5.9 |  |  |  | 5.9
SAN RAFAEL 1104 | 42011104 | 24.9 | 1.88 | 9.71 |  | 13.31
SAN RAFAEL 1105 | 42011105 | 23.01 |  | 1.62 |  | 21.39
SAN RAFAEL 1106 | 42011106 | 21.1 |  | 2.8 |  | 18.3
SAN RAFAEL 1107 | 42011107 | 29.14 | 18.24 | 2.98 |  | 7.92
SAN RAFAEL 1108 | 42011108 | 29.46 | 26.37 | 0.44 |  | 2.65
SAN RAFAEL 1109 | 42011109 | 26.32 |  | 9.79 |  | 16.53
SAN RAFAEL 1110 | 42011110 | 13.14 | 7.93 |  |  | 5.21
SAN RAMON 2101 | 14232101 | 1.08 |  | 0.61 |  | 0.47
SAN RAMON 2102 | 14232102 | 2.33 |  | 1.52 |  | 0.81
SAN RAMON 2103 | 14232103 | 2.76 | 0 |  |  | 2.76
SAN RAMON 2104 | 14232104 | 20.65 |  |  |  | 20.65
SAN RAMON 2105 | 14232105 | 3.44 |  |  |  | 3.44
SAN RAMON 2106 | 14232106 | 5.09 | 0.45 |  |  | 4.64
SAN RAMON 2107 | 14232107 | 27.43 | 14.33 | 0.17 |  | 12.93
SAN RAMON 2108 | 14232108 | 17.31 | 16.38 |  |  | 0.93
SAN RAMON 2110 | 14232110 | 0.1 |  |  |  | 0.1
SAN RAMON 2111 | 14232111 | 9.43 |  |  |  | 9.43
SAN RAMON 2114 | 14232114 | 1.61 |  |  |  | 1.61
SAN RAMON 2116 | 14232116 | 0 |  |  |  | 0
SAN RAMON 2117 | 14232117 | 1.67 |  | 0.56 |  | 1.11
SAN RAMON 2118 | 14232118 | 0.82 |  |  |  | 0.82
SAN RAMON 2119 | 14232119 | 3.02 |  | 0.59 |  | 2.43
SAND CREEK 1103 | 254601103 | 150.17 |  | 148.46 |  | 1.71
SANGER 1104 | 252351104 | 9.61 |  |  |  | 9.61
SANGER 1106 | 252351106 | 8.57 |  |  |  | 8.57
SANGER 1108 | 252351108 | 81.22 |  |  |  | 81.22
SANGER 1110 | 252351110 | 29.33 |  |  |  | 29.33
SANGER 1112 | 252351112 | 11.54 |  |  |  | 11.54
SANGER 1114 | 252351114 | 63.07 |  |  |  | 63.07
SANGER 1116 | 252351116 | 6.36 |  |  |  | 6.36
SANGER 1118 | 252351118 | 29.51 |  |  |  | 29.51
SANTA MARIA 1105 | 182671105 | 28.85 |  |  |  | 28.85
SANTA MARIA 1106 | 182671106 | 18.94 |  |  |  | 18.94
SANTA MARIA 1107 | 182671107 | 4.93 |  |  |  | 4.93
SANTA MARIA 1108 | 182671108 | 93.89 | 43.73 | 28.52 |  | 21.64
SANTA MARIA 1109 | 182671109 | 46.46 |  |  |  | 46.46
SANTA MARIA 1110 | 182671110 | 52.56 |  |  |  | 52.56
SANTA MARIA 1111 | 182671111 | 15.6 |  |  |  | 15.6
SANTA MARIA 1112 | 182671112 | 10.45 |  |  |  | 10.45
SANTA NELLA 1101 | 254051101 | 38.53 |  |  |  | 38.53
SANTA NELLA 1104 | 254051104 | 52.32 |  |  |  | 52.32
SANTA RITA 1102 | 253541102 | 89.22 |  |  |  | 89.22
SANTA RITA 1105 | 253541105 | 61.38 |  |  |  | 61.38
SANTA ROSA A 1101 | 42151101 | 4.52 |  |  |  | 4.52
SANTA ROSA A 1102 | 42151102 | 12.08 |  |  |  | 12.08
SANTA ROSA A 1103 | 42151103 | 10.95 |  |  |  | 10.95
SANTA ROSA A 1104 | 42151104 | 56.15 | 37.51 | 5.24 |  | 13.4
SANTA ROSA A 1105 | 42151105 | 9.38 |  |  |  | 9.38
SANTA ROSA A 1106 | 42151106 | 10 |  |  |  | 10
SANTA ROSA A 1107 | 42151107 | 8.43 | 2.88 |  |  | 5.55
SANTA ROSA A 1108 | 42151108 | 6.81 |  | 0.14 |  | 6.67
SANTA ROSA A 1109 | 42151109 | 5.92 |  |  |  | 5.92
SANTA ROSA A 1110 | 42151110 | 22.39 |  |  |  | 22.39
SANTA ROSA A 1111 | 42151111 | 26.1 |  | 5.67 |  | 20.43
SANTA ROSA A 1112 | 42151112 | 12.64 |  |  |  | 12.64
SANTA TERESA 2101 | 82962101 | 0.43 |  |  |  | 0.43
SANTA YNEZ 1101 | 182721101 | 58.86 | 14.55 | 14.07 |  | 30.24
SANTA YNEZ 1102 | 182721102 | 33.83 | 4.99 | 9.01 |  | 19.83
SANTA YNEZ 1104 | 182721104 | 84.8 | 4.59 | 37.72 |  | 42.49
SARANAP 0401 | 13560401 | 2.46 |  |  |  | 2.46
SARATOGA 1103 | 83371103 | 10.48 |  | 4.59 |  | 5.89
SARATOGA 1104 | 83371104 | 18.12 |  | 2.92 |  | 15.2
SARATOGA 1105 | 83371105 | 16.72 |  | 10.1 |  | 6.62
SARATOGA 1106 | 83371106 | 26.76 | 1.38 | 14.05 |  | 11.33
SARATOGA 1107 | 83371107 | 45.44 | 20.53 | 13.94 |  | 10.97
SARATOGA 1108 | 83371108 | 18.57 |  |  |  | 18.57
SARATOGA 1109 | 83371109 | 25.33 |  |  |  | 25.33
SARATOGA 1110 | 83371110 | 19.99 |  |  |  | 19.99
SARATOGA 1111 | 83371111 | 23.93 |  |  |  | 23.93
SARATOGA 1112 | 83371112 | 8.44 |  |  |  | 8.44
SARATOGA 1113 | 83371113 | 25.66 |  |  |  | 25.66
SARATOGA 1114 | 83371114 | 21.11 |  |  |  | 21.11
SARATOGA 1115 | 83371115 | 13.81 |  | 2.82 |  | 10.99
SAUSALITO 0401 | 42490401 | 2.01 |  |  |  | 2.01
SAUSALITO 0402 | 42490402 | 2.94 |  |  |  | 2.94
SAUSALITO 1101 | 42491101 | 6.74 |  | 1.25 |  | 5.49
SAUSALITO 1102 | 42491102 | 17.99 |  | 9.11 |  | 8.88
SCE MCFARLAND 1101 | 258111101 | 0.5 |  |  |  | 0.5
SCE REFUGIO 1701 | 188071701 | 0.08 | 0.08 |  |  | 0
SCE TEHACHAPI 1101 | 258131101 | 1.44 |  | 1.44 |  | 0
SCE TEJON TIE 1101 | 258191101 | 0.06 |  | 0.06 |  | 0
SCE VEGAS 1701 | 188881701 | 0.17 | 0.17 |  |  | 0
SCHINDLER 1104 | 252891104 | 0.01 |  |  |  | 0.01
SCHINDLER 1105 | 252891105 | 41.86 |  |  |  | 41.86
SCHINDLER 1107 | 252891107 | 1.43 |  |  |  | 1.43
SCHINDLER 1108 | 252891108 | 2.31 |  |  |  | 2.31
SCHINDLER 1109 | 252891109 | 1.67 |  |  |  | 1.67
SCHINDLER 1110 | 252891110 | 48.18 |  |  |  | 48.18
SCHINDLER 1111 | 252891111 | 41.63 |  |  |  | 41.63
SCHINDLER 1112 | 252891112 | 49.22 |  |  |  | 49.22
SCHINDLER 1114 | 252891114 | 58.36 |  |  |  | 58.36
SCHINDLER 1116 | 252891116 | 25.73 |  |  |  | 25.73
SEACLIFF 0401 | 83500401 | 9.16 | 6.52 | 1.23 |  | 1.41
SEACLIFF 0402 | 83500402 | 1.57 | 0.07 | 0.01 |  | 1.49
SEMITROPIC 1104 | 252901104 | 15.83 |  |  |  | 15.83
SEMITROPIC 1106 | 252901106 | 27.34 |  |  |  | 27.34
SEMITROPIC 1108 | 252901108 | 11.78 |  |  |  | 11.78
SEMITROPIC 1110 | 252901110 | 50.12 |  |  |  | 50.12
SEMITROPIC 1112 | 252901112 | 26.73 |  |  |  | 26.73
SERRAMONTE 1103 | 22861103 | 13.16 |  |  |  | 13.16
SERRAMONTE 1104 | 22861104 | 12.65 |  |  |  | 12.65
SF E 0401 | 22070401 | 3.52 |  |  |  | 3.52
SF E 0405 | 22070405 | 2.2 |  |  |  | 2.2
SF E 0406 | 22070406 | 1.47 |  |  |  | 1.47
SF E 0407 | 22070407 | 0.94 |  |  |  | 0.94
SF E 0408 | 22070408 | 2.68 |  |  |  | 2.68
SF E 0409 | 22070409 | 1.8 |  |  |  | 1.8
SF E 0410 | 22070410 | 1.87 |  |  |  | 1.87
SF E 1101 | 22071101 | 1.12 |  |  |  | 1.12
SF E 1103 | 22071103 | 3.14 |  |  |  | 3.14
SF E 1105 | 22071105 | 2.42 |  |  |  | 2.42
SF E 1107 | 22071107 | 3.75 |  |  |  | 3.75
SF G 0401 | 22090401 | 0.67 |  |  |  | 0.67
SF G 0402 | 22090402 | 1.56 |  |  |  | 1.56
SF G 0403 | 22090403 | 0.71 |  |  |  | 0.71
SF G 0404 | 22090404 | 0.96 |  |  |  | 0.96
SF G 0405 | 22090405 | 1.47 |  |  |  | 1.47
SF G 0406 | 22090406 | 1.28 |  |  |  | 1.28
SF G 0407 | 22090407 | 1.36 |  |  |  | 1.36
SF G 0408 | 22090408 | 1.28 |  |  |  | 1.28
SF G 0409 | 22090409 | 0.91 |  |  |  | 0.91
SF G 0410 | 22090410 | 0.58 |  |  |  | 0.58
SF G 0412 | 22090412 | 1.1 |  |  |  | 1.1
SF G 0413 | 22090413 | 0.98 |  |  |  | 0.98
SF G 0414 | 22090414 | 0.89 |  |  |  | 0.89
SF G 1101 | 22091101 | 1.02 |  |  |  | 1.02
SF G 1102 | 22091102 | 0.56 |  |  |  | 0.56
SF H 0401 | 22100401 | 4.61 |  |  |  | 4.61
SF H 0402 | 22100402 | 4.08 |  |  |  | 4.08
SF H 0403 | 22100403 | 1.06 |  |  |  | 1.06
SF H 0404 | 22100404 | 2.72 |  |  |  | 2.72
SF H 0405 | 22100405 | 2.46 |  |  |  | 2.46
SF H 1101 | 22101101 | 6.42 |  |  |  | 6.42
SF H 1102 | 22101102 | 6.91 |  |  |  | 6.91
SF H 1103 | 22101103 | 8.63 |  |  |  | 8.63
SF H 1104 | 22101104 | 0.65 |  |  |  | 0.65
SF H 1105 | 22101105 | 14.84 |  |  |  | 14.84
SF H 1106 | 22101106 | 7.93 |  |  |  | 7.93
SF H 1107 | 22101107 | 3.78 |  |  |  | 3.78
SF H 1108 | 22101108 | 13.42 |  |  |  | 13.42
SF H 1109 | 22101109 | 4.69 |  |  |  | 4.69
SF H 1110 | 22101110 | 13.13 |  |  |  | 13.13
SF H 1111 | 22101111 | 3.9 |  |  |  | 3.9
SF J 0402 | 22220402 | 0.87 |  |  |  | 0.87
SF J 0404 | 22220404 | 0.52 |  |  |  | 0.52
SF J 0406 | 22220406 | 0.52 |  |  |  | 0.52
SF J 0407 | 22220407 | 0 |  |  |  | 0
SF J 0409 | 22220409 | 0.15 |  |  |  | 0.15
SF J 1108 | 22221108 | 0 |  |  |  | 0
SF K 0401 | 22130401 | 2.48 |  |  |  | 2.48
SF K 0402 | 22130402 | 3.31 |  |  |  | 3.31
SF K 0403 | 22130403 | 2.49 |  |  |  | 2.49
SF K 0404 | 22130404 | 0.97 |  |  |  | 0.97
SF K 0405 | 22130405 | 2.81 |  |  |  | 2.81
SF K 0406 | 22130406 | 1.73 |  |  |  | 1.73
SF K 0407 | 22130407 | 1.28 |  |  |  | 1.28
SF K 0408 | 22130408 | 1.35 |  |  |  | 1.35
SF K 0409 | 22130409 | 2.39 |  |  |  | 2.39
SF K 0410 | 22130410 | 2.03 |  |  |  | 2.03
SF K 0411 | 22130411 | 2.27 |  |  |  | 2.27
SF K 1101 | 22131101 | 6.74 |  |  |  | 6.74
SF L 0401 | 22260401 | 2.47 |  |  |  | 2.47
SF L 0402 | 22260402 | 0 |  |  |  | 0
SF L 0403 | 22260403 | 0.25 |  |  |  | 0.25
SF L 0404 | 22260404 | 0.81 |  |  |  | 0.81
SF L 0405 | 22260405 | 2.3 |  |  |  | 2.3
SF L 0406 | 22260406 | 2.14 |  |  |  | 2.14
SF L 0407 | 22260407 | 0.55 |  |  |  | 0.55
SF L 0408 | 22260408 | 2.4 |  |  |  | 2.4
SF L 0409 | 22260409 | 0.15 |  |  |  | 0.15
SF L 1101 | 22261101 | 2.38 |  |  |  | 2.38
SF L 1102 | 22261102 | 7.95 |  |  |  | 7.95
SF L 1103 | 22261103 | 1.97 |  |  |  | 1.97
SF M 0401 | 22270401 | 3.73 |  |  |  | 3.73
SF M 0402 | 22270402 | 1.97 |  |  |  | 1.97
SF M 0403 | 22270403 | 3.69 |  |  |  | 3.69
SF M 0404 | 22270404 | 3.57 |  |  |  | 3.57
SF M 0405 | 22270405 | 2.35 |  |  |  | 2.35
SF M 0406 | 22270406 | 2.91 |  |  |  | 2.91
SF N 0401 | 22280401 | 3.13 |  |  |  | 3.13
SF N 0402 | 22280402 | 1.01 |  |  |  | 1.01
SF N 0403 | 22280403 | 2.47 |  |  |  | 2.47
SF N 0405 | 22280405 | 1.07 |  |  |  | 1.07
SF N 0406 | 22280406 | 0.8 |  |  |  | 0.8
SF N 0408 | 22280408 | 3.12 |  |  |  | 3.12
SF N 1101 | 22281101 | 0.27 |  |  |  | 0.27
SF N 1102 | 22281102 | 6.09 |  |  |  | 6.09
SHADY GLEN 1101 | 152431101 | 41.09 |  | 34.74 |  | 6.35
SHADY GLEN 1102 | 152431102 | 51.78 | 24.1 | 25.89 |  | 1.79
SHAFTER 1101 | 253651101 | 0.03 |  |  |  | 0.03
SHAFTER 1102 | 253651102 | 27.52 |  |  |  | 27.52
SHAFTER 1103 | 253651103 | 39.63 |  |  |  | 39.63
SHAFTER 1104 | 253651104 | 9.62 |  |  |  | 9.62
SHAFTER 1111 | 253651111 | 24.34 |  |  |  | 24.34
SHAFTER 1112 | 253651112 | 47.89 |  |  |  | 47.89
SHARON 1101 | 255331101 | 1.54 |  |  |  | 1.54
SHEPHERD 2109 | 252062109 | 4.35 |  |  |  | 4.35
SHEPHERD 2110 | 252062110 | 8.38 |  |  |  | 8.38
SHEPHERD 2111 | 252062111 | 69.07 |  | 29.52 |  | 39.55
SHEPHERD 2112 | 252062112 | 7.75 |  |  |  | 7.75
SHINGLE SPRINGS 1103 | 153651103 | 13.67 | 4.6 | 3.1 |  | 5.97
SHINGLE SPRINGS 1104 | 153651104 | 59.85 | 37.11 | 6.66 |  | 16.08
SHINGLE SPRINGS 2105 | 153652105 | 32.74 | 26.05 | 4.37 |  | 2.32
SHINGLE SPRINGS 2108 | 153652108 | 29.67 | 7.21 | 7.76 |  | 14.7
SHINGLE SPRINGS 2109 | 153652109 | 209.66 | 107.69 | 101.33 |  | 0.64
SHINGLE SPRINGS 2110 | 153652110 | 65.17 | 55.44 | 7.37 |  | 2.36
SILVER 0401 | 22670401 | 5.04 |  |  |  | 5.04
SILVERADO 2102 | 43432102 | 108.6 | 32.79 | 24.65 |  | 51.16
SILVERADO 2103 | 43432103 | 32.58 | 10.77 | 0.03 |  | 21.78
SILVERADO 2104 | 43432104 | 139.18 | 75.02 | 36.32 |  | 27.84
SILVERADO 2105 | 43432105 | 63.59 | 34.9 | 1.72 |  | 26.97
SISQUOC 1101 | 182811101 | 26.81 |  |  |  | 26.81
SISQUOC 1102 | 182811102 | 115.23 | 31.2 | 19.57 |  | 64.46
SISQUOC 1103 | 182811103 | 50.1 | 22.64 | 2.79 |  | 24.67
SISQUOC 1104 | 182811104 | 32.55 |  |  |  | 32.55
SKAGGS ISLAND 1101 | 43341101 | 0.05 |  |  |  | 0.05
SMARTVILLE 1101 | 153791101 | 16.07 |  | 15.75 |  | 0.32
SMUD 0401 | 158050401 | 0.01 |  | 0.01 |  | 0
SMYRNA 1101 | 253551101 | 43.48 |  |  |  | 43.48
SMYRNA 1102 | 253551102 | 66.66 |  |  |  | 66.66
SMYRNA 1104 | 253551104 | 44.55 |  |  |  | 44.55
SMYRNA 1105 | 253551105 | 51.92 |  |  |  | 51.92
SMYRNA 1106 | 253551106 | 46.54 |  |  |  | 46.54
SNEATH LANE 1101 | 22721101 | 9.42 |  | 2.26 |  | 7.16
SNEATH LANE 1102 | 22721102 | 10.53 |  | 1.24 |  | 9.29
SNEATH LANE 1106 | 22721106 | 11.62 |  | 2.62 |  | 9
SNEATH LANE 1107 | 22721107 | 10.47 |  | 0.91 |  | 9.56
SO. CAL. EDISON #3 1101 | 258861101 | 9.49 | 6.73 | 2.6 |  | 0.16
SO. CAL. EDISON 1001 | 258881001 | 2.02 |  |  |  | 2.02
SOBRANTE 1101 | 14671101 | 21.39 |  | 14.97 |  | 6.42
SOBRANTE 1102 | 14671102 | 27.62 | 1.26 | 26 |  | 0.36
SOBRANTE 1103 | 14671103 | 11.36 | 1.82 | 7.69 |  | 1.85
SOLANO 0402 | 13140402 | 6.32 |  |  |  | 6.32
SOLEDAD 2101 | 182052101 | 41.49 |  | 17.33 |  | 24.16
SOLEDAD 2102 | 182052102 | 48.97 |  | 11.6 |  | 37.37
SOLEDAD 2104 | 182052104 | 25.09 |  | 1.22 |  | 23.87
SOLEDAD 2105 | 182052105 | 47.73 |  | 4.47 |  | 43.26
SONOMA 1102 | 42721102 | 18.14 | 6.02 |  |  | 12.12
SONOMA 1103 | 42721103 | 25.42 | 12.68 |  |  | 12.74
SONOMA 1104 | 42721104 | 55.43 |  | 19.63 |  | 35.8
SONOMA 1105 | 42721105 | 63.43 | 3.47 | 10.14 |  | 49.82
SONOMA 1106 | 42721106 | 11.14 | 0.88 |  |  | 10.26
SONOMA 1107 | 42721107 | 51.96 |  | 3.87 |  | 48.09
SOQUEL 0402 | 83300402 | 6.58 |  |  |  | 6.58
SOTO 0402 | 13260402 | 2.04 |  |  |  | 2.04
SPAULDING 1101 | 152251101 | 23.94 | 1.19 | 19.15 | 0.37 | 3.23
SPENCE 1102 | 182201102 | 33.47 |  | 2.36 |  | 31.11
SPENCE 1103 | 182201103 | 12.37 |  |  |  | 12.37
SPENCE 1104 | 182201104 | 52.34 |  | 9.04 |  | 43.3
SPENCE 1105 | 182201105 | 7.18 |  |  |  | 7.18
SPRING GAP 1702 | 162831702 | 42.35 | 39.7 | 0.77 |  | 1.88
STAFFORD 1101 | 43201101 | 15.35 |  | 2.27 |  | 13.08
STAFFORD 1102 | 43201102 | 37.35 | 1.54 | 19.66 |  | 16.15
STAGG 1101 | 162421101 | 19.59 |  |  |  | 19.59
STAGG 1103 | 162421103 | 6.06 |  |  |  | 6.06
STAGG 1105 | 162421105 | 12.07 |  |  |  | 12.07
STAGG 1106 | 162421106 | 1.86 |  |  |  | 1.86
STAGG 2104 | 162422104 | 24.45 |  |  |  | 24.45
STAGG 2105 | 162422105 | 4.5 |  |  |  | 4.5
STAGG 2106 | 162422106 | 5.45 |  |  |  | 5.45
STAGG 2107 | 162422107 | 6.04 |  |  |  | 6.04
STAGG 2108 | 162422108 | 5.83 |  |  |  | 5.83
STANISLAUS 1701 | 162821701 | 74.89 | 22.65 | 51.99 |  | 0.25
STANISLAUS 1702 | 162821702 | 85 | 78.35 | 6.66 |  | -0.01
STELLING 1102 | 83481102 | 0.69 |  |  |  | 0.69
STELLING 1103 | 83481103 | 2.85 |  |  |  | 2.85
STELLING 1104 | 83481104 | 11.01 |  |  |  | 11.01
STELLING 1105 | 83481105 | 0.4 |  |  |  | 0.4
STELLING 1106 | 83481106 | 0 |  |  |  | 0
STELLING 1107 | 83481107 | 8.19 |  |  |  | 8.19
STELLING 1108 | 83481108 | 31.72 |  |  |  | 31.72
STELLING 1109 | 83481109 | 16.57 |  | 0.88 |  | 15.69
STELLING 1110 | 83481110 | 49.26 | 10.28 | 21.86 |  | 17.12
STELLING 1111 | 83481111 | 26.77 |  |  |  | 26.77
STELLING 1112 | 83481112 | 2.19 |  |  |  | 2.19
STELLING 1113 | 83481113 | 17.16 |  |  |  | 17.16
STILLWATER 1101 | 103561101 | 35.17 |  | 34.41 |  | 0.76
STILLWATER 1102 | 103561102 | 78.34 |  | 78.24 |  | 0.1
STOCKDALE 1105 | 254071105 | 5.05 |  |  |  | 5.05
STOCKDALE 1106 | 254071106 | 5.6 |  |  |  | 5.6
STOCKDALE 1108 | 254071108 | 3.84 |  |  |  | 3.84
STOCKDALE 1109 | 254071109 | 4.48 |  |  |  | 4.48
STOCKDALE 1110 | 254071110 | 6.31 |  |  |  | 6.31
STOCKDALE 1111 | 254071111 | 8.66 |  |  |  | 8.66
STOCKDALE 2105 | 254072105 | 5.01 |  |  |  | 5.01
STOCKDALE 2106 | 254072106 | 8.97 |  |  |  | 8.97
STOCKDALE 2107 | 254072107 | 1.84 |  |  |  | 1.84
STOCKDALE 2108 | 254072108 | 2.96 |  |  |  | 2.96
STOCKDALE 2109 | 254072109 | 8.53 |  |  |  | 8.53
STOCKDALE 2110 | 254072110 | 8.78 |  |  |  | 8.78
STOCKDALE 2111 | 254072111 | 2.87 |  |  |  | 2.87
STOCKDALE 2112 | 254072112 | 30.1 |  |  |  | 30.1
STOCKDALE 2113 | 254072113 | 15.7 |  |  |  | 15.7
STOCKDALE 2114 | 254072114 | 10.47 |  |  |  | 10.47
STOCKDALE 2115 | 254072115 | 0.45 |  |  |  | 0.45
STOCKTON A 0404 | 162370404 | 5.17 |  |  |  | 5.17
STOCKTON A 0405 | 162370405 | 0.39 |  |  |  | 0.39
STOCKTON A 0406 | 162370406 | 3.25 |  |  |  | 3.25
STOCKTON A 0410 | 162370410 | 6.31 |  |  |  | 6.31
STOCKTON A 1101 | 162371101 | 4.12 |  |  |  | 4.12
STOCKTON A 1102 | 162371102 | 6.47 |  |  |  | 6.47
STOCKTON A 1103 | 162371103 | 0.21 |  |  |  | 0.21
STOCKTON A 1104 | 162371104 | 15.88 |  |  |  | 15.88
STOCKTON A 1105 | 162371105 | 12.35 |  |  |  | 12.35
STOCKTON A 1106 | 162371106 | 16.95 |  |  |  | 16.95
STOCKTON A 1107 | 162371107 | 11.28 |  |  |  | 11.28
STOCKTON A 1108 | 162371108 | 9.3 |  |  |  | 9.3
STOCKTON A 1109 | 162371109 | 11.9 |  |  |  | 11.9
STOCKTON A 1110 | 162371110 | 10.08 |  |  |  | 10.08
STOCKTON A 1111 | 162371111 | 0.07 |  |  |  | 0.07
STOCKTON ACRES 0401 | 163220401 | 2.87 |  |  |  | 2.87
STOCKTON ACRES 0402 | 163220402 | 3.01 |  |  |  | 3.01
STONE 1101 | 83701101 | 19.95 |  |  |  | 19.95
STONE 1104 | 83701104 | 5.55 |  |  |  | 5.55
STONE 1107 | 83701107 | 11.97 |  |  |  | 11.97
STONE 1108 | 83701108 | 4.39 |  |  |  | 4.39
STONE 1109 | 83701109 | 8.25 |  |  |  | 8.25
STONE 1110 | 83701110 | 11.83 |  |  |  | 11.83
STONE CORRAL 1108 | 252921108 | 76.2 |  | 1.87 |  | 74.33
STONE CORRAL 1109 | 252921109 | 16.52 |  |  |  | 16.52
STONE CORRAL 1110 | 252921110 | 62.6 |  | 2.01 |  | 60.59
STOREY 1104 | 254611104 | 75.54 |  |  |  | 75.54
STOREY 1105 | 254611105 | 14.36 |  |  |  | 14.36
STOREY 1106 | 254611106 | 13.49 |  |  |  | 13.49
STOREY 1107 | 254611107 | 19.08 |  |  |  | 19.08
STOREY 1108 | 254611108 | 72.24 |  |  |  | 72.24
STOREY 1109 | 254611109 | 177.3 |  |  |  | 177.3
STOREY 1111 | 254611111 | 29.65 |  |  |  | 29.65
STROUD 1101 | 253661101 | 31.94 |  |  |  | 31.94
STROUD 1102 | 253661102 | 34.26 |  |  |  | 34.26
STROUD 1104 | 253661104 | 31.17 |  |  |  | 31.17
STUART 0401 | 13840401 | 2.94 |  |  |  | 2.94
STUART 0402 | 13840402 | 2.12 |  |  |  | 2.12
STUART 0403 | 13840403 | 3.12 |  |  |  | 3.12
STUART 0404 | 13840404 | 1.07 |  |  |  | 1.07
STUART 0405 | 13840405 | 2.8 |  |  |  | 2.8
STUART 0406 | 13840406 | 2.94 |  |  |  | 2.94
SUISUN 1101 | 62131101 | 6.17 |  |  |  | 6.17
SUISUN 1102 | 62131102 | 9.81 |  |  |  | 9.81
SUISUN 1103 | 62131103 | 2.73 |  |  |  | 2.73
SUISUN 1104 | 62131104 | 4.83 |  |  |  | 4.83
SUISUN 1105 | 62131105 | 5.37 |  |  |  | 5.37
SUISUN 1106 | 62131106 | 4.99 |  |  |  | 4.99
SUISUN 1107 | 62131107 | 9.67 |  |  |  | 9.67
SUISUN 1108 | 62131108 | 6.59 |  |  |  | 6.59
SUISUN 1109 | 62131109 | 8.06 |  |  |  | 8.06
SUISUN 1110 | 62131110 | 2.91 |  |  |  | 2.91
SUISUN 1111 | 62131111 | 0.63 |  |  |  | 0.63
SUISUN 1112 | 62131112 | 2.85 |  |  |  | 2.85
SULLIVAN 0402 | 22850402 | 3.2 |  |  |  | 3.2
SUMMIT 1101 | 152591101 | 15.19 |  | 7.2 | 2.05 | 5.94
SUMMIT 1102 | 152591102 | 5.04 |  | 5.04 |  | 0
SUNOL 1101 | 14241101 | 55.43 | 9.57 | 23.58 |  | 22.28
SWIFT 2102 | 83392102 | 2.95 |  | 0.35 |  | 2.6
SWIFT 2106 | 83392106 | 21.28 |  |  |  | 21.28
SWIFT 2107 | 83392107 | 11.89 |  | 1.89 |  | 10
SWIFT 2108 | 83392108 | 4.92 |  |  |  | 4.92
SWIFT 2109 | 83392109 | 5.46 |  | 0.15 |  | 5.31
SWIFT 2110 | 83392110 | 86.24 |  | 81.31 |  | 4.93
SWIFT 2111 | 83392111 | 8.58 |  |  |  | 8.58
SYCAMORE CREEK 1101 | 102971101 | 4.78 |  |  |  | 4.78
SYCAMORE CREEK 1102 | 102971102 | 7.55 |  |  |  | 7.55
SYCAMORE CREEK 1103 | 102971103 | 3.14 |  |  |  | 3.14
SYCAMORE CREEK 1104 | 102971104 | 8.13 |  |  |  | 8.13
SYCAMORE CREEK 1105 | 102971105 | 15.13 |  |  |  | 15.13
SYCAMORE CREEK 1107 | 102971107 | 6.01 |  |  |  | 6.01
SYCAMORE CREEK 1109 | 102971109 | 13.42 |  | 0.13 |  | 13.29
SYCAMORE CREEK 1110 | 102971110 | 8.42 |  |  |  | 8.42
SYCAMORE CREEK 1111 | 102971111 | 64.8 | 27.37 | 24.9 |  | 12.53
TAFT 1101 | 252081101 | 14.18 |  |  |  | 14.18
TAFT 1102 | 252081102 | 0.05 |  |  |  | 0.05
TAFT 1103 | 252081103 | 27.46 |  |  |  | 27.46
TAFT 1104 | 252081104 | 11.2 |  |  |  | 11.2
TAFT 1106 | 252081106 | 7.13 |  |  |  | 7.13
TAFT 1108 | 252081108 | 9.21 |  |  |  | 9.21
TAMARACK 1101 | 152291101 | 19.55 |  | 18.66 | 0.13 | 0.76
TAMARACK 1102 | 152291102 | 7.85 |  |  | 0.31 | 7.54
TAR FLAT 0401 | 163240401 | 3.62 | 0 | 3.15 |  | 0.47
TAR FLAT 0402 | 163240402 | 6.7 | 0.88 | 4.52 |  | 1.3
TARAVAL 0401 | 22500401 | 1.82 |  |  |  | 1.82
TARAVAL 0402 | 22500402 | 3.04 |  |  |  | 3.04
TARAVAL 0403 | 22500403 | 3.47 |  |  |  | 3.47
TASSAJARA 2103 | 14662103 | 19.56 | 0.18 | 0.3 |  | 19.08
TASSAJARA 2104 | 14662104 | 9.65 | 1.57 | 4.36 |  | 3.72
TASSAJARA 2106 | 14662106 | 2.92 |  | 0.35 |  | 2.57
TASSAJARA 2107 | 14662107 | 8.52 |  |  |  | 8.52
TASSAJARA 2108 | 14662108 | 24.1 | 1.7 |  |  | 22.4
TASSAJARA 2109 | 14662109 | 4.02 |  | 2.89 |  | 1.13
TASSAJARA 2112 | 14662112 | 18.54 | 6.79 | 3.56 |  | 8.19
TASSAJARA 2113 | 14662113 | 4.93 | 3.82 |  |  | 1.11
TECUYA 1101 | 254511101 | 0.04 |  |  |  | 0.04
TEJON 1102 | 252931102 | 60.73 |  | 36.83 |  | 23.9
TEJON 1103 | 252931103 | 32.57 |  | 2.96 |  | 29.61
TEJON 1105 | 252931105 | 31.29 |  |  |  | 31.29
TEJON 1106 | 252931106 | 36 |  |  |  | 36
TEJON 1107 | 252931107 | 0.54 |  |  |  | 0.54
TEMBLOR 1104 | 252551104 | 49.26 |  |  |  | 49.26
TEMBLOR 2103 | 252552103 | 30.3 |  |  |  | 30.3
TEMPLETON 2108 | 183052108 | 36.13 |  | 5.36 |  | 30.77
TEMPLETON 2109 | 183052109 | 211.96 |  |  |  | 211.96
TEMPLETON 2110 | 183052110 | 173.1 | 33.51 | 93.84 |  | 45.75
TEMPLETON 2111 | 183052111 | 63.83 | 0.88 | 45.94 |  | 17.01
TEMPLETON 2112 | 183052112 | 37.82 |  | 2.6 |  | 35.22
TEMPLETON 2113 | 183052113 | 323.88 | 53.34 | 143.01 |  | 127.53
TEMPORARY CARBONA 1101 | 169951101 | 0.64 |  |  |  | 0.64
TEMPORARY CARBONA 1102 | 169951102 | 3.44 |  |  |  | 3.44
TEMPORARY CARBONA 1104 | 169951104 | 31.68 |  |  |  | 31.68
TEMPORARY CARBONA 1105 | 169951105 | 1.64 |  |  |  | 1.64
TERMINOUS 1102 | 163021102 | 22.68 |  |  |  | 22.68
TERMINOUS 1103 | 163021103 | 40.02 |  |  |  | 40.02
TEVIS 2101 | 255322101 | 23.77 |  |  |  | 23.77
TEVIS 2102 | 255322102 | 2.27 |  |  |  | 2.27
TEVIS 2103 | 255322103 | 3.28 |  |  |  | 3.28
TEVIS 2104 | 255322104 | 18.2 |  |  |  | 18.2
TEVIS 2105 | 255322105 | 1.97 |  |  |  | 1.97
TEXACO EMIDIO 1101 | 255421101 | 0.02 |  |  |  | 0.02
TIDEWATER 2104 | 14652104 | 26 |  |  |  | 26
TIDEWATER 2105 | 14652105 | 14.06 |  |  |  | 14.06
TIDEWATER 2106 | 14652106 | 35.95 |  | 3.68 |  | 32.27
TIDEWATER 2107 | 14652107 | 21.72 |  |  |  | 21.72
TIDEWATER 2108 | 14652108 | 9.6 |  |  |  | 9.6
TIDEWATER 2109 | 14652109 | 30.53 |  |  |  | 30.53
TIDEWATER 2110 | 14652110 | 10.17 |  |  |  | 10.17
TIGER CREEK 0201 | 161380201 | 3.77 | 1.73 | 2.04 |  | 0
TIVY VALLEY 1106 | 252941106 | 26.82 |  |  |  | 26.82
TIVY VALLEY 1107 | 252941107 | 174.29 |  | 116.36 |  | 57.93
TOCALOMA 0241 | 43150241 | 0.05 |  | 0.05 |  | 0
TOKAY 1101 | 168881101 | 12.31 |  |  |  | 12.31
TRACY 0402 | 162880402 | 2.91 |  |  |  | 2.91
TRACY 0405 | 162880405 | 3.24 |  |  |  | 3.24
TRACY 1102 | 162881102 | 27.77 |  |  |  | 27.77
TRACY 1103 | 162881103 | 4.42 |  |  |  | 4.42
TRACY 1104 | 162881104 | 4.73 |  |  |  | 4.73
TRACY 1105 | 162881105 | 4.74 |  |  |  | 4.74
TRACY 1106 | 162881106 | 36.57 |  |  |  | 36.57
TRACY 1107 | 162881107 | 6.14 |  |  |  | 6.14
TRACY 1109 | 162881109 | 5.11 |  |  |  | 5.11
TRACY 1110 | 162881110 | 9.14 |  |  |  | 9.14
TRACY 1111 | 162881111 | 7.23 |  |  |  | 7.23
TRACY 1112 | 162881112 | 4.69 |  |  |  | 4.69
TRES PINOS 1111 | 183221111 | 32.91 |  | 0.11 |  | 32.8
TRES VIAS 1101 | 103251101 | 68.6 |  |  |  | 68.6
TRIDAM POWERHOUSE 2101 | 168152101 | 0.05 | 0.05 |  |  | 0
TRIMBLE 1103 | 83801103 | 2.73 |  |  |  | 2.73
TRIMBLE 1104 | 83801104 | 0.41 |  |  |  | 0.41
TRIMBLE 1105 | 83801105 | 1.44 |  |  |  | 1.44
TRIMBLE 1106 | 83801106 | 0.65 |  |  |  | 0.65
TRIMBLE 1107 | 83801107 | 1.05 |  |  |  | 1.05
TRIMBLE 1110 | 83801110 | 0.34 |  |  |  | 0.34
TRIMBLE 2114 | 83802114 | 0 |  |  |  | 0
TRIMBLE 2115 | 83802115 | 0.31 |  |  |  | 0.31
TRIMBLE 2116 | 83802116 | 3.38 |  |  |  | 3.38
TRIMBLE 2118 | 83802118 | 0.39 |  |  |  | 0.39
TRINIDAD 1101 | 192231101 | 26.53 |  |  |  | 26.53
TRINIDAD 1102 | 192231102 | 24.19 |  |  | 0.25 | 23.94
TUDOR 1101 | 153711101 | 31.73 |  |  |  | 31.73
TUDOR 1102 | 153711102 | 23.15 |  |  |  | 23.15
TULARE LAKE 1104 | 252951104 | 14.58 |  |  |  | 14.58
TULARE LAKE 1106 | 252951106 | 52.18 |  |  |  | 52.18
TULARE LAKE 1108 | 252951108 | 48.76 |  |  |  | 48.76
TULE POWER HOUSE 1101 | 258591101 | 4.07 |  | 4.07 |  | 0
TULUCAY 1101 | 42301101 | 19.94 |  | 3.77 |  | 16.17
TUPMAN 1103 | 254561103 | 45.02 |  |  |  | 45.02
TUPMAN 1104 | 254561104 | 53.33 |  |  |  | 53.33
TUPMAN 1105 | 254561105 | 17.69 |  |  |  | 17.69
TUPMAN 1106 | 254561106 | 36.62 |  |  |  | 36.62
TWISSELMAN 1101 | 254401101 | 0.02 |  |  |  | 0.02
TWISSELMAN 1102 | 254401102 | 49.23 |  |  |  | 49.23
TWISSELMAN 1104 | 254401104 | 0.02 |  |  |  | 0.02
TWISSELMAN 2105 | 254402105 | 88.97 |  |  |  | 88.97
TYLER 1103 | 103571103 | 6.41 |  |  |  | 6.41
TYLER 1104 | 103571104 | 25.49 |  |  |  | 25.49
TYLER 1105 | 103571105 | 111.8 |  | 60.18 |  | 51.62
UKIAH 1111 | 42771111 | 32 |  | 7.84 |  | 24.16
UKIAH 1113 | 42771113 | 15.84 |  | 7.5 |  | 8.34
UKIAH 1114 | 42771114 | 103.63 |  | 53.83 |  | 49.8
UKIAH 1115 | 42771115 | 50.62 |  | 35.13 |  | 15.49
UPPER LAKE 1101 | 42871101 | 79.83 | 1.44 | 41.6 |  | 36.79
VACA DIXON 1101 | 63591101 | 50.46 |  | 22.5 |  | 27.96
VACA DIXON 1102 | 63591102 | 1.96 |  |  |  | 1.96
VACA DIXON 1103 | 63591103 | 126.78 |  |  |  | 126.78
VACA DIXON 1104 | 63591104 | 7.49 |  |  |  | 7.49
VACA DIXON 1105 | 63591105 | 49.72 |  | 1.4 |  | 48.32
VACA DIXON 1106 | 63591106 | 11.11 |  |  |  | 11.11
VACA DIXON 1109 | 63591109 | 2.13 |  |  |  | 2.13
VACAVILLE 1102 | 63601102 | 1 |  |  |  | 1
VACAVILLE 1103 | 63601103 | 11.13 |  |  |  | 11.13
VACAVILLE 1104 | 63601104 | 15.09 |  | 12.86 |  | 2.23
VACAVILLE 1105 | 63601105 | 2.87 |  |  |  | 2.87
VACAVILLE 1106 | 63601106 | 1.76 |  |  |  | 1.76
VACAVILLE 1107 | 63601107 | 1.91 |  |  |  | 1.91
VACAVILLE 1108 | 63601108 | 51.98 |  | 29.74 |  | 22.24
VACAVILLE 1109 | 63601109 | 5.64 |  | 0.81 |  | 4.83
VACAVILLE 1110 | 63601110 | 2.36 |  |  |  | 2.36
VACAVILLE 1111 | 63601111 | 13.03 |  | 10.12 |  | 2.91
VACAVILLE 1112 | 63601112 | 3.33 |  | 0.19 |  | 3.14
VALLEJO B 0411 | 42450411 | 7.07 |  |  |  | 7.07
VALLEJO B 0413 | 42450413 | 6.46 |  |  |  | 6.46
VALLEJO B 0414 | 42450414 | 8.29 |  |  |  | 8.29
VALLEJO B 0415 | 42450415 | 7.61 |  |  |  | 7.61
VALLEJO B 1101 | 42451101 | 16.3 |  |  |  | 16.3
VALLEJO B 1102 | 42451102 | 2.49 |  |  |  | 2.49
VALLEJO C 0401 | 42550401 | 2.8 |  |  |  | 2.8
VALLEY HOME 1702 | 162981702 | 56.27 |  |  |  | 56.27
VALLEY HOME 1703 | 162981703 | 127.51 |  |  |  | 127.51
VALLEY HOME 1704 | 162981704 | 39.28 |  |  |  | 39.28
VALLEY VIEW 1103 | 14341103 | 18.13 | 0.59 |  |  | 17.54
VALLEY VIEW 1105 | 14341105 | 14.15 |  | 3.98 |  | 10.17
VALLEY VIEW 1106 | 14341106 | 21.32 | 1.97 | 6.78 |  | 12.57
VASCO 1101 | 13751101 | 2.56 |  |  |  | 2.56
VASCO 1102 | 13751102 | 88.13 |  | 45.63 |  | 42.5
VASCO 1103 | 13751103 | 14.67 |  |  |  | 14.67
VASONA 1101 | 83771101 | 9.94 |  |  |  | 9.94
VASONA 1102 | 83771102 | 15.36 |  | 0.12 |  | 15.24
VASONA 1103 | 83771103 | 15.52 |  |  |  | 15.52
VASONA 1104 | 83771104 | 3.73 |  |  |  | 3.73
VASONA 1105 | 83771105 | 11.62 |  |  |  | 11.62
VASONA 1108 | 83771108 | 10.93 |  |  |  | 10.93
VICTOR 1101 | 163281101 | 18.26 |  |  |  | 18.26
VICTOR 1102 | 163281102 | 87.15 |  |  |  | 87.15
VIEJO 2201 | 182852201 | 17.32 |  | 14.59 |  | 2.73
VIEJO 2202 | 182852202 | 46.34 |  | 14.57 |  | 31.77
VIEJO 2203 | 182852203 | 22.78 |  | 3.04 |  | 19.74
VIEJO 2204 | 182852204 | 24.57 |  | 4.39 |  | 20.18
VIERRA 1701 | 162701701 | 9.72 |  |  |  | 9.72
VIERRA 1702 | 162701702 | 6.9 |  |  |  | 6.9
VIERRA 1703 | 162701703 | 5.61 |  |  |  | 5.61
VIERRA 1706 | 162701706 | 6.88 |  |  |  | 6.88
VIERRA 1707 | 162701707 | 48.43 |  |  |  | 48.43
VINA 1101 | 103581101 | 56.34 |  |  |  | 56.34
VINEYARD 2104 | 14502104 | 3.86 |  |  |  | 3.86
VINEYARD 2105 | 14502105 | 3.93 |  |  |  | 3.93
VINEYARD 2106 | 14502106 | 5.5 |  |  |  | 5.5
VINEYARD 2107 | 14502107 | 13.89 |  | 3 |  | 10.89
VINEYARD 2108 | 14502108 | 13.41 | 5.17 |  |  | 8.24
VINEYARD 2109 | 14502109 | 4.72 |  |  |  | 4.72
VINEYARD 2110 | 14502110 | 11.21 |  | 5.91 |  | 5.3
VIRGINIA 0401 | 13780401 | 4.02 |  |  |  | 4.02
VOLTA 1101 | 102541101 | 149.13 | 6.23 | 140.75 |  | 2.15
VOLTA 1102 | 102541102 | 129.61 | 86.85 | 41.93 |  | 0.83
Valley Springs 1101 | 168891101 | 2.14 |  |  |  | 2.14
WAHTOKE 1106 | 254531106 | 13.92 |  |  |  | 13.92
WAHTOKE 1107 | 254531107 | 19.14 |  |  |  | 19.14
WAHTOKE 1108 | 254531108 | 108.42 |  |  |  | 108.42
WAHTOKE 1109 | 254531109 | 6.95 |  |  |  | 6.95
WAHTOKE 1110 | 254531110 | 16.19 |  |  |  | 16.19
WAHTOKE 1111 | 254531111 | 29.93 |  |  |  | 29.93
WALDO 0401 | 13350401 | 5.7 |  | 1.6 |  | 4.1
WALDO 0402 | 13350402 | 5.17 |  | 2.97 |  | 2.2
WALL 0401 | 13740401 | 5.38 |  |  |  | 5.38
WALNUT CREEK 0403 | 12200403 | 0.51 |  |  |  | 0.51
WALNUT CREEK 0404 | 12200404 | 6.44 |  |  |  | 6.44
WARD 0401 | 12980401 | 4.52 |  |  |  | 4.52
WASCO 1101 | 252961101 | 12.15 |  |  |  | 12.15
WASCO 1102 | 252961102 | 7.71 |  |  |  | 7.71
WASCO 1104 | 252961104 | 9.94 |  |  |  | 9.94
WATERLOO 1101 | 163151101 | 58 |  |  |  | 58
WATERLOO 1102 | 163151102 | 21.72 |  |  |  | 21.72
WATERSHED 0402 | 24240402 | 1.19 | 0.02 |  |  | 1.17
WATSONVILLE 0411 | 83330411 | 2.31 |  |  |  | 2.31
WATSONVILLE 0413 | 83330413 | 1.22 |  |  |  | 1.22
WATSONVILLE 0414 | 83330414 | 1.28 |  |  |  | 1.28
WATSONVILLE 2101 | 83332101 | 102.59 |  |  |  | 102.59
WEBER 1101 | 163481101 | 3.23 |  |  |  | 3.23
WEBER 1102 | 163481102 | 31.75 |  |  |  | 31.75
WEBER 1103 | 163481103 | 1.8 |  |  |  | 1.8
WEBER 1105 | 163481105 | 20.89 |  |  |  | 20.89
WEBER 1107 | 163481107 | 0.04 |  |  |  | 0.04
WEBER 1108 | 163481108 | 0.44 |  |  |  | 0.44
WEBER 1109 | 163481109 | 53.12 |  |  |  | 53.12
WEBER 1110 | 163481110 | 12.68 |  |  |  | 12.68
WEBER 1111 | 163481111 | 19.87 |  |  |  | 19.87
WEBER 1112 | 163481112 | 0.03 |  |  |  | 0.03
WEBER 1113 | 163481113 | 2.12 |  |  |  | 2.12
WEBER 1114 | 163481114 | 9.8 |  |  |  | 9.8
WEBER 1115 | 163481115 | 14.66 |  |  |  | 14.66
WEEDPATCH 1101 | 252971101 | 20.32 |  |  |  | 20.32
WEEDPATCH 1102 | 252971102 | 18.17 |  |  |  | 18.17
WEEDPATCH 1103 | 252971103 | 18.05 |  |  |  | 18.05
WEEDPATCH 1105 | 252971105 | 0.96 |  |  |  | 0.96
WEEDPATCH 1106 | 252971106 | 64.45 |  |  |  | 64.45
WEIMAR 1101 | 152491101 | 78.71 |  | 78.71 |  | 0
WEIMAR 1102 | 152491102 | 36.6 |  | 36.6 |  | 0
WELLFIELD 1102 | 254291102 | 37.87 |  |  |  | 37.87
WELLFIELD 1103 | 254291103 | 0.32 |  |  |  | 0.32
WELLFIELD 1104 | 254291104 | 5.27 |  |  |  | 5.27
WEST FRESNO 1101 | 253731101 | 16 |  |  |  | 16
WEST FRESNO 1102 | 253731102 | 4.16 |  |  |  | 4.16
WEST FRESNO 1103 | 253731103 | 5.9 |  |  |  | 5.9
WEST FRESNO 1104 | 253731104 | 16.63 |  |  |  | 16.63
WEST FRESNO 1105 | 253731105 | 6.02 |  |  |  | 6.02
WEST FRESNO 1106 | 253731106 | 5.92 |  |  |  | 5.92
WEST FRESNO 1107 | 253731107 | 4.32 |  |  |  | 4.32
WEST FRESNO 1108 | 253731108 | 2.48 |  |  |  | 2.48
WEST FRESNO 1109 | 253731109 | 20.28 |  |  |  | 20.28
WEST FRESNO 1110 | 253731110 | 5.25 |  |  |  | 5.25
WEST FRESNO 1111 | 253731111 | 27.95 |  |  |  | 27.95
WEST FRESNO 1112 | 253731112 | 29.37 |  |  |  | 29.37
WEST LANE 1101 | 163621101 | 10.01 |  |  |  | 10.01
WEST LANE 1102 | 163621102 | 14.57 |  |  |  | 14.57
WEST LANE 1103 | 163621103 | 4.91 |  |  |  | 4.91
WEST POINT 1101 | 163201101 | 63.13 | 63.09 | 0.04 |  | 0
WEST POINT 1102 | 163201102 | 252.39 | 184.3 | 67.58 |  | 0.51
WEST SACRAMENTO 1104 | 63131104 | 11.92 |  |  |  | 11.92
WEST SACRAMENTO 1105 | 63131105 | 6.31 |  |  |  | 6.31
WEST SACRAMENTO 1106 | 63131106 | 2.85 |  |  |  | 2.85
WEST SACRAMENTO 1107 | 63131107 | 18.71 |  |  |  | 18.71
WEST SACRAMENTO 1108 | 63131108 | 8.73 |  |  |  | 8.73
WEST SACRAMENTO 1109 | 63131109 | 39.04 |  |  |  | 39.04
WEST SACRAMENTO 1110 | 63131110 | 8.4 |  |  |  | 8.4
WEST SACRAMENTO 1111 | 63131111 | 0.01 |  |  |  | 0.01
WESTLAKE 0401 | 22600401 | 0.81 |  |  |  | 0.81
WESTLAKE 0403 | 22600403 | 1.76 |  |  |  | 1.76
WESTLEY 1101 | 162671101 | 86.69 |  |  |  | 86.69
WESTLEY 1102 | 162671102 | 0.07 |  |  |  | 0.07
WESTLEY 1103 | 162671103 | 95.97 |  | 0.43 |  | 95.54
WESTPARK 1101 | 253701101 | 11.34 |  |  |  | 11.34
WESTPARK 1102 | 253701102 | 3.75 |  |  |  | 3.75
WESTPARK 1103 | 253701103 | 16.92 |  |  |  | 16.92
WESTPARK 1104 | 253701104 | 10.4 |  |  |  | 10.4
WESTPARK 1105 | 253701105 | 2.29 |  |  |  | 2.29
WESTPARK 1106 | 253701106 | 2.76 |  |  |  | 2.76
WESTPARK 1107 | 253701107 | 5.37 |  |  |  | 5.37
WESTPARK 1108 | 253701108 | 19.8 |  |  |  | 19.8
WESTPARK 1109 | 253701109 | 9.84 |  |  |  | 9.84
WESTPARK 1110 | 253701110 | 12.99 |  |  |  | 12.99
WESTPARK 1111 | 253701111 | 5.22 |  |  |  | 5.22
WESTPARK 1112 | 253701112 | 6.91 |  |  |  | 6.91
WHEATLAND 1101 | 152811101 | 0 |  |  |  | 0
WHEATLAND 1102 | 152811102 | 30.05 |  |  |  | 30.05
WHEATLAND 1104 | 152811104 | 113.44 |  |  |  | 113.44
WHEATLAND 1105 | 152811105 | 74.76 |  | 10.65 |  | 64.11
WHEELER RIDGE 1101 | 253481101 | 73.76 |  |  |  | 73.76
WHEELER RIDGE 1102 | 253481102 | 34.37 |  |  |  | 34.37
WHEELER RIDGE 1103 | 253481103 | 38.83 |  |  |  | 38.83
WHISMAN 1101 | 83631101 | 5.09 |  |  |  | 5.09
WHISMAN 1102 | 83631102 | 1.76 |  |  |  | 1.76
WHISMAN 1103 | 83631103 | 2.67 |  |  |  | 2.67
WHISMAN 1104 | 83631104 | 0 |  |  |  | 0
WHISMAN 1105 | 83631105 | 0.96 |  |  |  | 0.96
WHISMAN 1106 | 83631106 | 7.12 |  |  |  | 7.12
WHISMAN 1107 | 83631107 | 0.13 |  |  |  | 0.13
WHISMAN 1108 | 83631108 | 7.33 |  |  |  | 7.33
WHISMAN 1110 | 83631110 | 1.99 |  |  |  | 1.99
WHISMAN 1111 | 83631111 | 2.2 |  |  |  | 2.2
WHITMORE 1101 | 103601101 | 90.96 | 31.87 | 59.09 |  | 0
WHITNEY 0402 | 13240402 | 1.85 |  |  |  | 1.85
WILDWOOD 1101 | 103611101 | 32.18 |  | 32.18 |  | 0
WILKINS SLOUGH 1101 | 62771101 | 52.44 |  |  |  | 52.44
WILKINS SLOUGH 1102 | 62771102 | 62.19 |  |  |  | 62.19
WILKINS SLOUGH 1103 | 62771103 | 34.46 |  |  |  | 34.46
WILLIAMS 1101 | 62051101 | 32.67 |  |  |  | 32.67
WILLIAMS 1102 | 62051102 | 98.73 |  |  |  | 98.73
WILLITS 1102 | 42661102 | 11.27 |  | 4.79 |  | 6.48
WILLITS 1103 | 42661103 | 154.71 | 49.97 | 91.44 |  | 13.3
WILLITS 1104 | 42661104 | 96.02 | 50.93 | 36.44 |  | 8.65
WILLOW CREEK 1101 | 192171101 | 56.6 | 25.95 | 20.11 |  | 10.54
WILLOW CREEK 1102 | 192171102 | 9.56 | 5.31 | 4.25 |  | 0
WILLOW CREEK 1103 | 192171103 | 76.19 | 0.54 | 74.5 |  | 1.15
WILLOW PASS 1101 | 13911101 | 7.07 |  | 1.12 |  | 5.95
WILLOW PASS 1102 | 13911102 | 5.1 |  |  |  | 5.1
WILLOW PASS 2107 | 13912107 | 3.08 |  | 0.66 |  | 2.42
WILLOW PASS 2108 | 13912108 | 21.22 |  | 0.23 |  | 20.99
WILLOWS A 1101 | 102741101 | 4.28 |  |  |  | 4.28
WILLOWS A 1103 | 102741103 | 9.85 |  |  |  | 9.85
WILLOWS A 1104 | 102741104 | 9.39 |  |  |  | 9.39
WILSON 1101 | 254301101 | 16.5 |  |  |  | 16.5
WILSON 1102 | 254301102 | 30.38 |  |  |  | 30.38
WILSON 1103 | 254301103 | 115.45 |  |  |  | 115.45
WINDSOR 1101 | 43501101 | 6.4 |  |  |  | 6.4
WINDSOR 1102 | 43501102 | 14.67 |  |  |  | 14.67
WINDSOR 1103 | 43501103 | 11.24 |  | 1.98 |  | 9.26
WINTERS 1101 | 63321101 | 12.9 |  |  |  | 12.9
WINTERS 1102 | 63321102 | 35.49 |  |  |  | 35.49
WISE 1101 | 152271101 | 13.61 |  | 5.77 |  | 7.84
WISE 1102 | 152271102 | 119.01 |  | 114.01 |  | 5
WISHON 1101 | 251511101 | 7.59 | 3.48 | 4.12 |  | -0.01
WOLFE 1104 | 83671104 | 6.79 |  |  |  | 6.79
WOLFE 1105 | 83671105 | 7.29 |  |  |  | 7.29
WOLFE 1106 | 83671106 | 9.13 |  |  |  | 9.13
WOLFE 1107 | 83671107 | 10.63 |  |  |  | 10.63
WOLFE 1109 | 83671109 | 8.89 |  |  |  | 8.89
WOLFE 1110 | 83671110 | 2.02 |  |  |  | 2.02
WOLFE 1113 | 83671113 | 17.29 |  |  |  | 17.29
WOLFE 1114 | 83671114 | 2.92 |  |  |  | 2.92
WOOD 0401 | 13380401 | 3.32 |  | 0.17 |  | 3.15
WOODACRE 1101 | 43021101 | 38.41 | 22.83 | 7.8 |  | 7.78
WOODACRE 1102 | 43021102 | 31.02 | 19.29 | 11.36 |  | 0.37
WOODLAND 1101 | 62031101 | 7.2 |  |  |  | 7.2
WOODLAND 1102 | 62031102 | 13.5 |  |  |  | 13.5
WOODLAND 1103 | 62031103 | 1.23 |  |  |  | 1.23
WOODLAND 1104 | 62031104 | 5.86 |  |  |  | 5.86
WOODLAND 1105 | 62031105 | 2.7 |  |  |  | 2.7
WOODLAND 1106 | 62031106 | 28.09 |  |  |  | 28.09
WOODLAND 1107 | 62031107 | 11.16 |  |  |  | 11.16
WOODLAND 1108 | 62031108 | 21.22 |  |  |  | 21.22
WOODLAND 1109 | 62031109 | 10.68 |  |  |  | 10.68
WOODLAND 1110 | 62031110 | 10.9 |  |  |  | 10.9
WOODLAND 1111 | 62031111 | 0.25 |  |  |  | 0.25
WOODLAND 1112 | 62031112 | 12.85 |  |  |  | 12.85
WOODLAND 1113 | 62031113 | 20.88 |  |  |  | 20.88
WOODSIDE 1101 | 24251101 | 61.87 | 42.65 | 0.49 |  | 18.73
WOODSIDE 1102 | 24251102 | 17.02 |  | 0.06 |  | 16.96
WOODSIDE 1104 | 24251104 | 44.13 | 7.16 | 13 |  | 23.97
WOODSIDE 1105 | 24251105 | 6.33 |  |  |  | 6.33
WOODWARD 2101 | 255292101 | 25.84 |  |  |  | 25.84
WOODWARD 2102 | 255292102 | 1.47 |  |  |  | 1.47
WOODWARD 2104 | 255292104 | 2.76 |  |  |  | 2.76
WOODWARD 2105 | 255292105 | 0.36 |  |  |  | 0.36
WOODWARD 2106 | 255292106 | 0.29 |  |  |  | 0.29
WOODWARD 2107 | 255292107 | 9.48 |  |  |  | 9.48
WOODWARD 2108 | 255292108 | 92.13 |  | 18.51 |  | 73.62
WOODWARD 2109 | 255292109 | 1.83 |  |  |  | 1.83
WRIGHT 1110 | 254641110 | 87.64 |  |  |  | 87.64
WYANDOTTE 1102 | 102911102 | 39.19 |  | 4.33 |  | 34.86
WYANDOTTE 1103 | 102911103 | 67.04 | 38.68 | 15.28 |  | 13.08
WYANDOTTE 1105 | 102911105 | 25.68 | 0.68 | 16.11 |  | 8.89
WYANDOTTE 1106 | 102911106 | 94.31 |  | 0.55 |  | 93.76
WYANDOTTE 1107 | 102911107 | 154.94 | 9.92 | 101.39 |  | 43.63
WYANDOTTE 1109 | 102911109 | 117.8 |  | 52.17 |  | 65.63
WYANDOTTE 1110 | 102911110 | 39.32 |  | 12.63 |  | 26.69
YOSEMITE 0401 | 22490401 | 3.55 |  |  |  | 3.55
YOSEMITE 0402 | 22490402 | 2.4 |  |  |  | 2.4
YOSEMITE 0403 | 22490403 | 0 |  |  |  | 0
ZACA 1101 | 182681101 | 26.18 | 1.3 | 16.63 |  | 8.25
ZACA 1102 | 182681102 | 80.28 | 22.35 | 40.6 |  | 17.33
ZAMORA 1105 | 63191105 | 45.61 |  |  |  | 45.61
ZAMORA 1106 | 63191106 | 52.81 |  |  |  | 52.81
ZAMORA 1107 | 63191107 | 76.92 |  |  |  | 76.92
|  |  | 6926.27 | 18133.67
25059.94